## Subparts 1, 2, 3
|  | 1) | 2) | 3)
| Mitigation | Projected Average Capital Cost per Circuit Mile of Projects Expected to be Completed in 2025 | Average Capital Cost per Circuit Mile of Projects Completed from January 1, 2021 to June 30, 2024 | Average Operation and Maintenance Cost per Circuit Mile of Projects Completed from January 1, 2021 to June 30, 2024 | Notes
i | Covered Conductor Installation; | Fire Rebuild: $2,280,610 Base SH: $1,187,633 | Fire Rebuild: $805,149 Base SH: $931,545 | Please note that operation and maintenance costs after mitigation work is complete are not traceable to a specific mitigation | Base System Hardening (Base SH) and Fire Rebuild (FRRB) are separated to provide visibility to the differences between the two programs
ii | Undergrounding; | Fire Rebuild: $4,078,915 Base SH: $3,310,697 | Fire Rebuild: $3,034,556 Base SH: $2,881,040 | Please note that operation and maintenance costs after mitigation work is complete are not traceable to a specific mitigation | Base System Hardening (Base SH) and Fire Rebuild (FRRB) are separated to provide visibility to the differences between the two programs
iii | Distribution Pole Replacements and Reinforcements; |  |  |  | N/A - NOT MEASURED BY CIRCUIT MILE
iv | Distribution Traditional Hardening; | N/A | N/A | N/A | We do not have a separate program for overhead system component hardening that aligns with the updated OEIS definition of traditional overhead hardening. Please see Section 8.1.2.5.2 of our 2023-2025 WMP.
v | Transmission Pole/Tower Protections and Reinforcements; |  |  |  | N/A - NOT MEASURED BY CIRCUIT MILE
vi | Transmission Traditional Hardening; | 1522276 | 1522276 | Please note that operation and maintenance costs after mitigation work is complete are not traceable to a specific mitigation
vii | Transmission Shunt Splices; |  |  |  | N/A - NOT MEASURED BY CIRCUIT MILE
viii | Distribution Protective Devices; |  |  |  | N/A - NOT MEASURED BY CIRCUIT MILE
ix | Breakaway Connector; |  |  |  | N/A - NOT MEASURED BY CIRCUIT MILE
x | Surge Arrestor Removal/Replacement; |  |  |  | N/A - NOT MEASURED BY CIRCUIT MILE
xi | Distribution Motorized Switch Operator (MSO) Replacements; |  |  |  | N/A - NOT MEASURED BY CIRCUIT MILE
xii | Non-Exempt Expulsion Fuse Removal/Replacement; |  |  |  | N/A - NOT MEASURED BY CIRCUIT MILE
xiii | Microgrids, including remote grids; | Fire Rebuild: N/A Base SH: $1,414,069 | Fire Rebuild: N/A Base SH: $1,483,756 | Please note that operation and maintenance costs after mitigation work is complete are not traceable to a specific mitigation | Please note, data is included for Remote Grid work only. Base System Hardening (Base SH) and Fire Rebuild (FRRB) are separated to provide visibility to the differences between the two programs
xiv | Avian/animal protection plan (D) |  |  |  | N/A - NOT MEASURED BY CIRCUIT MILE
xv | Enhanced Powerline Safety Settings (EPSS); |  |  |  | N/A - NOT MEASURED BY CIRCUIT MILE
xvi | Distribution, Transmission, and Substation: Fire Action Schemes and Technology (DTS-FAST); |  |  |  | N/A - NOT MEASURED BY CIRCUIT MILE
xvii | Downed Conductor Detection (DCD); |  |  |  | N/A - NOT MEASURED BY CIRCUIT MILE
xviii | Rapid Earth Fault Current Limiter (REFCL); |  |  |  | N/A - NOT MEASURED BY CIRCUIT MILE
xix | Pole Mounted Sensors; |  |  |  | N/A - NOT MEASURED BY CIRCUIT MILE
xx | Early Fault Detection (EFD); |  |  |  | N/A - NOT MEASURED BY CIRCUIT MILE
xxi | Distribution Fault Anticipation (DFA); |  |  |  | N/A - NOT MEASURED BY CIRCUIT MILE
xxii | Smart Tape |  |  |  | N/A - NOT MEASURED BY CIRCUIT MILE

## Subparts 4, 5
|  | 4) |  | 5)
| Mitigation | Factors resulting in projects completed from January 1, 2021 to June 30, 2024, with capital cost per circuit mile 20% more than the average. | Discussion of how factors impact cost | Factors resulting in projects completed from January 1, 2021 to June 30, 2024, with capital cost per circuit mile 20% less than the average. | Discussion of how factors impact cost | Notes
i | Covered Conductor Installation; | Traffic Control Redesign Materials Challenging Terrain | These factors entail additional resources, time, and equipment that could contribute to a higher than average unit cost. | Accessible terrain Large scope | Accessible terrain: a location with terrain that is easier to work with can lead to decreased resources and time spent on construction Large scope: projects with a larger scope allow for the benefits of economy of scale
ii | Undergrounding; | Challenging Terrain Hard Rock Small Scope Overtime Traffic Control Restoration/Paving Redesign Spoils CUPA | These factors entail additional resources, time, and equipment that could contribute to a higher than average unit cost. | Method of Installation Favorable soil conditions Low material cost Minimal restoration Large scope | Method of Installation: where possible, boring is used to create a space for the underground conduit instead of digging a trench, and where possible, a rockwheel is used to dig a trench faster than traditional methods Favorable soil conditions: less time, resources, and equipment needed to trench Low material cost: leads to lower overall and unit cost Minimal restoration: less time, resources, and equipment needed to restore a construction site after construction Large scope: projects with a larger scope allow for the benefits of economy of scale
iii | Distribution Pole Replacements and Reinforcements; |  |  |  |  | N/A - NOT MEASURED BY CIRCUIT MILE
iv | Distribution Traditional Hardening; | N/A | N/A | N/A | N/A | We do not have a separate program for overhead system component hardening that aligns with the updated OEIS definition of traditional overhead hardening. Please see Section 8.1.2.5.2 of our 2023-2025 WMP.
v | Transmission Pole/Tower Protections and Reinforcements; |  |  |  |  | N/A - NOT MEASURED BY CIRCUIT MILE
vi | Transmission Traditional Hardening; | Access and access roads, Units to complete, Weather/Clearances, Helicopter, Cranes, Retrofit | Difficult to access locations may be more costly to construct, projects with larger scope and/or need for temporary generation may be more costly | Reverse of column C | Reverse of Column D
vii | Transmission Shunt Splices; |  |  |  |  | N/A - NOT MEASURED BY CIRCUIT MILE
viii | Distribution Protective Devices; |  |  |  |  | N/A - NOT MEASURED BY CIRCUIT MILE
ix | Breakaway Connector; |  |  |  |  | N/A - NOT MEASURED BY CIRCUIT MILE
x | Surge Arrestor Removal/Replacement; |  |  |  |  | N/A - NOT MEASURED BY CIRCUIT MILE
xi | Distribution Motorized Switch Operator (MSO) Replacements; |  |  |  |  | N/A - NOT MEASURED BY CIRCUIT MILE
xii | Non-Exempt Expulsion Fuse Removal/Replacement; |  |  |  |  | N/A - NOT MEASURED BY CIRCUIT MILE
xiii | Microgrids, including remote grids; | Traffic Control Redesign Challenging Terrain | These factors entail additional resources, time, and equipment that could contribute to a higher than average unit cost. | Accessible terrain Large scope | Accessible terrain: a location with terrain that is easier to work with can lead to decreased resources and time spent on construction Large scope: projects with a larger scope allow for the benefits of economy of scale | Please note, data is included for Remote Grid work only.
xiv | Avian/animal protection plan; |  |  |  |  | N/A - NOT MEASURED BY CIRCUIT MILE
xv | Enhanced Powerline Safety Settings (EPSS); |  |  |  |  | N/A - NOT MEASURED BY CIRCUIT MILE
xvi | Distribution, Transmission, and Substation: Fire Action Schemes and Technology (DTS-FAST); |  |  |  |  | N/A - NOT MEASURED BY CIRCUIT MILE
xvii | Downed Conductor Detection (DCD); |  |  |  |  | N/A - NOT MEASURED BY CIRCUIT MILE
xviii | Rapid Earth Fault Current Limiter (REFCL); |  |  |  |  | N/A - NOT MEASURED BY CIRCUIT MILE
xix | Pole Mounted Sensors; |  |  |  |  | N/A - NOT MEASURED BY CIRCUIT MILE
xx | Early Fault Detection (EFD); |  |  |  |  | N/A - NOT MEASURED BY CIRCUIT MILE
xxi | Distribution Fault Anticipation (DFA); |  |  |  |  | N/A - NOT MEASURED BY CIRCUIT MILE
xxii | Smart Tape |  |  |  |  | N/A - NOT MEASURED BY CIRCUIT MILE

## Subpart 6
| Covered Conductor - Base SH (Completed in 2023) | [5 empty] | Undergrounding - Base SH (Completed in 2023) | [5 empty] | Remote Grid (Completed in 2023) | [5 empty] | Transmission Traditional Hardening
| Project ID | Location (City) | Project length (circuit miles) | Project Capital Cost | Project Duration(a) (days) | Capital Cost per circuit mile | Project ID | Location (City) | Project length (circuit miles) | Project Capital Cost | Project Duration(a) (days) | Capital Cost per circuit mile | Project ID | Location (City) | Project length (circuit miles) | Project Capital Cost | Project Duration(a) (days) | Capital Cost per circuit mile | Project ID | Location | Project length (circuit miles) | Project Capital Cost | Project Duration(a) (days) | Capital Cost per circuit mile
Highest 1 | 35240166 | Manton | 0.4786 | 2470539.01 | 505 | 5162028.4815 | 35283938 | Redwood City | 0.45341 | 4063427.3 | 620 | 8961944.9223 | 35238088 | Mariposa | 0.83617 | 2240829.69 | N/A | 2679859.7425 | 74032944 | CRAGVIEW-CASCADE 115KV | 8.6 | 17436202.25 | 974 days | 2027465.3779
Highest 2 | 35279121 | Murphys | 0.14905 | 537109.02 | 327 | 3603476.0173 | 35330245 | Clearlake Oaks | 0.077273 | 661881.44 | 126 | 8565524.5176 | 35246501 | Santa Rosa | 0.70227 | 1636192.87 | 304 | 2329853.9249 | 74030726 | Drum-Rio Oso 115 kV | 16 | 28987823.3 | 2821 days | 1811738.9563
Highest 3 | 35094513 | Arnold | 1.785 | 4909512.9 | 1204 | 2750369.0305 | 35227001 | Middletown | 0.69924 | 5077685.74 | 706 | 7261695.7495 | 35229051 | Red Bluff | 1.9998 | 2778281.08 | N/A | 1389272.0999 | 74046318 | STANISLAUS-NEWARK #2 IDLE REMOVAL | 4 | 5920231.76 | 368 days | 1480057.94
Highest 4 | 35279122 | MI Wuk Village | 0.83598 | 2016898 | 535 | 2412601.1418 | 35390288 | Grass Valley | 0.10549 | 763559 | 387 | 7238045.8169 | [6 empty] | 74033653 | Fulton-Calistoga 60 kV Line | 12.4 | 16385366.69 | 809 days | 1321400.5395
Highest 5 | 35114040 | Pioneer | 1.4932 | 3480667.65 | 1185 | 2331040.7397 | 35290808 | Potter Valley | 0.20587 | 1433317.16 | 383 | 6962202.9483 | [6 empty] | 74046520 | PORT COSTA BRICKYARD TAP REMOVAL | 1.9 | 1827138.97 | 233 days | 961652.0895
Highest 6 | 35219588 | Mariposa | 0.92273 | 1978029.27 | 502 | 2143677.0414 | 35259512 | Bella Vista | 0.10739 | 747574.69 | 569 | 6961542.0868 | [6 empty] | 74046382 | NEWARK LAWRENCE LAB 115KV COND. REMOVAL | 3 | 2464137.28 | 258 days | 821379.0933
Highest 7 | 35250577 | MI Wuk Village | 3.3477 | 7070151.4 | 571 | 2111925.7407 | 35227002 | Middletown | 0.43674 | 2928148.66 | 605 | 6704520.7827 | [6 empty] | 74046293 | Kilarc-Deschutes 60 kV Removal | 2.5 | 1001651.46 | 227 days | 400660.584
Highest 8 | 35250578 | MI Wuk Village | 2.225 | 4537617.23 | 535 | 2039378.5303 | 35342145 | Fairfield | 0.18068 | 1187736.3 | 429 | 6573634.8679 | [6 empty] | 74046341 | BRIGHTON-CLAYTON REMOVAL | 3 | 946732.33 | 359 days | 315577.4433
Highest 9 | 35362685 | Murphys | 0.42727 | 817280.85 | 519 | 1912784.9681 | 35223032 | Cool | 0.9358 | 5590190.9 | 725 | 5973731.6236 | [6 empty] | 74046298 | MENDOCINO # 1 60KV CONDUCTOR REMOVAL | 5 | 1180189.59 | 518 days | 236037.918
Highest 10 | 35337014 | Fairfield | 1.0078 | 1556430.53 | 200 | 1544437.737 | 35329009 | Oroville | 0.73163 | 4211038.86 | 553 | 5755704.1628
Lowest 10 | 35290298 | Ukiah | 1.1502 | 697046.44 | 384 | 606027.5322 | 35316567 | Cottonwood | 2.6917 | 4273792.35 | 380 | 1587786.6316
Lowest 9 | 35278888 | Paso Robles | 1.3629 | 817323.75 | 516 | 599703.9188 | 35337011 | Anderson | 2.9191 | 4579985.56 | 403 | 1568956.3198
Lowest 8 | 35264187 | Santa Ynez | 1.6919 | 988919.54 | 423 | 584517.5385 | 35332364 | Elk Creek | 1.0562 | 1608805.79 | 226 | 1523129.742
Lowest 7 | 35293845 | Potter Valley | 1.4479 | 844983.54 | 401 | 583585.7542 | 35339286 | Anderson | 1.9854 | 2997476.15 | 210 | 1509746.6443
Lowest 6 | 35283199 | Lakeport | 1.4758 | 848441.1 | 506 | 574919.0205 | 35293670 | Cool | 0.65417 | 927128.91 | 322 | 1417267.1236
Lowest 5 | 35264190 | Santa Ynez | 2.3576 | 1327152.42 | 431 | 562930.9751 | 35332363 | Elk Creek | 1.2686 | 1643663.14 | 310 | 1295691.457
Lowest 4 | 35264189 | Santa Ynez | 2.7369 | 1531437.25 | N/A | 559545.2688 | 35380376 | Covelo | 2.515 | 3054450.88 | 362 | 1214511.6836
Lowest 3 | 35264188 | Santa Ynez | 1.1292 | 579807.4 | N/A | 513482.5683 | 35338402 | Anderson | 1.4112 | 1609501.72 | 373 | 1140540.7437
Lowest 2 | 35293775 | Potter Valley | 0.81932 | 336100.68 | 391 | 410219.97 | 35421339 | Potter Valley | 0.37178 | 385868.22 | 33 | 1037893.1236
Lowest 1 | 35228188 | Middletown | 3.403 | 944411.74 | 442 | 277520.8141 | 35284364 | Murphys | 0.81458 | 729822.64 | 518 | 895945.9519
| Note: Base System Hardening (Base SH) and Fire Rebuild (FRRB) are separated to provide visibility to the differences between the two programs | [5 empty] | Note: Base System Hardening (Base SH) and Fire Rebuild (FRRB) are separated to provide visibility to the differences between the two programs | [5 empty] | Note: some projects do not currently have the necessary data in our system of record to calculate the project duration and are represented as "N/A"
| Covered Conductor - FRRB (Completed in 2023) | [5 empty] | Undergrounding -FRRB (Completed in 2023)
| Project ID | Location (City) | Project length (circuit miles) | Project Capital Cost | Project Duration(a) (days) | Capital Cost per circuit mile | Project ID | Location (City) | Project length (circuit miles) | Project Capital Cost | Project Duration(a) (days) | Capital Cost per circuit mile
Highest 1 | 35368118 | Berry Creek | 0.030303 | 119126.37 | 231 | 3931170.21 | 35290540 | Greenville | 1.4297 | 15293194.21 | 266 | 10696524.7621
Highest 2 | 35281816 | Burnt Ranch | 0.086174 | 329401.94 | 99 | 3822510.4246 | 35292780 | Greenville | 0.24318 | 2525074.63 | 465 | 10383484.4598
Highest 3 | 35280498 | Greenville | 0.15019 | 219514.31 | 274 | 1461583.2999 | 35282166 | Crescent Mills | 2.5703 | 24556127.6 | 494 | 9553927.7672
Highest 4 | 35342460 | Boulder Creek | 0.54129 | 773978.81 | 213 | 1429883.8757 | 35292755 | Greenville | 2.6481 | 24960547.85 | 338 | 9425811.2322
Highest 5 | 35398090 | Greenville | 0.46042 | 465300.76 | 159 | 1010607.9855 | 35334541 | Boulder Creek | 0.13617 | 1109248.06 | 359 | 8145799.3836
Highest 6 | 35396073 | Oroville | 0.16951 | 119797.48 | 136 | 706738.206 | 35292754 | Greenville | 4.0852 | 32780357.79 | 560 | 8024120.9611
Highest 7 | [6 empty] | 35281815 | Burnt Ranch | 0.51799 | 3796601.83 | 414 | 7329454.3555
Highest 8 | [6 empty] | 35318072 | Boulder Creek | 0.19413 | 1223735.95 | 507 | 6303732.5034
Highest 9 | [6 empty] | 35297693 | Burnt Ranch | 0.95928 | 4757421.87 | 116 | 4959365.7401
Highest 10 | [6 empty] | 35297694 | Burnt Ranch | 0.93371 | 4435344.38 | 121 | 4750226.8411
Lowest 10 | [6 empty] | 35297695 | Burnt Ranch | 0.45455 | 1108232.41 | 106 | 2438111.302
Lowest 9 | [6 empty] | 35374864 | Mariposa | 1.7504 | 3994654.78 | 367 | 2282165.899
Lowest 8 | [6 empty] | 35374862 | Mariposa | 1.6924 | 3834715.57 | 609 | 2265812.2437
Lowest 7 | [6 empty] | 35374686 | Mariposa | 2.5994 | 5735859.53 | 267 | 2206582.0268
Lowest 6 | [6 empty] | 35398093 | Greenville | 0.14508 | 313093 | 123 | 2158134.517
Lowest 5 | [6 empty] | 35375721 | Mariposa | 0.95928 | 2027810.08 | 619 | 2113886.9146
Lowest 4 | [6 empty] | 35374865 | Mariposa | 0.78883 | 1664060.18 | 294 | 2109540.8764
Lowest 3 | [6 empty] | 35290944 | Greenville | 0.48788 | 933137.25 | 350 | 1912641.5683
Lowest 2 | [6 empty] | 35297696 | Burnt Ranch | 0.8 | 1427641.98 | 515 | 1784552.475
Lowest 1 | [6 empty] | 35217274 | Pescadero | 2.5239 | 4367114.5 | 528 | 1730329.023