## Compatibility Table (D)
Mitigation | Covered Conductor Installation; | Undergrounding; | Distribution Pole Replacements and Reinforcements; | Distribution Traditional Hardening; | Distribution Protective Devices; | Breakaway Connector; | Surge Arrestor Removal/Replacement; | Distribution Motorized Switch Operator (MSO) Replacements; | Non-Exempt Expulsion Fuse Removal/Replacement; | Microgrids, including remote grids; | Avian/animal protection plan; | Enhanced Powerline Safety Settings (EPSS); | Distribution, Transmission, and Substation: Fire Action Schemes and Technology (DTS-FAST); | Downed Conductor Detection (DCD); | Rapid Earth Fault Current Limiter (REFCL); | Pole Mounted Sensors; | Early Fault Detection (EFD); | Distribution Fault Anticipation (DFA); | Smart Tape
Covered Conductor Installation;
Undergrounding; | Mitigations are not compatible/combination is impractical.
Distribution Pole Replacements and Reinforcements; | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk.
Distribution Traditional Hardening; | N/A | N/A | N/A
Distribution Protective Devices; | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | N/A
Breakaway Connector; | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | N/A | Mitigations are not compatible/combination is impractical.
Surge Arrestor Removal/Replacement; | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | N/A | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk.
Distribution Motorized Switch Operator (MSO) Replacements; | Mitigations are not compatible/combination is impractical. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are not compatible/combination is impractical. | N/A | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are not compatible/combination is impractical. | Mitigations are not compatible/combination is impractical.
Non-Exempt Expulsion Fuse Removal/Replacement; | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | N/A | Mitigations are not compatible/combination is impractical. | Mitigations are not compatible/combination is impractical. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are not compatible/combination is impractical.
Microgrids, including remote grids; | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | N/A | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are not compatible/combination is impractical. | Mitigations are not compatible/combination is impractical.
Avian/animal protection plan; | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | N/A | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are not compatible/combination is impractical. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk.
Enhanced Powerline Safety Settings (EPSS); | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | N/A | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are not compatible/combination is impractical. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible, but it is unknown if combination will further reduce wildfire risk. | Mitigations are compatible, but it is unknown if combination will further reduce wildfire risk. | Mitigations are not compatible/combination is impractical. | Mitigations are compatible and the combination will further reduce wildfire risk.
Distribution, Transmission, and Substation: Fire Action Schemes and Technology (DTS-FAST); | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Downed Conductor Detection (DCD); | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | N/A | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are not compatible/combination is impractical. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible, but it is unknown if combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are not compatible/combination is impractical. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | N/A
Rapid Earth Fault Current Limiter (REFCL); | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | N/A | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are not compatible/combination is impractical. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible, but it is unknown if combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are not compatible/combination is impractical. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are not compatible/combination is impractical. | N/A | Mitigations are not compatible/combination is impractical.
Pole Mounted Sensors; | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | N/A | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible, but it is unknown if combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | N/A | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk.
Early Fault Detection (EFD); | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | N/A | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are not compatible/combination is impractical. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are not compatible/combination is impractical. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | N/A | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk.
Distribution Fault Anticipation (DFA); | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | N/A | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are not compatible/combination is impractical. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are not compatible/combination is impractical. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | N/A | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are compatible and the combination will further reduce wildfire risk.
Smart Tape | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A

## Compatibility Table (T)
Mitigation | Transmission Pole/Tower Protections and Reinforcements | Transmission Traditional Hardening; | Transmission Shunt Splices;
Transmission Pole/Tower Protections and Reinforcements;
Transmission Traditional Hardening; | Mitigations are compatible and the combination will further reduce wildfire risk.
Transmission Shunt Splices; | Mitigations are compatible and the combination will further reduce wildfire risk. | Mitigations are not compatible/combination is impractical.

## Compatibility Table Notes (D)
Mitigation | Covered Conductor Installation; | Undergrounding; | Distribution Pole Replacements and Reinforcements; | Distribution Traditional Hardening; | Distribution Protective Devices; | Breakaway Connector; | Surge Arrestor Removal/Replacement; | Distribution Motorized Switch Operator (MSO) Replacements; | Non-Exempt Expulsion Fuse Removal/Replacement; | Microgrids, including remote grids; | Avian/animal protection plan; | Enhanced Powerline Safety Settings (EPSS); | Distribution, Transmission, and Substation: Fire Action Schemes and Technology (DTS-FAST); | Downed Conductor Detection (DCD); | Rapid Earth Fault Current Limiter (REFCL); | Pole Mounted Sensors; | Early Fault Detection (EFD); | Distribution Fault Anticipation (DFA); | Smart Tape
Covered Conductor Installation;
Undergrounding; | We list these mitigations as "not compatible" because we would only apply one to a given length of conductor, not both.
Distribution Pole Replacements and Reinforcements; |  | Mitigations are compatible assuming any length of the relevant circuit is not undergrounded.
Distribution Traditional Hardening; | We do not have a separate program for overhead system component hardening that aligns with the updated OEIS definition of traditional overhead hardening. Please see Section 8.1.2.5.2 of our 2023-2025 WMP. | Please see cell B5. | Please see cell B5.
Distribution Protective Devices; |  | Please see cell C4 |  | Please see cell B5.
Breakaway Connector; |  |  |  | Please see cell B5.
Surge Arrestor Removal/Replacement; |  | Please see cell C4 |  | Please see cell B5.
Distribution Motorized Switch Operator (MSO) Replacements; |  | Please see cell C4 |  | Please see cell B5.
Non-Exempt Expulsion Fuse Removal/Replacement; |  | Please see cell C4 |  | Please see cell B5.
Microgrids, including remote grids; |  | Please see cell C4 |  | Please see cell B5.
Avian/animal protection plan; |  | Please see cell C4 |  | Please see cell B5.
Enhanced Powerline Safety Settings (EPSS); |  | Please see cell C4 |  | Please see cell B5.
Distribution, Transmission, and Substation: Fire Action Schemes and Technology (DTS-FAST); | We are not actively executing this mitigation | Please see cell B14 | Please see cell B14 | Please see cells B5 and B14. | Please see cell B14 | Please see cell B14 | Please see cell B14 | Please see cell B14 | Please see cell B14 | Please see cell B14 | Please see cell B14 | Please see cell B14
Downed Conductor Detection (DCD); |  | Please see cell C4 |  | Please see cell B5. | [8 empty] | Please see cell B14
Rapid Earth Fault Current Limiter (REFCL); |  | Please see cell C4 |  | Please see cell B5. | [8 empty] | Please see cell B14
Pole Mounted Sensors; |  | Please see cell C4 |  | Please see cell B5. | [8 empty] | Please see cell B14
Early Fault Detection (EFD); |  | Please see cell C4 |  | Please see cell B5. | [8 empty] | Please see cell B14
Distribution Fault Anticipation (DFA); |  | Please see cell C4 |  | Please see cell B5. | [8 empty] | Please see cell B14
Smart Tape | We are not actively executing this mitigation | Please see cell B20 | Please see cell B20 | Please see cell B5. | Please see cell B20 | Please see cell B20 | Please see cell B20 | Please see cell B20 | Please see cell B20 | Please see cell B20 | Please see cell B20 | Please see cell B20 | Please see cells B14 and B20 | Please see cell B20 | Please see cell B20 | Please see cell B20 | Please see cell B20 | Please see cell B20

## Constraints
Mitigation | General Constraints Associated with Activity
Covered Conductor Installation; | Long spans have increased sag with covered conductor which at times may restrict its use and where tree removals are required but refused by owner/permitting.
Undergrounding; | Easements/permitting, some water/bridge crossings, environmental restrictions, culturally prohibited areas, steep slopes, and inaccessible terrain.
Distribution Pole Replacements and Reinforcements; | Distribution Pole Replacement: Access, Long lead permits Distribution Pole Reinforcements: Constraints #1 – There is minimum of (2) visits to the pole. First visit is a pre-fielding visit to visually collect information on the pole, delineate for 811 ticket, and to see if it’s a candidate to reinforce; No Construction or tools. If it is a candidate for reinforcement, a 2nd visit will be required for construction for reinforcement. Constraints #2 - Location of pole (ease of access for construction), weather, CGIs or Customer related access issues. Constraints #3 – Soil density or compaction, unknown below/above ground obstruction that may require more effort to drive the steel down.
Distribution Traditional Hardening; | N/A
Transmission Pole/Tower Protections and Reinforcements; | Access, long lead permitting, seasonal restrictions, clearance availability, etc.
Transmission Traditional Hardening; | Access, seasonal restrictions, clearance availability, etc.
Transmission Shunt Splices; | Access, helicopters may be required, weather can't use helicopters in high wind conditions
Distribution Protective Devices; | Easements/permitting restrictions,long lead permits such as Caltrans DSDD, inaccessible terrain, signal strength for SCADA communication, access issues due to customer refusal, seasonal restrictions, clearance availability, etc.
Breakaway Connector; | Only install the service breakaway disconnect in 1/0 Triplex neutral service drop (N-SD) service wire. Do not install over public roadways, on open-wire services, on poles with open-wire secondary, midspan, or on triplex aerial cable with ACSR neutral, or on the load side of a span of service wire.
Surge Arrestor Removal/Replacement; | Some locations may require pole to be replaced, Access issues due to customer refusal, Long lead permits such as Caltrans DSDD
Distribution Motorized Switch Operator (MSO) Replacements; | Some locations may require pole to be replaced, Access issues due to customer refusal, Long lead permits such as Caltrans DSDD
Non-Exempt Expulsion Fuse Removal/Replacement; | Some locations may require pole to be replaced, Access issues due to customer refusal, Long lead permits such as Caltrans DSDD
Microgrids, including remote grids; | Remote Grid: Customer load suitable to be served by remote grid system, land space/suitability (steep slopes, inaccessible terrain, shading), customer agreement, easement for site remote grid on customer land, easements for access, permitting, environmental restrictions, culturally prohibited areas.
Avian/animal protection plan; | Access, material unavailability or long lead time, clearances, time of year constraint (active nesting)
Enhanced Powerline Safety Settings (EPSS); | Access, Equipment failure, Material unavailability or long lead time, long lead time permits
Distribution, Transmission, and Substation: Fire Action Schemes and Technology (DTS-FAST); | N/A
Downed Conductor Detection (DCD); | Access, Equipment failure, Material unavailability or long lead time, long lead time permits
Rapid Earth Fault Current Limiter (REFCL); | Only 3-wire circuits, substation space limitations, charging current limits, only effective for ground faults
Pole Mounted Sensors; | Access, Long lead time permits, cell coverage requires a gateway install for Starlink
Early Fault Detection (EFD); | Access, pole space availibility, material lead times, construction permits, cell coverage,
Distribution Fault Anticipation (DFA); | Cell coverage
Smart Tape | N/A