## LU Table 2-1
LU Table 2‑1: Responsible Persons
WMP Section | Program Owner | Title
Executive-level Owner | Eric Schwarzrock | President
Section 1: Executive Summary | Eric Schwarzrock | President
Section 2: Responsible Persons | Jordan Parrillo | Manager, Rates and Regulatory Affairs
Section 3: Overview of WMP | Peter Stoltman | Director, Wildfire Prevention
Section 4: Overview of Service Territory | Peter Stoltman | Director, Wildfire Prevention
Section 5: Rick Methodology and Assessment | Cody Warner | Lead Analyst, Risk
| Peter Stoltman | Director, Wildfire Prevention
Section 6: Wildfire Mitigation Strategy Development | Cody Warner | Lead Analyst, Risk
| Peter Stoltman | Director, Wildfire Prevention
Section 7: Public Safety Power Shutoff | Peter Stoltman | Director, Wildfire Prevention
Section 8: Grid Design, Operations, and Maintenance | Peter Stoltman | Director, Wildfire Prevention
| Luis Garcia-Perez | Director, Engineering and Projects
| Amanda Chee | Project Manager II, Engineering
| Matt Wetzell | Senior Manager, Operations
Section 9: Vegetation Management and Inspections | Eric Oiler | Manager, Vegetation Management
Section 10: Situational Awareness and Forecasting | Scott Witt | Specialist III, Fire Protection
| Peter Stoltman | Director, Wildfire Prevention
Section 11: Emergency Preparedness, Collaboration and Public Awareness | Peter Stoltman | Director, Wildfire Prevention
| John Nalder | Manager, Emergency Management
| Anne Rarick | Lead, Community Outreach (Access and Functional Needs)
| Alison Vai | Senior Manager, Marketing and Communications
Section 12: Enterprise Systems | Peter Stoltman | Director, Wildfire Prevention
| Matt Wetzell | Senior Manager, Operations
| Eric Oiler | Manager, Vegetation Management
Section 13: Lessons Learned | Peter Stoltman | Director, Wildfire Prevention
Appendix A: Definitions | Jordan Parrillo | Manager, Rates and Regulatory Affairs
Appendix B: Supporting Documentation for Risk Assessment | Peter Stoltman | Director, Wildfire Prevention
Appendix C: Additional Maps | Peter Stoltman | Director, Wildfire Prevention
Appendix D: Areas for Continued Improvement | Peter Stoltman | Director, Wildfire Prevention
Appendix E: Referenced Regulations, Codes and Standards | Jordan Parrillo | Manager, Rates and Regulatory Affairs
Appendix F: Liberty 2026 AFN Plan | John Nalder | Manager, Emergency Management
| Anne Rarick | Lead, Community Outreach (Access and Functional Needs)

## LU Table 3-1
LU Table 3‑1: Liberty WMP Initiative Tracking IDs
WMP Initiative Category | WMP Initiative Activity | WMP Initiative ID
Risk Methodology and Assessment | Risk Methodology and Assessment | WMP-RISK-01
Grid Design, Operations, and Maintenance | Covered conductor installation | WMP-GDOM-GH-01
Grid Design, Operations, and Maintenance | Undergrounding of electric lines and/or equipment | WMP-GDOM-GH-02
Grid Design, Operations, and Maintenance | Distribution pole replacements and reinforcements | WMP-GDOM-GH-03
Grid Design, Operations, and Maintenance | Transmission pole/tower replacements and reinforcements | WMP-GDOM-GH-04
Grid Design, Operations, and Maintenance | Traditional overhead hardening | WMP-GDOM-GH-05
Grid Design, Operations, and Maintenance | Emerging grid hardening technology installations and pilot progress | WMP-GDOM-GH-06
Grid Design, Operations, and Maintenance | Microgrids | WMP-GDOM-GH-07
Grid Design, Operations, and Maintenance | Installation of system automation equipment | WMP-GDOM-GH-08
Grid Design, Operations, and Maintenance | Line removal (in HFTD) | WMP-GDOM-GH-09
Grid Design, Operations, and Maintenance | Other grid topology improvements to minimize risk of ignitions | WMP-GDOM-GH-10
Grid Design, Operations, and Maintenance | Other grid topology improvements to mitigate or reduce PSPS events | WMP-GDOM-GH-11
Grid Design, Operations, and Maintenance | Other technologies and systems not listed above: | WMP-GDOM-GH-12
Grid Design, Operations, and Maintenance | Tree attachment removals | WMP-GDOM-GH-12a
Grid Design, Operations, and Maintenance | Non-exempt fuse replacement | WMP-GDOM-GH-12b
Grid Design, Operations, and Maintenance | Animal guards | WMP-GDOM-GH-12c
Grid Design, Operations, and Maintenance | CalFIRE exempt hardware | WMP-GDOM-GH-12d
Grid Design, Operations, and Maintenance | Open wire/grey wire | WMP-GDOM-GH-12e
Grid Design, Operations, and Maintenance | Detailed inspections of distribution electric lines and equipment | WMP-GDOM-AI-01
Grid Design, Operations, and Maintenance | Intrusive pole inspections | WMP-GDOM-AI-02
Grid Design, Operations, and Maintenance | Patrol inspections of distribution electric lines and equipment | WMP-GDOM-AI-03
Grid Design, Operations, and Maintenance | Other discretionary inspections of distribution electric lines and equipment: Drone inspections | WMP-GDOM-AI-04
Grid Design, Operations, and Maintenance | Quality assurance / quality control of inspections | WMP-GDOM-AI-05
Grid Design, Operations, and Maintenance | Substation inspections | WMP-GDOM-AI-06
Grid Design, Operations, and Maintenance | Work Orders (Asset Management) | WMP-GDOM-AI-07
Grid Design, Operations, and Maintenance | Equipment maintenance and repair | WMP-GDOM-MR-01
Grid Design, Operations, and Maintenance | Equipment settings to reduce wildfire risk | WMP-GDOM-GO-01
Grid Design, Operations, and Maintenance | Grid response procedures and notifications | WMP-GDOM-GO-02
Grid Design, Operations, and Maintenance | Personnel work procedures and training in conditions of elevated fire risk | WMP-GDOM-GO-03
Grid Design, Operations, and Maintenance | Automatic recloser operations | WMP-GDOM-GO-04
Grid Design, Operations, and Maintenance | Asset Management and Inspection Enterprise System | WMP-GDOM-GO-05
Grid Design, Operations, and Maintenance | Workforce Planning (Asset Management) | WMP-GDOM-GO-06
Vegetation Management & Inspections | Vegetation Management Inspection Program - Detailed | WMP-VM-INSP-01
Vegetation Management & Inspections | Vegetation Management Inspection Program - Patrol | WMP-VM-INSP-02
Vegetation Management & Inspections | Vegetation Management Inspection Program - LiDAR | WMP-VM-INSP-03
Vegetation Management & Inspections | Pole Clearing – PRC 4292 Required | WMP-VM-VFM-01-R
Vegetation Management & Inspections | Pole Clearing – Discretionary | WMP-VM-VFM-01-D
Vegetation Management & Inspections | Wood and Slash Management | WMP-VM-VFM-02
Vegetation Management & Inspections | Substation Defensible Space | WMP-VM-VFM-03
Vegetation Management & Inspections | Integrated Vegetation Management | WMP-VM-VFM-04
Vegetation Management & Inspections | Clearance | WMP-VM-VFM-05
Vegetation Management & Inspections | Fall-In Mitigation | WMP-VM-VFM-06
Vegetation Management & Inspections | High-Risk Species | WMP-VM-VFM-07
Vegetation Management & Inspections | Emergency Response Vegetation Management | WMP-VM-VFM-08
Vegetation Management & Inspections | Vegetation Management Enterprise System | WMP-VM-ESG-01
Vegetation Management & Inspections | Quality Assurance and Quality Control | WMP-VM-QAQC-01
Vegetation Management & Inspections | Workforce Planning | WMP-VM-WFP-01
Situational Awareness & Forecasting | Environmental monitoring systems | WMP-SA-01
Situational Awareness & Forecasting | Grid monitoring systems | WMP-SA-02
Situational Awareness & Forecasting | Fire detection and alarm systems | WMP-SA-03
Situational Awareness & Forecasting | Weather forecasting | WMP-SA-04
Situational Awareness & Forecasting | Fire Potential Index | WMP-SA-05
Emergency Preparedness | Wildfire and PSPS emergency preparedness plan | WMP-EP-01
Emergency Preparedness | Collaboration and coordination with public safety partners | WMP-EP-02
Emergency Preparedness | Public notification and communication strategy | WMP-EP-03
Emergency Preparedness | Preparedness and planning for service restoration | WMP-EP-04
Emergency Preparedness | Customer support in wildfire and PSPS emergencies | WMP-EP-05
Emergency Preparedness | Learning after wildfire and PSPS events | WMP-EP-06
Community Outreach and Engagement | Public outreach and education awareness for wildfires, PSPS, outages from protective equipment and device settings, and vegetation management | WMP-CO-01
Community Outreach and Engagement | Public engagement in WMP decision-making process | WMP-CO-02
Community Outreach and Engagement | Engagement with AFN populations, local governments, and tribal communities | WMP-CO-03
Community Outreach and Engagement | Collaboration on local wildfire mitigation and planning | WMP-CO-04
Community Outreach and Engagement | Best practice sharing with other electrical corporations | WMP-CO-05

## Table 3-1
Table 3‑1: List of Risks and Risk Drivers to Prioritize
Priority | Risk | Risk Driver | % of ignitions in HFTD | Topographical and Climatological Risk Factors
1 | Equipment / facility failure or damage | Connector device | 15.79% | Extreme weather, heat, wind
1 | Vegetation contact | Fall-in (branch failure) | 10.53% | Elevation, slope, wind, extreme weather
1 | Vegetation contact | Fall-in (trunk failure) | 10.53% | Elevation, slope, wind, extreme weather
1 | Equipment / facility failure or damage | Conductor | 10.53% | Extreme weather, heat, wind
1 | Wire-to-wire contact | Wire-to-wire contact | 5.26% | Extreme weather, heat, wind
1 | Vegetation contact | Fall-in (root failure) | 0 | Elevation, slope, wind, extreme weather
1 | Vegetation contact | Blow-in | 0 | Elevation, slope, wind, extreme weather
1 | Vegetation contact | Grow-in | 0 | Elevation, slope, wind, extreme weather
1 | Equipment / facility failure or damage | Fuse | 0 | Extreme weather, heat, wind
1 | Protective Device Operation | Protective Device Operation | 0 | Extreme weather, wind
2 | Contact from object | Animal contact | 10.53% | N/A
2 | Equipment / facility failure or damage | Other | 5.26% | Extreme weather, heat, wind
2 | Equipment / facility failure or damage | Anchor/guy | 0 | Extreme weather, heat, wind
2 | Equipment / facility failure or damage | Capacitor bank | 0 | Extreme weather, heat, wind
2 | Equipment / facility failure or damage | Cross arm | 0 | Extreme weather, heat, wind
2 | Equipment / facility failure or damage | Cutout | 0 | Extreme weather, heat, wind
2 | Equipment / facility failure or damage | Insulator and bushing | 0 | Extreme weather, heat, wind
2 | Equipment / facility failure or damage | Lightning arrestor | 0 | Extreme weather, heat, wind
2 | Equipment / facility failure or damage | Pole | 0 | Extreme weather, heat, wind
2 | Equipment / facility failure or damage | Recloser | 0 | Extreme weather, heat, wind
2 | Equipment / facility failure or damage | Relay | 0 | Extreme weather, heat, wind
2 | Equipment / facility failure or damage | Sectionalizer | 0 | Extreme weather, heat, wind
2 | Equipment / facility failure or damage | Splice | 0 | Extreme weather, heat, wind
2 | Equipment / facility failure or damage | Switch | 0 | Extreme weather, heat, wind
2 | Equipment / facility failure or damage | Tap | 0 | Extreme weather, heat, wind
2 | Equipment / facility failure or damage | Tie wire | 0 | Extreme weather, heat, wind
2 | Equipment / facility failure or damage | Transformer | 0 | Extreme weather, heat, wind
2 | Equipment / facility failure or damage | Voltage regulator / booster | 0 | Extreme weather, heat, wind
2 | Equipment / facility failure or damage | Unknown | 0 | Extreme weather, heat, wind
3 | Unknown | Unknown | 10.53% | N/A
3 | Contact from object | Unknown | 5.26% | Extreme weather, heat, wind
3 | Vandalism/ theft | Vandalism / theft | 5.26% | N/A
3 | Contact from object | Ballon contact | 0 | Wind
3 | Contact from object | Land vehicle contact | 5.26% | N/A
3 | Contact from object | Aircraft vehicle contact | 0 | N/A
3 | Contact from object | Third-party contact | 5.26% | N/A
3 | Contact from object | Other contact from object | 0 | N/A
3 | Contamination | Contamination | 0 | Extreme weather, heat, wind
3 | Lightning | Lightning | 0 | Extreme weather
3 | Dig-in | Dig-in | 0 | N/A

## Table 3-2
Table 3‑2: Self-Identified Performance Metrics (N/A) [1]
[1] Liberty does not use performance metrics beyond those required by Energy Safety and thus does not provide a Table 3-2.

## Table 3-3
Table 3‑3: Summary of Liberty Projected WMP Expenditures, 2027
Year of WMP Cycle | Projected Spend (thousands $USD)
2027 | 44924

## Table 4-1
Table 4-1: Liberty Service Territory High-Level Statistics
Characteristic | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | Total
Area served (square miles) | 922.78 | 13.17 | 547.92 | 1483.87
Number of customers served | 42851 | 2956 | 3509 | 49316
Overhead transmission lines (circuit miles) | 28.41 | 2.36 | 2.12 | 32.89
Overhead distribution lines (circuit miles) | 1251.66 | 124.18 | 90.23 | 1466.07
Underground transmission lines (circuit miles) | 1.3 | 0 | 0 | 1.3
Underground distribution lines (circuit miles) | 544.63 | 10.33 | 38.8 | 593.76
Hardened overhead transmission lines (circuit miles) | 0 | 0 | 0 | 0
Hardened overhead distribution lines (circuit miles) | 47.45 | 0 | 0 | 47.45
Substations (#) | 9 | 1 | 2 | 12
Power generation facilities (#) | 0 | 0 | 0 | 0
Distribution transformers (#) | 7016 | 367 | 578 | 7961
Reclosers (#) | 41 | 1 | 3 | 45
Poles (#) | 21071 | 1726 | 1756 | 24553
Microgrids (#) | 1 | 0 | 0 | 1

## Table 4-2
Table 4‑2: Liberty Catastrophic Wildfire History [19]
Ignition Date | Fire Name | Official Cause | Fire Size | No. of Fatalities | No. of Structures Destroyed and Damaged | Financial Loss (US$) | Lessons Learned
(acres)
2020-11-17 | Mountain View Fire | Unknown | 20385 | 1 | 80 destroyed | $184M | Developed new PSPS screening criteria to account for late season weather conditions that occurred on the day of the fire.
[19] Source: https://ready.mono.ca.gov/pages/mountainview-fire.

## Table 4-3
Table 4‑3: Frequently Deenergized Circuits
Circuit ID | Name of Circuit | Dates of Outages | Number of Customer Hours of PSPS per Outage | Measures Taken, or Planned to Be Taken to Reduce the Need for and Impact of Future PSPS of Circuit | Estimated Annual Decline in PSPS Events and PSPS Impact on Customers
Muller 1296 | Muller 1296 | 11/11/2024, 11/20/2024, 11/22/2024, and 11/5/2025 | 10,516.33, 12,350.78, 9,550.23, and 9,261.2 | Measures taken include the installation of covered conductor, distribution pole replacements and reinforcements, additional situational awareness, sectionalizing devices, and Sensitive Relay Profile | Not currently quantified

## LU Table 5-1
LU Table 5-1: Taxonomy of Outage Causes
Driver | Sub-Driver | Cause Description
Asset | Third-Party Contact | • Contact from public • Contractors • Inanimate objects
Asset | Animal Contact | • Animal-initiated contact with energized equipment or conductor
Asset | Equipment Failure | • Hardware • Conductor • Connector • Transformer • Fuse
Asset | Vehicle Contact | • Vehicle contact with pole • Conductor • Guy wire
Asset | Asset Other | • Other known asset-related outage
Geo | Snow / Ice | • Snow loading • Ice loading • Snow shed • Ice-related asset impact
Geo | Vegetation | • Tree • Limb • Grow-in • Fall-in • Other vegetation contact with conductor or equipment
Geo | Weather (other) | • Lightning • Rain • Flooding
Geo | Wind | • Wire slap • Wind-driven conductor contact • Object-blow in

## LU Table 5-2
LU Table 5-2: Confusion Matrix for Probability of Outage Model
Model Prediction
Actual Event |  | No Outage | Outage
| No Outage | 648 | 378
| Outage | 408 | 638

## LU Table 5-3
LU Table 5-3: Estimated Historical Wildfire Losses Within 100 Miles of Liberty's Service Territory
|  | Count |  |  | Monetized ($ millions) Using Liberty's Consequence Parameters
Year​ | Fire Name​ | Buildings Destroyed | Acres Burned | Fatalities | Buildings Destroyed | Acres Burned | Fatalities | Total | Log Total
2018 | Camp | 18804 | 153336 | 85 | 18804 | 358 | 1394 | 20556 | 10.3
2021 | Dixie | 1311 | 963309 | 0 | 1311 | 2250 | 0 | 3561 | 9.6
2020 | North Complex | 2352 | 318935 | 16 | 2352 | 745 | 262 | 3359 | 9.5
2020 | Creek | 858 | 379895 | 0 | 858 | 887 | 0 | 1745 | 9.2
2024 | Park | 713 | 429603 | 0 | 713 | 1004 | 0 | 1717 | 9.2
2021 | Caldor | 1005 | 221835 | 0 | 1005 | 518 | 0 | 1523 | 9.2
2015 | Butte | 928 | 70868 | 2 | 928 | 166 | 33 | 1126 | 9.1
2013 | Rim | 112 | 257314 | 0 | 112 | 601 | 0 | 713 | 8.9
2017 | Detwiler | 134 | 81826 | 0 | 134 | 191 | 0 | 325 | 8.5
2017 | Cascade (Wind Complex) | 264 | 9989 | 0 | 264 | 23 | 0 | 287 | 8.5
2022 | Oak | 194 | 19244 | 0 | 194 | 45 | 0 | 239 | 8.4
2018 | Donnell | 135 | 36450 | 0 | 135 | 85 | 0 | 220 | 8.3
2021 | River | 154 | 9656 | 0 | 154 | 23 | 0 | 177 | 8.2
2020 | Mountain View | 97 | 20385 | 1 | 97 | 48 | 16 | 161 | 8.2
2017 | Wall | 93 | 6033 | 0 | 93 | 14 | 0 | 107 | 8

## LU Table 5-4
LU Table 5-4: Wildfire Monetary Consequence Parameters
Category | Consequence | Units | Value
Financial | Buildings Destroyed | $/Building | 1000000
Financial | Suppression Cost | $/Acre Burned | 876
Financial | Restoration Cost | $/Acre Burned | 1460
Safety | Fatalities | $/Fatality | 16500000
Safety | Fatalities | Fatality/Building Destroyed | 1/256
Safety | Serious Injuries | $/Serious Injury | 4125000
Safety | Serious Injuries | Serious Injury/Building Destroyed | 1/107

## LU Table 5-5
LU Table 5-5: Reliability Consequence Parameters
Customer Class | $/Customer Minute Interrupted
Residential | 0.081
Non-Residential | 23.47
System Average | 2.63
Table Notes: Calculated using Berkeley Lab’s ICE Calculator v2.2

## Table 5-1
Table 5-1: Primary Risk Modeling Assumptions and Limitations
Applicable Model | Assumption | Justification | Limitation
Wildfire Spread Model | The physical framework development is based on an idealized situation in steady state spread, which may not fit some extreme behavior of fires | The model is semi-empirical and as a result does not capture all possible wildfire scenarios | The model may not represent unique weather cases
Wildfire Spread Model | Fuels are assumed to be continuous and uniform for the scale of the input (typically 10-to-30-meter resolution) | This is the highest resolution data available across the service territory, and the standard for fuels mapping for fire agencies and IOUs in the US | Real fuels are more granular and thus not captured by the fire spread modeling
Wildfire Spread Model | Fire characteristics at a point consider only the conditions at that point (point-functional model) | Point-functional models are much faster to solve than non-local ones | Several non-local effects, such as radiation concentration from different parts of the front, are not considered
Wildfire Spread Model | Fire spread is assumed to be elliptical, although several variations exist (double ellipse, oval, egg-shape) | Fire perimeters obtained in constant wind and slope conditions are known to have a pseudo-elliptical shape; the difference between existing fire shape models is small | This approach only captures a macroscopic shape of the perimeter
Wildfire Spread Model | Weather is given hourly and assumed to remain constant during that time | Computing sub-hourly wind speeds is expensive, not standard among fire agencies or IOUs, and sub-hourly data is not readily available | Winds change more rapidly than at the hour level and thus are not captured by the fire spread model
Wildfire Spread Model | Reliability of weather inputs in the mid-range forecast (2 to 5 days) | Weather forecasts become less accurate further out in time; however, WRF models are proven accurate in reflecting past weather scenarios and predicting short-term future scenarios | Fire spread models are impacted due to imperfect weather
Wildfire Spread Model | Fire is not coupled with the atmosphere in any way | It is not technically feasible to run millions of simulations considering the coupling effect given current science and technology | Fire-atmosphere interactions are not captured
Wildfire Spread Model | Fire is assumed to be fully developed; fire acceleration, flashover, and decay are not considered | Fire acceleration only affects the initial time of fire expansion, and its effect on an 8-hour simulation may not be significant | Models are not valid for short-duration fires
Wildfire Spread Model | Atmospheric instability, which may have a deep impact on rate of spread, is not considered | Capturing atmospheric instability is challenging with the forecast data presently available | There is a significant range of fire behavior that may not be considered in the model
Wildfire Spread Model | Gusts are not considered in the model | Gust duration is highly unpredictable and could affect the fire very differently | Fire behavior at a lower scale is not expected to follow a simple symmetrical behavior with respect to wind and slope.
Wildfire Spread Model | No interaction between slope and wind other than creating an effective or equivalent wind | The slope-wind effect is known to be significantly symmetrical in fires under control conditions, and few non-physical models describe it non-symmetrically | Fire behavior at a lower scale is not expected to follow a simple symmetrical behavior with respect to wind and slope
Wildfire Spread Model | Fuel array description of the vegetation may not perfectly describe fuel characteristics | There are no perfect fuel datasets available at the territory scale; additional custom fuel models have been developed for WUI, agricultural, and timber areas | Fuel characteristics are not captured perfectly by the fire spread model
Wildfire Spread Model | Spotting is only considered in surface fires | Calculating crown spotting would require an accurate tree inventory (height, species, width) | Wildfire spread for crown fires is impacted
Risk Model Architecture | Risk is calculated at the circuit level, and all inputs are aggregated to the circuit level and assumed representative of the entire circuit | Circuit-level analysis matches the granularity and maturity of Liberty's currently available datasets | Wildfire risk is not homogeneous along a circuit, especially given varying circuit lengths
Risk Model Architecture | The model is developed on 45 circuits over a four-year outage record | This represents the set of Liberty's modeled distribution circuits with high-quality outage data available | Small sample size constrains statistical power, and model outputs may be sensitive to the addition of new data
Probability of Outage | Outages with no determinable cause are excluded from training | Unknown events cannot be reliably attributed to a failure mode and would introduce label noise | May under-represent failure modes that are inherently difficult to diagnose in the field, if such modes correlate with "unknown cause"
Probability of Outage | Planned outages and loss of supply are excluded | Planned outages are within Liberty's operational control and likely account for minimal wildfire risk | The model may under-represent wildfire risk from planned outages that could lead to an ignition
Probability of Outage | Circuits with zero primary overhead conductor miles are excluded
Probability of Outage | Training uses a balanced (50/50) outage/non-outage sample, and raw probabilities are rescaled per circuit before use | Balancing is standard practice to prevent the classifier from being biased toward the much larger non-outage class | Raw model output cannot be interpreted as a real-world probability directly and rescaling is required for usability in the risk model
Probability of Outage | Circuits with no recorded historical outages are assigned a scaling factor of 0.0005 rather than zero | Represents a very low baseline outage frequency (fewer than one expected outage in four years) while preventing an absence of historical outages from producing a zero risk estimate | The assigned floor is a modeling convention, not an empirically derived rate
Probability of Outage | Where a VPD/wind bin contains no modeled circuit-days, the bin's mean probability is assigned 0.0005 | Avoids an undefined value in the weighted bin aggregation
Probability of Outage | Weather stations more than 50 km from a circuit are excluded and elevation differences are not used in station weighting |  | Circuits without a nearby station may have less representative weather features, and elevation-driven weather effects in complex terrain are not separately captured
Probability of Outage | Historical weather observations from 2022–2025 are assumed representative of future weather conditions | Represents the full period over which consistent station observations and cause-coded outage records overlap | No adjustment is applied for projected climate change in current outage model
Probability of Outage | Transmission outage likelihood uses a different data source (lockout/operations logs) and is not cause-code filtered | Transmission events are relatively rare and tracked through a different operational system from distribution outages
Probability of Ignition | EFW is defined as VPD ≥ 2 kPa and maximum wind gust ≥ 50 mph occurring together | The VPD threshold was selected against a 12-year regional record of wildfires ≥5,000 acres using Peirce and Heidke skill scores, and VPD was selected over maximum temperature for physical interpretability despite a marginally lower skill score | A single fixed threshold is not varied by circuit, season, or local terrain
Probability of Ignition | The wind gust component of the EFW threshold is derived from Liberty's historical PSPS operational experience rather than fitted to fire-occurrence data
Probability of Ignition | Wildfire records used to calibrate the VPD threshold are regional (within 100 miles) and not limited to utility-caused ignitions | Liberty's own utility-caused ignition record and wildfire history is too sparse | The threshold reflects regional wildfire conditions generally rather than utility-specific ignitions within Liberty's service territory
Probability of Ignition | EFW occurrence at the circuit-level is estimated using 2022–2025 data only | Matches the period of overlapping weather station and outage data used to train the model | Four years is a short time horizon to estimate the combined frequency of VPD and wind gusts across the service territory
Probability of Ignition | The conditional probability of ignition given an outage under EFW conditions is set equal to 1, and outages outside EFW conditions are assumed to contribute zero wildfire ignition risk | Liberty's historical ignition record is too sparse to support an empirical ignition model | Assigns zero wildfire risk to outages below the EFW threshold
Probability of Ignition | Ignition likelihood and burn likelihood are produced as a single blended value rather than as two separately calculated components | Liberty's historical ignition record is too sparse to support an empirical ignition model and measure of burn likelihood | Specifying separate likelihood model components for (1) outages, (2) ignitions, and (3) wildfires, allows for additional modeling of response times, situational awareness, and other measures to contain ignitions
Wildfire Consequence | The 100th-percentile Technosylva consequence scenario is used as a fixed conditional severity value | The rarity of catastrophic outcomes is captured by ignition likelihood and EFW, and the specific weather conditions associated with each Technosylva percentile are not available | Consequence is not represented probabilistically, more deterministically with a binary flag for outages occurring under EFW
Wildfire Consequence | A scaling factor is applied to Technosylva consequence values to correct for underprediction | Benchmarking against USFS and CAL FIRE datasets and CAL FIRE historical incident data showed Technosylva simulated fire sizes roughly an order of magnitude below observed regional wildfires, attributable to Technosylva's 8-hour fire-spread simulation duration | The scaling factor is derived from historical California wildfires, rather than Liberty-specific events.
Wildfire Consequence | Technosylva consequence estimates are applied at the circuit level | Matches the current unit of analysis of the risk model | A single consequence value per circuit does not reflect within circuit variation in risk
Wildfire Consequence | Technosylva consequence modeling uses a projected 2030 fuelscape | Reflects anticipated future fuel conditions over the planning horizon | Differs in time basis from the backward-looking 2022–2025 weather record used on for likelihood calculations
Wildfire Consequence | Consequence monetization parameters (structure value, per-acre cost, VSL) are adopted from peer California utilities rather than independently derived | Peer values are documented and established | Values are not anchored directly to Liberty's service territory, for example suppression or restoration costs
Wildfire Consequence | Smoke and ash damage to structures, public health impacts of smoke exposure, ecological impacts, as well as other forms of insured losses, are not monetized in the consequence framework | No established valuation methodology has been adopted for these categories currently | Total wildfire consequence is likely understated
Wildfire Vulnerability | Physical structure vulnerability is assessed via Technosylva's Urban Conflagration and Dynamic Building Loss Factor methodology | dBLF is a machine-learning model trained on 16 years of post-fire structure damage inspection data, primarily from CAL FIRE | Validation is concentrated in Southern California WUI, which differs from Liberty's service territory, and urban conflagration is inherently challenging to model
Wildfire Vulnerability | Social vulnerability is not quantified within the risk model | Liberty does addresses AFN populations in its PSPS operational protocols | Community capacity to anticipate, cope with, and recover from a wildfire event is not reflected in modeled risk
PSPS Likelihood | PSPS likelihood is assigned as 1.0 event per year for the ten highest-risk feeders and 0.5 events per year for all other feeders | Reflects Liberty's operational experience that PSPS exposure is concentrated on a limited number of circuits | Frequencies are not empirically fitted to circuit-specific PSPS fire weather
PSPS Consequence | PSPS event duration is assumed to be 17 hours | Liberty's historical average is approximately 12 hours; 17 hours reflects anticipated resource constraints when patrolling and re-energizing more than two simultaneously de-energized circuits. Benchmarked against other California utilities' assumptions of 8 to 24 hours | The figure is an operational judgment rather than a fitted value, and the model does not vary the PSPS length by circuit
PSPS Consequence | Reliability consequence is monetized using ICE Calculator v2.2 $/CMI values applied by circuit-level residential/non-residential customer mix |  | ICE estimates are model-derived rather than observed for Liberty's specific customers, and do not vary by event circumstance or time of year
PSPS Vulnerability | PSPS vulnerability is not quantified within the risk model | AFN populations are addressed through separate PSPS operational protocols | Varying levels of vulnerability of medical baseline, critical facility, and AFN customers are not reflected in estimated PSPS risk

## Table 5-2
Table 5-2: Liberty Summary of Design Basis Scenarios
Scenario ID | Design Scenario | Purpose
WLC1 | Wind Load | Baseline wind load used in design, construction, and maintenance.
WLC2 | Wind Load | 95th percentile wind gusts based on maximum daily values over a 30-year history.
WLC3 | Wind Load | Wind gusts with a probability of exceedance of five percent over the three-year WMP cycle (i.e. 60-year return interval)
WLC4 | Wind Load | Wind gusts with a probability of exceedance of one percent over the three-year WMP cycle (i.e. 300-year return interval).
WLC5 | Wind Load | WFA models wind speeds to identify at what point a specific transmission or distribution circuit may fail in windy conditions. The results are based on three-hour aggregated probabilities based on the maximum wind gust during that three-hour period.
WC1 | Weather Condition | Anticipated weather conditions over the next three years. This is based on historical weather days that best represents the days when weather and fuel conditions can lead to increased risk of ignition.
WC2 | Weather Condition | Long-term conditions. Technosylva has calculated the historical weather days that best represent the days when weather and fuel conditions can lead to increased risk of ignition based on their Weather Research and Forecast (WRF) Model. WRF is calculated annually to capture new days that should be incorporated into the historical weather days to account for changing conditions in locations.
VC1 | Vegetation Condition | Modeling of current vegetation conditions to identify where current vegetation fuels risk.
VC2 | Vegetation Condition | Modeling of vegetation conditions to identify potential mid-range vegetation fuels risk.
VC3 | Vegetation Condition | Modeling of projected 2030 vegetation conditions to identify potential long-range vegetation fuels risk.

## Table 5-3
Table 5‑3: Liberty Summary of Extreme-Event Scenarios
Scenario ID | Extreme-Event Scenario | Purpose
EFW | Extreme Fire Weather VPD >= 2 kPa and Wind Gust >= 50 mph | To account for conditions when a utility-caused ignition is likely to spread rapidly and dangerously

## Table 5-4
Table 5-4: Summary of Fire Risk Model and PSPS Risk Model
ID | Risk Component | Design Scenario(s) | Key Inputs | Source of Inputs (Data and/or Models) | Key Outputs | Units
RSystem | Overall Utility Risk |  | Wildfire Risk | Previous modeling steps | Annual system and circuit-level overall utility risk | Dollars ($)
Outage Program Risk
RWF | Wildfire Risk |  | Probability of Ignition | Previous modeling steps | Annual system and circuit-level wildfire risk | Dollars ($)
Wildfire Consequence
ROP | Outage Program Risk |  | PSPS Risk | Previous modeling steps | Annual system and circuit-level outage program risk | Dollars ($)
PEDS Risk
RPSPS | PSPS Risk |  | PSPS Likelihood | Previous modeling steps | Annual system and circuit-level PSPS risk | Dollars ($)
PSPS Consequence
RPEDS | PEDS Risk |  | PEDS Likelihood | Not currently quantified | Not currently quantified | Not currently quantified
PEDS Consequence
P(i) | Probability of Ignition |  | Probability of Outage | Previous modeling steps | Annual probability of ignition at the circuit-level | Probability, annual expected ignition frequency
Probability of Extreme Fire Weather
P(EFW) | Probability of Extreme Fire Weather |  | Weather data | GRIDMET gridded weather data product | Circuit-level frequency of meeting EFW threshold | Days per year meeting EFW threshold
|  |  | Historical fire perimeters | CAL FIRE annual Redbooks
P(o) | Probability of Outage |  | Weather data | GRIDMET and Western Weather station data | Daily and annual outage probability at the circuit-level | Probability, daily and annual
|  |  | Asset and load data | Internal Liberty Data
|  |  | Vegetation conditions | LiDAR
|  |  | Inspection findings | Internal Liberty Data
CWF | Wildfire Consequence |  | Simulated structures destroyed | Technosylva WFA | Monetized wildfire consequence at the circuit-level | Dollars ($)
Simulated acres burned
CPSPS | PSPS Consequence |  | Historical PSPS events | Historical PSPS events | Monetized PSPS consequence at the circuit-level | Dollars ($)
|  |  | Residential and non-residential customer counts, load | Customer data
P(PSPS) | PSPS Likelihood |  | Historical PSPS events | Historical PSPS events | Two groupings of circuits based on PSPS likelihood (higher and lower likelihood) | PSPS events per circuit-year

## Table 5-5
Table 5-5: Liberty Top-Risk Circuits
Rank | Circuit ID | Wildfire Risk ($) | Outage Program Risk ($) | Overall Utility Risk ($) | % of Risk | Primary Risk Sub-Driver | Secondary Risk Sub-Driver | Version of Risk Model
1 | TPZ1202 | 139889565 | 3303175 | 143192740 | 17.5 | Equipment | Wind | 1
2 | MEY3400 | 78143003 | 9393758 | 87536761 | 10.7 | Equipment | Vegetation | 1
3 | MEY3200 | 65185834 | 18119288 | 83305122 | 10.2 | Equipment | Vegetation | 1
4 | MEY3300 | 58075016 | 5645445 | 63720461 | 7.8 | Equipment | Vegetation | 1
5 | STL3501 | 45416407 | 8162810 | 53579217 | 6.6 | Equipment | Vegetation | 1
6 | STL3101 | 46128236 | 6028378 | 52156614 | 6.4 | Equipment | Vegetation | 1
7 | MEY3500 | 43485679 | 7332014 | 50817694 | 6.2 | Equipment | Vegetation | 1
8 | MULLER1296 | 45370802 | 2580408 | 47951211 | 5.9 | Equipment | Wind | 1
9 | MEY3100 | 26556037 | 5262375 | 31818412 | 3.9 | Equipment | Vegetation | 1
10 | POR3200 | 15436074 | 3974838 | 19410911 | 2.4 | Equipment | Animal | 1
11 | TRK7202 | 14395453 | 459853 | 14855306 | 1.8 | Equipment | Vegetation | 1
12 | CAL2501 | 14452063 | 122594 | 14574657 | 1.8 | Equipment | Vegetation | 1
13 | GLS7400 | 13486792 | 801507 | 14288299 | 1.8 | Equipment | Vegetation | 1
14 | CEM41 | 13713025 | 473489 | 14186513 | 1.7 | Equipment | Wind | 1
15 | TAH5201 | 7986404 | 5728889 | 13715293 | 1.7 | Equipment | Vegetation | 1
16 | POR3100 | 11971751 | 1375891 | 13347642 | 1.6 | Equipment | Vegetation | 1
17 | STL2300 | 8953187 | 1902300 | 10855487 | 1.3 | Equipment | Vegetation | 1
18 | TAH7300 | 4433396 | 4616767 | 9050163 | 1.1 | Equipment | Vegetation | 1
19 | 640 | 8453105 | 0 | 8453105 | 1 | Equipment | Animal | 1
20 | KBH5200 | 4797599 | 3576355 | 8373954 | 1 | Equipment | Vegetation | 1

## LU Table 5-6
LU Table 5-6: Overall Utility Risk by Circuit Normalized per mile
Rank | Circuit ID | Overhead Miles | Overall Utility Risk | % of Risk | Risk per Overhead Mile
1 | MEY3200 | 21.6 | 83305122 | 10.2 | 3852411
2 | STL3501 | 13.9 | 53579217 | 6.6 | 3849669
3 | STL2300 | 3 | 10855487 | 1.3 | 3657636
4 | STL3101 | 15.6 | 52156614 | 6.4 | 3349176
5 | CAL2501 | 4.7 | 14574657 | 1.8 | 3119242
6 | TPZ1202 | 54.9 | 143192740 | 17.5 | 2607577
7 | CEM41 | 5.8 | 14186513 | 1.7 | 2436865
8 | MEY3500 | 27.4 | 50817694 | 6.2 | 1855403
9 | MEY3100 | 17.7 | 31818412 | 3.9 | 1795070
10 | MEY3400 | 54.4 | 87536761 | 10.7 | 1607843
11 | TRK7202 | 12.2 | 14855306 | 1.8 | 1222122
12 | MEY3300 | 52.7 | 63720461 | 7.8 | 1208991
13 | MULLER1296 | 43.7 | 47951211 | 5.9 | 1098233
14 | 640 | 8 | 8453105 | 1 | 1055355
15 | POR3100 | 13.4 | 13347642 | 1.6 | 999284
16 | POR3200 | 21 | 19410911 | 2.4 | 925550
17 | TAH5201 | 21.4 | 13715293 | 1.7 | 640701
18 | GLS7400 | 32.9 | 14288299 | 1.8 | 433832
19 | KBH5200 | 23.3 | 8373954 | 1 | 358902
20 | TAH7300 | 57.6 | 9050163 | 1.1 | 157198

## LU Table 5-7
LU Table 5-7: Summary of Risk Focus Group Meetings
Date | Topics covered | Results, including risk model methodology changes
17-Mar | Kickoff. Opening comments on the Draft Decision, Charter development, FEP engagement, Firescape proposal | Charter drafting assigned, target of May 29. Site visit set with FEP. No motions, pre-Charter
2-Apr | Final decision denying the 2026-2028 WMP, workplan, monthly Energy Safety cadence | Workplan adopted as the tracking basis. FEP asked to bucket improvements into immediate, pre-filing, and long term. No motions, pre-Charter
16-Apr | Data requests, benchmarking metrics, EFD pilot, tail adjustments | Tail risk adjustment identified as a key methodology decision. No motions, pre-Charter
23-Apr | Data requests, physics and machine learning models, Technosylva clarifications, meeting cadence | FEP confirmed both a physics model and a Liberty-specific machine learning model with documentation for each. Cadence moved to weekly. No motions, pre-Charter
30-Apr | Data requests, fragility curves, tree mortality, LiDAR, EFD, risk spend efficiency | Data gaps assigned to owners. No motions, pre-Charter
7-May | Charter, high impedance fault detection pilot, FEP model development | Charter adopted. FEP to bring model variables forward weekly for approval
14-May | Action items, data requests, model progress | Egress, climate change, and tree mortality discussed
21-May | Consequence, reliability, and financial variables, risk informed decision making framework | California adjusted value of statistical life adopted for safety monetization. ICE 2.2, $1M per structure, and SCE acres burned recommended, held for vote after quorum was lost
28-May | Model granularity and data quality, May 21 variables, PSPS likelihood | Circuit level granularity retained. ICE 2.2, $1M per structure, and $2,336 per acre burned adopted. Simplified PSPS likelihood adopted, historical events plus a minimum threshold for circuits with no PSPS history, with a climate change adjustment
4-Jun | PSPS consequence, PEDS outage risk, Gridscope business case | Adopted SCE ratios for serious injuries per customer de-energized, a 17-hour PSPS duration, and $550 per event per customer. PEDS risk deferred to the improvement plan, with a question to Energy Safety on excluding it for 2027. Gridscope pilot approved
9-Jun | Risk scaling, Mountain View Fire, expected against tail risk | Scaling of Technosylva outputs to observed fire costs identified as a needed methodology change, vote scheduled
11-Jun | Consequence scaling vote, Technosylva QA/QC | Consequence scaling factor of 1.27 approved (later refined to 1.26 on 6/18). Technosylva, CalFire, and USFS outputs compared, field validation recommended where the three diverge
16-Jun | Mitigation effectiveness analysis and assumptions | Benchmarking adopted as the effectiveness approach. Covered conductor confirmed as 3-ply, with the same cause code effectiveness for existing and proposed assets. ICE 2.2 produced a combined $2.63 per CMI for review
18-Jun | CMI approval, financial unit costs, initial mitigation effectiveness | $2.63 per CMI approved. Financial unit costs approved. Scaling factor revised from 1.27 to 1.26. PG&E identified as the closest benchmarking match
23-Jun | Probability of failure, machine learning and statistical | Model structure reviewed, probability of outage and probability of ignition, extreme fire weather derived from fire history, weather, and Liberty PSPS events. Asset Health Index reviewed. Deeper technical review scheduled
26-Jun | Mitigation effectiveness framework | PG&E confirmed as the benchmark, with cause code alignment to Energy Safety and PG&E drivers and sub-drivers. Overhead and covered conductor to yield a circuit specific score, PSPS and EPSS to be programmatic
30-Jun | Initial risk results, benefit-cost ratio framework | BCR framework reviewed
2-Jul | WMP outline, hardened circuit and SAIDI analysis | Section 5, 6, 8, Appendix B, and Appendix D drafting assigned, drafts due July 31. Distribution set as the impact focus, with a separate score for transmission
7-Jul | Traditional hardening against covered conductor, remaining model variables, BCR results | Real discount rate of 4.51% approved. Inflation set at 2.93% and WACC at 7.44%. Maturity adjustment strategy approved, using IWRMC maturity model scores, giving PSPS 75% and SRP 56%
9-Jul | Traditional hardening analysis, risk and BCR results, Section outline | Underground effectiveness strategy approved, PG&E values excluding secondary with a maturity adjustment. Asset life rounding approved, 60 years for overhead and underground. Dashboard access issued to Liberty for scenario testing
14-Jul | Overhead effectiveness value, SRP circuit confirmation | Overhead hardening effectiveness of 23% approved, derived empirically from Liberty pole replacement and outage data using a treatment and control comparison, applied to asset drivers only
16-Jul | Risk and BCR review, risk model improvement plan | Residential $0.08 and non-residential $23.47 per CMI approved, replacing the blended $2.63 value. One PSPS event per feeder per year confirmed as an assumption, with circuit specific likelihood routed to the improvement plan. Present value of benefits confirmed as excluded, to be disclosed in the WMP. Improvement plan items sorted into short- and long- term commitments
21-Jul | Risk modeling overview, fire partner meeting preparation | Overhead hardening unit costs reviewed
23-Jul | Energy Safety presentation status, fire partner collaboration | Presentation structured around the five critical issues and where each is addressed in the 2027 WMP
30-Jul | Overhead infrared finding prioritization, 2027 initiatives, fire partner meeting review | C2 Group thermal priority levels approved. Fire partner feedback on wind thresholds and tree mortality taken up, with interest in aligning thresholds to PEDS and PSPS device settings
6-Aug | Capital plan, risk ranking and circuit prioritization | Pole replacement target of 300 per year approved, 5 in favor and 1 opposed. Covered conductor target of 8 miles and four projects approved unanimously, MEY3400, MEY3300, CAL2501, and TPZ1202. Prioritization screens approved unanimously, circuits above 5% of total overall utility risk and above $2M per mile of overhead risk

## LU Table 5-8
LU Table 5-8: Tracking of Liberty's Previous RAI Plan Commitments
Prior ID | Prior Commitment | Status
RA-1 | Establish a process to continually test data quality and data input to improve the results of the tool | FEP performed two structured data quality reviews in 2026: independent benchmarking of Technosylva's consequence datasets against USFS and CAL FIRE data, and a QA/QC review of Liberty's asset spatial data. Additional data quality improvements are discussed in the updated RAI plan.
RA-2 | Establish a process to continually test the risk modeling methodology and benchmark with peer utilities. Include wildfire and PSPS risk assessment documentation, including both quantitative and qualitative approaches | Liberty overhauled the risk modeling methodology: the likelihood side of the wildfire risk model was rebuilt with FEP. Peer benchmarking against PG&E, SCE, and SDG&E methodologies is documented in this section and further discussed related to mitigation effectiveness. Liberty additionally performed a full independent replication of the vendor model.
RA-3 | Establish a feedback loop with subject matter experts to continually test and improve the results of the risk tool. This should include presentation of risk, including dashboards and assessments | The Risk Focus Group, chartered May 7, 2026, is the standing cross-functional forum for reviewing model results and assumptions. FEP delivered a risk model dashboard as part of the Liberty risk model.
RA-4 | Establish a process to track and reconstruct risk events for the purpose of integrating lessons learned and improvement | With Liberty’s new risk model, this item is no longer relevant for the WMP cycle. For validation purposes, Liberty’s previous risk model identified reconstruction of risk events as a roadmap item. Liberty’s new probability of outage model uses machine-learning techniques, including cross-validation, to predict risk events. Liberty will continue to cross-validate and update its probability of outage model with new outage data.
RA-5 | Establish a cadence to present and deliver the results with business planners and operators to be incorporated into the decision-making and design process. This should include justification for design basis scenarios | The Risk Focus Group provides the standing cadence, and its recorded motions demonstrate risk model outputs driving mitigation and investment decisions
RA-6 | Assign a dedicated resource the responsibility of improving and delivering risk-based results for better decision making. Place an emphasis on data quality, methodology, and subject matter expert and industry tested results | Lead Risk Analyst was onboarded June 2026 and has performed reviews and replication of the risk model, as well as writing and documenting key risk modeling methodological decisions.
RA-7 | Evaluate and improve the calculation and scaling of outage risk including, but not limited to, the items included in RN-LU-26-01 | Overall utility risk is now calculated as the sum of wildfire and outage program risk, denominated in dollars. The third-party model was replaced. Scaling and weighting were re-calculated based on peer benchmarks from PG&E, SCE, and SDG&E.

## Table 5-6
Table 5-6: Liberty Utility Risk Assessment Improvement Plan
ID | Key Area | Title of proposed improvement | Type | Anticipated benefit | Timeframe and key milestones
RA-1 | Risk assessment methodology | Refine risk model to circuit-segment unit of analysis | Technical | Enables segment-level likelihood, consequence, BCR, and scoped hardening projects. Yields a more accurate characterization of risk, given variation in risk along a circuit that can span tens of miles. | Scoping Q3 2026 - Q2 2027; develop Q3 2027 - Q4 2027; apply model Q1 2028
RA-2 | Risk assessment methodology | Develop PEDS risk model quantifying likelihood and consequence | Technical | Addresses limitation of current risk model that excludes PEDS outage risk and understates outage program risk | Formalize SRP data quality assessment Q4 2026; formalize thresholds to inform SRP likelihood Q4 2026; apply model Q1 2027
RA-3 | Risk assessment methodology | Probabilistic assessment of extreme fire weather and ignition likelihood | Technical | Replaces the binary EFW threshold proxy with a continuous probabilistic treatment | Develop the methodology Q2 2027; apply the methodology Q3 2027
RA-4 | Risk assessment methodology | Develop egress model and incorporate into wildfire consequence | Technical | Captures an important driver of wildfire consequence that is underrepresented in the current model | Scoping Q3 2026; apply Q4 2026
RA-5 | Risk assessment methodology | Develop tree-mortality predictive model for wildfire consequence | Technical | Incorporates heavy fuel loading from tree mortality | Scoping Q3 2026; apply Q4 2026
RA-6 | Risk assessment methodology | Refine calibration of Technosylva 8-hour fire spread outputs to actual losses | Technical | Reduces reliance on a scaling factor derived from historical fires, and places less weight on calibration in the risk model | Scoping Q2 2028 - Q3 2028; apply and re-estimate risk Q4 2028
RA-7 | Risk assessment methodology | Evaluate additional wildfire consequence categories (e.g., additional insured losses, ecosystem services) | Technical | Extends the risk model to capture additional dimensions of wildfire damages, given a focus on structures burned, acres burned, and safety may underrepresent the potential damages from wildfire | Scoping Q1 2029 - Q3 2029; apply Q4 2029
RA-8 | Risk assessment methodology | Incorporate climate change analysis into likelihood and consequence model components, including PSPS likelihood | Technical | More accurately characterizes risk that may arise from future climate change trajectories, including increased frequency of PSPS | Scoping Q3 2026 - Q4 2026, apply and re-estimate risk Q1 2027
RA-9 | Risk assessment methodology | Refine treatment of critical facilities, medical baseline, and AFN customers in PSPS and PEDS consequence | Technical | Addresses PSPS vulnerability, currently underrepresented in the risk model | Merging data availability and customer counts into risk model Q4 2026; apply and re-estimate outage program risk Q1 2027
RA-10 | Risk assessment methodology | For transmission-level, incorporate outage causes and risk sub-drivers into outage likelihood model | Technical | Allows for more targeted transmission-system mitigations based on outage cause | Investigate viability and sample size of transmission outage logs Q2 2028; implement Q3 2028
RA-11 | Risk assessment methodology | Incorporate blended mitigation effectiveness values (e.g., covered conductor + SRP + grid monitoring) | Technical | Reflects that mitigations are deployed in combination. Supports evaluation of multiple layers of mitigations | Benchmarking peer utilities for combined mitigation effectiveness; incorporating into risk model Q1 2027; expanded mitigations and capability Q1 2028
RA-12 | Risk assessment methodology | Expand variable mitigation effectiveness parameters by risk sub-driver beyond overhead hardening with covered conductor | Technical | More realistically represents the effect of mitigations and how they vary by fault cause | Benchmark Q4 2026, apply for undergrounding and overhead hardening without covered conductor Q1 2027; expanded mitigations Q1 2028
RA-13 | Risk assessment methodology | Develop empirical assessments of Liberty's mitigation activities on outage probabilities | Technical | Replaces benchmarked effectiveness values with Liberty-specific empirical evidence | Overhead hardening without covered conductor Q1 2027; refine estimate of overhead hardening without covered conductor Q1 2028; explore additional mitigations with sufficient data (e.g., covered conductor, vegetation management) Q1 2029
RA-14 | Risk assessment methodology | Develop circuit or circuit-segment level BCR estimation for vegetation management projects | Technical | Brings vegetation management into the same benefit-cost framework as hardening programs. Allows more direct linkage of risk model to vegetation management program prioritization. | Scoping vegetation management data and activity types Q2 2027; test and validate approaches to modeling economics of vegetation management Q3-Q4 2027; apply model Q1 2028; explore additional BCR estimation for activity types, such as fuel treatments
RA-15 | Risk assessment methodology | Include additional mitigations in BCR estimation | Technical | Widens the set of mitigations that can be compared on a consistent benefit-cost basis | See previous milestones for vegetation management; fuse replacement Q1 2027; grid monitoring technologies Q1 2028
RA-16 | Risk assessment methodology | Incorporate circuit or circuit-segment specific unit costs | Technical | Replaces system-average unit costs, improving BCR accuracy for variable terrain, permitting, and other cost challenges | Apply at the circuit-level Q1 2027; scope for circuit-segment level Q3 2029 - Q4 2029; apply to circuit-segment model Q1 2030
RA-17 | Risk assessment methodology | Refine BCR calculation including O&M savings/costs and NPV method | Technical | More accurately characterizes cost modeling of grid hardening mitigations | Explore and benchmark O&M costs Q4 2026, apply at the circuit-level Q1 2027
RA-18 | Risk assessment methodology | Establish model and input data version control; establish reanalysis capability | Programmatic | Allows clear documentation and version control as model inputs and calculations are edited and refined over time | Establish repository Q3 2026
RA-19 | Risk assessment methodology | Establish external independent review of risk model | Programmatic | Provides external critique of risk model methodology. Allows improvement over time as risk model advances | Select reviewer Q2 2027; engage and complete review Q3-Q4 2027
RA-20 | Risk event tracking | Standardize assignment of outage cause and sub-cause | Programmatic | Improves the cause taxonomy used to report and classify outages and risk events. Leads to a more cohesive set of sub-drivers that aligns clearly with mitigation effectiveness modeling | Review with operations and field teams Q4 2026 - Q1 2027
RA-21 | Risk event tracking | Set targets for reduction in unknown outage causes | Programmatic | Reduces the share of outage records excluded from model training | Baseline and targets set Q4 2026; re-evaluate targets Q4 2027
RA-22 | Risk event tracking | Establish a review process for outage cause determinations | Programmatic | Allows for data quality improvement in the risk model | Document the process Q4 2026
RA-23 | Risk event tracking | Standardize the process for recording and investigating ignitions including root cause | Programmatic | Allows for data quality improvement in the risk model. Creates a foundational dataset for measuring ignition likelihood and mitigation effectiveness, empirically | Document the process Q4 2026
RA-24 | Risk event tracking | Expand capture of ignition photographs and field data beyond reportable ignitions only | Programmatic | Allows for data quality improvement in the risk model. Creates a foundational dataset for measuring ignition likelihood and mitigation effectiveness, empirically | Document the process Q4 2026

## Table 6-1
Table 6‑1: Circuit Prioritization List Based on Overall Utility Risk
Rank | Circuit ID | Overhead Miles | Wildfire Risk ($) | Overall Utility Risk ($) | % of Risk | Risk per Overhead Mile | Qualifying Screen | Associated Risk Drivers
1 | TPZ1202 | 54.9 | 139889565 | 143192740 | 17.5 | 2607577 | Both | Equipment, Wind
2 | MEY3400 | 54.4 | 78143003 | 87536761 | 10.7 | 1607843 | Absolute risk | Equipment, Vegetation
3 | MEY3200 | 21.6 | 65185834 | 83305122 | 10.2 | 3852411 | Both | Equipment, Vegetation
4 | MEY3300 | 52.7 | 58075016 | 63720461 | 7.8 | 1208991 | Absolute risk | Equipment, Vegetation
5 | STL3501 | 13.9 | 45416407 | 53579217 | 6.6 | 3849669 | Both | Equipment, Vegetation
6 | STL3101 | 15.6 | 46128236 | 52156614 | 6.4 | 3349176 | Both | Equipment, Vegetation
7 | MEY3500 | 27.4 | 43485679 | 50817694 | 6.2 | 1855403 | Absolute risk | Equipment, Vegetation
8 | MULLER1296 | 43.7 | 45370802 | 47951211 | 5.9 | 1098233 | Absolute risk | Equipment, Wind
9 | CAL2501 | 4.7 | 14452063 | 14574657 | 1.8 | 3119242 | Risk per mile | Equipment, Vegetation
10 | CEM41 | 5.8 | 13713025 | 14186513 | 1.7 | 2436865 | Risk per mile | Equipment, Wind
11 | STL2300 | 3 | 8953187 | 10855487 | 1.3 | 3657636 | Risk per mile | Equipment, Vegetation

## LU Table 6-1
LU Table 6-1: Mitigation Effectiveness Parameters
Mitigation | Category | Effectiveness | Applies to | Source
Overhead hardening with covered conductor | Hardening | Ranges from 0.60 to 0.77 by sub-driver | Wildfire risk | PG&E overhead hardening values by risk driver, Joint IOU Grid Hardening Working Group Report
Undergrounding | Hardening | 0.95 for all sub-drivers | Wildfire risk | PG&E underground-primary with overhead-secondary values, Joint IOU Grid Hardening Working Group Report
Overhead hardening without covered conductor | Hardening | 0.23 for asset-related driver only | Wildfire risk | Empirical analysis of outage counts on Liberty distribution circuits
PSPS | Operational | 0.75 for all sub-drivers | Wildfire risk | PG&E 2026-2028 WMP, Table 6-3, adjusted for program maturity
Equipment settings to reduce wildfire risk (SRP) | Operational | 0.56 for all sub-drivers | Wildfire risk | PG&E 2026-2028 WMP, Table 6-3, adjusted for program maturity

## LU Table 6-2
LU Table 6-2: Initiative Activities for Risk Drivers of Prioritized Circuits
|  | Risk Reduction |  | Risk Reduction
|  | ($ millions-yr) |  | (% of Baseline)
Initiative | Estimated Cost | Wildfire | Outage Program | Unmitigated Baseline | No-Build Baseline | Schedule | Risk Driver
($ millions-yr)
Overhead hardening with covered conductor | 9 | 43 | - | 5% | 18% | See Section 8 | Equipment, Vegetation, Wind
Undergrounding | 25 | 69 | - | 9% | 30% | Not proposed for this WMP cycle | Equipment, Vegetation, Wind

## Table 6-2
Table 6‑2: Liberty Stakeholder Roles and Responsibilities in the Decision-Making Process
Stakeholder | Stakeholder Point of Contact | Electrical Corporation Point of Contact | Stakeholder Role | Engagement Methods | Activity | Level of Engagement Activity
Liberty Executive Leadership | Chief Executive Officer; Chief Operating Officer | Liberty President | Informed; Consulted | Quarterly Meetings; Emails; Phone Calls | All WMP activities | Local, state, federal, tribal
Board Level Safety Committee | Board of Directors | Liberty President | Informed; Consulted | Quarterly Meetings | All WMP activities, plus safety culture | Local, state, federal, tribal
Liberty Risk Focus Group (“RFG”) | Liberty President | Liberty President | Informed, Consulted, Decision-maker | Weekly Meetings | All WMP activities, WMP risk modeling and risk-based decision-making | Local, state
County | County Supervisor | Senior Manager, Customer Solutions; Emergency Manager | Informed | Meetings, exercises, workshops | System hardening, vegetation management, emergency preparedness | Local
Tahoe Regional Planning Agency | Special Projects Manager, Associate Environmental Specialist, Forester | Manager, Vegetation Management; Environmental Specialist | Decision-maker, consulted | Planning and prioritizing all WF mitigations | System hardening, vegetation management | Local
Sheriff's Department | Sheriff, Office of Emergency Services | Manager, Emergency Management | Informed, decision-maker | Meetings, exercises, workshops | Emergency preparedness | Local
Cal Fire | Battalion Chief, Assistant Chief | Fire Protection Specialist; System Forester; Manager, Emergency Management | Informed, consulted, decision-maker | Meetings, emails, phone calls, exercises | Vegetation management, emergency preparedness, community outreach | Local, state
California Tahoe Conservancy | Public Land Management Specialist, Associate Environmental Planner | Manager, Vegetation Management; Environmental Specialist | Decision-maker; consulted | Meetings, emails, phone calls | System hardening; vegetation management | Local, state
California State Parks | Senior Environmental Scientist, California State Parks - Sierra District | Manager, Vegetation Management; Environmental Specialist | Decision-maker; consulted | Meetings, emails, phone calls | System hardening, vegetation management | Local, state
City | City Manager | Senior Manager, Customer Solutions; Emergency Manager | Informed, consulted, decision-maker | Meetings, emails, phone calls | System hardening, vegetation management, emergency preparedness, community outreach | Local
US Forest Service | Recreation Management Specialist, Lands and Special Uses | Manager, Vegetation Management; Environmental Specialist | Decision-maker, consulted | Meetings, emails, phone calls, operating plans | System hardening, vegetation management | Local, federal
Cal Trans | District Permit Engineer | Manager, Vegetation Management; Manager, Lands | Decision-maker, consulted | Meetings, emails | System hardening, vegetation management | Local, state
Fire Department | Fire Chief | Fire Protection Specialist; Manager, Emergency Management; System Forester | Decision-maker, informed, consulted | Meetings, emails, exercises | Vegetation management, emergency preparedness, community outreach | Local
Public; customers | Varies; Manager, Communications | Varies | Informed | Workshops, outreach events, bill inserts, social media | System hardening, vegetation management, emergency preparedness | Local
Washoe Tribe | Emergency Manager, California Tribal Historic Preservation Officer | Key Account Manager, Emergency Manager, Environmental Specialist | Decision-maker, consulted, informed | Meetings, emails, phone calls | Emergency preparedness, community outreach, cultural consultation and monitoring | Tribal
Key Accounts; Critical Facilities | Varies | Key Account Manager; Sr. Manager Customer Solutions | Informed, consulted | Meetings, emails, phone call | System hardening, vegetation management, emergency preparedness, community outreach | Local
Bureau of Land Management | Sierra Front Office - Assistant Field Manager | Environmental Specialist | Decision-maker, consulted | Meetings, emails, phone calls | System hardening, vegetation management | Federal
NV Energy | Emergency Manager, Principal Meteorologist | Manager, Emergency Management; Sr. Manager, Wildfire Prevention | Decision-maker, consulted, informed |  | Emergency preparedness | Local
Community Based Organizations | Varies | Key Account Manager; Sr. Manager Customer Solutions | Informed, consulted | Workshops, outreach events, meetings, emails, phone calls | Emergency preparedness, community outreach | Local

## Table 6-3
Table 6‑3: Risk Impact Activities
Activity | Activity ID# | Activity Effectiveness – Overall Risk | Activity Effectiveness – Wildfire Risk | Activity Effectiveness – Outage Program Risk | Cost-Benefit Score – Overall Risk | Cost-Benefit Score – Wildfire Risk | Cost-Benefit Score – Outage Program Risk | % HFTD/ HFRA Covered | Expected % Risk Reduction | Model used to Calculate Risk Impact
Covered conductor installation | WMP-GDOM-GH-01 | 54% (^) | 63% | No impact | 10.8 | 10.8 | - | 2% | 2% | 1.0
Undergrounding of electric lines and/or equipment | WMP-GDOM-GH-02 | No projects proposed | No projects proposed | No projects proposed | No projects proposed | No projects proposed | - | 0% | 0% | 1.0
Distribution pole replacements and reinforcements | WMP-GDOM-GH-03 | 12% (^) | 23% | No impact | - | - | - | 2% | <1% | 1.0
Equipment settings to reduce wildfire risk | WMP-GDOM-GO-01 | - | 56% | (+) | - | - | - | 100% | (*) | 1.0
PSPS | WMP-GDOM-GO-01 | 65% | 75% | (+) | - | - | - | 100% | (*) | 1.0
Grid monitoring systems | WMP-SA-02 | - | - | - | - | - | - | 100% | - | -
Non-exempt fuse replacement | WMP-GDOM-GH-12b | - | - | - | - | - | - | 10% | - | -
Open wire/grey wire | WMP-GDOM-GH-12e | - | - | - | - | - | - | 33% | - | -
Vegetation Management Inspection Program - Detailed | WMP-VM-INSP-01 | - | - | - | - | - | - | 33% | - | -
Wood and Slash Management | WMP-VM-VFM-02 | - | - | - | - | - | - | 100% | - | -
Quality Assurance and Quality Control | WMP-VM-QAQC-01 | - | - | - | - | - | - | 33% (#) | - | -
Clearance | WMP-VM-VFM-05 | - | - | - | - | - | - | 100% | - | -
Fall-In Mitigation | WMP-VM-VFM-06 | - | - | - | - | - | - | 33% (#) | - | -
Detailed inspections of distribution electric lines and equipment | WMP-GDOM-AI-01 | - | - | - | - | - | - | 19% | - | -
Tree attachment removals | WMP-GDOM-GH-12a | - | - | - | - | - | - | 3% | - | -
Vegetation Inspection - LiDAR | WMP-VM-INSP-03 | - | - | - | - | - | - | 100% | - | -
Pole Clearing – PRC 4292 Required | WMP-VM-VFM-01-R | - | - | - | - | - | - | 100% | - | -
Pole Clearing – Discretionary | WMP-VM-VFM-01-D | - | - | - | - | - | - | 2% | - | -
Patrol inspections of distribution electric lines and equipment | WMP-GDOM-AI-03 | - | - | - | - | - | - | 81% | - | -
Intrusive pole inspections | WMP-GDOM-AI-02 | - | - | - | - | - | - | 11% | - | -
Other discretionary asset inspections: Drone inspections | WMP-GDOM-AI-04 | - | - | - | - | - | - | 7% | - | -
As discussed, Liberty’s current risk model calculates BCRs for two mitigations, overhead hardening with covered conductor, and undergrounding. With Liberty’s current risk model maturity, Liberty provides BCRs for actual proposed covered conductor projects in the above table. Liberty does not provide BCRs for undergrounding projects because no proposed projects are part of Liberty’s 2027 WMP.
(-): Not quantified as part of Liberty’s current risk model.
(^): Liberty does not currently quantify any improvements to outage program risk that hardening activities likely provide. Therefore, the effectiveness for overall utility risk shown is likely to be underestimated.
(+): PSPS and equipment settings (SRP) provide an increase in outage program risk. Liberty quantifies this increase in outage program risk for PSPS, as reflected in the overall effectiveness percentage. Liberty has not yet quantified the increase in outage program risk from PEDS/SRP/equipment settings.
(*): Liberty primarily measures risk reduction against the “no-build” baseline, which already factors in the reduction in wildfire risk from PSPS and PEDS/SRP/equipment settings. The risk reduction from PSPS and PEDS/SRP/equipment settings is calculated against the unmitigated baseline, as shown in Figure 6‑3. Together, these two initiatives provide an estimated 70% reduction in overall utility risk, as shown in Figure 6‑3. However, it is worth noting that the estimate is likely lower once additional outage program risk from PEDS is quantified in the risk model.
(#): See Table 9-6 for more detail on vegetation management initiatives and coverage. For example, for quality assurance and control, 33% of line-miles are sampled. However, additional areas of the HFTD are covered by the program beyond the 33% of line-miles due to additional samples being drawn for quality assurance.

## Table 6-4
Table 6‑4: Summary of Risk Reduction for Top Circuits
Circuit | Unmitigated Overall Utility Risk ($) | No-Build Overall Utility Risk ($) | 2027 Activities | 2027 Overall Utility Risk ($)
TPZ1202 | 143192740 | 18691027 | Grid hardening, including covered conductor, pole replacement, VM, PSPS, and SRP | 17671982
MEY3400 | 87536761 | 17989488 | Grid hardening, including covered conductor, pole replacement, VM, detailed inspections, PSPS, and SRP | 17623171
MEY3200 | 83305122 | 25289730 | Grid hardening, including pole replacement, VM, PSPS, and SRP | 25223957
MEY3300 | 63720461 | 12033697 | Grid hardening, including covered conductor, pole replacement, VM, PSPS, and SRP | 11883354
STL3501 | 53579217 | 12828333 | Grid hardening, including pole replacement, VM, PSPS, and SRP | 12785867
STL3101 | 52156614 | 10841438 | Grid hardening, including pole replacement, VM, PSPS, and SRP | 10797177
MEY3500 | 50817694 | 11911379 | Grid hardening, including pole replacement, VM, PSPS, and SRP | 11869679
MULLER1296 | 47951211 | 7143409 | Grid hardening, including pole replacement, VM, PSPS, and SRP | 7101393
MEY3100 | 31818412 | 8020830 | VM, PSPS, and SRP | 8020830
POR3200 | 19410911 | 5672806 | VM, PSPS, and SRP | 5672806
TRK7202 | 14855306 | 9457011 | VM, PSPS, and SRP | 9457011
CAL2501 | 14574657 | 9155133 | Grid hardening, including covered conductor, pole replacement, VM, PSPS, and SRP | 6654544
GLS7400 | 14288299 | 4510375 | VM, PSPS, and SRP | 4510375
CEM41 | 14186513 | 4244570 | Grid hardening, including pole replacement, VM, PSPS, and SRP | 4209798
TAH5201 | 13715293 | 7675885 | VM, PSPS, and SRP | 7675885
POR3100 | 13347642 | 4668123 | VM, PSPS, and SRP | 4668123
STL2300 | 10855487 | 6860229 | Grid hardening, including pole replacement, VM, PSPS, and SRP | 6815111
TAH7300 | 9050163 | 5835951 | VM, PSPS, and SRP | 5835951
640 | 8453105 | 5283191 | VM, PSPS, and SRP | 5283191
KBH5200 | 8373954 | 4895695 | VM, PSPS, and SRP | 4895695
Table Notes: Estimated reductions in risk between the no-build baseline and the 2027 column are primarily driven by modeled overhead hardening with covered conductor projects. Marginal risk reductions are also informed by overhead hardening without covered conductor, which are based on initiative targets for pole replacement distributed across Liberty’s prioritized list of circuits. Actual pole replacement work may differ from estimates captured in the table. Risk reduction from vegetation management is not currently quantified.

## LU Table 7-1
LU Table 7‑1: Lessons Learned from Liberty PSPS Events in 2024 and 2025
Observation | Corrective Action | Status of Corrective Action
Medical Baseline (MBL) customer tags on meters needed to be updated. | Perform field audit of all MBL meters on the system to confirm proper tags are in place. | Completed
Improved communication is needed between regulatory liaisons and other members of the IMT to record event information more efficiently, such as customer impact counts and communications with Public Safety Partners (“PSPs”). | Implement improvements to the incident tracking spreadsheet. | Completed
Improved logistics are needed to support the Washoe CRC location, which is relatively remote. More affordable options for lunch items at the CRC and more timely transport and distribution of repair supplies to the Walker and Coleville areas are needed. | Put contracts in place with vendors for CRC lunches. Stage repair materials in Liberty’s CONEX boxes for use in the Walker and Coleville areas. | Completed
During 2024 PSPS events, Liberty’s Community Outreach team took responsibility for notifying PSPs, community officials, and key accounts instead of the PSP liaison, who has multiple duties. | Officially assign PSP notification responsibility to the community outreach team. | Completed
Use different template for State Executive Briefing after de-energization has occurred | Use the correct template for future State Executive Briefings | Completed
CalOES form entry for customers potentially impacted should go to 0 once those customers are actually impacted | Discuss this issue with CalOES and have clarity on guidance moving forward | Completed
Track positive feedback received from stakeholders in internal event tracker during event | Include this information in the event tracker for future events | Completed
Include estimated time of restoration on all notifications during event; include CRC services available and where to access electricity during the hours the CRC is closed on customer notifications | Adapt notification templates to include estimated time of restoration and CRC services available; Liberty is assessing the requirement to include information on where to access electricity during the hours CRCs are closed | Completed
Internal cost tracking codes were not sufficiently explained until after the PSPS event | Publish cost tracking codes with explanations in Incident Action Plan prior to or in the beginning of the event | Completed
In-event customer numbers were different from post-event reporting due to duplicate and de-activated customer accounts included in in-event reporting | Update PSPS playbook to document process for removing duplicate and de-activated customer accounts for in-event reporting | Completed
Recent staffing changes have impacted list of CRC leads | Reassess list of CRC leads to address recent staffing changes | Planning
There were no signs at the CRC locations | Put up signs outside CRC locations during future PSPS events | Completed
Liberty has a vacancy for the Emergency Manager position | Fill the Emergency Manager Position | Completed
A couple customers requested larger sized bottles of water for toilet flushing | Determine if there is a reasonable solution to better prepare customers using well water | Implementing

## Table 8-1
Table 8‑1: Liberty Grid Design, Operation and Maintenance Targets by Year, 2027 [58]
WMP Initiative Category | Quantitative or Qualitative Target | WMP Initiative Activity | WMP Initiative Tracking ID | Target Unit | 2027 Target / Status | % Planned in HFTD/HFRA for 2027 | % Risk Reduction for 2027 | Section; Page Number
Grid Design, Operations, and Maintenance | Quantitative | Covered conductor installation | WMP-GDOM-GH-01 | Circuit miles | 8 | 100% | 2% | 8.2.1; pp.157-162
Grid Design, Operations, and Maintenance | Quantitative | Undergrounding of electric lines and/or equipment | WMP-GDOM-GH-02 | Circuit miles | 0 | 0 | 0 | 8.2.2; pp. 162-164
Grid Design, Operations, and Maintenance | Quantitative | Distribution pole replacements and reinforcements[59] | WMP-GDOM-GH-03 | Poles | 300 | 100% | <1% | 8.2.3; pp. 164-165
Grid Design, Operations, and Maintenance | Quantitative | Transmission pole/tower replacements and reinforcements | WMP-GDOM-GH-04 | Poles | N/A | N/A | N/A | 8.2.4; pp. 165-166
Grid Design, Operations, and Maintenance | Quantitative | Traditional overhead hardening | WMP-GDOM-GH-05 | Circuit miles | 0 | 0% | 0 | 8.2.5; pp. 166-167
Grid Design, Operations, and Maintenance | Quantitative | Emerging grid hardening technology installations and pilot progress | WMP-GDOM-GH-06 | No target unit identified | 0 | 0 | 0 | 8.2.6; p. 167
Grid Design, Operations, and Maintenance | Quantitative | Microgrids | WMP-GDOM-GH-07 | Microgrids | 0 | 0 | 0 | 8.2.7; pp. 167-168
Grid Design, Operations, and Maintenance | Quantitative | Installation of system automation equipment | WMP-GDOM-GH-08 | Automatic reclosers | 3 | 100% | 0 | 8.2.8; pp. 168-169
Grid Design, Operations, and Maintenance | Quantitative | Line removal (in HFTD) | WMP-GDOM-GH-09 | Circuit miles | 0 | 0 | 0 | 8.2.9; p. 169
Grid Design, Operations, and Maintenance | Quantitative | Other technologies and systems not listed above: | WMP-GDOM-GH-12 [60] | N/A | N/A | N/A | N/A | 8.2.12; p. 170
Grid Design, Operations, and Maintenance | Quantitative | Tree attachment removals | WMP-GDOM-GH-12a | Tree attachments | 60 | 100% | Not calculated | 8.2.12.1; pp. 170-171
Grid Design, Operations, and Maintenance | Quantitative | Non-exempt fuse replacement | WMP-GDOM-GH-12b | Non-exempt fuses | 1000 | 100% | Not calculated | 8.2.12.2; pp. 171-172
Grid Design, Operations, and Maintenance | Quantitative | Animal guards | WMP-GDOM-GH-12c | Animal guards | 0; initiative is complete | 0 | 0 | 8.2.12.3; pp. 172-173
Grid Design, Operations, and Maintenance | Quantitative | Open wire/grey wire | WMP-GDOM-GH-12e | Circuit miles | 7 | 100% | Not calculated | 8.2.12.5; p. 173
Grid Design, Operations, and Maintenance | Quantitative | Detailed inspections of distribution electric lines and equipment[61] | WMP-GDOM-AI-01 | Circuit miles | 198.5 | 99% | Not calculated | 8.3.1; pp. 177-178
Grid Design, Operations, and Maintenance | Quantitative | Intrusive pole inspections | WMP-GDOM-AI-02 | Poles | 2238 | 97% | Not calculated | 8.3.2; pp. 178-179
Grid Design, Operations, and Maintenance | Quantitative | Patrol inspections of distribution electric lines and equipment[3] | WMP-GDOM-AI-03 | Circuit miles | 568.8 | 93% | Not calculated | 8.3.3; p. 179
Grid Design, Operations, and Maintenance | Quantitative | Other discretionary inspections of distribution electric lines and equipment: Drone inspections | WMP-GDOM-AI-04 | # Assets inspected | 1769 | 7%, but 100% HFTD-3 | Not calculated | 8.3.4; pp. 180-181
Grid Design, Operations, and Maintenance | Quantitative | Quality assurance / quality control of inspections | WMP-GDOM-AI-05 | % of detailed inspections | 12% | TBD – based on QA/QC sample | Not calculated | 8.5; pp. 192-199
Grid Design, Operations, and Maintenance | Quantitative | Substation inspections | WMP-GDOM-AI-06 | Substations | 44 | 100% | Not calculated | 8.3.5; pp. 181-182
Grid Design, Operations, and Maintenance | Qualitative | Equipment Maintenance and Repair | WMP-GDOM-MR-01 | Utilization of Asset Tracking Application | All Asset Inspections and Repairs recorded in Asset Tracking | N/A | Not calculated | 8.4; pp. 183-191
Grid Design, Operations, and Maintenance | Quantitative | Equipment settings to reduce wildfire risk | WMP-GDOM-GO-01 | # of circuits with SRP | 0 | 100% | (*) [63] | 8.7.1; pp. 203-205
Grid Design, Operations, and Maintenance – Grid Operations and Procedures | Quantitative | Equipment settings to reduce wildfire risk | WMP-GDOM-GO-01 | SRP circuit settings | Review settings of 1/3 of SRP circuits | 83% | Not calculated | 8.7.1; pp. 203-205
Grid Design, Operations, and Maintenance | Quantitative | Work Orders (Asset Management) | WMP-GDOM-AI-07 | Past due work orders | 0 | N/A | Not calculated | 8.6; pp. 200-202
Grid Design, Operations, and Maintenance | Qualitative | Workforce Planning | WMP-GDOM-GO-06 | Inspector Training Program – Standards for Development | Implement Inspector Training Program | N/A | Not calculated | 8.7.4; pp.209-212
[58] WMP initiatives with qualitative targets have N/A values for % Planned in HFTD/HFRA columns because those targets are not directed to specific locations.
[59] Liberty does not have a separate WMP initiative for transmission pole and tower replacements. Liberty captures pole replacements on its transmission system within WMP-GDOM-03.
[60] Refer to WMP initiatives WMP-GDOM-GH-12a, WMP-GDOM-GH-12b, WMP-GDOM-GH-12c, WMP-GDOM-GH-12e for relevant information related to these initiatives. WMP initiative WMP-GDOM-12 does not have a specified target as it is a combination of the aforementioned initiatives and therefore values in this row are N/A.
[61] Liberty does not have a separate program for transmission inspections. Liberty has approximately 75 miles of 60kV lines and 19 miles of 120kV lines that are included in the distribution inspection program.
[62] Liberty does not have a separate program for transmission inspections. Liberty has approximately 75 miles of 60kV lines and 19 miles of 120kV lines that are included in the distribution inspection program.
[63] (*): Liberty primarily measures risk reduction against the “no-build” baseline, which already factors in the reduction in wildfire risk from PSPS and PEDS/SRP/equipment settings. The risk reduction from PSPS and PEDS/SRP/equipment settings is calculated against the unmitigated baseline, as shown in Figure 6‑3. Together, these two initiatives provide an estimated 70% reduction in overall utility risk, as shown in Figure 6‑3. However, it is worth noting that the estimate is likely lower once additional outage program risk from PEDS is quantified in the risk model.

## LU Table 8-1
LU Table 8-1: Planned Covered Conductor Projects [65]
Circuit | Project | Planned Circuit Miles | Circuit Level CC BCR | Circuit Level UG BCR
MEY3400 | Spring Creek | 0.9 | 3.9 | 1.7
MEY3300 | Rainbow Tract | 1.2 | 2.8 | 1.3
CAL2501 | Verdi Phase 2 | 2 | 34.5 | 21.4
TPZ1202 | Topaz | 5 | 5.6 | 3.1
Total | N/A | 9.1 | N/A | N/A
[65] Project mileage reflects current engineering estimates and totals approximately 9.1 circuit miles. Liberty’s 2027 target is 8 circuit miles. The additional planned scope provides flexibility to address project phasing, material availability, permitting, construction constraints, and other execution risks

## Table 8-2
Table 8‑2: Liberty Asset Inspection Frequency, Method and Criteria
Type [67] | Inspection Activity (Program) | Frequency or Trigger (Note 1) | Method of Inspection (Note 2) | Governing Standards & Operating Procedures | Cumulative Quarterly Target 2027, Q1 | Cumulative Quarterly Target 2027, Q2 | Cumulative Quarterly Target 2027, Q3 | Cumulative Quarterly Target 2027, Q4 | % of HFRA and HFTD Covered Annually by Inspection Type | Condition Find Rate Level 1 | Condition Find Rate Level 2 | Condition Find Rate Level 3
Distribution | Detailed Inspections | 5-year cycle for OH; 3-year cycle for UG | Ground and some Aerial | G.O. 165 | 20 circuit miles | 50 circuit miles | 150 circuit miles | 198.5 circuit miles | 20% | 0.03% (Assets) | 4.59% (Assets) | 26.06% (Assets)
Distribution | Intrusive Pole Inspections | 10-year cycle | Ground | G.O. 165 | 0 poles | 0 poles | 2,238 poles | 2,238 poles | 10% | Level findings not applicable for this type of inspection | Level findings not applicable for this type of inspection | Level findings not applicable for this type of inspection
Distribution | Patrol Inspections | Annually | Ground and some Aerial | G.O. 165 | 200 circuit miles | 568.8 circuit miles | 568.8 circuit miles | 568.8 circuit miles | 80% | 0.02% | 0.08% | 0.03% (Assets)
[10 empty] | (Assets) | (Assets)
Distribution | Other Discretionary Inspections: Drone inspections | Annually for HFTD 3 | Aerial | G.O. 165 | 0 assets | 1,769 assets | 1,769 assets | 1,769 assets | 7%, but 100% HFTD-3 | 0.4% | 15.26% | 24.62%
Substation | Substation Inspections | Quarterly | Ground | G.O. 174 | 10 substations | 22 substations | 34 substations | 44 substations | 100% | Level findings not applicable for this type of inspection | Level findings not applicable for this type of inspection | Level findings not applicable for this type of inspection
Note 1: The electrical corporation must provide electrical corporation-specific risk-informed triggers used for asset inspections.
Note 2: The electrical corporation must provide electrical corporation-specific definitions of the different methods of inspection.
[67] Liberty does not have a separate program for transmission inspections. Liberty has approximately 75 miles of 60kV lines and 19 miles of 120kV lines that are included in the distribution inspection program.

## Table 8-3
Table 8‑3: Grid Hardening and Asset Inspection QA and QC Program Objectives
Initiative/Activity Being Audited | Tracking ID | Quality Program Type | Objective of the Quality Program
New construction in Grid Hardening WMP initiatives (i.e., Covered Conductor Installation) | (i.e., WMP-GDOM-GH-01) | Post-construction inspections | Confirm new construction meets applicable standards. New construction follows Liberty’s construction standards and best practices in construction.
Detailed Inspections of Distribution Electric Lines and Equipment | WMP-GDOM-AI-01 | QC | Perform a statistical sampling of detailed asset inspections to verify acceptable quality level and conformance rate of the program.
Intrusive Pole Inspections | WMP-GDOM-AI-02 | QC | Perform a statistical sampling of intrusive pole inspections to verify acceptable quality level and conformance rate of the program.
Equipment Settings to Reduce Wildfire Risk | WMP-GDOM-GO-01 | QA/QC | Relay settings are peer reviewed before being issued to the field. In-service settings are reviewed on a three-year cycle.

## Table 8-4
Table 8‑4: Grid Hardening and Asset Inspection QA and QC Activity Targets
Initiative/ Activity Being Audited | Type of Audit | Population/ Sample Unit | 2027: Population Size | 2027: Sample Size | Percent of Sample in the HFTD | Confidence level / MOE | 2027: Pass Rate Target
New construction in Grid Hardening WMP initiatives (i.e., Covered Conductor Installation) | Field | Completed new construction | All new construction completed in 2027 | 100% of new construction completed by contractors and 10% of new construction completed by Liberty | 100% | Unknown – population and sample sizes vary year to year | 95%
Detailed Inspections of Distribution Electric Lines and Equipment | Field | Detailed inspections completed in 2027 | 142 circuit miles | 12% OH, 16% UG | 100% | 95/10 | 90%
Intrusive Pole Inspections | Field | Intrusive Pole inspections completed in 2027 | 2,238 poles | 1% | 100% | 99/7 | 99%
Other Discretionary Inspections of Distribution Electric Lines and Equipment: Drone Inspections | Field/Desktop | Drone Inspections completed in 2027 | Under Development | Under Development | 100% | Under Development | Under Development

## LU Table 8-2
LU Table 8‑2: QA/QC Procedures
Document Name and ID | Version | Effective Date
Asset Inspection QA-QC 2026 Final | 2 | 8/20/206
Underground Electric Standards | 02 | 11/2027
Overhead Electric Standards | 01 | 09/2019

## LU Table 8-3
LU Table 8‑3: Liberty Asset Inspection QA/QC Program Sample Size and Units
Inspection Type | Cycle | Total Circuit Miles | Total Units | Annual Circuit Miles | Annual Units | Statistical Sampling
[6 empty] | CL/MoE | % | Annual Sample Units
OH Poles, Devices, and Conductors | 5-year | 707 | Units N/A | 142 | Units N/A | 95/10 | 12% | 17 miles
Intrusive Pole | 10-year | N/A | 24700 | N/A | 2470 | 99/7 | 1% | 34 poles

## Table 8-5
Table 8‑5: Number of Past Due Asset Work Orders Categorized by Age
HTFD Area | 0-30 Days | 31-90 Days | 91-180 Days | 181+ Days
Non-HFTD | 0 | 0 | 0 | 0
HFTD Tier 2 | 0 | 0 | 0 | 2*
HFTD Tier 3 | 0 | 0 | 0 | 1*
Table 8-5 and 8-6 Note: *These past due repairs are waiting on permits. One is in a protected marsh in South Lake Tahoe, and the other is near a falcon’s nest on west shore. The pole in the protected marsh has two Level 2 concerns. The pole near the falcon’s nest has one Level 3. Liberty expects permits in Q4 and Q3 respectively and expects to perform repairs before year’s end.

## Table 8-6
Table 8‑6: Number of Past Due Asset Work Orders Categorized by Age for Priority Levels [76]
Priority Level | 0-30 Days | 31-90 Days | 91-180 Days | 181+ Days
Priority 1 | 0 | 0 | 0 | 0
Priority 2 | 0 | 0 | 0 | 2*
Priority 3 | 0 | 0 | 0 | 1*
Table 8-5 and 8-6 Note: *These past due repairs are waiting on permits. One is in a protected marsh in South Lake Tahoe, and the other is near a falcon’s nest on west shore. The pole in the protected marsh has two Level 2 concerns. The pole near the falcon’s nest has one Level 3. Liberty expects permits in Q4 and Q3 respectively and expects to perform repairs before year’s end.
[76] Priority levels as defined by GO 95 Rule 18.

## Table 8-7
Table 8‑7: Top Impacted Circuits from SRP Program in 2024 and 2025
Circuit/Circuit Segment ID | Circuit/Circuit Segment Name | Circuit/Circuit Segment Length (overhead circuit miles) | Number of Outages in Past Three Years | Cumulative Outage Duration | Cumulative Number of Customers Impacted by Outages
TPZ1202 | Topaz 1202 | 55.6 | 4 | 557.16 | 2179
TRK7203 [79] | Truckee 7203 | 9.8 | 1 | 182.59 | 1710
CEM41 | Cemetery 41 | 5.8 | 1 | 166.57 | 273
MEY3300 | Meyers 3300 | 52.6 | 1 | 128.58 | 19
[79] Truckee 7203 is protected by a circuit breaker owned by NV Energy. This outage occurred under NV Energy’s Fast-Trip Fire Mode which is analogous to SRP.

## LU Table 8-4
LU Table 8‑4: Liberty Workforce Planning, Asset Inspections, Grid Hardening and Risk Event Inspection
Worker Title | Minimum Qualifications | Training Practices
Inspector Foreman | • Journeyman lineman • Minimum two years journeyman lineman experience • Class A Driver’s License • Expert knowledge of G.O. 95 and company’s construction standards | • Fulcrum application and database training • FPP Training • On the job training of company standards and G.O. 95
Inspector | • Journeyman lineman • Minimum one year journeyman lineman experience • Class A Drivers' License • General knowledge of G.O. 95 and company’s construction standards | • Fulcrum application and database training • FPP Training • On the job training of company standards and G.O. 95
Qualified Electrical Worker (“QEW”) | • Journeyman lineman or Journeyman Electrician • Minimum one-year journeyman lineman experience • Class A Driver’s License • General knowledge of G.O. 95 and Liberty’s construction standards | • Fulcrum application and database training • FPP training • On the job training of company standards and G.O. 95
Lineman | • Journeyman lineman • Class A Driver's license | • On-the-job training of company standards and G.O. 95 • FPP training • On-the-job training of covered conductor
Lineman Working Foreman | • Journeyman lineman • Minimum two years' experience as Journeyman • Lineman • Class A Driver's license | • On-the-job training of company standards and G.O. 95 • FPP training • Hendrix training of covered conductor installation (ACS and Tree Wire)
Engineer IV | • Must possess a Bachelor of Science in Electrical Engineering or an equivalent engineering degree from an accredited four-year college or university • Must hold PE certification | • SEL, GIS, CAD, OCalc, Quadra, OSI PI, Aspen Oneliner, company standards
Capital Administrator | • Associates or Bachelor’s degree in Construction Administration, Accounting or a related field or a minimum of three years of technical experience with a utility or other related field • Working knowledge of accounting, project management and construction management practices | • SAP Job Cost Training, FERC Code Training, SOX Policy Training, Capital Expenditure Policy Training, Cost Control training, Excel Training
Project Manager | • Associates or Bachelor’s degree in Project Management, Construction Administration, Engineering in a related field or a PMP certification and a minimum of five years of technical experience with a utility or other related field. Must have a demonstrated working knowledge of project management and construction management practices. | • PM Basics, Capital Expenditure Policy Training, SAP training, GIS training, Excel Training, Electrical Distribution 101, OH & UG Const Training
Substation Electrician | • Journeyman Electrician • Must be qualified to perform switching | • On-the-job training of substation equipment maintenance and replacement • FPP training • On-the-job training of company standards
Substation Electrician Foreman | • Journeyman Electrician • Minimum two years' experience as journeyman electrician • Must be qualified to perform switching | • On-the-job training of substation equipment maintenance and replacement • FPP training • On-the-job training of company standards
Relay Technician | • Journeyman Electrician or equivalent combination of education and experience in system protection • Must be qualified to perform switching | • On-the-job training of substation equipment maintenance and replacement • FPP training • On-the-job training of protective relaying and controls
Job Facilitator | • Journeyman lineman • Minimum two years' experience as journeyman lineman • Class A Driver's License | • On-the-job training of company standards and G.O. 95 • On-the-job training of covered conductor installation (ACS and Tree Wire) • FPP training • On-the-job training of internal QA/QC process • Fulcrum application and database training

## Table 9-1
Table 9‑1: Liberty Vegetation Management Targets, 2027 (Non-inspection Targets)
Initiative | Quantitative or Qualitative | Activity (Tracking ID) | Target Unit | 2027 Target/Status | x% Risk Impact 2027 | Section; Page Number
Integrated Vegetation Management | Qualitative | WMP-VM-VFM-04 | N/A | Maintain Tree Line USA / Complete by December 31, 2027 | Not calculated | 9.7; pp. 233-235
Workforce Planning | Qualitative | WMP-VM-WFP-01 | N/A | Liberty will continue to report annually on its recruitment, retention, and training of vegetation management and inspection personnel / Complete by December 31, 2027 | Not calculated | 9.13; pp. 257-261
Wood and Slash Management | Quantitative | WMP-VM-VFM-02 | Acres | 280 | Not calculated | 9.5; pp. 229-231
Substation Defensible Space | Qualitative | WMP-VM-VFM-03 | N/A | Perform routine inspections and treat vegetation as needed to maintain substation defensible space / Complete by December 31, 2027 | Not calculated | 9.6; pp. 231-233
Clearance | Quantitative | WMP-VM-VFM-05 | Circuit miles | 700 | Not calculated | 9.3; pp.225-227
Fall-In Mitigation | Quantitative | WMP-VM-VFM-06 | Circuit miles | 220 | Not calculated | 9.3; pp.225-227

## Table 9-2
Table 9‑2: Liberty Vegetation Management Inspections and Pole Clearing Targets, 2027
Activity (Program) | Tracking ID | Target Unit | Cml. Quarterly Target 2027, Q1 | Cml. Quarterly Target 2027, Q2 | Cml. Quarterly Target 2027, Q3 | Cml. Quarterly Target 2027, Q4 | % HFTD Covered in 2027 | % Risk Reduction 2027 | Activity Timeline Target | Section; Page Number
Vegetation Management Inspection Program - Detailed | WMP-VM-INSP-01 | Circuit miles | 45 | 110 | 175 | 233 | 33% | Not calculated | 365 days | 9.2.1; pp. 217-222
Vegetation Management Program - LiDAR | WMP-VM-INSP-03 | Circuit miles | 0 | 0 | 700 | 700 | 100% | Not calculated | Approx. 90 days for acquisition to data delivery | 9.2.3; pp.223-225
Pole Clearing – PRC 4292 Required | WMP-VM-VFM-01-R | Poles | 0 | 1500 | 3000 | 4500 | 100% | Not calculated | Approx. 150 days | 9.4; pp.227-229
Pole Clearing – Discretionary | WMP-VM-VFM-01-D | Poles | 0 | 133 | 266 | 400 | 100% | Not calculated | Approx. 150 days | 9.4; pp.227-229

## Table 9-3
Table 9‑3: Vegetation Management Inspection Frequency, Method, and Criteria
Inspection Type | Inspection Activity (Program) | Area Inspected | Frequency
Transmission and Distribution | Vegetation Management Program - LiDAR | Territory | Annual
Transmission and Distribution | Vegetation Management Program – Detailed | Territory | Three-year cycle
Transmission and Distribution | Vegetation Management Program – Patrol | Territory | As needed

## LU Table 9-1
LU Table 9‑1: Vegetation Management Detailed Inspection Procedures
Document Name and ID | Version | Effective Date
Vegetation Management Plan (VM-02) | 3 | 2025-04-10
Hazard Tree Management Plan (VM-03) | 1 | 2021-04-28
Post Work Verification Procedure (VM-04) | 3 | 2026-02-17
Vegetation Threat Procedure (VM-05) | 2 | 2022-06-03
Vegetation Management Notification and Refusal Resolution Policy (VM-06) | 1 | 2024-01-01
Vegetation Management Inspection Manual (VM-07) | 1 | 2023-08-25

## LU Table 9-2
LU Table 9-2: Radial Clearance Requirements PRC 4293; GO 95, HFTD (Case 14)
Voltage | Regulation Clearance Distance ("RCD") | Maintenance Action Threshold ("MAT") | Maintenance Clearance Distance ("MCD")
12kV - 25kV | 4’ | 6’ | 12’-15’
60kV | 4’ | 6’ | 12’-15’
120kV | 10’ | 15’ | 30-35'

## LU Table 9-3
LU Table 9-3: Radial Clearance Requirements; GO 95, Rule 35, Non-HFTD (Case 13)
Voltage | Regulation Clearance Distance ("RCD") | Maintenance Action Threshold ("MAT") | Maintenance Clearance Distance ("MCD")
12kV - 25kV | 1.5’ | 6’ | 12’-15’
60kV | 1.5’ | 6’ | 12’-15’
120kV | 1.7’ | 15’ | 30-35'

## LU Table 9-4
LU Table 9-4: Hazard Tree Attributes
Hazard Tree Attributes
Basal wound
Bleeding or resinous
Bulges and/or swellings
Cankers, including bleeding and gall rust
Cavities
Codominant or multiple stems from base or higher on trunk
Conks indicating heart rot, root rot, sap rot or canker rot
Cracks including shear
Dead branches and/or top
Dieback of twigs and/or branches
Embedded wires or cables
Excessive lean toward electrical facilities or excessive bow
Fire damage
Foliage – off color, flagging or loss
Hazard beam
History of limb failure(s) on tree
Included bark
Insect activity such as frass from termites, bark beetles or carpenter ants
Lightning damage
Live crown ration below 30%
Mistletoe – dwarf or broad-leaf
Nesting holes – birds, mammals, insects
Past poor pruning practices
Roots injured, exposed, undermined, or uplifted
Seam
Species failure patterns
Unnatural or structurally unsound canopy weight distribution
Weak, unsound branch attachments

## LU Table 9-5
LU Table 9-5: Vegetation Management Site Attributes
Site Attributes
Areas known to be affected by introduced tree pathogens
Areas of recent clearing/new edge
Change in drainage
Change in grade
Construction – including trenching, paving or road construction
Cultural disturbance to landscape – natural or unnatural
Diseased center – dead tree in middle and dying trees around it
High stand density with single species composition
High winds (fire watch)
History of failure(s) at site
History of repeated outages on circuit
Fire damage
Recent thinning or logging
Slope (by grade or percentage)
Soils prone to slides
Specific conditions like high winds
Storm damage

## LU Table 9-6
LU Table 9-6: Vegetation Management LiDAR Inspection Procedures
Document Name and ID | Type | Version | Effective Date
Vegetation Management Plan (VM-02) | Plan | 3 | 2025-04-10
Vegetation Threat Procedure (VM-05) | Process | 2 | 2022-06-03
Vegetation Management Inspection Manual (VM-07) | Process | 1 | 2023-08-25

## LU Table 9-7
LU Table 9-7: Vegetation Grow-In Zones, LiDAR Grow-In Analysis
Category | 12kV - 25kV | 60kV | 120kV
Grow-In Zone 1 | 0 - 1.5 feet | 0 - 1.5 feet | 0 - 4 feet
Grow-In Zone 2 | 1.5 – 4 feet | 1.5 – 4 feet | 4 - 10 feet
Grow-In Zone 3 | 4 – 6 feet | 4 – 6 feet | 10 - 15 feet
Grow-In Zone 4 | 6 – 12 feet | 6 – 12 feet | 15 - 30 feet

## LU Table 9-8
LU Table 9‑8: Vegetation Fall-In Zone Categories, LiDAR Fall-In Analysis
Zone Category | Criteria
Fall-In Zone 1 | Overstrike over 6 feet
Fall-In Zone 2 | Strike/overstrike less than 6 feet
Fall-In Zone 3 | Fall within 6 feet of wire

## LU Table 9-9
LU Table 9-9: Vegetation Management Pruning and Removal Procedures
Document Name and ID | Type | Version | Effective Date
Vegetation Management Plan (VM-02) | Plan | 3 | 2025-04-10
Hazard Tree Management Plan (VM-03) | Plan | 1 | 2021-04-28
Post Work Verification Procedure (VM-04) | Process | 3 | 2026-02-17
Vegetation Threat Procedure (VM-05) | Process | 2 | 2022-06-03
Vegetation Management Notification and Refusal Resolution Policy (VM-06) | Process | 1 | 2024-01-01

## LU Table 9-10
LU Table 9-10: Vegetation Management Pole Clearing Procedures
Document Name and ID | Type | Version | Effective Date
Vegetation Management Plan (VM-02) | Plan | 3 | 2025-04-10
Post Work Verification Procedure (VM-04) | Process | 3 | 2026-02-17
Vegetation Management Notification and Refusal Resolution Policy (VM-06) | Process | 1 | 2024-01-01
Vegetation Management Inspection Manual (VM-07) | Process | 1 | 2023-08-25

## LU Table 9-11
LU Table 9-11: Vegetation Management Wood and Slash Management Procedures
Document Name and ID | Type | Version | Effective Date
Vegetation Management Plan (VM-02) | Plan | 3 | 2025-04-10
Post Work Verification Procedure (VM-04) | Process | 3 | 2026-02-17

## LU Table 9-12
LU Table 9‑12: Vegetation Management Defensible Space Procedures
Document Name and ID | Type | Version | Effective Date
Vegetation Management Plan (VM-02) | Plan | 3 | 2025-04-10
Vegetation Management Inspection Manual (VM-07) | Process | 1 | 2023-08-25

## LU Table 9-13
LU Table 9-13: Vegetation Management IVM Procedures
Document Name and ID | Type | Version | Effective Date
Vegetation Management Plan (VM-02) | Plan | 3 | 2025-04-10
Hazard Tree Management Plan (VM-03) | Plan | 1 | 2021-04-28
Post Work Verification Procedure (VM-04) | Process | 3 | 2026-02-17
Vegetation Threat Procedure (VM-05) | Process | 2 | 2022-06-03
Vegetation Management Notification and Refusal Resolution Policy (VM-06) | Process | 1 | 2024-01-01
Vegetation Management Inspection Manual (VM-07) | Process | 1 | 2023-08-25

## Table 9-4
Table 9‑4: Liberty Partnerships in Vegetation Management
Partnering Agency/Org. | Activities | Objectives | Liberty Role | Anticipated Accomplishments
National Forest Foundation and Lake Tahoe Basin Management Unit | Implementation of the Forest Resilience Corridor Project on National Forest Land adjacent to Liberty electrical infrastructure. | Forest Resiliency Corridors, ROWs | Liberty provides funding and in-kind contributions for project work. Liberty is a key stakeholder and involved in the planning and implementation process. | 1,138 acres along 28 miles of overhead powerlines on National Forest Land treated.
Arbor Day Foundation | Coordinate Tree Replacement Program in Liberty’s service territory | Tree Replacement Program | Client | 5,000 compatible plants distributed since the project began in 2022. Maintain Tree Line USA recognition.
Truckee Meadows Fire Protection District | Mastication, chipping, fuels removal, pole grubbing, fire standby, community outreach | Fuel Management, Asset Protection | Client | Implement fuel reduction projects and provide fire standby services to exempt PAL or other restricted operations during fire season.
Truckee Fire Protection District | Fuel management, forest thinning, community outreach. | Fuel reduction and wildfire mitigation work in Truckee Fire Protection jurisdiction and Liberty service area overlap. | Liberty develops specifications and implements fuels and thinning work around powerlines within Truckee Fire Protection District project footprints. Liberty has participated in joint utility and fire agency collaboration and ordinance review as a result of this partnership. | Continue collaboration on additional joint projects in the Truckee area.
Local Fire, Forestry, Resource Conservation, and Special Interest Groups | Coordination of fuels reduction and wildfire mitigation efforts; knowledge sharing | Wildfire risk reduction. | Participates in meetings and coordinates with representatives from agencies and organizations invested in wildfire mitigation efforts in the Tahoe Basin. Liberty may implement work based on feedback or to meet the mutual objectives of stakeholders. | Leverage opportunities to implement joint projects aimed at mitigating wildfire risk.

## LU Table 9-14
LU Table 9-14: Vegetation Management Procedures for Activities Based on Weather Conditions
Document Name and ID | Version | Effective Date
Hazard Tree Management Plan (VM-03) | 1 | 2021-04-28
Vegetation Threat Procedure (VM-05) | 2 | 2022-06-03
Fire Prevention Plan | 1 | 2020-10-09

## LU Table 9-15
LU Table 9-15: Procedures for Post-Fire Restoration
Document Name and ID | Type | Version | Effective Date
Vegetation Management Plan (VM-02) | Plan | 3 | 2025-04-10
Hazard Tree Management Plan (VM-03) | Plan | 1 | 2021-04-28
Post Work Verification Procedure (VM-04) | Process | 3 | 2026-02-17
Vegetation Threat Procedure (VM-05) | Process | 2 | 2022-06-03
Vegetation Management Inspection Manual (VM-07) | Process | 1 | 2023-08-25

## Table 9-5
Table 9‑5: Vegetation Management QA and QC Program Objectives
Initiative/Activity Being Audited | Tracking ID | Quality Program Type | Objective of the Quality Program
Completed Tree Work | WMP-VM-VFM-05 | QC | To provide reasonable assurance that Tree Work is being completed as prescribed and in compliance with applicable regulations
Detailed Inspections | WMP-VM-INSP-01 | QC | To provide reasonable assurance that Detailed Inspections are being performed as scheduled
Hazard Tree Work | WMP-VM-VFM-06 | QC | To provide reasonable assurance that Hazard Tree Work is being completed as prescribed and in compliance with applicable regulations
Pole Clearing | WMP-VM-VFM-01 | QC | To provide reasonable assurance that Pole Clearing Work is being completed as prescribed and in compliance with applicable regulations
Compliance with minimum clearance requirements | N/A | Compliance Audit | To provide reasonable assurance that minimum clearance requirements are being maintained

## Table 9-6
Table 9-6: Vegetation Management QA and QC Activity Targets
Initiative/ Activity Being Audited | Population /Sample Unit | 2027 Population Size | 2027 Sample Size | 2027 % of Sample in HFTD | Confidence level / MOE | 2027 Pass Rate Target
Completed Tree Work | Annual Circuit Miles | 700 Miles | 228 Miles | 100% | 99/7 | 95%
Detailed Inspections | Annual Circuit Miles | 233 Miles | 76 Miles | 100% | 99/7 [87] | 95%
Hazard Tree Work | Annual Hazard Trees | 6,000 Trees | 597 Trees | 100% | 99/5 | 95%
Pole Clearing | Annual Poles | 4,900 Poles | 584 Poles | 100% | 99/5 | 92%
Compliance Audit | Circuit Miles | 700 Miles | 40 Miles | 100% | 95/3 | 99%
[87] Due to the small number of units in this category, the sample size was based on the 3-year plan. 700 miles over the 3-year period (233 miles per year) at a CL of 99 and MoE of 7 results in 228 miles during that 3-year period or 76 miles annually

## LU Table 9-16
LU Table 9-16: Vegetation Management QA/QC Procedures
Document Name and ID | Type | Version | Effective Date
Vegetation Management Plan (VM-02) | Plan | 3 | 2025-04-10
Hazard Tree Management Plan (VM-03) | Plan | 1 | 2021-04-28
Post Work Verification Procedure (VM-04) | Process | 3 | 2026-02-17
Vegetation Threat Procedure (VM-05) | Process | 2 | 2022-06-03
Vegetation Management Inspection Manual (VM-07) | Process | 1 | 2023-08-25

## LU Table 9-17
LU Table 9-17: Vegetation Management QA/QC Sample Size
Work Type | Category | Annual Circuit Miles | Annual Hazard Trees | Annual Poles | Statistical Sampling
[5 empty] | CL/MoE | % | Units
Completed Tree Work | Transmission and Distribution | 700 | - | - | 99/7 | 33 | 228 Miles
Detailed Inspections | Transmission and Distribution | 233 | - | - | 99/7 [88] | 33 | 76 Miles
Hazard Tree Work | Transmission and Distribution | - | 6000 | - | 99/5 | 10 | 597 Trees
Pole Clearing | Transmission and Distribution | - | - | 4900 | 99/5 | 12 | 584 Poles
Compliance Audit | Transmission and Distribution | 700 | - | - | 95/3 [89] | 6 | 40 Miles
[88] Due to the small number of units, in this category, the sample size was based on the 3-year plan. 700 miles over the 3-year period (233 miles per year) at a CL of 99 and MoE of 7 results in 228 miles during that 3-year period or 76 miles annually.
[89] The sample size selection methodology for the Compliance Audit varies from the sample size selection methodology for QC inspections. A 95% CL, 3% MoE, and 99% Std Dev (historical rate of compliance) was used for the Compliance Audit.

## LU Table 9-18
LU Table 9-18: Pass Rate Sample Units
Work Type | Category | Sample Unit
Completed Tree Work | Transmission and Distribution | Single Tree
Detailed Inspections | Transmission and Distribution | Single Tree
Hazard Tree Work | Transmission and Distribution | Single Tree
Pole Clearing | Transmission and Distribution | Single Pole

## LU Table 9-19
LU Table 9-19: Completed Tree Work Criteria
Conditions Evaluated | Category
Work Performed as Prescribed | Pass / Fail
Maintenance Clearance Distance Achieved | Pass / Fail
Will Hold Until Next Inspection | Pass / Fail
Potential Hazard Remains | Pass / Fail
Site Clean | Pass / Fail
ANSI Pruning Applied | Pass / Fail
Other Trees Affected | Pass / Fail
Site Condition Stable | Pass / Fail

## LU Table 9-20
LU Table 9-20: VM Detailed Inspections Criteria
Conditions Evaluated | Category
Location Information Correct | Pass / Fail
Species Correct | Pass / Fail
Quantity Correct | Pass / Fail
Work Type Noted | Pass / Fail
Tree Health Noted | Pass / Fail
Priority Noted | Pass / Fail
Project Type Noted | Pass / Fail
Clean Up Method Noted | Pass / Fail
Quantity of Non-Listed Trees | Pass / Fail

## LU Table 9-21
LU Table 9-21: Hazard Tree Work Criteria
Conditions Evaluated | Category
Work Performed as Prescribed | Pass / Fail
Potential Hazard Remains | Pass / Fail
Site Clean | Pass / Fail
Other Trees Affected | Pass / Fail
Site Condition Stable | Pass / Fail

## LU Table 9-22
LU Table 9-22: Pole Clearing Criteria
Conditions Evaluated | Category
Location Information Correct | Pass / Fail
Subject Pole | Pass / Fail
Pole Clearing Tag | Pass / Fail
PRC 4292 Radial Clearance | Pass / Fail
PRC 4292 Vertical Clearance 0-8ft | Pass / Fail
PRC 4292 Vertical Clearance >8ft | Pass / Fail
ANSI Pruning Applied | Pass / Fail
Site Clean | Pass / Fail

## Table 9-7
Table 9‑7: Number of Past Due Vegetation Management Work Orders Categorized by Age and HFTD Tier
HTFD Area | 0-30 Days | 31-90 Days | 91-180 Days | 181+ Days
Non-HFTD | 0 | 0 | 0 | 0
HFTD Tier 2 | 0 | 0 | 0 | 0
HFTD Tier 3 | 0 | 0 | 0 | 0

## Table 9-8
Table 9‑8: Number of Past Due Vegetation Management Work Orders Categorized by Age and Priority Levels
HTFD Area | 0-30 Days | 31-90 Days | 91-180 Days | 181+ Days
Priority 1 | 0 | 0 | 0 | 0
Priority 2 | 0 | 0 | 0 | 0
Priority 3 | 0 | 0 | 0 | 0

## Table 9-9
Table 9‑9: Vegetation Management Qualifications and Training
Worker Title | Minimum Qualifications for Target Role | Applicable Certifications | # of Electrical Corporation Employees with Min Quals | # of Electrical Corporation Employees with Applicable Certifications | # of Contracted Employees with Min Quals | # of Contracted Employees with Applicable Certifications | Total # of Employees | Reference to Electrical Corporation Training/Qualification Programs
Manager, Vegetation Management | Five years’ experience in utility arboriculture; Bachelor's degree or equivalent | ISA Certified Arborist or Registered Professional Forester, ISA Utility Specialist | 1 | 1 | 0 | 0 | 1 | No formal training program required for this position.
Supervisor, Vegetation Management | Five years’ experience in utility arboriculture; Bachelor's degree or equivalent | ISA Certified Arborist or Registered Professional Forester, ISA Utility Specialist | 1 | 1 | 0 | 0 | 1 | No formal training program required for this position.
System Arborist/Forester | Three years’ experience in utility arboriculture; Bachelor’s degree or equivalent | ISA Certified Arborist or Registered Professional Forester, ISA Utility Specialist | 4 | 4 | 0 | 0 | 4 | No formal training program required for this position.
Program Administrator | Five years’ experience in a finance, accounting, business administration; Bachelor’s degree or equivalent | None | 1 | 1 | 0 | 0 | 1 | No formal training program required for this position.
Supervisor, Utility Forester | Three years’ experience in utility arboriculture | ISA Certified Arborist or Registered Professional Forester | 0 | 0 | 1 | 1 | 1 | No formal training program required for this position.
Utility Forester I | Less than one year experience in utility arboriculture | None | 0 | 0 | 0 | 0 | 0 | No formal training program required for this position.
Utility Forester II | One year experience in utility arboriculture | None | 0 | 0 | 1 | 1 | 1 | No formal training program required for this position.
Utility Forester III | Two years' experience in utility arboricultural | ISA Certified Arborist or Registered Professional Forester | 0 | 0 | 0 | 0 | 0 | No formal training program required for this position.
Utility Forester IV | Three years’ experience in utility arboriculture | ISA Certified Arborist or Registered Professional Forester | 0 | 0 | 2 | 2 | 2 | No formal training program required for this position.
Utility Forester V | Five years’ experience in utility arboriculture | ISA Certified Arborist, ISA Certified Utility Specialist or Registered Professional Forester | 0 | 0 | 3 | 3 | 3 | No formal training program required for this position.
Vegetation Coordinator | Less than one year experience in utility arboriculture | None | 1 | 1 | 0 | 0 | 1 | No formal training program required for this position.
Tree Crew Supervisor | 24 months experience as Line Clearance Certified Tree Worker | EHAP, CPR + First Aid, Line Clearance Arborist Certification | 0 | 0 | 4 | 4 | 4 | No formal training program required for this position.
Line Clearance Certified Tree Worker | 18 months experience as Apprentice Line Clearance Certified Tree Worker | EHAP, CPR + First Aid, Line Clearance Arborist Certification | 0 | 0 | 4 | 4 | 4 | No formal training program required for this position.
Apprentice Line Clearance Certified Tree Worker | 6 months’ experience as a Groundperson | EHAP, CPR + First Aid, Line Clearance Arborist Certification | 0 | 0 | 4 | 3 | 4 | No formal training program required for this position.
Equipment Operator | Commercial Driver’s License or 1 year experience operating equipment | EHAP, CPR + First Aid | 0 | 0 | 3 | 3 | 3 | No formal training program required for this position.
Groundperson | Entry-level; related training and on-the-job experience preferred | EHAP, CPR + First Aid | 0 | 0 | 4 | 4 | 4 | No formal training program required for this position.
Pole Clearing Inspector | Entry-level; related training and on-the-job experience preferred | EHAP, CPR + First Aid | 0 | 0 | 2 | 2 | 2 | No formal training program required for this position.
Pole Clearing Technician | Entry-level; related training and on-the-job experience preferred | EHAP, CPR + First Aid | 0 | 0 | 7 | 7 | 7 | No formal training program required for this position.
Note: Personnel and certificate holder numbers may fluctuate.

## LU Table 9-23
LU Table 9-23: Liberty VM Credentials or Certifications
Credential or Certification Type | Liberty Internal VM Full-Time Employees with Credentials
| Number | Percentage
ISA Certified Arborist | 5 | 55.6%
ISA Tree Risk Assessment Qualification | 6 | 66.7%
ISA Certified Utility Specialist | 6 | 66.7%
ISA Board Certified Master Arborist | 2 | 22.2%
Certified Tree Safety Professional | 1 | 11.1%
Utility Vegetation Management Professional Certificate | 1 | 11.1%
PMI Project Management Professional | 1 | 11.1%
SAF Certified Forester | 1 | 11.1%
Licensed Timber Operator | 1 | 11.1%
Geographic Information Systems (GIS) Certificate of Completion | 1 | 11.1%

## Table 10-1
Table 10‑1: Situational Awareness WMP Initiative Targets
WMP Initiative Category | Initiative | Activity (Tracking ID #) | Quantitative or Qualitative Target | Target Unit | 2027 Total / Status | % Risk Reduction for 2027 | Three-Year Total | Section; Page Number
Situational Awareness and Forecasting | Environmental monitoring systems | Fuel Moisture Sampling (WMP-SA-01) | Quantitative | Fuel sampling locations monitored | 5 | Not calculated | 15 | 10.2.1; pp. 266-270
Situational Awareness and Forecasting | Environmental monitoring systems | Fuel Moisture Sampling (WMP-SA-01) | Qualitative | Use field collected fuel moisture samples to supplement automated ERC percentiles | Complete December 31, 2027 | Not calculated | Complete | 10.2.1; pp. 266-270
Situational Awareness and Forecasting | Grid monitoring systems | WMP-SA-02 | Quantitative | Fault Indicators Installed | Complete | Not calculated | Complete | 10.3.1; pp. 273-275
Situational Awareness and Forecasting | Grid monitoring systems | WMP-SA-02 | Qualitative | Sensitive Earth Fault (SEF) protection module study | Complete | Not calculated | Complete | Appendix D; ACI: LU-25U-08
Situational Awareness and Forecasting | Ignition Detection Systems | WMP-SA-03 | Quantitative | Wildfire Cameras Sponsored | 8 | Not calculated | 24 | 10.4.1; pp. 277-280
Situational Awareness and Forecasting | Ignition Detection Systems | WMP-SA-03 | Qualitative | Finalize Agreement with UNR for wildfire camera sponsorship | Complete | Not calculated | Complete | 10.4.1; pp. 277-280
Situational Awareness and Forecasting | Weather forecasting | WMP-SA-04 | Quantitative | Percent of weather stations in service | 80% | Not calculated | 80% | 10.2.1; pp. 266-270 10.5.5; pp. 284-285
Situational Awareness and Forecasting | Weather forecasting | WMP-SA-04 | Qualitative | Maintain fire weather dashboard functionality | Complete December 31, 2027 | Not calculated | Complete | 10.5.1; pp. 281-283
Situational Awareness and Forecasting | Weather Station Maintenance and Calibration | Weather Station Inspections (WMP-SA-01) | Quantitative | Weather Stations Inspected | 39 | Not calculated | 117 | 10.5.5; pp. 284-285
Situational Awareness and Forecasting | Weather Station Maintenance and Calibration | Weather Station Health (WMP-SA-01) | Qualitative | Conduct necessary repairs and updates to maintain weather station network health | Complete December 31, 2027 | Not calculated | Complete | 10.5.5; pp. 284-285

## Table 10-2
Table 10‑2: Liberty Environmental Monitoring Systems
System | Measurement/ Observation | Frequency | Purpose and Integration
Weather stations | • Temperature (°F) • Dew Point (%) • Wind Speed (mph) • Wind Direction • Wind Gust (mph) • Wind Gust Direction • Latest Rain (inches) • Fuel Moisture (%) • Soil Moisture (%) • Soil Temperature (°F) | 6 observations per hour | • Improve weather forecasts with observed weather station data • Configure alerts • Generate reports
Remote sensing fuel moisture | • Fuel Moisture (%) | 6 observations per hour | • Calculate fuel moisture content
Remote sensing soil moisture | • Soil Moisture (%) | 6 observations per hour | • Calculate soil moisture content
Fuel moisture field sampling | • Live woody (%) • 1,000 hour (%) • Live fuel moisture by predominant species | 1 per week | • Calculate Energy Release Component • Fire behavior calculations

## Table 10-3
Table 10‑3: Liberty Grid Monitoring Systems
System | Measurement/ Observation | Frequency | Purpose and Integration
Fault indicators | Line tripped or Line not tripped | Varies based on trip events | Expedite response and location of tripped lines
Recloser Controllers | Real-time SCADA data, fault event data, SER data | Continuous | Provide real-time visibility into recloser operations, fault detection, and event logging. Majority integrated with SCADA for system-wide situational awareness and control.
Substation Protective Relays | SCADA data, fault event records, Sequence of Events (“SER”) logs | Continuous | Enable monitoring and diagnostics of substation events. Relay-triggered events automatically notify engineers via AcSELerator TEAM. Supports root cause analysis and corrective action planning.

## Table 10-4
Table 10‑4: Fire Detection Systems Currently Deployed
Detection System | Capabilities | Companion Technologies | Contribution to Fire Detection and Confirmation
Video Cameras (ALERTWest) | AI wildfire detection | None | Confirmed detections will generate alerts to assist in quicker response and suppression times.
Fire growth potential software (PyreCast) | Forecasts for active fires, risk, and fire weather | Satellite-based heat detection, weather models, weather station data | By combining satellite-based detection, predictive modeling, and weather forecast integration, PyreCast offers a comprehensive tool for fire detection and confirmation, enhancing wildfire situational awareness and response strategies.
Fire growth potential software (Technosylva Wildfire Analyst) | Wildfire spread predictions | FireRisk, FireSight | The ability to simulate fire spread under forecast weather conditions helps identify areas at greatest risk, supporting proactive planning and mitigation efforts.

## Table 10-5
Table 10-5: Fire Potential Features
Feature Group | Feature | Altitude | Description | Source | Update Cadence | Spatial Granularity | Temporal Granularity
Weather | Wind force | Surface | Wind gust force at surface | High Resolution Rapid Refresh (HRRR) Model | 4 times per day | 3 km | Hourly
Weather | Wind force | Surface | Wind gust force at surface | North American Mesoscale Model (NAM) Weather Model | 4 times per day | 3 km | Hourly
Weather | Wind force | Surface | Wind gust force at surface | Global Forecast System (GFS) Weather Model | 4 times per day | 13 km | 3 hours
Weather | Wind force | Surface | Wind gust force at surface | European Center for Medium Range Weather Forecasts (ECMWF) Weather Model | 4 times per day | 14 km | 12 hours
Weather | Wind speed | Surface | 3 second wind gust speed at surface | High Resolution Rapid Refresh (HRRR) Weather Model | 4 times per day | 3 km | Hourly
Weather | Wind speed | Surface | 3 second wind gust speed at surface | North American Mesoscale Model (NAM) Weather Model | 4 times per day | 3 km | Hourly
Weather | Wind speed | Surface | 3 second wind gust speed at surface | Global Forecast System (GFS) Weather Model | 4 times per day | 13 km | 3 Hours
Weather | Wind speed | Surface | 3 second wind gust speed at surface | European Center for Medium Range Weather Forecasts (ECMWF) Weather Model | 4 times per day | 14 km | 12 Hours
Fuel | Head fire flame length | Surface | Operational fire spread model used to calculate length | Eularian Level set Model of Fire Spread (ELMFIRE) | 4 times per day | 30 m | 6 Hours

## Table 11-1
Table 11‑1: Emergency Preparedness and Community Outreach Targets by Year
WMP Initiative Category | WMP Initiative | Activity (Tracking ID#) | 2027 Status | Section; Page Number
Emergency Preparedness | Collaboration and coordination with public safety partners (“PSPs”) | WMP-EP-02 | Conduct emergency drills; continue engagement with local stakeholders and PSPs to prepare for and respond to fire-related event; meet with Community Advisory Boards | 11.3.1; pp. 306-309
Emergency Preparedness | Customer support in wildfire and PSPS emergencies | WMP-EP-05 | Conduct Incident Command Training for all identified IC members and hold a PSPS Tabletop exercise; continue implementation of Liberty’s AFN Plan; continue maintenance of emergency response plans; enhance documentation and use of lessons learned to update plans. | 11.5; pp. 335-338
Emergency Preparedness | Learning after wildfire and PSPS events | WMP-EP-06 | After action reports for each event | 7; pp. 145-149
Community Outreach and Engagement | Public outreach and education awareness for wildfires, PSPS, outages from protective equipment and device settings, and vegetation management | WMP-CO-01 | Two wildfire and PSPS outreach surveys | 11.4.3; pp. 325-329
Community Outreach and Engagement | Engagement with AFN populations, local governments, and tribal communities | WMP-CO-03 | 9 Events | 11.4.4; pp. 330-332
Community Outreach and Engagement | Engagement with AFN populations, local governments, and tribal communities | WMP-CO-03 | Enhance accessibility based on community feedback and evolve best practices where possible | 11.4.4; pp. 330-332
Community Outreach and Engagement | Best practice sharing with other electrical corporations | WMP-CO-05 | Participation in working groups (i.e., Risk Modeling Working Group) and Joint IOU Councils (i.e., AFN Collaborative Council) | 5; p. 35-108 11.3.2; pp.309-312 11.4.4; pp. 330-332 13.1; pp. 346-350

## Table 11-2
Table 11‑2: Liberty Gaps and Limitations in Integrating Wildfire- and PSPS-Specific Strategies into Emergency Plan
Gap or Limitation Subject | Remedial Brief Description | Remedial Action Plan
Liberty’s 2024 CEMP lacked detailed descriptions of Incident Management Team Liaison functions. | Manager, Emergency management should work with IMT to update CEMP. | Liberty’s CEMP was updated on 05/06/2025 to include these descriptions.
Liberty’s 2024 CEMP included a description of how its Incident Command System (“ICS”) was organized, but not the Incident Action Planning Process. | Manager, Emergency management should work with IMT to update CEMP. | Liberty’s CEMP was updated on 05/06/2025 to list the steps in the Incident Action Planning Process.

## LU Table 11-1
LU Table 11‑1: Emergency Management Personnel Training
Training Topic | Purpose and Scope | Training Method | Training Frequency | Position or Title of Personnel Required to Take Training | Form of Verification or Reference
Community Resource Center (“CRC”) Response | • Train internal employees in Community Resource Center Lead positions. Training for the process of setting up and supporting Community Resource Center locations in the event of PSPS | Virtual or in-person | Annual | Community Resource Center Lead, CRC Contractor | Training logs
Introduction to the electrical corporation’s emergency preparedness plan | • The contents of emergency response plans, in particular those for wildfire- and PSPS specific incidents • The electrical corporation’s overall safety practices and those specific to wildfire and PSPS incidents • The organizational structure of how the electrical corporation responds to, manages, and recovers from incidents • The electrical corporation’s and public safety partners’ roles and responsibilities before, during, and after a wildfire or PSPS incident • The electrical corporation’s notification and activation protocols for wildfires and PSPS incidents | Online course, workshop, or in-person training | Annual | All-staff | Training materials and training logs
Emergency response procedures during a wildfire | • Incident Management Team Assignments during a wildfire scenario • Wildfire response procedures during Incident • Immediate Response, 0-2 hours • Intermediate Response, 2-12 hours • Extended Response, Greater than 12 hours • Demobilization/System Recovery | Workshop or in-person training | Annually, prior to fire season | Incident Management Team | Training logs
Practices, policies, and procedures for emergency response and service restoration for PSPS events | • Incident Management Team actions for PSPS Stages 1, 2a, 2b, 2c, 3, 4, and 5 as outlined in the PSPS Playbook | TTX and FSX | Annual | Incident Management Team | Training logs
Introduction to the electrical corporation’s mutual aid agreement with aid partner (contractor training) | • Familiarize aid partners with the concepts and actions in the mutual aid operations plan prior to implementation • Allow responding resources the opportunity to practice their procedures and responsibilities • Scope items include: o Contents of mutual aid operations plan, in particular those on wildfire- and PSPS-specific incidents o The electrical corporation’s overall safety practices and those specific to wildfire and PSPS incidents o The organizational structure and interoperability of how the mutual aid partners and resources collaborate and coordinate o The electrical corporation’s and public safety partners’ roles and responsibilities before, during, and after a wildfire or PSPS incident o The electrical corporation’s notification and activation protocols for wildfires and PSPS events | Online course, workshop, or in-person training | Annual | All potential mutual aid resources | Training materials and training logs

## Table 11-3
Table 11 3: Liberty Communication Protocols, Procedures, and Systems with Public Safety Partners
Public Safety Partner Group | Key Protocols | Frequency of Prearranged Communication Review and Update
City and county officials, fire, law enforcement, and critical infrastructure | Text, email, and/or voice message via OnSolve system; PSP partner portal; exercises; state executive briefings | Annually (April)
CPUC | Email notifications; state executive briefings; PSP portal | Annually (April)
CalOES | OES notification forms; state executive briefings; email communications; PSP portal | Annually (April)

## Table 11-4
Table 11‑4: Gaps and Limitations in Communication Coordination with PSPs
Gap or Limitation Subject | Remedial Brief Description | Remedial Action Plan
During an event, a complete list of Public Safety Partners (“PSPs”) that have been contacted is needed by the Regulatory Liaison in a timely manner to facilitate reporting to regulatory agencies. | A record of PSP contact should be added to Liberty’s in-event tracking spreadsheet for more efficient reporting by the Regulatory Liaison. | Strategy: IMT members will update the in -event tracking spreadsheet to create a section for PSP contact. Target timeline: Completed
For 2024 events, Liberty’s Customer Solutions team took over responsibility of notification to PSPs, community officials, and key accounts from the PSP Liaison position, which worked well. The PSP Liaison already has multiple duties. | Assign PSP notification officially to Liberty’s Customer Solutions team. | Strategy: Re-assignment of duties. Target timeline: Completed

## Table 11-5
Table 11‑5: Liberty Collaboration in Local Wildfire Mitigation Planning
Name of County, City, or Tribal Agency or Civil Society Organization (e.g., nongovernmental organization, fire safe council) | Program, Plan, or Document | Last Version of Collaboration | Level of Collaboration
Liberty, NV Energy, and Truckee Donner Public Utility District Fire Mitigation/PSPS Collaboration | None | Coordination on situational awareness, PSPS exercises and wildfire mitigation. | Meets weekly during fire season.
Washoe Tribe | Tribal Government Wildfire Safety | Review customer assistance programs and wildfire preparedness. | Schedule meetings and outreach for ongoing collaboration.
South Tahoe Public Utility District and Lake Valley Fire Protection District | 2026 South Tahoe Public Utility District and Lake Valley Fire Protection District Multi-Jurisdictional Hazard Mitigation Plan Update | Hazard Mitigation Planning Committee Meeting conducted on 04/02/2026 | Stakeholder participant for the 2026 Multi-Jurisdictional Hazard Mitigation Plan Update
California Tahoe Conservancy, Lake Valley Fire Protection District, USFS Lake Tahoe Basin Management Unit, and Tahoe Resource Conservation District | Liberty’s 2027 Wildfire Mitigation Plan | Risk Model review and feedback on 07/30/2026 | Liberty hosted meeting with governmental agencies and stakeholders for feedback on its risk modeling methodology and strategy
Tahoe Fire and Fuels Team | Planning and executing fuels reduction projects. | South Lake High School Fuels Reduction Project | Regular meetings and work as implementation partners.

## Table 11-6
Table 11‑6: Gaps and Limitations in Collaborating on Local Wildfire Mitigation Planning
Subject of Gap or Limitation | Brief Description of Gap or Limitation | Strategy for Improvement
More timely transport and distribution of repair supplies to the Walker / Coleville area is needed as well. | Repair materials for Walker / Coleville should be pre-staged. | Strategy: Store repair materials in CONEX boxes for more timely repairs. Target timeline: Completed

## Table 11-7
Table 11‑7: Collaboration with Tribal Agencies
Name of Tribal Agency | Program, Plan, or Document | Last Version of Collaboration | Level of Collaboration
Washoe Tribe | Memorandum of Understanding (“MOU”) | October 17, 2024 | Agreement reached for sue of tribal facility as CRC location.

## Table 11-8
Table 11‑8: Gaps and Limitations in Collaborating with Tribal Agencies
Subject of Gap or Limitation | Description of Gap or Limitation | Strategy for Improvement
The Washoe CRC location is somewhat remote. More affordable options are needed by the logistics team for lunch items at this CRC. | Vendor contracts are needed for acquisition of CRC lunches. | Strategy: Execute new contracts with vendors for food options. Target timeline: Complete

## Table 11-9
Table 11‑9: Protocols for Emergency Communication to Stakeholder Groups
Stakeholder Group | Event Type | Method(s) for Communicating | Means to Verify Message Receipt
General public | Wildfire | Wildfire-specific communications are conducted in three phases: before, during, and following an emergency event. Efforts before focus on immediate actions customers and the public can employ to remain safe, resilient, and updated during the emergency. This applies to all Liberty constituents to include the General Public, Priority Services, AFN populations, populations with limited English-speaking ability, and tribal populations. | Community Outreach; Public Workshops; Yearly surveys
General public | Wildfire-related outage | Liberty will employ standard communication channels to communicate wildfire-related outages including, but not limited to social media channels, broadcast and print media, and the Liberty website. As part of its expanded outreach, Liberty will coordinate roadside changeable message signs with Caltrans throughout affected communities to keep impacted residents informed. These signs will be critically important to educate tourists in Liberty’s service territory. Liberty Customers are notified via the OnSolve Communication system. | OnSolve acknowledgement receipt
General public | PSPS-related outage | Liberty will employ standard communication channels to promote emergency service resources including, but not limited to social media channels, broadcast and print media, and the Liberty website. As part of its expanded outreach, Liberty will coordinate roadside changeable message signs with Caltrans throughout affected communities to keep impacted residents informed. These signs will be critically important to educate tourists in Liberty’s service territory. Liberty has a PSPS Playbook with pre-scripted messages to deliver during all five stages of a PSPS. Liberty Customers are notified via the OnSolve Communication system. | OnSolve acknowledgement receipt
General public | Restoration of service | Following the event, Liberty focuses on transparency in educating customers and the public on the impact of the event and soliciting customer feedback to improve communication efforts for any future event. Liberty Customers are notified via the OnSolve Communication system. | OnSolve acknowledgement receipt, After Action Briefings and Reports
Priority essential services | Wildfire | Wildfire-specific communications are conducted in three phases: before, during, and following an emergency event. These efforts focus on immediate actions that customers and priority essential services can take to remain safe, resilient, and informed during an emergency. | Community Outreach; Public Workshops; Yearly surveys
Priority essential services | Wildfire related outage | During a major outage or emergency that affects a significant number of customers, an email is sent to personnel, agencies, and media to provide information, detail, and status of the outage. As the outage or emergency continues, status update emails and/or phone calls will be made to keep the agencies and media informed. Liberty will also disseminate detailed information on the wildfire including a list and maps of impacted communities, critical facilities, and estimated number of impacted customers and share it with local public safety partners and elected officials via our Public Safety Partner Portal. Public Safety Partners are notified via the OnSolve Communication system. | Notification receipt via OnSolve.
Priority essential services | PSPS-related outage | Liberty will disseminate detailed information on the PSPS event, including a list and maps of impacted communities, critical facilities, and estimated number of impacted customers and share it with local public safety partners and elected officials via our Public Safety Partner Portal. Public Safety Partners are notified via the OnSolve Communication system. | Notification receipt via OnSolve, feedback from public workshops.
Priority essential services | Restoration of service | Once the outage has concluded and the system is back to normal, a final email will be sent to close out the communication of the incident, and Public Safety Partners are notified via the OnSolve Communication system. | Notification receipt via OnSolve.
AFN populations | Wildfire Related outage | Medical Baseline or Green Cross customers who will be affected by the outage will receive a direct phone call from Liberty CalPeco staff notifying them of outage details, including but not limited to time, duration, and reason. Liberty’s goal, whenever possible, is to notify the medical baseline customer group 72 hours in advance of a planned outage. | Notification receipt via OnSolve.
AFN populations | PSPS related outage | Medical Baseline or Green Cross customers who will be affected by the outage will receive a direct phone call from Liberty CalPeco staff notifying them of outage details, including but not limited to time, duration, and reason. Liberty’s goal, whenever possible, is to notify the medical baseline customer group 72 hours in advance of a planned outage. If the customer can’t be contacted via OnSolve a Liberty staff member will place a phone call, and ultimately knock on the customer’s door and leave a door hanger if notification receipt has not been confirmed through the methods outlined above. | Notification receipt via OnSolve. In person door knock if no OnSolve receipt notification; Door hanger if door not answered.
AFN populations | Restoration of Service | Once the outage has concluded, a final update will be sent directly to customers and media, as well as posted to social media accounts and the Liberty website with a request that any customers still without power notify the Company. Liberty Customers are notified via the OnSolve Communication system. | Notification receipt via OnSolve.
Spanish population with limited English proficiency | Wildfire related outage | Wildfire-specific communications are conducted in three phases: before, during, and following an emergency event. Efforts before focus on immediate actions customers and the public can employ to remain safe, resilient, and updated during the emergency. English and Spanish have been identified as the most prevalent languages used in the Liberty service territory. Customers are notified via the OnSolve Communication system. As of June 2026, Liberty established utilization of Propio, a translation language service. Propio is available to customer service representatives, and supports in-language customer communication in over 300 languages. Liberty has customer-facing staff that are fluent in Spanish. | Customer Service in person communication; Notification receipt via OnSolve.
Spanish population with limited English proficiency | PSPS related outage | Liberty will employ standard communication channels to promote emergency service resources including, but not limited to social media channels, broadcast and print media, and the Liberty website. Customers are notified via the OnSolve Communication system. Liberty PSPS notifications are currently transmitted in English; however, to the extent possible, Liberty includes a line to notifications in Spanish directing customers to further information in Spanish. Liberty’s Onsolve notification system directs customers to Liberty’s website, which has an available Spanish translation option. | Customer Service in person communication; Notification receipt via OnSolve.
Spanish population with limited English proficiency | Restoration of Service | Once the outage has concluded, a final update will be sent directly to customers and media, as well as posted to social media accounts and the Liberty website with a request that any customers still without power notify the Company. Customers are notified via the OnSolve Communication system. | Customer Service in person communication; Notification receipt via OnSolve.
Washoe Tribe | Wildfire related outage | Wildfire-specific communications are conducted in three phases: before, during, and following an emergency event. Efforts before focus on immediate actions customers and the public can employ to remain safe, resilient, and updated during the emergency. Liberty has conducted in person briefings on emergency management at Tribal meetings. | Community Outreach; Public Workshops; Yearly surveys
Washoe Tribe | PSPS related outage | Liberty will employ standard communication channels to promote emergency service resources including, but not limited to social media channels, broadcast and print media, and the Liberty website. As part of its expanded outreach, Liberty will coordinate roadside changeable message signs with Caltrans throughout affected communities to keep impacted residents informed. Liberty has a PSPS Playbook with pre-scripted messages to deliver during all five stages of a PSPS. Liberty Customers are notified via the OnSolve Communication system. | Notification receipt via OnSolve.
Washoe Tribe | Restoration of Service | Once the outage has concluded, a final update will be sent directly to customers and media, as well as posted to social media accounts and the Liberty website with a request that any customers still without power notify the Company. Customers are notified via the OnSolve Communication system. | OnSolve acknowledgement receipt; After Action Briefings and Reports
People in remote areas | Wildfire related outage | Wildfire-specific communications are conducted in three phases: before, during, and following an emergency event. Efforts before focus on immediate actions customers and the public can employ to remain safe, resilient, and updated during the emergency. Liberty has made extensive efforts to present emergency management briefings in the towns of Portola and Loyalton in the north part of the service territory and in Alpine and Mono Counties in the southern portion of the service territory. | Community Outreach; Public Workshops; Yearly surveys
People in remote areas | PSPS related outage | Liberty will employ standard communication channels to promote emergency service resources including, but not limited to social media channels, broadcast and print media, and the Liberty website. As part of its expanded outreach, Liberty will coordinate roadside changeable message signs with Caltrans throughout affected communities to keep impacted residents informed. Liberty has a PSPS Playbook with pre-scripted messages to deliver during all five stages of a PSPS. Liberty Customers are notified via the OnSolve Communication system. | OnSolve acknowledgement receipt
People in remote areas | Restoration of Service | Once the outage has concluded, a final update will be sent directly to customers and media, as well as posted to social media accounts and the Liberty website with a request that any customers still without power notify the Company. Customers are notified via the OnSolve Communication system. | OnSolve acknowledgement receipt; After Action Briefings and Reports

## Table 11-10
Table 11‑10: List of Target Communities for Outreach and Awareness Efforts
Target Community | Interests or Concerns Before, During, and After Wildfire and PSPS events
Identified Access and Functional Needs individuals | Liberty understands customers with access and functional needs may require earlier communication to plan for needs before, during, and after PSPS events and require communication regarding available resources. Liberty values targeted outreach to Access and Functional Needs populations with a focus on PSPS preparedness measures, education around Liberty’s notification system, and importance of updated contact information.
Individuals enrolled in Medical Baseline Allowance Program | Liberty understands customers with medical needs may require earlier communication to plan for medical needs before, during, and after PSPS events and require communication regarding available resources.
Community Based Organizations (“CBOs”) | Liberty understands CBOs require communication regarding PSPS events to effectively communicate with and support their communities before, during, and after PSPS events.

## LU Table 11-2
LU Table 11‑2: List of Community Partners
Community Partners | County | City
Sierra Community House | Placer | Kings Beach, CA
Tahoe Truckee Community Foundation | Nevada | Truckee, CA
Placer County Health & Human Services | Placer | Carnelian Bay, CA
Sierra Senior Services | Nevada | Truckee, CA
North Tahoe Truckee Homeless Services | Nevada | Truckee, CA
FREED Independent Living Center | Nevada, Placer, Sierra | Grass Valley, CA
Placer Independent Resource Services (“PIRS”) | Placer, El Dorado, Alpine | Auburn, CA
211 Connecting Point | Nevada, Placer | Grass Valley, CA
Nevada County Health & Human Services | Nevada | Truckee, CA
Portola Family Resource Center | Plumas | Portola, CA
Plumas County Mental Health | Plumas | Portola, CA
Eastern Plumas Healthcare | Plumas | Portola, CA
Partnership HealthPlan of CA | Plumas | Fairfield, CA
Loyalton Senior Citizens of Sierra Co. | Sierra | Loyalton, CA
Sierra County Health and Human Services | Sierra | Loyalton, CA
Sierra County Public Health | Sierra | Loyalton, CA
Loyalton Family Resource Center | Sierra | Loyalton, CA
Boys and Girls Club of Lake Tahoe | El Dorado | South Lake Tahoe, CA
Live Violence Free | El Dorado | South Lake Tahoe, CA
Tahoe Coalition for the Homeless | El Dorado | South Lake Tahoe, CA
El Dorado Health and Human Services | El Dorado | Placerville, CA
First 5 / Community Hub El Dorado | El Dorado | Placerville, CA
South Lake Tahoe Family Resource Center | El Dorado | South Lake Tahoe, CA
Tahoe Youth and Family Services | El Dorado | South Lake Tahoe, CA
Tahoe Magic | El Dorado | South Lake Tahoe, CA
Bread and Broth | El Dorado | South Lake Tahoe, CA
Catalyst Community | El Dorado | South Lake Tahoe, CA
Rolling Start, Inc. Independent Living Center | Mono | San Bernardino, CA
Mono County Health and Human Services | Mono | Coleville, CA
Mono County Public Health | Mono | Mammoth Lakes, CA
Alpine County Health and Human Services | Alpine | Markleeville, CA
Washoe Tribe | Alpine | Markleeville, CA
Community Services Solutions | Mono | Gardnerville, NV
Tahoe Truckee Helping Hands | Placer | Truckee, CA

## LU Table 11-3
LU Table 11‑3: Community Outreach and Education Programs
Core Activity | Event Type | Period of Application (Before, During, After Incident) | Name of Outreach or Education Program | Description of Program | Target Audience
Digital, print, and radio advertising | Campaign | All | PSPS and Wildfire Mitigation Awareness Advertising | Campaign occurs from May-October of each year, covering PSPS and Wildfire Mitigation awareness topics. | All customers, medical baseline customers
Advertising in HOA publications and customer emails | Email, social media | Before | None | Perform general PSPS and Wildfire Mitigation outreach ahead of fire season. | All customers
Manage outreach /awareness webpage | Virtual | All | Liberty PSPS and Wildfire Mitigation awareness webpage | Social media posts, bill inserts, and customer emails help drive traffic to webpage that covers PSPS and wildfire mitigation awareness topics. | All customers
General Community Outreach Events | In-Person | Before | None | Liberty attendance at community outreach events to spread PSPS awareness and preparedness education, update contact information, and provide education on available customer programs and Liberty notification system. | All customers
Community Based Organization (“CBO”) Meetings | In-Person, Virtual | Before | None | Liberty staff meetings with local CBOs to share PSPS awareness and available materials, preparedness education, customer program updates, and to maintain up to date contract information for CBO facing communities. | CBOs, AFN customers
Collaborative Community Outreach with CBOs | In-Person | Before | None | Liberty involvement in collaborative outreach events to spread PSPS awareness and preparedness education, update contact information, and provide education on available customer programs and Liberty notification system. This form of outreach leverages CBO relationships within the community to access local communities and supports targeted outreach efforts to reach AFN populations. | All customers, AFN customers, CBOs
Provision of Shelf-Stable Meal Boxes to Senior Nutrition Programs | In-Person | Before | Shelf Stable Meal Box Delivery | Provide preparedness information, customer assistance program information and shelf stable food items to vulnerable seniors. | All customers

## Table 11-11
Table 11‑11: Gaps and Limitations in Public Emergency Communication Strategy
Gap or Limitation Subject | Remedial Brief Description | Remedial Action Plan
During 2024 PSPS events, some customers were notified as being in scope for events but were not de-energized and did not receive notices of cancellation. | Liberty should update its protocols an in-event tracking spreadsheet to make sure customers that are notified, but not, de-energized receive cancellation notices. | Strategy: Liberty will update its in-event tracker to specifically capture cancellation notifications. Target Timeline: Completed
2024 PSPS events highlighted the need to update Liberty’s MBL customer contact list, as some members of the list had recently passed away. | Liberty should do an internal review of its MBL customer list. | Target Timeline: Completed
Liberty’s 2025 PSPS event highlighted the need for additional signage outside CRC locations | Liberty should place external signage outside CRC locations during future PSPS events | Strategy: Liberty will work with their CRC contractor to implement signage placement during future events Target Timeline: Implementation in 2026
Liberty’s 2025 PSPS event identified the need for estimated time of restoration to be included on all notifications during event, including CRC services available and where to access electricity during the hours the CRC is closed on customer notifications | Liberty will adapt its notification templates to include the requested information | Strategy: Liberty will adapt its notification templates to include the requested information Target Timeline: Completed

## Table 12-1
Table 12‑1: Enterprise System Targets
WMP Initiative | Activity (Tracking ID#) | 2026 End-of-Year Total / Completion Date | 2027 Total / Status | 2028 Total / Status | Section; Page Number
Enterprise System – Vegetation Management | Vegetation Data Quality Management (WMP-VM-ESG-01) | Started: March 2026 | In Progress | Complete by December 31, 2028 | 12.1.1; pp. 339-340
Enterprise System – Asset Management and Inspection | Asset Management Inspection Application Reduction (WMP-GDOM-GO-05) | Started: March 2026 | In Progress | Complete by December 31, 2028 | 12.1.1; pp. 339-340

## Table 13-1
Table 13‑1: WMP Lessons Learned
ID # | Year of Lesson Learned | Subject | Category and Source of Lesson Learned | Description of Lesson Learned | Proposed WMP Improvement | Timeline for Implementation | Reference
1 | 2023-2024 | Grid Hardening | Feedback from government agencies | Permitting projects with multiple agencies can cause project delays. Delays can be due to lack of resources by permitting agencies to respond to requests within expected timelines and other projects within the same area may create need for additional collaboration. | Work with contractors familiar with permitting agency process and requirements. | Ongoing | 8.2; pp. 155-174
2 | 2024-2025 | Vegetation Management | QA/QC | In the 2023-2025 WMP Liberty determined pass rate targets for all conditions being evaluated in each QC program component. Liberty determined it is more beneficial to assess an overall pass rate for each of its QC program components to evaluate program effectiveness. Liberty still reviews QC failures for each condition being evaluated in each QC program component. However, Liberty measures overall work quality by looking at the overall pass rate, an average of all conditions evaluated. | Liberty is updating QC targets as detailed in its 2027 WMP, Section 9.11, Table 9-19 Vegetation Management QA and QC Activity Targets | Completed 2025 | 9.11; pp. 244-254
3 | 2025 | Vegetation Management | Fuel Management | Leverage joint IOU partnerships for potential of shared biomass utilization projects. | Liberty will continue to collaborate with neighboring utilities to explore opportunities for alternative biomass utilization, as well as other industry-specific benchmarking. | Completed 2025 | 9.3-9.7; pp. 225-235
4 | 2025 | Vegetation Management | Key Performance Indicators | Liberty identified the need to regularly track and report contractor key performance indicators (KPI) to monitor contractor production metrics. | Liberty developed KPI reporting to set targets to measure production against for its VM contractors. | Completed 2025 | 12; pp. 339-345
5 | 2025 | Vegetation Management | Contractor Safety | Liberty identified opportunities to continue enhancing safety oversite of contractor work. | Liberty has implemented routine safety observations of VM contractors and worked with its primary tree contractor to implement an updated job tailboard form to include a more detailed roping and rigging plan for tree work. | Completed 2025 | 9; pp. 213-262
6 | 2024 | Grid Design, Operations, and Maintenance | Collaboration efforts with other electrical corporations | NV Energy's new wildfire encroachment policy, if implemented on the 619 line, would lead to loss of power supply to all customers in Portola and Loyalton. | Plumas-Sierra Rural Electrical Cooperative could provide an alternate power supply to Portola and Loyalton. | Completed 2024 | 8; pp. 150-212
7 | 2024 | PSPS | 2024 PSPS Events | Refer to Table 7‑1. | Refer to Table 7‑1. | Ongoing | 7; pp. 145-149
8 | 2020-2024 | Risk Modeling | Risk Modeling Working Group | Liberty has gained a greater understanding of best practices across the CA IOUs regarding the following topics: • Modeling baselines • Fire consequence • Asset risk events and ignitions • Vegetation risk events and ignitions • PSPS likelihood • PSPS consequence and reliability analysis and impacts • Modeling algorithms, components, and interdependencies • Smoke and suppression impacts • Climate change impacts | Liberty will continue to participate in the Joint IOU Wildfire Risk Modeling Working Group to understand best practices across the California IOUs (i.e., further integration of community vulnerability, improvements to wildfire consequence modeling). | Ongoing | 5; pp. 35-108
9 | 2022 | Data tracking | Feedback from stakeholders; outcomes from previous WMP cycles | Liberty was lacking data quality for tracking and reporting WMP initiatives. | Refer to Section 12. | Completed 2024 | 12; pp. 339-345
10 | 2024 | Emergency Preparedness, Collaboration, and Public Awareness | Feedback from government agencies and stakeholders; outcomes from previous WMP cycles. | Liberty was lacking MBL specific door hangers for communication of critical information during PSPS events. | MBL specific letter to be used as part of the PSPS notification process to leave at customers' houses after exhausting other attempts to notify via text, phone, or other means. | Completed 2024 | 11; pp. 292-339
11 | 2024 | Emergency Preparedness, Collaboration, and Public Awareness | Feedback from government agencies and stakeholders | Some customers do not understand why PSPS may occur | Provide additional educational materials to Public Safety Partners for them to share through their community outreach channels. | Completed 2024 | 11; pp. 292-339
12 | 2026 | Risk model internal review processes | Energy Safety decision on the 2026-2028 Base WMP | Liberty’s risk model validation reporting and internal review processes were vague and lacked the detail necessary for progress tracking. | Establish an internal Risk Focus Group to provide governance for risk model development and validation. | Completed May 7, 2026 | 5.6.1; pp. 96-101
13 | 2026 | Risk model development | Energy Safety decision on the 2026-2028 Base WMP | Liberty relied heavily on outside consultants for the development of its risk model leading to a lack of internal subject matter expertise. | Hire a Lead Risk Analyst to drive risk model development and continuous improvement | Completed June 22, 2026 | 5.1.1; pp. 35-37
14 | 2026 | Mitigation strategy development | Energy Safety decision on the 2026-2028 Base WMP | The wildfire mitigation strategy must be risk informed and supported by an accurate assessment of mitigation effectiveness to effectively plan and prioritize WMP projects. | Improve risk mitigation strategy development by incorporating accurate cost benefit analysis and mitigation effectiveness to support risk informed decision making. | Initial model version completed July 23, 2026; additional improvements are outlined in the Risk Assessment Improvement Plan | 6; pp. 109-144 5.7; pp. 103-108

## Table 13-2
Table 13‑2: Lessons Learned from Discontinued Activities
Discontinued Activity (Tracking ID) | Rationale for Discontinuation | Lessons Learned | Replacement Activities
Substation Equipment Replacement (WMP-GDOM-GH-12f) | The activity, as previously described, encompassed general substation equipment replacements and upgrades—many of which were not directly tied to wildfire ignition risk. Furthermore, feedback from both internal reviews and Energy Safety emphasized that the initiative lacked clearly defined objectives and measurable outcomes specific to wildfire prevention | 1) Clarity and Risk Relevance Are Essential: Initiative activities must be clearly defined and directly tied to measurable wildfire risk reduction to be meaningful and auditable. 2) Program Discipline: Ongoing feedback loops with Energy Safety and operational teams are critical to see that WMP initiatives remain aligned with their intended purpose and are responsive to actual risk | The underlying work, such as substation inspections and emergency equipment replacements, continues as part of routine utility operations and capital upgrade programs. While the discontinued initiative will no longer be tracked under a separate WMP initiative, risk mitigation previously attributed to this initiative is now supported through the following ongoing activities and WMP initiatives: Substation Inspections (WMP-GDOM-AI-06) and Substation Defensible Space (WMP-VM-VFM-03)