## Data Request Log
LOG BEGINS SEPTEMBER 3, 2026
Liberty 2027 Base WMP Discovery Log
Last Updated: | 9/17/2026 at 12:00PM
Count | Party Name | DR Set # | Data Request | Question No. | Question ID | Question | Responses | Requestor | Date Received | Final Date Due | Date Sent | Links | Number of Attachments | Attachment Links | NDA Required? | WMP Section | Category | Subcategory
1 | OEIS | 1 | OEIS-P-WMP_2026-Liberty-001 | 1 | OEIS-001-Q01 | Q01. Regarding ESRI’s Utility Network Rules: On page 343 of Liberty’s 2027 Base WMP R0,1 Liberty stated that, as a result of ESRI’s Utility Network deployment, Liberty set rules to promote consistency in its GIS data, and the rules must be satisfied for the utility network to function as designed and will prevent its users from editing the utility subnetworks until all criteria are met. a. Describe the specific mechanism (e.g., software triggers, automated security checks, error-handling workflows) of the rules and criteria within Liberty’s ESRI Utility Network that prevent its users from updating the utility subnetworks until all criteria are fully satisfied. b. Provide specific examples of those rules and criteria. | a. ESRI’s Utility Network uses a combination of network rules, validation processes, dirty-area tracking, and user permissions to maintain consistency in the GIS data. The network rules define which features can connect, associate, or participate in a utility network. When a user creates or modifies a feature, the Utility Network evaluates the change against the applicable rules. If the change violates a rule or creates an invalid network condition, the system identifies the affected area as a “dirty area” and generates a validation error. The network cannot be considered fully validated until the applicable errors have been corrected and the dirty areas have been validated. For Liberty’s electric Utility Network, access to make changes is also controlled through GIS roles and permissions. Authorized GIS personnel may make edits, typically within a version separate from the default version. The changes can then be validated and reviewed for errors. Once the edits satisfy the applicable Utility Network rules and validation requirements, the version can be posted or reconciled to the default version, which represents the current network used by the broader enterprise. This process provides an additional quality-control mechanism because invalid or incomplete edits should not be incorporated into the authoritative network without being reviewed and validated. The Utility Network does not only rely on users to determine whether an edit is correct. The configured rules act as automated validation checks, while dirty areas and validation errors identify edits that require correction. Combined with GIS permissions and the versioning workflow, these controls help prevent unvalidated changes from becoming part of Liberty’s authoritative electric utility network. b. Examples of rules and criteria that may be applied within an electric Utility Network include: • Connectivity rules: Electrical features must connect to compatible network features. For example, a conductor must connect to an appropriate electrical device, structure, or other conductor at a valid connection point. The system can identify an invalid connection when features that are not permitted to connect are placed together.. • Device-to-device connectivity: Certain electrical devices can only connect to other devices or conductors through permitted connection types. For example, a transformer may be permitted to connect to conductors on its primary and secondary sides, while an incompatible device or feature type would produce a validation error. • Terminal rules: Devices that have multiple terminals must have connections made to the appropriate terminal. For example, an electrical transformer or switch may have designated terminals, and a conductor connected to the wrong terminal can create a network validation error. • Containment rules: Some features are modeled as containing other network features. For example, electrical equipment or an enclosure may contain certain devices or components. A feature that is placed inside a container when that feature type is not permitted to be contained there would violate the Utility Network rules. • Structural attachment rules: Certain electrical assets can be attached to structures, such as poles. For example, a transformer, switch, or other piece of electrical equipment may be permitted to attach to a utility pole, while an unrelated feature type may not be permitted to have that structural attachment. • Association rules: The Utility Network can require specific associations between features that are related but do not necessarily share physical geometric connectivity. For example, an electrical device may be associated with a structure or enclosure even when the device and structure are modeled as separate features. • Subnetwork rules and validation: Electric subnetworks must satisfy the applicable connectivity and network-configuration requirements before they can be successfully validated and updated. If a network feature is disconnected, incorrectly connected, or otherwise violates the configured rules, the affected area can remain marked as dirty until the underlying problem is corrected and the network is revalidated. | Jessica McHale | 2026-09-04 | 2026-09-10 | 2026-09-10 | LU Response to DR No. OEIS-P-WMP_2026-Liberty-001.pdf | 0 | - | No | 12 | Enterprise Systems | -
1 | OEIS | 1 | OEIS-P-WMP_2026-Liberty-001 | 2 | OEIS-001-Q02 | Q02. Regarding CSV Tabular Export to GIS Database: On page 343 of Liberty’s 2027 Base WMP R0, Liberty stated that as part of its data flow path, data transformations are made in SQL and tabular data is exported in CSV format. The GIS department converts these into feature classes stored in geodatabases for use in Liberty’s GIS enterprise database. a. Is it feasible for Liberty to replace its current intermediate CSV tabular export process with direct database-to-database (db2db) Extract-Transformation-Load (ETL)? i. If feasible, provide details and timelines of the direct db2db ETL implementation. 1. If feasible, but Liberty does not plan to implement db2db, explain why. ii. If not feasible, explain how Liberty controls potential operational errors and synchronization delays from the CSV tabular export step. | Based on the data flow described on page 343 of Liberty’s 2027 Base WMP R0, it is technically feasible to replace the intermediate CSV export with a direct database-to-database (DB2DB) Extract-Transformation-Load (ETL) process. i. The primary technical requirements for implementation would be establishing connectivity between the source and destination databases, replicating the existing SQL transformations and field mappings, ensuring that the required point geometry and attributes are correctly generated, and testing the resulting feature classes against the specifications of OEIS. None of these requirements inherently requires an intermediate CSV file. 1. While this approach is feasible, Liberty does not plan to implement DB2DB for the following reasons: • The CSV-to-geodatabase process is straightforward and repeatable. The existing process provides a consistent and efficient method for converting CSV data into feature classes without introducing unnecessary complexity. • Schema changes are more easily managed within the GIS environment. Any modifications required to the feature-class schema can be implemented more efficiently and transparently within the GIS, rather than requiring changes to the SQL-based application. • The risk of data corruption or unintended changes during conversion is minimal. The CSV-to-feature-class conversion process is well established, and GIS specialists review the resulting feature classes to verify that the data has been converted accurately and that no unintended changes have occurred. • The capacity to design and maintain an SQL-based ETL process has not yet been established. The level of SQL and GIS expertise required to develop, implement, and maintain the proposed ETL process is currently undetermined. Implementing DB2DB could therefore introduce additional development and maintenance requirements without a demonstrated benefit over the existing workflow. | Jessica McHale | 2026-09-04 | 2026-09-10 | 2026-09-10 | LU Response to DR No. OEIS-P-WMP_2026-Liberty-001.pdf | 0 | - | No | 12 | Enterprise Systems | -
1 | OEIS | 1 | OEIS-P-WMP_2026-Liberty-001 | 3 | OEIS-001-Q03 | Q03. Regarding Field Data Collection Training: On page 344 of Liberty’s 2027 Base WMP R0, Liberty stated that accuracy of compliance data is accomplished through consistent training of data collectors and that data analysts, system arborists, and electrical foreman are heavily involved in training inspectors, contractors, and other groups that are tasked with data collection. a. Describe Liberty’s training program provided to its personnel and contractors responsible for data collection. b. Explain how data analysts, system arborists, and electrical foreman conduct oversight and train the field data collectors to ensure accuracy of the self-policing in raw data collection prior to in-house Data Quality Management (DQM). | a. Liberty trains all internal staff and contractors performing inspection and maintenance activities on the system on data collection requirements. Workers are trained regularly on the data collection application Fulcrum based on the projects they are working on (G.O. Inspections, Repairs, WMP work, QAQC, etc.). Each project has a unique workflow with data governance and standard procedures. Trainings are performed in person before the start of each project. Afterwards, the training documentation is uploaded to Fulcrum’s Reference Files in the application, which can be downloaded by field crews as necessary. Additional trainings are completed at a monthly cadence or ad hoc when relevant updates are made to the data collection application. b. Data Analysts conduct the Fulcrum training and monitor data coming in during all steps of the data collection and reporting process. Asset Tracking, the inspection and maintenance Fulcrum application, uses code to trigger data review events, which are performed by the Data Analysts. Electrical Foremen work with data analysts to create training materials and conduct training seminars. Foremen also conduct peer to peer training on data collection, related to projects that field crews are working on. Liberty documents vegetation management data collection requirements through its plans, processes, procedures, contractor specifications, and scopes of work. Liberty’s vegetation management contractors provide training to their employees on the functionality of work management software and associated data collection requirements. Liberty works directly with its contractors to provide training on updates to work management software layers or configurations and data collection requirements on an as needed basis. Liberty's System Arborists provide oversight of vegetation management contractors and field data collectors to promote accurate and consistent data collection. System Arborists conduct periodic data quality reviews, field observations, and targeted checks of contractor-collected data to verify that inventories, work prescriptions, and completed work records are entered correctly. Additionally, data quality issues identified through standard QA/QC processes are communicated to contractors and are assigned for corrective action. To support ongoing data quality improvement, Liberty's Vegetation Management team and data analysts hold monthly meetings to review vegetation management dashboards, verify data accuracy, discuss data quality issues, and develop tracking tools. In addition, Liberty conducts monthly contractor meetings to review work progress, address quality concerns, and reinforce data collection and documentation expectations. This continuous oversight and feedback process helps improve the accuracy of raw data collection prior to in-house Data Quality Management (DQM) review. | Jessica McHale | 2026-09-04 | 2026-09-10 | 2026-09-10 | LU Response to DR No. OEIS-P-WMP_2026-Liberty-001.pdf | 0 | - | No | 12 | Enterprise Systems | -
1 | OEIS | 1 | OEIS-P-WMP_2026-Liberty-001 | 4 | OEIS-001-Q04 | Q04. Regarding Asset Identification Process: On page 342 of Liberty’s 2027 Base WMP R0, Liberty stated, to achieve 100 percent asset identification, it relies on a 5-year detailed asset inspection cycle by reconciling as-builts data against actual field data after assets are installed in the field. a. Explain the procedures Liberty uses to identify and correct any unrecorded field updates or asset discrepancies during the interim 5-year window. i. Explain how Liberty prevents unverified interim asset data from contaminating risk models prior to the full 5-year inspection reconciliation. | a. Liberty examines detailed inspection records in Fulcrum to identify any discrepancies in the GIS database that occurred during the drawing in of as-builts. GIS data will then be updated based on the more up to date data recorded in the field. Yearly LiDAR data is also used to reconcile GIS data by displaying the most up to date location of assets in the field. i. Liberty’s current risk model operates at the circuit-level based on the verified locations of overhead distribution and transmission circuits. Liberty has not developed an asset-level risk model that estimates specific failure probabilities down to individual system components (e.g., fuses, tree attachments). | Jessica McHale | 2026-09-04 | 2026-09-10 | 2026-09-10 | LU Response to DR No. OEIS-P-WMP_2026-Liberty-001.pdf | 0 | - | No | 12 | Enterprise Systems | -
1 | OEIS | 1 | OEIS-P-WMP_2026-Liberty-001 | 5 | OEIS-001-Q05 | Q05. Regarding Data Retention and Disposal Policy: On page 343 of Liberty’s 2027 Base WMP R0, Liberty stated it is required to maintain inspection data over a ten-year period. However, it stated that there is currently no determination for when a cutoff period will be put in place for disposal of its historical data and that, as it reaches the ten-year mark, it will create a plan to evaluate retention / disposal rate of historical data. a. State the exact year and quarter Liberty projects it will accumulate ten continuous years of historical inspection data. b. Given that Liberty’s formal data disposal policy will not be created until the ten-year mark is reached, explain how Liberty ensures compliance with retention mandates without performance degradation due to database bloat, or any data governance vulnerabilities in the interim. | a. Liberty projects that it will accumulate ten continuous years of historical inspection data by the end of Q4 2029. b. Liberty maintains a SQL Server database for its assets and their inspection and maintenance records. The database holds roughly 2 gigabytes of character and numeric data from G.O. inspections and maintenance work dating back to 2020, including quarterly archives of SQL Views. Photos are stored in Fulcrum’s database, as well as a Liberty hosted SharePoint site, for certain projects. Liberty’s current plan allows for 500 gigabytes of storage in Fulcrum’s database, of which roughly 175 gigabytes are accounted for. Due to Liberty’s ETL process, the use of Fulcrum’s database for storage, and the relatively small number of assets under management compared to larger ECs, database bloat, and the resulting performance degradation, is not a concern for retaining 10 years of historical data. | Jessica McHale | 2026-09-04 | 2026-09-10 | 2026-09-10 | LU Response to DR No. OEIS-P-WMP_2026-Liberty-001.pdf | 0 | - | No | 12 | Enterprise Systems | -
1 | OEIS | 1 | OEIS-P-WMP_2026-Liberty-001 | 6 | OEIS-001-Q06 | Q06. Regarding Employing a Registered Professional Forester: On page 244 of its 2023-2025 Base WMP R0, Liberty indicated that it employed a Registered Professional Forester. In Section 9.13 Workforce Planning of its 2027 Base WMP R0 (pages 257-262), it is not clear whether Liberty currently employs or contracts a Registered Professional Forester. a. Does Liberty employ, internally or contracted, a Registered Professional Forester? i. If yes, identify the Worker Title(s) in Table 9-9 of Liberty’s 2027 Base WMP R0 that currently holds a Registered Professional Forester license. ii. If Liberty does not employ or contract with a Registered Professional Forester, explain why it does not. | a. Liberty currently contracts with one Registered Professional Forester (RPF). i. This individual is represented under the Utility Forester V worker title in Table 9-9 of Liberty's 2027 Base WMP. The reference in the 2023-2025 Base WMP indicating that Liberty employed one RPF reflected the qualifications of Liberty's internal Vegetation Management staff at that time. Specifically, Table 8-32 identified one internal employee holding an RPF license. That employee is no longer employed by Liberty. As shown in Table 9-23 of the 2027 Base WMP, Liberty does not currently employ an internal Vegetation Management employee who holds an RPF license. However, Liberty does employ one individual who is a Society of American Foresters (SAF) Certified Forester. While this certification demonstrates professional forestry expertise, it is distinct from and does not constitute a California Registered Professional Forester license. | Jessica McHale | 2026-09-04 | 2026-09-10 | 2026-09-10 | LU Response to DR No. OEIS-P-WMP_2026-Liberty-001.pdf | 0 | - | No | 9 | Vegetation Management and Inspections | Post-Fire Service Restoration
1 | OEIS | 1 | OEIS-P-WMP_2026-Liberty-001 | 7 | OEIS-001-Q07 | Q07. Regarding Maintenance of Fire-Resilient Rights-of-Way: On page 193 of its 2026-2028 Base WMP R1 (Clean), Liberty indicated it “is developing a Right-of-Way Management Plan as a part of its IVM [Integrated Vegetation Management] Program.” However, in its 2027 Base WMP R0, Liberty did not state it was developing a Right-of-Way Management Plan. a. Has Liberty developed or is Liberty developing a Right-of-Way Management Plan? i. If Liberty has developed a Right-of-Way Management Plan, provide the plan. ii. If Liberty is in the process of developing a Right-of-Way Management Plan, specify: 1. When Liberty will complete the plan. 2. The purpose of the plan. iii. If Liberty has not developed or is not developing a Right-of-Way Management Plan, describe how it will ensure ongoing maintenance of the fire-resilient rights-of-way it has established. | a. Currently, Liberty is not developing a Right-of-Way Management Plan. i. N/A ii. N/A iii. While Liberty is currently not developing a standalone Right-of-Way Management Plan, it maintains fire-resilient rights-of-way through its established vegetation management, inspection, maintenance, and wildfire mitigation programs, which collectively ensure ongoing monitoring and upkeep of these corridors. Liberty is continue advancing fire-resilient right-of-way objectives through operational program implementation. This includes continued implementation of Forest Resilience Corridors, completing planned Zone 1 and Zone 2 treatments, and prioritizing future Zone 3 treatments. Because a significant portion of this work occurs on U.S. Forest Service lands, Liberty intends to continue coordinating with the U.S. Forest Service to develop and implement appropriate fuel reduction and maintenance strategies within and adjacent to utility rights-of-way. Liberty’s vegetation management personnel receive annual training on Integrated Vegetation Management principles, compatible vegetation management, and fire-resilient right-of-way practices. This training supports consistent application of vegetation management strategies for the ongoing maintenance of fire-resilient rights-of-way post treatment. Following completion of fire-resilient right-of-way and Forest Resilience Corridor projects, Liberty maintains established corridor conditions through its existing Vegetation Management Program. During routine maintenance cycles, Liberty removes newly established incompatible woody vegetation within treated rights-of-way, promotes the continued development of compatible vegetation cover, and performs ongoing inspections and maintenance activities to identify vegetation conditions that may warrant corrective action. Additionally, maintenance may be achieved through Liberty’s Fuel Management Program and collaborative projects with local land managers. For example, Liberty is currently working with the Tahoe National Forest and National Forest Foundation on the Big Jack East WUI Maintenance Project. The project includes maintenance activities along approximately 1.7 miles of 120 kV transmission lines across 46 structures and more than 470 acres which were originally treated in 2021. This project is an example of Liberty's collaborative approach to maintaining treated forest conditions, including vegetation within and adjacent to the powerline right-of-way. | Jessica McHale | 2026-09-04 | 2026-09-10 | 2026-09-10 | LU Response to DR No. OEIS-P-WMP_2026-Liberty-001.pdf | 0 | - | No | 8 | Grid Design, Operatoins, and Maintenance | Quality Assurance and Quality Control
1 | OEIS | 1 | OEIS-P-WMP_2026-Liberty-001 | 8 | OEIS-001-Q08 | Q08. Substation Inspection Scheduling: On page 232 of its 2027 Base WMP R0, Liberty states “A minimum of 12 substation inspections will occur each year. Generally, two site visits will occur per facility per year.” a. Does Liberty intend to inspect each individual substation facility at least once per year? b. What conditions would force Liberty not to conduct two inspections of a substation facility in a given year? c. In the past 5 years, how many times has Liberty inspected a substation facility only once during a calendar year? d. In the past 5 years, how many times has Liberty failed to inspect a substation facility during a calendar year? e. Provide substation inspection records for the past 5 years. | a. Yes. Liberty intends to inspect each substation under its Substation Defensible Space (WMP-VM-VFM-03) initiative at least once per year to identify vegetation management work requirements, including vegetation and debris removal within and adjacent to the substation perimeter. b. Conditions that may prevent Liberty from conducting two inspections of a substation within a calendar year include severe weather conditions (such as early snowfall that limits site access) and significant substation construction or rebuilding activities that restrict access or render routine vegetation management inspections unnecessary during the construction period. c. Refer to table “Substation Defensible Space (WMP-VM-VFM-03) Inspections.” (see link to DR, column M) d. Refer to table “Substation Defensible Space (WMP-VM-VFM-03) Inspections.” (see link to DR, column M) e. See files: “Substation Defensible Space (WMP-VM-VFM-03) Inspections 2022-2026.pdf” and “Substation Defensible Space (WMP-VM-VFM-03) Inspections 2022-2026.xlsx”. | Jessica McHale | 2026-09-04 | 2026-09-10 | 2026-09-10 | LU Response to DR No. OEIS-P-WMP_2026-Liberty-001.pdf | 2 | https://california.libertyutilities.com/uploads/WMP%20Data%20Requests/2022-2026-Chemical-Use-Report-Subsation.zip https://california.libertyutilities.com/uploads/WMP%20Data%20Requests/Substation%20Defensible%20Space%20Inspections%202022-2026.zip | No | 9 | Vegetation Management and Inspections | Defensible Space
2 | OEIS | 2 | OEIS-P-WMP_2026-Liberty-002 | 1 | OEIS-002-Q01 | Q01. Regarding Liberty’s 2027 Pole Clearing Target: On page 215 of its 2027 Base WMP R0, 1 Liberty indicated that it will clear 4,500 poles pursuantto Public Resources Code section 4292 (PRC 4292). On page 163 of its 2026-2028 Base WMP R1 (Clean), 2 Liberty also indicated it would clear 4,500 poles pursuant to PRC 4292. a. List the number of poles and towers subject to PRC 4292 in Liberty’s service territory. i. If this number is different than 4,500, explain why. b. Does Liberty anticipate the number of pole and towers subject to PRC 4292 will change in 2027? i. If yes, by how much will the number increase or decrease? c. List and describe the factors Liberty considers when deciding whether to install nonexempt or exempt equipment (e.g., cost, resource availability). | a. Liberty’s current inventory includes 4,521 poles subject to PRC 4292. i. Liberty established its target of 4,500 poles requiring clearing for PRC 4292 to reflect normal changes to Liberty’s asset inventory resulting from infrastructure upgrades, pole replacements, new construction, and ongoing asset management activities. For planning and reporting purposes, Liberty rounded the annual work target to 4,500. b. Yes. Liberty anticipates that the number of poles subject to PRC 4292 may change over time due to system modifications, including pole replacements, line extensions, system hardening projects, new business, and other infrastructure upgrades. i. Liberty is currently in the process of reviewing and evaluating the number of newly identified poles that may be subject to PRC 4292 requirements. This includes verification of newly identified subject poles, review of poles classified as exempt or supporting no equipment identified during pole-clearing inspections, evaluation of QAQC findings, general data governance and review, and asset data conflation. While this evaluation remains ongoing, Liberty preliminarily estimates that the poles subject to PRC 4292 may increase by approximately 4% (about 180 poles). Liberty will continue to refine the future pole clearing inventory as validation activities are completed. c. Liberty's standard practice is to install exempt equipment wherever an approved exempt alternative exists within Liberty's engineering standards. Non-exempt equipment is installed only where no approved exempt alternative can meet the functional requirements of the application while maintaining compliance with Liberty's construction and safety standards. | Jessica McHale | 2026-09-11 | 2026-09-16 | 2026-09-16 | Liberty Response to DR No. OEIS-P-WMP_2026-Liberty-002.pdf | 0 | - | No | 9 | Vegetation Management and Inspections | Quantitative Targets
2 | OEIS | 2 | OEIS-P-WMP_2026-Liberty-002 | 2 | OEIS-002-Q02 | Q02. Regarding Liberty’s Historical Outage Data: On page 36 of its 2027 Base WMP, Liberty states that it is using “four years of Liberty’s historical outage data to estimate the likelihood of an outage on each feeder.” a. Why is Liberty only using the past four years within its risk methodology data set? b. How many outages has Liberty recorded in the past four years? c. What actions has Liberty taken to expand upon its outage data set? | a. Liberty is using the past four years in its risk methodology data set because Liberty focused its analysis of historical outages to the date range of its updated outage management system. See response to (c) for a discussion of integrating outage records from Liberty’s previous outage management system. b. The initial dataset of outage records 3,473 outages. See Technical Appendix B (section “Outage and Ignition Data Methodology”). c. Liberty is investigating outage records back to 2018, pre-dating the change of outage management systems. Geo-referencing and pinpointing the coordinates of these outage records takes additional analytical work to match records to locations using address information or asset ID information. In addition, mapping these records to risk drivers and risk sub-drivers requires different logic than the current analytical workstream. A key benefit of a larger dataset of outage records is improved training and precision of the probability of failure model. | Jessica McHale | 2026-09-11 | 2026-09-16 | 2026-09-16 | Liberty Response to DR No. OEIS-P-WMP_2026-Liberty-002.pdf | 0 | - | No | 5 | Risk Methodology and Assessment | Overview
2 | OEIS | 2 | OEIS-P-WMP_2026-Liberty-002 | 3 | OEIS-002-Q03 | Q03. Regarding Table 6-4: Summary of Risk Reduction for Top Circuits: a. Provide a version of Table 6-4 (pp. 141-142) via Excel with the following additional columns: i. Overall Utility Risk Reduction from PSPS ($) ii. Overall Utility Risk Reduction from SRP ($) iii. Overall 2027 Utility Risk Reduction from Grid Hardening ($) iv. Overall 2027 Utility Risk Reduction from Covered Conductor ($) v. Overall 2027 Utility Risk Reduction from Pole Replacement ($) b. In Table 6-4, “Detailed inspections” is only listed as a 2027 activity for circuit MEY34000 (p. 141). i. Do any other circuits have detailed inspections planned for 2027? ii. Are there any other types of inspections planned in 2027 for the circuits in Table 6-4? iii. If yes to either or both (i) and (ii), provide a corrected version of Table 6-4 to reflect which circuits have detailed and additional inspections planned for 2027. | a. See attachment “DR-002-Q03.a.Table 6-4 Risk reduction by mitigation.xlsx.” b. i. Yes, see attachment “DR-002-Q03.b Table 6-4 Circuit List Planned Inspections.xlsx.” ii. Yes, see attachment “DR-002-Q03.b Table 6-4 Circuit List Planned Inspections.xlsx.” iii. See attachment “DR-002-Q03.b Table 6-4 Circuit List Planned Inspections.xlsx.” | Jessica McHale | 2026-09-11 | 2026-09-16 | 2026-09-16 | Liberty Response to DR No. OEIS-P-WMP_2026-Liberty-002.pdf | 2 | https://view.officeapps.live.com/op/view.aspx?src=https%3A%2F%2Fcalifornia.libertyutilities.com%2Fuploads%2FDR-002-Q03.a.%2520Table%25206-4%2520Risk%2520reduction%2520by%2520mitigation.xlsx&wdOrigin=BROWSELINK https://view.officeapps.live.com/op/view.aspx?src=https%3A%2F%2Fcalifornia.libertyutilities.com%2Fuploads%2FDR-002-Q03.b.%2520Table%25206-4%2520Circuit%2520List%2520Planned%2520Inspections.xlsx&wdOrigin=BROWSELINK | No | 6 | Wildfire Mitigation Strategy Development | Projected Risk Reduction on Highest-Risk Circuits in 2027
2 | OEIS | 2 | OEIS-P-WMP_2026-Liberty-002 | 4 | OEIS-002-Q04 | Q04. Regarding Table 5-5: Liberty Top-Risk Circuits: a. In Table 5-5, circuits TAH5201, TAH7300, and KBH5200 each have an outage program risk score that is over 40% of the overall utility risk score, at 42.9%, 51.0%, and 42.7% respectively. i. Provide an explanation for the relatively high outage program risk for these circuits. ii. How has the relatively high outage program risk impacted decision-making when determining mitigations for these circuits? b. Circuit 640 has an outage program risk score of 0. i. Provide an explanation for why this circuit has no outage program risk. | a. i. As described in the 2027 WMP, Liberty’s outage program risk is primarily based on PSPS risk. Liberty’s PSPS likelihood module is relatively coarse, projecting these three circuits respectively would experience a PSPS event once every two years. These three circuits face high outage program risk shares because they are relatively long circuits serving many residential and commercial customers across Tahoe City, the west shore of Lake Tahoe, and Dollar Point. In contrast, modeled wildfire risk is relatively low for each of the three circuits, because Technosylva wildfire simulations limit the fire spread potential in these areas. The circuits are immediately adjacent to the lake shore, may receive substantial annual snowfall, and typically see higher fuel moistures than portions of Liberty’s service territory further away from the Sierra Nevada crest. Nevertheless, wildfire risk remains a concern for these three circuits due to factors not currently captured well in Technosylva wildfire consequence outputs, including egress and potential future tree mortality events. ii. At present, Liberty’s risk model prioritizes circuits and mitigation choices based on the sum of wildfire and outage program risk denominated in dollars. The advantage of doing so is that wildfire and outage risk can be expressed in common units, and mitigations that address one or both risk types can be evaluated on a common basis. In other words, Liberty’s current risk model does not uniquely treat circuits with high proportions of outage program risk differently than ones with low proportions of outage program risk. Liberty targets the sum of wildfire and outage program risk. Going forward, as Liberty builds out the capabilities of the risk model to potentially factor in how hardening activities may influence PSPS and SRP decisions, then mitigations that are more effective at addressing outage program risk would likely be favored for TAH7300, TAH5201, and KBH5200. In addition, Liberty is assessing pilot locations for grid monitoring devices (i.e., Gridscope), which provide measurable outage program risk reductions. b. Circuit 640 is a transmission-level circuit. When de-energized, load served by 640 can be met through alternative transmission-level sources. Thus, Liberty’s PSPS risk model assumes no PSPS outage risk is introduced when 640 is proactively de-energized. | Jessica McHale | 2026-09-11 | 2026-09-16 | 2026-09-16 | Liberty Response to DR No. OEIS-P-WMP_2026-Liberty-002.pdf | 0 | - | No | 5 | Risk Methodology and Assessment | Top Risk-Contributing Circuits/Segments/Spans
2 | OEIS | 2 | OEIS-P-WMP_2026-Liberty-002 | 5 | OEIS-002-Q05 | Q05. Regarding WMP Expenditures: a. In Table 3-3 of its 2027 Base WMP, Liberty states that the projected spend on WMP expenditures is $44,924. Liberty does not include expenditures related to mitigation activities included in this WMP, for example, expenditures related to Overhead Hardening with Covered Conductor, in this total. i. List the expenses that are included in this total expenditure. ii. Why are other expenditures related to mitigation activities included in this WMP not included? | a. Energy Safety’s premise to this question is incorrect. Liberty’s stated expenditures in Table 3-3 of Liberty’s 2027 Base WMP do include all expenditures related to mitigation activities in the 2027 WMP. As directed in Energy Safety’s guidelines for Section 3.6, and as specified in Table 3-3 of Liberty’s 2027 Base WMP, Liberty presented its projected expenditures in thousands $USD. Thus, Liberty’s projected 2027 WMP expenditures is $44,924,100 and not $44,924. i. Liberty provides all 2027 WMP expenditures in Table 11 of its annual WMP submission: “Liberty_2027-WMP_R0.” ii. N/A. | Jessica McHale | 2026-09-11 | 2026-09-16 | 2026-09-16 | Liberty Response to DR No. OEIS-P-WMP_2026-Liberty-002.pdf | 0 | - | No | 3 | Overview of Base WMP | Projected Expenditures
2 | OEIS | 2 | OEIS-P-WMP_2026-Liberty-002 | 6 | OEIS-002-Q06 | Q06. Regarding Outage Program Risk: a. On page 41 of its 2027 Base WMP, Liberty states that, “Outage program risk is primarily based on PSPS risk.” i. Explain what factors other than PSPS risk (if any) contribute to Liberty’s outage program risk in Liberty’s current risk modeling methodology. ii. If there are no other factors, confirm that outage program is currently based solely on PSPS risk. | a. i. Liberty’s risk model architecture (2027 WMP Figure 5-1) shows that outage program risk is based on the sum of PSPS risk and PEDS risk denominated in dollars. However, as noted in the figure, Liberty’s PEDS risk model is currently under development. As discussed in 2027 WMP Table 5-6, quantification of PEDS outage program risk is a high-priority item of Liberty’s risk assessment improvement plan. Liberty provided a preliminary estimate of outage program risk associated with Liberty’s SRP program in 2027 WMP Section 5.2.2.2. See the corresponding section for the preliminary estimate and interpretation relative to estimated wildfire and PSPS risk. ii. As discussed in Liberty’s 2027 WMP (see for example, 2027 WMP Sections 5.2.2.2 and 5.2.2.3, 2027 WMP Tables 5-6 and 6-3, and 2027 WMP Appendix D Section 1.1), Liberty’s estimate of outage program risk is based on quantified PSPS risk. As discussed in 2027 WMP Table 5-6, quantification of PEDS outage program risk is a high-priority item of Liberty’s risk assessment improvement plan. | Jessica McHale | 2026-09-11 | 2026-09-16 | 2026-09-16 | Liberty Response to DR No. OEIS-P-WMP_2026-Liberty-002.pdf | 0 | - | No | 5 | Risk Methodology and Assessment | Risk and Risk Component Identification
2 | OEIS | 2 | OEIS-P-WMP_2026-Liberty-002 | 7 | OEIS-002-Q07 | Q07. Regarding IWRMC Survey Results: a. On page 118 of its 2027 Base WMP, Liberty states that it, “calculates maturity adjustments using IWRMC survey results related to PSPS and equipment settings categories. The maturity adjustments are approximately 80% yielding effectiveness parameters for PSPS and SRP of 0.75 and 0.56, respectively.” i. Provide a narrative description of the IWRMC survey. Describe who completed the survey and when it was completed. Provide survey questions and results, as applicable. ii. Provide a narrative description of how Liberty determined the maturity adjustment of 80%. | a. i. The mission of the International Wildfire Risk Mitigation Consortium (IWRMC) is to establish and facilitate a system of working and networking channels between members of the global utility community to support ongoing sharing of data, information, technology, and practices, and proactively address the wildfire issues through learning, innovation, analysis, assessment, and collaboration. The IWRMC is led by a utility executive steering group and consists of member utilities in nineteen states and provinces from the United States, Canada, and Australia. The IWRMC Wildfire Risk Mitigation Maturity Model Survey is a comprehensive self-assessment tool designed to evaluate how effectively an electric utility identifies, manages, and reduces wildfire risk. The survey examines the maturity of the utility’s key capabilities across nine categories: (A) Risk Mapping and Simulation; (B) Situational Awareness and Forecasting; (C) Grid Design and System Hardening; (D) Asset Management and Inspections; (E) Vegetation Management and Inspection; (F) Grid Operations and Protocols; (G) Resource Allocation Methodology; (H) Emergency Planning and Preparedness; and (I) Stakeholder Cooperation and Community Engagement. Within these categories, the survey evaluates the extent to which wildfire risk management practices are formalized, consistently implemented, supported by data and analytical tools, integrated across organizational functions, and subject to review and continuous improvement. Survey results allow participating utilities to evaluate their current capabilities, identify potential areas for improvement, and benchmark their practices against those of other participating utilities. The version of the maturity model used by Liberty was last revised on October 6, 2025, and included survey results from thirty participating companies. Liberty completed the IWRMC Maturity Model survey on December 30, 2025. The survey was completed by Liberty’s internal subject matter experts, with each subject matter expert providing responses for the categories and capabilities for their respective areas of responsibility and technical expertise. Liberty used the resulting scores to inform the maturity adjustments applied to the effectiveness estimates for its PSPS and Sensitive Relay Profile (SRP) mitigations. For the IWRMC Maturity Model survey questions see attachment “DR-002-Q07 IWRMC Maturity Model_ CONFIDENTIAL.xlsx”. The applicable results are provided in attachment “DR-002-Q07 Maturity Model Results_ CONFIDENTIAL.xlsx”. b. To calculate the maturity adjustment, Liberty identified IWMRC survey questions related to (F) Grid Operations and Protocols and (B) Situational Awareness and Forecasting. Within the two categories, Liberty identified survey questions that specifically related to Liberty’s PSPS program, SRP program, and weather forecasting capabilities. Using the survey responses, Liberty calculated average scores for PSPS and SRP programs, and Liberty used the average scores to derive the maturity-adjusted mitigation effectiveness values for PSPS and SRP. While the survey responses provide a quantitative method of estimating maturity, there remains a degree of subjectivity and uncertainty when relying on survey responses to calculate a maturity factor. | Jessica McHale | 2026-09-11 | 2026-09-16 | 2026-09-16 | Liberty Response to DR No. OEIS-P-WMP_2026-Liberty-002.pdf | 2 | - | Yes | 6 | Wildfire Mitigation Strategy Development | Identifying and Evaluating Initiative Activities
2 | OEIS | 2 | OEIS-P-WMP_2026-Liberty-002 | 8 | OEIS-002-Q08 | Q08. Regarding Mitigation Selection Using Risk Model Outputs: a. On page 110 of its 2027 Base WMP, Liberty states, “Overhead hardening with covered conductor and undergrounding are the two key mitigations that Liberty currently evaluates in its benefit-cost analysis.” i. Explain how Liberty currently uses risk model outputs to inform any mitigation activity selection, prioritization, or scheduling other than overhead hardening with covered conductor and undergrounding. | a. i. While Liberty’s current risk model only calculates benefit-cost ratios for overhead hardening with covered conductor and undergrounding, Liberty uses risk model outputs more broadly to inform risk mitigation activities. For example, the risk model informs locations of pilot grid monitoring devices (Gridscope), fuse replacements, and pole replacements. As noted in Liberty’s risk assessment improvement plan (2027 WMP Table 5-6), Liberty is prioritizing benefit-cost ratio quantification for such mitigations (i.e., fuse replacement). | Jessica McHale | 2026-09-11 | 2026-09-16 | 2026-09-16 | Liberty Response to DR No. OEIS-P-WMP_2026-Liberty-002.pdf | 0 | - | No | 6 | Wildfire Mitigation Strategy Development | Approach
3 | OEIS | 3 | OEIS-P-WMP_2026-Liberty-003 | 1 | OEIS-003-Q01 | Q01. Regarding Sensitive Analysis and Parameter Uncertainty: a. On page 121 of its 2027 Base WMP,1 Liberty states that it, “defers quantification of model uncertainty in its current version of the risk model, which would involve alternate specifications of the probability of outage model or the use of other wildfire spread models beyond Technosylva’s provided outputs.” i. Provide a timeframe with key milestones for assessing the uncertainty of Liberty’s risk model. ii. Describe how Liberty considers risk model uncertainty during its risk informed decision-making process. b. On page 121, Liberty also states that it, “can provide examples of parameter uncertainty, which includes inputting alternative mitigation effectiveness or cost parameters and comparing the results to the default parameter choices.” i. Describe how Liberty analyzed the sensitivity of parameters. Provide the sensitivity analysis notes, SME review or calibration notes, meeting notes, and other relevant documentation. ii. Identify any findings from the parameter sensitivity analysis and explain how Liberty considers the sensitivity of parameters during its risk informed decision-making process. |  | Jessica McHale | 2026-09-16 | 2026-09-21 | [5 empty] | 6 | Wildfire Mitigation Strategy Development | Identifying and Evaluating Initiative Activities
3 | OEIS | 3 | OEIS-P-WMP_2026-Liberty-003 | 2 | OEIS-003-Q02 | Q02. Regarding Sub-Driver Effectiveness of Overhead Hardening with Covered Conductor: a. On page 118 of its 2027 Base WMP, Liberty states, “For overhead hardening with covered conductor, Liberty’s mitigation effectiveness parameters ranging from highest to lowest are 0.77 for animal contact, 0.72 for vegetation contact, 0.70 for third-party contact, 0.64 for vehicle contact, and 0.60 for equipment failure.” i. Describe how Liberty determined these sub-driver effectiveness parameters. Provide the SME input or notes, survey responses, meeting notes, and other relevant documentation. |  | Jessica McHale | 2026-09-16 | 2026-09-21 | [5 empty] | 6 | Wildfire Mitigation Strategy Development | Identifying and Evaluating Initiative Activities
3 | OEIS | 3 | OEIS-P-WMP_2026-Liberty-003 | 3 | OEIS-003-Q03 | Q03. Regarding Liberty’s Empirical Effectiveness Estimate of Overhead Hardening Without Covered Conductor: a. On pages 120-121 of its 2027 Base WMP, Liberty explains its methodology for the empirical analysis of overhead hardening without covered conductor. i. Liberty states that it, “leveraged the outage dataset relied upon for training the probability of outage model, which includes outage records for the four-year period 2022-2025.” 1. How many outages are included in this dataset? 2. Explain how Liberty accounted for weather conditions for the outage data in the empirical analysis. |  | Jessica McHale | 2026-09-16 | 2026-09-21 | [5 empty] | 6 | Wildfire Mitigation Strategy Development | Identifying and Evaluating Initiative Activities
3 | OEIS | 3 | OEIS-P-WMP_2026-Liberty-003 | 4 | OEIS-003-Q04 | Q04. Regarding Activity Prioritization Schematic: a. On page 67 of the Energy Safety WMP Guidelines,2 Energy Safety requires electric corporations to provide, “A high-level schematic showing the procedures and evaluation criteria used to evaluate potential activities. At a minimum, the schematic must demonstrate the roles of quantitative risk assessment, resource allocation, evaluation of other plan objectives (e.g., cost, timing) identified by the electrical corporation, and SME judgment. Where specific local factors, which vary across the service territory, are considered in the decision-making process (e.g., the primary risk driver in a region is legacy equipment), they must be indicated in the schematic. The electrical corporation must explain why those local conditions are part of the decision process (i.e., there should not be simply one box in the schematic that is labeled ‘local conditions,’ which is then connected to the rest of the process).” i. Provide the schematic as required by the WMP guidelines. If Liberty cannot produce the schematic at this time, explain why Liberty is unable to produce the schematic and provide a timeline with key milestones for when Liberty will be able to produce the schematic |  | Jessica McHale | 2026-09-16 | 2026-09-21 | [5 empty] | 6 | Wildfire Mitigation Strategy Development | Initiative Activity Prioritization
3 | OEIS | 3 | OEIS-P-WMP_2026-Liberty-003 | 5 | OEIS-003-Q05 | Q05. Regarding Figure 6-3: Waterfall Diagram of Liberty’s Risk Model: a. On page 133 of its 2027 Base WMP, Liberty provides Figure 6-3: Waterfall Diagram of Liberty’s Risk Model. i. Explain how Liberty calculated the 16M risk reduction for Overhead Hardening Mitigation. 1. Identify which Overhead Hardening Mitigation activities were included in this total and which were not. 2. Identify the time range of implementation for the activities included in this risk reduction total. 3. Provide any relevant calculations or datasets. ii. Explain how Liberty calculated the 569M risk reduction for PEDS/PSPS Mitigation. 1. Explain how Liberty calculated and considered the joint effectiveness of these two mitigation activities. iii. Explain how Liberty calculated the 109M risk for PSPS Risk. iv. Liberty states, “The risk reduction modeled by ‘CC or UG Mitigation’ assumes all circuits with a BCR greater than or equal to one are hardened.” Does the 72M risk reduction for CC or UG Mitigation assume Covered Conductor is applied to all circuits with a BCR greater than or equal to one? Provide an explanation for this assumption. |  | Jessica McHale | 2026-09-16 | 2026-09-21 | [5 empty] | 6 | Wildfire Mitigation Strategy Development | Projected Overall Risk Reduction