## Data Request Log
LOG BEGINS SEPTEMBER 3, 2026
Liberty 2027 Base WMP Discovery Log
Last Updated: | 10/15/2026 at 12:00PM
Count | Party Name | DR Set # | Data Request | Question No. | Question ID | Question | Responses | Requestor | Date Received | Final Date Due | Date Sent | Links | Number of Attachments | Attachment Links | NDA Required? | WMP Section | Category | Subcategory
1 | OEIS | 1 | OEIS-P-WMP_2026-Liberty-001 | 1 | OEIS-001-Q01 | Q01. Regarding ESRI’s Utility Network Rules: On page 343 of Liberty’s 2027 Base WMP R0,1 Liberty stated that, as a result of ESRI’s Utility Network deployment, Liberty set rules to promote consistency in its GIS data, and the rules must be satisfied for the utility network to function as designed and will prevent its users from editing the utility subnetworks until all criteria are met. a. Describe the specific mechanism (e.g., software triggers, automated security checks, error-handling workflows) of the rules and criteria within Liberty’s ESRI Utility Network that prevent its users from updating the utility subnetworks until all criteria are fully satisfied. b. Provide specific examples of those rules and criteria. | a. ESRI’s Utility Network uses a combination of network rules, validation processes, dirty-area tracking, and user permissions to maintain consistency in the GIS data. The network rules define which features can connect, associate, or participate in a utility network. When a user creates or modifies a feature, the Utility Network evaluates the change against the applicable rules. If the change violates a rule or creates an invalid network condition, the system identifies the affected area as a “dirty area” and generates a validation error. The network cannot be considered fully validated until the applicable errors have been corrected and the dirty areas have been validated. For Liberty’s electric Utility Network, access to make changes is also controlled through GIS roles and permissions. Authorized GIS personnel may make edits, typically within a version separate from the default version. The changes can then be validated and reviewed for errors. Once the edits satisfy the applicable Utility Network rules and validation requirements, the version can be posted or reconciled to the default version, which represents the current network used by the broader enterprise. This process provides an additional quality-control mechanism because invalid or incomplete edits should not be incorporated into the authoritative network without being reviewed and validated. The Utility Network does not only rely on users to determine whether an edit is correct. The configured rules act as automated validation checks, while dirty areas and validation errors identify edits that require correction. Combined with GIS permissions and the versioning workflow, these controls help prevent unvalidated changes from becoming part of Liberty’s authoritative electric utility network. b. Examples of rules and criteria that may be applied within an electric Utility Network include: • Connectivity rules: Electrical features must connect to compatible network features. For example, a conductor must connect to an appropriate electrical device, structure, or other conductor at a valid connection point. The system can identify an invalid connection when features that are not permitted to connect are placed together.. • Device-to-device connectivity: Certain electrical devices can only connect to other devices or conductors through permitted connection types. For example, a transformer may be permitted to connect to conductors on its primary and secondary sides, while an incompatible device or feature type would produce a validation error. • Terminal rules: Devices that have multiple terminals must have connections made to the appropriate terminal. For example, an electrical transformer or switch may have designated terminals, and a conductor connected to the wrong terminal can create a network validation error. • Containment rules: Some features are modeled as containing other network features. For example, electrical equipment or an enclosure may contain certain devices or components. A feature that is placed inside a container when that feature type is not permitted to be contained there would violate the Utility Network rules. • Structural attachment rules: Certain electrical assets can be attached to structures, such as poles. For example, a transformer, switch, or other piece of electrical equipment may be permitted to attach to a utility pole, while an unrelated feature type may not be permitted to have that structural attachment. • Association rules: The Utility Network can require specific associations between features that are related but do not necessarily share physical geometric connectivity. For example, an electrical device may be associated with a structure or enclosure even when the device and structure are modeled as separate features. • Subnetwork rules and validation: Electric subnetworks must satisfy the applicable connectivity and network-configuration requirements before they can be successfully validated and updated. If a network feature is disconnected, incorrectly connected, or otherwise violates the configured rules, the affected area can remain marked as dirty until the underlying problem is corrected and the network is revalidated. | Jessica McHale | 2026-09-04 | 2026-09-10 | 2026-09-10 | LU Response to DR No. OEIS-P-WMP_2026-Liberty-001.pdf | 0 | - | No | 12 | Enterprise Systems | -
1 | OEIS | 1 | OEIS-P-WMP_2026-Liberty-001 | 2 | OEIS-001-Q02 | Q02. Regarding CSV Tabular Export to GIS Database: On page 343 of Liberty’s 2027 Base WMP R0, Liberty stated that as part of its data flow path, data transformations are made in SQL and tabular data is exported in CSV format. The GIS department converts these into feature classes stored in geodatabases for use in Liberty’s GIS enterprise database. a. Is it feasible for Liberty to replace its current intermediate CSV tabular export process with direct database-to-database (db2db) Extract-Transformation-Load (ETL)? i. If feasible, provide details and timelines of the direct db2db ETL implementation. 1. If feasible, but Liberty does not plan to implement db2db, explain why. ii. If not feasible, explain how Liberty controls potential operational errors and synchronization delays from the CSV tabular export step. | Based on the data flow described on page 343 of Liberty’s 2027 Base WMP R0, it is technically feasible to replace the intermediate CSV export with a direct database-to-database (DB2DB) Extract-Transformation-Load (ETL) process. i. The primary technical requirements for implementation would be establishing connectivity between the source and destination databases, replicating the existing SQL transformations and field mappings, ensuring that the required point geometry and attributes are correctly generated, and testing the resulting feature classes against the specifications of OEIS. None of these requirements inherently requires an intermediate CSV file. 1. While this approach is feasible, Liberty does not plan to implement DB2DB for the following reasons: • The CSV-to-geodatabase process is straightforward and repeatable. The existing process provides a consistent and efficient method for converting CSV data into feature classes without introducing unnecessary complexity. • Schema changes are more easily managed within the GIS environment. Any modifications required to the feature-class schema can be implemented more efficiently and transparently within the GIS, rather than requiring changes to the SQL-based application. • The risk of data corruption or unintended changes during conversion is minimal. The CSV-to-feature-class conversion process is well established, and GIS specialists review the resulting feature classes to verify that the data has been converted accurately and that no unintended changes have occurred. • The capacity to design and maintain an SQL-based ETL process has not yet been established. The level of SQL and GIS expertise required to develop, implement, and maintain the proposed ETL process is currently undetermined. Implementing DB2DB could therefore introduce additional development and maintenance requirements without a demonstrated benefit over the existing workflow. | Jessica McHale | 2026-09-04 | 2026-09-10 | 2026-09-10 | LU Response to DR No. OEIS-P-WMP_2026-Liberty-001.pdf | 0 | - | No | 12 | Enterprise Systems | -
1 | OEIS | 1 | OEIS-P-WMP_2026-Liberty-001 | 3 | OEIS-001-Q03 | Q03. Regarding Field Data Collection Training: On page 344 of Liberty’s 2027 Base WMP R0, Liberty stated that accuracy of compliance data is accomplished through consistent training of data collectors and that data analysts, system arborists, and electrical foreman are heavily involved in training inspectors, contractors, and other groups that are tasked with data collection. a. Describe Liberty’s training program provided to its personnel and contractors responsible for data collection. b. Explain how data analysts, system arborists, and electrical foreman conduct oversight and train the field data collectors to ensure accuracy of the self-policing in raw data collection prior to in-house Data Quality Management (DQM). | a. Liberty trains all internal staff and contractors performing inspection and maintenance activities on the system on data collection requirements. Workers are trained regularly on the data collection application Fulcrum based on the projects they are working on (G.O. Inspections, Repairs, WMP work, QAQC, etc.). Each project has a unique workflow with data governance and standard procedures. Trainings are performed in person before the start of each project. Afterwards, the training documentation is uploaded to Fulcrum’s Reference Files in the application, which can be downloaded by field crews as necessary. Additional trainings are completed at a monthly cadence or ad hoc when relevant updates are made to the data collection application. b. Data Analysts conduct the Fulcrum training and monitor data coming in during all steps of the data collection and reporting process. Asset Tracking, the inspection and maintenance Fulcrum application, uses code to trigger data review events, which are performed by the Data Analysts. Electrical Foremen work with data analysts to create training materials and conduct training seminars. Foremen also conduct peer to peer training on data collection, related to projects that field crews are working on. Liberty documents vegetation management data collection requirements through its plans, processes, procedures, contractor specifications, and scopes of work. Liberty’s vegetation management contractors provide training to their employees on the functionality of work management software and associated data collection requirements. Liberty works directly with its contractors to provide training on updates to work management software layers or configurations and data collection requirements on an as needed basis. Liberty's System Arborists provide oversight of vegetation management contractors and field data collectors to promote accurate and consistent data collection. System Arborists conduct periodic data quality reviews, field observations, and targeted checks of contractor-collected data to verify that inventories, work prescriptions, and completed work records are entered correctly. Additionally, data quality issues identified through standard QA/QC processes are communicated to contractors and are assigned for corrective action. To support ongoing data quality improvement, Liberty's Vegetation Management team and data analysts hold monthly meetings to review vegetation management dashboards, verify data accuracy, discuss data quality issues, and develop tracking tools. In addition, Liberty conducts monthly contractor meetings to review work progress, address quality concerns, and reinforce data collection and documentation expectations. This continuous oversight and feedback process helps improve the accuracy of raw data collection prior to in-house Data Quality Management (DQM) review. | Jessica McHale | 2026-09-04 | 2026-09-10 | 2026-09-10 | LU Response to DR No. OEIS-P-WMP_2026-Liberty-001.pdf | 0 | - | No | 12 | Enterprise Systems | -
1 | OEIS | 1 | OEIS-P-WMP_2026-Liberty-001 | 4 | OEIS-001-Q04 | Q04. Regarding Asset Identification Process: On page 342 of Liberty’s 2027 Base WMP R0, Liberty stated, to achieve 100 percent asset identification, it relies on a 5-year detailed asset inspection cycle by reconciling as-builts data against actual field data after assets are installed in the field. a. Explain the procedures Liberty uses to identify and correct any unrecorded field updates or asset discrepancies during the interim 5-year window. i. Explain how Liberty prevents unverified interim asset data from contaminating risk models prior to the full 5-year inspection reconciliation. | a. Liberty examines detailed inspection records in Fulcrum to identify any discrepancies in the GIS database that occurred during the drawing in of as-builts. GIS data will then be updated based on the more up to date data recorded in the field. Yearly LiDAR data is also used to reconcile GIS data by displaying the most up to date location of assets in the field. i. Liberty’s current risk model operates at the circuit-level based on the verified locations of overhead distribution and transmission circuits. Liberty has not developed an asset-level risk model that estimates specific failure probabilities down to individual system components (e.g., fuses, tree attachments). | Jessica McHale | 2026-09-04 | 2026-09-10 | 2026-09-10 | LU Response to DR No. OEIS-P-WMP_2026-Liberty-001.pdf | 0 | - | No | 12 | Enterprise Systems | -
1 | OEIS | 1 | OEIS-P-WMP_2026-Liberty-001 | 5 | OEIS-001-Q05 | Q05. Regarding Data Retention and Disposal Policy: On page 343 of Liberty’s 2027 Base WMP R0, Liberty stated it is required to maintain inspection data over a ten-year period. However, it stated that there is currently no determination for when a cutoff period will be put in place for disposal of its historical data and that, as it reaches the ten-year mark, it will create a plan to evaluate retention / disposal rate of historical data. a. State the exact year and quarter Liberty projects it will accumulate ten continuous years of historical inspection data. b. Given that Liberty’s formal data disposal policy will not be created until the ten-year mark is reached, explain how Liberty ensures compliance with retention mandates without performance degradation due to database bloat, or any data governance vulnerabilities in the interim. | a. Liberty projects that it will accumulate ten continuous years of historical inspection data by the end of Q4 2029. b. Liberty maintains a SQL Server database for its assets and their inspection and maintenance records. The database holds roughly 2 gigabytes of character and numeric data from G.O. inspections and maintenance work dating back to 2020, including quarterly archives of SQL Views. Photos are stored in Fulcrum’s database, as well as a Liberty hosted SharePoint site, for certain projects. Liberty’s current plan allows for 500 gigabytes of storage in Fulcrum’s database, of which roughly 175 gigabytes are accounted for. Due to Liberty’s ETL process, the use of Fulcrum’s database for storage, and the relatively small number of assets under management compared to larger ECs, database bloat, and the resulting performance degradation, is not a concern for retaining 10 years of historical data. | Jessica McHale | 2026-09-04 | 2026-09-10 | 2026-09-10 | LU Response to DR No. OEIS-P-WMP_2026-Liberty-001.pdf | 0 | - | No | 12 | Enterprise Systems | -
1 | OEIS | 1 | OEIS-P-WMP_2026-Liberty-001 | 6 | OEIS-001-Q06 | Q06. Regarding Employing a Registered Professional Forester: On page 244 of its 2023-2025 Base WMP R0, Liberty indicated that it employed a Registered Professional Forester. In Section 9.13 Workforce Planning of its 2027 Base WMP R0 (pages 257-262), it is not clear whether Liberty currently employs or contracts a Registered Professional Forester. a. Does Liberty employ, internally or contracted, a Registered Professional Forester? i. If yes, identify the Worker Title(s) in Table 9-9 of Liberty’s 2027 Base WMP R0 that currently holds a Registered Professional Forester license. ii. If Liberty does not employ or contract with a Registered Professional Forester, explain why it does not. | a. Liberty currently contracts with one Registered Professional Forester (RPF). i. This individual is represented under the Utility Forester V worker title in Table 9-9 of Liberty's 2027 Base WMP. The reference in the 2023-2025 Base WMP indicating that Liberty employed one RPF reflected the qualifications of Liberty's internal Vegetation Management staff at that time. Specifically, Table 8-32 identified one internal employee holding an RPF license. That employee is no longer employed by Liberty. As shown in Table 9-23 of the 2027 Base WMP, Liberty does not currently employ an internal Vegetation Management employee who holds an RPF license. However, Liberty does employ one individual who is a Society of American Foresters (SAF) Certified Forester. While this certification demonstrates professional forestry expertise, it is distinct from and does not constitute a California Registered Professional Forester license. | Jessica McHale | 2026-09-04 | 2026-09-10 | 2026-09-10 | LU Response to DR No. OEIS-P-WMP_2026-Liberty-001.pdf | 0 | - | No | 9 | Vegetation Management and Inspections | Post-Fire Service Restoration
1 | OEIS | 1 | OEIS-P-WMP_2026-Liberty-001 | 7 | OEIS-001-Q07 | Q07. Regarding Maintenance of Fire-Resilient Rights-of-Way: On page 193 of its 2026-2028 Base WMP R1 (Clean), Liberty indicated it “is developing a Right-of-Way Management Plan as a part of its IVM [Integrated Vegetation Management] Program.” However, in its 2027 Base WMP R0, Liberty did not state it was developing a Right-of-Way Management Plan. a. Has Liberty developed or is Liberty developing a Right-of-Way Management Plan? i. If Liberty has developed a Right-of-Way Management Plan, provide the plan. ii. If Liberty is in the process of developing a Right-of-Way Management Plan, specify: 1. When Liberty will complete the plan. 2. The purpose of the plan. iii. If Liberty has not developed or is not developing a Right-of-Way Management Plan, describe how it will ensure ongoing maintenance of the fire-resilient rights-of-way it has established. | a. Currently, Liberty is not developing a Right-of-Way Management Plan. i. N/A ii. N/A iii. While Liberty is currently not developing a standalone Right-of-Way Management Plan, it maintains fire-resilient rights-of-way through its established vegetation management, inspection, maintenance, and wildfire mitigation programs, which collectively ensure ongoing monitoring and upkeep of these corridors. Liberty is continue advancing fire-resilient right-of-way objectives through operational program implementation. This includes continued implementation of Forest Resilience Corridors, completing planned Zone 1 and Zone 2 treatments, and prioritizing future Zone 3 treatments. Because a significant portion of this work occurs on U.S. Forest Service lands, Liberty intends to continue coordinating with the U.S. Forest Service to develop and implement appropriate fuel reduction and maintenance strategies within and adjacent to utility rights-of-way. Liberty’s vegetation management personnel receive annual training on Integrated Vegetation Management principles, compatible vegetation management, and fire-resilient right-of-way practices. This training supports consistent application of vegetation management strategies for the ongoing maintenance of fire-resilient rights-of-way post treatment. Following completion of fire-resilient right-of-way and Forest Resilience Corridor projects, Liberty maintains established corridor conditions through its existing Vegetation Management Program. During routine maintenance cycles, Liberty removes newly established incompatible woody vegetation within treated rights-of-way, promotes the continued development of compatible vegetation cover, and performs ongoing inspections and maintenance activities to identify vegetation conditions that may warrant corrective action. Additionally, maintenance may be achieved through Liberty’s Fuel Management Program and collaborative projects with local land managers. For example, Liberty is currently working with the Tahoe National Forest and National Forest Foundation on the Big Jack East WUI Maintenance Project. The project includes maintenance activities along approximately 1.7 miles of 120 kV transmission lines across 46 structures and more than 470 acres which were originally treated in 2021. This project is an example of Liberty's collaborative approach to maintaining treated forest conditions, including vegetation within and adjacent to the powerline right-of-way. | Jessica McHale | 2026-09-04 | 2026-09-10 | 2026-09-10 | LU Response to DR No. OEIS-P-WMP_2026-Liberty-001.pdf | 0 | - | No | 8 | Grid Design, Operations, and Maintenance | Quality Assurance and Quality Control
1 | OEIS | 1 | OEIS-P-WMP_2026-Liberty-001 | 8 | OEIS-001-Q08 | Q08. Substation Inspection Scheduling: On page 232 of its 2027 Base WMP R0, Liberty states “A minimum of 12 substation inspections will occur each year. Generally, two site visits will occur per facility per year.” a. Does Liberty intend to inspect each individual substation facility at least once per year? b. What conditions would force Liberty not to conduct two inspections of a substation facility in a given year? c. In the past 5 years, how many times has Liberty inspected a substation facility only once during a calendar year? d. In the past 5 years, how many times has Liberty failed to inspect a substation facility during a calendar year? e. Provide substation inspection records for the past 5 years. | a. Yes. Liberty intends to inspect each substation under its Substation Defensible Space (WMP-VM-VFM-03) initiative at least once per year to identify vegetation management work requirements, including vegetation and debris removal within and adjacent to the substation perimeter. b. Conditions that may prevent Liberty from conducting two inspections of a substation within a calendar year include severe weather conditions (such as early snowfall that limits site access) and significant substation construction or rebuilding activities that restrict access or render routine vegetation management inspections unnecessary during the construction period. c. Refer to table “Substation Defensible Space (WMP-VM-VFM-03) Inspections.” (see link to DR, column M) d. Refer to table “Substation Defensible Space (WMP-VM-VFM-03) Inspections.” (see link to DR, column M) e. See files: “Substation Defensible Space (WMP-VM-VFM-03) Inspections 2022-2026.pdf” and “Substation Defensible Space (WMP-VM-VFM-03) Inspections 2022-2026.xlsx”. | Jessica McHale | 2026-09-04 | 2026-09-10 | 2026-09-10 | LU Response to DR No. OEIS-P-WMP_2026-Liberty-001.pdf | 2 | https://california.libertyutilities.com/uploads/WMP%20Data%20Requests/2022-2026-Chemical-Use-Report-Subsation.zip https://california.libertyutilities.com/uploads/WMP%20Data%20Requests/Substation%20Defensible%20Space%20Inspections%202022-2026.zip | No | 9 | Vegetation Management and Inspections | Defensible Space
2 | OEIS | 2 | OEIS-P-WMP_2026-Liberty-002 | 1 | OEIS-002-Q01 | Q01. Regarding Liberty’s 2027 Pole Clearing Target: On page 215 of its 2027 Base WMP R0, 1 Liberty indicated that it will clear 4,500 poles pursuantto Public Resources Code section 4292 (PRC 4292). On page 163 of its 2026-2028 Base WMP R1 (Clean), 2 Liberty also indicated it would clear 4,500 poles pursuant to PRC 4292. a. List the number of poles and towers subject to PRC 4292 in Liberty’s service territory. i. If this number is different than 4,500, explain why. b. Does Liberty anticipate the number of pole and towers subject to PRC 4292 will change in 2027? i. If yes, by how much will the number increase or decrease? c. List and describe the factors Liberty considers when deciding whether to install nonexempt or exempt equipment (e.g., cost, resource availability). | a. Liberty’s current inventory includes 4,521 poles subject to PRC 4292. i. Liberty established its target of 4,500 poles requiring clearing for PRC 4292 to reflect normal changes to Liberty’s asset inventory resulting from infrastructure upgrades, pole replacements, new construction, and ongoing asset management activities. For planning and reporting purposes, Liberty rounded the annual work target to 4,500. b. Yes. Liberty anticipates that the number of poles subject to PRC 4292 may change over time due to system modifications, including pole replacements, line extensions, system hardening projects, new business, and other infrastructure upgrades. i. Liberty is currently in the process of reviewing and evaluating the number of newly identified poles that may be subject to PRC 4292 requirements. This includes verification of newly identified subject poles, review of poles classified as exempt or supporting no equipment identified during pole-clearing inspections, evaluation of QAQC findings, general data governance and review, and asset data conflation. While this evaluation remains ongoing, Liberty preliminarily estimates that the poles subject to PRC 4292 may increase by approximately 4% (about 180 poles). Liberty will continue to refine the future pole clearing inventory as validation activities are completed. c. Liberty's standard practice is to install exempt equipment wherever an approved exempt alternative exists within Liberty's engineering standards. Non-exempt equipment is installed only where no approved exempt alternative can meet the functional requirements of the application while maintaining compliance with Liberty's construction and safety standards. | Jessica McHale | 2026-09-11 | 2026-09-16 | 2026-09-16 | Liberty Response to DR No. OEIS-P-WMP_2026-Liberty-002.pdf | 0 | - | No | 9 | Vegetation Management and Inspections | Quantitative Targets
2 | OEIS | 2 | OEIS-P-WMP_2026-Liberty-002 | 2 | OEIS-002-Q02 | Q02. Regarding Liberty’s Historical Outage Data: On page 36 of its 2027 Base WMP, Liberty states that it is using “four years of Liberty’s historical outage data to estimate the likelihood of an outage on each feeder.” a. Why is Liberty only using the past four years within its risk methodology data set? b. How many outages has Liberty recorded in the past four years? c. What actions has Liberty taken to expand upon its outage data set? | a. Liberty is using the past four years in its risk methodology data set because Liberty focused its analysis of historical outages to the date range of its updated outage management system. See response to (c) for a discussion of integrating outage records from Liberty’s previous outage management system. b. The initial dataset of outage records 3,473 outages. See Technical Appendix B (section “Outage and Ignition Data Methodology”). c. Liberty is investigating outage records back to 2018, pre-dating the change of outage management systems. Geo-referencing and pinpointing the coordinates of these outage records takes additional analytical work to match records to locations using address information or asset ID information. In addition, mapping these records to risk drivers and risk sub-drivers requires different logic than the current analytical workstream. A key benefit of a larger dataset of outage records is improved training and precision of the probability of failure model. | Jessica McHale | 2026-09-11 | 2026-09-16 | 2026-09-16 | Liberty Response to DR No. OEIS-P-WMP_2026-Liberty-002.pdf | 0 | - | No | 5 | Risk Methodology and Assessment | Overview
2 | OEIS | 2 | OEIS-P-WMP_2026-Liberty-002 | 3 | OEIS-002-Q03 | Q03. Regarding Table 6-4: Summary of Risk Reduction for Top Circuits: a. Provide a version of Table 6-4 (pp. 141-142) via Excel with the following additional columns: i. Overall Utility Risk Reduction from PSPS ($) ii. Overall Utility Risk Reduction from SRP ($) iii. Overall 2027 Utility Risk Reduction from Grid Hardening ($) iv. Overall 2027 Utility Risk Reduction from Covered Conductor ($) v. Overall 2027 Utility Risk Reduction from Pole Replacement ($) b. In Table 6-4, “Detailed inspections” is only listed as a 2027 activity for circuit MEY34000 (p. 141). i. Do any other circuits have detailed inspections planned for 2027? ii. Are there any other types of inspections planned in 2027 for the circuits in Table 6-4? iii. If yes to either or both (i) and (ii), provide a corrected version of Table 6-4 to reflect which circuits have detailed and additional inspections planned for 2027. | a. See attachment “DR-002-Q03.a.Table 6-4 Risk reduction by mitigation.xlsx.” b. i. Yes, see attachment “DR-002-Q03.b Table 6-4 Circuit List Planned Inspections.xlsx.” ii. Yes, see attachment “DR-002-Q03.b Table 6-4 Circuit List Planned Inspections.xlsx.” iii. See attachment “DR-002-Q03.b Table 6-4 Circuit List Planned Inspections.xlsx.” | Jessica McHale | 2026-09-11 | 2026-09-16 | 2026-09-16 | Liberty Response to DR No. OEIS-P-WMP_2026-Liberty-002.pdf | 2 | https://view.officeapps.live.com/op/view.aspx?src=https%3A%2F%2Fcalifornia.libertyutilities.com%2Fuploads%2FDR-002-Q03.a.%2520Table%25206-4%2520Risk%2520reduction%2520by%2520mitigation.xlsx&wdOrigin=BROWSELINK https://view.officeapps.live.com/op/view.aspx?src=https%3A%2F%2Fcalifornia.libertyutilities.com%2Fuploads%2FDR-002-Q03.b.%2520Table%25206-4%2520Circuit%2520List%2520Planned%2520Inspections.xlsx&wdOrigin=BROWSELINK | No | 6 | Wildfire Mitigation Strategy Development | Projected Risk Reduction on Highest-Risk Circuits in 2027
2 | OEIS | 2 | OEIS-P-WMP_2026-Liberty-002 | 4 | OEIS-002-Q04 | Q04. Regarding Table 5-5: Liberty Top-Risk Circuits: a. In Table 5-5, circuits TAH5201, TAH7300, and KBH5200 each have an outage program risk score that is over 40% of the overall utility risk score, at 42.9%, 51.0%, and 42.7% respectively. i. Provide an explanation for the relatively high outage program risk for these circuits. ii. How has the relatively high outage program risk impacted decision-making when determining mitigations for these circuits? b. Circuit 640 has an outage program risk score of 0. i. Provide an explanation for why this circuit has no outage program risk. | a. i. As described in the 2027 WMP, Liberty’s outage program risk is primarily based on PSPS risk. Liberty’s PSPS likelihood module is relatively coarse, projecting these three circuits respectively would experience a PSPS event once every two years. These three circuits face high outage program risk shares because they are relatively long circuits serving many residential and commercial customers across Tahoe City, the west shore of Lake Tahoe, and Dollar Point. In contrast, modeled wildfire risk is relatively low for each of the three circuits, because Technosylva wildfire simulations limit the fire spread potential in these areas. The circuits are immediately adjacent to the lake shore, may receive substantial annual snowfall, and typically see higher fuel moistures than portions of Liberty’s service territory further away from the Sierra Nevada crest. Nevertheless, wildfire risk remains a concern for these three circuits due to factors not currently captured well in Technosylva wildfire consequence outputs, including egress and potential future tree mortality events. ii. At present, Liberty’s risk model prioritizes circuits and mitigation choices based on the sum of wildfire and outage program risk denominated in dollars. The advantage of doing so is that wildfire and outage risk can be expressed in common units, and mitigations that address one or both risk types can be evaluated on a common basis. In other words, Liberty’s current risk model does not uniquely treat circuits with high proportions of outage program risk differently than ones with low proportions of outage program risk. Liberty targets the sum of wildfire and outage program risk. Going forward, as Liberty builds out the capabilities of the risk model to potentially factor in how hardening activities may influence PSPS and SRP decisions, then mitigations that are more effective at addressing outage program risk would likely be favored for TAH7300, TAH5201, and KBH5200. In addition, Liberty is assessing pilot locations for grid monitoring devices (i.e., Gridscope), which provide measurable outage program risk reductions. b. Circuit 640 is a transmission-level circuit. When de-energized, load served by 640 can be met through alternative transmission-level sources. Thus, Liberty’s PSPS risk model assumes no PSPS outage risk is introduced when 640 is proactively de-energized. | Jessica McHale | 2026-09-11 | 2026-09-16 | 2026-09-16 | Liberty Response to DR No. OEIS-P-WMP_2026-Liberty-002.pdf | 0 | - | No | 5 | Risk Methodology and Assessment | Top Risk-Contributing Circuits/Segments/Spans
2 | OEIS | 2 | OEIS-P-WMP_2026-Liberty-002 | 5 | OEIS-002-Q05 | Q05. Regarding WMP Expenditures: a. In Table 3-3 of its 2027 Base WMP, Liberty states that the projected spend on WMP expenditures is $44,924. Liberty does not include expenditures related to mitigation activities included in this WMP, for example, expenditures related to Overhead Hardening with Covered Conductor, in this total. i. List the expenses that are included in this total expenditure. ii. Why are other expenditures related to mitigation activities included in this WMP not included? | a. Energy Safety’s premise to this question is incorrect. Liberty’s stated expenditures in Table 3-3 of Liberty’s 2027 Base WMP do include all expenditures related to mitigation activities in the 2027 WMP. As directed in Energy Safety’s guidelines for Section 3.6, and as specified in Table 3-3 of Liberty’s 2027 Base WMP, Liberty presented its projected expenditures in thousands $USD. Thus, Liberty’s projected 2027 WMP expenditures is $44,924,100 and not $44,924. i. Liberty provides all 2027 WMP expenditures in Table 11 of its annual WMP submission: “Liberty_2027-WMP_R0.” ii. N/A. | Jessica McHale | 2026-09-11 | 2026-09-16 | 2026-09-16 | Liberty Response to DR No. OEIS-P-WMP_2026-Liberty-002.pdf | 0 | - | No | 3 | Overview of Base WMP | Projected Expenditures
2 | OEIS | 2 | OEIS-P-WMP_2026-Liberty-002 | 6 | OEIS-002-Q06 | Q06. Regarding Outage Program Risk: a. On page 41 of its 2027 Base WMP, Liberty states that, “Outage program risk is primarily based on PSPS risk.” i. Explain what factors other than PSPS risk (if any) contribute to Liberty’s outage program risk in Liberty’s current risk modeling methodology. ii. If there are no other factors, confirm that outage program is currently based solely on PSPS risk. | a. i. Liberty’s risk model architecture (2027 WMP Figure 5-1) shows that outage program risk is based on the sum of PSPS risk and PEDS risk denominated in dollars. However, as noted in the figure, Liberty’s PEDS risk model is currently under development. As discussed in 2027 WMP Table 5-6, quantification of PEDS outage program risk is a high-priority item of Liberty’s risk assessment improvement plan. Liberty provided a preliminary estimate of outage program risk associated with Liberty’s SRP program in 2027 WMP Section 5.2.2.2. See the corresponding section for the preliminary estimate and interpretation relative to estimated wildfire and PSPS risk. ii. As discussed in Liberty’s 2027 WMP (see for example, 2027 WMP Sections 5.2.2.2 and 5.2.2.3, 2027 WMP Tables 5-6 and 6-3, and 2027 WMP Appendix D Section 1.1), Liberty’s estimate of outage program risk is based on quantified PSPS risk. As discussed in 2027 WMP Table 5-6, quantification of PEDS outage program risk is a high-priority item of Liberty’s risk assessment improvement plan. | Jessica McHale | 2026-09-11 | 2026-09-16 | 2026-09-16 | Liberty Response to DR No. OEIS-P-WMP_2026-Liberty-002.pdf | 0 | - | No | 5 | Risk Methodology and Assessment | Risk and Risk Component Identification
2 | OEIS | 2 | OEIS-P-WMP_2026-Liberty-002 | 7 | OEIS-002-Q07 | Q07. Regarding IWRMC Survey Results: a. On page 118 of its 2027 Base WMP, Liberty states that it, “calculates maturity adjustments using IWRMC survey results related to PSPS and equipment settings categories. The maturity adjustments are approximately 80% yielding effectiveness parameters for PSPS and SRP of 0.75 and 0.56, respectively.” i. Provide a narrative description of the IWRMC survey. Describe who completed the survey and when it was completed. Provide survey questions and results, as applicable. ii. Provide a narrative description of how Liberty determined the maturity adjustment of 80%. | a. i. The mission of the International Wildfire Risk Mitigation Consortium (IWRMC) is to establish and facilitate a system of working and networking channels between members of the global utility community to support ongoing sharing of data, information, technology, and practices, and proactively address the wildfire issues through learning, innovation, analysis, assessment, and collaboration. The IWRMC is led by a utility executive steering group and consists of member utilities in nineteen states and provinces from the United States, Canada, and Australia. The IWRMC Wildfire Risk Mitigation Maturity Model Survey is a comprehensive self-assessment tool designed to evaluate how effectively an electric utility identifies, manages, and reduces wildfire risk. The survey examines the maturity of the utility’s key capabilities across nine categories: (A) Risk Mapping and Simulation; (B) Situational Awareness and Forecasting; (C) Grid Design and System Hardening; (D) Asset Management and Inspections; (E) Vegetation Management and Inspection; (F) Grid Operations and Protocols; (G) Resource Allocation Methodology; (H) Emergency Planning and Preparedness; and (I) Stakeholder Cooperation and Community Engagement. Within these categories, the survey evaluates the extent to which wildfire risk management practices are formalized, consistently implemented, supported by data and analytical tools, integrated across organizational functions, and subject to review and continuous improvement. Survey results allow participating utilities to evaluate their current capabilities, identify potential areas for improvement, and benchmark their practices against those of other participating utilities. The version of the maturity model used by Liberty was last revised on October 6, 2025, and included survey results from thirty participating companies. Liberty completed the IWRMC Maturity Model survey on December 30, 2025. The survey was completed by Liberty’s internal subject matter experts, with each subject matter expert providing responses for the categories and capabilities for their respective areas of responsibility and technical expertise. Liberty used the resulting scores to inform the maturity adjustments applied to the effectiveness estimates for its PSPS and Sensitive Relay Profile (SRP) mitigations. For the IWRMC Maturity Model survey questions see attachment “DR-002-Q07 IWRMC Maturity Model_ CONFIDENTIAL.xlsx”. The applicable results are provided in attachment “DR-002-Q07 Maturity Model Results_ CONFIDENTIAL.xlsx”. b. To calculate the maturity adjustment, Liberty identified IWMRC survey questions related to (F) Grid Operations and Protocols and (B) Situational Awareness and Forecasting. Within the two categories, Liberty identified survey questions that specifically related to Liberty’s PSPS program, SRP program, and weather forecasting capabilities. Using the survey responses, Liberty calculated average scores for PSPS and SRP programs, and Liberty used the average scores to derive the maturity-adjusted mitigation effectiveness values for PSPS and SRP. While the survey responses provide a quantitative method of estimating maturity, there remains a degree of subjectivity and uncertainty when relying on survey responses to calculate a maturity factor. | Jessica McHale | 2026-09-11 | 2026-09-16 | 2026-09-16 | Liberty Response to DR No. OEIS-P-WMP_2026-Liberty-002.pdf | 2 | - | Yes | 6 | Wildfire Mitigation Strategy Development | Identifying and Evaluating Initiative Activities
2 | OEIS | 2 | OEIS-P-WMP_2026-Liberty-002 | 8 | OEIS-002-Q08 | Q08. Regarding Mitigation Selection Using Risk Model Outputs: a. On page 110 of its 2027 Base WMP, Liberty states, “Overhead hardening with covered conductor and undergrounding are the two key mitigations that Liberty currently evaluates in its benefit-cost analysis.” i. Explain how Liberty currently uses risk model outputs to inform any mitigation activity selection, prioritization, or scheduling other than overhead hardening with covered conductor and undergrounding. | a. i. While Liberty’s current risk model only calculates benefit-cost ratios for overhead hardening with covered conductor and undergrounding, Liberty uses risk model outputs more broadly to inform risk mitigation activities. For example, the risk model informs locations of pilot grid monitoring devices (Gridscope), fuse replacements, and pole replacements. As noted in Liberty’s risk assessment improvement plan (2027 WMP Table 5-6), Liberty is prioritizing benefit-cost ratio quantification for such mitigations (i.e., fuse replacement). | Jessica McHale | 2026-09-11 | 2026-09-16 | 2026-09-16 | Liberty Response to DR No. OEIS-P-WMP_2026-Liberty-002.pdf | 0 | - | No | 6 | Wildfire Mitigation Strategy Development | Approach
3 | OEIS | 3 | OEIS-P-WMP_2026-Liberty-003 | 1 | OEIS-003-Q01 | Q01. Regarding Sensitive Analysis and Parameter Uncertainty: a. On page 121 of its 2027 Base WMP,1 Liberty states that it, “defers quantification of model uncertainty in its current version of the risk model, which would involve alternate specifications of the probability of outage model or the use of other wildfire spread models beyond Technosylva’s provided outputs.” i. Provide a timeframe with key milestones for assessing the uncertainty of Liberty’s risk model. ii. Describe how Liberty considers risk model uncertainty during its risk informed decision-making process. b. On page 121, Liberty also states that it, “can provide examples of parameter uncertainty, which includes inputting alternative mitigation effectiveness or cost parameters and comparing the results to the default parameter choices.” i. Describe how Liberty analyzed the sensitivity of parameters. Provide the sensitivity analysis notes, SME review or calibration notes, meeting notes, and other relevant documentation. ii. Identify any findings from the parameter sensitivity analysis and explain how Liberty considers the sensitivity of parameters during its risk informed decision-making process. | a. i) Liberty clarifies it defines model uncertainty as the underlying methodological uncertainty with quantitative risk modeling, and that parameter uncertainty reflects the varying deterministic values that can be inputted into a risk model. Liberty interprets the data request regarding “uncertainty of Liberty’s risk model” to refer to “model uncertainty,” not “parameter uncertainty,” given the citation associated with page 121. Liberty does not propose a timeline or milestones with assessing "model uncertainty" at this time. As described in the citation to page 121, addressing model uncertainty may involve leveraging multiple wildfire simulation vendors, and assessing how risk changes based on the use of different vendors (and thus different methodologies). This would be an inefficient use of resources to contract with multiple wildfire simulation vendors. One way Liberty already addresses model uncertainty is on the probability of outage side of the risk modeling equation. Liberty describes model specification and cross-validation in detail on pages 47-48, including Random Forest, Light Gradient Boosting (LightGBM), Extreme Gradient Boosting (XGBoost) and a Bayesian State-Space model. ii) Liberty’s current risk model provides a signal for which areas and assets within its service territory face higher wildfire and outage program risk. However, the signal can also be complicated by noise from the data-generating process. A four-year outage dataset to train the model likely introduces more noise than an eight-year outage dataset that can more adequately filter out near random occurrences. To address uncertainty in the risk model, Liberty approaches model results with healthy skepticism and questions counterintuitive conclusions. While quantitative measures of risk are foundational to investment decisions, caution must be exercised and cross-functional collaboration is critical, given the noise and extreme tail of wildfire risk. b) i) Liberty uses its risk model dashboard to change parameter values within the Power BI application within Microsoft Teams. By changing the parameter values, such as the capital cost of overhead hardening with covered conductor, or the likelihood of PSPS on the highest risk circuits, Liberty can understand how sensitive the model is to key parameter choices. Key parameter choices that are relevant to understanding the impact of uncertainty on model outputs include capital costs of grid hardening measures, the mitigation effectiveness of mitigation alternatives, monetized consequence parameters (e.g., $/CMI assumption), and the likelihood and duration of PSPS events. ii) At present, as discussed in the WMP, Liberty’s risk model currently focuses on estimating benefit-cost ratios for overhead hardening with covered conductor and undergrounding. In addition, Liberty’s risk models’ capabilities are well-suited towards understanding overall utility risk, wildfire risk, and PSPS risk at the circuit level. Therefore, the parameter sensitivity tests that Liberty has explored using the dashboard focus on what parameter values yield materially different results for covered conductor vs. undergrounding, as well as risk ranks at the circuit level. Liberty has found that despite the lower mitigation effectiveness value for covered conductor, the lower capital cost yields higher benefit-cost ratios for this mitigation vs. undergrounding. Liberty has varied the capital cost of undergrounding to see where this conclusion would be materially different. In addition, Liberty has varied the $/CMI assumption, given the inherent challenges in measuring the value of lost load. Varying this monetized reliability consequence parameter can affect the risk ranking, given the analysis is at the circuit level and circuits with higher customer counts and higher PSPS likelihood would result in higher PSPS risk. Liberty does not have a formal workpaper or documentation for the parameter sensitivity analysis because it lives within the recently developed risk model dashboard. | Jessica McHale | 2026-09-16 | 2026-09-21 | 2026-09-21 | LU Response to DR OEIS-P-WMP_2026-Liberty-003.pdf | 0 | - | No | 6 | Wildfire Mitigation Strategy Development | Identifying and Evaluating Initiative Activities
3 | OEIS | 3 | OEIS-P-WMP_2026-Liberty-003 | 2 | OEIS-003-Q02 | Q02. Regarding Sub-Driver Effectiveness of Overhead Hardening with Covered Conductor: a. On page 118 of its 2027 Base WMP, Liberty states, “For overhead hardening with covered conductor, Liberty’s mitigation effectiveness parameters ranging from highest to lowest are 0.77 for animal contact, 0.72 for vegetation contact, 0.70 for third-party contact, 0.64 for vehicle contact, and 0.60 for equipment failure.” i. Describe how Liberty determined these sub-driver effectiveness parameters. Provide the SME input or notes, survey responses, meeting notes, and other relevant documentation. | a. i. Liberty describes how it determined sub-driver effectiveness values for overhead hardening with covered conductor on page 119. For additional detail, including the full list of sub-drivers, effectiveness parameters, and the mapping to PG&E’s WDRM, please refer to Technical Appendix B, specifically the section on mitigation effectiveness. Liberty relies on this benchmarking analysis for mitigation effectiveness parameters, rather than SME input. | Jessica McHale | 2026-09-16 | 2026-09-21 | 2026-09-21 | LU Response to DR OEIS-P-WMP_2026-Liberty-003.pdf | 0 | - | No | 6 | Wildfire Mitigation Strategy Development | Identifying and Evaluating Initiative Activities
3 | OEIS | 3 | OEIS-P-WMP_2026-Liberty-003 | 3 | OEIS-003-Q03 | Q03. Regarding Liberty’s Empirical Effectiveness Estimate of Overhead Hardening Without Covered Conductor: a. On pages 120-121 of its 2027 Base WMP, Liberty explains its methodology for the empirical analysis of overhead hardening without covered conductor. i. Liberty states that it, “leveraged the outage dataset relied upon for training the probability of outage model, which includes outage records for the four-year period 2022-2025.” 1. How many outages are included in this dataset? 2. Explain how Liberty accounted for weather conditions for the outage data in the empirical analysis. | a. i. Liberty describes the outage dataset on page 44 of its 2027 WMP: “The model is trained on four years of historical outage records (January 1, 2022– December 31, 2025), producing an initial dataset of approximately 3,400 outage records.” The precise number of outages included in the dataset is 3,474. ii. The differences-in-differences analysis relies on a common trends assumption, or sometimes called parallel trends. The comparison is between a treatment group and a control group over the same time period, so any weather that affects both groups simultaneously during the time period will be accounted for in the relative differences in outage outcomes. For example, if it was particularly mild in terms of wind in 2023, and then exceptionally windy and hot in 2024, that would likely enter the estimation by driving up outage counts in 2024 relative to 2023. The advantage of the differences-in-differences analysis is that both treated and control groups would be subject to those common weather conditions, so the estimator acts by taking the relative change in outage counts between treatment and control group during the time period. As Liberty notes in its risk assessment improvement plan, Liberty will more robustly build out the methodology for empirically measuring mitigation effectiveness from this initial estimator. | Jessica McHale | 2026-09-16 | 2026-09-21 | 2026-09-21 | LU Response to DR OEIS-P-WMP_2026-Liberty-003.pdf | 0 | - | No | 6 | Wildfire Mitigation Strategy Development | Identifying and Evaluating Initiative Activities
3 | OEIS | 3 | OEIS-P-WMP_2026-Liberty-003 | 4 | OEIS-003-Q04 | Q04. Regarding Activity Prioritization Schematic: a. On page 67 of the Energy Safety WMP Guidelines,2 Energy Safety requires electric corporations to provide, “A high-level schematic showing the procedures and evaluation criteria used to evaluate potential activities. At a minimum, the schematic must demonstrate the roles of quantitative risk assessment, resource allocation, evaluation of other plan objectives (e.g., cost, timing) identified by the electrical corporation, and SME judgment. Where specific local factors, which vary across the service territory, are considered in the decision-making process (e.g., the primary risk driver in a region is legacy equipment), they must be indicated in the schematic. The electrical corporation must explain why those local conditions are part of the decision process (i.e., there should not be simply one box in the schematic that is labeled ‘local conditions,’ which is then connected to the rest of the process).” i. Provide the schematic as required by the WMP guidelines. If Liberty cannot produce the schematic at this time, explain why Liberty is unable to produce the schematic and provide a timeline with key milestones for when Liberty will be able to produce the schematic | a. i. Refer to Figure 6-1 of Liberty’s 2027 WMP for a schematic that shows Liberty’s risk informed decision-making process. Quantitative risk assessment is a component of Steps 1-5. Resource allocation, evaluation of other plan objectives (e.g., cost, timing), and SME judgement are components of Steps 6-7. Liberty provides an updated schematic below to specify these components of each step in the Figure 6-1 schematic. (See column M) | Jessica McHale | 2026-09-16 | 2026-09-21 | 2026-09-21 | LU Response to DR OEIS-P-WMP_2026-Liberty-003.pdf | 0 | - | No | 6 | Wildfire Mitigation Strategy Development | Initiative Activity Prioritization
3 | OEIS | 3 | OEIS-P-WMP_2026-Liberty-003 | 5 | OEIS-003-Q05 | Q05. Regarding Figure 6-3: Waterfall Diagram of Liberty’s Risk Model: a. On page 133 of its 2027 Base WMP, Liberty provides Figure 6-3: Waterfall Diagram of Liberty’s Risk Model. i. Explain how Liberty calculated the 16M risk reduction for Overhead Hardening Mitigation. 1. Identify which Overhead Hardening Mitigation activities were included in this total and which were not. 2. Identify the time range of implementation for the activities included in this risk reduction total. 3. Provide any relevant calculations or datasets. ii. Explain how Liberty calculated the 569M risk reduction for PEDS/PSPS Mitigation. 1. Explain how Liberty calculated and considered the joint effectiveness of these two mitigation activities. iii. Explain how Liberty calculated the 109M risk for PSPS Risk. iv. Liberty states, “The risk reduction modeled by ‘CC or UG Mitigation’ assumes all circuits with a BCR greater than or equal to one are hardened.” Does the 72M risk reduction for CC or UG Mitigation assume Covered Conductor is applied to all circuits with a BCR greater than or equal to one? Provide an explanation for this assumption. | a. i. Liberty calculates the $16M in risk reduction for overhead hardening without covered conductor in a similar manner as it calculates the risk reduction for undergrounding and overhead hardening with covered conductor. Refer to LU Table 6-1 for the mitigation effectiveness parameter. As described in the table, the mitigation effectiveness parameter applies to asset-related outages. For each applicable circuit (see below), Liberty calculates the risk reduction by reducing outage and ignition rates, accounting for the proportion of asset-related outages relative to other outage types. 1. Overhead hardening without covered conductor includes replacement of at-risk poles and hardware, and may include wider crossarms, shorter spans, new conductor, and upgraded brackets, insulators, fuses, and arrestors. 2. The time range includes 2022 through 2025. 3. See attachment: “DR-003-Q05a.i.3 Response.” ii. Liberty estimates the risk reduction associated with PEDS and PSPS using the mitigation effectiveness parameters listed in LU Table 6-1. The risk reduction is calculated by multiplying wildfire risk by the mitigation effectiveness parameter. For example, if initial wildfire risk is $100M, then residual risk after PEDS/PSPS is $100M * (1-X) * (1-Y), where X and Y represent mitigation effectiveness parameters in LU Table 6-1. Whether X or Y is applied first yields the same residual risk (idempotent). 1. Liberty does not consider the joint effectiveness of PSPS and PEDS. When a PSPS event occurs, Liberty does not credit SRP/PEDS with risk reduction. When SRP is enabled, Liberty does not credit PSPS with a risk reduction. iii. Liberty provides a detailed set of equations to calculate PSPS risk in WMP Section 5.2. This includes multiplying PSPS likelihood by PSPS consequence. PSPS likelihood is modeled using a 17-hour duration and circuit-level customer counts. PSPS consequence includes reliability impacts, valued using the Berkeley Lab ICE calculator. Please refer to the PSPS likelihood section (page 55) and the PSPS consequence section (pages 63-65, and page 67). Equations are provided in the cited sections alongside parameter values. iv. The risk reduction assumes all covered conductor projects with a BCR greater than one are deployed. The basis for the assumption is conventional benefit-cost methodology that investments are efficient when the expected benefits exceed the expected costs. In practice, quantifying benefits and costs is inherently challenging, especially in a setting like wildfire risk where risk is concentrated in the extreme tail of the distribution. Showing the residual risk when all covered conductor projects with BCRs greater than one is informative for planning purposes to visualize potential residual risk once covered conductor projects are deployed. Throughout Section 6 of the 2027 Base WMP, Liberty presents analysis and provides discussion on the practical nature of completing all modeled projects (please refer to Figure 6-2). | Jessica McHale | 2026-09-16 | 2026-09-21 | 2026-09-21 | LU Response to DR OEIS-P-WMP_2026-Liberty-003.pdf | 1 | https://california.libertyutilities.com/uploads/WMP%20Data%20Requests/DR-003-Q05a.i.3%20Response.zip | No | 6 | Wildfire Mitigation Strategy Development | Projected Overall Risk Reduction
4 | OEIS | 4 | OEIS-P-WMP_2026-Liberty-004 | 1 | OEIS-004-Q01 | Q01. Regarding Infrared Inspections: On page 45 of Appendix D in its 2027 Base WMP,1 Liberty states that it included infrared inspections of transformers, reclosers, and capacitor banks as part of its drone inspections in 2026. a. When reviewing drone inspection data, how does Liberty distinguish between infrared and non-infrared drone inspections and inspection findings? b. Describe the infrared inspection scheduling process, and all factors Liberty considers when scheduling drone inspections. | a. In Fulcrum, the Red Green Blue (“RGB”) imagery inspection is labeled as an Advanced Inspection and the infrared inspection is recorded as an Infrared Inspection. They are inspections that are performed separately. Both are performed with drones. As part of the Infrared Inspection, Libety captures both infrared and RGB imagery on structures with transformers, reclosers, and capacitor banks. Within the HFTD-3 zone, there are zero capacitor banks. Therefore, infrared inspection was only performed on transformers and reclosers. If there were capacitor banks within HFTD-3, then infrared inspection would have also been performed on those assets as well. The infrared and RGB shots are paired shots to give the inspector the physical context to identify which component a thermal signature belongs to. The inspector utilizes the thermal temperature bands, documented in Liberty’s Drone Inspection Program Manual, to determine priority levels of any concerns. Infrared and paired RGB files are uploaded to the thermal imagery path on the Liberty SharePoint for processing, and results are entered in Fulcurm as Pass or Fail with site conditions recorded. b. Asset data is first pulled from GIS to determine how many transformers, reclosers, and capacitor banks are in scope for the inspection the year. Because assets may be added or removed throughout the year, new data must be pulled each year. Further, if Fulcrum is missing certain assets, when they are found as part of the inspection, they are added to Fulcrum as part of the inspection to ensure a complete inspection of assets. Because the service territoy sits at higher elevations, weather and seasonality guide when the inpsections can be performed. For 2026, Liberty performed the inspections July through early September. For future years, Liberty plans to perform the drone inspections earlier in the year (closer to May and June) to be further ahead of peak fire season. FAA approval is required within the area of the Lake Tahoe Airport, and some assets are non-LANNC enabled so additional authorization is required. To enable the inspections, Liberty aims to submit for authorization at least 90 days, peferable 120 days, in advance. Daily, scope is reviewed - covering completed inspection, remaining inspection, production rates, and the forecast against the planned completion date. Forecast review and crew planning happen a week ahead. When there is downtime in the field, it is backfilled with door hanger placement and data packaging. Lastly, in scheudling inspections, Liberty also considers special events in the Tahoe area. For instance, for the 2026 inspections, Liberty deferred the start of the inspections one week until after the American Century Championship golf tournament which occurs the first two weeks of July. | Jessica McHale | 2026-09-16 | 2026-09-23 | 2026-09-23 | LU Response to DR OEIS-P-WMP_2026-Liberty-004.pdf | 0 | - | No | Appendix D | Critical Issues and Areas of Continued Improvement | Distribution Detailed Inspection Frequency
4 | OEIS | 4 | OEIS-P-WMP_2026-Liberty-004 | 2 | OEIS-004-Q02 | Q02. Regarding Hobart Mills and Stampede Substations: On page 182 of its 2027 Base WMP, Liberty states that Hobart Mills and Stampede substations are inspected annually, while its other 10 substations are inspected quarterly. a. Explain why the Hobart Mills and Stampede substations are inspected less frequently. | a. Hobart Mills and Stampede substations are located in more remote locations without paved road access. Weather conditions makes access challenging. Liberty aims to inspect these substations quarterly but weather conditions may result in an inspection once a year. At a minimum, Liberty will inspect at least once a year. Historically, if weather and access are not an issue, Liberty has inspected these substations more frequently in a year. For emegencies when access is challenging, Liberty has utilized snowcat, snowmobile, and helicopter for access. | Jessica McHale | 2026-09-16 | 2026-09-23 | 2026-09-23 | LU Response to DR OEIS-P-WMP_2026-Liberty-004.pdf | 0 | - | No | 8 | Grid Design, Operatoins, and Maintenance | Substation Inspections
4 | OEIS | 4 | OEIS-P-WMP_2026-Liberty-004 | 3 | OEIS-004-Q03 | Q03. Regarding Asset Inventory Database: a. On page 191 of Liberty’s 2027 Base WMP, Liberty states that it does not record failures by equipment type and it does not have an exact count of all listed assets, such as connectors or splices, in the field. i. What equipment components does Liberty track in its asset inventory database? (E.g., transformers, reclosers, switches.) ii. What equipment components does Liberty not track in its asset inventory database? (E.g., splices, bolts, brackets.) iii. Provide an explanation for why Liberty does not currently record equipment failures by equipment type, and a brief description of the steps Liberty is taking to begin tracking equipment failures by equipment type. b. Provide asset inventories for four distribution poles in Liberty’s HFTD Tier 3, and photographs of each pole from its 2026 drone inspection. In total, the four poles must include at least one of each of the following components: i. Transformer ii. Recloser iii. Capacitor bank iv. Down guy | a. i. Equipment components Liberty tracks in its asset inventory database include: transformers, wire, cable, reclosers, switches, regulators, capacitors, circuit breakers, fuses, and fault indicators. ii. Equipment components Liberty does not track include: splices, bolts, brackets, or connectors. iii. Liberty has developed a “Components” field in the Outage Management System which tracks components involved in outages. A reference document has been created to aid Dispatchers and Operators to document the incident resolution details in the OMS. Daily reviews of the historical incidents are performed to improve accuracy of data. b. Refer to supporting materials: “LU-DR-004-Q03.b Response.xlsx” for asset inventories and LU-DR-004-Q03.b Response.pdf” for photos. There are no poles with capacitor banks in Liberty’s HFTD Tier 3. i. 131598, MEY3500, Pole - Transformer ii. 300700, MEY3500, Pole - Transformer iii. 301047, MEY3500, Pole - Recloser iv. 146363, MEY3500, Pole – Down Guy | Jessica McHale | 2026-09-16 | 2026-09-23 | 2026-09-23 | LU Response to DR OEIS-P-WMP_2026-Liberty-004.pdf | 2 | https://california.libertyutilities.com/uploads/WMP%20Data%20Requests/LU-DR-004-Q03.b%20Response.xlsx https://california.libertyutilities.com/uploads/WMP%20Data%20Requests/LU-DR-004-Q03.b%20Response.pdf | No | 8 | Grid Design, Operatoins, and Maintenance | Equipment Maintenance and Repair
4 | OEIS | 4 | OEIS-P-WMP_2026-Liberty-004 | 4 | OEIS-004-Q04 | Q04. Regarding Multi-Sensor Program: On page 273 of its 2027 Base WMP, Liberty states that “…in 2026, Liberty plans to deploy GridScope multi-sensor units as part of a new EFD program to identify abnormal conditions on overhead electric infrastructure. Liberty will install 1,000 of the sensors…” a. Provide a summary of the GridScope implementation process, including, but not limited to: i. How many devices have been installed to date ii. The feasibility of achieving the goal of 1,000 units by the end of 2026 iii. Expected delays or issues b. Provide the name of each circuit where Liberty plans to install multi-sensors, the number of units planned for installation, and the estimated percent monitoring coverage for each circuit in the following format: Circut, Number of Units Installed, Estimated Percent Monitoring Coverage (span length / circuit length) i. If there are limitations in estimating the monitoring coverage of the sensors, state the reasoning accordingly. | a. i. Zero devices have been installed to date. ii. Deploying 1,000 units by year end is feasible. At this time, Liberty is working with the vendor to finalize the contract. If the vendor contract is finalized, most of the installations should be completed by the end of the year, with some installations to occur in 2027. iii. Liberty and the vendor are reviewing contract terms. Weather, network, cell coverage, and other connectivity issues may delay installations. b. See below for the requested table. Liberty notes that the following table does not list planned locations. Rather, it lists locations that Liberty has provided to the vendor for scoping purposes. Final locations will be determined following review of the feasibility study conducted by the vendor. The table includes more than 1,000 units in the event that some scoped locations are not feasible (for reasons such as connectivity or network limitations). (See column M) | Jessica McHale | 2026-09-16 | 2026-09-23 | 2026-09-23 | LU Response to DR OEIS-P-WMP_2026-Liberty-004.pdf | 0 | - | No | 10 | Situational Awareness and Forecasting | Grid Monitoring Systems
5 | OEIS | 5 | OEIS-P-WMP_2026-Liberty-005 | 1 | OEIS-005-Q01 | Q01. Regarding Liberty’s outage data set: In Liberty’s response to Data Request OEIS-P-WMP_2026-Liberty-002, Question 2, Liberty states that the “initial dataset of outage records 3,473 outages.” On page 46 of its 2027 Base WMP,1 Liberty states that “Liberty drops planned outages, outages resulting from loss of supply from NV Energy, and remaining outages with unknown causes from the dataset.” a. Provide the number of outages that were removed from the outage dataset related to planned outages. b. Provide the number of outages that were removed from the outage dataset related to loss of supply from NV Energy. c. Provide the number of outages that were removed from the outage dataset related to unknown causes. | 1. a. 1,950 b. 230 c. 79 | Jessica McHale | 2026-09-22 | 2026-09-25 | 2026-09-25 | LU Response to DR No. OEIS-P-WMP_2026-Liberty-005.pdf | 0 | - | No | 5 | Risk Methodology and Assessment | Risk and Risk Components Calculation
5 | OEIS | 5 | OEIS-P-WMP_2026-Liberty-005 | 2 | OEIS-005-Q02 | Q02. Regarding PSPS likelihood: On page 55 of Liberty’s 2027 Base WMP, Liberty states the following: “Liberty’s current risk model incorporates PSPS likelihood by modeling an expected number of PSPS events per circuit per year. This expression of expected PSPS events per year is differentiated coarsely by each circuit’s estimated wildfire risk: the top ten highest risk circuits in terms of aggregate risk receive a likelihood value of 1.0 PSPS events per year and the remaining circuits receive a likelihood value of 0.5 PSPS events per year.” a. How did Liberty determine the likelihood values of 1.0 and 0.5? b. How did Liberty determine the threshold of using the top ten highest risk circuits? c. Provide a list of the total number of PSPS events that Liberty has historically implemented, broken out by circuit. | a. Liberty’s risk model adopts a value of one PSPS event per year for high-risk circuits and one PSPS event every two years for lower risk circuits. This approach was adopted as a coarse approximation of PSPS likelihood, and it was selected over initial draft versions of the PSPS likelihood model that relied on one PSPS event per year for all circuits. Liberty found this assumption did not reflect the historical distribution of PSPS activity, which has focused on two circuits in the southern portion of Liberty’s service territory (see answer to part c below). Liberty built a tiered structure into the model so that PSPS likelihood would not be specified uniformly across all of Liberty’s service territory. Liberty considers this tiering a reasonable approach, but not a final result of Liberty’s risk model. Liberty has identified moving to a probabilistic, zone-specific PSPS likelihood model as a high priority in its risk assessment improvement plan. Considering the impacts of climate change on future fuel moisture and drought conditions, one PSPS event per year on the highest risk circuits could be an underestimate of PSPS likelihood over the multi-decade planning horizon of grid hardening investments. For example, academic research has projected that an increase in abnormally dry autumn fuel conditions may lead to a greater share of the population exposed to PSPS events in California.2 Liberty has identified in its risk assessment improvement plan that linking projections of climate change to PSPS likelihood is a high priority opportunity item. b. Liberty selected the top ten circuits by aggregate risk as the initial high-risk tier because Liberty’s historical PSPS activity has been concentrated on a small subset of highest-risk circuits. Liberty expanded the selection to ten circuits because Liberty does not believe it is appropriate to only estimate PSPS risk on the two circuits that have been subject to historical PSPS conditions. Indeed, this wildfire season additional circuits have been considered in the scope of potential PSPS events. The ten highest risk circuits were selected as an initial baseline of PSPS likelihood, while Liberty refines its PSPS likelihood to a zone-specific PSPS likelihood model as described in the risk assessment improvement plan. c. See the table below. (See column M) | Jessica McHale | 2026-09-22 | 2026-09-25 | 2026-09-25 | LU Response to DR No. OEIS-P-WMP_2026-Liberty-005.pdf | 0 | - | No | 5 | Risk Methodology and Assessment | Risk and Risk Components Calculation
6 | OEIS | 6 | OEIS-P-WMP_2026-Liberty-006 | 1 | OEIS-006-Q01 | Q01. Regarding PSPS Notifications: In Table 11-9 on page 320 of Liberty’s 2027 Base WMP,1 Liberty states that PSPS notifications are transmitted in English, with a Spanish line directing customers to additional information “to the extent possible.” a. Explain what is meant by “to the extent possible” as well as Liberty’s process for language selection, delivery verification, and follow-up with regard to PSPS notifications. b. Explain how essential warning, timing, service restoration and community resource center information reaches customers who cannot access translated web content. | a. Liberty communicates a potential PSPS directly to its customers in two ways: 1. E-mail. An email to potentially impacted customers. This email also includes the same communication in Spanish. In addition, there are links to documents in 5 other languages (French, Dutch, Chinese, Vietnamese, and Tagalog). These languages were selected to support the diverse customer populations within and around Liberty's service territory and to expand access to critical safety information for customers with limited English proficiency. This email communication is distributed once , at the time Liberty identifies a potential PSPS. Impacted customers will continue to receive updates about the potential PSPS event and/or PSPS event through OnSolve and access to real time updates on Liberty’s webpage. 2. OnSolve. OnSolve communications to impacted customers. Through the OnSolve platform, impacted customers will receive a phone call, email, and/or text message regarding the potential PSPS. This method of communication is used throughout the possible PSPS event. “To the extent possible” recognizes that certain communication channels, particularly SMS/text messages delivered through the OnSolve platform, are subject to character limitations and other technical constraints that may limit the amount of translated content that can be included within the message itself. Consistent with these limitations, Liberty strives to provide translated information through all available communication channels and directs customers to additional translated resources whenever full translations cannot be embedded in the notification. b. As stated above, all impacted customers receive an email in English and Spanish and links to the message in five (5) other languages. In addition, the PSPS Updates webpage link is included in all customer updates. There, customers can also view a Spanish translation of the content on the webpage. Lastly, Liberty engages with CBOs. Prior to a potential PSPS event, the AFN Coordinator will engage with CBOs that serve the impacted area through various means, including email, phone calls, text messages, and WhatsApp messaging with the goal of working with the CBOs to reach as many impacted customers as possible, and in particular, those who may not be able to access translated web content. | Jessica McHale | 2026-10-02 | 2026-10-07 | 2026-10-07 | LU Response to DR No. OEIS-P-WMP_2026-Liberty-006.pdf | 0 | - | No | 11 | Emergency Preparedness, Collaboration, and Public Awareness | Public Communication, Outreach, and Education Awareness
6 | OEIS | 6 | OEIS-P-WMP_2026-Liberty-006 | 2 | OEIS-006-Q02 | Q02. Regarding Data Disposal: On page 343 of Liberty’s 2027 Base WMP, Liberty states that its formal data disposal policy will not be created until the ten-year mark of its retained inspection data is reached. a. Provide a plan outlining how Liberty intends to protect, isolate, and secure undisposed data once its mandated retention periods have concluded. For example, how Liberty is going to address the access controls, encryption standards, and monitoring protocols applied to this post-retention data while it awaits formal disposal. b. Explain why waiting until the end of the ten-year mark to create a formal disposal policy would not cause cybersecurity risks. | a. Liberty will protect and secure any undisposed data in its SQL Server database in an isolated archive. This archive will have the same access controls, encryption standards, and monitoring protocols as current data which has not yet reached its retention period. The SQL server resides in a Liberty controlled data center. Liberty has a mature cybersecurity practice which is regularly tested and which provides ongoing data confidentiality, integrity, and accessibility with properly layered cybersecurity controls. b. Waiting until Liberty reaches the ten-year retention milestone to finalize a formal disposal policy does not create a cybersecurity risk because the data remains protected throughout its lifecycle under Liberty's established cybersecurity and information governance controls. The risk associated with data retention is not driven by the existence of a disposal policy itself, but by whether the retained information is adequately secured. Liberty's archived inspection data will remain subject to the same access controls, encryption, monitoring, and administrative safeguards that protect active records. All retained records continue to be maintained pursuant to applicable regulatory retention requirements. | Jessica McHale | 2026-10-02 | 2026-10-07 | 2026-10-07 | LU Response to DR No. OEIS-P-WMP_2026-Liberty-006.pdf | 0 | - | No | 12 | Enterprise Systems | Summary of Enterprise Systems
7 | OEIS | 7 | OEIS-P-WMP_2026-Liberty-007 | 1 | OEIS-007-Q01 | On page 164 of its 2027 Base WMP,1 Liberty states that “poles are identified for replacement or repair through routine patrol and detailed inspections performed in accordance with G.O. 165, drone inspections, and Liberty’s Intrusive Pole Inspection Program […] In addition to condition-based replacements, Liberty may proactively replace poles as part of wildfire mitigation projects, including overhead hardening with or without covered conductor.” a. Provide a disaggregation of the target of 300 distribution pole replacements into the following four categories, providing an estimate number of poles in each category. i. Condition-based pole replacements identified through inspections, excluding replacements included in categories ii-iv below. ii. Pole replacements performed as part of overhead hardening projects that do not include covered conductor installation. iii. Pole replacements performed as part of covered conductor projects. iv. Other pole replacements not included in categories i–iii. Describe the activities or reasons for replacement included in this category. b. If Liberty is unable to estimate the allocation among these categories, explain why. | a. i. 300 ii. 0 iii. 0 iv. 0 b. N/A | Jessica McHale | 2026-10-07 | 2026-10-12 | 2026-10-12 | LU Response to DR No. OEIS-P-WMP_2026-Liberty-007.pdf | 0 | - | No | 8 | Grid Design, Operations, and Maintenance | Grid Design and System Hardening
8 | OEIS | 8 | OEIS-P-WMP_2026-Liberty-008 | 1 | OEIS-008-Q01 | Q01. Regarding Risk Values: In Liberty’s 2027 Base WMP,1 for Table 5-5 (p. 94), LU Table 5-6 (p. 95), and Table 6-1 (p. 113), Liberty provides only whole numbers for the percentage of risk and overhead miles values. a. Are these values limited based on rounding or use of significant figures? i. If so, explain Liberty’s procedures and assumptions that impact its rounding or use of significant figures in reporting its risk values. |  | Jessica McHale | 2026-10-13 | 2026-10-16 | [5 empty] | 5, 6 | Risk Methodology and Assessment, Wildfire Mitigation Strategy Development | Top Risk Areas within the HFRA, Risk Evaluation
8 | OEIS | 8 | OEIS-P-WMP_2026-Liberty-008 | 2 | OEIS-008-Q02 | Q02. Regarding Unknown Outage Causes: In response to OEIS Data Request 5 Question 1,2 Liberty states that 79 outages out of the 3,473 within the outage dataset were excluded due to being “unknown” causes. In Table 3-1 on page 23 of its 2027 Base WMP, Liberty includes 10.53% of ignitions in the HFTD with an “Unknown” risk and risk driver, and 5.26% of ignitions within the HFTD with an “Unknown” risk driver under contact from object. a. Provide the number of unknown ignitions used to calculate the percentages in Table 3-1. b. On page 21 of its 2027 Base WMP, Liberty states that the prioritization of risk drivers is also based on “outage data from January 2022 through December 2025” in order to “supplement the dataset for prioritizing ignition risk.” How has this impacted the percentage of unknown values? c. Provide the number of unknown ignitions from January 2022 to December 2025. d. Given that the outage data set is from January 2022 to December 2025, while the ignition reporting data is from 2014 to 2025, has Liberty seen a decrease in the number of unknown ignitions since 2014? e. How has Liberty worked to decrease the number of unknown ignitions across its service territory? |  | Jessica McHale | 2026-10-13 | 2026-10-16 | [5 empty] | 3 | Overview of Base WMP | Prioritized List of Wildfire Risks and Risk Drivers