HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 6.4744e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00038847
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.0053378
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.041e-09
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.041e-09
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.6369e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.2453e-06
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.8001e-09
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.8001e-09
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.6201e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.782e-06
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.3794e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.3794e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.2415e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.1319e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 8.082e-10
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 8.082e-10
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.2738e-09
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.2491e-06
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 3.5965e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 3.5965e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 3.2368e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 5.5584e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 1.4676e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.4676e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 1.3209e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 2.2682e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.5246e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 1.5246e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 1.3721e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 2.3562e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 9.8875e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 9.8875e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 8.8988e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.00015281
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.9948e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 1.9948e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 1.7953e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 3.0829e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.7266e-09
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.7266e-09
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 1.5539e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 2.6685e-06
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 8.5173e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 8.5173e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 7.6656e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.00013163
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.022e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.6029e-09
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.1617e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 7.0926e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.0147e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 5.7353e-09
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.4412e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.7284e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.9106e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 4.1581e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.4948e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.4281e-06
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.0037e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.4338e-09
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 8.6029e-09
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.1821e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 5.9217e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 8.4595e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 5.0757e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 6.9744e-06
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 2.2081e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | dead | 3.1544e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | dead | 1.8926e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | dead | 2.6006e-06
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.7062e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 2.4375e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 1.4625e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 2.0096e-06
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 7.4272e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 1.061e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 6.3661e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 8.7475e-06
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.907e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 2.7242e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 1.6345e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 2.246e-06
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 2.0073e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 2.8676e-09
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | grow into | 1.7206e-08
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | grow into | 2.3642e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 1.0037e-06
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 1.4338e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 8.6029e-07
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 1.1821e-05
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 2.62e-05
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | animal contact | 7.4858e-06
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | animal contact | 0.00033686
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | animal contact | 0.034832
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 8.7335e-06
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 2.4953e-06
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | balloon contact | 0.00011229
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.011611
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 1.4556e-05
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 4.1588e-06
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00018715
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.019351
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 1.1645e-05
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 3.327e-06
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.00014972
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.015481
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contamination | contamination | 2.9112e-06
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Destructive Fires | contamination | contamination | 8.3176e-07
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Large Fires | contamination | contamination | 3.7429e-05
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Small Fires | contamination | contamination | 0.0038702
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 6.4746e-06
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 1.8499e-06
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 8.3245e-05
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.0086075
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.2949e-05
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 3.6998e-06
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00016649
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.017215
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 6.4746e-06
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 1.8499e-06
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 8.3245e-05
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.0086075
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | unknown | unknown | 8.7335e-06
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Destructive Fires | unknown | unknown | 2.4953e-06
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Large Fires | unknown | unknown | 0.00011229
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Small Fires | unknown | unknown | 0.011611
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0070461
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 1.4578
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0.0023487
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.48592
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.0039145
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.80986
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.0031316
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.64789
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contamination | contamination | 0.0007829
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.16197
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00075987
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.15721
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0015197
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.31442
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | transformer damage or failure | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | transformer damage or failure | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | transformer damage or failure | 0.00075987
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | transformer damage or failure | 0.15721
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 0
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0023487
non-HFTD - Transmission - 115 kV or Lower | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.48592
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 3.7845e-05
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Destructive Fires | contact from object | animal contact | 1.0813e-05
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Large Fires | contact from object | animal contact | 0.00048658
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Small Fires | contact from object | animal contact | 0.050312
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 8.7335e-06
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 2.4953e-06
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00011229
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.011611
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 2.0378e-05
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 5.8223e-06
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.000262
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Small Fires | contact from object | vehicle contact | 0.027091
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Catastrophic Fires | contamination | contamination | 2.9112e-06
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Destructive Fires | contamination | contamination | 8.3176e-07
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Large Fires | contamination | contamination | 3.7429e-05
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Small Fires | contamination | contamination | 0.0038702
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 1.9424e-05
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 5.5497e-06
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00024973
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.025823
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 6.4746e-06
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 1.8499e-06
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 8.3245e-05
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.0086075
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 6.4746e-06
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 1.8499e-06
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 8.3245e-05
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0086075
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 6.4746e-06
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 1.8499e-06
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 8.3245e-05
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0086075
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 6.4746e-06
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.8499e-06
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 8.3245e-05
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.0086075
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Catastrophic Fires | unknown | unknown | 2.9112e-06
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Destructive Fires | unknown | unknown | 8.3176e-07
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Large Fires | unknown | unknown | 3.7429e-05
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Small Fires | unknown | unknown | 0.0038702
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.010178
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 2.1056
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.0023487
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.48592
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | contact from object | vehicle contact | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Destructive Fires | contact from object | vehicle contact | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Large Fires | contact from object | vehicle contact | 0.0054803
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Small Fires | contact from object | vehicle contact | 1.1338
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Large Fires | contamination | contamination | 0.0007829
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.16197
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0022796
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.47162
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | crossarm damage or failure | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | crossarm damage or failure | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | crossarm damage or failure | 0.00075987
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | crossarm damage or failure | 0.15721
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00075987
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.15721
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00075987
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.15721
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00075987
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.15721
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 0
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0007829
non-HFTD - Transmission - 60/70 kV | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.16197
non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | contamination | contamination | 2.9112e-06
non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Destructive Fires | contamination | contamination | 8.3176e-07
non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Large Fires | contamination | contamination | 3.7429e-05
non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Small Fires | contamination | contamination | 0.0038702
non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 6.4746e-06
non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 1.8499e-06
non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 8.3245e-05
non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0086075
non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 2.9112e-06
non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 8.3176e-07
non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 3.7429e-05
non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.0038702
non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | contamination | contamination | 0
non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | contamination | contamination | 0
non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Large Fires | contamination | contamination | 0.0007829
non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Small Fires | contamination | contamination | 0.16197
non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0
non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0
non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00075987
non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.15721
non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0
non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 0
non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0.0007829
non-HFTD - Transmission - 230 kV or Higher | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.16197
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.0034676
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.0011928
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 3.3894e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00049537
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.0001704
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | animal contact | 4.842e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | animal contact | 0.0029722
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | animal contact | 0.0010224
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | animal contact | 2.9052e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | animal contact | 0.040841
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | animal contact | 0.014049
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | animal contact | 3.992e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0.00028897
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 9.9402e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 2.8245e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 4.1281e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 1.42e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 4.035e-08
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | balloon contact | 0.00024769
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | balloon contact | 8.5202e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | balloon contact | 2.421e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0034034
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0011707
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | balloon contact | 3.3266e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.0008669
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.00029821
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 8.4735e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0.00012384
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 4.2601e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 1.2105e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00074306
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00025561
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Large Fires | contact from object | other contact from object | 7.263e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.01021
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0035122
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Small Fires | contact from object | other contact from object | 9.9799e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.0024819
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00085374
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 2.4259e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00035455
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00012196
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 3.4656e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0021273
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00073178
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 2.0793e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.029231
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.010055
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 2.8572e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0016546
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00056916
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.6173e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00023637
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 8.1309e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 2.3104e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0014182
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00048785
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 1.3862e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.019487
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0067035
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 1.9048e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.0024819
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00085374
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 2.4259e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00035455
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00012196
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 3.4656e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0021273
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00073178
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 2.0793e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.029231
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.010055
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 2.8572e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.00028897
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | unknown | unknown | 9.9402e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | unknown | unknown | 2.8245e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | unknown | unknown | 4.1281e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | unknown | unknown | 1.42e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Destructive Fires | unknown | unknown | 4.035e-08
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | unknown | unknown | 0.00024769
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | unknown | unknown | 8.5202e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Large Fires | unknown | unknown | 2.421e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | unknown | unknown | 0.0034034
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | unknown | unknown | 0.0011707
HFTD - Transmission - Zone 1 - 115 kV or Lower | Red Flag Warning - Small Fires | unknown | unknown | 3.3266e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.00092467
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.00031808
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 9.0382e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00092467
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00031808
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 9.0382e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.008322
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0028627
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 8.1343e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 1.4291
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.49159
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.0013968
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 7.7056e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 2.6507e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 7.5318e-08
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 7.7056e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 2.6507e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 7.5318e-08
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0.0006935
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0.00023856
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 6.7786e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.11909
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.040966
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0001164
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.00023117
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 7.952e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 2.2595e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0.00023117
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 7.952e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 2.2595e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.0020805
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00071568
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 2.0336e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.35727
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.1229
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.00034921
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00021687
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 7.4602e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 2.1198e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00021687
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 7.4602e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 2.1198e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0019518
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00067142
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 1.9078e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.33518
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.1153
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.00032762
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00014458
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 4.9735e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.4132e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00014458
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 4.9735e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 1.4132e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0013012
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00044761
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 1.2719e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.22345
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.076865
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00021841
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00021687
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 7.4602e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 2.1198e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00021687
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 7.4602e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 2.1198e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0019518
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00067142
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 1.9078e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.33518
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.1153
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.00032762
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 7.7056e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 2.6507e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 7.5318e-08
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 7.7056e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 2.6507e-05
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 7.5318e-08
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0006935
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00023856
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Large Fires | unknown | unknown | 6.7786e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.11909
HFTD - Transmission - Tier 3 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.040966
HFTD - Transmission - Zone 1 - 115 kV or Lower | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.0001164
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 0.00029473
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 9.3401e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 5.1927e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 4.2104e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 1.3343e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Destructive Fires | contact from object | balloon contact | 7.4181e-08
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | contact from object | balloon contact | 0.00025263
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | contact from object | balloon contact | 8.0058e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Large Fires | contact from object | balloon contact | 4.4509e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0034713
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | contact from object | balloon contact | 0.0011001
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Small Fires | contact from object | balloon contact | 6.1158e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.00029473
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 9.3401e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 5.1927e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 4.2104e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 1.3343e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 7.4181e-08
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00025263
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | contact from object | other contact from object | 8.0058e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Large Fires | contact from object | other contact from object | 4.4509e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0034713
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0011001
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Small Fires | contact from object | other contact from object | 6.1158e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00084379
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.0002674
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 1.4866e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00012054
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 3.82e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 2.1237e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00072325
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0002292
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 1.2742e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.009938
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.0031494
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 1.7509e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.0016876
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.0005348
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 2.9732e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00024108
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 7.64e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 4.2475e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0014465
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0004584
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 2.5485e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.019876
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0062987
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 3.5018e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.00058946
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.0001868
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | unknown | unknown | 1.0385e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | unknown | unknown | 8.4209e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | unknown | unknown | 2.6686e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Destructive Fires | unknown | unknown | 1.4836e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | unknown | unknown | 0.00050525
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | unknown | unknown | 0.00016012
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Large Fires | unknown | unknown | 8.9017e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | unknown | unknown | 0.0069426
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | unknown | unknown | 0.0022001
HFTD - Transmission - Zone 1 - 230 kV or Higher | Red Flag Warning - Small Fires | unknown | unknown | 1.2232e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 7.8593e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 2.4906e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | contact from object | balloon contact | 1.3847e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 7.8593e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 2.4906e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | contact from object | balloon contact | 1.3847e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0.00070734
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 0.00022416
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | contact from object | balloon contact | 1.2462e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.12147
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.038493
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | contact from object | balloon contact | 0.000214
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 7.8593e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 2.4906e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 1.3847e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 7.8593e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 2.4906e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 1.3847e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00070734
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00022416
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 1.2462e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.12147
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.038493
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.000214
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 7.3733e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 2.3366e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 1.299e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 7.3733e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 2.3366e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 1.299e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00066359
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00021029
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 1.1691e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.11395
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.036112
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.00020077
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00014747
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 4.6732e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 2.5981e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00014747
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 4.6732e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 2.5981e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0013272
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00042059
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 2.3383e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.22791
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.072225
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.00040154
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 0.00015719
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 4.9813e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Catastrophic Fires | unknown | unknown | 2.7694e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 0.00015719
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 4.9813e-05
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Destructive Fires | unknown | unknown | 2.7694e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.0014147
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | unknown | unknown | 0.00044831
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Large Fires | unknown | unknown | 2.4924e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.24293
HFTD - Transmission - Tier 3 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.076985
HFTD - Transmission - Zone 1 - 230 kV or Higher | Non-Red Flag Warning - Small Fires | unknown | unknown | 0.000428
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.0039895
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.0010579
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 5.0588e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00056992
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00015113
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | contact from object | animal contact | 7.2269e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | contact from object | animal contact | 0.0034195
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | contact from object | animal contact | 0.00090681
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | contact from object | animal contact | 4.3361e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | contact from object | animal contact | 0.046987
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | contact from object | animal contact | 0.01246
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | contact from object | animal contact | 5.9582e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.00092065
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.00024414
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 1.1674e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0.00013152
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 3.4877e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | contact from object | other contact from object | 1.6677e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00078913
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00020926
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | contact from object | other contact from object | 1.0006e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.010843
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | contact from object | other contact from object | 0.0028754
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | contact from object | other contact from object | 1.375e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.0026357
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00069895
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 3.3422e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00037653
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 9.985e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 4.7746e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0022592
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0005991
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 2.8648e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.031043
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.0082321
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 3.9364e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.00087858
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 0.00023298
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 1.1141e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 0.00012551
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 3.3283e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 1.5915e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00075307
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.0001997
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 9.5492e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.010348
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.002744
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 1.3121e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0017572
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00046597
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 2.2281e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00025102
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 6.6567e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 3.1831e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0015061
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0003994
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 1.9098e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.020695
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0054881
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 2.6243e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.0017572
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00046597
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 2.2281e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00025102
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 6.6567e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 3.1831e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0015061
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0003994
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 1.9098e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.020695
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.0054881
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 2.6243e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.00087858
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 0.00023298
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 1.1141e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 0.00012551
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 3.3283e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 1.5915e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00075307
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.0001997
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 9.5492e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.010348
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.002744
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 1.3121e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | other | all other | 0.00030688
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | other | all other | 8.138e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | other | all other | 3.8914e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | other | all other | 4.384e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | other | all other | 1.1626e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | other | all other | 5.5591e-08
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | other | all other | 0.00026304
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | other | all other | 6.9754e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | other | all other | 3.3355e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | other | all other | 0.0036144
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | other | all other | 0.00095848
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | other | all other | 4.5832e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 0.00030688
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 8.138e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 3.8914e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 4.384e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 1.1626e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 5.5591e-08
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0.00026304
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 6.9754e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 3.3355e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.0036144
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.00095848
HFTD - Transmission - Zone 1 - 60/70 kV | Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 4.5832e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.0010638
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 0.00028211
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | contact from object | animal contact | 1.349e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.0010638
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 0.00028211
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | contact from object | animal contact | 1.349e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.0095745
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 0.002539
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | contact from object | animal contact | 1.2141e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 1.6441
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.436
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | contact from object | animal contact | 0.0020849
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 0.0002455
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 6.5102e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | contact from object | other contact from object | 3.113e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 0.0002455
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 6.5102e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | contact from object | other contact from object | 3.113e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.0022095
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 0.00058592
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | contact from object | other contact from object | 2.8017e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.37942
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.10062
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | contact from object | other contact from object | 0.00048112
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 0.00023032
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 6.1076e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | conductor damage or failure | 2.9205e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 0.00023032
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 6.1076e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | conductor damage or failure | 2.9205e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.0020729
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 0.00054969
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | conductor damage or failure | 2.6285e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.35596
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.094394
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | conductor damage or failure | 0.00045137
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 7.6773e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 2.0359e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | connection device damage or failure | 9.7351e-08
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 7.6773e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 2.0359e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | connection device damage or failure | 9.7351e-08
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00069095
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 0.00018323
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | connection device damage or failure | 8.7616e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.11865
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.031465
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | connection device damage or failure | 0.00015046
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00015355
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 4.0718e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | insulator and brushing damage or failure | 1.947e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00015355
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 4.0718e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | insulator and brushing damage or failure | 1.947e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.0013819
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00036646
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | insulator and brushing damage or failure | 1.7523e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.2373
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.062929
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | insulator and brushing damage or failure | 0.00030091
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0.00015355
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 4.0718e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 1.947e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0.00015355
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 4.0718e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 1.947e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0013819
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00036646
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 1.7523e-06
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.2373
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.062929
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.00030091
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 7.6773e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 2.0359e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | pole damage or failure | 9.7351e-08
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 7.6773e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 2.0359e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | pole damage or failure | 9.7351e-08
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00069095
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 0.00018323
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | equipment / facility failure | pole damage or failure | 8.7616e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.11865
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.031465
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | equipment / facility failure | pole damage or failure | 0.00015046
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | other | all other | 8.1833e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | other | all other | 2.1701e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | other | all other | 1.0377e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | other | all other | 8.1833e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | other | all other | 2.1701e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | other | all other | 1.0377e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | other | all other | 0.0007365
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | other | all other | 0.00019531
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | other | all other | 9.3391e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | other | all other | 0.12647
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | other | all other | 0.033539
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | other | all other | 0.00016037
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 8.1833e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 2.1701e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Catastrophic Fires | vandalism / theft | vandalism / theft | 1.0377e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 8.1833e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 2.1701e-05
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Destructive Fires | vandalism / theft | vandalism / theft | 1.0377e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0.0007365
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 0.00019531
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Large Fires | vandalism / theft | vandalism / theft | 9.3391e-07
HFTD - Transmission - Tier 2 - 60/70 kV | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.12647
HFTD - Transmission - Tier 3 - 60/70 kV | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.033539
HFTD - Transmission - Zone 1 - 60/70 kV | Non-Red Flag Warning - Small Fires | vandalism / theft | vandalism / theft | 0.00016037
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.9552e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.5838e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.7931e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 7.9768e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.6759e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.7861e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00023028
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.5764e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.3035e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.7225e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.8621e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 5.3179e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.1173e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.1907e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00015352
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.3843e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 9.4501e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.6988e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.35e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.8554e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 8.1001e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.3133e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.001113
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00031786
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.2587e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 9.3063e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 4.6552e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.3295e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.7931e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.9768e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.838e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.0961e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00019226
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 5.4907e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 2.7466e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 7.8438e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00016479
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 4.7063e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.0022644
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.00064668
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 7.169e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 2.0474e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.0241e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | dead | 2.9248e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | dead | 6.1449e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | dead | 1.7549e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | dead | 0.00084435
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | dead | 0.00024114
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 5.5397e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.5821e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 7.9139e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 2.2601e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 4.7483e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 1.3561e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.00065246
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.00018633
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00024114
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 6.8866e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 3.4449e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 9.838e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00020669
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 5.9028e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.0028401
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.00081109
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 6.1914e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.7682e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 8.8449e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 2.526e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 5.307e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 1.5156e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.00072922
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.00020825
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 6.5173e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.8613e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 9.3104e-07
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 2.6589e-07
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | grow into | 5.5863e-06
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | grow into | 1.5954e-06
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | grow into | 7.6759e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | grow into | 2.1921e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.00032587
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 9.3063e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 4.6552e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 1.3295e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00027931
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 7.9768e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.003838
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.0010961
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.486e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.9096e-06
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 2.1229e-06
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.5851e-07
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.2737e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.3511e-06
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 0.00017502
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 4.6046e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 9.9066e-06
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.6064e-06
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.4152e-06
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.7234e-07
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 8.4914e-06
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.2341e-06
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0.00011668
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.0698e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 7.1823e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.8896e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.026e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.6995e-06
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 6.1563e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.6197e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00084592
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00022256
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.4767e-06
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.516e-07
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 3.5381e-07
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 9.3085e-08
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.1229e-06
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.5851e-07
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.917e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.6744e-06
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0.00014612
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 3.8444e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 2.0875e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 5.492e-06
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 0.00012525
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 3.2952e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.001721
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.00045279
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 5.4487e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 1.4335e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | dead | 7.7838e-06
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | dead | 2.0479e-06
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | dead | 4.6703e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | dead | 1.2287e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | dead | 0.00064173
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | dead | 0.00016884
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 4.2103e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 1.1077e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 6.0148e-06
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 1.5825e-06
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 3.6089e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 9.4947e-06
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.00049588
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 0.00013046
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0.00018327
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 4.8218e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 2.6182e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 6.8883e-06
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 0.00015709
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 4.133e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.0021585
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.0005679
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 4.7057e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 1.238e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 6.7224e-06
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 1.7686e-06
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 4.0334e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 1.0612e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.00055422
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 0.00014581
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 4.9533e-06
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 1.3032e-06
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 7.0762e-07
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.8617e-07
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | grow into | 4.2457e-06
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | grow into | 1.117e-06
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | grow into | 5.8339e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | grow into | 1.5349e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0.00024767
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 6.516e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 3.5381e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 9.3085e-06
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 0.00021229
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 5.5851e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.002917
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.00076744
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | Contact from object | other contact from object | 0.00036171
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | Contact from object | other contact from object | 0.0001033
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Catastrophic Fires | Contact from object | other contact from object | 0.00046096
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Destructive Fires | Contact from object | other contact from object | 5.1673e-05
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Destructive Fires | Contact from object | other contact from object | 1.4757e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Destructive Fires | Contact from object | other contact from object | 6.5852e-05
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Large Fires | Contact from object | other contact from object | 0.00031004
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Large Fires | Contact from object | other contact from object | 8.8542e-05
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Large Fires | Contact from object | other contact from object | 0.00039511
HFTD - Transmission - Tier 2 - 115 kV or Lower | Red Flag Warning - Small Fires | Contact from object | other contact from object | 0.0042602
HFTD - Transmission - Tier 2 - 230 kV or Higher | Red Flag Warning - Small Fires | Contact from object | other contact from object | 0.0012166
HFTD - Transmission - Tier 2 - 60/70 kV | Red Flag Warning - Small Fires | Contact from object | other contact from object | 0.0054291
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | Equipment / facility failure | other equipment / facility failure | 0.00041236
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | Equipment / facility failure | other equipment / facility failure | 0.00010849
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Catastrophic Fires | Equipment / facility failure | other equipment / facility failure | 0.00040512
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Destructive Fires | Equipment / facility failure | other equipment / facility failure | 5.8909e-05
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Destructive Fires | Equipment / facility failure | other equipment / facility failure | 1.5499e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Destructive Fires | Equipment / facility failure | other equipment / facility failure | 5.7874e-05
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Large Fires | Equipment / facility failure | other equipment / facility failure | 0.00035346
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Large Fires | Equipment / facility failure | other equipment / facility failure | 9.2992e-05
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Large Fires | Equipment / facility failure | other equipment / facility failure | 0.00034725
HFTD - Transmission - Tier 3 - 115 kV or Lower | Red Flag Warning - Small Fires | Equipment / facility failure | other equipment / facility failure | 0.0048567
HFTD - Transmission - Tier 3 - 230 kV or Higher | Red Flag Warning - Small Fires | Equipment / facility failure | other equipment / facility failure | 0.0012778
HFTD - Transmission - Tier 3 - 60/70 kV | Red Flag Warning - Small Fires | Equipment / facility failure | other equipment / facility failure | 0.0047714
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Catastrophic Fires | Contact from object | other contact from object | 4.3026e-06
non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Catastrophic Fires | Contact from object | other contact from object | 4.451e-07
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Catastrophic Fires | Contact from object | other contact from object | 4.7477e-06
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Destructive Fires | Contact from object | other contact from object | 1.2293e-06
non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Destructive Fires | Contact from object | other contact from object | 1.2717e-07
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Destructive Fires | Contact from object | other contact from object | 1.3565e-06
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Large Fires | Contact from object | other contact from object | 5.532e-05
non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Large Fires | Contact from object | other contact from object | 5.7227e-06
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Large Fires | Contact from object | other contact from object | 6.1042e-05
non-HFTD - Transmission - 115 kV or Lower | Red Flag Warning - Small Fires | Contact from object | other contact from object | 0.0057201
non-HFTD - Transmission - 230 kV or Higher | Red Flag Warning - Small Fires | Contact from object | other contact from object | 0.00059173
non-HFTD - Transmission - 60/70 kV | Red Flag Warning - Small Fires | Contact from object | other contact from object | 0.0063118
non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 0
non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 0
non-HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.7114e-07
non-HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 3.5406e-05
non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0
non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 0
non-HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.1059e-07
non-HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.2881e-05
non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 0
non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 0
non-HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 4.8766e-07
non-HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 0.00010089
non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 0
non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 0
non-HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.0075e-08
non-HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.4498e-05
non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 0
non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 0
non-HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 1.105e-06
non-HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 0.00022861
non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 0
non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 0
non-HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 2.5313e-07
non-HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 5.2369e-05
non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 0
non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 0
non-HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 1.9211e-07
non-HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 3.9746e-05
non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 0
non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 0
non-HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 1.341e-06
non-HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.00027743
non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 0
non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 0
non-HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 2.393e-07
non-HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 4.9509e-05
non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 0
non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 0
non-HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 3.1319e-07
non-HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 6.4796e-05
non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 0
non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 0
non-HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 2.374e-06
non-HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.00049115
non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.112e-09
non-HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.4606e-09
non-HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.5726e-08
non-HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 6.7961e-06
non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 1.5865e-09
non-HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.5328e-10
non-HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.0398e-08
non-HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.1091e-06
non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.0224e-08
non-HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 2.9212e-09
non-HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.3145e-07
non-HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.3592e-05
non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 5.2883e-10
non-HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.5109e-10
non-HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 6.7992e-09
non-HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 7.0304e-07
non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 1.7451e-08
non-HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 4.9861e-09
non-HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 2.2437e-07
non-HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 2.32e-05
non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 4.9357e-09
non-HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | dead | 1.4102e-09
non-HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | dead | 6.346e-08
non-HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | dead | 6.5617e-06
non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 2.2916e-09
non-HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 6.5474e-10
non-HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 2.9463e-08
non-HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 3.0465e-06
non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 1.0224e-08
non-HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 2.9212e-09
non-HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 1.3145e-07
non-HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 1.3592e-05
non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 3.173e-09
non-HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 9.0657e-10
non-HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 4.0795e-08
non-HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 4.2182e-06
non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 5.4646e-09
non-HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 1.5613e-09
non-HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | grow into | 7.0259e-08
non-HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | grow into | 7.2648e-06
non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 4.4245e-08
non-HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 1.2642e-08
non-HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 5.6887e-07
non-HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 5.8821e-05
HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.7052e-09
HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.7052e-09
HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 5.1347e-08
HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.8174e-06
HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.5414e-09
HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.5414e-09
HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 2.2873e-08
HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 3.9278e-06
HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.9476e-08
HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.9476e-08
HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 1.7528e-07
HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.0099e-05
HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.141e-09
HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.141e-09
HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.0269e-08
HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.7635e-06
HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 5.0776e-08
HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 5.0776e-08
HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 4.5699e-07
HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 7.8475e-05
HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 2.072e-08
HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | dead | 2.072e-08
HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | dead | 1.8648e-07
HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | dead | 3.2023e-05
HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 2.1524e-08
HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 2.1524e-08
HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 1.9372e-07
HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 3.3266e-05
HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 1.396e-07
HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 1.396e-07
HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 1.2564e-06
HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 0.00021575
HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 2.8163e-08
HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 2.8163e-08
HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 2.5347e-07
HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 4.3526e-05
HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 2.4377e-09
HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | grow into | 2.4377e-09
HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | grow into | 2.1939e-08
HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | grow into | 3.7674e-06
HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 1.2025e-07
HFTD - Substation | Non-Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 1.2025e-07
HFTD - Substation | Non-Red Flag Warning - Large Fires | vegetation contact | other/unknown | 1.0823e-06
HFTD - Substation | Non-Red Flag Warning - Small Fires | vegetation contact | other/unknown | 0.00018585
HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, > 12ft) | 8.5021e-08
HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.2146e-08
HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, > 12ft) | 7.2875e-08
HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, > 12ft) | 1.0014e-06
HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, 4-12ft) | 5.6681e-08
HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, 4-12ft) | 8.0973e-09
HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, 4-12ft) | 4.8584e-08
HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, 4-12ft) | 6.6757e-07
HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, distance unknown) | 4.1094e-07
HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, distance unknown) | 5.8705e-08
HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, distance unknown) | 3.5223e-07
HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, distance unknown) | 4.8399e-06
HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.417e-08
HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | branch (not overhanging, within 4ft) | 2.0243e-09
HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.2146e-08
HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | branch (not overhanging, within 4ft) | 1.6689e-07
HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | branch (overhanging) | 8.3604e-07
HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | branch (overhanging) | 1.1943e-07
HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | branch (overhanging) | 7.1661e-07
HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | branch (overhanging) | 9.8467e-06
HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | dead | 3.1174e-07
HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | dead | 4.4535e-08
HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | dead | 2.6721e-07
HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | dead | 3.6717e-06
HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (moderate-severe defect) | 2.4089e-07
HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | fell into (moderate-severe defect) | 3.4413e-08
HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | fell into (moderate-severe defect) | 2.0648e-07
HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | fell into (moderate-severe defect) | 2.8372e-06
HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (no defect) | 1.0486e-06
HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | fell into (no defect) | 1.498e-07
HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | fell into (no defect) | 8.988e-07
HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | fell into (no defect) | 1.235e-05
HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | fell into (slight defect) | 2.6923e-07
HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | fell into (slight defect) | 3.8462e-08
HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | fell into (slight defect) | 2.3077e-07
HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | fell into (slight defect) | 3.171e-06
HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | grow into | 2.834e-08
HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | grow into | 4.0486e-09
HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | grow into | 2.4292e-08
HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | grow into | 3.3379e-07
HFTD - Substation | Red Flag Warning - Catastrophic Fires | vegetation contact | other/unknown | 1.417e-06
HFTD - Substation | Red Flag Warning - Destructive Fires | vegetation contact | other/unknown | 2.0243e-07
HFTD - Substation | Red Flag Warning - Large Fires | vegetation contact | other/unknown | 1.2146e-06
HFTD - Substation | Red Flag Warning - Small Fires | vegetation contact | other/unknown | 1.6689e-05
non-HFTD - Substation | Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 1.2949e-05
non-HFTD - Substation | Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 3.6998e-06
non-HFTD - Substation | Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.00016649
non-HFTD - Substation | Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.017215
non-HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | other equipment / facility failure | 0
non-HFTD - Substation | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | other equipment / facility failure | 0
non-HFTD - Substation | Non-Red Flag Warning - Large Fires | equipment / facility failure | other equipment / facility failure | 0.0015197
non-HFTD - Substation | Non-Red Flag Warning - Small Fires | equipment / facility failure | other equipment / facility failure | 0.31442
HFTD - Substation | Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.0011127
HFTD - Substation | Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00015895
HFTD - Substation | Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00095372
HFTD - Substation | Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.013105
HFTD - Substation | Non-Red Flag Warning - Catastrophic Fires | equipment / facility failure | voltage regulator / booster damage or failure | 9.7229e-05
HFTD - Substation | Non-Red Flag Warning - Destructive Fires | equipment / facility failure | voltage regulator / booster damage or failure | 9.7229e-05
HFTD - Substation | Non-Red Flag Warning - Large Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.00087506
HFTD - Substation | Non-Red Flag Warning - Small Fires | equipment / facility failure | voltage regulator / booster damage or failure | 0.15027

## 7.3.5.2_Exposure
Source file: | 2022 WMP MASTER financials reach out v6 2.14.22 1235 pm.xlsx
Source file location: | WMP -> 2022 -> Financials
[5 empty] | Units | Units
[5 empty] | Expense | Expense | Expense (Units) |  | Capital | Capital | Capital (Units)
|  |  | MWC | MAT | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
|  |  | HN | HN# | 1560055 | 1424718 | 1551625 | 1546783 | 0 | 0 | 0 | 0
Distribution - All tier Split | 8.772% | Tier 3 |  |  | 136854.3631 | 124982.0516 | 136114.8493 | 135690.0894 | 0 | 0 | 0 | 0
Distribution - All tier Split | 22.61% | Tier 2 |  |  | 352786.1277 | 322181.4271 | 350879.793 | 349784.8377 | 0 | 0 | 0 | 0
Distribution - All tier Split | 0.01852% | Zone 1 |  |  | 288.8848 | 263.8236 | 287.3238 | 286.4272 | 0 | 0 | 0 | 0
Distribution - All tier Split | 68.6% | Tier 1 |  |  | 1070125.6244 | 977290.6976 | 1064343.034 | 1061021.6458 | 0 | 0 | 0 | 0
From GRC filing, we have the following split by HFTD and non-HFTD:
| 2018-2020 annual average of trees worked on | % trees | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
HFTD | 711487.3333 | 52.17% | 778227.2794 | 718228.2749 | 718228.2749 | 718228.2749 | 718228.2749 | 718228.2749
non-HFTD | 652217.3333 | 47.83% | 713397.5506 | 658396.7251 | 658396.7251 | 658396.7251 | 658396.7251 | 658396.7251
Total | 1363704.6667 |  | 1491624.83 | 1376625 | 1376625 | 1376625 | 1376625 | 1376625

## 7.3.5.2_Financials
Source file: | 2022 WMP MASTER financials reach out v6 2.14.22 1235 pm.xlsx
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense ($) |  | Capital | Capital | Capital ($)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
|  | Routine (# of trees) |  |  | 707138699.4 | 651187505.1 | 556789980.1572 | 804238975.2564

## 7.3.5.2_Effectiveness_Source
Assumption: If the Vegetation Management program is halted, all trees not worked on as a result, are at high risk of causing an outage within a given year.
Tree Summary | A Annual cycle trees | B. 2 year cycle trees | C. 3 year cycle trees | D. New trees | E. Bi-Annual trees | Total Identified
2018 | 405206 | 405206 | 405206 | 130279 | 9761 | 1355656
2019 | 465297 | 465297 | 465297 | 336126 | 15906 | 1747923
2020 | 414338 | 414338 | 414338 | 333755 | 9518 | 1586287
Total Average 3 year | 428280.3333 | 428280.3333 | 428280.3333 | 266720 | 11728.3333 | 1563288.6667
27.4% | Calculated the annual average trees identified divided by the total identified average trees
13.7% | 2-year cycle percentage determined
9.132% | 3-year cycle percentage determined
17.06% | New tree percentage determined= total identified trees minus total sum of 1,2,3 and Bi-Annuals (Assumption: New tree percentage is roughly the same year to year)
0.7502% | Calculated the Bi-Annual average trees identified divided by the total identified average trees
The percentage of trees identified above through the different inspeciton cycles, would be at high risk of causing an outage if not worked on through Vegetation Management program each year. Hence summing up the find rates through each inspection cycle gives the overall probability of an untrimmed tree causing an outage within a year if this program were to cease:
Cycle | Annual find rate (2018-2020)
Annual | 27.4%
2 year | 13.7%
3 year | 9.132%
New (trees) | 17.06%
Bi-Annual | 0.7502%
Total % | 68.04%

## 7.3.5.2_Effectiveness
From GRC 2023 filing:
| Value | Reference
Est. Probability of unworked trees causing an outage in a year | 68.04% | SME provided calculations
tree-related Ignition to Outage ratio = Tree-related ignitions (566) / Tree-related outages (30795) | 1.838%
Effectiveness | 1.251%

## 7.3.5.8_Financials
Source file: | 2022 WMP MASTER financials reach out v6 2.14.22 1235 pm.xlsx
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense ($) |  | Capital | Capital | Capital ($)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
|  | LiDAR inspections of vegetation around transmission electric lines and equipment |  |  | 9927717.37 | 10120589.43 | 13000000 | 13390000

## 7.3.5.8_Effectiveness
From previous WMP submission:
Data Sources: | SME Input, Transmission Overhead Outage Data, Transmission Overhead Ignition Data, 1-EO_WLDFR_Frequency
Assumptions: | Used the number of trees detected and worked from primary LiDAR patrol as well as midcycle LiDAR patrol. Assumed relative consistency of tree population from year to year. The probability of untrimmed tree causing contact with the conductor in Transmission depends on the type of detection.
| 100% | Probability of untrimmed tree (UCD) causing an outage in Transmission
| 90% | Probability of untrimmed tree (grow-in) causing an outage in Transmission
| 2% | Probability of untrimmed tree (fall-in) causing an outage in Transmission
| 339.6966 | Number of units of UCDs | 339.6966 | 56147 | trees worked in 2020 were able to be matched to the VMYear 2020 lidar tree detection dataset | 700 | Number of units of UCDs
| 14558.427 | Number of units of Grow-in trees | 14558.427 |  |  | 30000 | Number of units of Grow-in trees
| 41248.8764 | Number of units of Fall-in trees | 41248.8764 |  |  | 85000 | Number of units of Fall-in trees
| 339.6966 | Number of UCD that could cause an outage
| 13102.5843 | Number of grow-in trees that could cause an outage
| 824.9775 | Number of fall-in trees that could cause an outage
| 1 | Tree-related ignitions from the Transmission Ignition Dataset in tab Pivots
| 304 | Tree-related outages from Transmission Overhead Outage in tab REF_FREQ(Excluding mom.)
| 0.3289% | Tree-related Ignition to Outage ratio
| 14267.2584 | Total number of UCD, grow-in trees & fall-in trees that could cause an outage
| 46.9318 | Number of ignitions avoided
| 1.08 | Number of ignitions in transmission from 1-EO_WLDFR_Frequency in tab Pivots
| 5 | Number of years 2015-2019
| 0.216 | Baseline frequency
| 99.54% | Effectiveness

## 7.3.5.9_Exposure
Source file: | 2022 WMP MASTER financials reach out v6 2.14.22 1235 pm.xlsx
Source file location: | WMP -> 2022 -> Financials
[5 empty] | Units | Units
[5 empty] | Expense | Expense | Expense (Units) |  | Capital | Capital | Capital (Units)
|  |  | MWC | MAT | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
|  | Tree Mortality - Other discretionary inspections of vegetation around distribution electric lines and equipment | IG | IG# | 65402 | 76871 | 95000 | 65000 | 0 | 0 | 0 | 0
Distribution - HTFD Split | 23.32% | Tier 3 |  |  | 5737.3292 | 6743.4364 | 8333.786 | 5702.0641 | 0 | 0 | 0 | 0
Distribution - HTFD Split | 60.13% | Tier 2 |  |  | 14789.8108 | 17383.3759 | 21483.0132 | 14698.9038 | 0 | 0 | 0 | 0
Distribution - HTFD Split | 0.04924% | Zone 1 |  |  | 12.1109 | 14.2347 | 17.5917 | 12.0364 | 0 | 0 | 0 | 0
Distribution - HTFD Split | 16.5% | Tier 1 |  |  | 44862.7491 | 52729.953 | 65165.6091 | 44586.9957 | 0 | 0 | 0 | 0
Source file: | Risk Bow-Tie Model support files -> EO-WLDFR-5_Data_Pivots_DOVHD_outages_2015-2020 -> Vegetation pivot tab using filters:
0_Driver Modified | Vegetation
In Scope (final)? Asset Type and Condition | Yes
Row Labels | Associated with Ignition | Not associated with Ignition | Grand Total | Ignition to Outage rate
Branch (Not overhanging, > 12ft) | 9 | 605 | 614 | 1.466%
Branch (Not overhanging, 4-12ft) | 2 | 341 | 343 | 0.5831%
Branch (Not overhanging, Distance Unknown) | 74 | 1787 | 1861 | 3.976%
Branch (Not overhanging, within 4ft) |  | 195 | 195 | 0%
Branch (OverHanging) | 96 | 4338 | 4434 | 2.165%
Dead | 25 | 1355 | 1380 | 1.812%
Fell into (Moderate-Severe defect) | 51 | 1212 | 1263 | 4.038%
Fell into (No defect) | 156 | 8172 | 8328 | 1.873%
Fell into (slight defect) | 54 | 1571 | 1625 | 3.323%
Grow Into | 8 | 776 | 784 | 1.02%
Other/Unknown | 91 | 9877 | 9968 | 0.9129%
Grand Total | 566 | 30229 | 30795

## 7.3.5.9_Financials
Source file: | 2022 WMP MASTER financials reach out v6 2.14.22 1235 pm.xlsx
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense ($) |  | Capital | Capital | Capital ($)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
|  | Tree Mortality - Other discretionary inspections of vegetation around distribution electric lines and equipment | IG | IG# | 82622525.5 | 79361901.6 | 123944230.7918 | 63868853.5597

## 7.3.5.9_Effectiveness
* Effectiveness calculation methodology the same as the WMP 2021, with data to support the probability of 'Outage caused by an untrimmed tree' calculation provided by the SME.
* New sub drivers chosen. Fell Into Moderate Severe Defect and Fell Into Slight Defect
Quantitative Effectiveness Method: Fell Into Moderate Severe Defect
75568.25 | Calculated trees worked by taking the average number of trees in 2020-2023 from the Plan
51415.0583 | Calculated the number of trees that could cause an outage = Tree units (61,373) x Probability of untrimmed tree causing an outage in Distribution (68.04%)
4.038% | Calculated tree-related Ignition to Outage ratio = Fell Into Moderate Severe Defect related ignitions in HFTD & Non HFTD from the 7.3.5.9_Exposure tab(51) / Fell Into Moderate Severe Defect-related outages in HFTD & Non HFTD from the 7.3.5.9_Exposure tab (1,263) = 4.04%
2076.1425 | Calculated the number of ignitions avoided = the number of trees that could cause an outage (41,757) x Ignition to Outage ratio (4.04%)
8.5 | Calculated the baseline frequency (based on 2015-2020) = Number of Fell Into Moderate Severe Defect ignitions in distribution from 7.3.5.9_Exposure tab (51) / The number of years 2015-2020 (6)
99.59% | Calculated effectiveness % = Avoided Ignitions (1,686) / (Avoided Ignitions (1,686) + Baseline Frequency (8.5))
Quantitative Effectiveness Method: Fell Into Slight Defect
75568.25 | Calculated trees worked by taking the average number of trees in 2020-2023 from the Plan
51415.0583 | Calculated the number of trees that could cause an outage = Tree units (61,373) x Probability of untrimmed tree causing an outage in Distribution (68.04%)
3.323% | Calculated tree-related Ignition to Outage ratio = Fell Into Slight Defect related ignitions in HFTD & Non HFTD from the 7.3.5.9_Exposure tab(54) / Fell Into Slight Defect related outages in HFTD & Non HFTD from the 7.3.5.9_Exposure tab (1,625) = 3.32%
1708.5619 | Calculated the number of ignitions avoided = the number of trees that could cause an outage (41,757) x Ignition to Outage ratio (3.32%)
9 | Calculated the baseline frequency (based on 2015-2020) = Number of Fell Into Slight Defect related ignitions in distribution from 7.3.5.9_Exposure tab (54) / The number of years 2015-2020 (6)
99.48% | Calculated effectiveness % = Avoided Ignitions (1,388) / (Avoided Ignitions (1,388) + Baseline Frequency (9))

## 7.3.5.15_Exposure
Source file: | 2022 WMP MASTER financials reach out v7_022222.xlsx
Source file location: | WMP -> 2022 -> Financials
|  |  | MWC | MAT | Expense | Expense | Expense (Units) |  | Capital | Capital | Capital (Units)
[5 empty] | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
|  | EVM - Remediation of at-risk species | IG | IG# | 1878 | 1983 | 1890 | 1800

## 7.3.5.15_Financials
Source file: | 2022 WMP MASTER financials reach out v7_022222.xlsx
Source file location: | WMP -> 2022 -> Financials
|  | MWC | MAT | Expense | Expense | Expense ($) |  | Capital | Capital | Capital ($)
|  |  |  | 2020 | 2021 | 2022 | 2023 | 2020 | 2021 | 2022 | 2023
|  |  |  | 451390239.3 | 770434505 | 916616000 | 118022400

## 7.3.5.15_Effectiveness
From GRC 2023 filing:
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | NPV Calculation: | 0 | 0
EVM miles | 1878 | 1870 | 1890 | 1890 | 1890 | 1890 | 1890 |  | 1703803147.398
total HFTD distribution miles | 25461.6694
EVM miles% | 7.376% | 7.344% | 7.423% | 7.423% | 7.423% | 7.423% | 7.423%
| 451390239.23 | 507241926 | 524596892 | 520607348 | 533268508 | 546238099 | 556891785
EVM cost | 451390239.23 | 507241926 | 524596892 | 520607348 | 533268508 | 546238099 | 556891785
EVM Effectiveness Justification by Vegetation Subdriver
Line No. | Vegetation subdriver | Component Effectiveness % | Benefit Length Years | Justification for Effectiveness
1 | Branch (Not overhanging, > 12ft) | 0% | 0 | Includes hazard tree removal, increased clearance, overhang elimination and associated tree removals.
2 | Branch (Not overhanging, 4-12ft) | 50% | 30 | Includes hazard tree removal, increased clearance, overhang elimination and associated tree removals.
3 | Branch (Not overhanging, Distance Unknown) | 0% | 0 | Includes hazard tree removal, increased clearance, overhang elimination and associated tree removals.
4 | Branch (Not overhanging, within 4ft) | 90% | 30 | Includes hazard tree removal, increased clearance, overhang elimination and associated tree removals.
5 | Branch (Overhanging) | 90% | 30 | EVM scope designed to eliminate 100% of overhang outages. Estimate a 90% effectiveness rate.
6 | Dead | 0% | 0 | Routine and Catastrophic Emergency Memorandum Account (CEMA) scopes already designed to prevent all instances of dead trees. Added EVM patrol not expected to further reduce occurrence.
7 | Fell into (Moderate-Severe defect) | 95% | 1 | Includes hazard tree removal, increased clearance, overhang elimination and associated tree removals.
8 | Fell into (No defect) | 0% | 0 | The removal of healthy trees with no sign of defect falls outside of the EVM hazard tree removal scope.
9 | Fell into (Slight defect) | 50% | 1 | Includes hazard tree removal, increased clearance, overhang elimination and associated tree removals.
10 | Grow Into | 50% | 1 | Routine scope already designed to prevent all instances of growth into primary. Added EVM patrol expected to reduce occurrence by estimated 50%.
11 | Other/Unknown | 0% | 0 | Includes hazard tree removal, increased clearance, overhang elimination and associated tree removals.

## 7.3.5.18.2 - Exposure - Source
Substation Name | - all - | [7 empty] | Planned Substation Inspections (Source: 2021 Wildfire Mitigation Plan)
Based on Distribution Substation or Transmission Substation
Count of Fire Zone (HFTD) | Sub/Bus Type Transmission, Generation, Distribution, Other | [15 empty] | Substation Exposure
Fire Zone (HFTD) | Dist | G | n/a | T | Total Result | All Substations | Count | % of tier total |  | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 |  | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
Other |  |  | 1 |  | 1 | D Substation: Tier 1 | 533 | 81.13% | D Substation: Tier 1 | 17.81% | 17.35% | 17.35% | 17.35% | 17.35% | 17.35% | 17.35% | D-Non-HFTD | 14.45% | 14.08% | 14.08% | 14.08% | 14.08% | 14.08% | 14.08%
T1 | 533 | 4 | 3 | 124 | 664 | D Substation: Tier 2 | 156 | 80.41% | D Substation: Tier 2 | 17.01% | 21.65% | 21.65% | 21.65% | 21.65% | 21.65% | 21.65%
T2 | 103 | 26 | 1 | 23 | 153 | D Substation: Tier 3 | 33 | 84.62% | D Substation: Tier 3 | 100% | 100% | 100% | 100% | 200% | 300% | 400%
T2/3A | 53 |  |  | 15 | 68 | D Substation: T2 & T3 | 189 | 81.12% | [8 empty] | D-HFTD | 26.11% | 27.85% | 27.85% | 27.85% | 27.85% | 27.85% | 27.85%
T3 | 33 | 10 | 1 | 6 | 50
Total Result | 722 | 40 | 6 | 168 | 936 | T Substation: Tier 1 | 124 | 18.87% | T Substation: Tier 1 | 17.81% | 17.35% | 17.35% | 17.35% | 17.35% | 17.35% | 17.35% | T-Non-HFTD | 3.361% | 3.275% | 3.275% | 3.275% | 3.275% | 3.275% | 3.275%
[6 empty] | T Substation: Tier 2 | 38 | 19.59% | T Substation: Tier 2 | 17.01% | 21.65% | 21.65% | 21.65% | 21.65% | 21.65% | 21.65%
[6 empty] | T Substation: Tier 3 | 6 | 15.38% | T Substation: Tier 3 | 100% | 100% | 100% | 100% | 200% | 300% | 400%
|  |  |  | HFTD Substations | 233 | T Substation: T2 & T3 | 44 | 18.88% | [8 empty] | T-HFTD | 6.079% | 6.484% | 6.484% | 6.484% | 6.484% | 6.484% | 6.484%
|  |  |  | non-HFTD | 657
[6 empty] | Total: Tier 1 | 657 |  | Total: Tier 1 | 117 | 114 | 114 | 114 | 114 | 114 | 114
[6 empty] | Total: Tier 2 | 194 |  | Total: Tier 2 | 33 | 42 | 42 | 42 | 42 | 42 | 42
[6 empty] | Total: Tier 3 | 39 |  | Total: Tier 3 | 42 | 38 | 38 | 38 | 38 | 38 | 38
[6 empty] | Total: T3 & T2 | 233 |  | Total: T3 & T2 | 75 | 80 | 80 | 80 | 80 | 80 | 80 |  | =(% of T or D substation*total planned substation)/total substation
[6 empty] | Total: All | 890 |  | Total: All | 192 | 194 | 194 | 194 | 194 | 194 | 194
*Figures in Tier 1 include Substations listed as "adjacent" to HFTD areas in the 2021 WMP.
2022-26 figures assume similar work scope to 2020-2021, per the WMP
[9 empty] | D Substation Non-HFTD | 94.9178 | 92.484 | 92.484 | 92.484 | 92.484 | 92.484 | 92.484
[9 empty] | D Substation HFTD | 62.0745 | 65.927 | 65.927 | 65.927 | 65.927 | 65.927 | 65.927

## 7.3.5.18.2 - Exposure
Per SME, 220 substations are worked on every year for the Defensible Space program – 70%/30% split between transmission/distribution and substation, respectively.
Source: EO-WLDFR-3_RSE Input File
Number of Distribution Substations worked on every year: | 66
% Exposure | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
HFTD - Substation | 34.92% | 34.92% | 34.92% | 34.92% | 34.92% | 34.92%

## 7.3.5.18.1 - Financials
Source: | 2022 WMP MASTER financials reach out v2_122721
|  |  |  | Headcount Related |  | 2020 Act link | 2021 Res link | 2022 Fcst | 2023 Fcst
[6 empty] | Financials | Financials
[5 empty] | Orig Plan | Expense | Expense | Expense ($) |  | Orig Plan | Capital | Capital | Capital ($)
Tier ID | Tier % | Tier | MWC | MAT | 2020 | 2020 | 2021 | 2022 | 2023 | 2020 | 2020 | 2021 | 2022 | 2023
Distribution - HTFD Split | 27.93% | Tier 3 |  |  | 838211.2341 | 843605.68 | 790739.8704 | 788065.2256 | 796740.1135 | 0 | 0 | 0 | 0 | 0
Distribution - HTFD Split | 72.01% | Tier 2 |  |  | 2160758.9904 | 2174664.9094 | 2038386.2855 | 2031491.5287 | 2053853.8416 | 0 | 0 | 0 | 0 | 0
Distribution - HTFD Split | 0.05896% | Zone 1 |  |  | 1769.3736 | 1780.7607 | 1669.1666 | 1663.5207 | 1681.8325 | 0 | 0 | 0 | 0 | 0
Distribution - HTFD Split | 0% | Tier 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total: |  |  |  |  | 3000739.598 | 3020051.35 | 2830795.3225 | 2821220.275 | 2852275.7876 | 0 | 0 | 0 | 0 | 0

## 7.3.5.18.2 - Financials
Source: | 2022 WMP MASTER financials reach out v2_122721
|  |  | Headcount Related |  | 2020 Act link | 2021 Res link | 2022 Fcst | 2023 Fcst
[5 empty] | Financials | Financials
|  |  |  | Orig Plan | Expense | Expense | Expense ($) |  | Orig Plan | Capital | Capital | Capital ($)
Tier % | Tier | MWC | MAT | 2020 | 2020 | 2021 | 2022 | 2023 | 2020 | 2020 | 2021 | 2022 | 2023
23.37% | Tier 3 |  |  | 715995.2083 | 648416.1522 | 920830.9293 | 812655.8821 | 835219.0563 | 0 | 0 | 0 | 0 | 0
76.52% | Tier 2 |  |  | 2344163.8784 | 2122910.4673 | 3014794.7609 | 2660630.3262 | 2734502.0187 | 0 | 0 | 0 | 0 | 0
0.1085% | Zone 1 |  |  | 3325.0551 | 3011.2205 | 4276.3046 | 3773.9437 | 3878.7263 | 0 | 0 | 0 | 0 | 0
0% | Tier 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total: |  |  |  | 3063484.1418 | 2774337.84 | 3939901.9949 | 3477060.152 | 3573599.8013 | 0 | 0 | 0 | 0 | 0

## Match esc definition
Define a Customer Extrapolation Multiplier
match | x_match | matching with other series | y[i, j]= y[i-1, j] * x_match[i]/x_match[i-1]
x_match | Description | Year1 | Year2 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121
case1 |  | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Data & Validation
Lookup tables
No. | A | B | C | Risk/Cross Cutting Factor Name | RISK ID | Program Cost Options
1 | 0% | 10% | 15% | Aviation Incident | AVATN | prorate by Program Exposure
2 | 0% | 10% | 15% | Electric Transmission System-Wide Blackout | BLKOT | % of Total Cost (specify to the right)
3 | 0% | 10% | 15% | Loss of Containment on Gas Customer Connected Equipment | CCEPQ
4 | 0% | 2.5% | 5% | Climate | CLIMT | Program Exposure Options
5 | 0% | 2.5% | 5% | Loss of Containment on CNG Station Equipment | CNGEQ | Exposure unit
6 | 0% | 2.5% | 5% | Contractor Safety Incident | CNTSI | % of tranche exposure
7 | 0% | 2.5% | 5% | Insufficient Capacity to Meet High Demand | CPCTY | Work unit
8 | 0% | 2.5% | 5% | Contract Management | CTMGT
9 | 0% | 2.5% | 5% | Cyber Attack | CYBER | Program Type Options
10 | 0% | 2.5% | 5% | Failure of Electric Distribution Network Assets | DNTWK | Mitigation
11 | 0% | 2.5% | 5% | Failure of Electric Distribution Overhead Assets | DOVHD | Control
12 | 0% | 2.5% | 5% | Data Loss Event | DTALS | Foundational Mitigation
13 | 0% | 2.5% | 5% | Failure of Electric Distribution Underground Assets | DUNGD | Foundational Control
|  |  |  | Business Model - Electric | EMODL
|  |  |  | Employee Safety Incident | EMPSI
|  |  |  | Emergency Preparedness and Response | EPNDR
|  |  |  | Business Model - Gas | GMODL | Consequence Options
|  |  |  | Extended Unplanned Shutdown of a Critical Power Generation Asset | GSHUT | Safety
|  |  |  | Hazardous Material Release | HZMAT | Electric Reliability
|  |  |  | IT Asset Failure | ITAFL | Gas Reliability
|  |  |  | Large Uncontrolled Water Release (Dam Failure) | LGUWR | Financial
|  |  |  | Loss of Containment on LNG/CNG Portable Equipment | LNCNG
|  |  |  | Loss of Containment on Gas Distribution Main or Service | LOCDM | Bow Tie Element
|  |  |  | Loss of Containment on Gas Transmission Pipeline | LOCTR | LOF
|  |  |  | Liquidity Shortage | LQDTY | COF
|  |  |  | Large Overpressure Event Downstream of Gas Measurement and Control Facility | LRGOP | LOF and COF
|  |  |  | Loss of Containment at Gas Measurement and Control or Compression and Processing Facility | MCCPF
|  |  |  | Motor Vehicle Safety Incident | MTRSI
|  |  |  | Nuclear Core Damaging Event | NCORE
|  |  |  | Loss of Containment at Natural Gas Storage Well or Reservoir | NGSWR
|  |  |  | Nuclear Extended Shutdown | NSHUT
|  |  |  | Physical Attack | PHYSA
|  |  |  | Records and Information Management | RECIM
|  |  |  | Real Estate and Facilities Failure | REFFL
|  |  |  | Failure of Substation Assets | SBSTN
|  |  |  | Skilled and Qualified Workforce | SQWKF
|  |  |  | Seismic | SSMIC
|  |  |  | 3rd-Party Safety Incident | TPTSI
|  |  |  | Third-Party Risk | TRDPY
|  |  |  | Failure of Electric Transmission Overhead Assets | TRNHD
|  |  |  | Failure of Electric Transmission Underground Assets | TUNGD
|  |  |  | Wildfire | WLDFR

## HFTD Miles
HFTD Line Miles | #REF!
| HFTD Tranche % based on WMP BowTie | Line Miles
Zone 1 | 0.06% | #REF!
Tier 3 | 27.93% | #REF!
Tier 2 | 72.01% | #REF!

## TablePVRR
Asset Group | PVRR Multiplier (no O&M) | Lifetime O&M as % of PVRR
Buildings | 1.4702 | 0
Communications equipment | 1.2527 | 0
Computer hardware | 1.1238 | 0.44918
Computer software | 1.1074 | 0.44918
Electric distribution (<69kV) - Overhead | 1.3891 | 1.1158
Electric distribution (<69kV) - Underground | 1.3891 | 0.38678
Electric transmission (69kV+) | 1.3758 | 0
Electric smart meter | 1.229 | 0
Gas distribution after 2010 | 1.4002 | 1.1518
Gas Meters | 1.3726 | 7.7616
Gas transmission & storage | 1.3686 | 1.7862
Gas (current) held for resale | 1.5881 | 0
Land easement | 1.5197 | 0
Land purchase | 1.448 | 0
Motor vehicles | 1.1661 | 0
Office furniture | 1.241 | 0
Hydro | 1.405 | 0
Hydro additions | 1.3416 | 0
Nuclear | 1.2779 | 0
Nuclear additions | 1.1917 | 0
Fuel cell | 1.1589 | 0
Custom | 0 | 0

## BowTie
TableDriverSubdriver |  | TableTranche |  |  |  | TableOutcome
Driver | Subdriver | Tranche | Exposure | Unit | 2021 miles | Outcome
Contact from object | Animal contact | HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 1QU LoRE | 163.6441 | Miles | 184.2524 | Red Flag Warning - Catastrophic Fires
Contact from object | Balloon contact | HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 2QU LoRE | 353.5334 | Miles | 342.1459 | Red Flag Warning - Destructive Fires
Contact from object | Other contact from object | HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 3QU LoRE | 1013.9529 | Miles | 1045.7977 | Red Flag Warning - Large Fires
Contact from object | Vehicle contact | HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 4QU LoRE | 1483.0022 | Miles | 1437.6834 | Red Flag Warning - Small Fires
Vegetation Contact | Branch (Not overhanging, > 12ft) | HFTD - Distribution - Tier 2 - 1QU CoRE ¦ 5QU LoRE | 1601.5759 | Miles | 1615.3706 | Non-Red Flag Warning - Catastrophic Fires
Vegetation Contact | Branch (Not overhanging, 4-12ft) | HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 1QU LoRE | 193.7699 | Miles | 179.7119 | Non-Red Flag Warning - Destructive Fires
Vegetation Contact | Branch (Not overhanging, Distance Unknown) | HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 2QU LoRE | 543.1039 | Miles | 509.5661 | Non-Red Flag Warning - Large Fires
Vegetation Contact | Branch (Not overhanging, within 4ft) | HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 3QU LoRE | 946.5765 | Miles | 950.8276 | Non-Red Flag Warning - Small Fires
Vegetation Contact | Branch (OverHanging) | HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 4QU LoRE | 1078.9824 | Miles | 1134.6096 | Seismic - Red Flag Warning - Catastrophic Fires
Vegetation Contact | Dead | HFTD - Distribution - Tier 2 - 2QU CoRE ¦ 5QU LoRE | 1464.9153 | Miles | 1463.3797 | Seismic - Non-Red Flag Warning - Catastrophic Fires
Vegetation Contact | Fell into (Moderate-Severe defect) | HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 1QU LoRE | 489.6273 | Miles | 494.5343
Vegetation Contact | Fell into (No defect) | HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 2QU LoRE | 791.1377 | Miles | 739.0344
Vegetation Contact | Fell into (slight defect) | HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 3QU LoRE | 791.1875 | Miles | 796.2245
Vegetation Contact | Grow Into | HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 4QU LoRE | 741.5879 | Miles | 757.6487
Vegetation Contact | Other/Unknown | HFTD - Distribution - Tier 2 - 3QU CoRE ¦ 5QU LoRE | 715.8465 | Miles | 721.5283
Contamination | Contamination | HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 1QU LoRE | 772.1066 | Miles | 734.0513
Equipment / facility failure | Anchor / guy damage or failure | HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 2QU LoRE | 522.2177 | Miles | 549.0677
Equipment / facility failure | Capacitor bank damage or failure | HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 3QU LoRE | 750.2287 | Miles | 758.0137
Equipment / facility failure | Conductor damage or failure | HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 4QU LoRE | 696.1473 | Miles | 682.1613
Equipment / facility failure | Connection device damage or failure | HFTD - Distribution - Tier 2 - 4QU CoRE ¦ 5QU LoRE | 470.836 | Miles | 487.3876
Equipment / facility failure | Crossarm damage or failure | HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 1QU LoRE | 752.6401 | Miles | 714.6389
Equipment / facility failure | Fuse damage or failure | HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 2QU LoRE | 768.4668 | Miles | 794.6718
Equipment / facility failure | Insulator and brushing damage or failure | HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 3QU LoRE | 467.0501 | Miles | 439.3061
Equipment / facility failure | Lightning arrestor damage or failure | HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 4QU LoRE | 347.2658 | Miles | 382.7904
Equipment / facility failure | Other equipment / facility failure | HFTD - Distribution - Tier 2 - 5QU CoRE ¦ 5QU LoRE | 406.8993 | Miles | 411.898
Equipment / facility failure | Pole damage or failure | HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 1QU LoRE | 58.7222 | Miles | 68.3395
Equipment / facility failure | Recloser damage or failure | HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 2QU LoRE | 156.5661 | Miles | 163.8201
Equipment / facility failure | Sectionalizer damage or failure | HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 3QU LoRE | 56.2394 | Miles | 39.0328
Equipment / facility failure | Switch damage or failure | HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 4QU LoRE | 111.286 | Miles | 119.909
Equipment / facility failure | Transformer damage or failure | HFTD - Distribution - Tier 3 - 1QU CoRE ¦ 5QU LoRE | 65.8407 | Miles | 57.0212
Equipment / facility failure | Voltage regulator / booster damage or failure | HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 1QU LoRE | 184.1265 | Miles | 226.4749
Other | All Other | HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 2QU LoRE | 264.4574 | Miles | 311.9586
Unknown | Unknown | HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 3QU LoRE | 279.2931 | Miles | 224.2508
Vandalism / Theft | Vandalism / Theft | HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 4QU LoRE | 108.7427 | Miles | 69.0654
Wire-to-wire contact | Wire-to-wire contact / contamination | HFTD - Distribution - Tier 3 - 2QU CoRE ¦ 5QU LoRE | 22.7224 | Miles | 33.5215
Utility work / Operation | Utility work / Operation | HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 1QU LoRE | 423.2024 | Miles | 449.4697
CC - Seismic Scenario | Seismic Scenario | HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 2QU LoRE | 595.3479 | Miles | 574.4306
|  | HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 3QU LoRE | 215.5262 | Miles | 247.7504
|  | HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 4QU LoRE | 223.3454 | Miles | 213.7942
|  | HFTD - Distribution - Tier 3 - 3QU CoRE ¦ 5QU LoRE | 134.3564 | Miles | 105.542
|  | HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 1QU LoRE | 607.6134 | Miles | 608.7309
|  | HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 2QU LoRE | 572.0063 | Miles | 551.9796
|  | HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 3QU LoRE | 384.7705 | Miles | 400.6021
|  | HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 4QU LoRE | 202.884 | Miles | 213.1612
|  | HFTD - Distribution - Tier 3 - 4QU CoRE ¦ 5QU LoRE | 117.3278 | Miles | 105.5226
|  | HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 1QU LoRE | 1430.0123 | Miles | 1412.9227
|  | HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 2QU LoRE | 527.1275 | Miles | 559.1759
|  | HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 3QU LoRE | 190.7177 | Miles | 189.2879
|  | HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 4QU LoRE | 95.1547 | Miles | 86.1355
|  | HFTD - Distribution - Tier 3 - 5QU CoRE ¦ 5QU LoRE | 97.3625 | Miles | 92.8527
|  | HFTD - Distribution - Zone 1 - 1QU CoRE ¦ 5QU LoRE | 0.18783 | Miles | 0.18783
|  | HFTD - Distribution - Zone 1 - 4QU CoRE ¦ 1QU LoRE | 0.13442 | Miles | 0.13442
|  | HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 1QU LoRE | 10.0154 | Miles | 10.0154
|  | HFTD - Distribution - Zone 1 - 5QU CoRE ¦ 4QU LoRE | 0.27822 | Miles | 0.27822
|  | HFTD - Substation | 1 | Unit | 1
|  | HFTD - Transmission - Tier 2 - 115 kV or Lower | 1299.3 | Miles | 1299.3
|  | HFTD - Transmission - Tier 2 - 230 kV or Higher | 1759.53 | Miles | 1759.53
|  | HFTD - Transmission - Tier 2 - 60/70 kV | 1419.51 | Miles | 1419.51
|  | HFTD - Transmission - Tier 3 - 115 kV or Lower | 446.95 | Miles | 446.95
|  | HFTD - Transmission - Tier 3 - 230 kV or Higher | 557.6 | Miles | 557.6
|  | HFTD - Transmission - Tier 3 - 60/70 kV | 376.43 | Miles | 376.43
|  | HFTD - Transmission - Zone 1 - 115 kV or Lower | 1.27 | Miles | 1.27
|  | HFTD - Transmission - Zone 1 - 230 kV or Higher | 3.1 | Miles | 3.1
|  | HFTD - Transmission - Zone 1 - 60/70 kV | 1.8 | Miles | 1.8
|  | non-HFTD - Distribution | 55300 | Miles | 55300
|  | non-HFTD - Substation | 1 | Unit | 1
|  | non-HFTD - Transmission - 115 kV or Lower | 4431.1 | Miles | 4431.1
|  | non-HFTD - Transmission - 230 kV or Higher | 5106.55 | Miles | 5106.55
|  | non-HFTD - Transmission - 60/70 kV | 3682.86 | Miles | 3682.86
|  | HFTD - Distribution - Zone 1 - All | 10.6159 | Miles
|  | HFTD - Distribution - Tier 2 - All | 18326.3019 | Miles
|  | HFTD - Distribution - Tier 3 - All | 7124.7516 | Miles
|  | HFTD - Distribution - All | 25461.6694 | Miles
|  | HFTD - Transmission - All | 5865.49 | Miles
|  | HFTD - All | 31327.1594 | Miles
|  | non-HFTD - Transmission - All | 13220.51 | Miles
|  | HFTD - Transmission - Tier 2 - All | 4478.34 | Miles
|  | HFTD - Transmission - Tier 3 - All | 1380.98 | Miles
|  | HFTD - Transmission - Zone 1 - All | 6.17 | Miles

## DPCache_Substation Ranking (hidden)
Functional Location | Substation Name | Functional Loc. | SM&C Area | SM&C HQ | Sub Categorization | Voltage Level | Sub Security Level | BES (Yes or No)? | Sub/Bus Type Transmission, Generation, Distribution, Other | Highest Voltage | Blackstart & Large Gen | # Bus Elements on all T Busses in Sub | Criticality Rank | b | Fire Zone (HFTD) | Tranche | Reliability Score (Outage History and Bus Operational Constraints) | PSPS Impact | RIBA Score | Safety (RIBA Score) | Commitment | b2 | Criticality Score | HFTD Score | Reliability Score | PSPS Impact Score | RIBA Score2 | Safety RIBA Score | Commitment Score | OVERALL SCORE | Sub 1-N Rank | Gen Opportunity | D Line Rank
ETS.10.16515 | 7TH STANDARD | ETS.10.16515 | South Valley | Bakersfield | DSub in FERC | 21,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 48 | 1 | 0 |  | 6 | 4 | n/a | 0 | 2 | 5 |  | 17 | 25 | N | 613
ETS.12.12002 | ACTON | ETS.12.12002 | Bay Area | Martin | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 258 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 541
ETS.10.16765 | ADOBE SW STA | ETS.10.16765 | South Valley | Bakersfield | SW STA - Trans | 115 | Tier 6 | Yes | T | 115 |  | 3 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 5 | 1 | 0 |  | 8 | 4 | n/a | 0 | 2 | 5 |  | 19 | 23 | N | n/a
ETS.07.13225 | AG WISHON PH | ETS.07.13225 | South Valley | Fresno | 0 | 70 | Tier 6 | No | Dist | 70 |  | 3 | 2 |  | T3 | HFTD - Non-critical Substation | 2 | 1 | 4 | 1 | 0 |  | 2 | 10 | 2 | 1 | 2 | 5 |  | 22 | 20 | N | 469
ETS.07.16495 | AIRWAYS | ETS.07.16495 | South Valley | Fresno | DSub in FERC | 12,115 | Tier 6 | No | Dist | 115 |  | 4 | 3 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 3 | 4 | n/a | 0 | 6 | 10 |  | 23 | 19 | N | 333
ETS.22.12013 | ALHAMBRA | ETS.22.12013 | Central Coast | Concord | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T2/3A | HFTD - Non-critical Substation | n/a | 1 | 225 | 178 | 0 |  | 6 | 6 | n/a | 1 | 6 | 10 |  | 29 | 13 | N | 93
ETS.19.12014 | ALLEGHANY | ETS.19.12014 | North Coast | Table Mountain | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T3 | HFTD - Non-critical Substation | 5 | 3 | 48 | 1 | 0 |  | 2 | 10 | 5 | 3 | 2 | 5 |  | 27 | 15 | N | 101
ETS.03.12015 | ALMADEN | ETS.03.12015 | Central Coast | Cupertino | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 385
ETS.08.12016 | ALPAUGH | ETS.08.12016 | South Valley | Gates | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 284 | 178 | 0 |  | 6 | 4 | 3 | 0 | 6 | 10 |  | 29 | 13 | N | 690
ETS.18.13501 | ALPINE | ETS.18.13501 | North Valley | Stockton | DSub not in FERC | 12,17 | Tier 6 | No | Dist | 17 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 2 | 198 | 178 | 0 |  | 1 | 4 | n/a | 2 | 4 | 10 |  | 21 | 21 | N | 535
ETS.04.16565 | ALTA PH | ETS.04.16565 | North Valley | Del Mar | 0 | 4,12 | Tier 6 | No | G | 12 |  | n/a | 4 |  | T3 | HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 4 | 10 | n/a | 0 | 1 | 1 |  | 16 | 26 | N | n/a
ETS.26.12017 | ALTAMONT | ETS.26.12017 | North Valley | Tesla | DSub in FERC | 4,60 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 186 | 178 | 0 |  | 2 | 4 | n/a | 0 | 4 | 10 |  | 20 | 22 | N | n/a
ETS.13.12018 | ALTO | ETS.13.12018 | North Coast | McMaude | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 5 | 2 |  | T1 | non-HFTD - Non-critical Substation | 5 | 2 | 746 | 178 | 0 |  | 2 | 4 | 5 | 2 | 8 | 10 |  | 31 | 11 | Y | 72
ETS.03.16040 | AMES DIST | ETS.03.16040 | Central Coast | Cupertino | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 3 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 198 | 178 | 0 |  | 6 | 4 | n/a | 0 | 4 | 10 |  | 24 | 18 | N | 564
ETS.03.12022 | AMES TRANS | ETS.03.12022 | Central Coast | Cupertino | SW STA - Trans | 115 | Tier 6 | Yes | T | 115 |  | 8 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 6 | 1 | 0 |  | 8 | 4 | n/a | 0 | 2 | 5 |  | 19 | 23 | N | n/a
ETS.02.12024 | ANDERSON | ETS.02.12024 | North Coast | Cottonwood | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T2/3A | HFTD - Non-critical Substation | 3 | 3 | 258 | 178 | 0 |  | 2 | 6 | 3 | 3 | 6 | 10 |  | 30 | 12 | N | 351
ETS.08.12025 | ANGIOLA | ETS.08.12025 | South Valley | Gates | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 196 | 178 | 0 |  | 2 | 4 | 3 | 0 | 4 | 10 |  | 23 | 19 | N | 736
ETS.19.12026 | ANITA | ETS.19.12026 | North Coast | Table Mountain | DSub in FERC | 12,60,115 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 2 | 202 | 178 | 0 |  | 2 | 4 | 3 | 2 | 6 | 10 |  | 27 | 15 | N | 300
ETS.20.12027 | ANNAPOLIS | ETS.20.12027 | North Coast | Ukiah | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T2 | HFTD - Non-critical Substation | 2 | 3 | 202 | 178 | 0 |  | 2 | 8 | 2 | 3 | 6 | 10 |  | 31 | 11 | N | 159
ETS.10.12028 | ANTELOPE | ETS.10.12028 | South Valley | Bakersfield | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 19 | 1 | 0 |  | 2 | 4 | n/a | 0 | 2 | 5 |  | 13 | 29 | N | 638
ETS.02.12030 | ANTLER | ETS.02.12030 | North Coast | Cottonwood | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T2 | HFTD - Non-critical Substation | 3 | 1 | 196 | 178 | 0 |  | 2 | 8 | 3 | 1 | 4 | 10 |  | 28 | 14 | N | 294
ETS.15.13839 | ANZAR JCT | ETS.15.13839 | Central Coast | Moss Landing | 0 | n/a | Tier 6 | No | T | 60 |  | n/a | 5 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 5 | 4 | n/a | 0 | 1 | 1 |  | 11 | 31 | N | n/a
ETS.04.12031 | APPLE HILL | ETS.04.12031 | North Valley | Del Mar | DSub in FERC | 12,21,115 | Tier 6 | No | Dist | 115 |  | n/a | 3 |  | T2 | HFTD - Non-critical Substation | 3 | 3 | 227 | 178 | 0 |  | 3 | 8 | 3 | 3 | 6 | 10 |  | 33 | 9 | N | 2
ETS.03.15618 | APPLIED MATERIALS SW STA | ETS.03.15618 | Central Coast | Cupertino | SW STA - Trans | 115 | Tier 6 | Yes | T | 115 |  | 4 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 10 | 1 | 0 |  | 8 | 4 | n/a | 0 | 2 | 5 |  | 19 | 23 | N | n/a
ETS.15.13503 | ARANA | ETS.15.13503 | Central Coast | Moss Landing | Unit Sub | 4,21 | Tier 6 | No | Dist | 21 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 202 | 178 | 0 |  | 1 | 4 | 2 | 0 | 6 | 10 |  | 23 | 19 | N | 706
ETS.21.12032 | ARBUCKLE | ETS.21.12032 | North Valley | Vaca-Dixon | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 3 | 362 | 178 | 0 |  | 2 | 4 | n/a | 3 | 6 | 10 |  | 25 | 17 | N | 97
ETS.06.12034 | ARCATA | ETS.06.12034 | North Coast | Eureka | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | 5 | 2 | 225 | 178 | 0 |  | 2 | 4 | 5 | 2 | 6 | 10 |  | 29 | 13 | Y | 180
ETS.08.10038 | ARCO | ETS.08.10038 | South Valley | Gates | T-Sub | 230,70 | Tier 6 | Yes | T | 230 |  | 11 | 8 |  | T1 | non-HFTD - Non-critical Substation | 4 | 0 | 48 | 1 | 0 |  | 8 | 4 | 4 | 0 | 2 | 5 |  | 23 | 19 | N | n/a
ETS.23.13504 | ARLINGTON | ETS.23.13504 | Bay Area | Oakport | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 1 | 202 | 178 | 0 |  | 1 | 4 | n/a | 1 | 6 | 10 |  | 22 | 20 | N | 523
ETS.08.12037 | ARMSTRONG SW STA | ETS.08.12037 | South Valley | Gates | SW STA - Trans | 70 | Tier 6 | No | T | 70 |  | 5 | 5 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 5 | 4 | n/a | 0 | 1 | 1 |  | 11 | 31 | N | n/a
ETS.10.12039 | ARVIN | ETS.10.12039 | South Valley | Bakersfield | DSub in FERC | 12,70 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 1 | 19 | 1 | 0 |  | 2 | 4 | n/a | 1 | 2 | 5 |  | 14 | 28 | N | 503
ETS.07.10039 | ASHLAN AVE | ETS.07.10039 | South Valley | Fresno | DSub in FERC | 12,230 | Tier 6 | Yes | Dist | 230 |  | 5 | 7 |  | T1 | non-HFTD - Non-critical Substation | 7 | 0 | 1184 | 178 | 0 |  | 7 | 4 | 7 | 0 | 10 | 10 |  | 38 | 4 | N | 460
ETS.17.12044 | ATASCADERO | ETS.17.12044 | South Valley | Pismo | DSub in FERC | 12,115 | Tier 6 | No | Dist | 70 |  | 8 | 2 |  | T2/3A | HFTD - Non-critical Substation | n/a | 0 | 238 | 178 | 0 |  | 2 | 6 | n/a | 0 | 6 | 10 |  | 24 | 18 | N | 254
ETS.04.10040 | ATLANTIC | ETS.04.10040 | North Valley | Del Mar | T-Sub | 230,60,115 | Tier 5 | Yes | T | 230 |  | 12 | 9 |  | T1 | non-HFTD - Critical Substation | n/a | 0 | 360 | 178 | 0 |  | 9 | 4 | n/a | 0 | 6 | 10 |  | 29 | 13 | N | n/a
ETS.14.12045 | ATWATER | ETS.14.12045 | North Valley | Merced | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 6 | 6 |  | T1 | non-HFTD - Non-critical Substation | 4 | 0 | 317 | 178 | 0 |  | 6 | 4 | 4 | 0 | 6 | 10 |  | 30 | 12 | N | 512
ETS.07.12046 | AUBERRY | ETS.07.12046 | South Valley | Fresno | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 3 | 2 |  | T2 | HFTD - Non-critical Substation | 3 | 1 | 238 | 178 | 0 |  | 2 | 8 | 3 | 1 | 6 | 10 |  | 30 | 12 | N | 133
ETS.04.13506 | AUBURN | ETS.04.13506 | North Valley | Del Mar | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T2/3A | HFTD - Non-critical Substation | 3 | 2 | 258 | 178 | 0 |  | 2 | 6 | 3 | 2 | 6 | 10 |  | 29 | 13 | N | 172
ETS.18.12048 | AVENA | ETS.18.12048 | North Valley | Stockton | DSub in FERC | 12,21,70,115 | Tier 6 | Yes | Dist | 115 |  | 3 | 6 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 500 | 178 | 0 |  | 6 | 4 | 2 | 0 | 6 | 10 |  | 28 | 14 | N | 598
ETS.08.13914 | AVENAL | ETS.08.13914 | South Valley | Gates | DSub in FERC | 21,70 | Tier 6 | No | Dist | 70 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 256 | 178 | 0 |  | 2 | 4 | 2 | 0 | 6 | 10 |  | 24 | 18 | N | 648
ETS.22.16830 | AVILA | ETS.22.16830 | Central Coast | Concord |  |  | Tier 6 | No | n/a | n/a |  | n/a | 5 |  | Other | HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 5 | 1 | n/a | 0 | 1 | 1 |  | 8 | 34 | N | n/a
ETS.22.13511 | BABEL | ETS.22.13511 | Central Coast | Concord | Unit Sub | 4,21 | Tier 6 | No | Dist | 21 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 202 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 213
ETS.13.10041 | BAHIA | ETS.13.10041 | North Coast | McMaude | DSub in FERC | 12,230 | Tier 6 | Yes | Dist | 230 |  | 7 | 7 |  | T1 | non-HFTD - Non-critical Substation | 1 | 0 | 362 | 178 | 0 |  | 7 | 4 | 1 | 0 | 6 | 10 |  | 28 | 14 | N | 391
ETS.16.12053 | BAIR | ETS.16.12053 | Central Coast | San Carlos | T&D | 12,115,60 | Tier 6 | Yes | T | 115 |  | 9 | 8 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 240 | 178 | 0 |  | 8 | 4 | 2 | 0 | 6 | 10 |  | 30 | 12 | N | 644
ETS.10.12054 | BAKERSFIELD | ETS.10.12054 | South Valley | Bakersfield | DSub in FERC | 12,21,230 | Tier 6 | Yes | Dist | 230 |  | 5 | 7 |  | T1 | non-HFTD - Non-critical Substation | 6 | 0 | 362 | 178 | 0 |  | 7 | 4 | 6 | 0 | 6 | 10 |  | 33 | 9 | N | 394
ETS.07.16490 | BALCH #1 PH | ETS.07.16490 | South Valley | Fresno | 0 | 115 | Tier 6 | No | G | 115 |  | 2 | 4 |  | T2 | HFTD - Non-critical Substation | 1 | 0 | 190 | 178 | 0 |  | 4 | 8 | 1 | 0 | 4 | 10 |  | 27 | 15 | N | 603
ETS.07.16320 | BALCH #2 PH | ETS.07.16320 | South Valley | Fresno | 0 | 230 | Tier 6 | No | G | 230 | 8 | 4 | 4 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | 31 | 1 | 0 |  | 4 | 8 | n/a | 0 | 2 | 5 |  | 19 | 23 | N | n/a
ETS.22.12055 | BALFOUR | ETS.22.12055 | Central Coast | Concord | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 198 | 178 | 0 |  | 2 | 4 | n/a | 0 | 4 | 10 |  | 20 | 22 | N | 462
ETS.23.13512 | BANCROFT | ETS.23.13512 | Bay Area | Oakport | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 1 | 227 | 178 | 0 |  | 1 | 4 | n/a | 1 | 6 | 10 |  | 22 | 20 | N | 662
ETS.19.12056 | BANGOR | ETS.19.12056 | North Coast | Table Mountain | DSub in FERC | 12,115 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T2 | HFTD - Non-critical Substation | 3 | 5 | 225 | 178 | 0 |  | 2 | 8 | 3 | 5 | 6 | 10 |  | 34 | 8 | N | 82
ETS.12.12057 | BANK OF AMERICA | ETS.12.12057 | Bay Area | Martin | Dist. Single Cust. | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 3 | 1 | 0 |  | 1 | 4 | n/a | 0 | 2 | 5 |  | 12 | 30 | N | n/a
ETS.26.16410 | BANTA | ETS.26.16410 | North Valley | Tesla | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 362 | 178 | 0 |  | 2 | 4 | 2 | 0 | 6 | 10 |  | 24 | 18 | N | 583
ETS.23.13513 | BARRETT | ETS.23.13513 | Bay Area | Oakport | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 227 | 178 | 0 |  | 1 | 4 | 3 | 0 | 6 | 10 |  | 24 | 18 | N | 635
ETS.04.12063 | BARRY | ETS.04.12063 | North Valley | Del Mar | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 227 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 322
ETS.07.12064 | BARTON | ETS.07.12064 | South Valley | Fresno | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 5 | 0 | 225 | 178 | 0 |  | 6 | 4 | 5 | 0 | 6 | 10 |  | 31 | 11 | N | 499
ETS.13.12065 | BASALT | ETS.13.12065 | North Coast | McMaude | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 2 | 258 | 178 | 0 |  | 2 | 4 | n/a | 2 | 6 | 10 |  | 24 | 18 | N | 119
ETS.21.12066 | BATAVIA | ETS.21.12066 | North Valley | Vaca-Dixon | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 198 | 178 | 0 |  | 2 | 4 | n/a | 0 | 4 | 10 |  | 20 | 22 | N | 767
ETS.16.12067 | BAY MEADOWS | ETS.16.12067 | Central Coast | San Carlos | DSub in FERC | 12,21,115 | Tier 6 | Yes | Dist | 115 |  | 6 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 1 | 416 | 178 | 0 |  | 6 | 4 | n/a | 1 | 6 | 10 |  | 27 | 15 | N | 373
ETS.17.12069 | BAYWOOD | ETS.17.12069 | South Valley | Pismo | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 19 | 1 | 0 |  | 2 | 4 | 2 | 0 | 2 | 5 |  | 15 | 27 | N | 534
ETS.12.12071 | BEACH ST | ETS.12.12071 | Bay Area | Martin | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 258 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 572
ETS.14.12073 | BEAR VALLEY | ETS.14.12073 | North Valley | Merced | DSub in FERC | 21,70 | Tier 6 | No | Dist | 70 |  | 2 | 2 |  | T2 | HFTD - Non-critical Substation | n/a | 2 | 238 | 178 | 0 |  | 2 | 8 | n/a | 2 | 6 | 10 |  | 28 | 14 | N | 179
ETS.23.13516 | BECK | ETS.23.13516 | Bay Area | Oakport | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 202 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 739
ETS.19.16605 | BELDEN PH | ETS.19.16605 | North Coast | Table Mountain | 0 | 230 | Tier 6 | No | T | 230 |  | 3 | 5 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 5 | 8 | n/a | 0 | 1 | 1 |  | 15 | 27 | N | n/a
ETS.04.12076 | BELL | ETS.04.12076 | North Valley | Del Mar | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T2/3A | HFTD - Non-critical Substation | n/a | 3 | 225 | 178 | 0 |  | 6 | 6 | n/a | 3 | 6 | 10 |  | 31 | 11 | N | 164
ETS.16.12079 | BELLE HAVEN | ETS.16.12079 | Central Coast | San Carlos | DSub in FERC | 4,12,60 | Tier 6 | No | Dist | 60 |  | 7 | 2 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 240 | 178 | 0 |  | 2 | 4 | 2 | 0 | 6 | 10 |  | 24 | 18 | N | 382
ETS.13.12080 | BELLEVUE | ETS.13.12080 | North Coast | McMaude | DSub in FERC | 12,21,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 5 | 2 | 258 | 178 | 0 |  | 6 | 4 | 5 | 2 | 6 | 10 |  | 33 | 9 | N | 117
ETS.18.10052 | BELLOTA | ETS.18.10052 | North Valley | Stockton | T-Sub | 230,115 | Tier 4 | Yes | T | 230 |  | 22 | 9 |  | T1 | non-HFTD - Critical Substation | 8 | 0 | 225 | 178 | 0 |  | 9 | 4 | 8 | 0 | 6 | 10 |  | 37 | 5 | N | n/a
ETS.10.12081 | BELLRIDGE 1A | ETS.10.12081 | South Valley | Bakersfield | DSub in FERC | 4,115 | Tier 6 | No | Dist | 115 |  | 3 | 3 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 198 | 178 | 0 |  | 3 | 4 | n/a | 0 | 4 | 10 |  | 21 | 21 | N | 770
ETS.10.12082 | BELLRIDGE 1B | ETS.10.12082 | South Valley | Bakersfield | DSub in FERC | 4115 | Tier 6 | No | Dist | 115 |  | n/a | 3 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 198 | 178 | 0 |  | 3 | 4 | n/a | 0 | 4 | 10 |  | 21 | 21 | N | 757
ETS.16.12083 | BELMONT | ETS.16.12083 | Central Coast | San Carlos | DSub in FERC | 4,12,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 1 | 317 | 178 | 0 |  | 6 | 4 | n/a | 1 | 6 | 10 |  | 27 | 15 | N | 272
ETS.15.12085 | BEN LOMOND | ETS.15.12085 | Central Coast | Moss Landing | Unit Sub | 4,21 | Tier 6 | No | Dist | 21 |  | n/a | 1 |  | T3 | HFTD - Non-critical Substation | n/a | 2 | 202 | 178 | 0 |  | 1 | 10 | n/a | 2 | 6 | 10 |  | 29 | 13 | N | 247
ETS.02.12086 | BENTON | ETS.02.12086 | North Coast | Cottonwood | SW STA - Trans | 60 | Tier 6 | No | T | 60 |  | 3 | 5 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | 12 | 1 | 0 |  | 5 | 8 | n/a | 0 | 2 | 5 |  | 20 | 22 | N | n/a
ETS.16.12087 | BERESFORD | ETS.16.12087 | Central Coast | San Carlos | DSub in FERC | 4,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 1 | 362 | 178 | 0 |  | 2 | 4 | n/a | 1 | 6 | 10 |  | 23 | 19 | N | 224
ETS.23.13550 | BERKELEY F | ETS.23.13550 | Bay Area | Oakport | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | 9 | 1 | 238 | 178 | 0 |  | 1 | 4 | 9 | 1 | 6 | 10 |  | 31 | 11 | N | 108
ETS.23.13366 | BERKELEY T | ETS.23.13366 | Bay Area | Oakport | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 362 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 653
ETS.08.14963 | BERRENDA A | ETS.08.14963 | South Valley | Gates | Dist. Single Cust. | 4,70 | Tier 6 | No | Dist | 70 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 202 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 749
ETS.10.12089 | BERRENDA C | ETS.10.12089 | South Valley | Bakersfield | DSub in FERC | 4,70 | Tier 6 | No | Dist | 70 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 188 | 178 | 0 |  | 2 | 4 | n/a | 0 | 4 | 10 |  | 20 | 22 | N | 751
ETS.15.12092 | BIG BASIN | ETS.15.12092 | Central Coast | Moss Landing | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T3 | HFTD - Non-critical Substation | n/a | 2 | 227 | 178 | 0 |  | 2 | 10 | n/a | 2 | 6 | 10 |  | 30 | 12 | N | 86
ETS.19.12093 | BIG BEND | ETS.19.12093 | North Coast | Table Mountain | SW STA - Trans | 115 | Tier 6 | Yes | T | 115 |  | 3 | 8 |  | T3 | HFTD - Non-critical Substation | n/a | 5 | n/a | n/a | 0 |  | 8 | 10 | n/a | 5 | 1 | 1 |  | 25 | 17 | N | 132
ETS.06.12095 | BIG LAGOON | ETS.06.12095 | North Coast | Eureka | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | 2 | 2 | 240 | 178 | 0 |  | 2 | 4 | 2 | 2 | 6 | 10 |  | 26 | 16 | N | 405
ETS.19.13517 | BIG MEADOWS | ETS.19.13517 | North Coast | Table Mountain | DSub in FERC | 21,44,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2 | HFTD - Non-critical Substation | 3 | 0 | 227 | 178 | 0 |  | 2 | 8 | 3 | 0 | 6 | 10 |  | 29 | 13 | N | 233
ETS.20.12096 | BIG RIVER | ETS.20.12096 | North Coast | Ukiah | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2 | HFTD - Non-critical Substation | 4 | 1 | 258 | 178 | 0 |  | 2 | 8 | 4 | 1 | 6 | 10 |  | 31 | 11 | N | 115
ETS.15.13790 | BIG TREES | ETS.15.13790 | Central Coast | Moss Landing | Unit Sub | 4,21 | Tier 6 | No | Dist | 21 |  | n/a | 1 |  | T2/3A | HFTD - Non-critical Substation | n/a | 2 | 202 | 178 | 0 |  | 1 | 6 | n/a | 2 | 6 | 10 |  | 25 | 17 | N | 500
ETS.07.12098 | BIOLA | ETS.07.12098 | South Valley | Fresno | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 362 | 178 | 0 |  | 2 | 4 | 3 | 0 | 6 | 10 |  | 25 | 17 | N | 558
ETS.21.16485 | BIRDS LANDING SW STA | ETS.21.16485 | North Valley | Vaca-Dixon | SW STA - Trans | 230 | Tier 6 | Yes | T | 230 |  | 8 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 6 | 1 | 0 |  | 8 | 4 | n/a | 0 | 2 | 5 |  | 19 | 23 | N | n/a
ETS.10.12099 | BLACKWELL | ETS.10.12099 | South Valley | Bakersfield | DSub in FERC | 12,21,70 | Tier 6 | No | Dist | 70 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 198 | 178 | 0 |  | 2 | 4 | 2 | 0 | 4 | 10 |  | 22 | 20 | N | 705
ETS.15.13520 | BLAINE ST | ETS.15.13520 | Central Coast | Moss Landing | Unit Sub | 4,21 | Tier 6 | No | Dist | 21 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 1 | 4 | n/a | 0 | 1 | 1 |  | 7 | 35 | N | n/a
ETS.06.12100 | BLUE LAKE | ETS.06.12100 | North Coast | Eureka | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 2 | 227 | 178 | 0 |  | 2 | 4 | n/a | 2 | 6 | 10 |  | 24 | 18 | N | 149
ETS.02.12102 | BOGARD | ETS.02.12102 | North Coast | Cottonwood | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2 | HFTD - Non-critical Substation | 3 | 0 | 188 | 178 | 0 |  | 2 | 8 | 3 | 0 | 4 | 10 |  | 27 | 15 | N | 761
ETS.04.12103 | BOGUE | ETS.04.12103 | North Valley | Del Mar | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 6 | 4 | n/a | 0 | 6 | 10 |  | 26 | 16 | N | 318
ETS.13.12104 | BOLINAS | ETS.13.12104 | North Coast | McMaude | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2 | HFTD - Non-critical Substation | n/a | 2 | 48 | 1 | 0 |  | 2 | 8 | n/a | 2 | 2 | 5 |  | 19 | 23 | N | 111
ETS.14.12108 | BONITA | ETS.14.12108 | North Valley | Merced | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | n/a | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 683
ETS.14.12109 | BONITA JCT | ETS.14.12109 | North Valley | Merced | 0 | 70 | Tier 6 | No | Dist | 70 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 2 | 4 | n/a | 0 | 1 | 1 |  | 8 | 34 | N | n/a
ETS.14.12109 | BONITA JCT SW STA | ETS.14.12109 | North Valley | Merced |  |  | Tier 6 | No | Dist | 70 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 2 | 4 | n/a | 0 | 1 | 1 |  | 8 | 34 | N | n/a
ETS.04.13521 | BONNIE NOOK | ETS.04.13521 | North Valley | Del Mar | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T3 | HFTD - Non-critical Substation | 3 | 3 | 258 | 178 | 0 |  | 2 | 10 | 3 | 3 | 6 | 10 |  | 34 | 8 | N | 134
ETS.07.10047 | BORDEN | ETS.07.10047 | South Valley | Fresno | T&D | 12,230,70 | Tier 6 | Yes | T | 230 |  | 11 | 8 |  | T1 | non-HFTD - Non-critical Substation | 5 | 0 | 256 | 178 | 0 |  | 8 | 4 | 5 | 0 | 6 | 10 |  | 33 | 9 | N | 345
ETS.15.12111 | BORONDA | ETS.15.12111 | Central Coast | Moss Landing | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 240 | 178 | 0 |  | 2 | 4 | 2 | 0 | 6 | 10 |  | 24 | 18 | N | 675
ETS.08.13791 | BOSWELL | ETS.08.13791 | South Valley | Gates | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 284 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 737
ETS.07.12113 | BOWLES | ETS.07.12113 | South Valley | Fresno | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 48 | 1 | 0 |  | 2 | 4 | 3 | 0 | 2 | 5 |  | 16 | 26 | N | 618
ETS.22.10050 | BRENTWOOD | ETS.22.10050 | Central Coast | Concord | DSub in FERC | 21,230 | Tier 6 | Yes | Dist | 230 |  | 5 | 7 |  | T1 | non-HFTD - Non-critical Substation | 6 | 1 | 317 | 178 | 0 |  | 7 | 4 | 6 | 1 | 6 | 10 |  | 34 | 8 | N | 123
ETS.06.12116 | BRIDGEVILLE | ETS.06.12116 | North Coast | Eureka | T&D | 12,60,115 | Tier 6 | Yes | T | 115 |  | 11 | 8 |  | T2 | HFTD - Non-critical Substation | 2 | 2 | 48 | 1 | 0 |  | 8 | 8 | 2 | 2 | 2 | 5 |  | 27 | 15 | N | 157
ETS.04.10051 | BRIGHTON | ETS.04.10051 | North Valley | Del Mar | T-Sub | 230,115 | Tier 6 | Yes | T | 230 |  | 10 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 317 | 178 | 0 |  | 8 | 4 | n/a | 0 | 6 | 10 |  | 28 | 14 | N | n/a
ETS.03.12119 | BRITTON | ETS.03.12119 | Central Coast | Cupertino | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 6 | 0 | 240 | 178 | 0 |  | 6 | 4 | 6 | 0 | 6 | 10 |  | 32 | 10 | N | 379
ETS.23.13523 | BROOKSIDE | ETS.23.13523 | Bay Area | Oakport | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 207 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 715
ETS.19.12121 | BROWNS VALLEY | ETS.19.12121 | North Coast | Table Mountain | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2 | HFTD - Non-critical Substation | 3 | 4 | 240 | 178 | 0 |  | 2 | 8 | 3 | 4 | 6 | 10 |  | 33 | 9 | N | 323
ETS.19.16810 | BROWNS VALLEY ENERGY | ETS.19.16810 | North Coast | Table Mountain | N/A | 60 | Tier 6 | No | n/a | 60 |  | n/a | 5 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 5 | 4 | n/a | 0 | 1 | 1 |  | 11 | 31 | N | n/a
ETS.04.12122 | BRUNSWICK | ETS.04.12122 | North Valley | Del Mar | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T2/3A | HFTD - Non-critical Substation | 4 | 4 | 317 | 178 | 0 |  | 6 | 6 | 4 | 4 | 6 | 10 |  | 36 | 6 | Y | 17
ETS.22.13524 | BRYANT | ETS.22.13524 | Central Coast | Concord | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T2/3A | HFTD - Non-critical Substation | n/a | 2 | 202 | 178 | 0 |  | 1 | 6 | n/a | 2 | 6 | 10 |  | 25 | 17 | N | 439
ETS.19.10046 | BUCKS CREEK PH | ETS.19.10046 | North Coast | Table Mountain | 0 | 230 | Tier 6 | No | G | 230 | 8 | 2 | 4 |  | T3 | HFTD - Non-critical Substation | 4 | 4 | 202 | 178 | 0 |  | 4 | 10 | 4 | 4 | 6 | 10 |  | 38 | 4 | N | 143
ETS.17.12125 | BUELLTON | ETS.17.12125 | South Valley | Pismo | DSub in FERC | 12,115 | Tier 6 | No | Dist | 115 |  | 0 | 3 |  | T2/3A | HFTD - Non-critical Substation | n/a | 0 | 256 | 178 | 0 |  | 3 | 6 | n/a | 0 | 6 | 10 |  | 25 | 17 | N | 384
ETS.15.12126 | BUENA VISTA | ETS.15.12126 | Central Coast | Moss Landing | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 196 | 178 | 0 |  | 2 | 4 | n/a | 0 | 4 | 10 |  | 20 | 22 | N | 297
ETS.07.12127 | BULLARD | ETS.07.12127 | South Valley | Fresno | DSub in FERC | 12,21,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 258 | 178 | 0 |  | 6 | 4 | n/a | 0 | 6 | 10 |  | 26 | 16 | N | 540
ETS.16.12128 | BURLINGAME | ETS.16.12128 | Central Coast | San Carlos | DSub in FERC | 4,21,115 | Tier 6 | Yes | Dist | 115 |  | 3 | 6 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 225 | 178 | 0 |  | 6 | 4 | 3 | 0 | 6 | 10 |  | 29 | 13 | N | 585
ETS.02.13525 | BURNEY | ETS.02.13525 | North Coast | Cottonwood | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2/3A | HFTD - Non-critical Substation | 3 | 0 | 240 | 178 | 0 |  | 2 | 6 | 3 | 0 | 6 | 10 |  | 27 | 15 | N | 344
ETS.15.12129 | BURNS | ETS.15.12129 | Central Coast | Moss Landing | DSub not in FERC | 21,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T3 | HFTD - Non-critical Substation | n/a | 2 | 186 | 178 | 0 |  | 2 | 10 | n/a | 2 | 4 | 10 |  | 28 | 14 | N | 434
ETS.19.16600 | BUTT VALLEY PH | ETS.19.16600 | North Coast | Table Mountain | N/A | 115 | Tier 6 | No | G | 115 |  | 2 | 4 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 4 | 8 | n/a | 0 | 1 | 1 |  | 14 | 28 | N | n/a
ETS.19.12132 | BUTTE | ETS.19.12132 | North Coast | Table Mountain | T&D | 12,115,60 | Tier 6 | Yes | T | 115 |  | 12 | 8 |  | T1 | non-HFTD - Non-critical Substation | 5 | 6 | 256 | 178 | 0 |  | 8 | 4 | 5 | 6 | 6 | 10 |  | 39 | 3 | N | 284
ETS.18.13761 | CABBAGE PATCH SW STA | ETS.18.13761 | North Valley | Stockton | SW STA - Dist | 12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | 3 | 1 | 0 |  | 1 | 8 | n/a | 0 | 2 | 5 |  | 16 | 26 | N | n/a
ETS.17.13832 | CABRILLO | ETS.17.13832 | South Valley | Pismo | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 3 | 6 |  | T2/3A | HFTD - Non-critical Substation | n/a | 0 | 238 | 178 | 0 |  | 6 | 6 | n/a | 0 | 6 | 10 |  | 28 | 14 | N | 436
ETS.10.12135 | CADET | ETS.10.12135 | South Valley | Bakersfield | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 284 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 745
ETS.10.16350 | CAL WATER | ETS.10.16350 | South Valley | Bakersfield | DSub in FERC | 12,115 | Tier 6 | No | Dist | 115 |  | 2 | 3 |  | T1 | non-HFTD - Non-critical Substation | n/a | 3 | 225 | 178 | 0 |  | 3 | 4 | n/a | 3 | 6 | 10 |  | 26 | 16 | N | 196
ETS.18.12137 | CALAVERAS CEMENT | ETS.18.12137 | North Valley | Stockton | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T2 | HFTD - Non-critical Substation | n/a | 3 | 258 | 178 | 0 |  | 2 | 8 | n/a | 3 | 6 | 10 |  | 29 | 13 | N | 96
ETS.08.12138 | CALFLAX | ETS.08.12138 | South Valley | Gates | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 240 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 729
ETS.10.16715 | CALIENTE SW STA | ETS.10.16715 | South Valley | Bakersfield | SW STA - Trans | 230 | Tier 6 | Yes | T | 230 |  | 5 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 7 | 1 | 0 |  | 8 | 4 | n/a | 0 | 2 | 5 |  | 19 | 23 | N | n/a
ETS.07.12140 | CALIFORNIA AVE | ETS.07.12140 | South Valley | Fresno | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 6 | 6 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 238 | 178 | 0 |  | 6 | 4 | 3 | 0 | 6 | 10 |  | 29 | 13 | N | 286
ETS.17.16805 | CALIFORNIA FLATS SW STA | ETS.17.16805 | South Valley | Pismo | SW STA - Trans | 230 | Tier 6 | No | T | 230 |  | n/a | 5 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 6 | 1 | 0 |  | 5 | 4 | n/a | 0 | 2 | 5 |  | 16 | 26 | N | n/a
ETS.13.12141 | CALISTOGA | ETS.13.12141 | North Coast | McMaude | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2/3A | HFTD - Non-critical Substation | 3 | 5 | 225 | 178 | 0 |  | 2 | 6 | 3 | 5 | 6 | 10 |  | 32 | 10 | Y | 24
ETS.17.12142 | CALLENDER SW STA | ETS.17.12142 | South Valley | Pismo | SW STA - Trans | 115 | Tier 6 | Yes | T | 115 |  | 3 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 6 | 1 | 0 |  | 8 | 4 | n/a | 0 | 2 | 5 |  | 19 | 23 | N | n/a
ETS.20.12143 | CALPELLA | ETS.20.12143 | North Coast | Ukiah | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T2/3A | HFTD - Non-critical Substation | 3 | 2 | 258 | 178 | 0 |  | 2 | 6 | 3 | 2 | 6 | 10 |  | 29 | 13 | N | 186
ETS.17.12147 | CAMBRIA | ETS.17.12147 | South Valley | Pismo | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 0 | 2 |  | T2/3A | HFTD - Non-critical Substation | 4 | 0 | 362 | 178 | 0 |  | 2 | 6 | 4 | 0 | 6 | 10 |  | 28 | 14 | N | 531
ETS.07.12148 | CAMDEN | ETS.07.12148 | South Valley | Fresno | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 258 | 178 | 0 |  | 2 | 4 | 3 | 0 | 6 | 10 |  | 25 | 17 | N | 474
ETS.15.12150 | CAMP EVERS | ETS.15.12150 | Central Coast | Moss Landing | DSub in FERC | 21,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T2/3A | HFTD - Non-critical Substation | n/a | 2 | 225 | 178 | 0 |  | 6 | 6 | n/a | 2 | 6 | 10 |  | 30 | 12 | N | 21
ETS.15.12152 | CAMPHORA | ETS.15.12152 | Central Coast | Moss Landing | DSub in FERC | 4,12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | 2 | 1 | 202 | 178 | 0 |  | 2 | 4 | 2 | 1 | 6 | 10 |  | 25 | 17 | N | 142
ETS.14.12153 | CANAL | ETS.14.12153 | North Valley | Merced | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 5 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 424
ETS.08.12154 | CANTUA | ETS.08.12154 | South Valley | Gates | DSub in FERC | 12,115 | Tier 6 | No | Dist | 70 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 202 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 676
ETS.02.12155 | CAPAY | ETS.02.12155 | North Coast | Cottonwood | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 362 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 492
ETS.02.16685 | CARBERRY SW STA | ETS.02.16685 | North Coast | Cottonwood | SW STA - Trans | 230 | Tier 6 | Yes | T | 230 |  | 3 | 8 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | 6 | 1 | 0 |  | 8 | 8 | n/a | 0 | 2 | 5 |  | 23 | 19 | N | n/a
ETS.26.16425 | CARBONA | ETS.26.16425 | North Valley | Tesla | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 362 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 314
ETS.19.12160 | CARIBOU PH #1 | ETS.19.12160 | North Coast | Table Mountain | 0 | 230 | Tier 6 | Yes | T | 60 | 8 | 9 | 8 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | 16 | 1 | 0 |  | 8 | 8 | n/a | 0 | 2 | 5 |  | 23 | 19 | N | n/a
ETS.19.10197 | CARIBOU PH #2 | ETS.19.10197 | North Coast | Table Mountain | 0 | 230,115 | Tier 6 | Yes | T | 230 | 8 | 8 | 8 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | 258 | 178 | 0 |  | 8 | 8 | n/a | 0 | 6 | 10 |  | 32 | 10 | N | n/a
ETS.06.12161 | CARLOTTA | ETS.06.12161 | North Coast | Eureka | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2 | HFTD - Non-critical Substation | 2 | 2 | 240 | 178 | 0 |  | 2 | 8 | 2 | 2 | 6 | 10 |  | 30 | 12 | N | 74
ETS.15.13530 | CARMEL | ETS.15.13530 | Central Coast | Moss Landing | Unit Sub | 4,21 | Tier 6 | No | Dist | 21 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 258 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 665
ETS.10.13792 | CARNATION | ETS.10.13792 | South Valley | Bakersfield | DSub in FERC | 21,70 | Tier 6 | No | Dist | 70 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 186 | 178 | 0 |  | 2 | 4 | n/a | 0 | 4 | 10 |  | 20 | 22 | N | 687
ETS.10.12163 | CARNERAS | ETS.10.12163 | South Valley | Bakersfield | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 186 | 178 | 0 |  | 2 | 4 | 2 | 0 | 4 | 10 |  | 22 | 20 | N | 416
ETS.16.12164 | CAROLANDS | ETS.16.12164 | Central Coast | San Carlos | DSub in FERC | 4,12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | 4 | 1 | 225 | 178 | 0 |  | 2 | 4 | 4 | 1 | 6 | 10 |  | 27 | 15 | N | 277
ETS.13.12165 | CARQUINEZ | ETS.13.12165 | North Coast | McMaude | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 1 | 240 | 178 | 0 |  | 6 | 4 | n/a | 1 | 6 | 10 |  | 27 | 15 | Y | 409
ETS.10.12167 | CARRIZO PLAINS | ETS.10.12167 | South Valley | Bakersfield | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 2 | 6 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 198 | 178 | 0 |  | 6 | 4 | 2 | 0 | 4 | 10 |  | 26 | 16 | N | 565
ETS.07.12169 | CARUTHERS | ETS.07.12169 | South Valley | Fresno | DSub in FERC | 12,60,70 | Tier 6 | No | Dist | 70 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 48 | 1 | 0 |  | 2 | 4 | n/a | 0 | 2 | 5 |  | 13 | 29 | N | 508
ETS.02.12170 | CASCADE | ETS.02.12170 | North Coast | Cottonwood | T-Sub | 115,60 | Tier 6 | Yes | T | 115 |  | 7 | 8 |  | T2 | HFTD - Non-critical Substation | 2 | 0 | 240 | 178 | 0 |  | 8 | 8 | 2 | 0 | 6 | 10 |  | 34 | 8 | N | n/a
ETS.15.13531 | CASSERLY | ETS.15.13531 | Central Coast | Moss Landing | Unit Sub | 4,21 | Tier 6 | No | Dist | 21 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 1 | 207 | 178 | 0 |  | 1 | 4 | n/a | 1 | 6 | 10 |  | 22 | 20 | N | 741
ETS.07.12172 | CASSIDY | ETS.07.12172 | South Valley | Fresno | DSub in FERC | 21,70 | Tier 6 | No | Dist | 70 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 48 | 1 | 0 |  | 2 | 4 | n/a | 0 | 2 | 5 |  | 13 | 29 | N | 285
ETS.12.12175 | CASTRO | ETS.12.12175 | Bay Area | Martin | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 227 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 674
ETS.09.10054 | CASTRO VALLEY | ETS.09.10054 | Central Coast | Hayward | DSub in FERC | 12,34,230 | Tier 6 | Yes | Dist | 230 |  | 5 | 7 |  | T1 | non-HFTD - Non-critical Substation | 7 | 2 | 200 | 178 | 0 |  | 7 | 4 | 7 | 2 | 4 | 10 |  | 34 | 8 | N | 10
ETS.15.12176 | CASTROVILLE | ETS.15.12176 | Central Coast | Moss Landing | DSub in FERC | 21,115 | Tier 6 | No | Dist | 115 |  | 3 | 3 |  | T1 | non-HFTD - Non-critical Substation | 4 | 0 | 238 | 178 | 0 |  | 3 | 4 | 4 | 0 | 6 | 10 |  | 27 | 15 | N | 316
ETS.04.12179 | CATLETT | ETS.04.12179 | North Valley | Del Mar | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 207 | 178 | 0 |  | 2 | 4 | 3 | 0 | 6 | 10 |  | 25 | 17 | N | 341
ETS.10.12180 | CAWELO B | ETS.10.12180 | South Valley | Bakersfield | DSub in FERC | 4,70 | Tier 6 | No | Dist | 70 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 186 | 178 | 0 |  | 2 | 4 | n/a | 0 | 4 | 10 |  | 20 | 22 | N | 748
ETS.10.12181 | CAWELO C | ETS.10.12181 | South Valley | Bakersfield | DSub in FERC | 4,115 | Tier 6 | Yes | Dist | 115 |  | 2 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 207 | 178 | 0 |  | 6 | 4 | n/a | 0 | 6 | 10 |  | 26 | 16 | N | 759
ETS.26.16390 | CAYETANO | ETS.26.16390 | North Valley | Tesla | DSub in FERC | 21,230 | Tier 6 | Yes | Dist | 230 |  | 3 | 7 |  | T2 | HFTD - Non-critical Substation | n/a | 1 | 225 | 178 | 0 |  | 7 | 8 | n/a | 1 | 6 | 10 |  | 32 | 10 | N | 174
ETS.17.12182 | CAYUCOS | ETS.17.12182 | South Valley | Pismo | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 372
ETS.02.12184 | CEDAR CREEK | ETS.02.12184 | North Coast | Cottonwood | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T3 | HFTD - Non-critical Substation | n/a | 3 | 196 | 178 | 0 |  | 2 | 10 | n/a | 3 | 4 | 10 |  | 29 | 13 | N | 177
ETS.10.13793 | CELERON HILL | ETS.10.13793 | South Valley | Bakersfield | DSub in FERC | n/a | Tier 6 | No | Dist | 70 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 216 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 766
ETS.19.12186 | CENTERVILLE PH | ETS.19.12186 | North Coast | Table Mountain | 0 | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T3 | HFTD - Non-critical Substation | 4 | 0 | 1 | 1 | 0 |  | 2 | 10 | 4 | 0 | 2 | 5 |  | 23 | 19 | N | n/a
ETS.19.12188 | CHALLENGE | ETS.19.12188 | North Coast | Table Mountain | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T3 | HFTD - Non-critical Substation | 4 | 4 | 362 | 178 | 0 |  | 2 | 10 | 4 | 4 | 6 | 10 |  | 36 | 6 | N | 103
ETS.18.12189 | CHANNEL | ETS.18.12189 | North Valley | Stockton | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 548
ETS.10.12190 | CHARCA | ETS.10.12190 | South Valley | Bakersfield | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 227 | 178 | 0 |  | 6 | 4 | 2 | 0 | 6 | 10 |  | 28 | 14 | N | 647
ETS.18.12193 | CHEROKEE | ETS.18.12193 | North Valley | Stockton | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 225 | 178 | 0 |  | 2 | 4 | 3 | 0 | 6 | 10 |  | 25 | 17 | N | 317
ETS.19.13958 | CHESTER | ETS.19.13958 | North Coast | Table Mountain | DSub in FERC | 13.8,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2/3A | HFTD - Non-critical Substation | n/a | 0 | 258 | 178 | 0 |  | 2 | 6 | n/a | 0 | 6 | 10 |  | 24 | 18 | N | 731
ETS.19.12196 | CHICO A | ETS.19.12196 | North Coast | Table Mountain | DSub in FERC | 4,12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | 4 | 0 | 227 | 178 | 0 |  | 2 | 4 | 4 | 0 | 6 | 10 |  | 26 | 16 | N | 634
ETS.19.12197 | CHICO B | ETS.19.12197 | North Coast | Table Mountain | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 258 | 178 | 0 |  | 6 | 4 | 3 | 0 | 6 | 10 |  | 29 | 13 | N | 390
ETS.19.13534 | CHICO C | ETS.19.13534 | North Coast | Table Mountain | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 198 | 178 | 0 |  | 1 | 4 | n/a | 0 | 4 | 10 |  | 19 | 23 | N | 722
ETS.04.16570 | CHILI BAR PH | ETS.04.16570 | North Valley | Del Mar | 0 | 21 | Tier 6 | No | G | 21 |  | n/a | 4 |  | T3 | HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 4 | 10 | n/a | 0 | 1 | 1 |  | 16 | 26 | N | n/a
ETS.17.12201 | CHOLAME | ETS.17.12201 | South Valley | Pismo | DSub in FERC | 12,21,70 | Tier 6 | No | Dist | 70 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 207 | 178 | 0 |  | 2 | 4 | 2 | 0 | 6 | 10 |  | 24 | 18 | N | 411
ETS.14.12204 | CHOWCHILLA | ETS.14.12204 | North Valley | Merced | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T1 | non-HFTD - Non-critical Substation | 5 | 0 | 240 | 178 | 0 |  | 6 | 4 | 5 | 0 | 6 | 10 |  | 31 | 11 | N | 619
ETS.22.12205 | CHRISTIE | ETS.22.12205 | Central Coast | Concord | T-Sub | 115,60 | Tier 6 | Yes | T | 115 |  | 9 | 8 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | 79 | 1 | 0 |  | 8 | 8 | n/a | 0 | 3 | 5 |  | 24 | 18 | N | n/a
ETS.19.12212 | CLARK RD | ETS.19.12212 | North Coast | Table Mountain | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2 | HFTD - Non-critical Substation | 2 | 6 | 238 | 178 | 0 |  | 2 | 8 | 2 | 6 | 6 | 10 |  | 34 | 8 | N | 181
ETS.04.12213 | CLARKSVILLE | ETS.04.12213 | North Valley | Del Mar | DSub in FERC | 21,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T2/3A | HFTD - Non-critical Substation | n/a | 2 | 225 | 178 | 0 |  | 6 | 6 | n/a | 2 | 6 | 10 |  | 30 | 12 | N | 94
ETS.18.12214 | CLAY | ETS.18.12214 | North Valley | Stockton | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T2 | HFTD - Non-critical Substation | 4 | 1 | 227 | 178 | 0 |  | 2 | 8 | 4 | 1 | 6 | 10 |  | 31 | 11 | N | 154
ETS.22.12215 | CLAYTON | ETS.22.12215 | Central Coast | Concord | DSub in FERC | 12,21,115 | Tier 6 | Yes | Dist | 115 |  | 12 | 6 |  | T1 | non-HFTD - Non-critical Substation | 4 | 1 | 498 | 178 | 0 |  | 6 | 4 | 4 | 1 | 6 | 10 |  | 31 | 11 | N | 70
ETS.20.12216 | CLEAR LAKE | ETS.20.12216 | North Coast | Ukiah | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 5 | 2 |  | T2/3A | HFTD - Non-critical Substation | n/a | 2 | 500 | 178 | 0 |  | 2 | 6 | n/a | 2 | 6 | 10 |  | 26 | 16 | Y | 184
ETS.15.13536 | CLIFF DR | ETS.15.13536 | Central Coast | Moss Landing | Unit Sub | 4,21 | Tier 6 | No | Dist | 21 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | 2 | 1 | 23 | 1 | 0 |  | 1 | 4 | 2 | 1 | 2 | 5 |  | 15 | 27 | N | 465
ETS.13.12218 | CLOVERDALE | ETS.13.12218 | North Coast | McMaude | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 3 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 4 | 500 | 178 | 0 |  | 6 | 4 | n/a | 4 | 6 | 10 |  | 30 | 12 | Y | 30
ETS.07.12219 | CLOVIS | ETS.07.12219 | South Valley | Fresno | DSub in FERC | 12,21,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 7 | 0 | 238 | 178 | 0 |  | 6 | 4 | 7 | 0 | 6 | 10 |  | 33 | 9 | N | 122
ETS.17.16260 | CMC | ETS.17.16260 | South Valley | Pismo | 3rd Party | 12,115 | Tier 6 | No | Dist | 115 |  | 2 | 3 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | 200 | 178 | 0 |  | 3 | 8 | n/a | 0 | 4 | 10 |  | 25 | 17 | N | 760
ETS.19.16615 | COAL CANYON PH | ETS.19.16615 | North Coast | Table Mountain | 0 | 12 | Tier 6 | No | G | 12 |  | n/a | 4 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 4 | 4 | n/a | 0 | 1 | 1 |  | 10 | 32 | N | n/a
ETS.08.12222 | COALINGA #1 | ETS.08.12222 | South Valley | Gates | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 5 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 362 | 178 | 0 |  | 2 | 4 | 3 | 0 | 6 | 10 |  | 25 | 17 | N | 332
ETS.08.12223 | COALINGA #2 | ETS.08.12223 | South Valley | Gates | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 19 | 1 | 0 |  | 2 | 4 | n/a | 0 | 2 | 5 |  | 13 | 29 | N | 349
ETS.07.12224 | COARSEGOLD | ETS.07.12224 | South Valley | Fresno | DSub in FERC | 21,115 | Tier 6 | No | Dist | 115 |  | 0 | 3 |  | T2 | HFTD - Non-critical Substation | n/a | 1 | 238 | 178 | 0 |  | 3 | 8 | n/a | 1 | 6 | 10 |  | 28 | 14 | N | 225
ETS.15.10057 | COBURN | ETS.15.10057 | Central Coast | Moss Landing | T-Sub | 230,60 | Tier 6 | No | T | 230 |  | 11 | 5 |  | T1 | non-HFTD - Non-critical Substation | 5 | 0 | 240 | 178 | 0 |  | 5 | 4 | 5 | 0 | 6 | 10 |  | 30 | 12 | N | n/a
ETS.02.15738 | COLEMAN PH | ETS.02.15738 | North Coast | Cottonwood | 0 | 60 | Tier 6 | No | G | 60 |  | 4 | 4 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | 12 | 1 | 0 |  | 4 | 8 | n/a | 0 | 2 | 5 |  | 19 | 23 | N | n/a
ETS.19.10058 | COLGATE PH | ETS.19.10058 | North Coast | Table Mountain | 3rd Party | 230,60 | Tier 6 | No | T | 230 |  | 5 | 5 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | 256 | 178 | 0 |  | 5 | 8 | n/a | 0 | 6 | 10 |  | 29 | 13 | N | n/a
ETS.19.12226 | COLGATE SW STA | ETS.19.12226 | North Coast | Table Mountain | SW STA - Trans | 60 | Tier 6 | No | T | 60 |  | 7 | 5 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | 4 | 1 | 0 |  | 5 | 8 | n/a | 0 | 2 | 5 |  | 20 | 22 | N | n/a
ETS.18.12228 | COLONY | ETS.18.12228 | North Valley | Stockton | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 240 | 178 | 0 |  | 2 | 4 | 3 | 0 | 6 | 10 |  | 25 | 17 | N | 608
ETS.19.12232 | COLUMBIA HILL | ETS.19.12232 | North Coast | Table Mountain | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T3 | HFTD - Non-critical Substation | n/a | 3 | 227 | 178 | 0 |  | 2 | 10 | n/a | 3 | 6 | 10 |  | 31 | 11 | N | 85
ETS.10.12234 | COLUMBUS | ETS.10.12234 | South Valley | Bakersfield | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 258 | 178 | 0 |  | 6 | 4 | 3 | 0 | 6 | 10 |  | 29 | 13 | N | 616
ETS.21.12236 | COLUSA | ETS.21.12236 | North Valley | Vaca-Dixon | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 258 | 178 | 0 |  | 2 | 4 | 2 | 0 | 6 | 10 |  | 24 | 18 | N | 661
ETS.21.13794 | COLUSA JUNCTION | ETS.21.13794 | North Valley | Vaca-Dixon | 0 | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 200 | 178 | 0 |  | 2 | 4 | n/a | 0 | 4 | 10 |  | 20 | 22 | N | 692
ETS.21.16690 | COLUSA PP | ETS.21.16690 | North Valley | Vaca-Dixon | N/A | n/a | Tier 6 | No | n/a | n/a |  | n/a | 5 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 5 | 4 | n/a | 0 | 1 | 1 |  | 11 | 31 | N | n/a
ETS.22.13537 | CONCORD | ETS.22.13537 | Central Coast | Concord | Unit Sub | 4,21 | Tier 6 | No | Dist | 21 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 196 | 178 | 0 |  | 1 | 4 | n/a | 0 | 4 | 10 |  | 19 | 23 | N | 570
ETS.22.10056 | CONTRA COSTA | ETS.22.10056 | Central Coast | Concord | T&D | 21,115,230,60 | Tier 6 | Yes | T | 230 |  | 18 | 8 |  | T1 | non-HFTD - Non-critical Substation | 5 | 1 | 500 | 178 | 0 |  | 8 | 4 | 5 | 1 | 6 | 10 |  | 34 | 8 | N | 381
ETS.22.10055 | CONTRA COSTA PP SW STA | ETS.22.10055 | Central Coast | Concord | SW STA - Trans | 230 | Tier 4 | Yes | T | 230 | 9 | 18 | 9 |  | T1 | non-HFTD - Critical Substation | n/a | 0 | 22 | 1 | 0 |  | 9 | 4 | n/a | 0 | 2 | 5 |  | 20 | 22 | N | n/a
ETS.16.10204 | COOLEY LANDING | ETS.16.10204 | Central Coast | San Carlos | T-Sub | 115,60 | Tier 6 | Yes | T | 115 |  | 11 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 8 | 4 | n/a | 0 | 6 | 10 |  | 28 | 14 | N | n/a
ETS.07.12237 | COPPERMINE | ETS.07.12237 | South Valley | Fresno | DSub in FERC | 12,21,70 | Tier 6 | No | Dist | 70 |  | 5 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 258 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 158
ETS.10.12238 | COPUS | ETS.10.12238 | South Valley | Bakersfield | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 207 | 178 | 0 |  | 2 | 4 | 3 | 0 | 6 | 10 |  | 25 | 17 | N | 486
ETS.08.12239 | CORCORAN | ETS.08.12239 | South Valley | Gates | T&D | 12,115,70 | Tier 6 | Yes | T | 115 |  | 9 | 8 |  | T1 | non-HFTD - Non-critical Substation | 1 | 0 | 225 | 178 | 0 |  | 8 | 4 | 1 | 0 | 6 | 10 |  | 29 | 13 | N | 547
ETS.21.12240 | CORDELIA | ETS.21.12240 | North Valley | Vaca-Dixon | DSub in FERC | 12,60,115 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 240 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 587
ETS.02.12243 | CORNING | ETS.02.12243 | North Coast | Cottonwood | DSub in FERC | 4,12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | 6 | 2 | 500 | 178 | 0 |  | 2 | 4 | 6 | 2 | 6 | 10 |  | 30 | 12 | N | 25
ETS.13.16000 | CORONA | ETS.13.16000 | North Coast | McMaude | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 3 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 2 | 225 | 178 | 0 |  | 6 | 4 | n/a | 2 | 6 | 10 |  | 28 | 14 | N | 263
ETS.18.12245 | CORRAL | ETS.18.12245 | North Valley | Stockton | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2/3A | HFTD - Non-critical Substation | n/a | 1 | 225 | 178 | 0 |  | 2 | 6 | n/a | 1 | 6 | 10 |  | 25 | 17 | N | 36
ETS.21.10059 | CORTINA | ETS.21.10059 | North Valley | Vaca-Dixon | T&D | 12,115,230,60 | Tier 5 | Yes | T | 230 |  | 15 | 9 |  | T1 | non-HFTD - Critical Substation | 8 | 3 | 317 | 178 | 0 |  | 9 | 4 | 8 | 3 | 6 | 10 |  | 40 | 2 | N | 237
ETS.13.12246 | COTATI | ETS.13.12246 | North Coast | McMaude | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T2 | HFTD - Non-critical Substation | 4 | 1 | 227 | 178 | 0 |  | 2 | 8 | 4 | 1 | 6 | 10 |  | 31 | 11 | Y | 170
ETS.18.10060 | COTTLE | ETS.18.10060 | North Valley | Stockton | DSub in FERC | 17,230 | Tier 6 | Yes | Dist | 230 |  | 4 | 7 |  | T1 | non-HFTD - Non-critical Substation | 4 | 0 | 227 | 178 | 0 |  | 7 | 4 | 4 | 0 | 6 | 10 |  | 31 | 11 | N | 388
ETS.02.10064 | COTTONWOOD | ETS.02.10064 | North Coast | Cottonwood | T&D | 12,115,230,60 | Tier 4 | Yes | T | 230 |  | 34 | 9 |  | T2/3A | HFTD - Critical Substation | 7 | 3 | 258 | 178 | 0 |  | 9 | 6 | 7 | 3 | 6 | 10 |  | 41 | 1 | N | 219
ETS.18.12249 | COUNTRY CLUB | ETS.18.12249 | North Valley | Stockton | DSub in FERC | 4,12,60 | Tier 6 | No | Dist | 60 |  | 7 | 2 |  | T1 | non-HFTD - Non-critical Substation | 4 | 0 | 500 | 178 | 0 |  | 2 | 4 | 4 | 0 | 6 | 10 |  | 26 | 16 | N | 483
ETS.20.12251 | COVELO | ETS.20.12251 | North Coast | Ukiah | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 1 | 362 | 178 | 0 |  | 2 | 4 | n/a | 1 | 6 | 10 |  | 23 | 19 | N | 183
ETS.02.16755 | COW CREEK PH | ETS.02.16755 | North Coast | Cottonwood | 0 | 2,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 2 | 8 | n/a | 0 | 1 | 1 |  | 12 | 30 | N | n/a
ETS.03.16475 | COYOTE SW STA | ETS.03.16475 | Central Coast | Cupertino | SW STA - Trans | 230 | Tier 6 | Yes | T | 230 |  | 5 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 6 | 1 | 0 |  | 8 | 4 | n/a | 0 | 2 | 5 |  | 19 | 23 | N | n/a
ETS.15.16520 | CRAZY HORSE CANYON SW STA | ETS.15.16520 | Central Coast | Moss Landing | SW STA - Trans | 115 | Tier 6 | Yes | T | 115 |  | 6 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 6 | 1 | 0 |  | 8 | 4 | n/a | 0 | 2 | 5 |  | 19 | 23 | N | n/a
ETS.19.13538 | CRESCENT MILLS | ETS.19.13538 | North Coast | Table Mountain | DSub not in FERC | 21,44 | Tier 6 | No | Dist | 44 |  | n/a | 2 |  | T2/3A | HFTD - Non-critical Substation | 2 | 0 | 202 | 178 | 0 |  | 2 | 6 | 2 | 0 | 6 | 10 |  | 26 | 16 | N | 326
ETS.08.16820 | CRESCENT SW STA | ETS.08.16820 | South Valley | Gates | SW STA - Trans | 70 | Tier 6 | No | T | 70 |  | n/a | 5 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 5 | 4 | n/a | 0 | 1 | 1 |  | 11 | 31 | N | n/a
ETS.14.12259 | CRESSEY | ETS.14.12259 | North Valley | Merced | DSub in FERC | 21,115 | Tier 6 | No | Dist | 115 |  | 0 | 3 |  | T1 | non-HFTD - Non-critical Substation | 4 | 0 | 48 | 1 | 0 |  | 3 | 4 | 4 | 0 | 2 | 5 |  | 18 | 24 | N | 655
ETS.19.10062 | CRESTA PH | ETS.19.10062 | North Coast | Table Mountain | 0 | 230 | Tier 6 | Yes | G | 230 |  | 3 | 8 |  | T2 | HFTD - Non-critical Substation | 1 | 0 | 15 | 1 | 0 |  | 8 | 8 | 1 | 0 | 2 | 5 |  | 24 | 18 | N | n/a
ETS.22.15004 | CROCKETT COGEN SW STA | ETS.22.15004 | Central Coast | Concord | 0 | n/a | Tier 6 | No | T | 230 |  | 2 | 5 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 5 | 8 | n/a | 0 | 1 | 1 |  | 15 | 27 | N | n/a
ETS.14.16800 | CROW CREEK SW STA | ETS.14.16800 | North Valley | Merced | SW STA - Trans | 60 | Tier 6 | No | T | 60 |  | n/a | 5 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 3 | 1 | 0 |  | 5 | 4 | n/a | 0 | 2 | 5 |  | 16 | 26 | N | n/a
ETS.14.12261 | CROWS LANDING | ETS.14.12261 | North Valley | Merced | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 240 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 701
ETS.15.12262 | CRUSHER | ETS.15.12262 | Central Coast | Moss Landing | DSub in FERC | 4,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | 198 | 178 | 0 |  | 2 | 8 | n/a | 0 | 4 | 10 |  | 24 | 18 | N | n/a
ETS.14.12265 | CURTIS | ETS.14.12265 | North Valley | Merced | DSub in FERC | 18,115 | Tier 6 | Yes | Dist | 115 |  | 3 | 6 |  | T2/3A | HFTD - Non-critical Substation | 4 | 2 | 360 | 178 | 0 |  | 6 | 6 | 4 | 2 | 6 | 10 |  | 34 | 8 | N | 33
ETS.10.12267 | CUYAMA | ETS.10.12267 | South Valley | Bakersfield | DSub in FERC | 12,21,70 | Tier 6 | No | Dist | 70 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 202 | 178 | 0 |  | 2 | 4 | 3 | 0 | 6 | 10 |  | 25 | 17 | N | 421
ETS.10.12268 | CYMRIC | ETS.10.12268 | South Valley | Bakersfield | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 2 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 198 | 178 | 0 |  | 6 | 4 | n/a | 0 | 4 | 10 |  | 24 | 18 | N | n/a
ETS.14.12269 | DAIRYLAND | ETS.14.12269 | North Valley | Merced | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 3 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 6 | 4 | n/a | 0 | 6 | 10 |  | 26 | 16 | N | 400
ETS.02.12270 | DAIRYVILLE | ETS.02.12270 | North Coast | Cottonwood | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | 2 | 2 | 198 | 178 | 0 |  | 2 | 4 | 2 | 2 | 4 | 10 |  | 24 | 18 | N | 368
ETS.12.10203 | DALY CITY | ETS.12.10203 | Bay Area | Martin | DSub in FERC | 4,12,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 8 | 0 | 360 | 178 | 0 |  | 6 | 4 | 8 | 0 | 6 | 10 |  | 34 | 8 | N | 261
ETS.21.12271 | DAVIS | ETS.21.12271 | North Valley | Vaca-Dixon | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 7 | 6 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 317 | 178 | 0 |  | 6 | 4 | 3 | 0 | 6 | 10 |  | 29 | 13 | N | 517
ETS.19.12272 | DAYTON RD | ETS.19.12272 | North Coast | Table Mountain | Unit Sub | 4, 12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 196 | 178 | 0 |  | 1 | 4 | n/a | 0 | 4 | 10 |  | 19 | 23 | N | 678
ETS.21.12275 | DEEPWATER | ETS.21.12275 | North Valley | Vaca-Dixon | DSub in FERC | 12,115 | Tier 6 | No | Dist | 115 |  | 4 | 3 |  | T1 | non-HFTD - Non-critical Substation | 4 | 0 | 225 | 178 | 0 |  | 3 | 4 | 4 | 0 | 6 | 10 |  | 27 | 15 | N | 472
ETS.04.16580 | DEER CREEK PH | ETS.04.16580 | North Valley | Del Mar | 0 | 2,60 | Tier 6 | No | G | 60 |  | 2 | 4 |  | T3 | HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 4 | 10 | n/a | 0 | 1 | 1 |  | 16 | 26 | N | n/a
ETS.04.12277 | DEL MAR | ETS.04.12277 | North Valley | Del Mar | DSub in FERC | 12,21,60 | Tier 6 | No | Dist | 60 |  | 6 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 1 | 256 | 178 | 0 |  | 2 | 4 | n/a | 1 | 6 | 10 |  | 23 | 19 | N | 301
ETS.15.12278 | DEL MONTE | ETS.15.12278 | Central Coast | Moss Landing | T&D | 12,21,115,60 | Tier 6 | Yes | T | 115 |  | 12 | 8 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 418 | 178 | 0 |  | 8 | 4 | 3 | 0 | 6 | 10 |  | 31 | 11 | N | 429
ETS.21.16655 | DELEVAN | ETS.21.16655 | North Valley | Vaca-Dixon | 0 | 12230 | Tier 5 | Yes | T | 230 |  | 10 | 9 |  | T1 | non-HFTD - Critical Substation | n/a | 0 | 19 | 1 | 0 |  | 9 | 4 | n/a | 0 | 2 | 5 |  | 20 | 22 | N | 769
ETS.08.13797 | DERRICK | ETS.08.13797 | South Valley | Gates | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 207 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | n/a
ETS.02.12281 | DESCHUTES | ETS.02.12281 | North Coast | Cottonwood | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 5 | 2 |  | T2/3A | HFTD - Non-critical Substation | n/a | 3 | 225 | 178 | 0 |  | 2 | 6 | n/a | 3 | 6 | 10 |  | 27 | 15 | N | 144
ETS.08.12283 | DEVILS DEN | ETS.08.12283 | South Valley | Gates | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 240 | 178 | 0 |  | 2 | 4 | 2 | 0 | 6 | 10 |  | 24 | 18 | N | 590
ETS.17.10065 | DIABLO CANYON PP | ETS.17.10065 | South Valley | Pismo | SW STA - Trans | 230500 | Tier 1 | Yes | T | 500 | 9 | 9 | 10 |  | T3 | HFTD - Critical Substation | n/a | 0 | 193 | 1 | 0 |  | 10 | 10 | n/a | 0 | 4 | 5 |  | 29 | 13 | N | n/a
ETS.04.12284 | DIAMOND SPRINGS | ETS.04.12284 | North Valley | Del Mar | DSub in FERC | 12,21,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T2/3A | HFTD - Non-critical Substation | n/a | 3 | 360 | 178 | 0 |  | 6 | 6 | n/a | 3 | 6 | 10 |  | 31 | 11 | N | 76
ETS.07.12285 | DINUBA | ETS.07.12285 | South Valley | Fresno | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 450
ETS.17.12291 | DIVIDE | ETS.17.12291 | South Valley | Pismo | T&D | 12,70,115 | Tier 6 | Yes | T | 115 |  | 12 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 258 | 178 | 0 |  | 8 | 4 | n/a | 0 | 6 | 10 |  | 28 | 14 | N | 430
ETS.21.12292 | DIXON | ETS.21.12292 | North Valley | Vaca-Dixon | DSub in FERC | 12,60,115 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 225 | 178 | 0 |  | 2 | 4 | 2 | 0 | 6 | 10 |  | 24 | 18 | N | 568
ETS.09.13821 | DIXON LANDING | ETS.09.13821 | Central Coast | Hayward | DSub in FERC | 21,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 6 | 0 | 238 | 178 | 0 |  | 6 | 4 | 6 | 0 | 6 | 10 |  | 32 | 10 | N | 442
ETS.19.12294 | DOBBINS | ETS.19.12294 | North Coast | Table Mountain | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2 | HFTD - Non-critical Substation | 2 | 4 | 207 | 178 | 0 |  | 2 | 8 | 2 | 4 | 6 | 10 |  | 32 | 10 | N | 114
ETS.15.12296 | DOLAN RD | ETS.15.12296 | Central Coast | Moss Landing | DSub in FERC | 12115 | Tier 6 | Yes | Dist | 115 |  | 3 | 6 |  | T1 | non-HFTD - Non-critical Substation | 4 | 0 | 225 | 178 | 0 |  | 6 | 4 | 4 | 0 | 6 | 10 |  | 30 | 12 | N | 623
ETS.14.12298 | DOS PALOS | ETS.14.12298 | North Valley | Merced | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 238 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 649
ETS.21.12301 | DRAKE | ETS.21.12301 | North Valley | Vaca-Dixon | DSub in FERC | 2.4,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 202 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | n/a
ETS.04.12302 | DRUM #1 PH | ETS.04.12302 | North Valley | Del Mar | 0 | 115 | Tier 6 | Yes | T | 115 |  | 12 | 8 |  | T3 | HFTD - Non-critical Substation | 2 | 2 | 225 | 178 | 0 |  | 8 | 10 | 2 | 2 | 6 | 10 |  | 38 | 4 | N | 148
ETS.09.12303 | DUMBARTON | ETS.09.12303 | Central Coast | Hayward | DSub in FERC | 12,21,115 | Tier 6 | Yes | Dist | 115 |  | 6 | 6 |  | T1 | non-HFTD - Non-critical Substation | 1 | 0 | 418 | 178 | 0 |  | 6 | 4 | 1 | 0 | 6 | 10 |  | 27 | 15 | N | 199
ETS.13.12304 | DUNBAR | ETS.13.12304 | North Coast | McMaude | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T2/3A | HFTD - Non-critical Substation | n/a | 4 | 500 | 178 | 0 |  | 2 | 6 | n/a | 4 | 6 | 10 |  | 28 | 14 | N | 13
ETS.07.12305 | DUNLAP | ETS.07.12305 | South Valley | Fresno | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 2 | 2 |  | T2 | HFTD - Non-critical Substation | 3 | 0 | 258 | 178 | 0 |  | 2 | 8 | 3 | 0 | 6 | 10 |  | 29 | 13 | N | 276
ETS.21.12306 | DUNNIGAN | ETS.21.12306 | North Valley | Vaca-Dixon | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 240 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 581
ETS.04.16575 | DUTCH FLAT #1 PH | ETS.04.16575 | North Valley | Del Mar | N/A | 115 | Tier 6 | No | G | 115 |  | 2 | 4 |  | T3 | HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 4 | 10 | n/a | 0 | 1 | 1 |  | 16 | 26 | N | n/a
ETS.13.12312 | EAGLE ROCK | ETS.13.12312 | North Coast | McMaude | T-Sub | 115,60 | Tier 6 | Yes | T | 115 |  | 9 | 8 |  | T3 | HFTD - Non-critical Substation | 2 | 0 | 240 | 178 | 0 |  | 8 | 10 | 2 | 0 | 6 | 10 |  | 36 | 6 | N | n/a
ETS.12.12315 | EAST GRAND | ETS.12.12315 | Bay Area | Martin | DSub in FERC | 4,12,115 | Tier 6 | Yes | Dist | 115 |  | 6 | 6 |  | T1 | non-HFTD - Non-critical Substation | 6 | 0 | 227 | 178 | 0 |  | 6 | 4 | 6 | 0 | 6 | 10 |  | 32 | 10 | N | 130
ETS.19.12316 | EAST MARYSVILLE | ETS.19.12316 | North Coast | Table Mountain | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 2 | 258 | 178 | 0 |  | 6 | 4 | n/a | 2 | 6 | 10 |  | 28 | 14 | N | 293
ETS.04.12317 | EAST NICOLAUS | ETS.04.12317 | North Valley | Del Mar | T&D | 12,115,60 | Tier 6 | Yes | Dist | 115 |  | 14 | 6 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 225 | 178 | 0 |  | 6 | 4 | 3 | 0 | 6 | 10 |  | 29 | 13 | N | 399
ETS.22.12318 | EAST PORTAL | ETS.22.12318 | Central Coast | Concord | Dist. Single Cust. | 34,115 | Tier 6 | Yes | Dist | 115 |  | 3 | 6 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | 198 | 178 | 0 |  | 6 | 8 | n/a | 0 | 4 | 10 |  | 28 | 14 | N | 777
ETS.19.12319 | EAST QUINCY | ETS.19.12319 | North Coast | Table Mountain | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2/3A | HFTD - Non-critical Substation | 4 | 0 | 240 | 178 | 0 |  | 2 | 6 | 4 | 0 | 6 | 10 |  | 28 | 14 | N | 289
ETS.18.12320 | EAST STOCKTON | ETS.18.12320 | North Valley | Stockton | DSub in FERC | 4,12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | 4 | 0 | 225 | 178 | 0 |  | 2 | 4 | 4 | 0 | 6 | 10 |  | 26 | 16 | N | 610
ETS.09.12321 | EASTSHORE | ETS.09.12321 | Central Coast | Hayward | T-Sub | 230,115 | Tier 5 | Yes | T | 230 |  | 14 | 9 |  | T1 | non-HFTD - Critical Substation | n/a | 0 | 317 | 178 | 0 |  | 9 | 4 | n/a | 0 | 6 | 10 |  | 29 | 13 | N | n/a
ETS.03.12322 | EDENVALE | ETS.03.12322 | Central Coast | Cupertino | DSub in FERC | 12,21,115 | Tier 5 | Yes | Dist | 115 |  | 7 | 9 |  | T1 | non-HFTD - Critical Substation | n/a | 1 | 317 | 178 | 0 |  | 9 | 4 | n/a | 1 | 6 | 10 |  | 30 | 12 | N | 230
ETS.23.12324 | EDES | ETS.23.12324 | Bay Area | Oakport | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T1 | non-HFTD - Non-critical Substation | 4 | 2 | 238 | 178 | 0 |  | 6 | 4 | 4 | 2 | 6 | 10 |  | 32 | 10 | N | 217
ETS.06.12325 | EEL RIVER | ETS.06.12325 | North Coast | Eureka | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 2 | 500 | 178 | 0 |  | 2 | 4 | 3 | 2 | 6 | 10 |  | 27 | 15 | N | 57
ETS.18.13303 | EIGHT MILE | ETS.18.13303 | North Valley | Stockton | DSub in FERC | 21,230 | Tier 6 | Yes | Dist | 230 |  | 6 | 7 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 256 | 178 | 0 |  | 7 | 4 | n/a | 0 | 6 | 10 |  | 27 | 15 | N | 580
ETS.12.12326 | EIGHTEENTH ST | ETS.12.12326 | Bay Area | Martin | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 240 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 520
ETS.23.13547 | EIGHTH AVE | ETS.23.13547 | Bay Area | Oakport | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 258 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 501
ETS.14.12328 | EL CAPITAN | ETS.14.12328 | North Valley | Merced | DSub in FERC | 12,21,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 5 | 0 | 227 | 178 | 0 |  | 6 | 4 | 5 | 0 | 6 | 10 |  | 31 | 11 | N | 562
ETS.23.12329 | EL CERRITO G | ETS.23.12329 | Bay Area | Oakport | DSub in FERC | 12,34,115 | Tier 6 | Yes | Dist | 115 |  | 9 | 6 |  | T2/3A | HFTD - Non-critical Substation | 8 | 2 | 319 | 178 | 0 |  | 6 | 6 | 8 | 2 | 6 | 10 |  | 38 | 4 | N | 232
ETS.04.13548 | EL DORADO PH | ETS.04.13548 | North Valley | Del Mar | DSub not in FERC | 21,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T3 | HFTD - Non-critical Substation | 6 | 3 | 256 | 178 | 0 |  | 6 | 10 | 6 | 3 | 6 | 10 |  | 41 | 1 | N | 5
ETS.14.12330 | EL NIDO | ETS.14.12330 | North Valley | Merced | DSub in FERC | 12,115 | Tier 6 | No | Dist | 115 |  | 0 | 3 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 205 | 178 | 0 |  | 3 | 4 | 2 | 0 | 6 | 10 |  | 25 | 17 | N | 471
ETS.03.12331 | EL PATIO | ETS.03.12331 | Central Coast | Cupertino | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 7 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 360 | 178 | 0 |  | 6 | 4 | n/a | 0 | 6 | 10 |  | 26 | 16 | N | 350
ETS.07.12332 | EL PECO | ETS.07.12332 | South Valley | Fresno | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 284 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 410
ETS.18.16180 | ELECTRA | ETS.18.16180 | North Valley | Stockton | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2 | HFTD - Non-critical Substation | n/a | 3 | 227 | 178 | 0 |  | 2 | 8 | n/a | 3 | 6 | 10 |  | 29 | 13 | N | 288
ETS.18.10069 | ELECTRA PH | ETS.18.10069 | North Valley | Stockton | 0 | 230 | Tier 6 | Yes | G | 230 |  | 3 | 8 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | 10 | 1 | 0 |  | 8 | 8 | n/a | 0 | 2 | 5 |  | 23 | 19 | N | n/a
ETS.20.12335 | ELK | ETS.20.12335 | North Coast | Ukiah | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2 | HFTD - Non-critical Substation | n/a | 1 | 225 | 178 | 0 |  | 2 | 8 | n/a | 1 | 6 | 10 |  | 27 | 15 | N | 129
ETS.19.12336 | ELK CREEK | ETS.19.12336 | North Coast | Table Mountain | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2/3A | HFTD - Non-critical Substation | 2 | 3 | 202 | 178 | 0 |  | 2 | 6 | 2 | 3 | 6 | 10 |  | 29 | 13 | N | 155
ETS.19.13798 | ELK CREEK JCT | ETS.19.13798 | North Coast | Table Mountain | SW STA - Trans | 60 | Tier 6 | No | T | 60 |  | n/a | 5 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 5 | 1 | 0 |  | 5 | 4 | 2 | 0 | 2 | 5 |  | 18 | 24 | N | n/a
ETS.10.12338 | ELK HILLS | ETS.10.12338 | South Valley | Bakersfield | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 200 | 178 | 0 |  | 2 | 4 | n/a | 0 | 4 | 10 |  | 20 | 22 | N | 733
ETS.16.12342 | EMERALD LAKE | ETS.16.12342 | Central Coast | San Carlos | DSub in FERC | 4,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2 | HFTD - Non-critical Substation | n/a | 1 | 238 | 178 | 0 |  | 2 | 8 | n/a | 1 | 6 | 10 |  | 27 | 15 | N | 126
ETS.19.12345 | ENCINAL | ETS.19.12345 | North Coast | Table Mountain | DSub in FERC | 2.4,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 196 | 178 | 0 |  | 2 | 4 | n/a | 0 | 4 | 10 |  | 20 | 22 | N | n/a
ETS.15.12346 | ERTA | ETS.15.12346 | Central Coast | Moss Landing | DSub in FERC | 4,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 240 | 178 | 0 |  | 2 | 4 | 3 | 0 | 6 | 10 |  | 25 | 17 | N | 728
ETS.19.12347 | ESQUON | ETS.19.12347 | North Coast | Table Mountain | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 202 | 178 | 0 |  | 2 | 4 | 3 | 0 | 6 | 10 |  | 25 | 17 | N | 612
ETS.06.12348 | ESSEX JCT | ETS.06.12348 | North Coast | Eureka | SW STA - Trans | 60 | Tier 6 | No | T | 60 |  | n/a | 5 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 26 | 1 | 0 |  | 5 | 4 | n/a | 0 | 2 | 5 |  | 16 | 26 | N | n/a
ETS.09.13549 | ESTUDILLO | ETS.09.13549 | Central Coast | Hayward | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T2/3A | HFTD - Non-critical Substation | n/a | 1 | 207 | 178 | 0 |  | 1 | 6 | n/a | 1 | 6 | 10 |  | 24 | 18 | N | 504
ETS.06.12350 | EUREKA A | ETS.06.12350 | North Coast | Eureka | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | 4 | 2 | 48 | 1 | 0 |  | 2 | 4 | 4 | 2 | 2 | 5 |  | 19 | 23 | N | 280
ETS.06.12351 | EUREKA E | ETS.06.12351 | North Coast | Eureka | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | 4 | 2 | 225 | 178 | 0 |  | 2 | 4 | 4 | 2 | 6 | 10 |  | 28 | 14 | N | 295
ETS.03.12352 | EVERGREEN | ETS.03.12352 | Central Coast | Cupertino | T&D | 21,115,60 | Tier 6 | Yes | T | 115 |  | 10 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 317 | 178 | 0 |  | 8 | 4 | n/a | 0 | 6 | 10 |  | 28 | 14 | N | 309
ETS.08.16796 | EXCELSIOR SW STA | ETS.08.16796 | South Valley | Gates | SW STA - Trans | 115 | Tier 6 | Yes | T | 115 |  | 0 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 5 | 1 | 0 |  | 8 | 4 | n/a | 0 | 2 | 5 |  | 19 | 23 | N | n/a
ETS.14.12353 | EXCHEQUER PH | ETS.14.12353 | North Valley | Merced | 3rd Party | 70 | Tier 6 | No | T | 70 |  | 7 | 5 |  | T2/3A | HFTD - Non-critical Substation | n/a | 0 | 12 | 1 | 0 |  | 5 | 6 | n/a | 0 | 2 | 5 |  | 18 | 24 | N | n/a
ETS.06.12354 | FAIRHAVEN | ETS.06.12354 | North Coast | Eureka | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | 2 | 2 | 196 | 178 | 0 |  | 2 | 4 | 2 | 2 | 4 | 10 |  | 24 | 18 | N | 537
ETS.23.13551 | FAIRMOUNT | ETS.23.13551 | Bay Area | Oakport | 0 | - | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 1 | 240 | 178 | 0 |  | 1 | 4 | n/a | 1 | 6 | 10 |  | 22 | 20 | N | 516
ETS.22.12355 | FAIRVIEW | ETS.22.12355 | Central Coast | Concord | DSub in FERC | 21,115 | Tier 6 | No | Dist | 115 |  | 0 | 3 |  | T1 | non-HFTD - Non-critical Substation | 5 | 1 | 1184 | 178 | 0 |  | 3 | 4 | 5 | 1 | 10 | 10 |  | 33 | 9 | N | 327
ETS.17.12356 | FAIRWAY | ETS.17.12356 | South Valley | Pismo | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 238 | 178 | 0 |  | 6 | 4 | n/a | 0 | 6 | 10 |  | 26 | 16 | N | 579
ETS.10.12357 | FAMOSO | ETS.10.12357 | South Valley | Bakersfield | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 202 | 178 | 0 |  | 6 | 4 | 2 | 0 | 6 | 10 |  | 28 | 14 | N | 711
ETS.10.12360 | FELLOWS | ETS.10.12360 | South Valley | Bakersfield | DSub in FERC | 21,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 196 | 178 | 0 |  | 6 | 4 | 2 | 0 | 4 | 10 |  | 26 | 16 | N | 601
ETS.15.13721 | FELTON | ETS.15.13721 | Central Coast | Moss Landing | Unit Sub | 4,21 | Tier 6 | No | Dist | 21 |  | n/a | 1 |  | T3 | HFTD - Non-critical Substation | n/a | 2 | 362 | 178 | 0 |  | 1 | 10 | n/a | 2 | 6 | 10 |  | 29 | 13 | N | 511
ETS.07.12364 | FIGARDEN | ETS.07.12364 | South Valley | Fresno | DSub in FERC | 21,230 | Tier 6 | Yes | Dist | 230 |  | 4 | 7 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 317 | 178 | 0 |  | 7 | 4 | 3 | 0 | 6 | 10 |  | 30 | 12 | N | 470
ETS.14.12366 | FIREBAUGH | ETS.14.12366 | North Valley | Merced | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 654
ETS.15.12367 | FIRESTONE SW STA | ETS.15.12367 | Central Coast | Moss Landing | SW STA - Trans | 60 | Tier 6 | No | T | 60 |  | 3 | 5 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 21 | 1 | 0 |  | 5 | 4 | n/a | 0 | 2 | 5 |  | 16 | 26 | N | n/a
ETS.13.12368 | FITCH MTN | ETS.13.12368 | North Coast | McMaude | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 3 | 258 | 178 | 0 |  | 2 | 4 | 3 | 3 | 6 | 10 |  | 28 | 14 | N | 32
ETS.08.16806 | FIVE POINTS SW STA | ETS.08.16806 | South Valley | Gates | SW STA - Trans | 70 | Tier 6 | No | T | 70 |  | n/a | 5 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 3 | 1 | 0 |  | 5 | 4 | n/a | 0 | 2 | 5 |  | 16 | 26 | N | n/a
ETS.04.12370 | FLINT | ETS.04.12370 | North Valley | Del Mar | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 3 | 6 |  | T2 | HFTD - Non-critical Substation | 5 | 2 | 500 | 178 | 0 |  | 6 | 8 | 5 | 2 | 6 | 10 |  | 37 | 5 | N | 325
ETS.23.13552 | FLORENCE | ETS.23.13552 | Bay Area | Oakport | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T2 | HFTD - Non-critical Substation | n/a | 1 | 207 | 178 | 0 |  | 1 | 8 | n/a | 1 | 6 | 10 |  | 26 | 16 | N | 502
ETS.03.12372 | FMC | ETS.03.12372 | Central Coast | Cupertino | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 225 | 178 | 0 |  | 6 | 4 | 3 | 0 | 6 | 10 |  | 29 | 13 | N | 582
ETS.17.12375 | FOOTHILL | ETS.17.12375 | South Valley | Pismo | DSub in FERC | 12,21,115 | Tier 6 | Yes | Dist | 115 |  | 3 | 6 |  | T2 | HFTD - Non-critical Substation | 2 | 0 | 258 | 178 | 0 |  | 6 | 8 | 2 | 0 | 6 | 10 |  | 32 | 10 | N | 375
ETS.04.13554 | FORESTHILL | ETS.04.13554 | North Valley | Del Mar | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T3 | HFTD - Non-critical Substation | 5 | 4 | 48 | 1 | 0 |  | 2 | 10 | 5 | 4 | 2 | 5 |  | 28 | 14 | N | 42
ETS.20.12379 | FORT BRAGG A | ETS.20.12379 | North Coast | Ukiah | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | 4 | 1 | 48 | 1 | 0 |  | 2 | 4 | 4 | 1 | 2 | 5 |  | 18 | 24 | Y | 151
ETS.15.12380 | FORT ORD | ETS.15.12380 | Central Coast | Moss Landing | DSub in FERC | 12,21,60,115 | Tier 6 | No | Dist | 60 |  | 6 | 2 |  | T1 | non-HFTD - Non-critical Substation | 5 | 0 | 258 | 178 | 0 |  | 2 | 4 | 5 | 0 | 6 | 10 |  | 27 | 15 | N | 525
ETS.13.12382 | FORT ROSS | ETS.13.12382 | North Coast | McMaude | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2 | HFTD - Non-critical Substation | n/a | 1 | 202 | 178 | 0 |  | 2 | 8 | n/a | 1 | 6 | 10 |  | 27 | 15 | N | 128
ETS.06.12383 | FORT SEWARD | ETS.06.12383 | North Coast | Eureka | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2 | HFTD - Non-critical Substation | 3 | 2 | 19 | 1 | 0 |  | 2 | 8 | 3 | 2 | 2 | 5 |  | 22 | 20 | N | 160
ETS.22.12386 | FRANKLIN | ETS.22.12386 | Central Coast | Concord | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | 5 | 1 | 225 | 178 | 0 |  | 2 | 4 | 5 | 1 | 6 | 10 |  | 28 | 14 | N | 104
ETS.15.13556 | FREEDOM | ETS.15.13556 | Central Coast | Moss Landing | Unit Sub | 4,21 | Tier 6 | No | Dist | 21 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 202 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | n/a
ETS.09.12388 | FREMONT | ETS.09.12388 | Central Coast | Hayward | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 4 | 2 | 317 | 178 | 0 |  | 6 | 4 | 4 | 2 | 6 | 10 |  | 32 | 10 | N | 100
ETS.18.12389 | FRENCH CAMP | ETS.18.12389 | North Valley | Stockton | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 248
ETS.02.12390 | FRENCH GULCH | ETS.02.12390 | North Coast | Cottonwood | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2 | HFTD - Non-critical Substation | 4 | 2 | 202 | 178 | 0 |  | 2 | 8 | 4 | 2 | 6 | 10 |  | 32 | 10 | N | 178
ETS.18.12391 | FROGTOWN | ETS.18.12391 | North Valley | Stockton | DSub in FERC | 17,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T2 | HFTD - Non-critical Substation | 5 | 3 | 500 | 178 | 0 |  | 6 | 8 | 5 | 3 | 6 | 10 |  | 38 | 4 | N | 198
ETS.06.12392 | FRUITLAND | ETS.06.12392 | North Coast | Eureka | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2 | HFTD - Non-critical Substation | n/a | 2 | 362 | 178 | 0 |  | 2 | 8 | n/a | 2 | 6 | 10 |  | 28 | 14 | N | 124
ETS.10.12393 | FRUITVALE | ETS.10.12393 | South Valley | Bakersfield | DSub in FERC | 12,70,115 | Tier 6 | No | Dist | 70 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 258 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 493
ETS.13.10073 | FULTON | ETS.13.10073 | North Coast | McMaude | T&D | 12,230,115,60 | Tier 5 | Yes | T | 230 |  | 27 | 9 |  | T1 | non-HFTD - Critical Substation | 6 | 5 | 317 | 178 | 0 |  | 9 | 4 | 6 | 5 | 6 | 10 |  | 40 | 2 | N | 59
ETS.15.12395 | GABILAN | ETS.15.12395 | Central Coast | Moss Landing | DSub in FERC | 12,115 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 1 | 227 | 178 | 0 |  | 2 | 4 | n/a | 1 | 6 | 10 |  | 23 | 19 | N | 265
ETS.14.12396 | GALLO | ETS.14.12396 | North Valley | Merced | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 0 | 6 |  | T1 | non-HFTD - Non-critical Substation | 1 | 0 | 13 | 1 | 0 |  | 6 | 4 | 1 | 0 | 2 | 5 |  | 18 | 24 | N | 764
ETS.19.13557 | GANSNER | ETS.19.13557 | North Coast | Table Mountain | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2/3A | HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 2 | 6 | n/a | 0 | 6 | 10 |  | 24 | 18 | N | 299
ETS.10.12397 | GANSO | ETS.10.12397 | South Valley | Bakersfield | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 2 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 198 | 178 | 0 |  | 6 | 4 | n/a | 0 | 4 | 10 |  | 24 | 18 | N | 688
ETS.06.12398 | GARBERVILLE | ETS.06.12398 | North Coast | Eureka | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T3 | HFTD - Non-critical Substation | 3 | 2 | 225 | 178 | 0 |  | 2 | 10 | 3 | 2 | 6 | 10 |  | 33 | 9 | N | 39
ETS.20.12399 | GARCIA | ETS.20.12399 | North Coast | Ukiah | DSub in FERC | 4,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2 | HFTD - Non-critical Substation | n/a | 1 | 190 | 178 | 0 |  | 2 | 8 | n/a | 1 | 4 | 10 |  | 25 | 17 | N | 240
ETS.10.13800 | GARDNER | ETS.10.13800 | South Valley | Bakersfield | DSub in FERC | 4,70 | Tier 6 | No | Dist | 70 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 196 | 178 | 0 |  | 2 | 4 | n/a | 0 | 4 | 10 |  | 20 | 22 | N | 747
ETS.08.10086 | GATES | ETS.08.10086 | South Valley | Gates | T&D | 12,115,230,500,70 | Tier 2 | Yes | T | 500 |  | 24 | 10 |  | T1 | non-HFTD - Critical Substation | n/a | 0 | 500 | 178 | 0 |  | 10 | 4 | n/a | 0 | 6 | 10 |  | 30 | 12 | N | 696
ETS.22.16695 | GATEWAY PP | ETS.22.16695 | Central Coast | Concord | 0 | 230 | Tier 6 | No | T | 230 |  | 5 | 5 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 5 | 4 | n/a | 0 | 1 | 1 |  | 11 | 31 | N | n/a
ETS.02.12402 | GERBER | ETS.02.12402 | North Coast | Cottonwood | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 2 | 258 | 178 | 0 |  | 2 | 4 | 3 | 2 | 6 | 10 |  | 27 | 15 | N | 229
ETS.13.12406 | GEYSERS 3 & 4 PP SW STA | ETS.13.12406 | North Coast | McMaude |  |  | Tier 6 | Yes | T | 115 |  | 3 | 8 |  | T3 | HFTD - Non-critical Substation | n/a | 0 | 13 | 1 | 0 |  | 8 | 10 | n/a | 0 | 2 | 5 |  | 25 | 17 | N | n/a
ETS.13.12409 | GEYSERVILLE | ETS.13.12409 | North Coast | McMaude | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 3 | 500 | 178 | 0 |  | 2 | 4 | n/a | 3 | 6 | 10 |  | 25 | 17 | N | 88
ETS.08.12410 | GIFFEN | ETS.08.12410 | South Valley | Gates | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 284 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 495
ETS.22.13568 | GILL | ETS.22.13568 | Central Coast | Concord | Unit Sub | 4,21 | Tier 6 | No | Dist | 21 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 202 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 658
ETS.14.16730 | GILL RANCH | ETS.14.16730 | North Valley | Merced | 0 | 12,115 | Tier 6 | No | Dist | 115 |  | n/a | 3 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 19 | 1 | 0 |  | 3 | 4 | n/a | 0 | 2 | 5 |  | 14 | 28 | N | n/a
ETS.02.12412 | GIRVAN | ETS.02.12412 | North Coast | Cottonwood | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2/3A | HFTD - Non-critical Substation | n/a | 3 | 225 | 178 | 0 |  | 2 | 6 | n/a | 3 | 6 | 10 |  | 27 | 15 | N | 207
ETS.14.12414 | GLASS | ETS.14.12414 | North Valley | Merced | SW STA - Trans | 12,70 | Tier 6 | No | T | 70 |  | 4 | 5 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 5 | 1 | 0 |  | 5 | 4 | n/a | 0 | 2 | 5 |  | 16 | 26 | N | n/a
ETS.02.10088 | GLENN | ETS.02.10088 | North Coast | Cottonwood | T&D | 12,60,230 | Tier 6 | Yes | T | 230 |  | 12 | 8 |  | T1 | non-HFTD - Non-critical Substation | 4 | 3 | 258 | 178 | 0 |  | 8 | 4 | 4 | 3 | 6 | 10 |  | 35 | 7 | N | 121
ETS.16.12416 | GLENWOOD | ETS.16.12416 | Central Coast | San Carlos | DSub in FERC | 4,12,60 | Tier 6 | No | Dist | 60 |  | 5 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 227 | 178 | 0 |  | 2 | 4 | 3 | 0 | 6 | 10 |  | 25 | 17 | N | 404
ETS.04.10087 | GOLD HILL | ETS.04.10087 | North Valley | Del Mar | T-Sub | 115,60,230 | Tier 4 | Yes | T | 230 |  | 20 | 9 |  | T1 | non-HFTD - Critical Substation | n/a | 0 | 360 | 178 | 0 |  | 9 | 4 | n/a | 0 | 6 | 10 |  | 29 | 13 | N | n/a
ETS.17.12418 | GOLDTREE | ETS.17.12418 | South Valley | Pismo | DSub in FERC | 12,115 | Tier 6 | No | Dist | 115 |  | 0 | 3 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 3 | 8 | n/a | 0 | 6 | 10 |  | 27 | 15 | N | 485
ETS.15.12419 | GONZALES | ETS.15.12419 | Central Coast | Moss Landing | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | 4 | 1 | 500 | 178 | 0 |  | 2 | 4 | 4 | 1 | 6 | 10 |  | 27 | 15 | N | 166
ETS.10.12420 | GOOSE LAKE | ETS.10.12420 | South Valley | Bakersfield | DSub in FERC | 12,21,115 | Tier 6 | Yes | Dist | 115 |  | 3 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 198 | 178 | 0 |  | 6 | 4 | n/a | 0 | 4 | 10 |  | 24 | 18 | N | 695
ETS.10.16650 | GOSFORD | ETS.10.16650 | South Valley | Bakersfield | N/A | n/a | Tier 6 | No | n/a | n/a |  | n/a | 5 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 5 | 4 | n/a | 0 | 1 | 1 |  | 11 | 31 | N | n/a
ETS.21.12422 | GRAND ISLAND | ETS.21.12422 | North Valley | Vaca-Dixon | DSub in FERC | 12,21,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 6 | 0 | 238 | 178 | 0 |  | 6 | 4 | 6 | 0 | 6 | 10 |  | 32 | 10 | N | 348
ETS.09.12425 | GRANT | ETS.09.12425 | Central Coast | Hayward | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 317 | 178 | 0 |  | 6 | 4 | n/a | 0 | 6 | 10 |  | 26 | 16 | N | 163
ETS.04.12427 | GRASS VALLEY | ETS.04.12427 | North Valley | Del Mar | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T2 | HFTD - Non-critical Substation | n/a | 3 | 362 | 178 | 0 |  | 2 | 8 | n/a | 3 | 6 | 10 |  | 29 | 13 | N | 192
ETS.19.13569 | GRAYS FLAT | ETS.19.13569 | North Coast | Table Mountain | DSub in FERC | 4,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2 | HFTD - Non-critical Substation | 1 | 0 | 207 | 178 | 0 |  | 2 | 8 | 1 | 0 | 6 | 10 |  | 27 | 15 | N | 336
ETS.15.12428 | GREEN VALLEY | ETS.15.12428 | Central Coast | Moss Landing | T&D | 21,115,60 | Tier 6 | Yes | T | 115 |  | 9 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 2 | 362 | 178 | 0 |  | 8 | 4 | n/a | 2 | 6 | 10 |  | 30 | 12 | N | 216
ETS.13.12429 | GREENBRAE | ETS.13.12429 | North Coast | McMaude | DSub in FERC | 12,60,115 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 1 | 225 | 178 | 0 |  | 2 | 4 | n/a | 1 | 6 | 10 |  | 23 | 19 | Y | 241
ETS.07.10089 | GREGG | ETS.07.10089 | South Valley | Fresno | SW STA - Trans | 230 | Tier 4 | Yes | T | 230 |  | 10 | 9 |  | T1 | non-HFTD - Critical Substation | 5 | 0 | 11 | 1 | 0 |  | 9 | 4 | 5 | 0 | 2 | 5 |  | 25 | 17 | N | n/a
ETS.19.16595 | GRIZZLY PH | ETS.19.16595 | North Coast | Table Mountain | 0 | 7115 | Tier 6 | No | G | 115 |  | 2 | 4 |  | T3 | HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 4 | 10 | n/a | 0 | 1 | 1 |  | 16 | 26 | N | n/a
ETS.20.12438 | GUALALA | ETS.20.12438 | North Coast | Ukiah | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2 | HFTD - Non-critical Substation | n/a | 1 | 500 | 178 | 0 |  | 2 | 8 | n/a | 1 | 6 | 10 |  | 27 | 15 | Y | 112
ETS.08.12440 | GUERNSEY | ETS.08.12440 | South Valley | Gates | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 19 | 1 | 0 |  | 2 | 4 | n/a | 0 | 2 | 5 |  | 13 | 29 | N | 605
ETS.14.12441 | GUSTINE | ETS.14.12441 | North Valley | Merced | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 238 | 178 | 0 |  | 2 | 4 | 3 | 0 | 6 | 10 |  | 25 | 17 | N | 245
ETS.08.16162 | GWF HANFORD SW STA | ETS.08.16162 | South Valley | Gates | SW STA - Trans | 115 | Tier 6 | Yes | T | 115 |  | 3 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 6 | 1 | 0 |  | 8 | 4 | n/a | 0 | 2 | 5 |  | 19 | 23 | N | n/a
ETS.07.16310 | HAAS PH | ETS.07.16310 | South Valley | Fresno | 0 | 230 | Tier 6 | No | T | 230 | 8 | 2 | 5 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | 500 | 178 | 0 |  | 5 | 8 | n/a | 0 | 6 | 10 |  | 29 | 13 | N | n/a
ETS.16.12445 | HALF MOON BAY | ETS.16.12445 | Central Coast | San Carlos | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 5 | 2 |  | T1 | non-HFTD - Non-critical Substation | 5 | 3 | 240 | 178 | 0 |  | 2 | 4 | 5 | 3 | 6 | 10 |  | 30 | 12 | N | 43
ETS.04.12446 | HALSEY PH | ETS.04.12446 | North Valley | Del Mar | 0 | 7,12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2 | HFTD - Non-critical Substation | 3 | 3 | 8 | 1 | 0 |  | 2 | 8 | 3 | 3 | 2 | 5 |  | 23 | 19 | N | 52
ETS.19.12447 | HAMILTON A | ETS.19.12447 | North Coast | Table Mountain | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 362 | 178 | 0 |  | 2 | 4 | 3 | 0 | 6 | 10 |  | 25 | 17 | N | 621
ETS.19.10095 | HAMILTON BRANCH | ETS.19.10095 | North Coast | Table Mountain | DSub not in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T2 | HFTD - Non-critical Substation | 3 | 0 | 256 | 178 | 0 |  | 2 | 8 | 3 | 0 | 6 | 10 |  | 29 | 13 | N | 334
ETS.18.12449 | HAMMER | ETS.18.12449 | North Valley | Stockton | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | 4 | 0 | 225 | 178 | 0 |  | 2 | 4 | 4 | 0 | 6 | 10 |  | 26 | 16 | N | 624
ETS.14.12450 | HAMMONDS | ETS.14.12450 | North Valley | Merced | DSub in FERC | 12,115 | Tier 6 | No | Dist | 115 |  | 0 | 3 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 196 | 178 | 0 |  | 3 | 4 | n/a | 0 | 4 | 10 |  | 21 | 21 | N | 721
ETS.08.12451 | HANFORD SW STA | ETS.08.12451 | South Valley | Gates | SW STA - Trans | 70115 | Tier 6 | No | T | 70 |  | 3 | 5 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 6 | 1 | 0 |  | 5 | 4 | n/a | 0 | 2 | 5 |  | 16 | 26 | N | n/a
ETS.18.12452 | HARDING | ETS.18.12452 | North Valley | Stockton | DSub in FERC | 4,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 500 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 596
ETS.07.12453 | HARDWICK | ETS.07.12453 | South Valley | Fresno | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 651
ETS.21.12454 | HARRINGTON | ETS.21.12454 | North Valley | Vaca-Dixon | DSub in FERC | 2.4,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 202 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | n/a
ETS.06.12455 | HARRIS | ETS.06.12455 | North Coast | Eureka | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 2 | 225 | 178 | 0 |  | 2 | 4 | 3 | 2 | 6 | 10 |  | 27 | 15 | Y | 71
ETS.19.12457 | HARTER | ETS.19.12457 | North Coast | Table Mountain | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 614
ETS.20.12458 | HARTLEY | ETS.20.12458 | North Coast | Ukiah | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T2 | HFTD - Non-critical Substation | n/a | 2 | 258 | 178 | 0 |  | 2 | 8 | n/a | 2 | 6 | 10 |  | 28 | 14 | N | 162
ETS.02.12460 | HAT CREEK #1 PH | ETS.02.12460 | North Coast | Cottonwood | 0 | 70 | Tier 6 | No | G | 60 |  | 2 | 4 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | 3 | 1 | 0 |  | 4 | 8 | n/a | 0 | 2 | 5 |  | 19 | 23 | N | n/a
ETS.02.16545 | HAT CREEK #2 PH | ETS.02.16545 | North Coast | Cottonwood | 0 | 60 | Tier 6 | No | G | 60 |  | 2 | 4 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 4 | 8 | n/a | 0 | 1 | 1 |  | 14 | 28 | N | n/a
ETS.15.12462 | HATTON | ETS.15.12462 | Central Coast | Moss Landing | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2 | HFTD - Non-critical Substation | 4 | 0 | 225 | 178 | 0 |  | 2 | 8 | 4 | 0 | 6 | 10 |  | 30 | 12 | N | 259
ETS.09.13585 | HAYWARD O | ETS.09.13585 | Central Coast | Hayward | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 227 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 697
ETS.07.10091 | HELM | ETS.07.10091 | South Valley | Fresno | T-Sub | 230,70 | Tier 6 | Yes | T | 230 |  | 8 | 8 |  | T1 | non-HFTD - Non-critical Substation | 5 | 0 | 1184 | 178 | 0 |  | 8 | 4 | 5 | 0 | 10 | 10 |  | 37 | 5 | N | n/a
ETS.07.16505 | HELMS PH | ETS.07.16505 | South Valley | Fresno | 0 | 230 | Tier 4 | Yes | G | 230 | 9 | 5 | 9 |  | T1 | non-HFTD - Critical Substation | n/a | 0 | 10 | 1 | 0 |  | 9 | 4 | n/a | 0 | 2 | 5 |  | 20 | 22 | N | n/a
ETS.08.10092 | HENRIETTA | ETS.08.10092 | South Valley | Gates | T&D | 12,70,230,115 | Tier 6 | Yes | T | 230 |  | 16 | 8 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 498 | 178 | 0 |  | 8 | 4 | 3 | 0 | 6 | 10 |  | 31 | 11 | N | 714
ETS.26.16430 | HERDLYN | ETS.26.16430 | North Valley | Tesla | T&D | 12,60,70 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 240 | 178 | 0 |  | 2 | 4 | 3 | 0 | 6 | 10 |  | 25 | 17 | N | 440
ETS.07.10096 | HERNDON | ETS.07.10096 | South Valley | Fresno | T-Sub | 230,115 | Tier 4 | Yes | T | 230 |  | 15 | 9 |  | T1 | non-HFTD - Critical Substation | 2 | 0 | 317 | 178 | 0 |  | 9 | 4 | 2 | 0 | 6 | 10 |  | 31 | 11 | N | n/a
ETS.03.10093 | HICKS | ETS.03.10093 | Central Coast | Cupertino | DSub in FERC | 12,21,230 | Tier 6 | Yes | Dist | 230 |  | 6 | 7 |  | T1 | non-HFTD - Non-critical Substation | 3 | 2 | 360 | 178 | 0 |  | 7 | 4 | 3 | 2 | 6 | 10 |  | 32 | 10 | N | 7
ETS.04.12473 | HIGGINS | ETS.04.12473 | North Valley | Del Mar | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T2 | HFTD - Non-critical Substation | 4 | 3 | 240 | 178 | 0 |  | 6 | 8 | 4 | 3 | 6 | 10 |  | 37 | 5 | N | 228
ETS.20.12474 | HIGHLANDS | ETS.20.12474 | North Coast | Ukiah | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T2 | HFTD - Non-critical Substation | 3 | 3 | 225 | 178 | 0 |  | 6 | 8 | 3 | 3 | 6 | 10 |  | 36 | 6 | Y | 31
ETS.13.12475 | HIGHWAY | ETS.13.12475 | North Coast | McMaude | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T1 | non-HFTD - Non-critical Substation | 5 | 2 | 225 | 178 | 0 |  | 6 | 4 | 5 | 2 | 6 | 10 |  | 33 | 9 | Y | 60
ETS.16.12476 | HILLSDALE | ETS.16.12476 | Central Coast | San Carlos | DSub in FERC | 4,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 500 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 593
ETS.16.13903 | HILLSDALE JCT | ETS.16.13903 | Central Coast | San Carlos | SW STA - Trans | 60 | Tier 6 | No | T | 60 |  | 4 | 5 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | 8 | 1 | 0 |  | 5 | 8 | n/a | 0 | 2 | 5 |  | 20 | 22 | N | n/a
ETS.15.12477 | HOLLISTER | ETS.15.12477 | Central Coast | Moss Landing | DSub in FERC | 21,60,115 | Tier 6 | Yes | Dist | 115 |  | 6 | 6 |  | T1 | non-HFTD - Non-critical Substation | 4 | 1 | 258 | 178 | 0 |  | 6 | 4 | 4 | 1 | 6 | 10 |  | 31 | 11 | N | 141
ETS.23.13572 | HOLLYWOOD | ETS.23.13572 | Bay Area | Oakport | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T2/3A | HFTD - Non-critical Substation | 2 | 1 | 240 | 178 | 0 |  | 1 | 6 | 2 | 1 | 6 | 10 |  | 26 | 16 | N | 393
ETS.19.12481 | HONCUT | ETS.19.12481 | North Coast | Table Mountain | DSub in FERC | 12,115 | Tier 6 | No | Dist | 115 |  | 0 | 3 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 258 | 178 | 0 |  | 3 | 4 | 3 | 0 | 6 | 10 |  | 26 | 16 | N | 428
ETS.06.12483 | HOOPA | ETS.06.12483 | North Coast | Eureka | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2/3A | HFTD - Non-critical Substation | n/a | 2 | 500 | 178 | 0 |  | 2 | 6 | n/a | 2 | 6 | 10 |  | 26 | 16 | N | 50
ETS.20.12485 | HOPLAND | ETS.20.12485 | North Coast | Ukiah | T&D | 12,60,115 | Tier 6 | No | T | 115 |  | 2 | 5 |  | T2/3A | HFTD - Non-critical Substation | n/a | 4 | 284 | 178 | 0 |  | 5 | 6 | n/a | 4 | 6 | 10 |  | 31 | 11 | N | 28
ETS.04.12486 | HORSESHOE | ETS.04.12486 | North Valley | Del Mar | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 0 | 6 |  | T1 | non-HFTD - Non-critical Substation | 5 | 2 | 225 | 178 | 0 |  | 6 | 4 | 5 | 2 | 6 | 10 |  | 33 | 9 | N | 315
ETS.18.12489 | HOWLAND RD | ETS.18.12489 | North Valley | Stockton | Dist. Single Cust. | 12, 115 | Tier 6 | No | Dist | 115 |  | 0 | 3 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 198 | 178 | 0 |  | 3 | 4 | n/a | 0 | 4 | 10 |  | 21 | 21 | N | n/a
ETS.06.12493 | HUMBOLDT | ETS.06.12493 | North Coast | Eureka | T-Sub | 115,60 | Tier 6 | Yes | T | 115 |  | 15 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 2 | 48 | 1 | 0 |  | 8 | 4 | n/a | 2 | 2 | 5 |  | 21 | 21 | N | 188
ETS.06.10097 | HUMBOLDT BAY PP | ETS.06.10097 | North Coast | Eureka | DSub in FERC | 2,12,13.8,115,60 | Tier 5 | No | Dist | 60 |  | 7 | 9 |  | T1 | non-HFTD - Critical Substation | 3 | 0 | 227 | 178 | 0 |  | 9 | 4 | 3 | 0 | 6 | 10 |  | 32 | 10 | N | n/a
ETS.08.12497 | HURON | ETS.08.12497 | South Valley | Gates | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 258 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 699
ETS.02.13939 | HYAMPOM SW STA | ETS.02.13939 | North Coast | Cottonwood | SW STA - Trans | 60 | Tier 6 | No | T | 60 |  | 2 | 5 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 5 | 8 | n/a | 0 | 1 | 1 |  | 15 | 27 | N | n/a
ETS.13.10100 | IGNACIO | ETS.13.10100 | North Coast | McMaude | T&D | 12,115,230,60 | Tier 5 | Yes | T | 230 |  | 24 | 9 |  | T2/3A | HFTD - Critical Substation | 5 | 1 | 317 | 178 | 0 |  | 9 | 6 | 5 | 1 | 6 | 10 |  | 37 | 5 | Y | 175
ETS.22.12504 | IMHOFF | ETS.22.12504 | Central Coast | Concord | Dist. Single Cust. | 12,115 | Tier 6 | Yes | Dist | 115 |  | 2 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 196 | 178 | 0 |  | 6 | 4 | n/a | 0 | 4 | 10 |  | 24 | 18 | N | n/a
ETS.14.12506 | INDIAN FLAT | ETS.14.12506 | North Valley | Merced | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 3 | 2 |  | T2 | HFTD - Non-critical Substation | 2 | 1 | 240 | 178 | 0 |  | 2 | 8 | 2 | 1 | 6 | 10 |  | 29 | 13 | N | 338
ETS.15.12508 | INDUSTRIAL ACRES | ETS.15.12508 | Central Coast | Moss Landing | DSub in FERC | 4,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 258 | 178 | 0 |  | 2 | 4 | 3 | 0 | 6 | 10 |  | 25 | 17 | N | 538
ETS.18.12514 | IONE | ETS.18.12514 | North Valley | Stockton | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T3 | HFTD - Non-critical Substation | n/a | 0 | 196 | 178 | 0 |  | 2 | 10 | n/a | 0 | 4 | 10 |  | 26 | 16 | N | 527
ETS.09.12515 | IUKA | ETS.09.12515 | Central Coast | Hayward | DSub in FERC | 4,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 202 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | n/a
ETS.08.13723 | JACALITOS | ETS.08.13723 | South Valley | Gates | Dist. Single Cust. | 12,70 | Tier 6 | No | Dist | 70 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 2 | 4 | n/a | 0 | 1 | 1 |  | 8 | 34 | N | n/a
ETS.19.12517 | JACINTO | ETS.19.12517 | North Coast | Table Mountain | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 461
ETS.08.12518 | JACOBS CORNER | ETS.08.12518 | South Valley | Gates | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 256 | 178 | 0 |  | 2 | 4 | 2 | 0 | 6 | 10 |  | 24 | 18 | N | 606
ETS.02.16540 | JAMES B BLACK PH | ETS.02.16540 | North Coast | Cottonwood | 0 | 230 | Tier 6 | No | G | 230 | 8 | 3 | 4 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 4 | 8 | n/a | 0 | 1 | 1 |  | 14 | 28 | N | n/a
ETS.21.13760 | JAMESON | ETS.21.13760 | North Valley | Vaca-Dixon | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 2 | 225 | 178 | 0 |  | 6 | 4 | n/a | 2 | 6 | 10 |  | 28 | 14 | N | 58
ETS.06.12519 | JANES CREEK | ETS.06.12519 | North Coast | Eureka | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 2 | 227 | 178 | 0 |  | 2 | 4 | 3 | 2 | 6 | 10 |  | 27 | 15 | N | 153
ETS.09.12520 | JARVIS | ETS.09.12520 | Central Coast | Hayward | DSub in FERC | 12,34,115 | Tier 6 | Yes | Dist | 115 |  | 13 | 6 |  | T1 | non-HFTD - Non-critical Substation | 3 | 2 | 418 | 178 | 0 |  | 6 | 4 | 3 | 2 | 6 | 10 |  | 31 | 11 | N | 102
ETS.08.16760 | JAYNE SW STA | ETS.08.16760 | South Valley | Gates | SW STA - Trans | 70 | Tier 6 | No | T | 70 |  | n/a | 5 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 3 | 1 | 0 |  | 5 | 4 | n/a | 0 | 2 | 5 |  | 16 | 26 | N | n/a
ETS.16.10102 | JEFFERSON | ETS.16.10102 | Central Coast | San Carlos | T-Sub | 230,60 | Tier 5 | Yes | T | 230 |  | 12 | 9 |  | T2/3A | HFTD - Critical Substation | 7 | 0 | 256 | 178 | 0 |  | 9 | 6 | 7 | 0 | 6 | 10 |  | 38 | 4 | N | n/a
ETS.02.12524 | JESSUP | ETS.02.12524 | North Coast | Cottonwood | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 3 | 6 |  | T2/3A | HFTD - Non-critical Substation | n/a | 3 | 362 | 178 | 0 |  | 6 | 6 | n/a | 3 | 6 | 10 |  | 31 | 11 | Y | 227
ETS.15.12527 | JOLON | ETS.15.12527 | Central Coast | Moss Landing | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | 207 | 178 | 0 |  | 2 | 8 | n/a | 0 | 6 | 10 |  | 26 | 16 | N | 454
ETS.12.12530 | JUDAH | ETS.12.12530 | Bay Area | Martin | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 240 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 716
ETS.19.12533 | KANAKA | ETS.19.12533 | North Coast | Table Mountain | DSub in FERC | 12,115 | Tier 6 | No | Dist | 115 |  | 0 | 3 |  | T3 | HFTD - Non-critical Substation | n/a | 6 | 198 | 178 | 0 |  | 3 | 10 | n/a | 6 | 4 | 10 |  | 33 | 9 | N | 116
ETS.26.16435 | KASSON | ETS.26.16435 | North Valley | Tesla | T-Sub | 115,60 | Tier 6 | Yes | T | 115 |  | 9 | 8 |  | T1 | non-HFTD - Non-critical Substation | 4 | 0 | 240 | 178 | 0 |  | 8 | 4 | 4 | 0 | 6 | 10 |  | 32 | 10 | N | n/a
ETS.26.16440 | KELSO | ETS.26.16440 | North Valley | Tesla | Dist. Single Cust. | 12,230 | Tier 6 | Yes | Dist | 230 |  | 4 | 7 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 200 | 178 | 0 |  | 7 | 4 | n/a | 0 | 4 | 10 |  | 25 | 17 | N | n/a
ETS.08.16775 | KENT SW STA | ETS.08.16775 | South Valley | Gates | SW STA - Trans | 70 | Tier 6 | No | T | 70 |  | n/a | 5 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 3 | 1 | 0 |  | 5 | 4 | n/a | 0 | 2 | 5 |  | 16 | 26 | N | n/a
ETS.07.12540 | KERCKHOFF #1 PH | ETS.07.12540 | South Valley | Fresno | 0 | 12,70 | Tier 6 | Yes | G | 115 |  | 5 | 8 |  | T2 | HFTD - Non-critical Substation | n/a | 1 | 284 | 178 | 0 |  | 8 | 8 | n/a | 1 | 6 | 10 |  | 33 | 9 | N | n/a
ETS.07.12541 | KERCKHOFF #2 PH | ETS.07.12541 | South Valley | Fresno | 0 | 115 | Tier 6 | Yes | T | 115 |  | 5 | 8 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | 11 | 1 | 0 |  | 8 | 8 | n/a | 0 | 2 | 5 |  | 23 | 19 | N | n/a
ETS.07.12542 | KERMAN | ETS.07.12542 | South Valley | Fresno | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 225 | 178 | 0 |  | 2 | 4 | 3 | 0 | 6 | 10 |  | 25 | 17 | N | 463
ETS.10.10103 | KERN CANYON PH | ETS.10.10103 | South Valley | Bakersfield | 0 | 12,70 | Tier 6 | No | G | 70 |  | 2 | 4 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 4 | 4 | n/a | 0 | 1 | 1 |  | 10 | 32 | N | n/a
ETS.10.12544 | KERN OIL | ETS.10.12544 | South Valley | Bakersfield | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 7 | 6 |  | T1 | non-HFTD - Non-critical Substation | 6 | 2 | 225 | 178 | 0 |  | 6 | 4 | 6 | 2 | 6 | 10 |  | 34 | 8 | N | 402
ETS.10.10108 | KERN PP | ETS.10.10108 | South Valley | Bakersfield | T-Sub | 230,115,70 | Tier 3 | Yes | T | 230 |  | 29 | 9 |  | T1 | non-HFTD - Critical Substation | 3 | 0 | 416 | 178 | 0 |  | 9 | 4 | 3 | 0 | 6 | 10 |  | 32 | 10 | N | 591
ETS.10.13963 | KERN PP DIST | ETS.10.13963 | South Valley | Bakersfield | DSub in FERC | 21,115 | Tier 6 | No | Dist | 115 |  | n/a | 3 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 238 | 178 | 0 |  | 3 | 4 | n/a | 0 | 6 | 10 |  | 23 | 19 | N | n/a
ETS.02.10105 | KESWICK | ETS.02.10105 | North Coast | Cottonwood | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T3 | HFTD - Non-critical Substation | n/a | 2 | 196 | 178 | 0 |  | 2 | 10 | n/a | 2 | 4 | 10 |  | 28 | 14 | N | 257
ETS.08.12549 | KETTLEMAN HILLS | ETS.08.12549 | South Valley | Gates | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | 1 | 0 | 362 | 178 | 0 |  | 2 | 4 | 1 | 0 | 6 | 10 |  | 23 | 19 | N | 563
ETS.02.15739 | KILARC PH | ETS.02.15739 | North Coast | Cottonwood | 0 | 2,60 | Tier 6 | No | G | 60 |  | 3 | 4 |  | T3 | HFTD - Non-critical Substation | n/a | 0 | 16 | 1 | 0 |  | 4 | 10 | n/a | 0 | 2 | 5 |  | 21 | 21 | N | n/a
ETS.15.12553 | KING CITY | ETS.15.12553 | Central Coast | Moss Landing | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | 5 | 0 | 258 | 178 | 0 |  | 2 | 4 | 5 | 0 | 6 | 10 |  | 27 | 15 | N | 441
ETS.07.16370 | KINGS RIVER PH | ETS.07.16370 | South Valley | Fresno | 0 | 115 | Tier 6 | No | G | 115 |  | 4 | 4 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 4 | 8 | n/a | 0 | 1 | 1 |  | 14 | 28 | N | n/a
ETS.07.12554 | KINGSBURG | ETS.07.12554 | South Valley | Fresno | T&D | 12,115,70 | Tier 6 | Yes | T | 115 |  | 11 | 8 |  | T1 | non-HFTD - Non-critical Substation | 4 | 0 | 225 | 178 | 0 |  | 8 | 4 | 4 | 0 | 6 | 10 |  | 32 | 10 | N | 223
ETS.22.12557 | KIRKER | ETS.22.12557 | Central Coast | Concord | DSub in FERC | 21,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 3 | 1 | 746 | 178 | 0 |  | 6 | 4 | 3 | 1 | 8 | 10 |  | 32 | 10 | N | 150
ETS.21.12560 | KNIGHTS LANDING | ETS.21.12560 | North Valley | Vaca-Dixon | DSub in FERC | 12,115 | Tier 6 | No | Dist | 115 |  | 0 | 3 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 227 | 178 | 0 |  | 3 | 4 | 2 | 0 | 6 | 10 |  | 25 | 17 | N | 685
ETS.20.12561 | KONOCTI | ETS.20.12561 | North Coast | Ukiah | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 5 | 2 |  | T2 | HFTD - Non-critical Substation | n/a | 2 | 227 | 178 | 0 |  | 2 | 8 | n/a | 2 | 6 | 10 |  | 28 | 14 | Y | 27
ETS.15.13801 | LAGUNA SECA | ETS.15.13801 | Central Coast | Moss Landing | N/A | n/a | Tier 6 | No | Dist | 21 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 1 | 4 | n/a | 0 | 1 | 1 |  | 7 | 35 | N | n/a
ETS.15.12562 | LAGUNITAS | ETS.15.12562 | Central Coast | Moss Landing | DSub in FERC | 2.4,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2/3A | HFTD - Non-critical Substation | n/a | 0 | 196 | 178 | 0 |  | 2 | 6 | n/a | 0 | 4 | 10 |  | 22 | 20 | N | n/a
ETS.10.12564 | LAKEVIEW | ETS.10.12564 | South Valley | Bakersfield | DSub in FERC | 12,70 | Tier 6 | Yes | Dist | 70 |  | 3 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 1 | 240 | 178 | 0 |  | 6 | 4 | n/a | 1 | 6 | 10 |  | 27 | 15 | N | 387
ETS.13.10109 | LAKEVILLE | ETS.13.10109 | North Coast | McMaude | T&D | 12,115,230,60 | Tier 4 | Yes | T | 230 |  | 23 | 9 |  | T1 | non-HFTD - Critical Substation | 5 | 2 | 317 | 178 | 0 |  | 9 | 4 | 5 | 2 | 6 | 10 |  | 36 | 6 | N | 243
ETS.22.12565 | LAKEWOOD | ETS.22.12565 | Central Coast | Concord | DSub in FERC | 12,21,34,115 | Tier 6 | Yes | Dist | 115 |  | 9 | 6 |  | T1 | non-HFTD - Non-critical Substation | 6 | 2 | 500 | 178 | 0 |  | 6 | 4 | 6 | 2 | 6 | 10 |  | 34 | 8 | N | 63
ETS.21.16360 | LAMBIE SW STA | ETS.21.16360 | North Valley | Vaca-Dixon | SW STA - Trans | 230 | Tier 6 | Yes | T | 230 |  | 4 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 6 | 1 | 0 |  | 8 | 4 | n/a | 0 | 2 | 5 |  | 19 | 23 | N | n/a
ETS.26.16445 | LAMMERS | ETS.26.16445 | North Valley | Tesla | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 6 | 4 | n/a | 0 | 6 | 10 |  | 26 | 16 | N | 528
ETS.10.12566 | LAMONT | ETS.10.12566 | South Valley | Bakersfield | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T1 | non-HFTD - Non-critical Substation | 3 | 3 | 256 | 178 | 0 |  | 6 | 4 | 3 | 3 | 6 | 10 |  | 32 | 10 | N | 290
ETS.15.16807 | LAS AGUILAS SW STA | ETS.15.16807 | Central Coast | Moss Landing | SW STA - Trans | 230 | Tier 6 | No | T | 230 |  | n/a | 5 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 5 | 4 | n/a | 0 | 1 | 1 |  | 11 | 31 | N | n/a
ETS.13.12569 | LAS GALLINAS A | ETS.13.12569 | North Coast | McMaude | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 6 | 1 | 240 | 178 | 0 |  | 6 | 4 | 6 | 1 | 6 | 10 |  | 33 | 9 | Y | 140
ETS.07.12570 | LAS PALMAS | ETS.07.12570 | South Valley | Fresno | Dist. Single Cust. | 12,115 | Tier 6 | No | Dist | 115 |  | 0 | 3 |  | T1 | non-HFTD - Non-critical Substation | 1 | 0 | 188 | 178 | 0 |  | 3 | 4 | 1 | 0 | 4 | 10 |  | 22 | 20 | N | 746
ETS.26.10110 | LAS POSITAS | ETS.26.10110 | North Valley | Tesla | T&D | 12,21,115,230,60 | Tier 6 | Yes | T | 230 |  | 9 | 8 |  | T1 | non-HFTD - Non-critical Substation | 6 | 2 | 360 | 178 | 0 |  | 8 | 4 | 6 | 2 | 6 | 10 |  | 36 | 6 | N | 120
ETS.16.12572 | LAS PULGAS | ETS.16.12572 | Central Coast | San Carlos | DSub in FERC | 4,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 1 | 225 | 178 | 0 |  | 2 | 4 | 3 | 1 | 6 | 10 |  | 26 | 16 | N | 464
ETS.15.12573 | LAURELES | ETS.15.12573 | Central Coast | Moss Landing | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2/3A | HFTD - Non-critical Substation | n/a | 0 | 362 | 178 | 0 |  | 2 | 6 | n/a | 0 | 6 | 10 |  | 24 | 18 | N | 355
ETS.12.12576 | LAWNDALE | ETS.12.12576 | Bay Area | Martin | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 717
ETS.03.12577 | LAWRENCE | ETS.03.12577 | Central Coast | Cupertino | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 5 | 0 | 500 | 178 | 0 |  | 6 | 4 | 5 | 0 | 6 | 10 |  | 31 | 11 | N | 515
ETS.20.12583 | LAYTONVILLE | ETS.20.12583 | North Coast | Ukiah | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2 | HFTD - Non-critical Substation | n/a | 1 | 227 | 178 | 0 |  | 2 | 8 | n/a | 1 | 6 | 10 |  | 27 | 15 | N | 138
ETS.14.13711 | LE GRAND | ETS.14.13711 | North Valley | Merced | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 48 | 1 | 0 |  | 6 | 4 | n/a | 0 | 2 | 5 |  | 17 | 25 | N | 408
ETS.08.12589 | LEMOORE | ETS.08.12589 | South Valley | Gates | DSub in FERC | 12,70,115 | Tier 6 | No | Dist | 70 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | 4 | 0 | 225 | 178 | 0 |  | 2 | 4 | 4 | 0 | 6 | 10 |  | 26 | 16 | N | 571
ETS.08.16794 | LEPRINO SW STA | ETS.08.16794 | South Valley | Gates | SW STA - Trans | 115 | Tier 6 | No | T | 115 |  | n/a | 5 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 5 | 1 | 0 |  | 5 | 4 | n/a | 0 | 2 | 5 |  | 16 | 26 | N | n/a
ETS.10.12590 | LERDO | ETS.10.12590 | South Valley | Bakersfield | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 196 | 178 | 0 |  | 6 | 4 | 3 | 0 | 4 | 10 |  | 27 | 15 | N | 607
ETS.02.14972 | LEWISTON | ETS.02.14972 | North Coast | Cottonwood | SW STA - Trans | 60 | Tier 6 | No | T | 60 |  | 3 | 5 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 5 | 8 | n/a | 0 | 1 | 1 |  | 15 | 27 | N | n/a
ETS.19.16610 | LIME SADDLE PH | ETS.19.16610 | North Coast | Table Mountain | 0 | 12 | Tier 6 | No | G | 12 |  | n/a | 4 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 4 | 8 | n/a | 0 | 1 | 1 |  | 14 | 28 | N | n/a
ETS.04.12598 | LIMESTONE | ETS.04.12598 | North Valley | Del Mar | DSub in FERC | 2.4,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T3 | HFTD - Non-critical Substation | n/a | 0 | 240 | 178 | 0 |  | 2 | 10 | n/a | 0 | 6 | 10 |  | 28 | 14 | N | n/a
ETS.04.12599 | LINCOLN | ETS.04.12599 | North Valley | Del Mar | DSub in FERC | 12,21,60,115 | Tier 6 | Yes | Dist | 60 |  | 0 | 6 |  | T1 | non-HFTD - Non-critical Substation | 3 | 3 | 225 | 178 | 0 |  | 6 | 4 | 3 | 3 | 6 | 10 |  | 32 | 10 | N | 274
ETS.18.12601 | LINDEN | ETS.18.12601 | North Valley | Stockton | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 500 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 437
ETS.19.12603 | LIVE OAK | ETS.19.12603 | North Coast | Table Mountain | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 500 | 178 | 0 |  | 2 | 4 | 3 | 0 | 6 | 10 |  | 25 | 17 | N | 310
ETS.10.13803 | LIVE OAK SW STA | ETS.10.13803 | South Valley | Bakersfield | SW STA - Trans | 115 | Tier 6 | Yes | T | 115 |  | 3 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 8 | 1 | 0 |  | 8 | 4 | n/a | 0 | 2 | 5 |  | 19 | 23 | N | n/a
ETS.26.12604 | LIVERMORE | ETS.26.12604 | North Valley | Tesla | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 5 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 500 | 178 | 0 |  | 2 | 4 | 3 | 0 | 6 | 10 |  | 25 | 17 | N | 652
ETS.14.12605 | LIVINGSTON | ETS.14.12605 | North Valley | Merced | DSub in FERC | 12,70,115 | Tier 6 | No | Dist | 115 |  | 5 | 3 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 202 | 178 | 0 |  | 3 | 4 | n/a | 0 | 6 | 10 |  | 23 | 19 | N | 412
ETS.14.12606 | LIVINGSTON SW STA | ETS.14.12606 | North Valley | Merced | SW STA - Trans | 70115 | Tier 6 | No | T | 70 |  | 3 | 5 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 10 | 1 | 0 |  | 5 | 4 | n/a | 0 | 2 | 5 |  | 16 | 26 | N | n/a
ETS.03.12607 | LLAGAS | ETS.03.12607 | Central Coast | Cupertino | DSub in FERC | 21,115 | Tier 6 | Yes | Dist | 115 |  | 7 | 6 |  | T1 | non-HFTD - Non-critical Substation | 4 | 1 | 258 | 178 | 0 |  | 6 | 4 | 4 | 1 | 6 | 10 |  | 31 | 11 | N | 145
ETS.18.10111 | LOCKEFORD | ETS.18.10111 | North Valley | Stockton | T&D | 21,115,60,230 | Tier 6 | Yes | T | 230 |  | 16 | 8 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 258 | 178 | 0 |  | 8 | 4 | 2 | 0 | 6 | 10 |  | 30 | 12 | N | 329
ETS.03.12610 | LOCKHEED #1 | ETS.03.12610 | Central Coast | Cupertino | DSub in FERC | 12115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 9 | 1 | 0 |  | 6 | 4 | n/a | 0 | 2 | 5 |  | 17 | 25 | N | 726
ETS.03.12611 | LOCKHEED #2 | ETS.03.12611 | Central Coast | Cupertino | DSub in FERC | 12,115 | Tier 6 | No | Dist | 115 |  | 5 | 3 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 202 | 178 | 0 |  | 3 | 4 | n/a | 0 | 6 | 10 |  | 23 | 19 | N | 521
ETS.18.12613 | LODI | ETS.18.12613 | North Valley | Stockton | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 5 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 256 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 574
ETS.19.10112 | LOGAN CREEK | ETS.19.10112 | North Coast | Table Mountain | DSub in FERC | 21,230 | Tier 6 | Yes | Dist | 230 |  | 3 | 7 |  | T1 | non-HFTD - Non-critical Substation | n/a | 3 | 258 | 178 | 0 |  | 7 | 4 | n/a | 3 | 6 | 10 |  | 30 | 12 | N | 218
ETS.22.15418 | LONE TREE | ETS.22.15418 | Central Coast | Concord | DSub in FERC | 21230 | Tier 6 | No | Dist | 230 |  | 5 | 3 |  | T1 | non-HFTD - Non-critical Substation | n/a | 1 | 238 | 178 | 0 |  | 3 | 4 | n/a | 1 | 6 | 10 |  | 24 | 18 | N | 475
ETS.03.12618 | LOS ALTOS | ETS.03.12618 | Central Coast | Cupertino | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 500 | 178 | 0 |  | 2 | 4 | 3 | 0 | 6 | 10 |  | 25 | 17 | N | 629
ETS.14.10113 | LOS BANOS | ETS.14.10113 | North Valley | Merced | T-Sub | 500,230,70 | Tier 1 | Yes | T | 500 |  | 23 | 10 |  | T1 | non-HFTD - Critical Substation | 4 | 0 | 317 | 178 | 0 |  | 10 | 4 | 4 | 0 | 6 | 10 |  | 34 | 8 | N | n/a
ETS.15.12619 | LOS COCHES | ETS.15.12619 | Central Coast | Moss Landing | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 240 | 178 | 0 |  | 2 | 4 | 3 | 0 | 6 | 10 |  | 25 | 17 | N | 427
ETS.03.16010 | LOS ESTEROS | ETS.03.16010 | Central Coast | Cupertino | T-Sub | 230,115 | Tier 6 | Yes | T | 230 |  | 13 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 317 | 178 | 0 |  | 8 | 4 | n/a | 0 | 6 | 10 |  | 28 | 14 | N | n/a
ETS.03.12620 | LOS GATOS | ETS.03.12620 | Central Coast | Cupertino | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | 4 | 2 | 238 | 178 | 0 |  | 2 | 4 | 4 | 2 | 6 | 10 |  | 28 | 14 | N | 26
ETS.02.12621 | LOS MOLINOS | ETS.02.12621 | North Coast | Cottonwood | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 2 | 225 | 178 | 0 |  | 2 | 4 | n/a | 2 | 6 | 10 |  | 24 | 18 | N | 253
ETS.15.12622 | LOS OSITOS | ETS.15.12622 | Central Coast | Moss Landing | DSub in FERC | 21,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 227 | 178 | 0 |  | 2 | 4 | 2 | 0 | 6 | 10 |  | 24 | 18 | N | 353
ETS.08.12623 | LOST HILLS | ETS.08.12623 | South Valley | Gates | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 240 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 738
ETS.18.12625 | LOUISE | ETS.18.12625 | North Valley | Stockton | SW STA - Trans | 60 | Tier 6 | No | T | 60 |  | 4 | 5 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 8 | 1 | 0 |  | 5 | 4 | n/a | 0 | 2 | 5 |  | 16 | 26 | N | n/a
ETS.06.12626 | LOW GAP | ETS.06.12626 | North Coast | Eureka | DSub in FERC | 12,115 | Tier 6 | No | Dist | 115 |  | 0 | 3 |  | T2 | HFTD - Non-critical Substation | 3 | 2 | 198 | 178 | 0 |  | 3 | 8 | 3 | 2 | 4 | 10 |  | 30 | 12 | N | 131
ETS.20.12629 | LOWER LAKE | ETS.20.12629 | North Coast | Ukiah | SW STA - Trans | 115 | Tier 6 | No | T | 115 |  | 2 | 5 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | 15 | 1 | 0 |  | 5 | 8 | n/a | 0 | 2 | 5 |  | 20 | 22 | N | n/a
ETS.03.12630 | LOYOLA | ETS.03.12630 | Central Coast | Cupertino | DSub in FERC | 4,12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | 4 | 1 | 500 | 178 | 0 |  | 2 | 4 | 4 | 1 | 6 | 10 |  | 27 | 15 | N | 201
ETS.20.12631 | LUCERNE | ETS.20.12631 | North Coast | Ukiah | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T2 | HFTD - Non-critical Substation | n/a | 3 | 240 | 178 | 0 |  | 6 | 8 | n/a | 3 | 6 | 10 |  | 33 | 9 | N | 23
ETS.03.12634 | MABURY | ETS.03.12634 | Central Coast | Cupertino | DSub in FERC | 12,60,115 | Tier 6 | No | Dist | 115 |  | 4 | 3 |  | T1 | non-HFTD - Non-critical Substation | 5 | 0 | 240 | 178 | 0 |  | 3 | 4 | 5 | 0 | 6 | 10 |  | 28 | 14 | N | 392
ETS.14.12636 | MADERA | ETS.14.12636 | North Valley | Merced | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 6 | 2 |  | T1 | non-HFTD - Non-critical Substation | 5 | 0 | 258 | 178 | 0 |  | 2 | 4 | 5 | 0 | 6 | 10 |  | 27 | 15 | N | 467
ETS.21.12637 | MADISON | ETS.21.12637 | North Valley | Vaca-Dixon | DSub in FERC | 12,21,60,115 | Tier 6 | No | Dist | 115 |  | 0 | 3 |  | T1 | non-HFTD - Non-critical Substation | 3 | 3 | 284 | 178 | 0 |  | 3 | 4 | 3 | 3 | 6 | 10 |  | 29 | 13 | N | 84
ETS.10.12639 | MAGUNDEN | ETS.10.12639 | South Valley | Bakersfield | DSub in FERC | 12,21,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T1 | non-HFTD - Non-critical Substation | 5 | 0 | 317 | 178 | 0 |  | 6 | 4 | 5 | 0 | 6 | 10 |  | 31 | 11 | N | 426
ETS.21.12640 | MAINE PRAIRIE | ETS.21.12640 | North Valley | Vaca-Dixon | DSub in FERC | 4,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 202 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 763
ETS.07.12643 | MALAGA | ETS.07.12643 | South Valley | Fresno | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 6 | 6 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 500 | 178 | 0 |  | 6 | 4 | 3 | 0 | 6 | 10 |  | 29 | 13 | N | 320
ETS.07.12644 | MANCHESTER | ETS.07.12644 | South Valley | Fresno | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 238 | 178 | 0 |  | 6 | 4 | 3 | 0 | 6 | 10 |  | 29 | 13 | N | 519
ETS.18.12645 | MANTECA | ETS.18.12645 | North Valley | Stockton | T&D | 17,115,60 | Tier 6 | Yes | T | 115 |  | 16 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 227 | 178 | 0 |  | 8 | 4 | n/a | 0 | 6 | 10 |  | 28 | 14 | N | 135
ETS.23.13804 | MAPLE | ETS.23.13804 | Bay Area | Oakport | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 227 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 710
ETS.06.12648 | MAPLE CREEK | ETS.06.12648 | North Coast | Eureka | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T2 | HFTD - Non-critical Substation | 5 | 2 | 284 | 178 | 0 |  | 2 | 8 | 5 | 2 | 6 | 10 |  | 33 | 9 | N | 202
ETS.10.12652 | MARICOPA | ETS.10.12652 | South Valley | Bakersfield | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 207 | 178 | 0 |  | 2 | 4 | 2 | 0 | 6 | 10 |  | 24 | 18 | N | 646
ETS.14.13367 | MARIPOSA | ETS.14.13367 | North Valley | Merced | DSub in FERC | 21,70 | Tier 6 | No | Dist | 70 |  | 4 | 2 |  | T2 | HFTD - Non-critical Substation | 5 | 0 | 256 | 178 | 0 |  | 2 | 8 | 5 | 0 | 6 | 10 |  | 31 | 11 | N | 255
ETS.22.12656 | MARSH | ETS.22.12656 | Central Coast | Concord | Dist. Single Cust. | 4,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 202 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | n/a
ETS.18.12657 | MARTELL | ETS.18.12657 | North Valley | Stockton | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2/3A | HFTD - Non-critical Substation | n/a | 3 | 362 | 178 | 0 |  | 2 | 6 | n/a | 3 | 6 | 10 |  | 27 | 15 | N | 273
ETS.22.12658 | MARTINEZ PP | ETS.22.12658 | Central Coast | Concord | SW STA - Trans | 115 | Tier 6 | Yes | T | 115 |  | 9 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 15 | 1 | 0 |  | 8 | 4 | n/a | 0 | 2 | 5 |  | 19 | 23 | N | n/a
ETS.04.12660 | MARYSVILLE | ETS.04.12660 | North Valley | Del Mar | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 5 | 2 |  | T1 | non-HFTD - Non-critical Substation | 4 | 0 | 258 | 178 | 0 |  | 2 | 4 | 4 | 0 | 6 | 10 |  | 26 | 16 | N | 451
ETS.21.12662 | MAXWELL | ETS.21.12662 | North Valley | Vaca-Dixon | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 2 | 240 | 178 | 0 |  | 2 | 4 | n/a | 2 | 6 | 10 |  | 24 | 18 | N | 244
ETS.02.12664 | MCARTHUR | ETS.02.12664 | North Coast | Cottonwood | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2/3A | HFTD - Non-critical Substation | 4 | 0 | 225 | 178 | 0 |  | 2 | 6 | 4 | 0 | 6 | 10 |  | 28 | 14 | N | 340
ETS.07.10115 | MCCALL | ETS.07.10115 | South Valley | Fresno | T&D | 12,115,230 | Tier 3 | Yes | T | 230 |  | 22 | 9 |  | T1 | non-HFTD - Critical Substation | 6 | 0 | 317 | 178 | 0 |  | 9 | 4 | 6 | 0 | 6 | 10 |  | 35 | 7 | N | 448
ETS.18.12666 | MCDONALD ISLAND | ETS.18.12666 | North Valley | Stockton | Dist. Single Cust. | 4,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 196 | 178 | 0 |  | 2 | 4 | n/a | 0 | 4 | 10 |  | 20 | 22 | N | n/a
ETS.10.12667 | MCFARLAND | ETS.10.12667 | South Valley | Bakersfield | DSub in FERC | 12,70,115 | Tier 6 | No | Dist | 70 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | 5 | 0 | 48 | 1 | 0 |  | 2 | 4 | 5 | 0 | 2 | 5 |  | 18 | 24 | N | 389
ETS.03.12668 | MCKEE | ETS.03.12668 | Central Coast | Cupertino | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 6 | 2 | 418 | 178 | 0 |  | 6 | 4 | 6 | 2 | 6 | 10 |  | 34 | 8 | N | 45
ETS.10.12672 | MCKITTRICK | ETS.10.12672 | South Valley | Bakersfield | DSub in FERC | 12,70 | Tier 6 | No | Dist | 115 |  | 0 | 3 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 19 | 1 | 0 |  | 3 | 4 | n/a | 0 | 2 | 5 |  | 14 | 28 | N | 682
ETS.07.12673 | MCMULLIN | ETS.07.12673 | South Valley | Fresno | DSub in FERC | 12,230 | Tier 6 | No | Dist | 230 |  | 2 | 3 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 3 | 4 | n/a | 0 | 6 | 10 |  | 23 | 19 | N | 551
ETS.22.12678 | MEADOW LANE | ETS.22.12678 | Central Coast | Concord | DSub in FERC | 21,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 7 | 1 | 258 | 178 | 0 |  | 6 | 4 | 7 | 1 | 6 | 10 |  | 34 | 8 | N | 67
ETS.14.12680 | MELONES SW STA | ETS.14.12680 | North Valley | Merced | SW STA - Trans | 115 | Tier 6 | Yes | T | 115 |  | 5 | 8 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | 8 | 1 | 0 |  | 8 | 8 | n/a | 0 | 2 | 5 |  | 23 | 19 | N | n/a
ETS.20.12681 | MENDOCINO | ETS.20.12681 | North Coast | Ukiah | T&D | 12,60,115 | Tier 6 | Yes | T | 115 |  | 13 | 8 |  | T2/3A | HFTD - Non-critical Substation | n/a | 1 | 362 | 178 | 0 |  | 8 | 6 | n/a | 1 | 6 | 10 |  | 31 | 11 | N | 90
ETS.14.12682 | MENDOTA | ETS.14.12682 | North Valley | Merced | T&D | 12,115,70 | Tier 6 | No | T | 115 |  | 8 | 5 |  | T1 | non-HFTD - Non-critical Substation | 1 | 0 | 225 | 178 | 0 |  | 5 | 4 | 1 | 0 | 6 | 10 |  | 26 | 16 | N | 377
ETS.16.12683 | MENLO | ETS.16.12683 | Central Coast | San Carlos | DSub in FERC | 4,12,60 | Tier 6 | No | Dist | 60 |  | 6 | 2 |  | T1 | non-HFTD - Non-critical Substation | 4 | 2 | 258 | 178 | 0 |  | 2 | 4 | 4 | 2 | 6 | 10 |  | 28 | 14 | N | 77
ETS.14.12684 | MERCED | ETS.14.12684 | North Valley | Merced | T&D | 12,21,115,70 | Tier 6 | Yes | T | 115 |  | 9 | 8 |  | T1 | non-HFTD - Non-critical Substation | 4 | 0 | 256 | 178 | 0 |  | 8 | 4 | 4 | 0 | 6 | 10 |  | 32 | 10 | N | 536
ETS.14.10124 | MERCED FALLS PH | ETS.14.10124 | North Valley | Merced | 0 | 12,70 | Tier 6 | No | Dist | 70 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | 7 | 1 | 240 | 178 | 0 |  | 2 | 4 | 7 | 1 | 6 | 10 |  | 30 | 12 | N | 107
ETS.14.12685 | MERCY SPRINGS | ETS.14.12685 | North Valley | Merced | DSub in FERC | 2.4,12,60 | Tier 6 | No | Dist | 70 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 202 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | n/a
ETS.14.16786 | MERCY SPRINGS SW STA | ETS.14.16786 | North Valley | Merced | SW STA - Trans | 70 | Tier 6 | No | T | 70 |  | n/a | 5 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 8 | 1 | 0 |  | 5 | 4 | n/a | 0 | 2 | 5 |  | 16 | 26 | N | n/a
ETS.21.12686 | MERIDIAN | ETS.21.12686 | North Valley | Vaca-Dixon | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 19 | 1 | 0 |  | 2 | 4 | n/a | 0 | 2 | 5 |  | 13 | 29 | N | 673
ETS.17.10117 | MESA | ETS.17.10117 | South Valley | Pismo | T&D | 12,230,115 | Tier 5 | Yes | T | 230 |  | 13 | 9 |  | T2/3A | HFTD - Critical Substation | n/a | 0 | 317 | 178 | 0 |  | 9 | 6 | n/a | 0 | 6 | 10 |  | 31 | 11 | N | 468
ETS.03.10118 | METCALF | ETS.03.10118 | Central Coast | Cupertino | T-Sub | 500,230,115 | Tier 1 | Yes | T | 500 |  | 37 | 10 |  | T1 | non-HFTD - Critical Substation | 2 | 0 | 362 | 178 | 0 |  | 10 | 4 | 2 | 0 | 6 | 10 |  | 32 | 10 | N | n/a
ETS.18.12688 | METTLER | ETS.18.12688 | North Valley | Stockton | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 240 | 178 | 0 |  | 2 | 4 | 3 | 0 | 6 | 10 |  | 25 | 17 | N | 363
ETS.18.12691 | MIDDLE RIVER | ETS.18.12691 | North Valley | Stockton | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 196 | 178 | 0 |  | 2 | 4 | n/a | 0 | 4 | 10 |  | 20 | 22 | N | 549
ETS.20.12692 | MIDDLETOWN | ETS.20.12692 | North Coast | Ukiah | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T2 | HFTD - Non-critical Substation | 3 | 4 | 238 | 178 | 0 |  | 2 | 8 | 3 | 4 | 6 | 10 |  | 33 | 9 | Y | 51
ETS.10.12696 | MIDSUN SW STA | ETS.10.12696 | South Valley | Bakersfield | SW STA - Trans | 115 | Tier 6 | Yes | T | 115 |  | 3 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 8 | 1 | 0 |  | 8 | 4 | n/a | 0 | 2 | 5 |  | 19 | 23 | N | n/a
ETS.10.10119 | MIDWAY | ETS.10.10119 | South Valley | Bakersfield | T&D | 12,115,230,500 | Tier 1 | Yes | T | 500 | 10 | 45 | 10 |  | T1 | non-HFTD - Critical Substation | 3 | 0 | 416 | 178 | 0 |  | 10 | 4 | 3 | 0 | 6 | 10 |  | 33 | 9 | N | 702
ETS.12.12700 | MILLBRAE | ETS.12.12700 | Bay Area | Martin | T&D | 4,12,60,115 | Tier 6 | Yes | T | 115 |  | 9 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 500 | 178 | 0 |  | 8 | 4 | n/a | 0 | 6 | 10 |  | 28 | 14 | N | 337
ETS.03.12702 | MILPITAS | ETS.03.12702 | Central Coast | Cupertino | DSub in FERC | 12,21,115 | Tier 6 | Yes | Dist | 115 |  | 7 | 6 |  | T1 | non-HFTD - Non-critical Substation | 6 | 2 | 238 | 178 | 0 |  | 6 | 4 | 6 | 2 | 6 | 10 |  | 34 | 8 | N | 152
ETS.02.13578 | MINERAL | ETS.02.13578 | North Coast | Cottonwood | DSub not in FERC | 12,21 | Tier 6 | No | Dist | 21 |  | n/a | 1 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | 240 | 178 | 0 |  | 1 | 8 | n/a | 0 | 6 | 10 |  | 25 | 17 | N | n/a
ETS.23.13579 | MIRA VISTA | ETS.23.13579 | Bay Area | Oakport | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | 4 | 0 | 240 | 178 | 0 |  | 1 | 4 | 4 | 0 | 6 | 10 |  | 25 | 17 | N | 657
ETS.13.12704 | MIRABEL | ETS.13.12704 | North Coast | McMaude | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 1 | 258 | 178 | 0 |  | 2 | 4 | n/a | 1 | 6 | 10 |  | 23 | 19 | Y | 92
ETS.04.12710 | MISSOURI FLAT SW STA | ETS.04.12710 | North Valley | Del Mar | SW STA - Trans | 115 | Tier 6 | No | T | 115 |  | n/a | 5 |  | T2/3A | HFTD - Non-critical Substation | n/a | 0 | 6 | 1 | 0 |  | 5 | 6 | n/a | 0 | 2 | 5 |  | 18 | 24 | N | n/a
ETS.14.12689 | MI-WUK | ETS.14.12689 | North Valley | Merced | DSub in FERC | 17,115 | Tier 6 | Yes | Dist | 115 |  | 3 | 6 |  | T3 | HFTD - Non-critical Substation | 6 | 2 | 227 | 178 | 0 |  | 6 | 10 | 6 | 2 | 6 | 10 |  | 40 | 2 | N | 46
ETS.13.12719 | MOLINO | ETS.13.12719 | North Coast | McMaude | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 1 | 317 | 178 | 0 |  | 2 | 4 | n/a | 1 | 6 | 10 |  | 23 | 19 | Y | 4
ETS.18.12721 | MONARCH | ETS.18.12721 | North Valley | Stockton | DSub in FERC | 4,60 | Tier 6 | No | Dist | 60 |  | 0 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 50 | 1 | 0 |  | 2 | 4 | n/a | 0 | 2 | 5 |  | 13 | 29 | N | 628
ETS.13.12722 | MONROE | ETS.13.12722 | North Coast | McMaude | DSub in FERC | 12,21,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 3 | 317 | 178 | 0 |  | 6 | 4 | n/a | 3 | 6 | 10 |  | 29 | 13 | N | 296
ETS.03.10126 | MONTA VISTA | ETS.03.10126 | Central Coast | Cupertino | T-Sub | 230,60,115 | Tier 4 | Yes | T | 230 |  | 27 | 9 |  | T1 | non-HFTD - Critical Substation | 7 | 0 | 317 | 178 | 0 |  | 9 | 4 | 7 | 0 | 6 | 10 |  | 36 | 6 | N | n/a
ETS.03.12724 | MONTAGUE | ETS.03.12724 | Central Coast | Cupertino | DSub in FERC | 21,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 238 | 178 | 0 |  | 6 | 4 | 3 | 0 | 6 | 10 |  | 29 | 13 | N | 489
ETS.13.12725 | MONTE RIO | ETS.13.12725 | North Coast | McMaude | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T3 | HFTD - Non-critical Substation | 4 | 1 | 238 | 178 | 0 |  | 2 | 10 | 4 | 1 | 6 | 10 |  | 33 | 9 | Y | 35
ETS.15.12726 | MONTEREY | ETS.15.12726 | Central Coast | Moss Landing | DSub in FERC | 4,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 500 | 178 | 0 |  | 2 | 4 | 3 | 0 | 6 | 10 |  | 25 | 17 | N | 620
ETS.13.12729 | MONTICELLO | ETS.13.12729 | North Coast | McMaude | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T2 | HFTD - Non-critical Substation | 3 | 6 | 362 | 178 | 0 |  | 6 | 8 | 3 | 6 | 6 | 10 |  | 39 | 3 | N | 165
ETS.22.10125 | MORAGA | ETS.22.10125 | Central Coast | Concord | T&D | 12,115,230 | Tier 3 | Yes | T | 230 |  | 25 | 9 |  | T2 | HFTD - Critical Substation | 6 | 2 | 238 | 178 | 0 |  | 9 | 8 | 6 | 2 | 6 | 10 |  | 41 | 1 | N | 47
ETS.03.12731 | MORGAN HILL | ETS.03.12731 | Central Coast | Cupertino | DSub in FERC | 21,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 4 | 2 | 238 | 178 | 0 |  | 6 | 4 | 4 | 2 | 6 | 10 |  | 32 | 10 | N | 38
ETS.18.12732 | MORMON | ETS.18.12732 | North Valley | Stockton | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 225 | 178 | 0 |  | 2 | 4 | 3 | 0 | 6 | 10 |  | 25 | 17 | N | 319
ETS.17.16020 | MORRO BAY DIST | ETS.17.16020 | South Valley | Pismo | N/A | n/a | Tier 6 | No | T | 115 |  | 11 | 5 |  | T1 | non-HFTD - Non-critical Substation | 10 | 0 | 360 | 178 | 0 |  | 5 | 4 | 10 | 0 | 6 | 10 |  | 35 | 7 | N | 453
ETS.17.10123 | MORRO BAY SW STA | ETS.17.10123 | South Valley | Pismo | T&D | 12115230 | Tier 2 | Yes | T | 230 |  | 11 | 10 |  | T2/3A | HFTD - Critical Substation | n/a | 0 | 238 | 178 | 0 |  | 10 | 6 | n/a | 0 | 6 | 10 |  | 32 | 10 | N | n/a
ETS.12.13806 | MOSCONE | ETS.12.13806 | Bay Area | Martin | Dist. Single Cust. | 4,34.5 | Tier 6 | No | Dist | 34.5 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 3 | 1 | 0 |  | 1 | 4 | n/a | 0 | 2 | 5 |  | 12 | 30 | N | n/a
ETS.18.12734 | MOSHER | ETS.18.12734 | North Valley | Stockton | DSub in FERC | 21,60,115 | Tier 6 | No | Dist | 60 |  | 5 | 2 |  | T1 | non-HFTD - Non-critical Substation | 4 | 0 | 238 | 178 | 0 |  | 2 | 4 | 4 | 0 | 6 | 10 |  | 26 | 16 | N | 533
ETS.15.10122 | MOSS LANDING PP | ETS.15.10122 | Central Coast | Moss Landing | T-Sub | 500,230,115 | Tier 1 | Yes | T | 500 | 9 | 30 | 10 |  | T1 | non-HFTD - Critical Substation | n/a | 0 | 746 | 178 | 0 |  | 10 | 4 | n/a | 0 | 8 | 10 |  | 32 | 10 | N | n/a
ETS.03.12737 | MOUNTAIN VIEW | ETS.03.12737 | Central Coast | Cupertino | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 418 | 178 | 0 |  | 6 | 4 | n/a | 0 | 6 | 10 |  | 26 | 16 | N | 331
ETS.09.12736 | MT EDEN | ETS.09.12736 | Central Coast | Hayward | DSub in FERC | 12115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 317 | 178 | 0 |  | 6 | 4 | 3 | 0 | 6 | 10 |  | 29 | 13 | N | 266
ETS.02.13785 | MTN GATE JUNCTION | ETS.02.13785 | North Coast | Cottonwood |  |  | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | 8 | 1 | 0 |  | 2 | 8 | n/a | 0 | 2 | 5 |  | 17 | 25 | N | n/a
ETS.04.13581 | MTN QUARRIES | ETS.04.13581 | North Valley | Del Mar | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T2 | HFTD - Non-critical Substation | n/a | 3 | 225 | 178 | 0 |  | 2 | 8 | n/a | 3 | 6 | 10 |  | 29 | 13 | N | 53
ETS.08.16795 | MUSTANG SW STA | ETS.08.16795 | South Valley | Gates | SW STA - Trans | 230 | Tier 6 | No | T | 230 |  | n/a | 5 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 6 | 1 | 0 |  | 5 | 4 | n/a | 0 | 2 | 5 |  | 16 | 26 | N | n/a
ETS.13.12742 | NAPA | ETS.13.12742 | North Coast | McMaude | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 5 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 2 | 240 | 178 | 0 |  | 2 | 4 | 3 | 2 | 6 | 10 |  | 27 | 15 | N | 118
ETS.19.13946 | NARROWS | ETS.19.13946 | North Coast | Table Mountain | DSub in FERC | 21,60 | Tier 6 | No | Dist | 60 |  | 5 | 2 |  | T2 | HFTD - Non-critical Substation | 5 | 4 | 225 | 178 | 0 |  | 2 | 8 | 5 | 4 | 6 | 10 |  | 35 | 7 | N | 78
ETS.19.16825 | NARROWS PH #1 | ETS.19.16825 | North Coast | Table Mountain | 0 | 60 | Tier 6 | No | G | 60 |  | n/a | 4 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 4 | 8 | n/a | 0 | 1 | 1 |  | 14 | 28 | N | n/a
ETS.15.13906 | NAVY LAB | ETS.15.13906 | Central Coast | Moss Landing | Dist. Single Cust. | 4,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 198 | 178 | 0 |  | 2 | 4 | n/a | 0 | 4 | 10 |  | 20 | 22 | N | n/a
ETS.15.12748 | NAVY SCHOOL | ETS.15.12748 | Central Coast | Moss Landing | Dist. Single Cust. | 4,60 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 202 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | n/a
ETS.19.16630 | NEW DE SABLA PH | ETS.19.16630 | North Coast | Table Mountain | 0 | n/a | Tier 6 | No | G | 60 |  | 2 | 4 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 4 | 4 | n/a | 0 | 1 | 1 |  | 10 | 32 | N | n/a
ETS.18.12751 | NEW HOPE | ETS.18.12751 | North Valley | Stockton | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 240 | 178 | 0 |  | 2 | 4 | 2 | 0 | 6 | 10 |  | 24 | 18 | N | 530
ETS.07.16080 | NEW KEARNEY | ETS.07.16080 | South Valley | Fresno | T-Sub | 230,70 | Tier 6 | Yes | T | 230 |  | 12 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 500 | 178 | 0 |  | 8 | 4 | n/a | 0 | 6 | 10 |  | 28 | 14 | N | n/a
ETS.09.10185 | NEWARK | ETS.09.10185 | Central Coast | Hayward | T&D | 12,115,21,230,60 | Tier 2 | Yes | T | 230 |  | 44 | 10 |  | T1 | non-HFTD - Critical Substation | 7 | 0 | 416 | 178 | 0 |  | 10 | 4 | 7 | 0 | 6 | 10 |  | 37 | 5 | N | 386
ETS.09.10186 | NEWARK DIST | ETS.09.10186 | Central Coast | Hayward | DSub in FERC | 21,230 | Tier 6 | Yes | Dist | 230 |  | 4 | 7 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 7 | 4 | n/a | 0 | 6 | 10 |  | 27 | 15 | N | n/a
ETS.06.12752 | NEWBURG | ETS.06.12752 | North Coast | Eureka | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | 4 | 2 | 240 | 178 | 0 |  | 2 | 4 | 4 | 2 | 6 | 10 |  | 28 | 14 | Y | 279
ETS.04.16590 | NEWCASTLE PH | ETS.04.16590 | North Valley | Del Mar | 0 | 115 | Tier 6 | No | Dist | 115 |  | 3 | 3 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 3 | 8 | n/a | 0 | 1 | 1 |  | 13 | 29 | N | n/a
ETS.14.12754 | NEWHALL | ETS.14.12754 | North Valley | Merced | DSub in FERC | 12,115 | Tier 6 | No | Dist | 115 |  | 4 | 3 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 198 | 178 | 0 |  | 3 | 4 | n/a | 0 | 4 | 10 |  | 21 | 21 | N | 361
ETS.14.12755 | NEWMAN | ETS.14.12755 | North Valley | Merced | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 225 | 178 | 0 |  | 2 | 4 | 2 | 0 | 6 | 10 |  | 24 | 18 | N | 588
ETS.10.12760 | NORCO | ETS.10.12760 | South Valley | Bakersfield | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 2 | 6 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 30 | 1 | 0 |  | 6 | 4 | 2 | 0 | 2 | 5 |  | 19 | 23 | N | 740
ETS.19.12761 | NORD | ETS.19.12761 | North Coast | Table Mountain | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 258 | 178 | 0 |  | 6 | 4 | n/a | 0 | 6 | 10 |  | 26 | 16 | N | 639
ETS.12.12762 | NORIEGA | ETS.12.12762 | Bay Area | Martin | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 196 | 178 | 0 |  | 1 | 4 | n/a | 0 | 4 | 10 |  | 19 | 23 | N | 303
ETS.03.16140 | NORTECH | ETS.03.16140 | Central Coast | Cupertino | DSub in FERC | 21,115 | Tier 6 | Yes | Dist | 115 |  | 3 | 6 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 200 | 178 | 0 |  | 6 | 4 | 3 | 0 | 4 | 10 |  | 27 | 15 | N | 459
ETS.18.12764 | NORTH BRANCH | ETS.18.12764 | North Valley | Stockton | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T2 | HFTD - Non-critical Substation | 4 | 1 | 258 | 178 | 0 |  | 2 | 8 | 4 | 1 | 6 | 10 |  | 31 | 11 | N | 231
ETS.09.16400 | NORTH DUBLIN | ETS.09.16400 | Central Coast | Hayward | DSub in FERC | 21,230 | Tier 6 | No | Dist | 230 |  | 3 | 3 |  | T2 | HFTD - Non-critical Substation | n/a | 1 | 225 | 178 | 0 |  | 3 | 8 | n/a | 1 | 6 | 10 |  | 28 | 14 | N | 156
ETS.13.12767 | NORTH TOWER | ETS.13.12767 | North Coast | McMaude | DSub in FERC | 12,21,115 | Tier 6 | Yes | Dist | 115 |  | 7 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 317 | 178 | 0 |  | 6 | 4 | n/a | 0 | 6 | 10 |  | 26 | 16 | N | 524
ETS.19.16480 | NOTRE DAME | ETS.19.16480 | North Coast | Table Mountain | DSub in FERC | 12,115 | Tier 6 | No | Dist | 115 |  | 3 | 3 |  | T1 | non-HFTD - Non-critical Substation | 3 | 6 | 225 | 178 | 0 |  | 3 | 4 | 3 | 6 | 6 | 10 |  | 32 | 10 | N | 37
ETS.13.12769 | NOVATO | ETS.13.12769 | North Coast | McMaude | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 1 | 225 | 178 | 0 |  | 2 | 4 | n/a | 1 | 6 | 10 |  | 23 | 19 | N | 212
ETS.23.13586 | OAK | ETS.23.13586 | Bay Area | Oakport | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T2 | HFTD - Non-critical Substation | n/a | 1 | 227 | 178 | 0 |  | 1 | 8 | n/a | 1 | 6 | 10 |  | 26 | 16 | N | 497
ETS.19.16625 | OAK FLAT PH | ETS.19.16625 | North Coast | Table Mountain | 0 | 21 | Tier 6 | No | G | 21 |  | n/a | 4 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 4 | 8 | n/a | 0 | 1 | 1 |  | 14 | 28 | N | n/a
ETS.18.12772 | OAK PARK | ETS.18.12772 | North Valley | Stockton | DSub in FERC | 4,12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 240 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 725
ETS.07.12774 | OAKHURST | ETS.07.12774 | South Valley | Fresno | DSub in FERC | 12,115 | Tier 6 | No | Dist | 115 |  | 4 | 3 |  | T3 | HFTD - Non-critical Substation | 5 | 1 | 500 | 178 | 0 |  | 3 | 10 | 5 | 1 | 6 | 10 |  | 35 | 7 | N | 19
ETS.23.13588 | OAKLAND C (OAKLAND PP) | ETS.23.13588 | Bay Area | Oakport | DSub in FERC | 12115230 | Tier 6 | Yes | Dist | 115 |  | 10 | 6 |  | T1 | non-HFTD - Non-critical Substation | 6 | 0 | 362 | 178 | 0 |  | 6 | 4 | 6 | 0 | 6 | 10 |  | 32 | 10 | N | 578
ETS.23.12776 | OAKLAND D | ETS.23.12776 | Bay Area | Oakport | DSub in FERC | 4,12,115 | Tier 6 | Yes | Dist | 115 |  | 7 | 6 |  | T1 | non-HFTD - Non-critical Substation | 10 | 1 | 1184 | 178 | 0 |  | 6 | 4 | 10 | 1 | 10 | 10 |  | 41 | 1 | N | 260
ETS.23.13573 | OAKLAND I | ETS.23.13573 | Bay Area | Oakport | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 362 | 178 | 0 |  | 1 | 4 | 3 | 0 | 6 | 10 |  | 24 | 18 | N | 576
ETS.23.12777 | OAKLAND J | ETS.23.12777 | Bay Area | Oakport | DSub in FERC | 4,12,60,115 | Tier 6 | Yes | Dist | 115 |  | 7 | 6 |  | T1 | non-HFTD - Non-critical Substation | 5 | 1 | 225 | 178 | 0 |  | 6 | 4 | 5 | 1 | 6 | 10 |  | 32 | 10 | N | 281
ETS.23.13368 | OAKLAND K (CLAREMONT) | ETS.23.13368 | Bay Area | Oakport | DSub in FERC | 12115 | Tier 6 | Yes | Dist | 115 |  | 7 | 6 |  | T1 | non-HFTD - Non-critical Substation | 7 | 2 | 746 | 178 | 0 |  | 6 | 4 | 7 | 2 | 8 | 10 |  | 37 | 5 | N | 189
ETS.23.12778 | OAKLAND L | ETS.23.12778 | Bay Area | Oakport | DSub in FERC | 4,12,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 319 | 178 | 0 |  | 6 | 4 | n/a | 0 | 6 | 10 |  | 26 | 16 | N | 356
ETS.23.12779 | OAKLAND X | ETS.23.12779 | Bay Area | Oakport | DSub in FERC | 4,12,115 | Tier 6 | Yes | Dist | 115 |  | 10 | 6 |  | T1 | non-HFTD - Non-critical Substation | 9 | 2 | 240 | 178 | 0 |  | 6 | 4 | 9 | 2 | 6 | 10 |  | 37 | 5 | N | 197
ETS.13.10132 | OAKMONT NORTH | ETS.13.10132 | North Coast | McMaude | N/A | - | Tier 6 | No | n/a | n/a |  | n/a | 5 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 5 | 8 | n/a | 0 | 1 | 1 |  | 15 | 27 | N | n/a
ETS.13.10133 | OAKMONT SOUTH | ETS.13.10133 | North Coast | McMaude | N/A | - | Tier 6 | No | n/a | n/a |  | n/a | 5 |  | T3 | HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 5 | 10 | n/a | 0 | 1 | 1 |  | 17 | 25 | N | n/a
ETS.12.12780 | OCEAN AVE | ETS.12.12780 | Bay Area | Martin | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 258 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 543
ETS.17.12781 | OCEANO | ETS.17.12781 | South Valley | Pismo | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T2 | HFTD - Non-critical Substation | 4 | 0 | 360 | 178 | 0 |  | 6 | 8 | 4 | 0 | 6 | 10 |  | 34 | 8 | N | 370
ETS.15.12784 | OIL FIELDS | ETS.15.12784 | Central Coast | Moss Landing | DSub in FERC | 12, 34.5,60 | Tier 6 | No | Dist | 60 |  | 6 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 227 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 509
ETS.07.10107 | OLD KEARNEY | ETS.07.10107 | South Valley | Fresno | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 258 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | n/a
ETS.10.12785 | OLD RIVER | ETS.10.12785 | South Valley | Bakersfield | DSub in FERC | 12,70,115 | Tier 6 | No | Dist | 70 |  | 5 | 2 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 196 | 178 | 0 |  | 2 | 4 | 2 | 0 | 4 | 10 |  | 22 | 20 | N | 659
ETS.13.12786 | OLEMA | ETS.13.12786 | North Coast | McMaude | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T2/3A | HFTD - Non-critical Substation | n/a | 1 | 258 | 178 | 0 |  | 2 | 6 | n/a | 1 | 6 | 10 |  | 25 | 17 | N | 270
ETS.18.12787 | OLETA | ETS.18.12787 | North Valley | Stockton | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T2 | HFTD - Non-critical Substation | 3 | 3 | 258 | 178 | 0 |  | 2 | 8 | 3 | 3 | 6 | 10 |  | 32 | 10 | N | 268
ETS.22.12788 | OLEUM PP | ETS.22.12788 | Central Coast | Concord | SW STA - Trans | 115 | Tier 6 | Yes | T | 115 |  | 8 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 19 | 1 | 0 |  | 8 | 4 | n/a | 0 | 2 | 5 |  | 19 | 23 | N | n/a
ETS.08.16735 | OLIVE SW STA | ETS.08.16735 | South Valley | Gates | SW STA - Trans | 115 | Tier 6 | Yes | T | 115 |  | 3 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 5 | 1 | 0 |  | 8 | 4 | n/a | 0 | 2 | 5 |  | 19 | 23 | N | n/a
ETS.04.12789 | OLIVEHURST | ETS.04.12789 | North Valley | Del Mar | DSub in FERC | 12,115 | Tier 6 | No | Dist | 115 |  | n/a | 3 |  | T1 | non-HFTD - Non-critical Substation | 5 | 0 | 225 | 178 | 0 |  | 3 | 4 | 5 | 0 | 6 | 10 |  | 28 | 14 | N | 490
ETS.15.13589 | OPAL CLIFFS | ETS.15.13589 | Central Coast | Moss Landing | Unit Sub | 4,21 | Tier 6 | No | Dist | 21 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 240 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 713
ETS.02.12791 | OREGON TRAIL | ETS.02.12791 | North Coast | Cottonwood | DSub in FERC | 12,60,115 | Tier 6 | Yes | Dist | 60 |  | 3 | 6 |  | T2 | HFTD - Non-critical Substation | 5 | 3 | 225 | 178 | 0 |  | 6 | 8 | 5 | 3 | 6 | 10 |  | 38 | 4 | N | 292
ETS.06.12792 | ORICK | ETS.06.12792 | North Coast | Eureka | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 2 | 202 | 178 | 0 |  | 2 | 4 | n/a | 2 | 6 | 10 |  | 24 | 18 | N | 169
ETS.22.13590 | ORINDA | ETS.22.13590 | Central Coast | Concord | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T3 | HFTD - Non-critical Substation | n/a | 2 | 207 | 178 | 0 |  | 1 | 10 | n/a | 2 | 6 | 10 |  | 29 | 13 | N | 262
ETS.02.12794 | ORLAND B | ETS.02.12794 | North Coast | Cottonwood | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 500 | 178 | 0 |  | 2 | 4 | 3 | 0 | 6 | 10 |  | 25 | 17 | N | 584
ETS.19.12796 | ORO FINO | ETS.19.12796 | North Coast | Table Mountain | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T3 | HFTD - Non-critical Substation | 4 | 6 | 258 | 178 | 0 |  | 2 | 10 | 4 | 6 | 6 | 10 |  | 38 | 4 | N | 22
ETS.14.12797 | ORO LOMA | ETS.14.12797 | North Valley | Merced | T&D | 12,70,115 | Tier 6 | Yes | T | 115 |  | 8 | 8 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 500 | 178 | 0 |  | 8 | 4 | 3 | 0 | 6 | 10 |  | 31 | 11 | N | 526
ETS.07.12798 | OROSI | ETS.07.12798 | South Valley | Fresno | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | 4 | 0 | 238 | 178 | 0 |  | 2 | 4 | 4 | 0 | 6 | 10 |  | 26 | 16 | N | 438
ETS.19.12799 | OROVILLE | ETS.19.12799 | North Coast | Table Mountain | DSub in FERC | 4,12,60 | Tier 6 | No | Dist | 60 |  | 6 | 2 |  | T1 | non-HFTD - Non-critical Substation | 7 | 3 | 258 | 178 | 0 |  | 2 | 4 | 7 | 3 | 6 | 10 |  | 32 | 10 | Y | 264
ETS.14.12800 | ORTIGA | ETS.14.12800 | North Valley | Merced | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 48 | 1 | 0 |  | 2 | 4 | 3 | 0 | 2 | 5 |  | 16 | 26 | N | 597
ETS.15.13592 | OTTER | ETS.15.13592 | Central Coast | Moss Landing | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T3 | HFTD - Non-critical Substation | n/a | 0 | 227 | 178 | 0 |  | 2 | 10 | n/a | 0 | 6 | 10 |  | 28 | 14 | N | 403
ETS.15.13369 | PACIFIC GROVE | ETS.15.13369 | Central Coast | Moss Landing | Unit Sub | 4,21 | Tier 6 | No | Dist | 21 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 258 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 677
ETS.12.12805 | PACIFICA | ETS.12.12805 | Bay Area | Martin | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | 6 | 1 | 227 | 178 | 0 |  | 2 | 4 | 6 | 1 | 6 | 10 |  | 29 | 13 | N | 65
ETS.14.16835 | PADRE FLATS | ETS.14.16835 | North Valley | Merced | SW STA - Trans | 230 | Tier 6 | No | T | 230 |  | n/a | 5 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 5 | 4 | n/a | 0 | 1 | 1 |  | 11 | 31 | N | n/a
ETS.19.10135 | PALERMO | ETS.19.10135 | North Coast | Table Mountain | T-Sub | 230,60,115 | Tier 5 | Yes | T | 230 |  | 15 | 9 |  | T2/3A | HFTD - Critical Substation | n/a | 0 | 317 | 178 | 0 |  | 9 | 6 | n/a | 0 | 6 | 10 |  | 31 | 11 | N | n/a
ETS.17.12806 | PALMER | ETS.17.12806 | South Valley | Pismo | DSub in FERC | 12,115 | Tier 6 | No | Dist | 115 |  | 3 | 3 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 200 | 178 | 0 |  | 3 | 4 | n/a | 0 | 4 | 10 |  | 21 | 21 | N | 419
ETS.03.12807 | PALO ALTO SW STA | ETS.03.12807 | Central Coast | Cupertino | SW STA - Trans | 115 | Tier 6 | Yes | T | 115 |  | 6 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 13 | 1 | 0 |  | 8 | 4 | n/a | 0 | 2 | 5 |  | 19 | 23 | N | n/a
ETS.23.13594 | PALO SECO | ETS.23.13594 | Bay Area | Oakport | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T2 | HFTD - Non-critical Substation | n/a | 1 | 225 | 178 | 0 |  | 1 | 8 | n/a | 1 | 6 | 10 |  | 26 | 16 | N | 506
ETS.10.12809 | PANAMA | ETS.10.12809 | South Valley | Bakersfield | DSub in FERC | 21,70 | Tier 6 | No | Dist | 70 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 317 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 561
ETS.14.10136 | PANOCHE | ETS.14.10136 | North Valley | Merced | T&D | 12,230,115 | Tier 4 | Yes | T | 230 |  | 20 | 9 |  | T1 | non-HFTD - Critical Substation | 2 | 0 | 317 | 178 | 0 |  | 9 | 4 | 2 | 0 | 6 | 10 |  | 31 | 11 | N | 458
ETS.02.12811 | PANORAMA | ETS.02.12811 | North Coast | Cottonwood | DSub in FERC | 12,115 | Tier 6 | No | Dist | 115 |  | 2 | 3 |  | T2/3A | HFTD - Non-critical Substation | n/a | 3 | 240 | 178 | 0 |  | 3 | 6 | n/a | 3 | 6 | 10 |  | 28 | 14 | N | 211
ETS.19.12812 | PARADISE | ETS.19.12812 | North Coast | Table Mountain | DSub in FERC | 12,60,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T2/3A | HFTD - Non-critical Substation | 3 | 6 | 238 | 178 | 0 |  | 6 | 6 | 3 | 6 | 6 | 10 |  | 37 | 5 | N | 56
ETS.13.15398 | PARKWAY | ETS.13.15398 | North Coast | McMaude | DSub in FERC | 12,230 | Tier 6 | Yes | Dist | 230 |  | 3 | 7 |  | T1 | non-HFTD - Non-critical Substation | n/a | 1 | 225 | 178 | 0 |  | 7 | 4 | n/a | 1 | 6 | 10 |  | 28 | 14 | N | 423
ETS.07.12815 | PARLIER | ETS.07.12815 | South Valley | Fresno | DSub in FERC | 12,115 | Tier 6 | No | Dist | 70 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 48 | 1 | 0 |  | 2 | 4 | n/a | 0 | 2 | 5 |  | 13 | 29 | N | 457
ETS.09.13595 | PARSONS | ETS.09.13595 | Central Coast | Hayward | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 240 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 704
ETS.17.12816 | PASO ROBLES | ETS.17.12816 | South Valley | Pismo | DSub in FERC | 12,21,70 | Tier 6 | No | Dist | 70 |  | 10 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 167
ETS.15.12819 | PAUL SWEET | ETS.15.12819 | Central Coast | Moss Landing | DSub in FERC | 21,115 | Tier 6 | Yes | Dist | 115 |  | 6 | 6 |  | T2/3A | HFTD - Non-critical Substation | n/a | 2 | 418 | 178 | 0 |  | 6 | 6 | n/a | 2 | 6 | 10 |  | 30 | 12 | N | 185
ETS.21.10137 | PEABODY | ETS.21.10137 | North Valley | Vaca-Dixon | DSub in FERC | 21,230 | Tier 6 | No | Dist | 230 |  | 5 | 3 |  | T1 | non-HFTD - Non-critical Substation | 4 | 2 | 317 | 178 | 0 |  | 3 | 4 | 4 | 2 | 6 | 10 |  | 29 | 13 | N | 190
ETS.19.12822 | PEACHTON | ETS.19.12822 | North Coast | Table Mountain | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 284 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 700
ETS.19.12824 | PEASE | ETS.19.12824 | North Coast | Table Mountain | T&D | 12,115,60 | Tier 6 | Yes | T | 115 |  | 11 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 258 | 178 | 0 |  | 8 | 4 | n/a | 0 | 6 | 10 |  | 28 | 14 | N | 269
ETS.13.12826 | PENNGROVE | ETS.13.12826 | North Coast | McMaude | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 2 | 6 |  | T1 | non-HFTD - Non-critical Substation | 3 | 2 | 258 | 178 | 0 |  | 6 | 4 | 3 | 2 | 6 | 10 |  | 31 | 11 | N | 34
ETS.04.13596 | PENRYN | ETS.04.13596 | North Valley | Del Mar | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T2/3A | HFTD - Non-critical Substation | n/a | 2 | 227 | 178 | 0 |  | 2 | 6 | n/a | 2 | 6 | 10 |  | 26 | 16 | N | 246
ETS.14.12827 | PEORIA | ETS.14.12827 | North Valley | Merced | DSub in FERC | 17,18,115 | Tier 6 | No | Dist | 115 |  | 4 | 3 |  | T2 | HFTD - Non-critical Substation | 4 | 2 | 362 | 178 | 0 |  | 3 | 8 | 4 | 2 | 6 | 10 |  | 33 | 9 | N | 68
ETS.17.13597 | PERRY | ETS.17.13597 | South Valley | Pismo | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 3 | 2 |  | T2 | HFTD - Non-critical Substation | 3 | 0 | 227 | 178 | 0 |  | 2 | 8 | 3 | 0 | 6 | 10 |  | 29 | 13 | N | 380
ETS.13.12829 | PETALUMA A | ETS.13.12829 | North Coast | McMaude | DSub in FERC | 4,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 1 | 240 | 178 | 0 |  | 2 | 4 | n/a | 1 | 6 | 10 |  | 23 | 19 | N | 720
ETS.13.12830 | PETALUMA C | ETS.13.12830 | North Coast | McMaude | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 5 | 2 |  | T1 | non-HFTD - Non-critical Substation | 5 | 2 | 317 | 178 | 0 |  | 2 | 4 | 5 | 2 | 6 | 10 |  | 29 | 13 | N | 83
ETS.10.12831 | PETROL | ETS.10.12831 | South Valley | Bakersfield | SW STA - Trans | 115 | Tier 6 | Yes | T | 115 |  | 2 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 8 | 4 | n/a | 0 | 1 | 1 |  | 14 | 28 | N | 762
ETS.20.13808 | PHILO | ETS.20.13808 | North Coast | Ukiah | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T2/3A | HFTD - Non-critical Substation | n/a | 1 | 500 | 178 | 0 |  | 2 | 6 | n/a | 1 | 6 | 10 |  | 25 | 17 | N | 66
ETS.20.12833 | PHILO JCT SW STA | ETS.20.12833 | North Coast | Ukiah |  |  | Tier 6 | No | T | 60 |  | 3 | 5 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 5 | 8 | n/a | 0 | 1 | 1 |  | 15 | 27 | N | n/a
ETS.03.16160 | PIERCY | ETS.03.16160 | Central Coast | Cupertino | DSub in FERC | 21,115 | Tier 6 | Yes | Dist | 115 |  | 3 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 2 | 225 | 178 | 0 |  | 6 | 4 | n/a | 2 | 6 | 10 |  | 28 | 14 | N | 222
ETS.19.12835 | PIKE CITY | ETS.19.12835 | North Coast | Table Mountain | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T3 | HFTD - Non-critical Substation | 5 | 3 | 196 | 178 | 0 |  | 2 | 10 | 5 | 3 | 4 | 10 |  | 34 | 8 | N | 147
ETS.18.12837 | PINE GROVE | ETS.18.12837 | North Valley | Stockton | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T2 | HFTD - Non-critical Substation | 3 | 3 | 258 | 178 | 0 |  | 2 | 8 | 3 | 3 | 6 | 10 |  | 32 | 10 | N | 3
ETS.14.13750 | PINECREST | ETS.14.13750 | North Valley | Merced | Unit Sub | 4,17 | Tier 6 | No | Dist | 17 |  | n/a | 1 |  | T3 | HFTD - Non-critical Substation | n/a | 2 | 200 | 178 | 0 |  | 1 | 10 | n/a | 2 | 4 | 10 |  | 27 | 15 | N | 308
ETS.07.16161 | PINEDALE | ETS.07.16161 | South Valley | Fresno | DSub in FERC | 21,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 6 | 4 | n/a | 0 | 6 | 10 |  | 26 | 16 | N | 611
ETS.02.10143 | PIT #1 PH | ETS.02.10143 | North Coast | Cottonwood | 0 | 12,60,230,11 | Tier 6 | Yes | G | 230 |  | 5 | 8 |  | T2 | HFTD - Non-critical Substation | 6 | 0 | 500 | 178 | 0 |  | 8 | 8 | 6 | 0 | 6 | 10 |  | 38 | 4 | N | 630
ETS.02.10145 | PIT #3 PH | ETS.02.10145 | North Coast | Cottonwood | 0 | 12,21 | Tier 6 | Yes | G | 230 |  | 3 | 8 |  | T2 | HFTD - Non-critical Substation | 3 | 0 | 19 | 1 | 0 |  | 8 | 8 | 3 | 0 | 2 | 5 |  | 26 | 16 | N | 328
ETS.02.16550 | PIT #4 PH | ETS.02.16550 | North Coast | Cottonwood | 0 | 230 | Tier 6 | No | G | 230 |  | 2 | 4 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 4 | 8 | n/a | 0 | 1 | 1 |  | 14 | 28 | N | n/a
ETS.02.10147 | PIT #5 PH | ETS.02.10147 | North Coast | Cottonwood | 0 | 11.4,12.47 | Tier 6 | No | G | 230 |  | 5 | 4 |  | T2 | HFTD - Non-critical Substation | 3 | 2 | 196 | 178 | 0 |  | 4 | 8 | 3 | 2 | 4 | 10 |  | 31 | 11 | N | 139
ETS.02.16555 | PIT #6 PH | ETS.02.16555 | North Coast | Cottonwood | 0 | 230 | Tier 6 | No | G | 230 | 8 | 3 | 4 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 4 | 8 | n/a | 0 | 1 | 1 |  | 14 | 28 | N | n/a
ETS.02.16560 | PIT #7 PH | ETS.02.16560 | North Coast | Cottonwood | 0 | 230 | Tier 6 | No | G | 230 |  | 3 | 4 |  | T2 | HFTD - Non-critical Substation | n/a | 2 | n/a | n/a | 0 |  | 4 | 8 | n/a | 2 | 1 | 1 |  | 16 | 26 | N | 510
ETS.22.10139 | PITTSBURG | ETS.22.10139 | Central Coast | Concord | DSub in FERC | 4,60 | Tier 2 | Yes | T | 230 |  | 41 | 10 |  | T1 | non-HFTD - Critical Substation | 2 | 0 | 202 | 178 | 0 |  | 10 | 4 | 2 | 0 | 6 | 10 |  | 32 | 10 | N | 732
ETS.22.10142 | PITTSBURG PP | ETS.22.10142 | Central Coast | Concord | T-Sub | 230,115 | Tier 6 | Yes | T | 230 | 9 | 35 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 317 | 178 | 0 |  | 8 | 4 | n/a | 0 | 6 | 10 |  | 28 | 14 | N | n/a
ETS.04.12843 | PLACER | ETS.04.12843 | North Valley | Del Mar | T&D | 12,115,60 | Tier 6 | Yes | T | 115 |  | 9 | 8 |  | T2/3A | HFTD - Non-critical Substation | 5 | 2 | 362 | 178 | 0 |  | 8 | 6 | 5 | 2 | 6 | 10 |  | 37 | 5 | N | 258
ETS.04.12844 | PLACERVILLE | ETS.04.12844 | North Valley | Del Mar | DSub in FERC | 12,21,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T3 | HFTD - Non-critical Substation | 5 | 3 | 258 | 178 | 0 |  | 6 | 10 | 5 | 3 | 6 | 10 |  | 40 | 2 | Y | 9
ETS.21.12845 | PLAINFIELD | ETS.21.12845 | North Valley | Vaca-Dixon | DSub in FERC | 12,60,115 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | 4 | 0 | 227 | 178 | 0 |  | 2 | 4 | 4 | 0 | 6 | 10 |  | 26 | 16 | N | 553
ETS.04.13598 | PLEASANT GROVE | ETS.04.13598 | North Valley | Del Mar | DSub in FERC | 21,60 | Tier 6 | Yes | Dist | 115 |  | 6 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 6 | 4 | n/a | 0 | 6 | 10 |  | 26 | 16 | N | 445
ETS.04.12847 | PLUMAS | ETS.04.12847 | North Valley | Del Mar | DSub in FERC | 12,21,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 359
ETS.12.12848 | PLYMOUTH | ETS.12.12848 | Bay Area | Martin | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 362 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 554
ETS.19.15658 | POE PH | ETS.19.15658 | North Coast | Table Mountain | 0 | 230 | Tier 6 | Yes | G | 230 |  | 4 | 8 |  | T3 | HFTD - Non-critical Substation | n/a | 0 | 10 | 1 | 0 |  | 8 | 10 | n/a | 0 | 2 | 5 |  | 25 | 17 | N | n/a
ETS.20.12851 | POINT ARENA | ETS.20.12851 | North Coast | Ukiah | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T2 | HFTD - Non-critical Substation | n/a | 1 | 202 | 178 | 0 |  | 2 | 8 | n/a | 1 | 6 | 10 |  | 27 | 15 | N | 171
ETS.15.12852 | POINT MORETTI | ETS.15.12852 | Central Coast | Moss Landing | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T2 | HFTD - Non-critical Substation | 2 | 2 | 227 | 178 | 0 |  | 2 | 8 | 2 | 2 | 6 | 10 |  | 30 | 12 | N | 365
ETS.23.12853 | POINT PINOLE | ETS.23.12853 | Bay Area | Oakport | DSub in FERC | 12,115 | Tier 6 | No | Dist | 115 |  | 3 | 3 |  | T1 | non-HFTD - Non-critical Substation | 6 | 0 | 225 | 178 | 0 |  | 3 | 4 | 6 | 0 | 6 | 10 |  | 29 | 13 | N | 256
ETS.12.12856 | PORTOLA | ETS.12.12856 | Bay Area | Martin | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 227 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 532
ETS.10.12858 | POSO MTN | ETS.10.12858 | South Valley | Bakersfield | DSub in FERC | 21115 | Tier 6 | Yes | Dist | 115 |  | 2 | 6 |  | T2 | HFTD - Non-critical Substation | n/a | 2 | 205 | 178 | 0 |  | 6 | 8 | n/a | 2 | 6 | 10 |  | 32 | 10 | N | 206
ETS.20.12860 | POTTER VALLEY PH | ETS.20.12860 | North Coast | Ukiah | DSub not in FERC | 2.4,12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T2 | HFTD - Non-critical Substation | 2 | 3 | 202 | 178 | 0 |  | 2 | 8 | 2 | 3 | 6 | 10 |  | 31 | 11 | N | 99
ETS.15.12865 | PRUNEDALE | ETS.15.12865 | Central Coast | Moss Landing | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T1 | non-HFTD - Non-critical Substation | 3 | 1 | 256 | 178 | 0 |  | 6 | 4 | 3 | 1 | 6 | 10 |  | 30 | 12 | N | 69
ETS.13.12869 | PUEBLO | ETS.13.12869 | North Coast | McMaude | DSub in FERC | 12,21,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 4 | 4 | 1184 | 178 | 0 |  | 6 | 4 | 4 | 4 | 10 | 10 |  | 38 | 4 | N | 1
ETS.17.12871 | PURISIMA | ETS.17.12871 | South Valley | Pismo | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 2 | 6 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 6 | 8 | n/a | 0 | 6 | 10 |  | 30 | 12 | N | 313
ETS.21.12872 | PUTAH CREEK | ETS.21.12872 | North Valley | Vaca-Dixon | DSub in FERC | 12,115 | Tier 6 | No | Dist | 115 |  | 4 | 3 |  | T1 | non-HFTD - Non-critical Substation | n/a | 4 | 258 | 178 | 0 |  | 3 | 4 | n/a | 4 | 6 | 10 |  | 27 | 15 | N | 250
ETS.14.16785 | QUINTO SW STA | ETS.14.16785 | North Valley | Merced | SW STA - Trans | 230 | Tier 6 | No | T | 230 |  | 3 | 5 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 6 | 1 | 0 |  | 5 | 4 | n/a | 0 | 2 | 5 |  | 16 | 26 | N | n/a
ETS.14.12875 | RACETRACK | ETS.14.12875 | North Valley | Merced | DSub in FERC | 17115 | Tier 6 | No | Dist | 115 |  | 3 | 3 |  | T2 | HFTD - Non-critical Substation | n/a | 2 | 240 | 178 | 0 |  | 3 | 8 | n/a | 2 | 6 | 10 |  | 29 | 13 | N | 109
ETS.09.12876 | RADUM | ETS.09.12876 | Central Coast | Hayward | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 5 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 1 | 500 | 178 | 0 |  | 2 | 4 | n/a | 1 | 6 | 10 |  | 23 | 19 | N | 220
ETS.07.12877 | RAINBOW | ETS.07.12877 | South Valley | Fresno | DSub in FERC | 12,115 | Tier 6 | No | Dist | 115 |  | 3 | 3 |  | T1 | non-HFTD - Non-critical Substation | 4 | 0 | 240 | 178 | 0 |  | 3 | 4 | 4 | 0 | 6 | 10 |  | 27 | 15 | N | 425
ETS.16.13747 | RALSTON | ETS.16.13747 | Central Coast | San Carlos | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 1 | 240 | 178 | 0 |  | 2 | 4 | n/a | 1 | 6 | 10 |  | 23 | 19 | N | 236
ETS.07.12878 | RANCHERS COTTON | ETS.07.12878 | South Valley | Fresno | DSub in FERC | 12,115 | Tier 6 | No | Dist | 115 |  | 3 | 3 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 225 | 178 | 0 |  | 3 | 4 | 2 | 0 | 6 | 10 |  | 25 | 17 | N | 625
ETS.12.12879 | RANDOLPH | ETS.12.12879 | Bay Area | Martin | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 362 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 539
ETS.16.10151 | RAVENSWOOD | ETS.16.10151 | Central Coast | San Carlos | T-Sub | 230,115 | Tier 4 | Yes | T | 230 |  | 18 | 9 |  | T1 | non-HFTD - Critical Substation | 2 | 0 | 317 | 178 | 0 |  | 9 | 4 | 2 | 0 | 6 | 10 |  | 31 | 11 | N | n/a
ETS.02.12881 | RAWSON | ETS.02.12881 | North Coast | Cottonwood | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 2 | 258 | 178 | 0 |  | 2 | 4 | n/a | 2 | 6 | 10 |  | 24 | 18 | Y | 298
ETS.21.12288 | RECLAMATION DIST#108 | ETS.21.12288 | North Valley | Vaca-Dixon | Dist. Single Cust. | 2.4,60 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 240 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | n/a
ETS.21.12289 | RECLAMATION DIST#1500 | ETS.21.12289 | North Valley | Vaca-Dixon | Dist. Single Cust. | 2.4,12,60 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 202 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | n/a
ETS.21.12290 | RECLAMATION DIST#2047 | ETS.21.12290 | North Valley | Vaca-Dixon | Dist. Single Cust. | 2.4,60 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 198 | 178 | 0 |  | 2 | 4 | n/a | 0 | 4 | 10 |  | 20 | 22 | N | n/a
ETS.21.16380 | RECLAMATION DIST#999 | ETS.21.16380 | North Valley | Vaca-Dixon | Dist. Single Cust. | 2.4,21 | Tier 6 | No | Dist | 21 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 202 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | n/a
ETS.02.12885 | RED BLUFF | ETS.02.12885 | North Coast | Cottonwood | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 5 | 2 |  | T1 | non-HFTD - Non-critical Substation | 4 | 3 | 258 | 178 | 0 |  | 2 | 4 | 4 | 3 | 6 | 10 |  | 29 | 13 | N | 221
ETS.20.12886 | REDBUD | ETS.20.12886 | North Coast | Ukiah | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T2 | HFTD - Non-critical Substation | 3 | 2 | 258 | 178 | 0 |  | 6 | 8 | 3 | 2 | 6 | 10 |  | 35 | 7 | Y | 80
ETS.16.12889 | REDWOOD CITY | ETS.16.12889 | Central Coast | San Carlos | DSub in FERC | 4,12,60 | Tier 6 | No | Dist | 60 |  | 7 | 2 |  | T1 | non-HFTD - Non-critical Substation | 6 | 0 | 500 | 178 | 0 |  | 2 | 4 | 6 | 0 | 6 | 10 |  | 28 | 14 | N | 417
ETS.07.12891 | REEDLEY | ETS.07.12891 | South Valley | Fresno | T&D | 12,70,115 | Tier 6 | Yes | T | 115 |  | 11 | 8 |  | T1 | non-HFTD - Non-critical Substation | 6 | 0 | 258 | 178 | 0 |  | 8 | 4 | 6 | 0 | 6 | 10 |  | 34 | 8 | N | 205
ETS.10.15598 | RENFRO | ETS.10.15598 | South Valley | Bakersfield | DSub in FERC | 21,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 238 | 178 | 0 |  | 6 | 4 | n/a | 0 | 6 | 10 |  | 26 | 16 | N | 518
ETS.15.12893 | RESERVATION ROAD | ETS.15.12893 | Central Coast | Moss Landing | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | 500 | 178 | 0 |  | 2 | 8 | n/a | 0 | 6 | 10 |  | 26 | 16 | N | 302
ETS.08.12894 | RESERVE OIL | ETS.08.12894 | South Valley | Gates | DSub in FERC | 4,12,70 | Tier 6 | No | Dist | 70 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | 1 | 0 | 284 | 178 | 0 |  | 2 | 4 | 1 | 0 | 6 | 10 |  | 23 | 19 | N | 622
ETS.21.12896 | RICE | ETS.21.12896 | North Valley | Vaca-Dixon | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | 1 | 0 | 500 | 178 | 0 |  | 2 | 4 | 1 | 0 | 6 | 10 |  | 23 | 19 | N | 592
ETS.23.12897 | RICHMOND R | ETS.23.12897 | Bay Area | Oakport | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T1 | non-HFTD - Non-critical Substation | 8 | 0 | 140 | 1 | 0 |  | 6 | 4 | 8 | 0 | 4 | 5 |  | 27 | 15 | N | 567
ETS.23.13810 | RIDGE | ETS.23.13810 | Bay Area | Oakport | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T2 | HFTD - Non-critical Substation | n/a | 2 | 202 | 178 | 0 |  | 1 | 8 | n/a | 2 | 6 | 10 |  | 27 | 15 | N | 507
ETS.06.16300 | RIDGE CABIN | ETS.06.16300 | North Coast | Eureka | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | 202 | 178 | 0 |  | 2 | 8 | n/a | 0 | 6 | 10 |  | 26 | 16 | N | n/a
ETS.13.12901 | RINCON | ETS.13.12901 | North Coast | McMaude | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T2 | HFTD - Non-critical Substation | n/a | 5 | 256 | 178 | 0 |  | 6 | 8 | n/a | 5 | 6 | 10 |  | 35 | 7 | N | 8
ETS.10.12902 | RIO BRAVO | ETS.10.12902 | South Valley | Bakersfield | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T1 | non-HFTD - Non-critical Substation | 5 | 0 | 362 | 178 | 0 |  | 6 | 4 | 5 | 0 | 6 | 10 |  | 31 | 11 | N | 600
ETS.15.13811 | RIO DEL MAR | ETS.15.13811 | Central Coast | Moss Landing | Unit Sub | 4,21 | Tier 6 | No | Dist | 21 |  | n/a | 1 |  | T2 | HFTD - Non-critical Substation | 2 | 2 | 19 | 1 | 0 |  | 1 | 8 | 2 | 2 | 2 | 5 |  | 20 | 22 | N | 513
ETS.06.12903 | RIO DELL | ETS.06.12903 | North Coast | Eureka | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 2 | 258 | 178 | 0 |  | 2 | 4 | 3 | 2 | 6 | 10 |  | 27 | 15 | N | 113
ETS.06.13748 | RIO DELL JCT | ETS.06.13748 | North Coast | Eureka | SW STA - Trans | 60 | Tier 6 | No | T | 60 |  | 3 | 5 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 4 | 1 | 0 |  | 5 | 4 | 3 | 0 | 2 | 5 |  | 19 | 23 | N | n/a
ETS.04.10153 | RIO OSO | ETS.04.10153 | North Valley | Del Mar | T-Sub | 230,115 | Tier 4 | Yes | T | 230 |  | 21 | 9 |  | T1 | non-HFTD - Critical Substation | 2 | 0 | 500 | 178 | 0 |  | 9 | 4 | 2 | 0 | 6 | 10 |  | 31 | 11 | N | n/a
ETS.18.12904 | RIPON | ETS.18.12904 | North Valley | Stockton | DSub in FERC | 17,18,115 | Tier 6 | No | Dist | 115 |  | 3 | 3 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 238 | 178 | 0 |  | 3 | 4 | 3 | 0 | 6 | 10 |  | 26 | 16 | N | 559
ETS.02.12906 | RISING RIVER | ETS.02.12906 | North Coast | Cottonwood | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | 200 | 178 | 0 |  | 2 | 8 | n/a | 0 | 4 | 10 |  | 24 | 18 | N | 577
ETS.03.15458 | RIVER OAKS | ETS.03.15458 | Central Coast | Cupertino | DSub in FERC | 21,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 196 | 178 | 0 |  | 6 | 4 | 2 | 0 | 4 | 10 |  | 26 | 16 | N | 447
ETS.07.12907 | RIVER ROCK | ETS.07.12907 | South Valley | Fresno | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | 1 | 0 | 190 | 178 | 0 |  | 2 | 4 | 1 | 0 | 4 | 10 |  | 21 | 21 | N | 750
ETS.18.12908 | RIVERBANK | ETS.18.12908 | North Valley | Stockton | DSub in FERC | 18,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 240 | 178 | 0 |  | 6 | 4 | 3 | 0 | 6 | 10 |  | 29 | 13 | N | 378
ETS.18.12910 | RIVERBANK SW STA | ETS.18.12910 | North Valley | Stockton | SW STA - Trans | 115 | Tier 6 | No | T | 115 |  | n/a | 5 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 6 | 1 | 0 |  | 5 | 4 | n/a | 0 | 2 | 5 |  | 16 | 26 | N | n/a
ETS.15.12911 | ROB ROY | ETS.15.12911 | Central Coast | Moss Landing | DSub in FERC | 21,115 | Tier 6 | Yes | Dist | 115 |  | 2 | 6 |  | T2 | HFTD - Non-critical Substation | n/a | 2 | 418 | 178 | 0 |  | 6 | 8 | n/a | 2 | 6 | 10 |  | 32 | 10 | N | 64
ETS.19.10154 | ROCK CREEK PH | ETS.19.10154 | North Coast | Table Mountain | 0 | 230 | Tier 6 | Yes | G | 230 |  | 4 | 8 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | 10 | 1 | 0 |  | 8 | 8 | n/a | 0 | 2 | 5 |  | 23 | 19 | N | n/a
ETS.04.13606 | ROCKLIN | ETS.04.13606 | North Valley | Del Mar | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | 5 | 0 | 258 | 178 | 0 |  | 2 | 4 | 5 | 0 | 6 | 10 |  | 27 | 15 | N | 626
ETS.15.13812 | ROLAND | ETS.15.13812 | Central Coast | Moss Landing | Unit Sub | 4,21 | Tier 6 | No | Dist | 21 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 34 | 1 | 0 |  | 1 | 4 | 3 | 0 | 2 | 5 |  | 15 | 27 | N | 730
ETS.10.12916 | ROSEDALE | ETS.10.12916 | South Valley | Bakersfield | DSub in FERC | 12,21,115 | Tier 6 | Yes | Dist | 115 |  | 2 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 256 | 178 | 0 |  | 6 | 4 | n/a | 0 | 6 | 10 |  | 26 | 16 | N | 656
ETS.22.10155 | ROSSMOOR | ETS.22.10155 | Central Coast | Concord | DSub in FERC | 12,230 | Tier 6 | Yes | Dist | 230 |  | 4 | 7 |  | T2/3A | HFTD - Non-critical Substation | 6 | 2 | 418 | 178 | 0 |  | 7 | 6 | 6 | 2 | 6 | 10 |  | 37 | 5 | N | 29
ETS.18.12918 | ROUGH & READY | ETS.18.12918 | North Valley | Stockton | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 225 | 178 | 0 |  | 2 | 4 | 3 | 0 | 6 | 10 |  | 25 | 17 | N | 305
ETS.02.10152 | ROUND MTN | ETS.02.10152 | North Coast | Cottonwood | T-Sub | 230500 | Tier 3 | Yes | T | 500 | 10 | 12 | 10 |  | T2 | HFTD - Critical Substation | n/a | 0 | 317 | 178 | 0 |  | 10 | 8 | n/a | 0 | 6 | 10 |  | 34 | 8 | N | n/a
ETS.06.12920 | RUSS RANCH | ETS.06.12920 | North Coast | Eureka | Dist. Single Cust. | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T2/3A | HFTD - Non-critical Substation | n/a | 1 | 190 | 178 | 0 |  | 2 | 6 | n/a | 1 | 4 | 10 |  | 23 | 19 | N | 238
ETS.23.10156 | RUSSELL | ETS.23.10156 | Bay Area | Oakport | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 240 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 684
ETS.14.12927 | SALADO | ETS.14.12927 | North Valley | Merced | T-Sub | 115,60 | Tier 6 | Yes | T | 115 |  | 4 | 8 |  | T1 | non-HFTD - Non-critical Substation | 6 | 0 | 61 | 1 | 0 |  | 8 | 4 | 6 | 0 | 3 | 5 |  | 26 | 16 | N | n/a
ETS.15.12929 | SALINAS | ETS.15.12929 | Central Coast | Moss Landing | T&D | 12,115,60 | Tier 6 | Yes | T | 115 |  | 17 | 8 |  | T1 | non-HFTD - Non-critical Substation | 4 | 0 | 317 | 178 | 0 |  | 8 | 4 | 4 | 0 | 6 | 10 |  | 32 | 10 | N | 545
ETS.13.12930 | SALMON CREEK | ETS.13.12930 | North Coast | McMaude | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 1 | 225 | 178 | 0 |  | 2 | 4 | n/a | 1 | 6 | 10 |  | 23 | 19 | N | 204
ETS.18.12932 | SALT SPRINGS PH | ETS.18.12932 | North Valley | Stockton | 0 | 14.4,21 | Tier 6 | No | G | 115 |  | 2 | 4 |  | T2 | HFTD - Non-critical Substation | 3 | 3 | 202 | 178 | 0 |  | 4 | 8 | 3 | 3 | 6 | 10 |  | 34 | 8 | Y | 49
ETS.12.13813 | SAN ANDREAS | ETS.12.13813 | Bay Area | Martin | Dist. Single Cust. | 4,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T2/3A | HFTD - Non-critical Substation | n/a | 0 | 198 | 178 | 0 |  | 2 | 6 | n/a | 0 | 4 | 10 |  | 22 | 20 | N | n/a
ETS.15.12933 | SAN ARDO | ETS.15.12933 | Central Coast | Moss Landing | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 198 | 178 | 0 |  | 2 | 4 | 3 | 0 | 4 | 10 |  | 23 | 19 | N | 456
ETS.15.16705 | SAN BENITO | ETS.15.16705 | Central Coast | Moss Landing | DSub in FERC | 21,115 | Tier 6 | Yes | Dist | 115 |  | 3 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 1 | 48 | 1 | 0 |  | 6 | 4 | n/a | 1 | 2 | 5 |  | 18 | 24 | N | 357
ETS.10.12934 | SAN BERNARD | ETS.10.12934 | South Valley | Bakersfield | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | 4 | 1 | 207 | 178 | 0 |  | 2 | 4 | 4 | 1 | 6 | 10 |  | 27 | 15 | N | 395
ETS.12.12935 | SAN BRUNO | ETS.12.12935 | Bay Area | Martin | DSub in FERC | 4,12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 258 | 178 | 0 |  | 2 | 4 | 3 | 0 | 6 | 10 |  | 25 | 17 | N | 693
ETS.16.12936 | SAN CARLOS | ETS.16.12936 | Central Coast | San Carlos | DSub in FERC | 4,12,60 | Tier 6 | No | Dist | 60 |  | 5 | 2 |  | T1 | non-HFTD - Non-critical Substation | 5 | 1 | 258 | 178 | 0 |  | 2 | 4 | 5 | 1 | 6 | 10 |  | 28 | 14 | N | 311
ETS.12.10141 | SAN FRAN A (POTRERO PP) | ETS.12.10141 | Bay Area | Martin | T&D | 12115230 | Tier 4 | Yes | T | 115 |  | 17 | 9 |  | T1 | non-HFTD - Critical Substation | 8 | 0 | 225 | 178 | 0 |  | 9 | 4 | 8 | 0 | 6 | 10 |  | 37 | 5 | N | 168
ETS.12.12938 | SAN FRAN AIRPORT | ETS.12.12938 | Bay Area | Martin | Dist. Single Cust. | 12,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 196 | 178 | 0 |  | 6 | 4 | n/a | 0 | 4 | 10 |  | 24 | 18 | N | n/a
ETS.12.12939 | SAN FRAN E | ETS.12.12939 | Bay Area | Martin | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 258 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 529
ETS.12.12653 | SAN FRAN F (MARINA) | ETS.12.12653 | Bay Area | Martin | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 500 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 252
ETS.12.12940 | SAN FRAN G | ETS.12.12940 | Bay Area | Martin | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 496
ETS.12.12941 | SAN FRAN H (MARTIN) | ETS.12.12941 | Bay Area | Martin | T&D | 12,115,230,60 | Tier 1 | Yes | T | 115 |  | 28 | 10 |  | T1 | non-HFTD - Critical Substation | 8 | 0 | 500 | 178 | 0 |  | 10 | 4 | 8 | 0 | 6 | 10 |  | 38 | 4 | N | 282
ETS.12.12943 | SAN FRAN J | ETS.12.12943 | Bay Area | Martin | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 330
ETS.12.12944 | SAN FRAN K | ETS.12.12944 | Bay Area | Martin | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | 6 | 0 | 225 | 178 | 0 |  | 1 | 4 | 6 | 0 | 6 | 10 |  | 27 | 15 | N | 433
ETS.12.12945 | SAN FRAN L | ETS.12.12945 | Bay Area | Martin | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 396
ETS.12.12946 | SAN FRAN M | ETS.12.12946 | Bay Area | Martin | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 362 | 178 | 0 |  | 1 | 4 | 3 | 0 | 6 | 10 |  | 24 | 18 | N | 636
ETS.12.12947 | SAN FRAN N | ETS.12.12947 | Bay Area | Martin | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | 4 | 0 | 48 | 1 | 0 |  | 1 | 4 | 4 | 0 | 2 | 5 |  | 16 | 26 | N | 491
ETS.12.12948 | SAN FRAN P(HUNTERS POINT) | ETS.12.12948 | Bay Area | Martin | DSub in FERC | 12115 | Tier 5 | Yes | Dist | 115 |  | 8 | 9 |  | T1 | non-HFTD - Critical Substation | n/a | 0 | 1184 | 178 | 0 |  | 9 | 4 | n/a | 0 | 10 | 10 |  | 33 | 9 | N | 358
ETS.12.12068 | SAN FRAN W (BAYSHORE) | ETS.12.12068 | Bay Area | Martin | Dist. Single Cust. | 34.5,115 | Tier 6 | No | Dist | 115 |  | 4 | 3 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 198 | 178 | 0 |  | 3 | 4 | n/a | 0 | 4 | 10 |  | 21 | 21 | N | 776
ETS.12.12949 | SAN FRAN X (MISSION) | ETS.12.12949 | Bay Area | Martin | DSub in FERC | 4,12,115 | Tier 4 | Yes | Dist | 115 |  | 11 | 9 |  | T1 | non-HFTD - Critical Substation | 6 | 0 | 317 | 178 | 0 |  | 9 | 4 | 6 | 0 | 6 | 10 |  | 35 | 7 | N | 127
ETS.12.12568 | SAN FRAN Y (LARKIN) | ETS.12.12568 | Bay Area | Martin | DSub in FERC | 12115 | Tier 5 | Yes | Dist | 115 |  | 9 | 9 |  | T1 | non-HFTD - Critical Substation | 10 | 0 | 196 | 178 | 0 |  | 9 | 4 | 10 | 0 | 4 | 10 |  | 37 | 5 | N | 366
ETS.12.12951 | SAN FRAN Z (EMBARCADERO) | ETS.12.12951 | Bay Area | Martin | DSub in FERC | 34.5,230 | Tier 4 | Yes | Dist | 230 |  | 7 | 9 |  | T1 | non-HFTD - Critical Substation | 4 | 0 | 360 | 178 | 0 |  | 9 | 4 | 4 | 0 | 6 | 10 |  | 33 | 9 | N | 235
ETS.07.12955 | SAN JOAQUIN | ETS.07.12955 | South Valley | Fresno | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 664
ETS.07.12953 | SAN JOAQUIN #2 PH | ETS.07.12953 | South Valley | Fresno | 0 | n/a | Tier 6 | No | G | 70 |  | 4 | 4 |  | T3 | HFTD - Non-critical Substation | 3 | 1 | 196 | 178 | 0 |  | 4 | 10 | 3 | 1 | 4 | 10 |  | 32 | 10 | N | 369
ETS.07.12954 | SAN JOAQUIN #3 PH | ETS.07.12954 | South Valley | Fresno | 0 | 12,70 | Tier 6 | No | G | 70 |  | 3 | 4 |  | T2 | HFTD - Non-critical Substation | n/a | 1 | 202 | 178 | 0 |  | 4 | 8 | n/a | 1 | 6 | 10 |  | 29 | 13 | N | 125
ETS.03.12956 | SAN JOSE A | ETS.03.12956 | Central Coast | Cupertino | DSub in FERC | 4,12,21,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 5 | 0 | 258 | 178 | 0 |  | 6 | 4 | 5 | 0 | 6 | 10 |  | 31 | 11 | N | 480
ETS.03.12957 | SAN JOSE B | ETS.03.12957 | Central Coast | Cupertino | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 8 | 6 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 225 | 178 | 0 |  | 6 | 4 | 2 | 0 | 6 | 10 |  | 28 | 14 | N | 449
ETS.15.13610 | SAN JUSTO | ETS.15.13610 | Central Coast | Moss Landing | DSub not in FERC | 12,21 | Tier 6 | No | Dist | 21 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 1 | 6 | 1 | 0 |  | 1 | 4 | n/a | 1 | 2 | 5 |  | 13 | 29 | N | 194
ETS.09.12959 | SAN LEANDRO U | ETS.09.12959 | Central Coast | Hayward | DSub in FERC | 12,34,115 | Tier 6 | Yes | Dist | 115 |  | 8 | 6 |  | T1 | non-HFTD - Non-critical Substation | 7 | 2 | 258 | 178 | 0 |  | 6 | 4 | 7 | 2 | 6 | 10 |  | 35 | 7 | N | 267
ETS.09.13611 | SAN LORENZO | ETS.09.13611 | Central Coast | Hayward | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 198 | 178 | 0 |  | 1 | 4 | n/a | 0 | 4 | 10 |  | 19 | 23 | N | 719
ETS.14.12961 | SAN LUIS #3 | ETS.14.12961 | North Valley | Merced | Dist. Single Cust. | 2.4,115 | Tier 6 | No | Dist | 115 |  | 3 | 3 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 207 | 178 | 0 |  | 3 | 4 | n/a | 0 | 6 | 10 |  | 23 | 19 | N | n/a
ETS.14.12962 | SAN LUIS #5 | ETS.14.12962 | North Valley | Merced | Dist. Single Cust. | 2115 | Tier 6 | No | Dist | 115 |  | 3 | 3 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 198 | 178 | 0 |  | 3 | 4 | n/a | 0 | 4 | 10 |  | 21 | 21 | N | n/a
ETS.17.10189 | SAN LUIS OBISPO | ETS.17.10189 | South Valley | Pismo | T&D | 12,115,60,70 | Tier 6 | Yes | T | 115 |  | 11 | 8 |  | T1 | non-HFTD - Non-critical Substation | 4 | 0 | 317 | 178 | 0 |  | 8 | 4 | 4 | 0 | 6 | 10 |  | 32 | 10 | N | 251
ETS.16.10157 | SAN MATEO | ETS.16.10157 | Central Coast | San Carlos | T&D | 4,21,60,115,230 | Tier 1 | Yes | T | 230 |  | 31 | 10 |  | T1 | non-HFTD - Critical Substation | 5 | 0 | 360 | 178 | 0 |  | 10 | 4 | 5 | 0 | 6 | 10 |  | 35 | 7 | N | 420
ETS.17.12964 | SAN MIGUEL | ETS.17.12964 | South Valley | Pismo | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 225 | 178 | 0 |  | 2 | 4 | 3 | 0 | 6 | 10 |  | 25 | 17 | N | 478
ETS.23.12965 | SAN PABLO | ETS.23.12965 | Bay Area | Oakport | DSub in FERC | 12,115,230,60 | Tier 6 | Yes | Dist | 115 |  | 3 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 48 | 1 | 0 |  | 6 | 4 | n/a | 0 | 2 | 5 |  | 17 | 25 | N | 418
ETS.13.12966 | SAN RAFAEL | ETS.13.12966 | North Coast | McMaude | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 1 | 500 | 178 | 0 |  | 6 | 4 | n/a | 1 | 6 | 10 |  | 27 | 15 | Y | 16
ETS.09.10165 | SAN RAMON | ETS.09.10165 | Central Coast | Hayward | T&D | 21,230,60 | Tier 4 | Yes | T | 230 |  | 9 | 9 |  | T1 | non-HFTD - Critical Substation | n/a | 2 | 317 | 178 | 0 |  | 9 | 4 | n/a | 2 | 6 | 10 |  | 31 | 11 | N | 41
ETS.09.15498 | SAN RAMON RESEARCH CTR | ETS.09.15498 | Central Coast | Hayward | 0 | 21,230 | Tier 6 | No | Dist | 230 |  | 2 | 3 |  | T1 | non-HFTD - Non-critical Substation | n/a | 1 | 225 | 178 | 0 |  | 3 | 4 | n/a | 1 | 6 | 10 |  | 24 | 18 | N | 81
ETS.07.12968 | SAND CREEK | ETS.07.12968 | South Valley | Fresno | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 2 | 2 |  | T2 | HFTD - Non-critical Substation | 3 | 0 | 225 | 178 | 0 |  | 2 | 8 | 3 | 0 | 6 | 10 |  | 29 | 13 | N | 367
ETS.07.12970 | SANGER | ETS.07.12970 | South Valley | Fresno | T&D | 12,115 | Tier 5 | Yes | Dist | 115 |  | 14 | 9 |  | T1 | non-HFTD - Critical Substation | 5 | 0 | 258 | 178 | 0 |  | 9 | 4 | 5 | 0 | 6 | 10 |  | 34 | 8 | N | 343
ETS.17.12975 | SANTA MARIA | ETS.17.12975 | South Valley | Pismo | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 4 | 0 | 225 | 178 | 0 |  | 6 | 4 | 4 | 0 | 6 | 10 |  | 30 | 12 | N | 275
ETS.14.12976 | SANTA NELLA | ETS.14.12976 | North Valley | Merced | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 240 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 422
ETS.14.12977 | SANTA RITA | ETS.14.12977 | North Valley | Merced | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 284 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 556
ETS.13.12978 | SANTA ROSA A | ETS.13.12978 | North Coast | McMaude | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 6 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 4 | 317 | 178 | 0 |  | 6 | 4 | n/a | 4 | 6 | 10 |  | 30 | 12 | N | 11
ETS.17.12979 | SANTA YNEZ | ETS.17.12979 | South Valley | Pismo | DSub in FERC | 12,115 | Tier 6 | No | Dist | 115 |  | 3 | 3 |  | T2/3A | HFTD - Non-critical Substation | 4 | 0 | 256 | 178 | 0 |  | 3 | 6 | 4 | 0 | 6 | 10 |  | 29 | 13 | N | 321
ETS.17.12980 | SANTA YNEZ SW STA | ETS.17.12980 | South Valley | Pismo | SW STA - Trans | 115 | Tier 6 | Yes | T | 115 |  | 4 | 8 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | 19 | 1 | 0 |  | 8 | 8 | n/a | 0 | 2 | 5 |  | 23 | 19 | N | n/a
ETS.22.13614 | SARANAP | ETS.22.13614 | Central Coast | Concord | Unit Sub | 4,21 | Tier 6 | No | Dist | 21 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 202 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 709
ETS.03.10158 | SARATOGA | ETS.03.10158 | Central Coast | Cupertino | DSub in FERC | 12,230 | Tier 6 | Yes | Dist | 230 |  | 5 | 7 |  | T1 | non-HFTD - Non-critical Substation | 7 | 2 | 498 | 178 | 0 |  | 7 | 4 | 7 | 2 | 6 | 10 |  | 36 | 6 | N | 62
ETS.13.12984 | SAUSALITO | ETS.13.12984 | North Coast | McMaude | DSub in FERC | 4,12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 2 | 362 | 178 | 0 |  | 2 | 4 | 3 | 2 | 6 | 10 |  | 27 | 15 | N | 208
ETS.08.12985 | SCHINDLER | ETS.08.12985 | South Valley | Gates | T&D | 12,115,70 | Tier 6 | Yes | T | 115 |  | 9 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 8 | 4 | n/a | 0 | 6 | 10 |  | 28 | 14 | N | 718
ETS.26.16450 | SCHULTE SW STA | ETS.26.16450 | North Valley | Tesla | SW STA - Trans | 115 | Tier 6 | Yes | T | 115 |  | 5 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 5 | 1 | 0 |  | 8 | 4 | n/a | 0 | 2 | 5 |  | 19 | 23 | N | n/a
ETS.15.13907 | SEACLIFF | ETS.15.13907 | Central Coast | Moss Landing | Unit Sub | 4,21 | Tier 6 | No | Dist | 21 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 1 | 198 | 178 | 0 |  | 1 | 4 | n/a | 1 | 4 | 10 |  | 20 | 22 | N | 360
ETS.10.12988 | SEMITROPIC | ETS.10.12988 | South Valley | Bakersfield | T&D | 12,115,70 | Tier 6 | Yes | T | 115 |  | 8 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 256 | 178 | 0 |  | 8 | 4 | n/a | 0 | 6 | 10 |  | 28 | 14 | N | 589
ETS.12.12992 | SERRAMONTE | ETS.12.12992 | Bay Area | Martin | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 2 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 1 | 258 | 178 | 0 |  | 6 | 4 | n/a | 1 | 6 | 10 |  | 27 | 15 | N | 599
ETS.04.13618 | SHADY GLEN | ETS.04.13618 | North Valley | Del Mar | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T2 | HFTD - Non-critical Substation | 4 | 3 | 362 | 178 | 0 |  | 2 | 8 | 4 | 3 | 6 | 10 |  | 33 | 9 | N | 137
ETS.10.12994 | SHAFTER | ETS.10.12994 | South Valley | Bakersfield | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 500 | 178 | 0 |  | 6 | 4 | n/a | 0 | 6 | 10 |  | 26 | 16 | N | 671
ETS.14.13751 | SHARON | ETS.14.13751 | North Valley | Merced | DSub in FERC | 12,115 | Tier 6 | No | Dist | 115 |  | 2 | 3 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 196 | 178 | 0 |  | 3 | 4 | n/a | 0 | 4 | 10 |  | 21 | 21 | N | 768
ETS.07.16640 | SHEPHERD | ETS.07.16640 | South Valley | Fresno | DSub in FERC | 21,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 48 | 1 | 0 |  | 6 | 4 | n/a | 0 | 2 | 5 |  | 17 | 25 | N | 364
ETS.04.12999 | SHINGLE SPRINGS | ETS.04.12999 | North Valley | Del Mar | DSub in FERC | 12,21,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T3 | HFTD - Non-critical Substation | n/a | 3 | 256 | 178 | 0 |  | 6 | 10 | n/a | 3 | 6 | 10 |  | 35 | 7 | N | 79
ETS.16.13001 | SHREDDER | ETS.16.13001 | Central Coast | San Carlos | Dist. Single Cust. | 4,115 | Tier 6 | No | Dist | 115 |  | 3 | 3 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 207 | 178 | 0 |  | 3 | 4 | n/a | 0 | 6 | 10 |  | 23 | 19 | N | n/a
ETS.12.13004 | SILVER AVE | ETS.12.13004 | Bay Area | Martin | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 227 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 686
ETS.13.13005 | SILVERADO | ETS.13.13005 | North Coast | McMaude | DSub in FERC | 21,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T1 | non-HFTD - Non-critical Substation | 3 | 4 | 227 | 178 | 0 |  | 6 | 4 | 3 | 4 | 6 | 10 |  | 33 | 9 | N | 6
ETS.17.13008 | SISQUOC | ETS.17.13008 | South Valley | Pismo | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 6 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 200 | 178 | 0 |  | 6 | 4 | n/a | 0 | 4 | 10 |  | 24 | 18 | N | 291
ETS.12.13009 | SIXTH AVE | ETS.12.13009 | Bay Area | Martin | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 362 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 278
ETS.13.13010 | SKAGGS ISLAND | ETS.13.13010 | North Coast | McMaude | Dist. Single Cust. | 12,115 | Tier 6 | No | Dist | 115 |  | n/a | 3 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | n/a | n/a | 0 |  | 3 | 4 | 2 | 0 | 1 | 1 |  | 11 | 31 | N | 754
ETS.19.13016 | SMARTVILLE | ETS.19.13016 | North Coast | Table Mountain | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T2 | HFTD - Non-critical Substation | n/a | 4 | 207 | 178 | 0 |  | 2 | 8 | n/a | 4 | 6 | 10 |  | 30 | 12 | N | 431
ETS.10.13020 | SMYRNA | ETS.10.13020 | South Valley | Bakersfield | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 240 | 178 | 0 |  | 6 | 4 | 3 | 0 | 6 | 10 |  | 29 | 13 | N | 680
ETS.12.13021 | SNEATH LANE | ETS.12.13021 | Bay Area | Martin | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 6 | 2 |  | T2 | HFTD - Non-critical Substation | n/a | 1 | 258 | 178 | 0 |  | 2 | 8 | n/a | 1 | 6 | 10 |  | 27 | 15 | N | 195
ETS.22.10162 | SOBRANTE | ETS.22.10162 | Central Coast | Concord | T&D | 12,115,230 | Tier 5 | Yes | T | 230 |  | 20 | 9 |  | T2 | HFTD - Critical Substation | 4 | 2 | 240 | 178 | 0 |  | 9 | 8 | 4 | 2 | 6 | 10 |  | 39 | 3 | N | 234
ETS.23.13814 | SOLANO | ETS.23.13814 | Bay Area | Oakport | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 258 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 645
ETS.10.16725 | SOLAR SW STA | ETS.10.16725 | South Valley | Bakersfield | SW STA - Trans | 230 | Tier 6 | Yes | T | 230 |  | 6 | 8 |  | T2/3A | HFTD - Non-critical Substation | n/a | 0 | 6 | 1 | 0 |  | 8 | 6 | n/a | 0 | 2 | 5 |  | 21 | 21 | N | n/a
ETS.15.13023 | SOLEDAD | ETS.15.13023 | Central Coast | Moss Landing | T&D | 12,21,60,115 | Tier 6 | No | T | 115 |  | 13 | 5 |  | T1 | non-HFTD - Non-critical Substation | 4 | 1 | 258 | 178 | 0 |  | 5 | 4 | 4 | 1 | 6 | 10 |  | 30 | 12 | Y | 146
ETS.13.13024 | SONOMA A | ETS.13.13024 | North Coast | McMaude | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 5 | 3 | 227 | 178 | 0 |  | 6 | 4 | 5 | 3 | 6 | 10 |  | 34 | 8 | N | 187
ETS.15.13915 | SOQUEL | ETS.15.13915 | Central Coast | Moss Landing | Unit Sub | 4,21 | Tier 6 | No | Dist | 21 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 2 | 362 | 178 | 0 |  | 1 | 4 | n/a | 2 | 6 | 10 |  | 23 | 19 | N | 698
ETS.09.13620 | SOTO | ETS.09.13620 | Central Coast | Hayward | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | 4 | 0 | 362 | 178 | 0 |  | 1 | 4 | 4 | 0 | 6 | 10 |  | 25 | 17 | N | 666
ETS.02.13028 | SOUTH PH | ETS.02.13028 | North Coast | Cottonwood | 0 | 60 | Tier 6 | No | G | 60 |  | 3 | 4 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | 12 | 1 | 0 |  | 4 | 8 | n/a | 0 | 2 | 5 |  | 19 | 23 | N | n/a
ETS.19.13621 | SPANISH CREEK | ETS.19.13621 | North Coast | Table Mountain | DSub in FERC | 44,60 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T2 | HFTD - Non-critical Substation | 3 | 0 | 188 | 178 | 0 |  | 2 | 8 | 3 | 0 | 4 | 10 |  | 27 | 15 | N | 335
ETS.04.13030 | SPAULDING #1 PH | ETS.04.13030 | North Valley | Del Mar | 0 | n/a | Tier 6 | No | G | 60 |  | 4 | 4 |  | T2 | HFTD - Non-critical Substation | 2 | 2 | 19 | 1 | 0 |  | 4 | 8 | 2 | 2 | 2 | 5 |  | 23 | 19 | N | 200
ETS.15.13622 | SPENCE | ETS.15.13622 | Central Coast | Moss Landing | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 207 | 178 | 0 |  | 2 | 4 | 2 | 0 | 6 | 10 |  | 24 | 18 | N | 522
ETS.14.10163 | SPRING GAP PH | ETS.14.10163 | North Valley | Merced | DSub not in FERC | 17115 | Tier 6 | No | Dist | 115 |  | 2 | 3 |  | T3 | HFTD - Non-critical Substation | 4 | 2 | 3 | 1 | 0 |  | 3 | 10 | 4 | 2 | 2 | 5 |  | 26 | 16 | N | 110
ETS.16.13908 | SRI | ETS.16.13908 | Central Coast | San Carlos | Dist. Single Cust. | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 196 | 178 | 0 |  | 2 | 4 | n/a | 0 | 4 | 10 |  | 20 | 22 | N | n/a
ETS.13.13046 | STAFFORD | ETS.13.13046 | North Coast | McMaude | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T2 | HFTD - Non-critical Substation | 4 | 1 | 227 | 178 | 0 |  | 2 | 8 | 4 | 1 | 6 | 10 |  | 31 | 11 | N | 73
ETS.18.10167 | STAGG | ETS.18.10167 | North Valley | Stockton | T&D | 12,21,60,230 | Tier 6 | Yes | T | 230 |  | 13 | 8 |  | T1 | non-HFTD - Non-critical Substation | 7 | 0 | 360 | 178 | 0 |  | 8 | 4 | 7 | 0 | 6 | 10 |  | 35 | 7 | N | 604
ETS.18.13055 | STANISLAUS PH | ETS.18.13055 | North Valley | Stockton | 0 | 17,115 | Tier 6 | No | G | 115 |  | 5 | 4 |  | T2 | HFTD - Non-critical Substation | 6 | 3 | 258 | 178 | 0 |  | 4 | 8 | 6 | 3 | 6 | 10 |  | 37 | 5 | N | 15
ETS.12.16261 | STATION MA | ETS.12.16261 | Bay Area | Martin | 0 | 12115 | Tier 6 | No | Dist | 115 |  | 3 | 3 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 3 | 4 | n/a | 0 | 1 | 1 |  | 9 | 33 | N | n/a
ETS.22.13057 | STAUFFER | ETS.22.13057 | Central Coast | Concord | Dist. Single Cust. | 4,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 202 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | n/a
ETS.03.13058 | STELLING | ETS.03.13058 | Central Coast | Cupertino | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 4 | 2 | 319 | 178 | 0 |  | 6 | 4 | 4 | 2 | 6 | 10 |  | 32 | 10 | N | 14
ETS.02.13059 | STILLWATER | ETS.02.13059 | North Coast | Cottonwood | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T2/3A | HFTD - Non-critical Substation | 4 | 2 | 227 | 178 | 0 |  | 2 | 6 | 4 | 2 | 6 | 10 |  | 30 | 12 | N | 193
ETS.10.13061 | STOCKDALE | ETS.10.13061 | South Valley | Bakersfield | DSub in FERC | 12,21,115,230 | Tier 6 | Yes | Dist | 230 |  | 9 | 7 |  | T1 | non-HFTD - Non-critical Substation | 4 | 0 | 360 | 178 | 0 |  | 7 | 4 | 4 | 0 | 6 | 10 |  | 31 | 11 | N | 443
ETS.18.13062 | STOCKTON A | ETS.18.13062 | North Valley | Stockton | DSub in FERC | 4,12,60,115 | Tier 6 | Yes | Dist | 115 |  | 11 | 6 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 238 | 178 | 0 |  | 6 | 4 | 3 | 0 | 6 | 10 |  | 29 | 13 | N | 342
ETS.18.13063 | STOCKTON ACRES | ETS.18.13063 | North Valley | Stockton | DSub in FERC | 4,60 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 207 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 691
ETS.03.13066 | STONE | ETS.03.13066 | Central Coast | Cupertino | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 418 | 178 | 0 |  | 6 | 4 | n/a | 0 | 6 | 10 |  | 26 | 16 | N | 406
ETS.07.13067 | STONE CORRAL | ETS.07.13067 | South Valley | Fresno | DSub in FERC | 12,60,70 | Tier 6 | No | Dist | 70 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 207 | 178 | 0 |  | 2 | 4 | 2 | 0 | 6 | 10 |  | 24 | 18 | N | 546
ETS.14.10168 | STOREY | ETS.14.10168 | North Valley | Merced | DSub in FERC | 12,230 | Tier 6 | Yes | Dist | 230 |  | 4 | 7 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 7 | 4 | n/a | 0 | 6 | 10 |  | 27 | 15 | N | 283
ETS.08.13069 | STROUD | ETS.08.13069 | South Valley | Gates | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 196 | 178 | 0 |  | 2 | 4 | 3 | 0 | 4 | 10 |  | 23 | 19 | N | 679
ETS.23.13628 | STUART | ETS.23.13628 | Bay Area | Oakport | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 258 | 178 | 0 |  | 1 | 4 | 3 | 0 | 6 | 10 |  | 24 | 18 | N | 304
ETS.21.13071 | SUISUN | ETS.21.13071 | North Valley | Vaca-Dixon | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 6 | 1 | 258 | 178 | 0 |  | 6 | 4 | 6 | 1 | 6 | 10 |  | 33 | 9 | N | 432
ETS.12.13073 | SULLIVAN | ETS.12.13073 | Bay Area | Martin | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 362 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 734
ETS.04.13075 | SUMMIT | ETS.04.13075 | North Valley | Del Mar | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T2 | HFTD - Non-critical Substation | n/a | 2 | 238 | 178 | 0 |  | 2 | 8 | n/a | 2 | 6 | 10 |  | 28 | 14 | N | 339
ETS.09.13077 | SUNOL | ETS.09.13077 | Central Coast | Hayward | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T2/3A | HFTD - Non-critical Substation | 2 | 2 | 196 | 178 | 0 |  | 2 | 6 | 2 | 2 | 4 | 10 |  | 26 | 16 | N | 214
ETS.18.16791 | SUTTER HOME SW STA | ETS.18.16791 | North Valley | Stockton | SW STA - Trans | 60 | Tier 6 | No | T | 60 |  | n/a | 5 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 3 | 1 | 0 |  | 5 | 4 | n/a | 0 | 2 | 5 |  | 16 | 26 | N | n/a
ETS.03.13081 | SWIFT | ETS.03.13081 | Central Coast | Cupertino | DSub in FERC | 12,21,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 5 | 2 | 238 | 178 | 0 |  | 6 | 4 | 5 | 2 | 6 | 10 |  | 33 | 9 | N | 215
ETS.19.13082 | SYCAMORE CREEK | ETS.19.13082 | North Coast | Table Mountain | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 4 | 258 | 178 | 0 |  | 6 | 4 | n/a | 4 | 6 | 10 |  | 30 | 12 | N | 87
ETS.19.10173 | TABLE MTN | ETS.19.10173 | North Coast | Table Mountain | T-Sub | 60,70,115,230,500 | Tier 1 | Yes | T | 500 |  | 26 | 10 |  | T1 | non-HFTD - Critical Substation | 7 | 0 | 500 | 178 | 0 |  | 10 | 4 | 7 | 0 | 6 | 10 |  | 37 | 5 | N | n/a
ETS.10.13088 | TAFT | ETS.10.13088 | South Valley | Bakersfield | T&D | 12,115,70 | Tier 6 | Yes | T | 115 |  | 14 | 8 |  | T1 | non-HFTD - Non-critical Substation | 4 | 0 | 500 | 178 | 0 |  | 8 | 4 | 4 | 0 | 6 | 10 |  | 32 | 10 | N | 542
ETS.04.13093 | TAMARACK | ETS.04.13093 | North Valley | Del Mar | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 2 | 19 | 1 | 0 |  | 2 | 4 | 3 | 2 | 2 | 5 |  | 18 | 24 | N | 173
ETS.14.13629 | TAR FLAT | ETS.14.13629 | North Valley | Merced | Unit Sub | 4,17 | Tier 6 | No | Dist | 17 |  | n/a | 1 |  | T2/3A | HFTD - Non-critical Substation | n/a | 2 | 240 | 178 | 0 |  | 1 | 6 | n/a | 2 | 6 | 10 |  | 25 | 17 | N | 452
ETS.12.13094 | TARAVAL | ETS.12.13094 | Bay Area | Martin | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 240 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 660
ETS.09.10169 | TASSAJARA | ETS.09.10169 | Central Coast | Hayward | DSub in FERC | 21,230 | Tier 6 | Yes | Dist | 230 |  | 4 | 7 |  | T1 | non-HFTD - Non-critical Substation | n/a | 2 | 225 | 178 | 0 |  | 7 | 4 | n/a | 2 | 6 | 10 |  | 29 | 13 | N | 40
ETS.10.13096 | TECUYA | ETS.10.13096 | South Valley | Bakersfield | DSub in FERC | 2.4,70 | Tier 6 | No | Dist | 70 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 284 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 765
ETS.10.13097 | TEJON | ETS.10.13097 | South Valley | Bakersfield | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 5 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 3 | 240 | 178 | 0 |  | 2 | 4 | 3 | 3 | 6 | 10 |  | 28 | 14 | N | 203
ETS.10.13098 | TEMBLOR | ETS.10.13098 | South Valley | Bakersfield | DSub in FERC | 12,21,115 | Tier 6 | No | Dist | 115 |  | 4 | 3 |  | T1 | non-HFTD - Non-critical Substation | 1 | 0 | 196 | 178 | 0 |  | 3 | 4 | 1 | 0 | 4 | 10 |  | 22 | 20 | N | 560
ETS.17.13099 | TEMPLETON | ETS.17.13099 | South Valley | Pismo | T&D | 21,230,70 | Tier 6 | Yes | T | 230 |  | 8 | 8 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 744 | 178 | 0 |  | 8 | 4 | 3 | 0 | 8 | 10 |  | 33 | 9 | N | 226
ETS.18.13101 | TERMINOUS | ETS.18.13101 | North Valley | Stockton | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 202 | 178 | 0 |  | 2 | 4 | 2 | 0 | 6 | 10 |  | 24 | 18 | N | 555
ETS.09.13913 | TES SAN RAMON | ETS.09.13913 | Central Coast | Hayward |  |  | Tier 6 | No | Dist | 230 |  | n/a | 3 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 202 | 178 | 0 |  | 3 | 4 | n/a | 0 | 6 | 10 |  | 23 | 19 | N | n/a
ETS.26.16460 | TESLA | ETS.26.16460 | North Valley | Tesla | T-Sub | 500,230,115 | Tier 1 | Yes | T | 500 |  | 40 | 10 |  | T1 | non-HFTD - Critical Substation | 3 | 0 | 360 | 178 | 0 |  | 10 | 4 | 3 | 0 | 6 | 10 |  | 33 | 9 | N | n/a
ETS.22.10170 | TESORO | ETS.22.10170 | Central Coast | Concord | SW STA - Trans | 230 | Tier 6 | Yes | T | 230 |  | 4 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 6 | 1 | 0 |  | 8 | 4 | n/a | 0 | 2 | 5 |  | 19 | 23 | N | n/a
ETS.10.13103 | TEVIS | ETS.10.13103 | South Valley | Bakersfield | DSub in FERC | 21,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 238 | 178 | 0 |  | 6 | 4 | n/a | 0 | 6 | 10 |  | 26 | 16 | N | 550
ETS.22.10171 | TIDEWATER | ETS.22.10171 | Central Coast | Concord | DSub in FERC | 21,230 | Tier 6 | Yes | Dist | 230 |  | 6 | 7 |  | T1 | non-HFTD - Non-critical Substation | 5 | 1 | 360 | 178 | 0 |  | 7 | 4 | 5 | 1 | 6 | 10 |  | 33 | 9 | N | 105
ETS.18.10172 | TIGER CREEK PH | ETS.18.10172 | North Valley | Stockton | 0 | 115,230 | Tier 6 | Yes | T | 230 |  | 5 | 8 |  | T3 | HFTD - Non-critical Substation | 3 | 3 | 200 | 178 | 0 |  | 8 | 10 | 3 | 3 | 4 | 10 |  | 38 | 4 | N | 239
ETS.07.13108 | TIVY VALLEY | ETS.07.13108 | South Valley | Fresno | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 401
ETS.19.16620 | TOADTOWN PH | ETS.19.16620 | North Coast | Table Mountain | 0 | 12 | Tier 6 | No | G | 12 |  | n/a | 4 |  | T3 | HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 4 | 10 | n/a | 0 | 1 | 1 |  | 16 | 26 | N | n/a
ETS.13.13109 | TOCALOMA | ETS.13.13109 | North Coast | McMaude | DSub in FERC | 4,60 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | 198 | 178 | 0 |  | 2 | 8 | n/a | 0 | 4 | 10 |  | 24 | 18 | N | 756
ETS.26.16465 | TRACY | ETS.26.16465 | North Valley | Tesla | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 6 | 6 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 500 | 178 | 0 |  | 6 | 4 | 3 | 0 | 6 | 10 |  | 29 | 13 | N | 191
ETS.07.16792 | TRANQUILLITY SW STA | ETS.07.16792 | South Valley | Fresno | SW STA - Trans | 230 | Tier 6 | No | T | 230 |  | n/a | 5 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 6 | 1 | 0 |  | 5 | 4 | n/a | 0 | 2 | 5 |  | 16 | 26 | N | n/a
ETS.15.13632 | TRES PINOS | ETS.15.13632 | Central Coast | Moss Landing | DSub not in FERC | 12,21 | Tier 6 | No | Dist | 21 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 6 | 1 | 0 |  | 1 | 4 | n/a | 0 | 2 | 5 |  | 12 | 30 | N | 573
ETS.19.13118 | TRES VIAS | ETS.19.13118 | North Coast | Table Mountain | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 566
ETS.03.13119 | TRIMBLE | ETS.03.13119 | Central Coast | Cupertino | DSub in FERC | 12,21,115 | Tier 6 | Yes | Dist | 115 |  | 8 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 238 | 178 | 0 |  | 6 | 4 | n/a | 0 | 6 | 10 |  | 26 | 16 | N | 514
ETS.06.13120 | TRINIDAD | ETS.06.13120 | North Coast | Eureka | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 2 | 227 | 178 | 0 |  | 2 | 4 | 3 | 2 | 6 | 10 |  | 27 | 15 | N | 182
ETS.02.13121 | TRINITY | ETS.02.13121 | North Coast | Cottonwood | T-Sub | 115,60 | Tier 6 | Yes | T | 115 |  | 7 | 8 |  | T2/3A | HFTD - Non-critical Substation | n/a | 0 | 256 | 178 | 0 |  | 8 | 6 | n/a | 0 | 6 | 10 |  | 30 | 12 | N | n/a
ETS.04.13124 | TUDOR | ETS.04.13124 | North Valley | Del Mar | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 284 | 178 | 0 |  | 2 | 4 | 3 | 0 | 6 | 10 |  | 25 | 17 | N | 669
ETS.08.13125 | TULARE LAKE | ETS.08.13125 | South Valley | Gates | DSub in FERC | 12,60,70 | Tier 6 | No | Dist | 70 |  | 5 | 2 |  | T1 | non-HFTD - Non-critical Substation | 4 | 0 | 240 | 178 | 0 |  | 2 | 4 | 4 | 0 | 6 | 10 |  | 26 | 16 | N | 602
ETS.10.16330 | TULE RIVER PH | ETS.10.16330 | South Valley | Bakersfield | 0 | 70 | Tier 6 | No | Dist | 70 |  | 3 | 2 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 2 | 8 | n/a | 0 | 1 | 1 |  | 12 | 30 | N | 414
ETS.13.10174 | TULUCAY | ETS.13.10174 | North Coast | McMaude | T&D | 12,60,230 | Tier 6 | Yes | T | 230 |  | 9 | 8 |  | T1 | non-HFTD - Non-critical Substation | 2 | 2 | 256 | 178 | 0 |  | 8 | 4 | 2 | 2 | 6 | 10 |  | 32 | 10 | N | 161
ETS.10.13129 | TUPMAN | ETS.10.13129 | South Valley | Bakersfield | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 198 | 178 | 0 |  | 6 | 4 | 3 | 0 | 4 | 10 |  | 27 | 15 | N | 637
ETS.12.13131 | TWENTY-FIRST AVE | ETS.12.13131 | Bay Area | Martin | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 240 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 354
ETS.08.13132 | TWISSELMAN | ETS.08.13132 | South Valley | Gates | DSub in FERC | 12,21,70 | Tier 6 | No | Dist | 70 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 196 | 178 | 0 |  | 2 | 4 | 2 | 0 | 4 | 10 |  | 22 | 20 | N | 609
ETS.02.13133 | TYLER | ETS.02.13133 | North Coast | Cottonwood | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 3 | 362 | 178 | 0 |  | 2 | 4 | n/a | 3 | 6 | 10 |  | 25 | 17 | Y | 249
ETS.20.13136 | UKIAH | ETS.20.13136 | North Coast | Ukiah | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T2/3A | HFTD - Non-critical Substation | 3 | 2 | 227 | 178 | 0 |  | 6 | 6 | 3 | 2 | 6 | 10 |  | 33 | 9 | Y | 98
ETS.20.13147 | UPPER LAKE | ETS.20.13147 | North Coast | Ukiah | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T2 | HFTD - Non-critical Substation | n/a | 3 | 500 | 178 | 0 |  | 2 | 8 | n/a | 3 | 6 | 10 |  | 29 | 13 | N | 95
ETS.22.13148 | URICH | ETS.22.13148 | Central Coast | Concord | Dist. Single Cust. | 4,60 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 198 | 178 | 0 |  | 2 | 4 | n/a | 0 | 4 | 10 |  | 20 | 22 | N | n/a
ETS.21.10176 | VACA DIXON | ETS.21.10176 | North Valley | Vaca-Dixon | T&D | 12,115,230,60,500 | Tier 1 | Yes | T | 500 |  | 40 | 10 |  | T1 | non-HFTD - Critical Substation | 6 | 2 | 498 | 178 | 0 |  | 10 | 4 | 6 | 2 | 6 | 10 |  | 38 | 4 | N | 271
ETS.21.13151 | VACAVILLE | ETS.21.13151 | North Valley | Vaca-Dixon | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 5 | 3 | 238 | 178 | 0 |  | 6 | 4 | 5 | 3 | 6 | 10 |  | 34 | 8 | N | 136
ETS.09.13153 | VALLECITOS | ETS.09.13153 | Central Coast | Hayward | Dist. Single Cust. | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 202 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | n/a
ETS.13.13634 | VALLEJO B | ETS.13.13634 | North Coast | McMaude | DSub not in FERC | 4,12,21,24 | Tier 6 | No | Dist | 21 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | 4 | 1 | 258 | 178 | 0 |  | 1 | 4 | 4 | 1 | 6 | 10 |  | 26 | 16 | N | 631
ETS.13.13635 | VALLEJO C | ETS.13.13635 | North Coast | McMaude | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 1 | 202 | 178 | 0 |  | 1 | 4 | n/a | 1 | 6 | 10 |  | 22 | 20 | N | 487
ETS.18.13154 | VALLEY HOME | ETS.18.13154 | North Valley | Stockton | DSub in FERC | 17,60,115 | Tier 6 | No | Dist | 115 |  | 4 | 3 |  | T1 | non-HFTD - Non-critical Substation | 5 | 0 | 202 | 178 | 0 |  | 3 | 4 | 5 | 0 | 6 | 10 |  | 28 | 14 | N | 312
ETS.18.10177 | VALLEY SPRINGS | ETS.18.10177 | North Valley | Stockton | T-Sub | 230,60 | Tier 6 | Yes | T | 230 |  | 12 | 8 |  | T2/3A | HFTD - Non-critical Substation | 3 | 0 | 240 | 178 | 0 |  | 8 | 6 | 3 | 0 | 6 | 10 |  | 33 | 9 | N | n/a
ETS.22.13157 | VALLEY VIEW | ETS.22.13157 | Central Coast | Concord | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T1 | non-HFTD - Non-critical Substation | 3 | 2 | 258 | 178 | 0 |  | 6 | 4 | 3 | 2 | 6 | 10 |  | 31 | 11 | N | 54
ETS.26.13163 | VASCO | ETS.26.13163 | North Valley | Tesla | DSub in FERC | 12,21,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 1 | 258 | 178 | 0 |  | 2 | 4 | n/a | 1 | 6 | 10 |  | 23 | 19 | N | 44
ETS.03.13818 | VASONA | ETS.03.13818 | Central Coast | Cupertino | DSub in FERC | 12,230 | Tier 6 | Yes | Dist | 230 |  | 4 | 7 |  | T1 | non-HFTD - Non-critical Substation | 5 | 1 | 317 | 178 | 0 |  | 7 | 4 | 5 | 1 | 6 | 10 |  | 33 | 9 | N | 287
ETS.18.13166 | VICTOR | ETS.18.13166 | North Valley | Stockton | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 324
ETS.15.13168 | VIEJO | ETS.15.13168 | Central Coast | Moss Landing | DSub in FERC | 21,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T2 | HFTD - Non-critical Substation | 4 | 0 | 225 | 178 | 0 |  | 2 | 8 | 4 | 0 | 6 | 10 |  | 30 | 12 | N | 595
ETS.18.15478 | VIERRA | ETS.18.15478 | North Valley | Stockton | DSub in FERC | 17,18,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 4 | 0 | 225 | 178 | 0 |  | 6 | 4 | 4 | 0 | 6 | 10 |  | 30 | 12 | N | 376
ETS.02.13169 | VINA | ETS.02.13169 | North Coast | Cottonwood | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | 4 | 2 | 207 | 178 | 0 |  | 2 | 4 | 4 | 2 | 6 | 10 |  | 28 | 14 | N | 473
ETS.09.13637 | VINEYARD | ETS.09.13637 | Central Coast | Hayward | DSub in FERC | 21,60 | Tier 6 | No | Dist | 230 |  | 4 | 3 |  | T1 | non-HFTD - Non-critical Substation | 5 | 1 | 317 | 178 | 0 |  | 3 | 4 | 5 | 1 | 6 | 10 |  | 29 | 13 | N | 55
ETS.23.13638 | VIRGINIA | ETS.23.13638 | Bay Area | Oakport | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 198 | 178 | 0 |  | 1 | 4 | n/a | 0 | 4 | 10 |  | 19 | 23 | N | 689
ETS.02.13171 | VOLTA #1 PH | ETS.02.13171 | North Coast | Cottonwood | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T3 | HFTD - Non-critical Substation | 4 | 4 | 225 | 178 | 0 |  | 2 | 10 | 4 | 4 | 6 | 10 |  | 36 | 6 | N | 48
ETS.07.13175 | WAHTOKE | ETS.07.13175 | South Valley | Fresno | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 238 | 178 | 0 |  | 6 | 4 | 3 | 0 | 6 | 10 |  | 29 | 13 | N | 482
ETS.23.13639 | WALDO | ETS.23.13639 | Bay Area | Oakport | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 1 | 258 | 178 | 0 |  | 1 | 4 | n/a | 1 | 6 | 10 |  | 22 | 20 | N | 479
ETS.23.13640 | WALL | ETS.23.13640 | Bay Area | Oakport | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 198 | 178 | 0 |  | 1 | 4 | n/a | 0 | 4 | 10 |  | 19 | 23 | N | 641
ETS.22.13177 | WALNUT CREEK | ETS.22.13177 | Central Coast | Concord | Unit Sub | 4,21 | Tier 6 | No | Dist | 21 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 240 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 594
ETS.09.13641 | WARD | ETS.09.13641 | Central Coast | Hayward | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 240 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 703
ETS.10.13178 | WASCO | ETS.10.13178 | South Valley | Bakersfield | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 362 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 484
ETS.18.13180 | WATERLOO | ETS.18.13180 | North Valley | Stockton | DSub in FERC | 12,60 | Tier 6 | Yes | Dist | 60 |  | 2 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 240 | 178 | 0 |  | 6 | 4 | n/a | 0 | 6 | 10 |  | 26 | 16 | N | 670
ETS.16.13181 | WATERSHED | ETS.16.13181 | Central Coast | San Carlos | Dist. Single Cust. | 4,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 1 | 190 | 178 | 0 |  | 2 | 4 | n/a | 1 | 4 | 10 |  | 21 | 21 | N | 374
ETS.15.13182 | WATSONVILLE | ETS.15.13182 | Central Coast | Moss Landing | DSub in FERC | 4,12,21,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | 1 | 0 | 238 | 178 | 0 |  | 2 | 4 | 1 | 0 | 6 | 10 |  | 23 | 19 | N | 398
ETS.08.16750 | WAUKENA SW STA | ETS.08.16750 | South Valley | Gates | SW STA - Trans | 115 | Tier 6 | Yes | T | 115 |  | 3 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 5 | 1 | 0 |  | 8 | 4 | n/a | 0 | 2 | 5 |  | 19 | 23 | N | n/a
ETS.18.10179 | WEBER | ETS.18.10179 | North Valley | Stockton | T&D | 12,60,230 | Tier 6 | Yes | T | 230 |  | 16 | 8 |  | T1 | non-HFTD - Non-critical Substation | 7 | 0 | 362 | 178 | 0 |  | 8 | 4 | 7 | 0 | 6 | 10 |  | 35 | 7 | N | 362
ETS.10.13186 | WEEDPATCH | ETS.10.13186 | South Valley | Bakersfield | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 5 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 225 | 178 | 0 |  | 2 | 4 | 3 | 0 | 6 | 10 |  | 25 | 17 | N | 586
ETS.04.13643 | WEIMAR | ETS.04.13643 | North Valley | Del Mar | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T2 | HFTD - Non-critical Substation | 3 | 3 | 362 | 178 | 0 |  | 2 | 8 | 3 | 3 | 6 | 10 |  | 32 | 10 | N | 242
ETS.10.13187 | WELLFIELD | ETS.10.13187 | South Valley | Bakersfield | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 202 | 178 | 0 |  | 2 | 4 | 3 | 0 | 6 | 10 |  | 25 | 17 | N | 712
ETS.07.13191 | WEST FRESNO | ETS.07.13191 | South Valley | Fresno | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 4 | 0 | 227 | 178 | 0 |  | 6 | 4 | 4 | 0 | 6 | 10 |  | 30 | 12 | N | 481
ETS.18.13192 | WEST LANE | ETS.18.13192 | North Valley | Stockton | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 383
ETS.18.13193 | WEST POINT PH | ETS.18.13193 | North Valley | Stockton | DSub not in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T3 | HFTD - Non-critical Substation | 3 | 3 | 258 | 178 | 0 |  | 2 | 10 | 3 | 3 | 6 | 10 |  | 34 | 8 | N | 20
ETS.21.13194 | WEST SACRAMENTO | ETS.21.13194 | North Valley | Vaca-Dixon | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 7 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 227 | 178 | 0 |  | 6 | 4 | n/a | 0 | 6 | 10 |  | 26 | 16 | N | 435
ETS.12.13196 | WESTLAKE | ETS.12.13196 | Bay Area | Martin | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 202 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 667
ETS.07.13197 | WESTLANDS | ETS.07.13197 | South Valley | Fresno | DSub in FERC | 4,70 | Tier 6 | No | Dist | 70 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 198 | 178 | 0 |  | 2 | 4 | n/a | 0 | 4 | 10 |  | 20 | 22 | N | n/a
ETS.26.13201 | WESTLEY | ETS.26.13201 | North Valley | Tesla | DSub in FERC | 12,60 | Tier 6 | No | Dist | 70 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 2 | 227 | 178 | 0 |  | 2 | 4 | n/a | 2 | 6 | 10 |  | 24 | 18 | N | 455
ETS.10.13202 | WESTPARK | ETS.10.13202 | South Valley | Bakersfield | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 6 | 6 |  | T1 | non-HFTD - Non-critical Substation | 4 | 0 | 362 | 178 | 0 |  | 6 | 4 | 4 | 0 | 6 | 10 |  | 30 | 12 | N | 544
ETS.26.16470 | WESTSIDE | ETS.26.16470 | North Valley | Tesla | DSub in FERC | 2.4,60 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 207 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | n/a
ETS.19.13717 | WESTWOOD SW STA | ETS.19.13717 | North Coast | Table Mountain | SW STA - Trans | 60 | Tier 6 | No | T | 60 |  | 4 | 5 |  | T2/3A | HFTD - Non-critical Substation | n/a | 0 | 16 | 1 | 0 |  | 5 | 6 | n/a | 0 | 2 | 5 |  | 18 | 24 | N | n/a
ETS.04.13205 | WHEATLAND | ETS.04.13205 | North Valley | Del Mar | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 3 | 227 | 178 | 0 |  | 2 | 4 | 3 | 3 | 6 | 10 |  | 28 | 14 | N | 346
ETS.10.10180 | WHEELER RIDGE | ETS.10.10180 | South Valley | Bakersfield | T&D | 12,70,115,230 | Tier 6 | Yes | T | 230 |  | 14 | 8 |  | T1 | non-HFTD - Non-critical Substation | 5 | 1 | 500 | 178 | 0 |  | 8 | 4 | 5 | 1 | 6 | 10 |  | 34 | 8 | N | 476
ETS.03.13209 | WHISMAN | ETS.03.13209 | Central Coast | Cupertino | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 240 | 178 | 0 |  | 6 | 4 | 3 | 0 | 6 | 10 |  | 29 | 13 | N | 407
ETS.02.13211 | WHITMORE | ETS.02.13211 | North Coast | Cottonwood | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T2 | HFTD - Non-critical Substation | 4 | 3 | 19 | 1 | 0 |  | 2 | 8 | 4 | 3 | 2 | 5 |  | 24 | 18 | N | 176
ETS.22.13644 | WHITNEY | ETS.22.13644 | Central Coast | Concord | Unit Sub | 4,21 | Tier 6 | No | Dist | 21 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 202 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 707
ETS.02.13213 | WILDWOOD | ETS.02.13213 | North Coast | Cottonwood | DSub in FERC | 12,115 | Tier 6 | No | Dist | 115 |  | 3 | 3 |  | T2 | HFTD - Non-critical Substation | 2 | 2 | 19 | 1 | 0 |  | 3 | 8 | 2 | 2 | 2 | 5 |  | 22 | 20 | N | 210
ETS.21.13214 | WILKINS SLOUGH | ETS.21.13214 | North Valley | Vaca-Dixon | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | 2 | 0 | 284 | 178 | 0 |  | 2 | 4 | 2 | 0 | 6 | 10 |  | 24 | 18 | N | 672
ETS.21.13215 | WILLIAMS | ETS.21.13215 | North Valley | Vaca-Dixon | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 225 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 477
ETS.20.13216 | WILLITS A | ETS.20.13216 | North Coast | Ukiah | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 5 | 2 |  | T2/3A | HFTD - Non-critical Substation | n/a | 1 | 240 | 178 | 0 |  | 2 | 6 | n/a | 1 | 6 | 10 |  | 25 | 17 | Y | 75
ETS.06.13217 | WILLOW CREEK | ETS.06.13217 | North Coast | Eureka | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 2 | 2 |  | T3 | HFTD - Non-critical Substation | n/a | 2 | 225 | 178 | 0 |  | 2 | 10 | n/a | 2 | 6 | 10 |  | 30 | 12 | N | 89
ETS.22.13218 | WILLOW PASS | ETS.22.13218 | Central Coast | Concord | DSub in FERC | 12,21,60,115 | Tier 6 | No | Dist | 115 |  | 3 | 3 |  | T1 | non-HFTD - Non-critical Substation | 3 | 1 | 227 | 178 | 0 |  | 3 | 4 | 3 | 1 | 6 | 10 |  | 27 | 15 | Y | 61
ETS.19.13219 | WILLOWS A | ETS.19.13219 | North Coast | Table Mountain | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 258 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 650
ETS.14.10182 | WILSON | ETS.14.10182 | North Valley | Merced | T&D | 12,115,230 | Tier 5 | Yes | T | 230 |  | 16 | 9 |  | T1 | non-HFTD - Critical Substation | 6 | 0 | 317 | 178 | 0 |  | 9 | 4 | 6 | 0 | 6 | 10 |  | 35 | 7 | N | 505
ETS.13.16530 | WINDSOR | ETS.13.16530 | North Coast | McMaude | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | n/a | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 2 | 48 | 1 | 0 |  | 2 | 4 | n/a | 2 | 2 | 5 |  | 15 | 27 | Y | 306
ETS.21.13222 | WINTERS | ETS.21.13222 | North Valley | Vaca-Dixon | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 19 | 1 | 0 |  | 2 | 4 | 3 | 0 | 2 | 5 |  | 16 | 26 | N | 708
ETS.04.13224 | WISE PH | ETS.04.13224 | North Valley | Del Mar | DSub not in FERC | 12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T2 | HFTD - Non-critical Substation | 2 | 3 | 3 | 1 | 0 |  | 1 | 8 | 2 | 3 | 2 | 5 |  | 21 | 21 | N | 91
ETS.10.13370 | WITCO SW STA | ETS.10.13370 | South Valley | Bakersfield | SW STA - Trans | 115 | Tier 6 | Yes | T | 115 |  | 3 | 8 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 13 | 1 | 0 |  | 8 | 4 | n/a | 0 | 2 | 5 |  | 19 | 23 | N | n/a
ETS.03.13227 | WOLFE | ETS.03.13227 | Central Coast | Cupertino | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 3 | 0 | 258 | 178 | 0 |  | 6 | 4 | 3 | 0 | 6 | 10 |  | 29 | 13 | N | 397
ETS.23.13646 | WOOD | ETS.23.13646 | Bay Area | Oakport | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | n/a | 1 |  | T2/3A | HFTD - Non-critical Substation | 2 | 1 | 202 | 178 | 0 |  | 1 | 6 | 2 | 1 | 6 | 10 |  | 26 | 16 | N | 466
ETS.13.13228 | WOODACRE | ETS.13.13228 | North Coast | McMaude | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 3 | 2 |  | T3 | HFTD - Non-critical Substation | 3 | 1 | 362 | 178 | 0 |  | 2 | 10 | 3 | 1 | 6 | 10 |  | 32 | 10 | N | 106
ETS.07.13229 | WOODCHUCK | ETS.07.13229 | South Valley | Fresno | DSub in FERC | 21,70 | Tier 6 | No | Dist | 70 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | 4 | 0 | 190 | 178 | 0 |  | 2 | 4 | 4 | 0 | 4 | 10 |  | 24 | 18 | N | 552
ETS.21.13230 | WOODLAND | ETS.21.13230 | North Valley | Vaca-Dixon | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 6 | 6 |  | T1 | non-HFTD - Non-critical Substation | 4 | 0 | 227 | 178 | 0 |  | 6 | 4 | 4 | 0 | 6 | 10 |  | 30 | 12 | N | 498
ETS.16.13233 | WOODSIDE | ETS.16.13233 | Central Coast | San Carlos | DSub in FERC | 12,60 | Tier 6 | No | Dist | 60 |  | 4 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 3 | 225 | 178 | 0 |  | 2 | 4 | n/a | 3 | 6 | 10 |  | 25 | 17 | N | 18
ETS.07.13234 | WOODWARD | ETS.07.13234 | South Valley | Fresno | DSub in FERC | 21,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 5 | 1 | 238 | 178 | 0 |  | 6 | 4 | 5 | 1 | 6 | 10 |  | 32 | 10 | N | 307
ETS.14.13235 | WRIGHT | ETS.14.13235 | North Valley | Merced | DSub in FERC | 12,70 | Tier 6 | No | Dist | 70 |  | 2 | 2 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 202 | 178 | 0 |  | 2 | 4 | n/a | 0 | 6 | 10 |  | 22 | 20 | N | 444
ETS.19.13237 | WYANDOTTE | ETS.19.13237 | North Coast | Table Mountain | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 5 | 6 |  | T1 | non-HFTD - Non-critical Substation | 3 | 7 | 240 | 178 | 0 |  | 6 | 4 | 3 | 7 | 6 | 10 |  | 36 | 6 | N | 12
ETS.03.16500 | YERBA BUENA | ETS.03.16500 | Central Coast | Cupertino | DSub not in FERC | 12,21 | Tier 6 | No | Dist | 21 |  | n/a | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | n/a | n/a | 0 |  | 1 | 4 | n/a | 0 | 1 | 1 |  | 7 | 35 | N | n/a
ETS.12.13239 | YOSEMITE | ETS.12.13239 | Bay Area | Martin | Unit Sub | 4,12 | Tier 6 | No | Dist | 12 |  | 3 | 1 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 240 | 178 | 0 |  | 1 | 4 | n/a | 0 | 6 | 10 |  | 21 | 21 | N | 575
ETS.14.13819 | YOSEMITE PARK | ETS.14.13819 | North Valley | Merced | Dist. Single Cust. | 12,70 | Tier 6 | No | Dist | 70 |  | n/a | 2 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | 198 | 178 | 0 |  | 2 | 8 | n/a | 0 | 4 | 10 |  | 24 | 18 | N | n/a
ETS.17.13243 | ZACA | ETS.17.13243 | South Valley | Pismo | DSub in FERC | 12,115 | Tier 6 | No | Dist | 115 |  | 2 | 3 |  | T2 | HFTD - Non-critical Substation | n/a | 0 | 61 | 1 | 0 |  | 3 | 8 | n/a | 0 | 3 | 5 |  | 19 | 23 | N | 347
ETS.21.13244 | ZAMORA | ETS.21.13244 | North Valley | Vaca-Dixon | DSub in FERC | 12,115 | Tier 6 | Yes | Dist | 115 |  | 4 | 6 |  | T1 | non-HFTD - Non-critical Substation | n/a | 0 | 207 | 178 | 0 |  | 6 | 4 | n/a | 0 | 6 | 10 |  | 26 | 16 | N | 642