## Summary
The EVM findings that included an additional finding of 10’ radial clearance of pole clearing, we disagree. The pole clearing program was not a 2021 WMP commitment. As background, the pole clearing program cycle begins October 1 and ends September 30 of the following year. At the time of these field findings, the pole clearing inspections had just completed on April 30, 2022. In several instances, the inspection occurs and if the pole cannot be cleared immediately, the work crews are assigned the scope and return to the pole to clear to the 10’ radial clearance. In many instances, crews had not yet been released to perform the work. As a courtesy, we did perform a field inspection to ensure the findings are resolved.
In summary, we field inspected 194 poles:
189 poles we disagree with the finding
2 poles we disbursed crews to clear the pole
1 pole is access/customer constrained

## Pole Clearing
Inspection ID | Sample Area | Circuit Name | Division | Region | Inspection Type | Inspection Justification | Pole Equipment IDs tied to finding upon field review: (list both if GPS is midspan | VC Pole number/s tied to finding upon field review: (list both if applicable) | Agree with CPUC finding? Y/N | Rationale for agree/disagree | Is Corrective Action Required? Y/N | Corrective Action Description | Status (was pole in question a refusal/previously cleared/not applicable?) | Notes
F-0037 | 13 | SOBRANTE 1102 | Diablo | Bay | Subject Pole | Subject Pole Clearance (10 feet) | 100474796 | N/A | N | Exempt from PRC 4292 liquid fuses, compression connectors | N | N/A | N/A | Exempt from PRC 4292 liquid fuses, compression connectors
F-0041 | 13 | SOBRANTE 1102 | Diablo | Bay | Subject Pole | Radial Clearance (12 feet), Subject Pole Clearance (10 feet) | 100473759 | N/A | N | Exempt from PRC 4292, compression connectors | N | N/A | N/A | Exempt from PRC 4292, compression connectors
F-0048 | 13 | SOBRANTE 1102 | Diablo | Bay | Subject Pole | Radial Clearance (12 feet), Subject Pole Clearance (10 feet) | 100473675 | N/A | N | Exempt from PRC 4292, compression connectors | N | N/A | N/A | Exempt from PRC 4292, compression connectors
F-0049 | 13 | SOBRANTE 1102 | Diablo | Bay | Subject Pole | Subject Pole Clearance (10 feet) | 100473672 | N/A | N | Exempt from PRC 4292, compression connectors | N | N/A | N/A | Exempt from PRC 4292, compression connectors
F-0089 | 18 | TIVY VALLEY 1107 | Fresno | Central Valley | Subject Pole | Radial Clearance (12 feet), Subject Pole Clearance (10 feet) | 104093907 | N/A | N | exempt liquids/exempt hot tap clamps | N | N/A | N/A | Exempt from PRC 4292
F-0058 | 14 | WOODSIDE 1101 | Peninsula | Bay | Regular | Radial Clearance (12 feet), Dry Fuel | 103805452 |  | N | Carrier pole with neither exempt or non exempt equipment | N
F-0119 | 4 | LAYTONVILLE 1102 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102193878 | N/A | N | Carrier pole with neither exempt or non exempt equiptment | N | N/A | N/A | Not A Subject Pole
F-0120 | 4 | LAYTONVILLE 1102 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102194659 | N/A | N | Ex Hot Tap And Ex Fault Tamers | N | N/A | N/A | Not A Subject Pole
F-0122 | 4 | LAYTONVILLE 1102 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102183212 | N/A | N | Ex Hot Taps / Liquid Fuses | N | N/A | N/A | Not A Subject Pole
F-0123 | 4 | LAYTONVILLE 1102 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102194077 | N/A | N | Ex Hot Tap And Ex Fault Tamers | N | N/A | N/A | Not A Subject Pole
F-0124 | 4 | LAYTONVILLE 1102 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102194080 | N/A | N | Ex Hot Taps / Non explotion Fuses | N | N/A | N/A | Not A Subject Pole
F-0125 | 4 | LAYTONVILLE 1102 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102193980 | 11156 | N | Cylinder is clear up 10 ft. | N | N/A | N/A | Cylinder is clear up 10 ft.
F-0126 | 4 | LAYTONVILLE 1102 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102193968 | N/A | N | Ex Hot Tap And Ex Fault Tamers | N | N/A | N/A | Not A Subject Pole
F-0127 | 4 | LAYTONVILLE 1102 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102194220 | N/A | N | Ex Hot Tap And Ex Fault Tamers | N | N/A | N/A | Not A Subject Pole
F-0128 | 4 | LAYTONVILLE 1102 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102194226 | N/A | N | Ex Connectors / Liquid Fuses | N | N/A | N/A | Not A Subject Pole
F-0129 | 5 | UKIAH 1111 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102174860 | N/A | N | Ex hot tap clamps and compression fittings | N | N/A | N/A | Not A Subject Pole
F-0130 | 5 | UKIAH 1111 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102174880 | N/A | N | Alley Arm Carrier pole w/risers | N | N/A | N/A | Not A Subject Pole
F-0131 | 5 | UKIAH 1111 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102174927 | N/A | N | Crossarm Carrier Pole w/risers, Automatic Line Splicers | N | N/A | N/A | Not A Subject Pole
F-0132 | 5 | UKIAH 1111 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102175010 | N/A | N | Tangent Crossarm w/wedge connectors | N | N/A | N/A | Not A Subject Pole
F-0133 | 5 | UKIAH 1111 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102175015 | 226231 | Y | P is subject, has dead stumps in cylinder | Y | Fill out Observation Report for Stumps | Previously cleared | Filled out Obs. Rep. for Stumps; stump removal contractor being assigned
F-0134 | 5 | UKIAH 1111 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 103792930 | N/A | N | Crossarm Carrier Pole w/risers | N | N/A | N/A | Not A Subject Pole
F-0135 | 5 | UKIAH 1111 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102175380 | N/A | N | Tangent Crossarm w/Parallel Groove Connectors | N | N/A | N/A | Not A Subject Pole
F-0136 | 5 | UKIAH 1111 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102175391 | N/A | N | Ex Abb & Fault Tamers & Hot Tap Clamps | N | N/A | N/A | Not A Subject Pole
F-0137 | 5 | UKIAH 1111 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102175390 | N/A | N | Tangent Crossarm w/Ex Hot Clamps & Compression Connectors | N | N/A | N/A | Not A Subject Pole
F-0138 | 5 | UKIAH 1111 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | N/A | N/A | N | Duplicate w/ F-0137 | N | N/A | N/A | Same Pole as F-0137
F-0139 | 5 | UKIAH 1111 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102175408 | N/A | N | Ex Liquid Fuse & Ex Hot Tap Clamps | N | N/A | N/A | Not A Subject Pole
F-0140 | 5 | UKIAH 1111 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102175407 | N/A | N | Ex Liquid Fuse & Ex Hot Tap Clamps | N | N/A | N/A | Not A Subject Pole
F-0141 | 5 | UKIAH 1111 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102175389 | N/A | N | Tangent Crossarm w/wedge connectors | N | N/A | N/A | Not A Subject Pole
F-0142 | 5 | UKIAH 1111 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 103311204 | N/A | N | Crossarm Carrier Pole w/risers | N | N/A | N/A | Not A Subject Pole
F-0143 | 5 | UKIAH 1111 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 103311203 | N/A | N | Crossarm Carrier Pole w/risers | N | N/A | N/A | Not A Subject Pole
F-0144 | 5 | UKIAH 1111 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102175373 | N/A | N | Crossarm Carrier Pole w/risers | N | N/A | N/A | Not A Subject Pole
F-0145 | 5 | UKIAH 1111 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102175372 | N/A | N | Crossarm Carrier Pole w/risers | N | N/A | N/A | Not A Subject Pole
F-0146 | 5 | UKIAH 1111 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102175371 | N/A | N | Crossarm Carrier w/risers & Compression Connectors | N | N/A | N/A | Not A Subject Pole
F-0147 | 5 | UKIAH 1111 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102175363 | N/A | N | Ex Liquid Fuse & Ex Hot Tap Clamps | N | N/A | N/A | Not A Subject Pole
F-0148 | 5 | UKIAH 1111 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102175362 | N/A | N | Crossarm Carrier Pole w/risers | N | N/A | N/A | Not A Subject Pole
F-0149 | 5 | UKIAH 1111 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102302381 | N/A | N | Tangent Crossarm w/Ex Hot Clamps & Compression Connectors | N | N/A | N/A | Not A Subject Pole
F-0150 | 5 | UKIAH 1111 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102302381 | N/A | N | Duplicate w/ F-0149 | N | N/A | N/A | Same Pole as F-0149
F-0151 | 6 | PHILO 1101 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 103617291 | 249844 | Y | Non Exempt Equip lightening arrestors | Y | Add subject pole | Need to be cleared | Environmental review was complete; pole cleared on 8/4
F-0152 | 6 | PHILO 1101 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102213994 | N/A | N | Ex Fault Tamers & Ex Compression Clamps | N | N/A | N/A | Not A Subject Pole
F-0155 | 6 | PHILO 1101 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102197359 | N/A | N | Ex Transformer / Ex Compression Clamps | N | N/A | N/A | Not A Subject Pole
F-0156 | 6 | PHILO 1101 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102197389 | N/A | N | Ex Liqid Filleds / Ex Hot Tap Clamps | N | N/A | N/A | Not A Subject Pole
F-0159 | 6 | PHILO 1101 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102214998 | N/A | N | Ex Fault Tamers / Ex Copession Clamps | N | N/A | N/A | Not A Subject Pole
F-0160 | 6 | PHILO 1101 | Humboldt | North Coast | Subject Pole | Overhang Clearance (4 feet), Subject Pole Clearance (10 feet) | 102197902 | N/A | N | Ex Liquid Filleds / Ex Copession Clamps | N | N/A | N/A | Not A Subject Pole
F-0161 | 6 | PHILO 1101 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102197925 | N/A | N | Ex Liquid Filleds / Ex Hot Tap Clamps | N | N/A | N/A | Not A Subject Pole
F-0163 | 6 | PHILO 1101 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102203550 | N/A | N | Ex Compression Clamps - Carrier pole | N | N/A | N/A | Not A Subject Pole
F-0164 | 6 | PHILO 1101 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102216174 / 102203547 | N/A | N | Ex Connections / Ex Fault Tamers | N | N/A | N/A | Not A Subject Pole
F-0165 | 6 | PHILO 1101 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102203447 / 102213251 | N/A | N | Ex Transformer / Ex connctions | N | N/A | N/A | Not A Subject Pole
F-0166 | 6 | PHILO 1101 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102213256 / 103926511 | N/A | N | Carrier poles / Ex Connections | N | N/A | N/A | Not A Subject Pole
F-0174 | Alt 2 | GARBERVILLE 1102 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 100987291 | N/A | N | Ex None Expulsion Fuse & Ex Hot Tap Clamps | N | N/A | N/A | Not A Subject Pole
F-0176 | Alt 2 | GARBERVILLE 1102 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 100987409 | N/A | N | Ex Abb & Fault Tamers & compression Clamps | N | N/A | N/A | Not A Subject Pole
F-0177 | Alt 2 | GARBERVILLE 1102 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 104032650 | N/A | N | Ex Fault Tamers & Ex Compression Clamps | N | N/A | N/A | Not A Subject Pole
F-0178 | Alt 2 | GARBERVILLE 1102 | Humboldt | North Coast | Subject Pole | Dry Fuel, Subject Pole Clearance (10 feet) | 103657498 | N/A | N | Ex Fault Tamers & Ex Compression Clamps | N | N/A | N/A | Not A Subject Pole
F-0181 | Alt 2 | GARBERVILLE 1102 | Humboldt | North Coast | Subject Pole | Radial Clearance (12 feet), Subject Pole Clearance (10 feet) | 100987246 | N/A | N | Ex Liquid Fuse & Ex Hot Tap Clamps | N | N/A | N/A | Not A Subject Pole
F-0185 | Alt 3 | WILLITS 1102 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 103803970 | L196611 | N | Pole still clear | N | N/A | N/A | Subject Pole previously cleared and still compliant
F-0186 | Alt 3 | WILLITS 1102 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102170537 | N/A | N | Not A Subject Pole | N | None | N/A | Not A Subject Pole
F-0187 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 103631950 | N/A | N | Not A Subject Pole | N | None | N/A | Not A Subject Pole
F-0190 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102208768 | N/A | N | Not A Subject Pole | N | None | N/A | Not A Subject Pole
F-0192 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 103380621 | N/A | N | Not A Subject Pole | N | None | N/A | Not A Subject Pole
F-0193 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102208830 | N/A | N | Not A Subject Pole | N | None | N/A | Not A Subject Pole
F-0194 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102208833 | N/A | N | Not A Subject Pole | N | None | N/A | Not A Subject Pole
F-0195 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102208840 | N/A | N | Not A Subject Pole | N | None | N/A | Not A Subject Pole
F-0196 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102209191 | N/A | N | Not A Subject Pole | N | None | N/A | Not A Subject Pole
F-0197 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102209113 | N/A | N | Not A Subject Pole | N | None | N/A | Not A Subject Pole
F-0198 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102209115 | N/A | N | Not A Subject Pole | N | None | N/A | Not A Subject Pole
F-0199 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102209109 | N/A | N | Not A Subject Pole | N | None | N/A | Not A Subject Pole
F-0200 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102209169 | N/A | N | Not A Subject Pole | N | None | N/A | Not A Subject Pole
F-0201 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102209165 | N/A | N | Not A Subject Pole | N | None | N/A | Not A Subject Pole
F-0202 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Radial Clearance (12 feet), Subject Pole Clearance (10 feet) | 102209187 | N/A | N | Not A Subject Pole | N | None | N/A | Not A Subject Pole
F-0203 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102209189 | N/A | N | Not A Subject Pole | N | None | N/A | Not A Subject Pole
F-0206 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102209300 | N/A | N | Not A Subject Pole | N | None | N/A | Not A Subject Pole
F-0207 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102209300 | N/A | N | exmpt liquids/exempt hot tap clamps | N | N/A | N/A | Not A Subject Pole
F-0210 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102211129 | N/A | N | exempt liquids/exempt hot tap clamps | N | N/A | N/A | Not A Subject Pole
F-0212 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 103905789 | N/A | N | exempt fault tamers/exempt hot tap clamps | N | N/A | N/A | Not A Subject Pole
F-0213 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102168668 | N/A | N | exempt fault tamers/exempt hot tap clamps | N | N/A | N/A | Not A Subject Pole
F-0214 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102211107 | N/A | N | exept liquids/exempt hot tap clamps | N | N/A | N/A | Not A Subject Pole
F-0215 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 103783234 | N/A | N | exempt fault tamers/exempt hot tap clamps | N | N/A | N/A | Not A Subject Pole
F-0216 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102209087 | N/A | N | exempt fault tamers/exempt hot tap clamps | N | N/A | N/A | Not A Subject Pole
F-0217 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Dry Fuel, Subject Pole Clearance (10 feet) | 102208906 | N/A | N | exempt non expulsion/ exempt hot taps | N | N/A | N/A | Not A Subject Pole
F-0218 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102211110 | N/A | N | exempt fault tamers/exempt hot tap clamps | N | N/A | N/A | Not A Subject Pole
F-0219 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102210785 | N/A | N | exempt/carrier pole | N | N/A | N/A | Not A Subject Pole
F-0220 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 103315036 | N/A | N | exempt fault tamers/exempt hot tap clamps | N | N/A | N/A | Not A Subject Pole
F-0221 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102211113 | N/A | N | exempt non expulsion/ exempt hot taps | N | N/A | N/A | Not A Subject Pole
F-0222 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Dry Fuel, Subject Pole Clearance (10 feet) | 102208911 | N/A | N | exempt carrier pole | N | N/A | N/A | Not A Subject Pole
F-0223 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Dry Fuel, Subject Pole Clearance (10 feet) | 102208688 | N/A | N | exempt carrier pole | N | N/A | N/A | Not A Subject Pole
F-0225 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Dry Fuel, Subject Pole Clearance (10 feet) | 103381674 | N/A | N | Fault tamers | N | N/A | N/A | Not A Subject Pole
F-0226 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102168641 | N/A | N | Ex Hot Tap And Ex Fault Tamers | N | N/A | N/A | Not A Subject Pole
F-0227 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Radial Clearance (12 feet), Subject Pole Clearance (10 feet) | 102211117 | N/A | N | Liquid Fuses | N | N/A | N/A | Not A Subject Pole
F-0228 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102211119 | N/A | N | Liquid Fuses | N | N/A | N/A | Not A Subject Pole
F-0229 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102211122 | N/A | N | Liquid Fuses | N | N/A | N/A | Not A Subject Pole
F-0230 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Dry Fuel, Subject Pole Clearance (10 feet) | 102208947 | N/A | N | Ex Hot Tap And Ex Fault Tamers | N | N/A | N/A | Not A Subject Pole
F-0231 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102211123 | N/A | N | Commpression Conn SMU 20 Fuses Fault Tamers | N | N/A | N/A | Not A Subject Pole
F-0232 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 103381673 | N/A | N | Carrier pole | N | N/A | N/A | Not A Subject Pole
F-0233 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102168654 | N/A | N | Parr Grue Conn. Liquid Fuses | N | N/A | N/A | Not A Subject Pole
F-0234 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102168645 | N/A | N | Commpression Conn. Ex Hot Taps Fault Tammers | N | N/A | N/A | Not A Subject Pole
F-0236 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 104033948 | N/A | N | Ex Hot Taps Ex ABB Arresturs Fault Tamers | N | N/A | N/A | Not A Subject Pole
F-0237 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102209053 | N/A | N | Ex Hot Taps Fault Tamers | N | N/A | N/A | Not A Subject Pole
F-0238 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102168651 | N/A | N | Ex Connectors. Liquid Fuses | N | N/A | N/A | Not A Subject Pole
F-0239 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Dry Fuel, Subject Pole Clearance (10 feet) | 102209057 | N/A | N | Fault tamers | N | N/A | N/A | Not A Subject Pole
F-0240 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Dry Fuel, Subject Pole Clearance (10 feet) | 102211042 | N/A | N | Ex Connectors | N | N/A | N/A | Not A Subject Pole
F-0241 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102211040 | N/A | N | Ex Connectors | N | N/A | N/A | Not A Subject Pole
F-0242 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Dry Fuel, Subject Pole Clearance (10 feet) | 102211035 | N/A | N | Exempt Conn. Liquid Fuses | N | N/A | N/A | Not A Subject Pole
F-0243 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102211030 | N/A | N | Exempt Hot Taps | N | N/A | N/A | Not A Subject Pole
F-0244 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102211095 | N/A | N | Fault tamers | N | N/A | N/A | Not A Subject Pole
F-0245 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 103799992 | N/A | N | Fault tamers | N | N/A | N/A | Not A Subject Pole
F-0246 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102211046 | N/A | N | Carrier pole | N | N/A | N/A | Not A Subject Pole
F-0247 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102209043 | N/A | N | Parr Grue Conn. | N | N/A | N/A | Not A Subject Pole
F-0248 | Alt 3 | WILLITS 1103 | Humboldt | North Coast | Subject Pole | Dry Fuel, Subject Pole Clearance (10 feet) | 102211058 | N/A | N | Liquid Fuses Hot tap | N | N/A | N/A | Not A Subject Pole
F-0251 | Alt 4 | MIDDLETOWN 1101 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102151767 | N/A | N | Fault tamers | N | N/A | N/A | Not A Subject Pole
F-0252 | Alt 4 | MIDDLETOWN 1101 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 103964725 | N/A | N | Fault tamers | N | N/A | N/A | Not A Subject Pole
F-0253 | Alt 4 | MIDDLETOWN 1101 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 103313394 | N/A | N | Fault tamers | N | N/A | N/A | Not A Subject Pole
F-0256 | Alt 4 | MIDDLETOWN 1101 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 103965809 | N/A | N | exempt anchor post | N | N/A | NA | Not A Subject Pole
F-0257 | Alt 4 | MIDDLETOWN 1101 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 104055022 | N/A | N | exempt service drop | N | N/A | N/A | Not A Subject Pole
F-0258 | Alt 4 | MIDDLETOWN 1101 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 103967653 | N/A | N | exempt fault tamers/hot tap clamps | N | N/A | N/A | Not A Subject Pole
F-0259 | Alt 4 | MIDDLETOWN 1101 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 103979535 | N/A | N | exempt fault tamers/hot tap clamps | N | N/A | N/A | Not A Subject Pole
F-0260 | Alt 4 | MIDDLETOWN 1101 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102166479 | N/A | N | exempt fault tamers/hot tap clamps | N | N/A | N/A | Not A Subject Pole
F-0261 | Alt 4 | MIDDLETOWN 1101 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 104014509 | N/A | N | exempt fault tamers/hot tap clamps | N | N/A | N/A | Not A Subject Pole
F-0262 | Alt 4 | MIDDLETOWN 1101 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102307512 | N/A | N | Ex smu-20 | N | N/A | N/A | Not a subject pole
F-0263 | Alt 4 | MIDDLETOWN 1101 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 104028800 | N/A | N | Ex fault tamers hot tap clamps | N | N/A | N/A | Not A Subject Pole
F-0265 | Alt 4 | MIDDLETOWN 1101 | Humboldt | North Coast | Subject Pole | Radial Clearance (12 feet), Subject Pole Clearance (10 feet) | 102166257 | N/A | N | Hot tap clamps | N | N/A | N/A | Not A Subject Pole
F-0266 | Alt 4 | MIDDLETOWN 1101 | Humboldt | North Coast | Regular | Dry Fuel | 103162945 | N/A | N | JMU 20's / Solid Blade / Fuse Saver / ABB LA's | N | N/A | N/A | Not A Subject Pole
F-0269 | Alt 4 | MIDDLETOWN 1101 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 103966921 | N/A | N | Fault tamers / ABB LA's | N | N/A | N/A | Not A Subject Pole
F-0270 | Alt 4 | MIDDLETOWN 1101 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 103967232 | N/A | N | Fault tamers | N | N/A | N/A | Not A Subject Pole
F-0271 | Alt 4 | MIDDLETOWN 1101 | Humboldt | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102166654 | N/A | N | Fault tamers | N | N/A | N/A | Not A Subject Pole
F-0001 | 1 | ANTLER 1101 | North Valley | North Valley | Subject Pole | Subject Pole Clearance (10 feet) | 101455619 | N/A | N | Exempt pole SMU20 | N | N/A | N/A | Exempt pole SMU20
F-0002 | 1 | ANTLER 1101 | North Valley | North Valley | Regular | Subject Pole Clearance (10 feet) | 103640474 | N/A | N | Exempt carrier pole | N | N/A | N/A | Exempt carrier pole
F-0003 | 1 | ANTLER 1101 | North Valley | North Valley | Subject Pole | Radial Clearance (12 feet), Subject Pole Clearance (10 feet) | 101455589 | N/A | N | Exempt pole Fault Tamers | N | N/A | N/A | Exempt pole Fault Tamers
F-0004 | 1 | ANTLER 1101 | North Valley | North Valley | Subject Pole | Subject Pole Clearance (10 feet) | 101455590 | N/A | N | Exempt pole Fault Tamers | N | N/A | N/A | Exempt pole Fault Tamers
F-0005 | 1 | ANTLER 1101 | North Valley | North Valley | Subject Pole | Subject Pole Clearance (10 feet) | 101455577 | N/A | N | Exempt carrier pole | N | N/A | N/A | Exempt carrier pole
F-0006 | 1 | ANTLER 1101 | North Valley | North Valley | Subject Pole | Subject Pole Clearance (10 feet) | 101455570 | N/A | N | Exempt pole Fault Tamers | N | N/A | N/A | Exempt pole Fault Tamers
F-0008 | 1 | ANTLER 1101 | North Valley | North Valley | Subject Pole | Subject Pole Clearance (10 feet) | 101458073 | N/A | N | Exempt pole liquid fuses and exempt hot tap clamps | N | N/A | N/A | Exempt pole liquid fuses and exempt hot tap clamps
F-0009 | 1 | ANTLER 1101 | North Valley | North Valley | Subject Pole | Subject Pole Clearance (10 feet) | 102308840 | N/A | N | Exempt carrier pole | N | N/A | N/A | Exempt carrier pole
F-0094 | 2 | GIRVAN 1102 | North Valley | North Valley | Subject Pole | Subject Pole Clearance (10 feet) | 101472595 | N/A | N | Exempt pole parallel groove connectors | N | N/A | N/A | Exempt pole parallel groove connectors
F-0095 | 2 | GIRVAN 1102 | North Valley | North Valley | Subject Pole | Subject Pole Clearance (10 feet) | 101472583 | N/A | N | Exempt pole Fault Tamers and exempt hot tap clamps | N | N/A | N/A | Exempt pole Fault Tamers and exempt hot tap clamps
F-0096 | 2 | GIRVAN 1102 | North Valley | North Valley | Subject Pole | Subject Pole Clearance (10 feet) | 101472579 | N/A | N | Exempt pole Fault Tamers and exempt hot tap clamps | N | N/A | N/A | Exempt pole Fault Tamers and exempt hot tap clamps
F-0097 | 2 | GIRVAN 1102 | North Valley | North Valley | Subject Pole | Subject Pole Clearance (10 feet) | 101472316 | N/A | N | Exempt pole parallel groove connectors | N | N/A | N/A | Exempt pole parallel groove connectors
F-0098 | 2 | GIRVAN 1102 | North Valley | North Valley | Subject Pole | Subject Pole Clearance (10 feet) | 101472274 | N/A | N | Exempt pole exempt hot tap clamps | N | N/A | N/A | Exempt pole exempt hot tap clamps
F-0099 | 2 | GIRVAN 1102 | North Valley | North Valley | Subject Pole | Subject Pole Clearance (10 feet) | 101472276 | N/A | N | Exempt pole ABB and ELF fuses | N | N/A | N/A | Exempt pole ABB and ELF fuses
F-0100 | 2 | GIRVAN 1102 | North Valley | North Valley | Subject Pole | Subject Pole Clearance (10 feet) | N/A | N/A | N | City of Redding not PG&E | N | N/A | N/A | City of Redding not PG&E
F-0102 | 2 | GIRVAN 1102 | North Valley | North Valley | Subject Pole | Subject Pole Clearance (10 feet) | 101473345 | N/A | N | Exempt pole liquid fuses | N | N/A | N/A | Exempt pole liquid fuses
F-0105 | 2 | GIRVAN 1102 | North Valley | North Valley | Subject Pole | Radial Clearance (12 feet), Subject Pole Clearance (10 feet) | 101473310 | N/A | N | Exempt pole Fault Tamers | N | N/A | N/A | Exempt pole Fault Tamers
F-0108 | 2 | GIRVAN 1102 | North Valley | North Valley | Subject Pole | Radial Clearance (12 feet), Subject Pole Clearance (10 feet) | 101473476 | L228892 | N | Universal Fuse,LA's (cleared to compliance) | N | N/A | N/A | Universal Fuse,LA's (cleared to compliance)
F-0109 | 2 | GIRVAN 1102 | North Valley | North Valley | Subject Pole | Radial Clearance (12 feet), Subject Pole Clearance (10 feet) | 101473473 | N/A | N | Exempt pole Fault Tamers and exempt hot tap clamps | N | N/A | N/A | Exempt pole Fault Tamers and exempt hot tap clamps
F-0110 | 2 | GIRVAN 1102 | North Valley | North Valley | Subject Pole | Subject Pole Clearance (10 feet) | 101473189 | N/A | N | Exempt pole ABB and Exempt Hot Tap Clamps | N | N/A | N/A | Exempt pole ABB and Exempt Hot Tap Clamps
F-0111 | 2 | GIRVAN 1102 | North Valley | North Valley | Subject Pole | Subject Pole Clearance (10 feet) | 101473217 | N/A | N | Exempt Parallel Groove Connectors | N | N/A | N/A | Exempt Parallel Groove Connectors
F-0274 | Alt 5 | ELK CREEK 1101 | North Valley | North Valley | Subject Pole | Radial Clearance (12 feet), Subject Pole Clearance (10 feet) | 100338807 | N/A | N | Liquid Filled fuses exempt from PRC 4292 | N | N/A | N/A | Pole is exempt from PRC 4292 Liquid filled fuses
F-0052 | 14 | WOODSIDE 1101 | Peninsula | Bay | Subject Pole | Subject Pole Clearance (10 feet) | 100269871 | 144239 | N | Normal Leaf Litter After 3 Months since clearing | N | Pole Re Cleared | Previously cleared | Pole had minor leaf litter
F-0057 | 14 | WOODSIDE 1101 | Peninsula | Bay | Subject Pole | Subject Pole Clearance (10 feet) | 100305827 | 144227 | N | Pole equiped with SMU-20s | N | N/A | Previously cleared | Pole Deleted from inventory
F-0059 | 14 | WOODSIDE 1101 | Peninsula | Bay | Regular | Radial Clearance (12 feet), Dry Fuel | 103805440 |  | N | Carrier pole with neither exempt or non exempt equipment | N
F-0091 | 18 | TIVY VALLEY 1107 | Fresno | Central Valley | Subject Pole | High Risk Trees in Fall Zone, Subject Pole Clearance (10 feet) | 103275176 |  |  | Access issue / Bad dog |  |  |  | Refusal customer pending refusal # as of 8/4
F-0061 | 14 | WOODSIDE 1101 | Peninsula | Bay | Subject Pole | Radial Clearance (12 feet), Subject Pole Clearance (10 feet) | 103483091 | N/A | N | Carrier Pole no Non Exempt Equiptment | N | N/A | N/A | Not a subject pole
F-0062 | 14 | WOODSIDE 1101 | Peninsula | Bay | Subject Pole | Subject Pole Clearance (10 feet) | 100269849 | N/A | N | Liquid Fuses , Exempt Hot Tap Clamps | N | N/A | N/A | Not a subject pole
F-0063 | 14 | WOODSIDE 1101 | Peninsula | Bay | Subject Pole | Subject Pole Clearance (10 feet) | 100269849 | N/A | N | SMU-20s | N | N/A | N/A | Not a subject pole
F-0064 | 14 | WOODSIDE 1101 | Peninsula | Bay | Subject Pole | Overhang Clearance (4 feet), Subject Pole Clearance (10 feet) | 103488109 | N/A | N | Carrier Pole no Non Exempt Equiptment | N | N/A | N/A | Not a subject pole
F-0065 | 14 | WOODSIDE 1101 | Peninsula | Bay | Subject Pole | Subject Pole Clearance (10 feet) | 100269844 | N/A | N | Fault Tamers | N | N/A | N/A | Not a subject pole
F-0068 | 14 | WOODSIDE 1101 | Peninsula | Bay | Subject Pole | Subject Pole Clearance (10 feet) | 100277083 | 144190 | N | Normal Regrowth | N | Pole Re cleared | Previously cleared | Pole had normal regrowth
F-0070 | 14 | WOODSIDE 1101 | Peninsula | Bay | Subject Pole | Subject Pole Clearance (10 feet) | 100277091 | N/A | N | SMU-20s | N | N/A | N/A | Not a subject pole
F-0071 | 14 | WOODSIDE 1101 | Peninsula | Bay | Subject Pole | Subject Pole Clearance (10 feet) | 100277036 | N/A | N | Fault Tamers | N | N/A | N/A | Not a subject pole
F-0072 | 14 | WOODSIDE 1101 | Peninsula | Bay | Subject Pole | Subject Pole Clearance (10 feet) | 100277038 | N/A | N | Fault Tamers | N | N/A | N/A | Not a subject pole
F-0073 | 14 | WOODSIDE 1101 | Peninsula | Bay | Subject Pole | Subject Pole Clearance (10 feet) | 100277040 | N/A | N | SMU-20s | N | N/A | N/A | Not a subject pole
F-0076 | 14 | WOODSIDE 1101 | Peninsula | Bay | Subject Pole | Subject Pole Clearance (10 feet) | 100310979 | L224752 | N | FUUN Fuses | N | Pole Re cleared | Previously cleared | Pole cleared
F-0077 | 14 | WOODSIDE 1101 | Peninsula | Bay | Subject Pole | Subject Pole Clearance (10 feet) | 100277050 | L227980 | N | Solid Blades / Split Bolts | N | N/A | N/A | Solid Blade / Split Bolts / ICA Clearing not required
F-0078 | 14 | WOODSIDE 1101 | Peninsula | Bay | Subject Pole | Radial Clearance (12 feet), Overhang Clearance (4 feet), Subject Pole Clearance (10 feet) | 100277050 | N/A | N | Compression Clamps / Parallel Groove Concectors | N | N/A | N/A | Not a subject pole
F-0079 | 14 | WOODSIDE 1101 | Peninsula | Bay | Subject Pole | Subject Pole Clearance (10 feet) | 100273559 | L224751 | N | FUUN Fuses | N | Partial clear | Partial Clear 1254 | ICA Location Partial clear 1254 Will Submit Refusal form
F-0080 | 14 | WOODSIDE 1101 | Peninsula | Bay | Subject Pole | Subject Pole Clearance (10 feet) | 100305908 | N/A | N | SMU-20s | N | N/A | N/A | Not a subject pole
F-0081 | 14 | WOODSIDE 1101 | Peninsula | Bay | Subject Pole | Subject Pole Clearance (10 feet) | 100275982 | L200981 | N | Pole replanted from inside fence | N | N/A | Prviously cleared | Previously cleared Owner replanted will submit refusal form
F-0082 | 14 | WOODSIDE 1101 | Peninsula | Bay | Subject Pole | Subject Pole Clearance (10 feet) | 1003088851 | L200982 | N | Normal Regrowth | N | Pole Re cleared | Prviously cleared | Pole had normal regrowth
F-0010 | 10 | BANGOR 1101 | Sierra | Sierra | Subject Pole | Subject Pole Clearance (10 feet) | 103676552 | N/A | N | Exempt Pole,Fault Tamers crimp connectors | N | N/A | N/A | Exempt Pole,Fault Tamers crimp connectors
F-0013 | 10 | BANGOR 1101 | Sierra | Sierra | Subject Pole | Radial Clearance (12 feet), Subject Pole Clearance (10 feet) | 101340064 | N/A | N | Exempt pole liquid fuse, Parallel Groove connectors | N | N/A | N/A | exempt pole liquid fuse, Parallel Groove connectors
F-0015 | 10 | BANGOR 1101 | Sierra | Sierra | Subject Pole | Subject Pole Clearance (10 feet) | 101288587 | N/A | N | Exempt Pole Liquid fuse,exempt hot tap clamp | N | N/A | N/A | Exempt Pole Liquid fuse,exempt hot tap clamp
F-0017 | 10 | BANGOR 1101 | Sierra | Sierra | Subject Pole | Subject Pole Clearance (10 feet) | 103794181 | N/A | N | Exempt Voltage regulator w/solid blades | N | N/A | N/A | Exempt Voltage regulator w/solid blades
F-0018 | 10 | BANGOR 1101 | Sierra | Sierra | Subject Pole | Subject Pole Clearance (10 feet) | 101336580 | N/A | N | Exempt Hot Tap Clamps | N | N/A | N/A | Exempt Hot Tap Clamps
F-0019 | 10 | BANGOR 1101 | Sierra | Sierra | Subject Pole | Subject Pole Clearance (10 feet) | 101291097 | N/A | N | Exempt Hot Tap Clamps, Fault Tamers | N | N/A | N/A | Exempt Hot Tap Clamps, Fault Tamers
F-0020 | 10 | BANGOR 1101 | Sierra | Sierra | Subject Pole | Subject Pole Clearance (10 feet) | 101291126 | N/A | N | Exempt Hot Tap Clamps, Fault Tamers | N | N/A | N/A | Exempt Hot Tap Clamps, Fault Tamers
F-0021 | 11 | COLUMBIA HILL 1101 | Sierra | Sierra | Subject Pole | Subject Pole Clearance (10 feet) | 103850166 | N/A | N | Exempt pole compression connectors | N | N/A | N/A | Exempt pole compression connectors
F-0022 | 11 | COLUMBIA HILL 1101 | Sierra | Sierra | Subject Pole | Subject Pole Clearance (10 feet) | 100000074 | N/A | N | Exempt pole liquid fuse, Parallel Groove connectors | N | N/A | N/A | Exempt pole liquid fuse, Parallel Groove connectors
F-0024 | 11 | COLUMBIA HILL 1101 | Sierra | Sierra | Subject Pole | Subject Pole Clearance (10 feet) | 100082582 | N/A | N | Exempt Pole Fault Tamers,exempt hot tap clamp | N | N/A | N/A | Exempt Pole Fault Tamers,exempt hot tap clamp
F-0025 | 11 | COLUMBIA HILL 1101 | Sierra | Sierra | Subject Pole | Subject Pole Clearance (10 feet) | 103971120 | N/A | N | Exempt pole fired wedge connector | N | N/A | N/A | Exempt pole fired wedge connector
F-0026 | 11 | COLUMBIA HILL 1101 | Sierra | Sierra | Subject Pole | Subject Pole Clearance (10 feet) | 100002269 | N/A | N | Exempt Pole Compression connectors,exempt hot tap clamp | N | N/A | N/A | Exempt Pole Compression connectors,exempt hot tap clamp
F-0027 | 11 | COLUMBIA HILL 1101 | Sierra | Sierra | Subject Pole | Subject Pole Clearance (10 feet) | 100001621 | 61393 | N | Subject pole LA's - Pole was in compliance upon arrival | N | N/A | N/A | Subject pole LA's - Pole was in compliance upon arrival
F-0028 | 11 | COLUMBIA HILL 1101 | Sierra | Sierra | Subject Pole | Subject Pole Clearance (10 feet) | 100001642 | N/A | N | Exempt Pole Fault Tamers,exempt hot tap clamp | N | N/A | N/A | Exempt Pole Fault Tamers,exempt hot tap clamp
F-0029 | 11 | COLUMBIA HILL 1101 | Sierra | Sierra | Subject Pole | Radial Clearance (12 feet), Subject Pole Clearance (10 feet) | 103894603 | N/A | N | Exempt Pole Fault Tamers | N | N/A | N/A | Exempt Pole Fault Tamers
F-0030 | 11 | COLUMBIA HILL 1101 | Sierra | Sierra | Subject Pole | Subject Pole Clearance (10 feet) | 100001623 | N/A | N | Exempt Pole exempt hot tap clamp | N | N/A | N/A | Exempt Pole exempt hot tap clamp
F-0032 | 11 | COLUMBIA HILL 1101 | Sierra | Sierra | Subject Pole | Subject Pole Clearance (10 feet) | 100001626 | N/A | N | Exempt Carrier pole | N | N/A | N/A | Exempt Carrier pole
F-0033 | 11 | COLUMBIA HILL 1101 | Sierra | Sierra | Subject Pole | Dry Fuel, Subject Pole Clearance (10 feet) | 100001631 | N/A | N | Exempt Carrier pole | N | N/A | N/A | Exempt Carrier pole
F-0034 | 11 | COLUMBIA HILL 1101 | Sierra | Sierra | Subject Pole | Dry Fuel, Subject Pole Clearance (10 feet) | 100001634 | N/A | N | Exempt Carrier pole | N | N/A | N/A | Exempt Carrier pole
F-0035 | 11 | COLUMBIA HILL 1101 | Sierra | Sierra | Subject Pole | Radial Clearance (12 feet), Dry Fuel, Subject Pole Clearance (10 feet) | 100001616 | N/A | N | Exempt Pole Fault Tamers,exempt hot tap clamp | N | N/A | N/A | Exempt Pole Fault Tamers,exempt hot tap clamp
F-0168 | 8 | GEYSERVILLE 1101 | Sonoma | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 101956816 | N/A | N | Fault tamers | N | N/A | N/A | Not A Subject Pole
F-0169 | 8 | GEYSERVILLE 1101 | Sonoma | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102036355 | N/A | N | Liquid fuse | N | N/A | N/A | Not A Subject Pole
F-0170 | 8 | GEYSERVILLE 1101 | Sonoma | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 103839048 | N/A | N | Fault tamers | N | N/A | N/A | Not A Subject Pole
F-0171 | 8 | GEYSERVILLE 1101 | Sonoma | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 103839098 | N/A | N | Fault tamers | N | N/A | N/A | Not A Subject Pole
F-0172 | 8 | GEYSERVILLE 1101 | Sonoma | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 102035568 | N/A | N | Liquid Fuse | N | N/A | N/A | Not A Subject Pole
F-0173 | 8 | GEYSERVILLE 1101 | Sonoma | North Coast | Subject Pole | Subject Pole Clearance (10 feet) | 101956926 | N/A | N | Liquid Fuse | N | N/A | N/A | Not A Subject Pole
F-0084 | 16 | OAKHURST 1101 | Yosemite | Central Valley | Subject Pole | Radial Clearance (12 feet), Overhang Clearance (4 feet), Subject Pole Clearance (10 feet) | 101027915 | N/A | N | Pole not required to prc 4292 clearing | N | N/A | N/A | No clearing required under PRC 4292 pole clearing standards
F-0085 | 16 | OAKHURST 1101 | Yosemite | Central Valley | Regular | Radial Clearance (12 feet), High Risk Trees in Fall Zone, Overhang Clearance (4 feet), Dry Fuel, | N/A | N/A | N | No subject pole in photos | N | N/A | N/A | No pole in photo provided

## Pivot
IE Findings as of 8.2.22
Region | Disagree w/ CPUC Finding | Confirm CPUC Finding | Total | Unable to Access | Awaiting Field Review | Grand Total
Region | (empty)
Bay
Central Valley |  |  |  | 2 |  | 25
North Coast |  |  |  | 1 |  | 4
North Valley | [5 empty] | 123
Sierra | [5 empty] | 22
(empty) | [5 empty] | 20
Total Result
|  |  |  | 3 |  | 194