## Dictionary
Column | Description
Outage ID | Unique event identification number
County | County
Circuit | Overhead Distribution Circuit Name
Cause | Outage Suspected Initiating Cause
3rd | Third Party
AN | Animal
CI | Company Initiated
EF | Equipment Failure
ENV | Environmental
UNK | Unknown
VEG | Vegetation
FNL_Date_Time | "First No Light"; Outage Start Day & Time
Week | Reporting Week by FNL
End_Date_Time | Outage End Day & Time
EPSS Outage Type | FTS or HLT
FTS | "Fast Trip Setting"; Post-Optimized Circuit Settings
HLT | "Hot Line Tag"; Pre-Optimized Circuit Settings
T-EPSS | "Transmission"-EPSS; EPSS outages on transmission lines
CESO | Count of Customers Experiencing Sustained Outages
Medical_Baseline | Count of Medical Baseline customer service points
Life_Support | Count of Life Support customer service points
Critical_Customer | Count of Critical Customer service points
Schools | Count of School customer service points
Hospitals | Count of Hospital customer service points
Well_Water_Dependent | Count of Well Water Depended customer service points
Customer Minutes | Sum of total outage customer minutes
CAIDI | Customer Average Interruption Duration Index, in minutes
Comments | Flag for outage data under additional review

## Summary
2022 YTD Summary
Category | Count
Medical Baseline | 55045
Life Support | 38356
Critical Customers | 14010
Hospitals | 91
Schools | 1646
Overall CAIDI | 189.4747
Restored <60 Mins | 86
Total Outages | 964
Total Customers Experiencing Outages | 852179
July 2022 Summary
Category | Count
Medical Baseline | 22734
Life Support | 15870
Critical Customers | 5453
Hospitals | 42
Schools | 604
Overall CAIDI | 180.6099
Restored <60 Mins | 42
Total Outages | 383
Total Customers Experiencing Outages | 351076

## YTD 010122_073122
Outages | County | Circuit | CPZ | Cause | FNL | Week | End Date | Restoration Time (min) | EPSS Outage Type | Customer Minutes | CESO | Medical_Baseline | Life_Support | Critical_Customer | Schools | Hospitals | Well_Water_Dependent | CAIDI
22-0016063 | Santa Barbara | SISQUOC 1102 | SISQUOC 1102M54 | Unknown | 2022-01-29 14:31 | 1/24 - 1/30 | 2022-01-29 19:15 | 284 | HLT | 24180 | 129 | 0 | 0 | 1 | 0 | 0 | 0 | 187.4419
22-0030492 | Sonoma | LAKEVILLE 1102 | LAKEVILLE 1102347280 | Unknown | 2022-03-07 06:12 | 3/7 - 3/13 | 2022-03-07 07:31 | 79 | HLT | 7663 | 97 | 2 | 1 | 1 | 0 | 0 | 2 | 79
22-0030499 | Lake | MIDDLETOWN 1101 | MIDDLETOWN 1101548 | Animal | 2022-03-07 06:38 | 3/7 - 3/13 | 2022-03-07 10:55 | 257 | FTS | 233710 | 1102 | 51 | 35 | 17 | 1 | 0 | 0 | 212.078
22-0039073 | Fresno | CANTUA 1103 | CANTUA 11039900 | 3rd Party | 2022-03-27 19:51 | 3/21 - 3/27 | 2022-03-28 16:19 | 1228 | FTS | 12596 | 17 | 0 | 0 | 1 | 0 | 0 | 0 | 740.9412
22-0043342 | San Luis Obispo | BAYWOOD 1101 | BAYWOOD 11011101/2 | Unknown | 2022-04-06 10:10 | 4/4 - 4/10 | 2022-04-06 14:31 | 261 | HLT | 75690 | 290 | 9 | 5 | 14 | 11 | 0 | 0 | 261
22-0043478 | San Luis Obispo | PERRY 1101 | PERRY 1101V88 | Equipment | 2022-04-06 12:54 | 4/4 - 4/10 | 2022-04-06 23:52 | 658 | FTS | 194376 | 740 | 25 | 18 | 15 | 2 | 0 | 0 | 262.6703
22-0043815 | San Benito | HOLLISTER 2106 | HOLLISTER 21064004 | Animal | 2022-04-07 08:57 | 4/4 - 4/10 | 2022-04-07 11:40 | 163 | HLT | 24149 | 311 | 17 | 12 | 3 | 1 | 0 | 0 | 77.6495
22-0044438 | San Luis Obispo | ATASCADERO 1103 | ATASCADERO 1103A46 | Unknown | 2022-04-08 09:59 | 4/4 - 4/10 | 2022-04-08 17:38 | 459 | FTS | 171099 | 806 | 22 | 16 | 12 | 1 | 0 | 0 | 212.2816
22-0044448 | Tehama | CORNING 1102 | CORNING 110253184 | Unknown | 2022-04-08 10:00 | 4/4 - 4/10 | 2022-04-08 14:01 | 241 | FTS | 43969 | 193 | 11 | 9 | 6 | 1 | 0 | 1 | 227.8187
22-0044741 | Santa Clara | LOS GATOS 1108 | LOS GATOS 1108LB44 | Unknown | 2022-04-08 17:29 | 4/4 - 4/10 | 2022-04-08 18:01 | 32 | FTS | 7442 | 335 | 22 | 18 | 8 | 4 | 0 | 1 | 22.2149
22-0044783 | Glenn | ELK CREEK 1101 | ELK CREEK 110137334 | Unknown | 2022-04-08 22:09 | 4/4 - 4/10 | 2022-04-09 07:50 | 581 | FTS | 63910 | 110 | 22 | 19 | 11 | 5 | 0 | 0 | 581
22-0044819 | San Luis Obispo | CUYAMA 1103 | CUYAMA 1103622728 | Animal | 2022-04-09 07:29 | 4/4 - 4/10 | 2022-04-09 16:02 | 513 | FTS | 26090 | 54 | 0 | 0 | 4 | 0 | 0 | 0 | 483.1481
22-0044917 | Shasta | JESSUP 1101 | JESSUP 11019002 | Vegetation | 2022-04-09 12:00 | 4/4 - 4/10 | 2022-04-09 15:28 | 208 | FTS | 171400 | 1791 | 170 | 120 | 19 | 4 | 0 | 0 | 95.7007
22-0045023 | Sonoma | SONOMA 1102 | SONOMA 1102441730 | Unknown | 2022-04-09 19:58 | 4/4 - 4/10 | 2022-04-10 10:28 | 870 | FTS | 100050 | 115 | 3 | 2 | 4 | 0 | 0 | 0 | 870
22-0045020 | San Luis Obispo | CAMBRIA 1102 | CAMBRIA 1102W50 | Animal | 2022-04-09 20:00 | 4/4 - 4/10 | 2022-04-09 22:38 | 158 | HLT | 97170 | 615 | 25 | 21 | 6 | 0 | 0 | 0 | 158
22-0045027 | Yolo | PUTAH CREEK 1105 | PUTAH CREEK 1105617260 | Unknown | 2022-04-09 21:12 | 4/4 - 4/10 | 2022-04-09 22:38 | 86 | HLT | 860 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 86
22-0045043 | Fresno | COALINGA NO 2 1105 | COALINGA NO 2 11059000 | Unknown | 2022-04-09 23:02 | 4/4 - 4/10 | 2022-04-10 09:24 | 622 | FTS | 14154 | 24 | 0 | 0 | 7 | 0 | 0 | 0 | 589.75
22-0045046 | Napa | SILVERADO 2102 | SILVERADO 210298998 | Unknown | 2022-04-10 00:50 | 4/4 - 4/10 | 2022-04-10 01:44 | 54 | FTS | 87966 | 1629 | 33 | 22 | 20 | 1 | 0 | 0 | 54
22-0045052 | Monterey | OTTER 1101 | OTTER 11012052 | Unknown | 2022-04-10 01:50 | 4/4 - 4/10 | 2022-04-10 06:24 | 274 | FTS | 33614 | 139 | 6 | 3 | 2 | 0 | 0 | 0 | 241.8273
22-0045060 | Sonoma | SONOMA 1105 | SONOMA 1105229588 | Vegetation | 2022-04-10 02:43 | 4/4 - 4/10 | 2022-04-10 16:00 | 797 | FTS | 99195 | 183 | 6 | 6 | 0 | 0 | 0 | 5 | 542.0492
22-0045064 | Stanislaus | WESTLEY 1103 | WESTLEY 1103237522 | 3rd Party | 2022-04-10 05:27 | 4/4 - 4/10 | 2022-04-10 16:35 | 668 | FTS | 18338 | 41 | 0 | 0 | 13 | 0 | 0 | 0 | 447.2683
22-0045065 | Yolo | MADISON 1105 | MADISON 11057712 | Unknown | 2022-04-10 06:24 | 4/4 - 4/10 | 2022-04-10 09:37 | 193 | HLT | 34412 | 188 | 6 | 6 | 2 | 0 | 0 | 0 | 183.0426
22-0045093 | Monterey | OTTER 1101 | OTTER 1101696967 | Vegetation | 2022-04-10 07:02 | 4/4 - 4/10 | 2022-04-11 01:50 | 1128 | FTS | 21869 | 73 | 4 | 2 | 2 | 0 | 0 | 0 | 299.5753
22-0045069 | Glenn | ELK CREEK 1101 | ELK CREEK 11012002 | Unknown | 2022-04-10 07:08 | 4/4 - 4/10 | 2022-04-10 17:28 | 620 | FTS | 211545 | 570 | 36 | 26 | 27 | 3 | 0 | 0 | 371.1316
22-0045080 | Yolo | MADISON 2101 | MADISON 21011606 | Animal | 2022-04-10 07:55 | 4/4 - 4/10 | 2022-04-10 13:39 | 344 | FTS | 238602 | 708 | 19 | 9 | 15 | 12 | 0 | 1 | 337.0085
22-0045364 | Glenn | LOGAN CREEK 2102 | LOGAN CREEK 21022226 | Equipment | 2022-04-11 10:38 | 4/11 - 4/17 | 2022-04-11 14:09 | 211 | FTS | 14348 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 211
22-0045651 | Tehama | RED BLUFF 1103 | RED BLUFF 11031103/2 | Vegetation | 2022-04-11 15:20 | 4/11 - 4/17 | 2022-04-11 19:44 | 264 | FTS | 587311 | 2725 | 215 | 148 | 28 | 12 | 1 | 3 | 215.527
22-0056966 | Tehama | CORNING 1102 | CORNING 110253184 | Unknown | 2022-05-02 15:13 | 5/2 - 5/8 | 2022-05-03 10:18 | 1145 | FTS | 181680 | 213 | 11 | 9 | 7 | 1 | 0 | 1 | 852.9577
22-0058047 | San Benito | HOLLISTER 2106 | HOLLISTER 21064004 | Unknown | 2022-05-04 16:31 | 5/2 - 5/8 | 2022-05-04 19:00 | 149 | FTS | 31060 | 312 | 17 | 12 | 3 | 1 | 0 | 0 | 99.5513
22-0058124 | Santa Barbara | ZACA 1102 | ZACA 1102Y02 | Unknown | 2022-05-04 21:32 | 5/2 - 5/8 | 2022-05-04 22:34 | 62 | FTS | 24944 | 547 | 17 | 8 | 9 | 1 | 0 | 1 | 45.6015
22-0058838 | Monterey | JOLON 1103 | JOLON 11031103/2 | Unknown | 2022-05-06 08:49 | 5/2 - 5/8 | 2022-05-06 11:49 | 180 | FTS | 3600 | 20 | 0 | 0 | 15 | 0 | 0 | 0 | 180
22-0059159 | San Luis Obispo | CHOLAME 2102 | CHOLAME 2102X16 | Animal | 2022-05-06 17:45 | 5/2 - 5/8 | 2022-05-07 00:30 | 405 | FTS | 63473 | 285 | 8 | 4 | 15 | 2 | 0 | 0 | 222.7123
22-0059214 | San Luis Obispo | OILFIELDS 1103 | OILFIELDS 1103N44 | Unknown | 2022-05-07 05:47 | 5/2 - 5/8 | 2022-05-07 07:13 | 86 | FTS | 45928 | 1186 | 28 | 16 | 25 | 1 | 0 | 2 | 38.7251
22-0060384 | Yuba | SMARTVILLE SUB | N/A | Equipment | 2022-05-10 15:51 | 5/9 - 5/15 | 2022-05-10 17:44 | 113 | T-EPSS | 30623 | 271 | 23 | 18 | 13 | 0 | 0 | 1 | 113
22-0060412 | Napa | CALISTOGA SUB | N/A | Equipment | 2022-05-10 17:40 | 5/9 - 5/15 | 2022-05-10 20:01 | 141 | T-EPSS | 522092 | 3810 | 126 | 84 | 53 | 6 | 0 | 7 | 137.032
22-0060483 | Fresno | COPPERMINE 1104 | COPPERMINE 1104556430 | Equipment | 2022-05-11 03:44 | 5/9 - 5/15 | 2022-05-11 09:34 | 350 | FTS | 37100 | 106 | 9 | 9 | 0 | 0 | 0 | 0 | 350
22-0060954 | Fresno | TIVY VALLEY 1107 | TIVY VALLEY 1107584840 | Unknown | 2022-05-11 17:11 | 5/9 - 5/15 | 2022-05-11 19:51 | 160 | FTS | 83200 | 520 | 49 | 30 | 3 | 0 | 0 | 0 | 160
22-0060977 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113A70 | Unknown | 2022-05-11 18:25 | 5/9 - 5/15 | 2022-05-12 02:05 | 460 | FTS | 759076 | 1706 | 90 | 68 | 19 | 2 | 0 | 12 | 444.9449
22-0061063 | Fresno | COPPERMINE 1104 | COPPERMINE 1104556430 | Equipment | 2022-05-12 02:25 | 5/9 - 5/15 | 2022-05-12 09:24 | 419 | FTS | 44414 | 106 | 9 | 9 | 0 | 0 | 0 | 0 | 419
22-0061525 | Monterey | KING CITY 1103 | KING CITY 11037038 | Animal | 2022-05-12 17:37 | 5/9 - 5/15 | 2022-05-13 11:11 | 1054 | FTS | 264244 | 794 | 52 | 39 | 15 | 0 | 0 | 0 | 332.801
22-0062027 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113A08 | Animal | 2022-05-14 05:43 | 5/9 - 5/15 | 2022-05-14 08:44 | 181 | FTS | 166477 | 927 | 63 | 42 | 19 | 0 | 0 | 8 | 179.5868
22-0062145 | San Luis Obispo | SAN LUIS OBISPO 1107 | SAN LUIS OBISPO 1107V18 | Unknown | 2022-05-14 14:47 | 5/9 - 5/15 | 2022-05-14 16:13 | 86 | FTS | 89698 | 1043 | 38 | 25 | 10 | 0 | 0 | 0 | 86
22-0062248 | Contra Costa | KIRKER 2104 | KIRKER 21042104/2 | Animal | 2022-05-15 17:29 | 5/9 - 5/15 | 2022-05-15 22:14 | 285 | FTS | 992190 | 5094 | 451 | 288 | 42 | 9 | 0 | 0 | 194.7762
22-0062247 | Calaveras | STANISLAUS 1701 | STANISLAUS 17017144 | Equipment | 2022-05-15 17:45 | 5/9 - 5/15 | 2022-05-16 11:59 | 1094 | FTS | 435033 | 893 | 58 | 38 | 16 | 0 | 0 | 0 | 487.159
22-0062303 | San Luis Obispo | OCEANO 1104 | OCEANO 1104Q12 | Company Initiated | 2022-05-16 05:49 | 5/16 - 5/22 | 2022-05-16 06:54 | 65 | HLT | 11180 | 172 | 11 | 11 | 2 | 0 | 0 | 1 | 65
22-0062392 | Madera | COARSEGOLD 2104 | COARSEGOLD 21042104/2 | Company Initiated | 2022-05-16 09:42 | 5/16 - 5/22 | 2022-05-16 11:28 | 106 | FTS | 429158 | 4382 | 483 | 350 | 82 | 9 | 0 | 0 | 97.9366
22-0062558 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 21012181 | 3rd Party | 2022-05-16 14:21 | 5/16 - 5/22 | 2022-05-17 17:25 | 1624 | FTS | 10640 | 50 | 0 | 0 | 2 | 0 | 0 | 0 | 212.8
22-0062673 | Tulare | DUNLAP 1102 | DUNLAP 11027290 | Equipment | 2022-05-16 18:22 | 5/16 - 5/22 | 2022-05-17 19:00 | 1478 | FTS | 66448 | 57 | 0 | 0 | 5 | 0 | 0 | 0 | 1165.7544
22-0062695 | Yolo | MADISON 2101 | MADISON 210189332 | Unknown | 2022-05-17 03:47 | 5/16 - 5/22 | 2022-05-17 11:24 | 457 | FTS | 321345 | 711 | 19 | 9 | 15 | 12 | 0 | 1 | 451.962
22-0063174 | Yolo | PUTAH CREEK 1105 | PUTAH CREEK 1105617260 | Equipment | 2022-05-18 06:15 | 5/16 - 5/22 | 2022-05-18 08:20 | 125 | FTS | 1250 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 125
22-0063281 | Yolo | PUTAH CREEK 1105 | PUTAH CREEK 1105617260 | Equipment | 2022-05-18 09:19 | 5/16 - 5/22 | 2022-05-18 10:40 | 81 | FTS | 810 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 81
22-0063323 | Nevada | COLUMBIA HILL 1101 | COLUMBIA HILL 1101764 | Vegetation | 2022-05-18 10:05 | 5/16 - 5/22 | 2022-05-18 19:45 | 580 | FTS | 25928 | 260 | 41 | 36 | 3 | 2 | 0 | 3 | 99.7231
22-0063544 | Tuolumne | MIWUK 1701 | MIWUK 1701953336 | Equipment | 2022-05-18 14:14 | 5/16 - 5/22 | 2022-05-18 19:24 | 310 | FTS | 282972 | 920 | 51 | 38 | 11 | 1 | 0 | 0 | 307.5783
22-0063756 | Napa | SILVERADO 2104 | SILVERADO 2104708 | Vegetation | 2022-05-19 01:46 | 5/16 - 5/22 | 2022-05-19 14:27 | 761 | FTS | 1362451 | 2374 | 107 | 67 | 63 | 9 | 20 | 4 | 573.9052
22-0063764 | El Dorado | SHINGLE SPRINGS 2108 | SHINGLE SPRINGS 210819622 | Animal | 2022-05-19 05:42 | 5/16 - 5/22 | 2022-05-19 10:14 | 272 | FTS | 724441 | 2882 | 238 | 159 | 33 | 3 | 0 | 0 | 251.3675
22-0063773 | Glenn | LOGAN CREEK 2102 | LOGAN CREEK 21022428 | Equipment | 2022-05-19 06:04 | 5/16 - 5/22 | 2022-05-19 09:01 | 177 | FTS | 24072 | 136 | 3 | 3 | 0 | 0 | 0 | 0 | 177
22-0063807 | Sonoma | MONTE RIO 1113 | MONTE RIO 1113346 | Animal | 2022-05-19 07:32 | 5/16 - 5/22 | 2022-05-19 13:48 | 376 | FTS | 67360 | 517 | 36 | 22 | 15 | 5 | 0 | 0 | 130.2901
22-0063872 | El Dorado | DIAMOND SPRINGS 1105 | DIAMOND SPRINGS 11052102 | Unknown | 2022-05-19 09:01 | 5/16 - 5/22 | 2022-05-19 11:08 | 127 | FTS | 117457 | 1091 | 98 | 51 | 24 | 7 | 0 | 2 | 107.6599
22-0064081 | Yolo | MADISON 2101 | MADISON 210189332 | 3rd Party | 2022-05-19 14:25 | 5/16 - 5/22 | 2022-05-20 11:18 | 1253 | FTS | 1366043 | 2088 | 106 | 73 | 47 | 26 | 0 | 2 | 654.2352
22-0064119 | Napa | MONTICELLO 1101 | MONTICELLO 110193384 | 3rd Party | 2022-05-19 15:08 | 5/16 - 5/22 | 2022-05-20 02:47 | 699 | FTS | 286786 | 1243 | 61 | 42 | 22 | 1 | 0 | 3 | 230.7208
22-0064127 | Butte | ORO FINO 1101 | ORO FINO 11011101/2 | Animal | 2022-05-19 15:17 | 5/16 - 5/22 | 2022-05-19 18:23 | 186 | FTS | 257544 | 2379 | 280 | 209 | 19 | 1 | 0 | 0 | 108.2573
22-0064197 | Monterey | SAN ARDO 1101 | SAN ARDO 11017632 | Unknown | 2022-05-19 17:29 | 5/16 - 5/22 | 2022-05-19 19:33 | 124 | FTS | 2492 | 24 | 0 | 0 | 2 | 0 | 0 | 0 | 103.8333
22-0064204 | Tehama | RED BLUFF 1104 | RED BLUFF 11041302 | Unknown | 2022-05-19 17:45 | 5/16 - 5/22 | 2022-05-20 10:47 | 1022 | FTS | 390795 | 896 | 79 | 47 | 18 | 1 | 0 | 1 | 436.1551
22-0064235 | San Luis Obispo | TEMPLETON 2110 | TEMPLETON 2110901690 | Equipment | 2022-05-19 21:20 | 5/16 - 5/22 | 2022-05-20 12:46 | 926 | FTS | 248602 | 287 | 7 | 7 | 5 | 0 | 0 | 9 | 866.2091
22-0064261 | Tehama | GERBER 1102 | GERBER 11021560 | Animal | 2022-05-19 23:33 | 5/16 - 5/22 | 2022-05-20 01:59 | 146 | FTS | 18980 | 130 | 2 | 1 | 1 | 0 | 0 | 0 | 146
22-0064263 | Glenn | LOGAN CREEK 2102 | LOGAN CREEK 210262032 | Equipment | 2022-05-20 00:15 | 5/16 - 5/22 | 2022-05-20 09:07 | 532 | FTS | 28452 | 81 | 0 | 0 | 6 | 0 | 0 | 0 | 351.2593
22-0064267 | Glenn | LOGAN CREEK 2102 | LOGAN CREEK 210237316 | Unknown | 2022-05-20 01:27 | 5/16 - 5/22 | 2022-05-20 03:56 | 149 | FTS | 49021 | 329 | 1 | 1 | 9 | 2 | 0 | 0 | 149
22-0064270 | San Luis Obispo | SAN LUIS OBISPO 1107 | SAN LUIS OBISPO 1107V18 | Equipment | 2022-05-20 02:04 | 5/16 - 5/22 | 2022-05-20 03:27 | 83 | FTS | 46633 | 1043 | 38 | 25 | 10 | 0 | 0 | 0 | 44.7105
22-0064276 | Nevada | COLUMBIA HILL 1101 | COLUMBIA HILL 1101764 | Vegetation | 2022-05-20 04:12 | 5/16 - 5/22 | 2022-05-20 07:39 | 207 | FTS | 51964 | 260 | 41 | 36 | 3 | 2 | 0 | 3 | 199.8615
22-0064281 | Yuba | PIKE CITY 1101 | PIKE CITY 11011730 | Vegetation | 2022-05-20 05:12 | 5/16 - 5/22 | 2022-05-22 14:07 | 3415 | FTS | 176461 | 139 | 24 | 17 | 2 | 0 | 0 | 0 | 1269.5036
22-0064282 | Placer | LINCOLN 1104 | LINCOLN 110451756 | Unknown | 2022-05-20 05:17 | 5/16 - 5/22 | 2022-05-20 11:25 | 368 | FTS | 104281 | 431 | 32 | 22 | 4 | 0 | 0 | 1 | 241.9513
22-0064294 | Tehama | RAWSON 1103 | RAWSON 11033314 | Vegetation | 2022-05-20 06:16 | 5/16 - 5/22 | 2022-05-20 09:33 | 197 | FTS | 113348 | 705 | 57 | 42 | 12 | 9 | 0 | 0 | 160.7773
22-0064297 | Butte | KANAKA 1101 | KANAKA 1101LR1101/2 | Unknown | 2022-05-20 06:22 | 5/16 - 5/22 | 2022-05-20 14:19 | 477 | FTS | 156651 | 538 | 42 | 30 | 17 | 0 | 0 | 0 | 291.1729
22-0064305 | Placer | HALSEY 1102 | HALSEY 110239104 | Vegetation | 2022-05-20 06:42 | 5/16 - 5/22 | 2022-05-20 10:31 | 229 | FTS | 205642 | 898 | 72 | 48 | 20 | 7 | 0 | 11 | 229
22-0064309 | Shasta | GIRVAN 1101 | GIRVAN 11011330 | Unknown | 2022-05-20 07:00 | 5/16 - 5/22 | 2022-05-20 12:01 | 301 | FTS | 216130 | 1170 | 90 | 61 | 30 | 6 | 0 | 0 | 184.7265
22-0064314 | Glenn | ELK CREEK 1101 | ELK CREEK 11012002 | Equipment | 2022-05-20 07:12 | 5/16 - 5/22 | 2022-05-20 14:10 | 418 | FTS | 169169 | 570 | 36 | 26 | 27 | 3 | 0 | 0 | 296.7877
22-0064315 | Tehama | CORNING 1102 | CORNING 11021622 | Unknown | 2022-05-20 07:12 | 5/16 - 5/22 | 2022-05-20 11:38 | 266 | FTS | 53634 | 213 | 11 | 9 | 7 | 1 | 0 | 1 | 251.8028
22-0064321 | Yolo | PUTAH CREEK 1105 | PUTAH CREEK 1105617260 | Vegetation | 2022-05-20 07:42 | 5/16 - 5/22 | 2022-05-20 18:58 | 676 | FTS | 6760 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 676
22-0064465 | Santa Barbara | SANTA YNEZ 1102 | SANTA YNEZ 1102Y18 | Unknown | 2022-05-20 09:46 | 5/16 - 5/22 | 2022-05-20 12:26 | 160 | FTS | 53064 | 537 | 16 | 7 | 15 | 0 | 0 | 0 | 98.8156
22-0064555 | Butte | PARADISE 1106 | PARADISE 110636042 | 3rd Party | 2022-05-20 11:58 | 5/16 - 5/22 | 2022-05-20 12:58 | 60 | FTS | 18180 | 303 | 15 | 11 | 7 | 0 | 0 | 0 | 60
22-0064669 | San Luis Obispo | TEMPLETON 2111 | TEMPLETON 2111A66 | Equipment | 2022-05-20 13:16 | 5/16 - 5/22 | 2022-05-21 00:31 | 675 | FTS | 177825 | 977 | 71 | 37 | 20 | 4 | 0 | 1 | 182.0113
22-0064615 | Napa | SILVERADO 2102 | SILVERADO 210298998 | Equipment | 2022-05-20 13:49 | 5/16 - 5/22 | 2022-05-20 22:05 | 496 | FTS | 43358 | 278 | 1 | 1 | 7 | 0 | 0 | 0 | 155.964
22-0064715 | Sonoma | DUNBAR 1101 | DUNBAR 1101440 | Unknown | 2022-05-20 19:17 | 5/16 - 5/22 | 2022-05-20 21:55 | 158 | FTS | 9480 | 60 | 89 | 51 | 33 | 5 | 0 | 8 | 158
22-0064739 | El Dorado | SHINGLE SPRINGS 2108 | SHINGLE SPRINGS 210819622 | Unknown | 2022-05-20 23:37 | 5/16 - 5/22 | 2022-05-21 01:35 | 118 | FTS | 226560 | 1920 | 165 | 111 | 16 | 1 | 0 | 0 | 118
22-0064742 | San Luis Obispo | SAN LUIS OBISPO 1107 | SAN LUIS OBISPO 1107V18 | Equipment | 2022-05-21 01:59 | 5/16 - 5/22 | 2022-05-21 02:55 | 56 | FTS | 58408 | 1043 | 38 | 25 | 10 | 0 | 0 | 0 | 56
22-0064749 | Calaveras | CORRAL 1101 | CORRAL 110136652 | Unknown | 2022-05-21 05:30 | 5/16 - 5/22 | 2022-05-21 10:37 | 307 | FTS | 118732 | 442 | 46 | 29 | 3 | 0 | 0 | 2 | 268.6244
22-0064753 | Placer | WISE 1101 | WISE 11011404 | Animal | 2022-05-21 06:01 | 5/16 - 5/22 | 2022-05-21 09:16 | 195 | FTS | 128895 | 661 | 53 | 34 | 10 | 0 | 0 | 1 | 195
22-0064824 | Butte | BIG BEND 1102 | BIG BEND 11021102/2 | Unknown | 2022-05-21 11:34 | 5/16 - 5/22 | 2022-05-21 17:11 | 337 | FTS | 65383 | 202 | 8 | 4 | 11 | 0 | 0 | 0 | 323.6782
22-0064838 | El Dorado | MOUNTAIN QUARRIES 2101 | MOUNTAIN QUARRIES 210135466 | Unknown | 2022-05-21 11:59 | 5/16 - 5/22 | 2022-05-21 18:08 | 369 | FTS | 145611 | 527 | 45 | 28 | 8 | 0 | 0 | 1 | 276.3017
22-0064843 | Nevada | NARROWS 2105 | NARROWS 21052748 | Animal | 2022-05-21 12:30 | 5/16 - 5/22 | 2022-05-21 18:30 | 360 | FTS | 322560 | 896 | 239 | 139 | 36 | 4 | 0 | 23 | 360
22-0064884 | Butte | CLARK ROAD 1102 | CLARK ROAD 1102212118 | Unknown | 2022-05-21 16:42 | 5/16 - 5/22 | 2022-05-21 17:45 | 63 | FTS | 4221 | 67 | 3 | 2 | 6 | 2 | 0 | 0 | 63
22-0064926 | Tehama | COTTONWOOD 1101 | COTTONWOOD 11011610 | Unknown | 2022-05-22 05:30 | 5/16 - 5/22 | 2022-05-22 09:39 | 249 | FTS | 54531 | 219 | 25 | 16 | 4 | 0 | 0 | 0 | 249
22-0064964 | Santa Clara | LOS GATOS 1106 | LOS GATOS 1106LB44 | Unknown | 2022-05-22 15:34 | 5/16 - 5/22 | 2022-05-22 18:03 | 149 | FTS | 35304 | 336 | 22 | 18 | 8 | 4 | 0 | 1 | 105.0714
22-0064977 | Napa | SILVERADO 2102 | SILVERADO 210258626 | Unknown | 2022-05-22 18:25 | 5/16 - 5/22 | 2022-05-23 10:50 | 985 | FTS | 103415 | 335 | 3 | 3 | 5 | 0 | 0 | 2 | 308.7015
22-0065052 | Santa Cruz | CAMP EVERS 2105 | CAMP EVERS 21055188 | Unknown | 2022-05-23 00:50 | 5/23 - 5/29 | 2022-05-23 03:12 | 142 | FTS | 2840 | 20 | 2 | 2 | 0 | 0 | 0 | 0 | 142
22-0065063 | Sonoma | MONTE RIO 1111 | MONTE RIO 111164758 | Unknown | 2022-05-23 05:41 | 5/23 - 5/29 | 2022-05-23 10:00 | 259 | FTS | 40303 | 283 | 16 | 10 | 9 | 1 | 0 | 0 | 142.4134
22-0065111 | San Luis Obispo | ATASCADERO 1101 | ATASCADERO 11011101/2 | Unknown | 2022-05-23 08:31 | 5/23 - 5/29 | 2022-05-23 10:07 | 96 | FTS | 237912 | 3458 | 187 | 113 | 28 | 6 | 0 | 2 | 68.8005
22-0065144 | Butte | PARADISE 1104 | PARADISE 11041104/2 | Unknown | 2022-05-23 08:59 | 5/23 - 5/29 | 2022-05-23 11:27 | 148 | FTS | 188772 | 2256 | 164 | 107 | 41 | 1 | 0 | 0 | 83.6755
22-0065198 | Santa Barbara | SANTA YNEZ 1104 | SANTA YNEZ 110477098 | Company Initiated | 2022-05-23 11:01 | 5/23 - 5/29 | 2022-05-23 13:13 | 132 | FTS | 18216 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 132
22-0065214 | Solano | VACA DIXON 1105 | VACA DIXON 110540092 | 3rd Party | 2022-05-23 11:43 | 5/23 - 5/29 | 2022-05-23 21:23 | 580 | FTS | 102522 | 1412 | 146 | 108 | 20 | 0 | 0 | 9 | 72.6076
22-0065221 | Placer | PENRYN 1103 | PENRYN 1103604 | Vegetation | 2022-05-23 11:50 | 5/23 - 5/29 | 2022-05-23 16:43 | 293 | FTS | 52009 | 329 | 15 | 8 | 3 | 0 | 0 | 5 | 158.0821
22-0065293 | Nevada | NARROWS 2105 | NARROWS 21052748 | Vegetation | 2022-05-23 13:49 | 5/23 - 5/29 | 2022-05-23 20:23 | 394 | FTS | 893409 | 3002 | 239 | 139 | 36 | 4 | 0 | 23 | 297.6046
22-0065363 | Santa Cruz | CAMP EVERS 2106 | CAMP EVERS 21065020 | Unknown | 2022-05-23 15:27 | 5/23 - 5/29 | 2022-05-23 20:14 | 287 | FTS | 70085 | 292 | 19 | 14 | 3 | 0 | 0 | 2 | 240.0171
22-0065369 | Santa Cruz | CAMP EVERS 2106 | CAMP EVERS 210637210 | 3rd Party | 2022-05-23 15:27 | 5/23 - 5/29 | 2022-05-23 16:36 | 69 | FTS | 9798 | 142 | 16 | 13 | 2 | 0 | 0 | 2 | 69
22-0065403 | Napa | SILVERADO 2102 | SILVERADO 2102636 | Equipment | 2022-05-23 17:17 | 5/23 - 5/29 | 2022-05-23 23:38 | 381 | FTS | 27891 | 132 | 2 | 2 | 5 | 0 | 0 | 0 | 211.2955
22-0065431 | Sonoma | GEYSERVILLE 1101 | GEYSERVILLE 110137454 | Unknown | 2022-05-23 18:25 | 5/23 - 5/29 | 2022-05-24 10:43 | 978 | FTS | 70116 | 120 | 3 | 2 | 1 | 0 | 0 | 1 | 584.3
22-0065428 | Solano | JAMESON 1102 | JAMESON 11028842 | Unknown | 2022-05-23 19:18 | 5/23 - 5/29 | 2022-05-24 10:32 | 914 | FTS | 206694 | 783 | 72 | 52 | 22 | 0 | 0 | 2 | 263.977
22-0065426 | Madera | OAKHURST 1101 | OAKHURST 1101636114 | Vegetation | 2022-05-23 19:21 | 5/23 - 5/29 | 2022-05-24 04:16 | 535 | FTS | 503732 | 1550 | 175 | 128 | 31 | 2 | 0 | 0 | 324.9884
22-0065468 | Nevada | COLUMBIA HILL 1101 | COLUMBIA HILL 110190730 | Equipment | 2022-05-23 22:50 | 5/23 - 5/29 | 2022-05-25 15:01 | 2411 | FTS | 62009 | 87 | 2 | 2 | 1 | 0 | 0 | 0 | 712.7471
22-0065470 | Nevada | NARROWS 2102 | NARROWS 210248484 | Equipment | 2022-05-23 23:14 | 5/23 - 5/29 | 2022-05-24 17:26 | 1092 | FTS | 712544 | 890 | 56 | 33 | 20 | 7 | 0 | 11 | 800.6112
22-0065485 | San Luis Obispo | SAN MIGUEL 1106 | SAN MIGUEL 1106428314 | 3rd Party | 2022-05-24 05:09 | 5/23 - 5/29 | 2022-05-24 11:51 | 402 | FTS | 23718 | 59 | 1 | 0 | 1 | 0 | 0 | 0 | 402
22-0065486 | Yuba | WHEATLAND 1105 | WHEATLAND 1105248490 | Unknown | 2022-05-24 05:30 | 5/23 - 5/29 | 2022-05-24 11:01 | 331 | FTS | 109942 | 394 | 24 | 16 | 8 | 0 | 0 | 4 | 279.0406
22-0065585 | Placer | WISE 1102 | WISE 1102697216 | Unknown | 2022-05-24 08:52 | 5/23 - 5/29 | 2022-05-24 13:35 | 283 | FTS | 62260 | 220 | 14 | 11 | 0 | 0 | 0 | 4 | 283
22-0065606 | Marin | ALTO 1124 | ALTO 1124884949 | Unknown | 2022-05-24 09:41 | 5/23 - 5/29 | 2022-05-24 10:56 | 75 | FTS | 3000 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 75
22-0065642 | Santa Clara | MORGAN HILL 2104 | MORGAN HILL 2104152774 | Unknown | 2022-05-24 11:02 | 5/23 - 5/29 | 2022-05-24 15:41 | 279 | FTS | 69537 | 385 | 25 | 17 | 10 | 0 | 0 | 0 | 180.6156
22-0065722 | Marin | ALTO 1125 | ALTO 1125296476 | Unknown | 2022-05-24 13:04 | 5/23 - 5/29 | 2022-05-24 14:00 | 56 | FTS | 4816 | 86 | 6 | 6 | 1 | 0 | 0 | 0 | 56
22-0065746 | Mariposa | MARIPOSA 2101 | MARIPOSA 210110990 | Unknown | 2022-05-24 13:22 | 5/23 - 5/29 | 2022-05-24 18:07 | 285 | FTS | 139194 | 526 | 50 | 41 | 4 | 0 | 0 | 0 | 264.6274
22-0065747 | Mariposa | MARIPOSA 2101 | MARIPOSA 210110170 | Unknown | 2022-05-24 13:22 | 5/23 - 5/29 | 2022-05-24 17:19 | 237 | FTS | 53088 | 224 | 15 | 6 | 7 | 0 | 0 | 0 | 237
22-0065768 | Shasta | DESCHUTES 1104 | DESCHUTES 11049726 | Equipment | 2022-05-24 13:42 | 5/23 - 5/29 | 2022-05-24 22:24 | 522 | FTS | 42963 | 269 | 27 | 19 | 3 | 0 | 0 | 0 | 159.7138
22-0065898 | Tuolumne | MIWUK 1702 | MIWUK 1702823548 | Equipment | 2022-05-24 16:18 | 5/23 - 5/29 | 2022-05-24 21:21 | 303 | FTS | 96063 | 841 | 66 | 49 | 12 | 0 | 0 | 0 | 114.2247
22-0065921 | Lake | MIDDLETOWN 1102 | MIDDLETOWN 1102514 | Equipment | 2022-05-24 17:37 | 5/23 - 5/29 | 2022-05-24 22:28 | 291 | FTS | 34666 | 494 | 41 | 30 | 3 | 0 | 0 | 0 | 70.1741
22-0065935 | Sonoma | GEYSERVILLE 1101 | GEYSERVILLE 110137454 | Unknown | 2022-05-24 18:25 | 5/23 - 5/29 | 2022-05-24 20:40 | 135 | FTS | 12247 | 120 | 3 | 2 | 1 | 0 | 0 | 1 | 102.0583
22-0065938 | Sonoma | FITCH MOUNTAIN 1113 | FITCH MOUNTAIN 111324550 | Unknown | 2022-05-24 19:04 | 5/23 - 5/29 | 2022-05-25 09:31 | 867 | FTS | 191607 | 221 | 6 | 4 | 7 | 0 | 0 | 2 | 867
22-0065946 | Santa Clara | LLAGAS 2101 | LLAGAS 2101XR584 | Equipment | 2022-05-24 20:03 | 5/23 - 5/29 | 2022-05-25 01:14 | 311 | FTS | 23276 | 243 | 11 | 10 | 3 | 0 | 0 | 0 | 95.786
22-0065948 | Amador | ELECTRA 1101 | ELECTRA 11017104 | Unknown | 2022-05-24 20:13 | 5/23 - 5/29 | 2022-05-24 22:53 | 160 | FTS | 99680 | 623 | 63 | 41 | 7 | 0 | 0 | 1 | 160
22-0066064 | Butte | WYANDOTTE 1109 | WYANDOTTE 110913052 | Unknown | 2022-05-25 07:41 | 5/23 - 5/29 | 2022-05-25 11:11 | 210 | FTS | 51801 | 345 | 31 | 24 | 2 | 0 | 0 | 1 | 150.1478
22-0066107 | Monterey | SOLEDAD 2102 | SOLEDAD 21027008 | Animal | 2022-05-25 08:41 | 5/23 - 5/29 | 2022-05-25 10:55 | 134 | FTS | 12730 | 95 | 0 | 0 | 5 | 0 | 0 | 0 | 134
22-0066118 | Sonoma | SONOMA 1102 | SONOMA 1102441730 | Unknown | 2022-05-25 08:45 | 5/23 - 5/29 | 2022-05-25 10:54 | 129 | FTS | 14835 | 115 | 3 | 2 | 4 | 0 | 0 | 0 | 129
22-0066119 | Santa Clara | HICKS 2101 | HICKS 2101XR162 | Unknown | 2022-05-25 08:50 | 5/23 - 5/29 | 2022-05-25 13:48 | 298 | FTS | 432067 | 1549 | 94 | 68 | 23 | 3 | 0 | 0 | 278.9329
22-0066148 | Napa | CALISTOGA 1102 | CALISTOGA 11021102/2 | Company Initiated | 2022-05-25 09:25 | 5/23 - 5/29 | 2022-05-25 15:13 | 348 | FTS | 457221 | 2156 | 64 | 40 | 31 | 6 | 0 | 1 | 212.0691
22-0066191 | Santa Clara | MORGAN HILL 2111 | MORGAN HILL 2111997000 | Equipment | 2022-05-25 10:15 | 5/23 - 5/29 | 2022-05-26 01:52 | 937 | FTS | 119679 | 397 | 18 | 9 | 4 | 0 | 0 | 0 | 301.4584
22-0066239 | Sonoma | FITCH MOUNTAIN 1113 | FITCH MOUNTAIN 111324550 | Vegetation | 2022-05-25 11:21 | 5/23 - 5/29 | 2022-05-25 12:53 | 92 | FTS | 20240 | 220 | 6 | 4 | 7 | 0 | 0 | 2 | 92
22-0066309 | Napa | PUEBLO 2104 | PUEBLO 2104378860 | Company Initiated | 2022-05-25 13:16 | 5/23 - 5/29 | 2022-05-25 15:58 | 162 | FTS | 57024 | 352 | 7 | 4 | 5 | 1 | 0 | 3 | 162
22-0066356 | Santa Clara | HICKS 2101 | HICKS 2101XR250 | Unknown | 2022-05-25 13:50 | 5/23 - 5/29 | 2022-05-25 14:28 | 38 | FTS | 115048 | 3154 | 178 | 121 | 51 | 9 | 0 | 0 | 36.4769
22-0066368 | Amador | CLAY 1101 | CLAY 110184572 | Equipment | 2022-05-25 14:16 | 5/23 - 5/29 | 2022-05-26 00:01 | 585 | FTS | 22266 | 298 | 22 | 13 | 6 | 2 | 0 | 0 | 74.7181
22-0066401 | Sonoma | GEYSERVILLE 1101 | GEYSERVILLE 110137454 | Unknown | 2022-05-25 14:19 | 5/23 - 5/29 | 2022-05-25 15:57 | 98 | FTS | 11023 | 120 | 3 | 2 | 1 | 0 | 0 | 1 | 91.8583
22-0066386 | Shasta | PANORAMA 1102 | PANORAMA 11021526 | Unknown | 2022-05-25 14:41 | 5/23 - 5/29 | 2022-05-25 16:45 | 124 | FTS | 12658 | 103 | 8 | 7 | 2 | 0 | 0 | 0 | 122.8932
22-0066516 | Sonoma | FITCH MOUNTAIN 1113 | FITCH MOUNTAIN 1113356 | Vegetation | 2022-05-25 18:13 | 5/23 - 5/29 | 2022-05-26 02:55 | 522 | FTS | 29406 | 318 | 6 | 3 | 4 | 0 | 0 | 1 | 92.4717
22-0066530 | Napa | CALISTOGA 1102 | CALISTOGA 11021102/2 | Company Initiated | 2022-05-25 18:59 | 5/23 - 5/29 | 2022-05-25 20:27 | 88 | FTS | 114112 | 2156 | 64 | 40 | 31 | 6 | 0 | 1 | 52.9276
22-0066580 | Napa | SILVERADO 2104 | SILVERADO 2104632 | Unknown | 2022-05-25 22:35 | 5/23 - 5/29 | 2022-05-26 01:58 | 203 | FTS | 149323 | 741 | 33 | 20 | 17 | 3 | 0 | 1 | 201.5155
22-0066612 | Yolo | MADISON 2101 | MADISON 2101888814 | Unknown | 2022-05-26 05:26 | 5/23 - 5/29 | 2022-05-26 05:42 | 16 | FTS | 16 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 16
22-0066639 | Monterey | JOLON 1103 | JOLON 11031103/2 | Unknown | 2022-05-26 06:51 | 5/23 - 5/29 | 2022-05-26 13:10 | 379 | FTS | 5532 | 20 | 0 | 0 | 15 | 0 | 0 | 0 | 276.6
22-0066890 | Yolo | MADISON 2101 | MADISON 21011606 | Unknown | 2022-05-26 11:23 | 5/23 - 5/29 | 2022-05-26 15:38 | 255 | FTS | 130560 | 512 | 18 | 8 | 6 | 0 | 0 | 1 | 255
22-0067241 | Madera | SAN JOAQUIN #3 1101 | SAN JOAQUIN #3 1101673480 | Unknown | 2022-05-26 20:54 | 5/23 - 5/29 | 2022-05-27 09:19 | 745 | FTS | 166898 | 582 | 32 | 23 | 15 | 0 | 0 | 0 | 286.7663
22-0067257 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 210619732 | Vegetation | 2022-05-26 22:24 | 5/23 - 5/29 | 2022-05-27 03:17 | 293 | FTS | 251798 | 1994 | 148 | 92 | 26 | 4 | 1 | 4 | 126.2778
22-0067720 | Mariposa | BEAR VALLEY 2105 | BEAR VALLEY 210521160 | Equipment | 2022-05-28 03:22 | 5/23 - 5/29 | 2022-05-28 10:06 | 404 | FTS | 92920 | 230 | 14 | 10 | 1 | 0 | 0 | 0 | 404
22-0067736 | Mariposa | MARIPOSA 2102 | MARIPOSA 2102440236 | Unknown | 2022-05-28 07:50 | 5/23 - 5/29 | 2022-05-28 10:44 | 174 | FTS | 377058 | 2167 | 203 | 146 | 40 | 6 | 0 | 0 | 174
22-0067821 | Contra Costa | SOBRANTE 1101 | SOBRANTE 11011101/2 | Vegetation | 2022-05-28 16:49 | 5/23 - 5/29 | 2022-05-29 05:33 | 764 | FTS | 59050 | 1348 | 83 | 59 | 22 | 2 | 0 | 1 | 43.8056
22-0067904 | Calaveras | CALAVERAS CEMENT 1101 | CALAVERAS CEMENT 110111236 | Unknown | 2022-05-29 05:30 | 5/23 - 5/29 | 2022-05-29 09:11 | 221 | FTS | 35360 | 160 | 9 | 7 | 6 | 0 | 0 | 0 | 221
22-0067989 | San Joaquin | LOCKEFORD 2102 | LOCKEFORD 210212468 | Unknown | 2022-05-29 19:04 | 5/23 - 5/29 | 2022-05-30 10:37 | 933 | FTS | 80192 | 324 | 18 | 7 | 15 | 0 | 0 | 0 | 247.5062
22-0068020 | Shasta | GIRVAN 1102 | GIRVAN 110280726 | 3rd Party | 2022-05-30 03:21 | 5/30 - 6/5 | 2022-05-30 17:48 | 867 | FTS | 105971 | 545 | 29 | 23 | 8 | 0 | 0 | 1 | 194.4422
22-0068025 | El Dorado | SHINGLE SPRINGS 2108 | SHINGLE SPRINGS 210819622 | Unknown | 2022-05-30 06:26 | 5/30 - 6/5 | 2022-05-30 07:42 | 76 | FTS | 145920 | 1920 | 165 | 111 | 16 | 1 | 0 | 0 | 76
22-0068074 | Amador | CLAY 1102 | CLAY 11021102/2 | Unknown | 2022-05-30 18:21 | 5/30 - 6/5 | 2022-05-30 18:35 | 14 | FTS | 42 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 14
22-0068082 | Tulare | DUNLAP 1102 | DUNLAP 11027290 | Equipment | 2022-05-30 21:05 | 5/30 - 6/5 | 2022-05-31 15:52 | 1127 | FTS | 48319 | 57 | 0 | 0 | 5 | 0 | 0 | 0 | 847.7018
22-0068177 | Santa Cruz | BEN LOMOND 0401 | BEN LOMOND 04015206 | Unknown | 2022-05-31 07:56 | 5/30 - 6/5 | 2022-05-31 11:14 | 198 | FTS | 18414 | 93 | 12 | 9 | 1 | 0 | 0 | 1 | 198
22-0068242 | Nevada | NARROWS 2105 | NARROWS 21052748 | Company Initiated | 2022-05-31 10:29 | 5/30 - 6/5 | 2022-05-31 10:58 | 29 | FTS | 24563 | 847 | 58 | 36 | 8 | 0 | 0 | 3 | 29
22-0068363 | Placer | PENRYN 1103 | PENRYN 110351658 | 3rd Party | 2022-05-31 13:27 | 5/30 - 6/5 | 2022-05-31 15:55 | 148 | FTS | 100196 | 677 | 46 | 32 | 8 | 0 | 0 | 8 | 148
22-0068377 | Amador | CLAY 1102 | CLAY 11021102/2 | Unknown | 2022-05-31 13:47 | 5/30 - 6/5 | 2022-05-31 14:12 | 25 | FTS | 75 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 25
22-0068379 | El Dorado | APPLE HILL 2102 | APPLE HILL 2102186912 | Unknown | 2022-05-31 13:47 | 5/30 - 6/5 | 2022-06-01 10:36 | 1249 | FTS | 879429 | 1224 | 110 | 85 | 17 | 3 | 0 | 4 | 718.4877
22-0068414 | El Dorado | CLARKSVILLE 2110 | CLARKSVILLE 211019692 | Company Initiated | 2022-05-31 14:45 | 5/30 - 6/5 | 2022-05-31 15:01 | 16 | FTS | 37776 | 2361 | 135 | 76 | 39 | 3 | 0 | 0 | 16
22-0068556 | Tulare | DUNLAP 1102 | DUNLAP 11027290 | Equipment | 2022-05-31 20:32 | 5/30 - 6/5 | 2022-06-01 15:05 | 1113 | FTS | 51761 | 57 | 0 | 0 | 5 | 0 | 0 | 0 | 908.0877
22-0068550 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 210623190 | Vegetation | 2022-05-31 20:58 | 5/30 - 6/5 | 2022-06-01 07:07 | 609 | FTS | 348329 | 1994 | 148 | 92 | 26 | 4 | 1 | 4 | 174.6886
22-0068605 | Placer | LINCOLN 1104 | LINCOLN 110451756 | Unknown | 2022-06-01 05:13 | 5/30 - 6/5 | 2022-06-01 07:56 | 163 | FTS | 63670 | 430 | 32 | 22 | 4 | 0 | 0 | 1 | 148.0698
22-0068606 | Tehama | TYLER 1105 | TYLER 11051704 | Unknown | 2022-06-01 05:19 | 5/30 - 6/5 | 2022-06-01 10:33 | 314 | FTS | 251630 | 833 | 87 | 55 | 13 | 2 | 0 | 1 | 302.0768
22-0068607 | Napa | SILVERADO 2104 | SILVERADO 2104632 | Vegetation | 2022-06-01 06:09 | 5/30 - 6/5 | 2022-06-02 14:11 | 1922 | FTS | 781455 | 1275 | 64 | 42 | 34 | 5 | 3 | 3 | 612.9059
22-0068699 | El Dorado | SHINGLE SPRINGS 2108 | SHINGLE SPRINGS 210819622 | Unknown | 2022-06-01 08:53 | 5/30 - 6/5 | 2022-06-01 09:14 | 21 | FTS | 40320 | 1920 | 165 | 111 | 16 | 1 | 0 | 0 | 21
22-0068701 | Butte | ORO FINO 1102 | ORO FINO 11022560 | Animal | 2022-06-01 09:03 | 5/30 - 6/5 | 2022-06-01 11:06 | 123 | FTS | 85430 | 1090 | 88 | 57 | 13 | 1 | 0 | 0 | 78.3761
22-0068736 | Tuolumne | CURTIS 1704 | CURTIS 17046060 | Animal | 2022-06-01 09:45 | 5/30 - 6/5 | 2022-06-01 13:33 | 228 | FTS | 287052 | 1259 | 175 | 124 | 16 | 0 | 0 | 2 | 228
22-0068958 | Madera | COARSEGOLD 2104 | COARSEGOLD 2104570682 | Equipment | 2022-06-01 15:03 | 5/30 - 6/5 | 2022-06-01 18:50 | 227 | FTS | 206103 | 1131 | 119 | 88 | 14 | 0 | 0 | 0 | 182.2308
22-0068990 | Napa | SILVERADO 2105 | SILVERADO 2105247660 | Company Initiated | 2022-06-01 15:53 | 5/30 - 6/5 | 2022-06-02 10:21 | 1108 | FTS | 24860 | 47 | 1 | 1 | 1 | 0 | 0 | 0 | 528.9362
22-0068995 | Calaveras | CORRAL 1102 | CORRAL 110236666 | 3rd Party | 2022-06-01 15:58 | 5/30 - 6/5 | 2022-06-02 02:38 | 640 | FTS | 66200 | 425 | 44 | 30 | 8 | 0 | 0 | 0 | 155.7647
22-0069039 | San Luis Obispo | CAYUCOS 1101 | CAYUCOS 1101W58 | Equipment | 2022-06-01 18:37 | 5/30 - 6/5 | 2022-06-01 22:07 | 210 | FTS | 69720 | 332 | 4 | 3 | 7 | 0 | 0 | 0 | 210
22-0069072 | Monterey | KING CITY 1103 | KING CITY 11037038 | Equipment | 2022-06-01 22:12 | 5/30 - 6/5 | 2022-06-02 06:58 | 526 | FTS | 410764 | 794 | 52 | 39 | 15 | 0 | 0 | 0 | 517.335
22-0069086 | Yolo | MADISON 2101 | MADISON 21011606 | Unknown | 2022-06-02 05:27 | 5/30 - 6/5 | 2022-06-02 07:32 | 125 | FTS | 64000 | 512 | 18 | 8 | 6 | 0 | 0 | 1 | 125
22-0069105 | Santa Clara | LOS GATOS 1106 | LOS GATOS 1106LB48 | Vegetation | 2022-06-02 07:00 | 5/30 - 6/5 | 2022-06-02 08:09 | 69 | FTS | 7974 | 125 | 5 | 1 | 4 | 0 | 0 | 1 | 63.792
22-0069189 | Sonoma | SONOMA 1102 | SONOMA 1102441730 | Unknown | 2022-06-02 08:45 | 5/30 - 6/5 | 2022-06-02 13:55 | 310 | FTS | 35650 | 115 | 3 | 2 | 4 | 0 | 0 | 0 | 310
22-0069442 | Santa Clara | HICKS 2101 | HICKS 2101XR162 | Unknown | 2022-06-02 14:15 | 5/30 - 6/5 | 2022-06-02 17:24 | 189 | FTS | 239463 | 1549 | 94 | 68 | 23 | 3 | 0 | 0 | 154.592
22-0069476 | Sonoma | MIRABEL 1101 | MIRABEL 1101228 | Vegetation | 2022-06-02 15:07 | 5/30 - 6/5 | 2022-06-02 16:07 | 60 | FTS | 7752 | 245 | 17 | 15 | 4 | 0 | 0 | 3 | 31.6408
22-0069586 | Santa Clara | LOS GATOS 1106 | LOS GATOS 110660116 | Animal | 2022-06-02 18:55 | 5/30 - 6/5 | 2022-06-02 21:45 | 170 | FTS | 190782 | 1134 | 91 | 72 | 23 | 3 | 0 | 3 | 168.2381
22-0069589 | Calaveras | CORRAL 1101 | CORRAL 110175204 | Unknown | 2022-06-02 19:02 | 5/30 - 6/5 | 2022-06-02 22:10 | 188 | FTS | 33276 | 177 | 3 | 2 | 4 | 0 | 0 | 0 | 188
22-0069593 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 21012181 | Animal | 2022-06-02 19:35 | 5/30 - 6/5 | 2022-06-03 11:25 | 950 | FTS | 32236 | 51 | 0 | 0 | 2 | 0 | 0 | 0 | 632.0784
22-0069605 | Napa | PUEBLO 2104 | PUEBLO 2104279478 | Unknown | 2022-06-02 20:48 | 5/30 - 6/5 | 2022-06-03 10:01 | 793 | FTS | 4333 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 333.3077
22-0069653 | Tehama | TYLER 1105 | TYLER 11051704 | Unknown | 2022-06-03 00:46 | 5/30 - 6/5 | 2022-06-03 10:09 | 563 | FTS | 458492 | 833 | 87 | 55 | 13 | 2 | 0 | 1 | 550.4106
22-0069660 | Madera | OAKHURST 1103 | OAKHURST 11031103/2 | Unknown | 2022-06-03 04:21 | 5/30 - 6/5 | 2022-06-03 08:53 | 272 | FTS | 1030802 | 3957 | 239 | 180 | 105 | 27 | 0 | 1 | 260.5009
22-0069662 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 21067522 | Unknown | 2022-06-03 05:36 | 5/30 - 6/5 | 2022-06-03 12:36 | 420 | FTS | 392532 | 1036 | 85 | 62 | 18 | 5 | 0 | 2 | 378.8919
22-0069665 | Tehama | RED BLUFF 1104 | RED BLUFF 1104952448 | Animal | 2022-06-03 05:47 | 5/30 - 6/5 | 2022-06-03 07:34 | 107 | FTS | 4708 | 44 | 6 | 1 | 0 | 0 | 0 | 0 | 107
22-0069664 | Lake | REDBUD 1102 | REDBUD 1102432 | Animal | 2022-06-03 05:53 | 5/30 - 6/5 | 2022-06-03 07:35 | 102 | FTS | 200879 | 2832 | 247 | 160 | 35 | 2 | 1 | 0 | 70.9319
22-0069729 | Colusa | CORTINA 1101 | CORTINA 1101528460 | 3rd Party | 2022-06-03 08:17 | 5/30 - 6/5 | 2022-06-03 10:36 | 139 | FTS | 1251 | 9 | 1 | 0 | 1 | 0 | 0 | 0 | 139
22-0069977 | Santa Cruz | CAMP EVERS 2106 | CAMP EVERS 210660120 | Unknown | 2022-06-03 16:31 | 5/30 - 6/5 | 2022-06-03 18:34 | 123 | FTS | 67191 | 547 | 52 | 34 | 7 | 0 | 0 | 5 | 122.8355
22-0070054 | Santa Barbara | SANTA YNEZ 1101 | SANTA YNEZ 1101Y52 | Unknown | 2022-06-04 05:53 | 5/30 - 6/5 | 2022-06-04 08:05 | 132 | FTS | 25344 | 192 | 1 | 1 | 26 | 0 | 0 | 0 | 132
22-0070116 | Lake | HIGHLANDS 1102 | HIGHLANDS 110275140 | Animal | 2022-06-04 09:14 | 5/30 - 6/5 | 2022-06-04 10:44 | 90 | FTS | 233640 | 2596 | 295 | 209 | 31 | 9 | 0 | 0 | 90
22-0070130 | Madera | OAKHURST 1102 | OAKHURST 11021102/2 | Animal | 2022-06-04 09:49 | 5/30 - 6/5 | 2022-06-04 14:56 | 307 | FTS | 408281 | 3185 | 300 | 221 | 86 | 5 | 0 | 0 | 128.1887
22-0070190 | Fresno | AUBERRY 1101 | AUBERRY 110149122 | Unknown | 2022-06-04 14:57 | 5/30 - 6/5 | 2022-06-04 19:06 | 249 | FTS | 193708 | 784 | 71 | 43 | 43 | 1 | 0 | 0 | 247.0765
22-0070197 | San Luis Obispo | ATASCADERO 1103 | ATASCADERO 1103A46 | Animal | 2022-06-04 15:26 | 5/30 - 6/5 | 2022-06-04 17:49 | 143 | FTS | 114237 | 807 | 22 | 16 | 12 | 1 | 0 | 0 | 141.5576
22-0070281 | Calaveras | PEORIA 1704 | PEORIA 170459596 | Unknown | 2022-06-05 05:30 | 5/30 - 6/5 | 2022-06-05 10:16 | 286 | FTS | 222794 | 779 | 63 | 52 | 31 | 1 | 0 | 1 | 286
22-0070296 | Napa | MONTICELLO 1101 | MONTICELLO 110152910 | Animal | 2022-06-05 08:02 | 5/30 - 6/5 | 2022-06-05 10:52 | 170 | FTS | 92996 | 1243 | 61 | 42 | 22 | 1 | 0 | 3 | 74.8158
22-0070360 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 21011703 | Animal | 2022-06-05 18:27 | 5/30 - 6/5 | 2022-06-05 21:38 | 191 | FTS | 191 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 191
22-0070409 | Santa Barbara | ZACA 1101 | ZACA 1101M82 | Equipment | 2022-06-06 03:54 | 6/6 - 6/12 | 2022-06-06 11:16 | 442 | FTS | 139703 | 750 | 21 | 15 | 8 | 1 | 0 | 0 | 186.2707
22-0070450 | Santa Barbara | SISQUOC 1102 | SISQUOC 1102M52 | Unknown | 2022-06-06 07:53 | 6/6 - 6/12 | 2022-06-06 16:54 | 541 | FTS | 48778 | 106 | 4 | 2 | 1 | 0 | 0 | 0 | 460.1698
22-0070738 | Lake | REDBUD 1101 | REDBUD 110191960 | Company Initiated | 2022-06-06 15:44 | 6/6 - 6/12 | 2022-06-06 17:04 | 80 | FTS | 39440 | 493 | 42 | 31 | 10 | 0 | 0 | 0 | 80
22-0070780 | Santa Barbara | SISQUOC 1102 | SISQUOC 1102M52 | 3rd Party | 2022-06-06 18:20 | 6/6 - 6/12 | 2022-06-06 19:26 | 66 | FTS | 4620 | 70 | 4 | 2 | 1 | 0 | 0 | 0 | 66
22-0070821 | Santa Clara | MORGAN HILL 2105 | MORGAN HILL 2105XR176 | Animal | 2022-06-06 22:22 | 6/6 - 6/12 | 2022-06-07 00:05 | 103 | FTS | 111529 | 1101 | 66 | 51 | 17 | 3 | 0 | 2 | 101.2979
22-0070832 | Napa | SILVERADO 2105 | SILVERADO 21051306 | Animal | 2022-06-07 01:34 | 6/6 - 6/12 | 2022-06-07 03:56 | 142 | FTS | 27107 | 194 | 3 | 3 | 4 | 0 | 0 | 0 | 139.7268
22-0070855 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113A32 | Unknown | 2022-06-07 07:17 | 6/6 - 6/12 | 2022-06-07 08:30 | 73 | FTS | 87162 | 1194 | 51 | 33 | 12 | 3 | 0 | 0 | 73
22-0070875 | Fresno | DUNLAP 1103 | DUNLAP 11037220 | Equipment | 2022-06-07 07:53 | 6/6 - 6/12 | 2022-06-07 13:32 | 339 | FTS | 165415 | 557 | 42 | 28 | 5 | 3 | 0 | 0 | 296.9749
22-0071011 | San Luis Obispo | SAN LUIS OBISPO 1107 | SAN LUIS OBISPO 1107V18 | Equipment | 2022-06-07 10:52 | 6/6 - 6/12 | 2022-06-07 11:39 | 47 | FTS | 49021 | 1043 | 38 | 25 | 10 | 0 | 0 | 0 | 47
22-0071037 | Shasta | COTTONWOOD 1102 | COTTONWOOD 11029026 | Vegetation | 2022-06-07 11:23 | 6/6 - 6/12 | 2022-06-08 00:05 | 762 | FTS | 97559 | 989 | 105 | 78 | 10 | 3 | 0 | 4 | 98.6441
22-0071287 | Nevada | HIGGINS 1104 | HIGGINS 11041374 | Unknown | 2022-06-07 19:27 | 6/6 - 6/12 | 2022-06-07 22:07 | 160 | FTS | 82388 | 968 | 91 | 55 | 10 | 0 | 0 | 0 | 85.1116
22-0071294 | Sonoma | SANTA ROSA A 1107 | SANTA ROSA A 1107LR1107/2 | Unknown | 2022-06-07 20:01 | 6/6 - 6/12 | 2022-06-07 21:58 | 117 | FTS | 142038 | 1214 | 30 | 23 | 24 | 1 | 1 | 0 | 117
22-0071361 | Contra Costa | TASSAJARA 2113 | TASSAJARA 2113MR276 | Unknown | 2022-06-08 04:49 | 6/6 - 6/12 | 2022-06-08 08:00 | 191 | FTS | 70867 | 449 | 30 | 24 | 10 | 0 | 0 | 1 | 157.833
22-0071444 | Plumas | BIG MEADOWS 2101 | BIG MEADOWS 21012016 | Animal | 2022-06-08 08:12 | 6/6 - 6/12 | 2022-06-08 09:08 | 56 | FTS | 76002 | 1390 | 42 | 31 | 15 | 0 | 0 | 0 | 54.6777
22-0071524 | Napa | NAPA 1112 | NAPA 11121302 | Equipment | 2022-06-08 10:08 | 6/6 - 6/12 | 2022-06-08 11:34 | 86 | FTS | 22116 | 549 | 30 | 20 | 10 | 0 | 0 | 10 | 40.2842
22-0071528 | San Luis Obispo | SAN LUIS OBISPO 1107 | SAN LUIS OBISPO 11071107/2 | Vegetation | 2022-06-08 10:14 | 6/6 - 6/12 | 2022-06-08 11:24 | 70 | FTS | 249900 | 3570 | 86 | 56 | 59 | 4 | 2 | 21 | 70
22-0071600 | Napa | NAPA 1110 | NAPA 1110373667 | Company Initiated | 2022-06-08 11:03 | 6/6 - 6/12 | 2022-06-08 11:51 | 48 | FTS | 3648 | 76 | 2 | 2 | 0 | 0 | 0 | 0 | 48
22-0071841 | Calaveras | WEST POINT 1102 | WEST POINT 110236676 | 3rd Party | 2022-06-08 16:55 | 6/6 - 6/12 | 2022-06-09 12:04 | 1149 | FTS | 56188 | 198 | 14 | 12 | 3 | 0 | 0 | 0 | 283.7778
22-0071844 | Alameda | FREMONT 1104 | FREMONT 1104645342 | Unknown | 2022-06-08 17:07 | 6/6 - 6/12 | 2022-06-08 23:30 | 383 | FTS | 7871 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 314.84
22-0071861 | Contra Costa | LAKEWOOD 2107 | LAKEWOOD 2107396264 | Unknown | 2022-06-08 17:45 | 6/6 - 6/12 | 2022-06-08 21:22 | 217 | FTS | 349665 | 1905 | 143 | 104 | 26 | 1 | 0 | 0 | 183.5512
22-0071881 | San Luis Obispo | SAN LUIS OBISPO 1107 | SAN LUIS OBISPO 1107V18 | Equipment | 2022-06-08 18:52 | 6/6 - 6/12 | 2022-06-08 20:49 | 117 | FTS | 122031 | 1043 | 38 | 25 | 10 | 0 | 0 | 0 | 117
22-0071894 | Santa Clara | MC KEE 1111 | MC KEE 1111711900 | 3rd Party | 2022-06-08 19:47 | 6/6 - 6/12 | 2022-06-08 20:21 | 34 | FTS | 20536 | 604 | 29 | 15 | 7 | 0 | 0 | 0 | 34
22-0071901 | Monterey | LOS OSITOS 2103 | LOS OSITOS 21033010 | Unknown | 2022-06-08 20:10 | 6/6 - 6/12 | 2022-06-09 09:17 | 787 | FTS | 339197 | 431 | 9 | 4 | 4 | 0 | 0 | 0 | 787
22-0071938 | Sonoma | SONOMA 1102 | SONOMA 1102441730 | Unknown | 2022-06-08 22:35 | 6/6 - 6/12 | 2022-06-09 09:48 | 673 | FTS | 77395 | 115 | 3 | 2 | 4 | 0 | 0 | 0 | 673
22-0071945 | Santa Cruz | ROB ROY 2104 | ROB ROY 210412596 | Animal | 2022-06-08 23:57 | 6/6 - 6/12 | 2022-06-09 03:11 | 194 | HLT | 79540 | 410 | 37 | 32 | 4 | 0 | 0 | 0 | 194
22-0071966 | Lake | UPPER LAKE 1101 | UPPER LAKE 11011101/2 | Unknown | 2022-06-09 06:01 | 6/6 - 6/12 | 2022-06-09 10:16 | 255 | FTS | 258280 | 1256 | 79 | 46 | 15 | 4 | 0 | 1 | 205.6369
22-0071974 | Lake | CLEAR LAKE 1102 | CLEAR LAKE 1102904 | Unknown | 2022-06-09 06:45 | 6/6 - 6/12 | 2022-06-09 08:31 | 106 | FTS | 5194 | 49 | 5 | 4 | 0 | 0 | 0 | 0 | 106
22-0072006 | Trinity | WILLOW CREEK 1103 | WILLOW CREEK 11032936 | Unknown | 2022-06-09 07:39 | 6/6 - 6/12 | 2022-06-09 22:37 | 898 | FTS | 200018 | 252 | 14 | 9 | 5 | 1 | 0 | 0 | 793.7222
22-0072059 | Monterey | RESERVATION ROAD 1102 | RESERVATION ROAD 11021102/2 | 3rd Party | 2022-06-09 09:05 | 6/6 - 6/12 | 2022-06-09 16:59 | 474 | FTS | 299647 | 2116 | 88 | 64 | 38 | 2 | 0 | 0 | 141.6101
22-0072138 | San Luis Obispo | SAN LUIS OBISPO 1107 | SAN LUIS OBISPO 1107V18 | Equipment | 2022-06-09 10:37 | 6/6 - 6/12 | 2022-06-09 12:02 | 85 | FTS | 35615 | 419 | 17 | 15 | 6 | 0 | 0 | 0 | 85
22-0072322 | Solano | PEABODY 2113 | PEABODY 21132113/2 | Equipment | 2022-06-09 14:28 | 6/6 - 6/12 | 2022-06-10 01:02 | 634 | FTS | 767512 | 5668 | 423 | 287 | 62 | 6 | 0 | 0 | 135.4114
22-0072328 | Mendocino | LAYTONVILLE 1102 | LAYTONVILLE 110237586 | Unknown | 2022-06-09 14:35 | 6/6 - 6/12 | 2022-06-09 18:21 | 226 | FTS | 28327 | 127 | 6 | 1 | 6 | 1 | 0 | 0 | 223.0472
22-0072371 | Mendocino | POTTER VALLEY P H 1105 | POTTER VALLEY P H 1105195738 | 3rd Party | 2022-06-09 15:09 | 6/6 - 6/12 | 2022-06-09 16:12 | 63 | FTS | 2520 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 63
22-0072421 | Marin | WOODACRE 1102 | WOODACRE 1102137662 | Vegetation | 2022-06-09 16:56 | 6/6 - 6/12 | 2022-06-10 21:10 | 1694 | FTS | 637871 | 1891 | 90 | 49 | 28 | 6 | 0 | 0 | 337.3194
22-0072426 | Contra Costa | BRENTWOOD 2105 | BRENTWOOD 21056512 | Equipment | 2022-06-09 17:14 | 6/6 - 6/12 | 2022-06-09 17:51 | 37 | FTS | 37 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 37
22-0072432 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 21012101/2 | Unknown | 2022-06-09 17:25 | 6/6 - 6/12 | 2022-06-09 20:24 | 179 | FTS | 26025 | 147 | 4 | 3 | 5 | 0 | 0 | 0 | 177.0408
22-0072435 | Santa Cruz | CAMP EVERS 2105 | CAMP EVERS 210512590 | Equipment | 2022-06-09 17:40 | 6/6 - 6/12 | 2022-06-10 03:22 | 582 | FTS | 62506 | 348 | 38 | 33 | 6 | 1 | 0 | 0 | 179.6149
22-0072447 | San Luis Obispo | PASO ROBLES 1104 | PASO ROBLES 1104R14 | 3rd Party | 2022-06-09 18:08 | 6/6 - 6/12 | 2022-06-10 00:42 | 394 | FTS | 260196 | 2368 | 82 | 49 | 26 | 9 | 0 | 1 | 109.8801
22-0072452 | Contra Costa | ALHAMBRA 1102 | ALHAMBRA 11021102/2 | 3rd Party | 2022-06-09 18:34 | 6/6 - 6/12 | 2022-06-09 19:19 | 45 | FTS | 137710 | 3128 | 146 | 100 | 47 | 10 | 4 | 0 | 44.0249
22-0072456 | Lake | HARTLEY 1101 | HARTLEY 1101658 | Unknown | 2022-06-09 18:47 | 6/6 - 6/12 | 2022-06-10 10:24 | 937 | FTS | 206760 | 360 | 20 | 12 | 8 | 0 | 0 | 1 | 574.3333
22-0072518 | Sonoma | MONTE RIO 1111 | MONTE RIO 111164758 | Vegetation | 2022-06-10 04:11 | 6/6 - 6/12 | 2022-06-10 13:32 | 561 | FTS | 175142 | 564 | 31 | 22 | 16 | 1 | 0 | 0 | 310.5355
22-0072519 | Amador | OLETA 1102 | OLETA 1102186326 | Unknown | 2022-06-10 04:53 | 6/6 - 6/12 | 2022-06-10 09:55 | 302 | FTS | 287096 | 966 | 38 | 24 | 19 | 1 | 0 | 6 | 297.2008
22-0072526 | Monterey | LOS OSITOS 2103 | LOS OSITOS 21033010 | Unknown | 2022-06-10 06:30 | 6/6 - 6/12 | 2022-06-10 10:48 | 258 | FTS | 111198 | 431 | 9 | 4 | 4 | 0 | 0 | 0 | 258
22-0072565 | Marin | STAFFORD 1102 | STAFFORD 1102524 | Unknown | 2022-06-10 07:39 | 6/6 - 6/12 | 2022-06-10 09:36 | 117 | FTS | 184158 | 1574 | 94 | 54 | 13 | 1 | 0 | 0 | 117
22-0072606 | Shasta | JESSUP 1102 | JESSUP 11021102/2 | 3rd Party | 2022-06-10 08:22 | 6/6 - 6/12 | 2022-06-10 16:51 | 509 | FTS | 148685 | 2353 | 214 | 164 | 18 | 2 | 0 | 0 | 63.1895
22-0072628 | Butte | BIG BEND 1102 | BIG BEND 1102884340 | Unknown | 2022-06-10 08:45 | 6/6 - 6/12 | 2022-06-10 10:57 | 132 | FTS | 21930 | 169 | 4 | 1 | 4 | 0 | 0 | 0 | 129.7633
22-0072632 | Sonoma | SONOMA 1102 | SONOMA 1102441730 | Unknown | 2022-06-10 08:47 | 6/6 - 6/12 | 2022-06-10 12:00 | 193 | FTS | 22195 | 115 | 3 | 2 | 4 | 0 | 0 | 0 | 193
22-0072723 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 21011703 | 3rd Party | 2022-06-10 10:43 | 6/6 - 6/12 | 2022-06-10 13:10 | 147 | FTS | 147 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 147
22-0072844 | Yuba | CHALLENGE 1101 | CHALLENGE 11011101/2 | 3rd Party | 2022-06-10 12:33 | 6/6 - 6/12 | 2022-06-11 03:15 | 882 | FTS | 583293 | 703 | 47 | 32 | 10 | 0 | 0 | 0 | 829.7198
22-0072867 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 21062224 | Unknown | 2022-06-10 13:00 | 6/6 - 6/12 | 2022-06-10 18:57 | 357 | FTS | 305650 | 995 | 72 | 58 | 42 | 11 | 0 | 1 | 307.1859
22-0072886 | Fresno | AUBERRY 1102 | AUBERRY 1102R902 | Unknown | 2022-06-10 13:17 | 6/6 - 6/12 | 2022-06-10 17:22 | 245 | FTS | 148849 | 719 | 73 | 47 | 8 | 0 | 0 | 2 | 207.0223
22-0072892 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 21012101/2 | Animal | 2022-06-10 13:32 | 6/6 - 6/12 | 2022-06-10 14:32 | 60 | FTS | 8382 | 147 | 4 | 3 | 5 | 0 | 0 | 0 | 57.0204
22-0072928 | Mendocino | HOPLAND 1101 | HOPLAND 110194006 | Vegetation | 2022-06-10 14:42 | 6/6 - 6/12 | 2022-06-10 21:26 | 404 | FTS | 22616 | 118 | 20 | 15 | 2 | 0 | 0 | 0 | 191.661
22-0072995 | San Mateo | HALF MOON BAY 1103 | HALF MOON BAY 1103655644 | Unknown | 2022-06-10 15:51 | 6/6 - 6/12 | 2022-06-10 16:18 | 27 | FTS | 3726 | 138 | 2 | 2 | 11 | 0 | 0 | 0 | 27
22-0072983 | Napa | PUEBLO 2103 | PUEBLO 2103678 | Equipment | 2022-06-10 15:56 | 6/6 - 6/12 | 2022-06-10 21:24 | 328 | FTS | 99554 | 313 | 6 | 4 | 3 | 2 | 0 | 2 | 318.0639
22-0072993 | San Luis Obispo | MORRO BAY 1101 | MORRO BAY 1101V66 | Unknown | 2022-06-10 16:13 | 6/6 - 6/12 | 2022-06-10 20:27 | 254 | FTS | 83058 | 327 | 14 | 11 | 4 | 0 | 0 | 0 | 254
22-0073056 | San Mateo | HALF MOON BAY 1101 | HALF MOON BAY 1101818874 | Unknown | 2022-06-10 16:54 | 6/6 - 6/12 | 2022-06-10 19:53 | 179 | FTS | 7339 | 41 | 1 | 1 | 1 | 1 | 0 | 0 | 179
22-0073062 | Santa Cruz | PAUL SWEET 2105 | PAUL SWEET 2105959032 | Vegetation | 2022-06-10 18:24 | 6/6 - 6/12 | 2022-06-11 09:30 | 906 | FTS | 22430 | 25 | 3 | 3 | 1 | 0 | 0 | 0 | 897.2
22-0073069 | Santa Clara | HICKS 2101 | HICKS 2101XR250 | Unknown | 2022-06-10 19:04 | 6/6 - 6/12 | 2022-06-11 13:38 | 1114 | FTS | 738788 | 3155 | 178 | 121 | 51 | 9 | 0 | 0 | 234.1642
22-0073083 | San Luis Obispo | OILFIELDS 1103 | OILFIELDS 110387034 | Equipment | 2022-06-10 19:19 | 6/6 - 6/12 | 2022-06-12 03:13 | 1914 | FTS | 340401 | 1187 | 28 | 16 | 25 | 1 | 0 | 2 | 286.7742
22-0073077 | Butte | ORO FINO 1101 | ORO FINO 11012022 | Vegetation | 2022-06-10 19:28 | 6/6 - 6/12 | 2022-06-11 14:47 | 1159 | FTS | 99677 | 1043 | 128 | 93 | 11 | 1 | 0 | 0 | 95.5676
22-0073086 | Butte | ORO FINO 1102 | ORO FINO 11022096 | Unknown | 2022-06-10 19:31 | 6/6 - 6/12 | 2022-06-10 20:42 | 71 | FTS | 24027 | 343 | 23 | 16 | 12 | 2 | 0 | 0 | 70.0496
22-0073104 | San Mateo | HALF MOON BAY 1101 | HALF MOON BAY 1101818874 | Equipment | 2022-06-10 20:13 | 6/6 - 6/12 | 2022-06-11 12:26 | 973 | FTS | 39893 | 41 | 1 | 1 | 1 | 1 | 0 | 0 | 973
22-0073138 | Contra Costa | BRENTWOOD 2105 | BRENTWOOD 210598606 | Unknown | 2022-06-10 22:06 | 6/6 - 6/12 | 2022-06-11 07:44 | 578 | FTS | 167393 | 298 | 15 | 7 | 12 | 0 | 0 | 0 | 561.7215
22-0073195 | Alameda | SAN RAMON 2103 | SAN RAMON 2103MR279 | Unknown | 2022-06-11 00:12 | 6/6 - 6/12 | 2022-06-11 13:26 | 794 | FTS | 141788 | 184 | 0 | 0 | 7 | 0 | 0 | 0 | 770.587
22-0073155 | Santa Cruz | CAMP EVERS 2103 | CAMP EVERS 210311056 | Vegetation | 2022-06-11 00:37 | 6/6 - 6/12 | 2022-06-11 12:31 | 714 | FTS | 322014 | 451 | 39 | 27 | 2 | 0 | 0 | 3 | 714
22-0073161 | Placer | WISE 1102 | WISE 1102307494 | Unknown | 2022-06-11 02:32 | 6/6 - 6/12 | 2022-06-11 12:29 | 597 | FTS | 126301 | 273 | 23 | 16 | 3 | 0 | 0 | 4 | 462.641
22-0073162 | Shasta | OREGON TRAIL 1102 | OREGON TRAIL 110249144 | Unknown | 2022-06-11 03:02 | 6/6 - 6/12 | 2022-06-11 10:05 | 423 | FTS | 215090 | 534 | 61 | 45 | 6 | 0 | 0 | 0 | 402.7903
22-0073163 | Nevada | BRUNSWICK 1105 | BRUNSWICK 11052210 | Unknown | 2022-06-11 03:30 | 6/6 - 6/12 | 2022-06-11 10:02 | 392 | FTS | 310138 | 878 | 55 | 35 | 18 | 0 | 0 | 2 | 353.2323
22-0073167 | San Luis Obispo | SAN LUIS OBISPO 1107 | SAN LUIS OBISPO 1107V18 | Equipment | 2022-06-11 05:38 | 6/6 - 6/12 | 2022-06-11 09:42 | 244 | FTS | 97858 | 418 | 17 | 15 | 6 | 0 | 0 | 0 | 234.11
22-0073169 | Marin | SAN RAFAEL 1106 | SAN RAFAEL 110648752 | Animal | 2022-06-11 06:04 | 6/6 - 6/12 | 2022-06-11 09:26 | 202 | FTS | 214132 | 1912 | 56 | 36 | 22 | 9 | 0 | 0 | 111.9937
22-0073174 | Shasta | COTTONWOOD 1102 | COTTONWOOD 11029026 | 3rd Party | 2022-06-11 06:35 | 6/6 - 6/12 | 2022-06-11 15:46 | 551 | FTS | 81069 | 713 | 76 | 57 | 8 | 2 | 0 | 2 | 113.7013
22-0073178 | Calaveras | CORRAL 1101 | CORRAL 110112612 | Unknown | 2022-06-11 06:58 | 6/6 - 6/12 | 2022-06-11 09:19 | 141 | FTS | 39311 | 321 | 16 | 13 | 8 | 0 | 0 | 0 | 122.4642
22-0073222 | Yolo | MADISON 2101 | MADISON 21011606 | Unknown | 2022-06-11 10:18 | 6/6 - 6/12 | 2022-06-11 16:03 | 345 | FTS | 174655 | 512 | 18 | 8 | 6 | 0 | 0 | 1 | 341.123
22-0073241 | Santa Barbara | SANTA YNEZ 1102 | SANTA YNEZ 1102320270 | Equipment | 2022-06-11 12:17 | 6/6 - 6/12 | 2022-06-12 08:46 | 1229 | FTS | 50562 | 228 | 4 | 1 | 9 | 0 | 0 | 0 | 221.7632
22-0073256 | Alameda | CASTRO VALLEY 1111 | CASTRO VALLEY 1111MR334 | Unknown | 2022-06-11 13:17 | 6/6 - 6/12 | 2022-06-11 16:21 | 184 | FTS | 72470 | 415 | 20 | 11 | 7 | 0 | 0 | 0 | 174.6265
22-0073284 | Placer | HORSESHOE 1101 | HORSESHOE 11011101/2 | Vegetation | 2022-06-11 16:19 | 6/6 - 6/12 | 2022-06-11 23:44 | 445 | FTS | 383185 | 1364 | 94 | 60 | 20 | 2 | 0 | 2 | 280.9274
22-0073295 | Butte | CHALLENGE 1101 | CHALLENGE 11011101/2 | Equipment | 2022-06-11 17:17 | 6/6 - 6/12 | 2022-06-11 21:55 | 278 | FTS | 187186 | 703 | 47 | 32 | 10 | 0 | 0 | 0 | 266.2674
22-0073299 | El Dorado | CLARKSVILLE 2106 | CLARKSVILLE 21062106/2 | Equipment | 2022-06-11 17:29 | 6/6 - 6/12 | 2022-06-11 21:54 | 265 | FTS | 1137058 | 4792 | 315 | 200 | 68 | 6 | 0 | 0 | 237.2826
22-0073312 | Nevada | NARROWS 2102 | NARROWS 21022220 | Animal | 2022-06-11 18:47 | 6/6 - 6/12 | 2022-06-12 09:50 | 903 | FTS | 488786 | 890 | 56 | 33 | 20 | 7 | 0 | 11 | 549.1978
22-0073314 | Nevada | NARROWS 2102 | NARROWS 210276952 | Unknown | 2022-06-11 18:47 | 6/6 - 6/12 | 2022-06-11 22:54 | 247 | FTS | 223041 | 903 | 80 | 52 | 13 | 0 | 0 | 1 | 247
22-0073328 | Yolo | MADISON 1105 | MADISON 11057712 | Unknown | 2022-06-11 20:56 | 6/6 - 6/12 | 2022-06-12 10:15 | 799 | FTS | 151011 | 189 | 6 | 6 | 2 | 0 | 0 | 0 | 799
22-0073331 | San Luis Obispo | TEMPLETON 2110 | TEMPLETON 2110307832 | Vegetation | 2022-06-11 21:11 | 6/6 - 6/12 | 2022-06-12 20:23 | 1392 | FTS | 351222 | 1323 | 42 | 31 | 18 | 0 | 0 | 13 | 265.4739
22-0073377 | Marin | GREENBRAE 1102 | GREENBRAE 11021254 | Unknown | 2022-06-12 06:46 | 6/6 - 6/12 | 2022-06-12 10:17 | 211 | FTS | 541848 | 2568 | 74 | 44 | 34 | 1 | 0 | 0 | 211
22-0073385 | Nevada | BRUNSWICK 1103 | BRUNSWICK 11032784 | Unknown | 2022-06-12 07:51 | 6/6 - 6/12 | 2022-06-12 12:37 | 286 | FTS | 353146 | 1276 | 72 | 44 | 12 | 1 | 0 | 5 | 276.7602
22-0073387 | Contra Costa | SOBRANTE 1102 | SOBRANTE 1102690098 | Animal | 2022-06-12 09:05 | 6/6 - 6/12 | 2022-06-12 11:57 | 172 | FTS | 100448 | 584 | 37 | 28 | 13 | 2 | 0 | 0 | 172
22-0073392 | Calaveras | STANISLAUS 1701 | STANISLAUS 17011812 | 3rd Party | 2022-06-12 09:31 | 6/6 - 6/12 | 2022-06-12 20:40 | 669 | FTS | 219673 | 913 | 55 | 44 | 23 | 2 | 0 | 0 | 240.6057
22-0073403 | Santa Cruz | GREEN VALLEY 2101 | GREEN VALLEY 2101942143 | Unknown | 2022-06-12 11:30 | 6/6 - 6/12 | 2022-06-12 14:52 | 202 | FTS | 29896 | 148 | 4 | 4 | 0 | 0 | 0 | 4 | 202
22-0073406 | El Dorado | EL DORADO PH 2101 | EL DORADO PH 210152456 | Vegetation | 2022-06-12 11:30 | 6/6 - 6/12 | 2022-06-12 16:39 | 309 | FTS | 319351 | 1087 | 26 | 18 | 49 | 1 | 0 | 0 | 293.7912
22-0073412 | Tehama | VOLTA 1101 | VOLTA 110180454 | Vegetation | 2022-06-12 12:31 | 6/6 - 6/12 | 2022-06-12 16:43 | 252 | FTS | 60480 | 240 | 16 | 13 | 7 | 3 | 0 | 0 | 252
22-0073414 | Santa Cruz | BIG BASIN 1101 | BIG BASIN 110195690 | Vegetation | 2022-06-12 12:32 | 6/6 - 6/12 | 2022-06-12 22:09 | 577 | FTS | 52515 | 2027 | 163 | 131 | 28 | 1 | 0 | 1 | 25.9077
22-0073422 | San Luis Obispo | ATASCADERO 1103 | ATASCADERO 1103A46 | Animal | 2022-06-12 13:24 | 6/6 - 6/12 | 2022-06-12 15:15 | 111 | FTS | 89577 | 807 | 22 | 16 | 12 | 1 | 0 | 0 | 111
22-0073431 | Placer | BELL 1107 | BELL 11072400 | Vegetation | 2022-06-12 15:10 | 6/6 - 6/12 | 2022-06-13 02:38 | 688 | FTS | 76886 | 521 | 37 | 26 | 2 | 1 | 0 | 5 | 147.5739
22-0073430 | Shasta | PANORAMA 1101 | PANORAMA 11011101/2 | Vegetation | 2022-06-12 15:15 | 6/6 - 6/12 | 2022-06-13 02:07 | 652 | FTS | 162735 | 1504 | 144 | 102 | 15 | 0 | 0 | 0 | 108.2015
22-0073439 | Tehama | TYLER 1105 | TYLER 110585132 | Unknown | 2022-06-12 16:39 | 6/6 - 6/12 | 2022-06-12 20:11 | 212 | FTS | 37524 | 177 | 13 | 7 | 5 | 0 | 0 | 0 | 212
22-0073442 | Sonoma | ANNAPOLIS 1101 | ANNAPOLIS 1101528344 | Unknown | 2022-06-12 16:56 | 6/6 - 6/12 | 2022-06-13 10:06 | 1030 | FTS | 104279 | 152 | 4 | 4 | 5 | 5 | 0 | 2 | 686.0461
22-0073459 | Placer | PENRYN 1103 | PENRYN 1103660 | Vegetation | 2022-06-12 19:45 | 6/6 - 6/12 | 2022-06-12 22:10 | 145 | FTS | 65395 | 451 | 28 | 15 | 3 | 0 | 0 | 4 | 145
22-0073464 | Tulare | STONE CORRAL 1108 | STONE CORRAL 1108255186 | Unknown | 2022-06-12 20:46 | 6/6 - 6/12 | 2022-06-13 09:21 | 755 | FTS | 41525 | 55 | 2 | 1 | 0 | 0 | 0 | 0 | 755
22-0073490 | Santa Cruz | ROB ROY 2105 | ROB ROY 210512586 | Vegetation | 2022-06-13 02:35 | 6/13 - 6/19 | 2022-06-13 05:25 | 170 | FTS | 163070 | 1077 | 95 | 80 | 8 | 3 | 0 | 0 | 151.4113
22-0073492 | Contra Costa | NORTH DUBLIN 2103 | NORTH DUBLIN 21032103/2 | Unknown | 2022-06-13 02:55 | 6/13 - 6/19 | 2022-06-13 09:12 | 377 | FTS | 1016768 | 4926 | 164 | 114 | 51 | 6 | 0 | 0 | 206.4084
22-0073622 | Santa Cruz | CAMP EVERS 2105 | CAMP EVERS 210595050 | Animal | 2022-06-13 10:15 | 6/13 - 6/19 | 2022-06-13 11:55 | 100 | FTS | 88891 | 1971 | 146 | 110 | 33 | 3 | 0 | 1 | 45.0994
22-0073667 | Mendocino | HOPLAND 1101 | HOPLAND 110180620 | 3rd Party | 2022-06-13 11:46 | 6/13 - 6/19 | 2022-06-13 15:12 | 206 | FTS | 92590 | 457 | 37 | 28 | 21 | 13 | 0 | 0 | 202.6039
22-0073699 | San Mateo | HALF MOON BAY 1103 | HALF MOON BAY 1103H82 | Vegetation | 2022-06-13 12:16 | 6/13 - 6/19 | 2022-06-13 20:10 | 474 | FTS | 235596 | 1944 | 59 | 47 | 55 | 10 | 0 | 4 | 121.1914
22-0073758 | Santa Cruz | GREEN VALLEY 2101 | GREEN VALLEY 210112106 | Animal | 2022-06-13 14:35 | 6/13 - 6/19 | 2022-06-13 21:37 | 422 | FTS | 51983 | 1012 | 86 | 69 | 9 | 1 | 0 | 0 | 51.3666
22-0073900 | Santa Cruz | CAMP EVERS 2105 | CAMP EVERS 210533542 | Vegetation | 2022-06-13 22:48 | 6/13 - 6/19 | 2022-06-14 17:36 | 1128 | FTS | 112436 | 525 | 49 | 38 | 13 | 0 | 0 | 0 | 214.1638
22-0073915 | Shasta | STILLWATER 1101 | STILLWATER 11011320 | Unknown | 2022-06-14 04:28 | 6/13 - 6/19 | 2022-06-14 12:06 | 458 | FTS | 136226 | 705 | 55 | 38 | 12 | 0 | 0 | 0 | 193.2284
22-0073935 | Alameda | LAS POSITAS 2108 | LAS POSITAS 2108MR190 | Unknown | 2022-06-14 06:58 | 6/13 - 6/19 | 2022-06-14 11:03 | 245 | FTS | 226041 | 1872 | 95 | 68 | 28 | 0 | 2 | 0 | 120.7484
22-0073959 | El Dorado | DIAMOND SPRINGS 1106 | DIAMOND SPRINGS 110676088 | Unknown | 2022-06-14 08:05 | 6/13 - 6/19 | 2022-06-14 10:21 | 136 | FTS | 45760 | 406 | 41 | 35 | 1 | 0 | 0 | 14 | 112.7094
22-0073977 | Santa Barbara | SANTA YNEZ 1102 | SANTA YNEZ 1102320270 | Equipment | 2022-06-14 08:44 | 6/13 - 6/19 | 2022-06-14 15:26 | 402 | FTS | 56440 | 225 | 4 | 1 | 9 | 0 | 0 | 0 | 250.8444
22-0073986 | Shasta | DESCHUTES 1101 | DESCHUTES 11011380 | Unknown | 2022-06-14 08:48 | 6/13 - 6/19 | 2022-06-14 11:05 | 137 | FTS | 63641 | 588 | 45 | 32 | 8 | 1 | 0 | 2 | 108.233
22-0073996 | Santa Cruz | PAUL SWEET 2106 | PAUL SWEET 21065178 | Vegetation | 2022-06-14 09:05 | 6/13 - 6/19 | 2022-06-14 12:36 | 211 | FTS | 22682 | 267 | 30 | 27 | 5 | 0 | 0 | 1 | 84.9513
22-0073999 | Marin | WOODACRE 1102 | WOODACRE 1102137662 | Unknown | 2022-06-14 09:10 | 6/13 - 6/19 | 2022-06-14 11:42 | 152 | FTS | 115612 | 1890 | 90 | 49 | 28 | 6 | 0 | 0 | 61.1704
22-0074003 | Shasta | STILLWATER 1102 | STILLWATER 11021466 | 3rd Party | 2022-06-14 09:12 | 6/13 - 6/19 | 2022-06-14 12:47 | 215 | FTS | 102125 | 475 | 44 | 32 | 7 | 0 | 0 | 0 | 215
22-0074014 | Tehama | VOLTA 1101 | VOLTA 110185234 | Vegetation | 2022-06-14 09:35 | 6/13 - 6/19 | 2022-06-14 14:43 | 308 | FTS | 165946 | 540 | 22 | 17 | 8 | 1 | 0 | 0 | 307.3074
22-0074036 | Alameda | SUNOL 1101 | SUNOL 1101MR299 | Company Initiated | 2022-06-14 10:01 | 6/13 - 6/19 | 2022-06-14 11:50 | 109 | FTS | 48491 | 499 | 22 | 17 | 29 | 3 | 0 | 0 | 97.1764
22-0074045 | Napa | SILVERADO 2103 | SILVERADO 2103617828 | Unknown | 2022-06-14 10:29 | 6/13 - 6/19 | 2022-06-16 09:54 | 2845 | FTS | 6845 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 207.4242
22-0074057 | Sonoma | MOLINO 1102 | MOLINO 1102104 | Company Initiated | 2022-06-14 10:43 | 6/13 - 6/19 | 2022-06-14 11:55 | 72 | FTS | 149046 | 2094 | 116 | 78 | 25 | 1 | 0 | 17 | 71.1777
22-0074101 | Sonoma | FORT ROSS 1121 | FORT ROSS 1121913812 | Unknown | 2022-06-14 10:46 | 6/13 - 6/19 | 2022-06-14 13:25 | 159 | FTS | 3975 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 159
22-0074128 | Monterey | JOLON 1102 | JOLON 11027004 | Equipment | 2022-06-14 12:34 | 6/13 - 6/19 | 2022-06-24 08:07 | 14133 | FTS | 92621 | 148 | 6 | 5 | 9 | 0 | 0 | 3 | 625.8176
22-0074239 | Fresno | TIVY VALLEY 1107 | TIVY VALLEY 1107822606 | Unknown | 2022-06-14 15:09 | 6/13 - 6/19 | 2022-06-14 17:56 | 167 | FTS | 136608 | 836 | 64 | 46 | 13 | 0 | 0 | 0 | 163.4067
22-0074237 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 21012181 | 3rd Party | 2022-06-14 15:10 | 6/13 - 6/19 | 2022-06-14 18:35 | 205 | FTS | 10455 | 51 | 0 | 0 | 2 | 0 | 0 | 0 | 205
22-0074238 | Shasta | ANTLER SUB | N/A | Equipment | 2022-06-14 15:13 | 6/13 - 6/19 | 2022-06-14 16:35 | 82 | T-EPSS | 71735 | 944 | 61 | 38 | 27 | 2 | 0 | 0 | 75.9905
22-0074288 | Marin | WOODACRE 1101 | WOODACRE 1101404 | Unknown | 2022-06-14 16:23 | 6/13 - 6/19 | 2022-06-14 18:02 | 99 | FTS | 73260 | 740 | 42 | 25 | 18 | 1 | 0 | 0 | 99
22-0074304 | Santa Cruz | BEN LOMOND 0401 | BEN LOMOND 040116010 | Vegetation | 2022-06-14 16:52 | 6/13 - 6/19 | 2022-06-14 18:09 | 77 | FTS | 33974 | 564 | 46 | 36 | 15 | 1 | 0 | 0 | 60.2376
22-0074317 | Madera | SAN JOAQUIN #3 1102 | SAN JOAQUIN #3 11021102/2 | Unknown | 2022-06-14 17:28 | 6/13 - 6/19 | 2022-06-14 20:47 | 199 | FTS | 52138 | 262 | 23 | 18 | 4 | 0 | 0 | 0 | 199
22-0074343 | Tehama | CORNING 1102 | CORNING 11021900 | Animal | 2022-06-14 20:33 | 6/13 - 6/19 | 2022-06-14 22:54 | 141 | FTS | 53104 | 384 | 22 | 15 | 11 | 3 | 0 | 1 | 138.2917
22-0074379 | Tehama | TYLER 1105 | TYLER 11051704 | Unknown | 2022-06-14 23:08 | 6/13 - 6/19 | 2022-06-15 09:14 | 606 | FTS | 167363 | 833 | 87 | 55 | 13 | 2 | 0 | 1 | 200.916
22-0074391 | San Luis Obispo | OCEANO 1104 | OCEANO 1104V38 | Equipment | 2022-06-15 03:52 | 6/13 - 6/19 | 2022-06-15 10:46 | 414 | FTS | 183315 | 1502 | 59 | 51 | 15 | 3 | 0 | 11 | 122.0473
22-0074393 | Nevada | HIGGINS 1104 | HIGGINS 11041006 | Unknown | 2022-06-15 04:23 | 6/13 - 6/19 | 2022-06-15 05:49 | 86 | FTS | 116545 | 1871 | 130 | 90 | 19 | 1 | 0 | 4 | 62.2902
22-0074394 | Monterey | CHOLAME 2102 | CHOLAME 2102796386 | Unknown | 2022-06-15 05:52 | 6/13 - 6/19 | 2022-06-15 09:49 | 237 | FTS | 35316 | 172 | 4 | 4 | 7 | 2 | 0 | 0 | 205.3256
22-0074397 | Lake | HARTLEY 1101 | HARTLEY 1101738 | Animal | 2022-06-15 06:11 | 6/13 - 6/19 | 2022-06-15 07:48 | 97 | FTS | 115624 | 1192 | 78 | 50 | 12 | 6 | 0 | 1 | 97
22-0074401 | Tuolumne | CURTIS 1705 | CURTIS 17058170 | Animal | 2022-06-15 06:23 | 6/13 - 6/19 | 2022-06-15 08:04 | 101 | FTS | 50702 | 502 | 54 | 43 | 4 | 0 | 0 | 0 | 101
22-0074453 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113R82 | 3rd Party | 2022-06-15 08:23 | 6/13 - 6/19 | 2022-06-15 17:07 | 524 | FTS | 93067 | 1706 | 90 | 68 | 19 | 2 | 0 | 12 | 54.5528
22-0074501 | Placer | WISE 1101 | WISE 11011101/2 | Unknown | 2022-06-15 09:04 | 6/13 - 6/19 | 2022-06-15 12:05 | 181 | FTS | 501851 | 2793 | 205 | 142 | 34 | 4 | 0 | 28 | 179.6817
22-0074534 | Placer | PENRYN 1105 | PENRYN 110550550 | 3rd Party | 2022-06-15 09:49 | 6/13 - 6/19 | 2022-06-15 17:57 | 488 | FTS | 52532 | 265 | 17 | 11 | 2 | 0 | 0 | 2 | 198.234
22-0074667 | Sonoma | LAKEVILLE 1102 | LAKEVILLE 110287432 | Unknown | 2022-06-15 13:15 | 6/13 - 6/19 | 2022-06-15 15:10 | 115 | FTS | 7378 | 70 | 5 | 5 | 5 | 0 | 0 | 0 | 105.4
22-0074692 | San Mateo | HALF MOON BAY 1103 | HALF MOON BAY 1103880484 | Unknown | 2022-06-15 14:04 | 6/13 - 6/19 | 2022-06-15 18:25 | 261 | HLT | 283425 | 1947 | 59 | 47 | 55 | 10 | 0 | 4 | 145.5701
22-0074757 | Monterey | LOS OSITOS 2102 | LOS OSITOS 2102258878 | Unknown | 2022-06-15 15:57 | 6/13 - 6/19 | 2022-06-15 17:32 | 95 | FTS | 1520 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 95
22-0074788 | Contra Costa | BRENTWOOD 2105 | BRENTWOOD 2105502672 | 3rd Party | 2022-06-15 17:36 | 6/13 - 6/19 | 2022-06-16 14:27 | 1251 | FTS | 104480 | 117 | 5 | 1 | 17 | 0 | 0 | 0 | 892.9915
22-0074799 | Nevada | BRUNSWICK 1106 | BRUNSWICK 110651486 | Vegetation | 2022-06-15 18:41 | 6/13 - 6/19 | 2022-06-16 02:54 | 493 | FTS | 577585 | 2123 | 144 | 100 | 19 | 3 | 0 | 13 | 272.0608
22-0074812 | Santa Clara | MORGAN HILL 2105 | MORGAN HILL 21052105/2 | 3rd Party | 2022-06-15 20:17 | 6/13 - 6/19 | 2022-06-15 21:12 | 55 | FTS | 236115 | 4293 | 289 | 208 | 47 | 9 | 1 | 4 | 55
22-0074902 | Sonoma | SONOMA 1107 | SONOMA 1107844168 | Unknown | 2022-06-16 02:33 | 6/13 - 6/19 | 2022-06-16 10:34 | 481 | FTS | 60125 | 125 | 2 | 2 | 4 | 0 | 0 | 0 | 481
22-0074905 | Napa | SILVERADO 2103 | SILVERADO 2103403102 | Unknown | 2022-06-16 05:24 | 6/13 - 6/19 | 2022-06-16 09:40 | 256 | FTS | 7680 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 256
22-0074906 | Napa | SILVERADO 2105 | SILVERADO 2105443258 | Unknown | 2022-06-16 05:31 | 6/13 - 6/19 | 2022-06-16 09:58 | 267 | FTS | 3471 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 267
22-0074927 | Placer | WISE 1101 | WISE 11011404 | Animal | 2022-06-16 06:26 | 6/13 - 6/19 | 2022-06-16 08:01 | 95 | FTS | 62795 | 661 | 53 | 34 | 10 | 0 | 0 | 1 | 95
22-0074920 | Shasta | GIRVAN 1101 | GIRVAN 11011101/2 | Animal | 2022-06-16 06:27 | 6/13 - 6/19 | 2022-06-16 07:26 | 59 | FTS | 75461 | 1279 | 103 | 71 | 31 | 6 | 0 | 0 | 59
22-0074943 | Alameda | SAN RAMON 2103 | SAN RAMON 2103MR279 | Unknown | 2022-06-16 06:42 | 6/13 - 6/19 | 2022-06-16 07:49 | 67 | FTS | 12328 | 184 | 0 | 0 | 7 | 0 | 0 | 0 | 67
22-0074938 | Santa Cruz | GREEN VALLEY 2101 | GREEN VALLEY 210111054 | Animal | 2022-06-16 06:49 | 6/13 - 6/19 | 2022-06-16 08:01 | 72 | FTS | 22176 | 308 | 16 | 14 | 10 | 5 | 0 | 0 | 72
22-0074940 | Santa Cruz | ROB ROY 2105 | ROB ROY 21055090 | Unknown | 2022-06-16 06:56 | 6/13 - 6/19 | 2022-06-16 11:14 | 258 | FTS | 111714 | 433 | 24 | 18 | 5 | 1 | 0 | 4 | 258
22-0075093 | Santa Cruz | PAUL SWEET 2107 | PAUL SWEET 210710986 | Unknown | 2022-06-16 11:39 | 6/13 - 6/19 | 2022-06-16 12:47 | 68 | FTS | 11900 | 175 | 10 | 8 | 15 | 0 | 0 | 0 | 68
22-0075174 | Contra Costa | TASSAJARA 2103 | TASSAJARA 21032103/2 | Equipment | 2022-06-16 13:24 | 6/13 - 6/19 | 2022-06-16 15:55 | 151 | FTS | 236721 | 2983 | 207 | 136 | 45 | 6 | 0 | 0 | 79.3567
22-0075281 | Santa Clara | MC KEE 1107 | MC KEE 1107XR010 | Vegetation | 2022-06-16 16:00 | 6/13 - 6/19 | 2022-06-17 03:12 | 672 | FTS | 57335 | 419 | 21 | 15 | 3 | 0 | 0 | 1 | 136.8377
22-0075336 | Marin | WOODACRE 1102 | WOODACRE 1102137662 | Vegetation | 2022-06-16 19:06 | 6/13 - 6/19 | 2022-06-16 19:43 | 37 | FTS | 67730 | 1890 | 90 | 49 | 28 | 6 | 0 | 0 | 35.836
22-0075344 | San Benito | HOLLISTER 2106 | HOLLISTER 21064004 | Unknown | 2022-06-16 19:25 | 6/13 - 6/19 | 2022-06-17 06:57 | 692 | FTS | 41674 | 312 | 17 | 12 | 3 | 1 | 0 | 0 | 133.5705
22-0075359 | Contra Costa | TASSAJARA 2103 | TASSAJARA 21032103/2 | Equipment | 2022-06-16 21:32 | 6/13 - 6/19 | 2022-06-17 12:34 | 902 | FTS | 264523 | 2983 | 207 | 136 | 45 | 6 | 0 | 0 | 88.6768
22-0075381 | Alameda | CASTRO VALLEY 1110 | CASTRO VALLEY 1110MR273 | Vegetation | 2022-06-16 22:33 | 6/13 - 6/19 | 2022-06-17 11:14 | 761 | FTS | 158288 | 208 | 11 | 8 | 1 | 1 | 0 | 2 | 761
22-0075383 | San Luis Obispo | SAN LUIS OBISPO 1107 | SAN LUIS OBISPO 1107V18 | Equipment | 2022-06-16 23:44 | 6/13 - 6/19 | 2022-06-17 09:35 | 591 | FTS | 90541 | 419 | 17 | 15 | 6 | 0 | 0 | 0 | 216.0883
22-0075385 | Santa Clara | MILPITAS 1105 | MILPITAS 11051105/2 | Unknown | 2022-06-17 00:07 | 6/13 - 6/19 | 2022-06-17 01:54 | 107 | FTS | 172205 | 3689 | 128 | 83 | 26 | 8 | 0 | 0 | 46.6807
22-0075396 | Yolo | MADISON 2101 | MADISON 21011606 | Unknown | 2022-06-17 05:30 | 6/13 - 6/19 | 2022-06-17 10:28 | 298 | FTS | 150028 | 512 | 18 | 8 | 6 | 0 | 0 | 1 | 293.0234
22-0075398 | Santa Cruz | ROB ROY 2105 | ROB ROY 210512584 | Unknown | 2022-06-17 05:43 | 6/13 - 6/19 | 2022-06-17 08:58 | 195 | FTS | 464415 | 2737 | 173 | 133 | 41 | 6 | 0 | 0 | 169.6803
22-0075498 | Santa Cruz | PAUL SWEET 2105 | PAUL SWEET 21052105/2 | 3rd Party | 2022-06-17 09:05 | 6/13 - 6/19 | 2022-06-17 12:03 | 178 | FTS | 1135284 | 6378 | 322 | 261 | 65 | 10 | 1 | 1 | 178
22-0075652 | Santa Cruz | PAUL SWEET 2105 | PAUL SWEET 2105959032 | Unknown | 2022-06-17 09:05 | 6/13 - 6/19 | 2022-06-17 12:51 | 226 | FTS | 5650 | 25 | 3 | 3 | 1 | 0 | 0 | 0 | 226
22-0075562 | Sonoma | PETALUMA C 1109 | PETALUMA C 1109820458 | Unknown | 2022-06-17 09:47 | 6/13 - 6/19 | 2022-06-17 12:33 | 166 | FTS | 8964 | 54 | 1 | 0 | 0 | 0 | 0 | 0 | 166
22-0075691 | Sonoma | MIRABEL 1101 | MIRABEL 1101116 | Vegetation | 2022-06-17 13:15 | 6/13 - 6/19 | 2022-06-17 15:34 | 139 | FTS | 38227 | 385 | 16 | 13 | 2 | 0 | 0 | 0 | 99.2909
22-0075788 | Sonoma | MONTE RIO 1111 | MONTE RIO 1111256 | Vegetation | 2022-06-17 15:00 | 6/13 - 6/19 | 2022-06-17 21:59 | 419 | FTS | 185270 | 1488 | 69 | 42 | 32 | 3 | 0 | 2 | 124.5094
22-0075777 | Mendocino | WILLITS 1104 | WILLITS 110434008 | Unknown | 2022-06-17 15:22 | 6/13 - 6/19 | 2022-06-17 17:02 | 100 | FTS | 36700 | 571 | 38 | 31 | 19 | 0 | 0 | 0 | 64.2732
22-0075846 | Santa Cruz | CAMP EVERS 2106 | CAMP EVERS 2106737512 | Vegetation | 2022-06-17 20:19 | 6/13 - 6/19 | 2022-06-18 07:50 | 691 | FTS | 23440 | 917 | 71 | 48 | 10 | 0 | 0 | 0 | 25.5616
22-0075847 | Butte | PARADISE 1106 | PARADISE 110636042 | Equipment | 2022-06-17 20:43 | 6/13 - 6/19 | 2022-06-18 04:12 | 449 | FTS | 51686 | 304 | 15 | 11 | 7 | 0 | 0 | 0 | 170.0197
22-0075848 | Butte | ORO FINO 1101 | ORO FINO 11011101/2 | Equipment | 2022-06-17 20:45 | 6/13 - 6/19 | 2022-06-18 00:44 | 239 | FTS | 396082 | 2379 | 280 | 209 | 19 | 1 | 0 | 0 | 166.491
22-0075865 | Napa | SILVERADO 2102 | SILVERADO 210258626 | Unknown | 2022-06-18 03:33 | 6/13 - 6/19 | 2022-06-18 11:01 | 448 | FTS | 149824 | 335 | 3 | 3 | 5 | 0 | 0 | 2 | 447.2358
22-0075872 | Butte | WYANDOTTE 1109 | WYANDOTTE 110979932 | Unknown | 2022-06-18 06:14 | 6/13 - 6/19 | 2022-06-18 10:43 | 269 | FTS | 109752 | 408 | 52 | 36 | 1 | 0 | 0 | 1 | 269
22-0075896 | Plumas | CHESTER 1102 | CHESTER 11021102/2 | Unknown | 2022-06-18 09:24 | 6/13 - 6/19 | 2022-06-18 10:04 | 40 | FTS | 26600 | 665 | 33 | 29 | 21 | 2 | 0 | 0 | 40
22-0075902 | San Luis Obispo | FOOTHILL 1102 | FOOTHILL 110299432 | 3rd Party | 2022-06-18 10:15 | 6/13 - 6/19 | 2022-06-18 11:37 | 82 | FTS | 183024 | 2232 | 52 | 38 | 23 | 3 | 0 | 0 | 82
22-0075908 | Nevada | BRUNSWICK 1102 | BRUNSWICK 11021010 | 3rd Party | 2022-06-18 10:56 | 6/13 - 6/19 | 2022-06-18 19:01 | 485 | FTS | 248814 | 668 | 43 | 31 | 3 | 0 | 0 | 5 | 372.476
22-0075931 | Contra Costa | NORTH DUBLIN 2103 | NORTH DUBLIN 21032103/2 | Equipment | 2022-06-18 13:32 | 6/13 - 6/19 | 2022-06-19 03:23 | 831 | FTS | 756121 | 4925 | 164 | 114 | 51 | 6 | 0 | 0 | 153.5271
22-0075947 | Contra Costa | LAKEWOOD 1103 | LAKEWOOD 1103857172 | 3rd Party | 2022-06-18 15:41 | 6/13 - 6/19 | 2022-06-18 16:32 | 51 | FTS | 3978 | 78 | 5 | 3 | 1 | 0 | 0 | 0 | 51
22-0075950 | El Dorado | SHINGLE SPRINGS 1104 | SHINGLE SPRINGS 1104556218 | 3rd Party | 2022-06-18 16:15 | 6/13 - 6/19 | 2022-06-18 17:45 | 90 | FTS | 57330 | 637 | 65 | 41 | 4 | 0 | 0 | 13 | 90
22-0075969 | Marin | SAN RAFAEL 1107 | SAN RAFAEL 11071276 | Animal | 2022-06-18 19:00 | 6/13 - 6/19 | 2022-06-18 19:45 | 45 | FTS | 13545 | 301 | 14 | 8 | 3 | 0 | 0 | 0 | 45
22-0075991 | Alameda | VINEYARD 2108 | VINEYARD 2108MR172 | Equipment | 2022-06-18 22:38 | 6/13 - 6/19 | 2022-06-19 13:38 | 900 | FTS | 1675677 | 3026 | 173 | 116 | 38 | 2 | 0 | 0 | 553.7597
22-0075996 | El Dorado | APPLE HILL 2102 | APPLE HILL 210251792 | Equipment | 2022-06-19 00:40 | 6/13 - 6/19 | 2022-06-19 09:45 | 545 | FTS | 466242 | 856 | 60 | 36 | 11 | 0 | 0 | 3 | 544.6752
22-0076002 | Yuba | BANGOR 1101 | BANGOR 1101870548 | Equipment | 2022-06-19 02:39 | 6/13 - 6/19 | 2022-06-19 13:07 | 628 | FTS | 21498 | 60 | 8 | 6 | 0 | 0 | 0 | 0 | 358.3
22-0076008 | Contra Costa | SAN RAMON 2107 | SAN RAMON 21072107/2 | Animal | 2022-06-19 06:42 | 6/13 - 6/19 | 2022-06-19 08:27 | 105 | FTS | 521059 | 5135 | 242 | 170 | 66 | 8 | 0 | 1 | 101.4721
22-0076013 | El Dorado | SHINGLE SPRINGS 2105 | SHINGLE SPRINGS 210511172 | Animal | 2022-06-19 07:32 | 6/13 - 6/19 | 2022-06-19 09:00 | 88 | FTS | 51744 | 588 | 52 | 34 | 6 | 0 | 0 | 0 | 88
22-0076022 | Humboldt | GARBERVILLE 1102 | GARBERVILLE 11022124 | Unknown | 2022-06-19 09:05 | 6/13 - 6/19 | 2022-06-19 10:34 | 89 | FTS | 356 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 89
22-0076028 | Nevada | BRUNSWICK 1102 | BRUNSWICK 11021010 | Animal | 2022-06-19 09:54 | 6/13 - 6/19 | 2022-06-19 12:56 | 182 | FTS | 121576 | 668 | 43 | 31 | 3 | 0 | 0 | 5 | 182
22-0076030 | Santa Cruz | BIG BASIN 1101 | BIG BASIN 110110720 | Unknown | 2022-06-19 10:09 | 6/13 - 6/19 | 2022-06-19 14:53 | 284 | FTS | 621604 | 2225 | 177 | 141 | 32 | 3 | 0 | 1 | 279.3726
22-0076040 | San Benito | HOLLISTER 2105 | HOLLISTER 21054048 | 3rd Party | 2022-06-19 12:19 | 6/13 - 6/19 | 2022-06-20 02:06 | 827 | FTS | 29069 | 127 | 4 | 2 | 2 | 2 | 0 | 0 | 228.8898
22-0076052 | San Luis Obispo | OCEANO 1104 | OCEANO 1104V38 | Vegetation | 2022-06-19 15:12 | 6/13 - 6/19 | 2022-06-19 16:31 | 79 | FTS | 118658 | 1502 | 59 | 51 | 15 | 3 | 0 | 11 | 79
22-0076066 | Tehama | COTTONWOOD 1103 | COTTONWOOD 11031616 | Unknown | 2022-06-19 18:15 | 6/13 - 6/19 | 2022-06-19 20:35 | 140 | FTS | 77420 | 553 | 38 | 25 | 6 | 0 | 0 | 0 | 140
22-0076102 | Santa Cruz | ROB ROY 2104 | ROB ROY 210410298 | Vegetation | 2022-06-20 04:08 | 6/20 - 6/26 | 2022-06-20 06:41 | 153 | FTS | 34272 | 224 | 14 | 12 | 0 | 0 | 0 | 0 | 153
22-0076103 | Yolo | MADISON 2101 | MADISON 210189332 | Unknown | 2022-06-20 05:10 | 6/20 - 6/26 | 2022-06-20 09:30 | 260 | FTS | 184462 | 711 | 19 | 9 | 15 | 12 | 0 | 1 | 259.4402
22-0076115 | Santa Clara | STELLING 1110 | STELLING 1110LL72 | 3rd Party | 2022-06-20 06:32 | 6/20 - 6/26 | 2022-06-21 02:15 | 1183 | FTS | 266873 | 855 | 24 | 21 | 13 | 0 | 0 | 0 | 312.1322
22-0076133 | Napa | SILVERADO 2104 | SILVERADO 2104632 | Animal | 2022-06-20 09:07 | 6/20 - 6/26 | 2022-06-20 12:11 | 184 | FTS | 134051 | 742 | 33 | 20 | 17 | 3 | 0 | 1 | 180.6617
22-0076143 | Tehama | CORNING 1101 | CORNING 110182846 | Animal | 2022-06-20 09:53 | 6/20 - 6/26 | 2022-06-20 11:43 | 110 | FTS | 14630 | 133 | 11 | 8 | 4 | 2 | 0 | 0 | 110
22-0076173 | San Luis Obispo | SAN LUIS OBISPO 1107 | SAN LUIS OBISPO 1107V58 | Vegetation | 2022-06-20 12:13 | 6/20 - 6/26 | 2022-06-20 14:13 | 120 | FTS | 99643 | 2520 | 65 | 46 | 48 | 4 | 2 | 21 | 39.5409
22-0076191 | Santa Barbara | SANTA YNEZ 1104 | SANTA YNEZ 110477098 | Equipment | 2022-06-20 13:19 | 6/20 - 6/26 | 2022-06-20 14:18 | 59 | FTS | 8201 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 59
22-0076224 | Monterey | SAN MIGUEL 1106 | SAN MIGUEL 1106605393 | Unknown | 2022-06-20 16:08 | 6/20 - 6/26 | 2022-06-20 19:52 | 224 | FTS | 20160 | 90 | 2 | 1 | 1 | 0 | 0 | 0 | 224
22-0076231 | Santa Cruz | BIG BASIN 1102 | BIG BASIN 110296986 | Vegetation | 2022-06-20 16:34 | 6/20 - 6/26 | 2022-06-21 01:17 | 523 | FTS | 106056 | 831 | 48 | 33 | 14 | 1 | 0 | 1 | 127.6245
22-0076236 | Santa Clara | LOS GATOS 1106 | LOS GATOS 1106LB44 | Vegetation | 2022-06-20 16:52 | 6/20 - 6/26 | 2022-06-21 01:56 | 544 | FTS | 77104 | 336 | 22 | 18 | 8 | 4 | 0 | 1 | 229.4762
22-0076263 | Sonoma | GEYSERVILLE 1102 | GEYSERVILLE 1102274 | Unknown | 2022-06-20 19:37 | 6/20 - 6/26 | 2022-06-20 21:15 | 98 | FTS | 35116 | 422 | 11 | 3 | 8 | 1 | 0 | 1 | 83.2133
22-0076270 | Santa Clara | SARATOGA 1107 | SARATOGA 1107LC26 | Animal | 2022-06-20 19:55 | 6/20 - 6/26 | 2022-06-21 11:38 | 943 | FTS | 247585 | 672 | 32 | 22 | 9 | 1 | 0 | 0 | 368.4301
22-0076307 | Contra Costa | MORAGA 1105 | MORAGA 11051105/2 | Equipment | 2022-06-20 23:08 | 6/20 - 6/26 | 2022-06-21 18:35 | 1167 | FTS | 545697 | 1896 | 98 | 74 | 17 | 6 | 0 | 0 | 287.8149
22-0076308 | El Dorado | SHINGLE SPRINGS 2105 | SHINGLE SPRINGS 210511172 | Equipment | 2022-06-20 23:08 | 6/20 - 6/26 | 2022-06-21 02:12 | 184 | FTS | 108192 | 588 | 52 | 34 | 6 | 0 | 0 | 0 | 184
22-0076320 | Glenn | ELK CREEK 1101 | ELK CREEK 110137334 | Animal | 2022-06-21 04:31 | 6/20 - 6/26 | 2022-06-21 07:09 | 158 | FTS | 49840 | 322 | 22 | 19 | 11 | 5 | 0 | 0 | 154.7826
22-0076332 | Santa Barbara | BUELLTON 1101 | BUELLTON 1101Y26 | Unknown | 2022-06-21 06:31 | 6/20 - 6/26 | 2022-06-21 08:55 | 144 | FTS | 20592 | 188 | 7 | 5 | 7 | 0 | 0 | 0 | 109.5319
22-0076355 | Contra Costa | FAIRVIEW 2207 | FAIRVIEW 2207P148 | Unknown | 2022-06-21 08:10 | 6/20 - 6/26 | 2022-06-21 10:48 | 158 | FTS | 116920 | 740 | 39 | 27 | 7 | 2 | 0 | 0 | 158
22-0076359 | Contra Costa | FAIRVIEW 2207 | FAIRVIEW 2207M501R | Company Initiated | 2022-06-21 08:10 | 6/20 - 6/26 | 2022-06-21 13:11 | 301 | FTS | 269779 | 1349 | 59 | 35 | 28 | 4 | 0 | 0 | 199.9844
22-0076411 | Tehama | LOS MOLINOS 1101 | LOS MOLINOS 11011308 | Unknown | 2022-06-21 09:50 | 6/20 - 6/26 | 2022-06-21 11:54 | 124 | FTS | 20034 | 233 | 15 | 9 | 4 | 3 | 0 | 0 | 85.9828
22-0076449 | Marin | OLEMA 1101 | OLEMA 11011200 | Unknown | 2022-06-21 10:41 | 6/20 - 6/26 | 2022-06-21 12:18 | 97 | FTS | 22601 | 233 | 6 | 4 | 6 | 1 | 0 | 0 | 97
22-0076483 | Monterey | SOLEDAD 2105 | SOLEDAD 2105315500 | Equipment | 2022-06-21 11:46 | 6/20 - 6/26 | 2022-06-21 18:46 | 420 | FTS | 3192 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 187.7647
22-0076507 | San Mateo | MENLO 1102 | MENLO 1102W80 | Vegetation | 2022-06-21 12:49 | 6/20 - 6/26 | 2022-06-21 20:05 | 436 | FTS | 53628 | 123 | 52 | 42 | 31 | 2 | 0 | 3 | 436
22-0076511 | San Mateo | HALF MOON BAY 1103 | HALF MOON BAY 1103655644 | Unknown | 2022-06-21 12:58 | 6/20 - 6/26 | 2022-06-21 16:30 | 212 | FTS | 29256 | 138 | 2 | 2 | 11 | 0 | 0 | 0 | 212
22-0076527 | San Mateo | HALF MOON BAY 1103 | HALF MOON BAY 1103655644 | Equipment | 2022-06-21 12:58 | 6/20 - 6/26 | 2022-06-22 14:23 | 1525 | FTS | 79799 | 97 | 3 | 3 | 9 | 4 | 0 | 0 | 822.6701
22-0076582 | Napa | CALISTOGA 1102 | CALISTOGA 11021102/2 | Company Initiated | 2022-06-21 14:21 | 6/20 - 6/26 | 2022-06-21 17:55 | 214 | FTS | 407107 | 2154 | 64 | 40 | 31 | 6 | 0 | 1 | 189.0005
22-0076640 | Santa Cruz | PAUL SWEET 2107 | PAUL SWEET 210710986 | Unknown | 2022-06-21 16:24 | 6/20 - 6/26 | 2022-06-21 18:27 | 123 | FTS | 20655 | 175 | 10 | 8 | 15 | 0 | 0 | 0 | 118.0286
22-0076664 | Santa Clara | MORGAN HILL 2111 | MORGAN HILL 21112111/2 | 3rd Party | 2022-06-21 17:19 | 6/20 - 6/26 | 2022-06-22 05:57 | 758 | FTS | 1828274 | 2685 | 156 | 104 | 38 | 4 | 0 | 3 | 680.9214
22-0076666 | Santa Clara | MORGAN HILL 2109 | MORGAN HILL 2109XR246 | Unknown | 2022-06-21 17:19 | 6/20 - 6/26 | 2022-06-21 20:29 | 190 | FTS | 504775 | 4180 | 204 | 132 | 44 | 5 | 0 | 0 | 120.7596
22-0076665 | Shasta | RISING RIVER 1101 | RISING RIVER 11011101/2 | Equipment | 2022-06-21 17:26 | 6/20 - 6/26 | 2022-06-22 04:22 | 656 | FTS | 363384 | 725 | 46 | 44 | 14 | 0 | 0 | 0 | 501.2193
22-0076676 | El Dorado | APPLE HILL 1104 | APPLE HILL 110413512 | Unknown | 2022-06-21 17:59 | 6/20 - 6/26 | 2022-06-21 21:22 | 203 | FTS | 190008 | 936 | 59 | 35 | 12 | 0 | 0 | 1 | 203
22-0076678 | Santa Clara | SARATOGA 1103 | SARATOGA 1103LC40 | Equipment | 2022-06-21 18:06 | 6/20 - 6/26 | 2022-06-21 22:00 | 234 | FTS | 81464 | 1218 | 30 | 17 | 21 | 4 | 0 | 0 | 66.8834
22-0076689 | Alameda | SAN RAMON 2107 | SAN RAMON 2107MR284 | Equipment | 2022-06-21 18:29 | 6/20 - 6/26 | 2022-06-22 10:39 | 970 | FTS | 204733 | 1168 | 46 | 36 | 20 | 1 | 0 | 1 | 175.2851
22-0076766 | Alameda | SAN RAMON 2103 | SAN RAMON 2103MR279 | Equipment | 2022-06-21 18:36 | 6/20 - 6/26 | 2022-06-22 03:26 | 530 | FTS | 81643 | 184 | 0 | 0 | 7 | 0 | 0 | 0 | 443.712
22-0076695 | Alameda | OAKLAND X 1104 | OAKLAND X 1104CR101 | Company Initiated | 2022-06-21 18:51 | 6/20 - 6/26 | 2022-06-21 19:47 | 56 | FTS | 34552 | 617 | 22 | 18 | 8 | 0 | 0 | 0 | 56
22-0076709 | Kern | MAGUNDEN 1108 | MAGUNDEN 1108250674 | Unknown | 2022-06-21 20:14 | 6/20 - 6/26 | 2022-06-21 22:21 | 127 | FTS | 13208 | 104 | 1 | 1 | 1 | 0 | 0 | 0 | 127
22-0076714 | Sonoma | RINCON 1101 | RINCON 1101576 | Equipment | 2022-06-21 20:16 | 6/20 - 6/26 | 2022-06-22 19:34 | 1398 | FTS | 1603636 | 2381 | 219 | 167 | 36 | 0 | 0 | 5 | 673.5136
22-0076722 | Humboldt | HOOPA 1101 | HOOPA 11013174 | Vegetation | 2022-06-21 20:55 | 6/20 - 6/26 | 2022-06-22 13:24 | 989 | FTS | 482632 | 488 | 9 | 7 | 13 | 3 | 0 | 0 | 989
22-0076752 | Santa Clara | SARATOGA 1106 | SARATOGA 1106340986 | Vegetation | 2022-06-21 22:26 | 6/20 - 6/26 | 2022-06-21 23:45 | 79 | FTS | 45583 | 577 | 30 | 14 | 5 | 0 | 0 | 0 | 79
22-0076761 | Napa | PUEBLO 2104 | PUEBLO 2104656 | Unknown | 2022-06-21 22:54 | 6/20 - 6/26 | 2022-06-22 09:22 | 628 | FTS | 209124 | 333 | 12 | 7 | 12 | 0 | 0 | 0 | 628
22-0076763 | Shasta | PIT NO 3 2101 | PIT NO 3 21012101/2 | Equipment | 2022-06-21 23:27 | 6/20 - 6/26 | 2022-06-22 13:55 | 868 | FTS | 45375 | 152 | 4 | 4 | 3 | 0 | 0 | 0 | 298.5197
22-0076776 | Kern | POSO MOUNTAIN 2103 | POSO MOUNTAIN 21032103/2 | Unknown | 2022-06-22 03:22 | 6/20 - 6/26 | 2022-06-22 04:36 | 74 | FTS | 1998 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 74
22-0076777 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 21014456 | Unknown | 2022-06-22 03:45 | 6/20 - 6/26 | 2022-06-23 13:01 | 1996 | FTS | 144874 | 79 | 4 | 3 | 2 | 0 | 0 | 0 | 1833.8481
22-0076785 | Tulare | OROSI 1102 | OROSI 11021102/2 | Equipment | 2022-06-22 05:32 | 6/20 - 6/26 | 2022-06-22 09:02 | 210 | FTS | 50363 | 375 | 5 | 4 | 1 | 0 | 0 | 0 | 134.3013
22-0076788 | Fresno | TIVY VALLEY 1107 | TIVY VALLEY 11077380 | Equipment | 2022-06-22 05:42 | 6/20 - 6/26 | 2022-06-23 04:20 | 1358 | FTS | 272420 | 750 | 53 | 34 | 16 | 0 | 0 | 0 | 363.2267
22-0076791 | Marin | LAS GALLINAS A 1107 | LAS GALLINAS A 1107554 | Animal | 2022-06-22 05:49 | 6/20 - 6/26 | 2022-06-22 07:12 | 83 | FTS | 70052 | 844 | 39 | 20 | 16 | 4 | 0 | 0 | 83
22-0076794 | Kern | POSO MOUNTAIN 2103 | POSO MOUNTAIN 21032103/2 | Environmental/External | 2022-06-22 05:50 | 6/20 - 6/26 | 2022-06-22 17:50 | 720 | FTS | 16983 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 629
22-0076793 | San Luis Obispo | OCEANO 1104 | OCEANO 1104V38 | Animal | 2022-06-22 05:56 | 6/20 - 6/26 | 2022-06-22 08:19 | 143 | FTS | 203132 | 1502 | 59 | 51 | 15 | 3 | 0 | 11 | 135.241
22-0076795 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 21012181 | Animal | 2022-06-22 05:59 | 6/20 - 6/26 | 2022-06-23 02:08 | 1209 | FTS | 61659 | 51 | 0 | 0 | 2 | 0 | 0 | 0 | 1209
22-0076798 | Amador | CLAY 1103 | CLAY 11031230 | Unknown | 2022-06-22 06:15 | 6/20 - 6/26 | 2022-06-22 08:53 | 158 | FTS | 16748 | 106 | 3 | 3 | 4 | 0 | 0 | 0 | 158
22-0076804 | San Benito | SAN JUSTO 1101 | SAN JUSTO 11014002 | Animal | 2022-06-22 06:30 | 6/20 - 6/26 | 2022-06-22 08:20 | 110 | FTS | 18700 | 170 | 9 | 5 | 13 | 0 | 0 | 1 | 110
22-0076809 | Fresno | AUBERRY 1101 | AUBERRY 1101R2578 | Unknown | 2022-06-22 06:36 | 6/20 - 6/26 | 2022-06-22 12:38 | 362 | FTS | 394531 | 1375 | 117 | 81 | 17 | 4 | 0 | 6 | 286.9316
22-0076818 | Contra Costa | FAIRVIEW 2207 | FAIRVIEW 22072207/2 | Company Initiated | 2022-06-22 06:59 | 6/20 - 6/26 | 2022-06-22 09:15 | 136 | FTS | 629408 | 4628 | 217 | 137 | 90 | 10 | 0 | 0 | 136
22-0076821 | Fresno | KERCKHOFF 1101 | KERCKHOFF 1101R308 | Unknown | 2022-06-22 07:07 | 6/20 - 6/26 | 2022-06-22 13:33 | 386 | FTS | 11580 | 30 | 2 | 0 | 1 | 0 | 0 | 0 | 386
22-0076823 | Fresno | WOODWARD 2108 | WOODWARD 2108R2860 | Equipment | 2022-06-22 07:09 | 6/20 - 6/26 | 2022-06-23 12:37 | 1768 | FTS | 107794 | 464 | 33 | 19 | 13 | 0 | 0 | 0 | 232.3147
22-0076850 | Madera | COARSEGOLD 2103 | COARSEGOLD 21035020 | Unknown | 2022-06-22 07:33 | 6/20 - 6/26 | 2022-06-22 15:41 | 488 | FTS | 297255 | 1189 | 126 | 86 | 59 | 6 | 0 | 0 | 250.0042
22-0076860 | Madera | COARSEGOLD 2102 | COARSEGOLD 210210890 | Unknown | 2022-06-22 07:43 | 6/20 - 6/26 | 2022-06-22 14:01 | 378 | FTS | 351614 | 1365 | 109 | 83 | 34 | 6 | 0 | 2 | 257.5927
22-0076888 | Fresno | DUNLAP 1102 | DUNLAP 11021102/2 | Vegetation | 2022-06-22 08:00 | 6/20 - 6/26 | 2022-06-22 13:12 | 312 | FTS | 218400 | 700 | 34 | 25 | 13 | 1 | 0 | 0 | 312
22-0076914 | Fresno | BALCH NO 1 1101 | BALCH NO 1 1101105414 | Equipment | 2022-06-22 08:22 | 6/20 - 6/26 | 2022-06-24 17:48 | 3446 | FTS | 93897 | 28 | 0 | 0 | 1 | 2 | 0 | 0 | 3353.4643
22-0076956 | Fresno | TIVY VALLEY 1107 | TIVY VALLEY 1107822606 | Unknown | 2022-06-22 09:19 | 6/20 - 6/26 | 2022-06-22 13:38 | 259 | FTS | 216244 | 837 | 64 | 46 | 13 | 0 | 0 | 0 | 258.356
22-0076963 | Tulare | OROSI 1102 | OROSI 11021102/2 | Equipment | 2022-06-22 09:20 | 6/20 - 6/26 | 2022-06-23 10:47 | 1527 | FTS | 449442 | 383 | 5 | 4 | 1 | 0 | 0 | 0 | 1173.4778
22-0076975 | Solano | VACAVILLE 1108 | VACAVILLE 11088762 | 3rd Party | 2022-06-22 09:31 | 6/20 - 6/26 | 2022-06-22 12:28 | 177 | FTS | 37915 | 425 | 22 | 15 | 15 | 1 | 0 | 2 | 89.2118
22-0076978 | Kern | LAMONT 1104 | LAMONT 11044113 | Environmental/External | 2022-06-22 09:35 | 6/20 - 6/26 | 2022-06-22 20:35 | 660 | FTS | 5806 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 175.9394
22-0076995 | Kern | LAMONT 1102 | LAMONT 11021644 | Unknown | 2022-06-22 09:35 | 6/20 - 6/26 | 2022-06-22 13:47 | 252 | FTS | 22176 | 88 | 1 | 0 | 3 | 0 | 0 | 0 | 252
22-0076976 | Kern | MAGUNDEN 1108 | MAGUNDEN 1108250674 | 3rd Party | 2022-06-22 09:36 | 6/20 - 6/26 | 2022-06-22 12:32 | 176 | FTS | 18304 | 104 | 1 | 1 | 1 | 0 | 0 | 0 | 176
22-0076989 | Madera | SAN JOAQUIN #3 1102 | SAN JOAQUIN #3 11021102/2 | Vegetation | 2022-06-22 09:49 | 6/20 - 6/26 | 2022-06-22 15:06 | 317 | FTS | 79926 | 262 | 23 | 18 | 4 | 0 | 0 | 0 | 305.0611
22-0077008 | Tulare | SAND CREEK 1103 | SAND CREEK 11037070 | Unknown | 2022-06-22 09:52 | 6/20 - 6/26 | 2022-06-22 16:22 | 390 | FTS | 115440 | 296 | 9 | 6 | 12 | 1 | 0 | 0 | 390
22-0077134 | Placer | PENRYN 1105 | PENRYN 11051105/2 | 3rd Party | 2022-06-22 11:50 | 6/20 - 6/26 | 2022-06-22 22:00 | 610 | FTS | 182871 | 1888 | 115 | 72 | 32 | 9 | 0 | 18 | 96.8596
22-0077221 | Placer | BONNIE NOOK 1102 | BONNIE NOOK 11021102/2 | 3rd Party | 2022-06-22 13:55 | 6/20 - 6/26 | 2022-06-22 18:36 | 281 | FTS | 150335 | 535 | 27 | 16 | 15 | 2 | 0 | 0 | 281
22-0077226 | Nevada | NARROWS 2105 | NARROWS 21052228 | Animal | 2022-06-22 14:18 | 6/20 - 6/26 | 2022-06-22 19:05 | 287 | FTS | 72337 | 263 | 10 | 6 | 5 | 0 | 0 | 2 | 275.0456
22-0077233 | Nevada | NARROWS 2105 | NARROWS 21052426 | Animal | 2022-06-22 14:18 | 6/20 - 6/26 | 2022-06-22 18:46 | 268 | FTS | 511187 | 2105 | 179 | 103 | 28 | 4 | 0 | 19 | 242.8442
22-0077274 | Napa | SILVERADO 2104 | SILVERADO 2104632 | Unknown | 2022-06-22 15:01 | 6/20 - 6/26 | 2022-06-22 18:33 | 212 | FTS | 157092 | 741 | 33 | 20 | 17 | 3 | 0 | 1 | 212
22-0077282 | Tulare | STONE CORRAL 1108 | STONE CORRAL 1108255186 | Unknown | 2022-06-22 15:26 | 6/20 - 6/26 | 2022-06-22 17:28 | 122 | FTS | 6710 | 55 | 2 | 1 | 0 | 0 | 0 | 0 | 122
22-0077385 | Kern | LAMONT 1104 | LAMONT 11044113 | Environmental/External | 2022-06-22 17:07 | 6/20 - 6/26 | 2022-06-24 02:04 | 1977 | FTS | 7806 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 260.2
22-0077399 | Monterey | LOS OSITOS 2103 | LOS OSITOS 21031132 | Environmental/External | 2022-06-22 18:56 | 6/20 - 6/26 | 2022-06-24 00:28 | 1772 | FTS | 183548 | 165 | 3 | 3 | 4 | 1 | 0 | 0 | 1112.4121
22-0077405 | Monterey | SOLEDAD 2101 | SOLEDAD 21017048 | Unknown | 2022-06-22 19:13 | 6/20 - 6/26 | 2022-06-23 10:52 | 939 | FTS | 59482 | 172 | 3 | 3 | 3 | 0 | 0 | 0 | 345.8256
22-0077481 | Sonoma | GEYSERVILLE 1102 | GEYSERVILLE 1102274 | Company Initiated | 2022-06-22 22:46 | 6/20 - 6/26 | 2022-06-23 06:41 | 475 | FTS | 200060 | 422 | 11 | 3 | 8 | 1 | 0 | 1 | 474.0758
22-0077506 | Shasta | GIRVAN 1102 | GIRVAN 11021102/2 | Animal | 2022-06-23 01:01 | 6/20 - 6/26 | 2022-06-23 08:47 | 466 | FTS | 282772 | 1452 | 96 | 72 | 18 | 0 | 0 | 1 | 194.7466
22-0077523 | El Dorado | CLARKSVILLE 2103 | CLARKSVILLE 2103593454 | 3rd Party | 2022-06-23 05:03 | 6/20 - 6/26 | 2022-06-23 12:30 | 447 | FTS | 42969 | 375 | 32 | 26 | 13 | 4 | 0 | 14 | 114.584
22-0077529 | Monterey | DEL MONTE 2104 | DEL MONTE 21042624 | Animal | 2022-06-23 06:05 | 6/20 - 6/26 | 2022-06-23 09:50 | 225 | FTS | 313275 | 3227 | 163 | 123 | 90 | 1 | 0 | 1 | 97.0793
22-0077533 | Santa Clara | SARATOGA 1104 | SARATOGA 110413314 | Unknown | 2022-06-23 06:11 | 6/20 - 6/26 | 2022-06-23 08:52 | 161 | FTS | 132102 | 1008 | 60 | 44 | 11 | 2 | 0 | 0 | 131.0536
22-0077549 | Contra Costa | MORAGA 1105 | MORAGA 1105829530 | Unknown | 2022-06-23 06:51 | 6/20 - 6/26 | 2022-06-23 08:46 | 115 | FTS | 43815 | 381 | 20 | 14 | 3 | 0 | 0 | 0 | 115
22-0077556 | Nevada | NARROWS 2105 | NARROWS 21052426 | Animal | 2022-06-23 07:08 | 6/20 - 6/26 | 2022-06-23 10:45 | 217 | FTS | 317981 | 2105 | 179 | 103 | 28 | 4 | 0 | 19 | 151.0599
22-0077560 | Solano | JAMESON 1105 | JAMESON 1105466348 | Animal | 2022-06-23 07:21 | 6/20 - 6/26 | 2022-06-23 08:53 | 92 | FTS | 32476 | 353 | 12 | 6 | 8 | 2 | 0 | 2 | 92
22-0077623 | Yuba | BANGOR 1101 | BANGOR 11017446 | Unknown | 2022-06-23 09:08 | 6/20 - 6/26 | 2022-06-23 10:41 | 93 | FTS | 49662 | 534 | 47 | 31 | 4 | 0 | 0 | 2 | 93
22-0077670 | San Benito | HOLLISTER 2105 | HOLLISTER 21054048 | Equipment | 2022-06-23 10:11 | 6/20 - 6/26 | 2022-06-23 21:23 | 672 | FTS | 31104 | 127 | 4 | 2 | 2 | 2 | 0 | 0 | 244.9134
22-0077692 | San Benito | SAN JUSTO 1101 | SAN JUSTO 1101201311 | Unknown | 2022-06-23 10:52 | 6/20 - 6/26 | 2022-06-23 12:17 | 85 | FTS | 14110 | 166 | 9 | 8 | 3 | 0 | 0 | 0 | 85
22-0077725 | Lake | HIGHLANDS 1102 | HIGHLANDS 1102623120 | 3rd Party | 2022-06-23 11:48 | 6/20 - 6/26 | 2022-06-23 12:52 | 64 | FTS | 39936 | 624 | 52 | 35 | 11 | 0 | 0 | 4 | 64
22-0077755 | San Benito | SAN JUSTO 1101 | SAN JUSTO 1101201311 | Equipment | 2022-06-23 12:29 | 6/20 - 6/26 | 2022-06-23 19:47 | 438 | FTS | 14680 | 166 | 9 | 8 | 3 | 0 | 0 | 0 | 88.4337
22-0077759 | Fresno | SAND CREEK 1103 | SAND CREEK 1103818064 | Unknown | 2022-06-23 12:32 | 6/20 - 6/26 | 2022-06-23 16:02 | 210 | FTS | 108570 | 517 | 93 | 58 | 8 | 0 | 0 | 0 | 210
22-0077836 | Solano | VACA DIXON 1105 | VACA DIXON 110540092 | 3rd Party | 2022-06-23 13:56 | 6/20 - 6/26 | 2022-06-24 04:03 | 847 | FTS | 118659 | 1410 | 146 | 108 | 20 | 0 | 0 | 9 | 84.1553
22-0077853 | Calaveras | SALT SPRINGS 2101 | SALT SPRINGS 21011232 | Equipment | 2022-06-23 14:18 | 6/20 - 6/26 | 2022-06-24 10:30 | 1212 | FTS | 301600 | 917 | 14 | 12 | 10 | 2 | 0 | 0 | 328.8986
22-0077403 | San Mateo | SAN CARLOS 1104 | SAN CARLOS 11048858 | Company Initiated | 2022-06-23 15:50 | 6/20 - 6/26 | 2022-06-23 16:49 | 59 | FTS | 13556 | 261 | 58 | 45 | 22 | 1 | 0 | 1 | 51.9387
22-0077905 | Plumas | GANSNER 1101 | GANSNER 1101782320 | Unknown | 2022-06-23 16:25 | 6/20 - 6/26 | 2022-06-23 18:49 | 144 | FTS | 3456 | 24 | 3 | 1 | 0 | 0 | 0 | 0 | 144
22-0077934 | Napa | SILVERADO 2105 | SILVERADO 2105658898 | Vegetation | 2022-06-23 18:20 | 6/20 - 6/26 | 2022-06-23 19:30 | 70 | FTS | 9170 | 131 | 2 | 1 | 2 | 0 | 0 | 0 | 70
22-0077962 | Calaveras | CORRAL 1101 | CORRAL 110112606 | Unknown | 2022-06-23 19:53 | 6/20 - 6/26 | 2022-06-23 23:01 | 188 | FTS | 62604 | 333 | 23 | 17 | 7 | 0 | 0 | 0 | 188
22-0077982 | Mendocino | PHILO 1102 | PHILO 1102920 | Vegetation | 2022-06-23 21:45 | 6/20 - 6/26 | 2022-06-24 09:00 | 675 | FTS | 482079 | 733 | 17 | 11 | 13 | 1 | 0 | 1 | 657.6794
22-0078017 | Butte | BIG BEND 1102 | BIG BEND 1102884340 | Unknown | 2022-06-24 03:43 | 6/20 - 6/26 | 2022-06-24 06:42 | 179 | FTS | 28979 | 217 | 4 | 1 | 4 | 0 | 0 | 0 | 133.5438
22-0078021 | Sonoma | DUNBAR 1101 | DUNBAR 1101534 | Vegetation | 2022-06-24 04:58 | 6/20 - 6/26 | 2022-06-24 11:34 | 396 | FTS | 64944 | 164 | 5 | 4 | 4 | 0 | 0 | 5 | 396
22-0078037 | Lake | HIGHLANDS 1102 | HIGHLANDS 1102556 | Animal | 2022-06-24 06:43 | 6/20 - 6/26 | 2022-06-24 08:39 | 116 | FTS | 72154 | 624 | 52 | 35 | 11 | 0 | 0 | 4 | 115.6314
22-0078046 | San Luis Obispo | ATASCADERO 1102 | ATASCADERO 1102A28 | Unknown | 2022-06-24 07:02 | 6/20 - 6/26 | 2022-06-24 10:11 | 189 | FTS | 324751 | 1795 | 65 | 35 | 9 | 2 | 0 | 0 | 180.9198
22-0078060 | Humboldt | EEL RIVER 1102 | EEL RIVER 11021902 | Unknown | 2022-06-24 07:50 | 6/20 - 6/26 | 2022-06-24 14:53 | 423 | FTS | 38661 | 106 | 2 | 1 | 12 | 0 | 0 | 0 | 364.7264
22-0078067 | Tehama | CORNING 1101 | CORNING 11011624 | 3rd Party | 2022-06-24 08:10 | 6/20 - 6/26 | 2022-06-24 10:12 | 122 | FTS | 120067 | 1139 | 109 | 72 | 20 | 2 | 0 | 0 | 105.4144
22-0078125 | El Dorado | APPLE HILL 1103 | APPLE HILL 11038412 | Animal | 2022-06-24 09:55 | 6/20 - 6/26 | 2022-06-24 12:00 | 125 | FTS | 32500 | 260 | 15 | 10 | 3 | 0 | 0 | 0 | 125
22-0078162 | Sierra | ALLEGHANY 1101 | ALLEGHANY 1101978 | Company Initiated | 2022-06-24 11:21 | 6/20 - 6/26 | 2022-06-24 13:00 | 99 | FTS | 9306 | 94 | 2 | 1 | 1 | 0 | 0 | 0 | 99
22-0078196 | Santa Cruz | POINT MORETTI 1101 | POINT MORETTI 110136514 | Animal | 2022-06-24 12:30 | 6/20 - 6/26 | 2022-06-24 13:59 | 89 | FTS | 6853 | 77 | 4 | 2 | 2 | 0 | 0 | 1 | 89
22-0078308 | Mendocino | PHILO 1101 | PHILO 110137222 | Vegetation | 2022-06-24 15:35 | 6/20 - 6/26 | 2022-06-25 00:26 | 531 | FTS | 25272 | 152 | 3 | 1 | 3 | 0 | 0 | 0 | 166.2632
22-0078324 | San Luis Obispo | CAYUCOS 1102 | CAYUCOS 1102317156 | Vegetation | 2022-06-24 16:20 | 6/20 - 6/26 | 2022-06-25 10:05 | 1065 | FTS | 10300 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 198.0769
22-0078329 | Contra Costa | ALHAMBRA 1105 | ALHAMBRA 110581514 | Unknown | 2022-06-24 17:03 | 6/20 - 6/26 | 2022-06-25 10:04 | 1021 | FTS | 280468 | 1828 | 135 | 96 | 25 | 1 | 0 | 4 | 153.4289
22-0078341 | Tuolumne | PEORIA 1701 | PEORIA 17013186 | Equipment | 2022-06-24 18:11 | 6/20 - 6/26 | 2022-06-25 01:40 | 449 | FTS | 165696 | 1260 | 74 | 57 | 14 | 0 | 0 | 0 | 131.5048
22-0078343 | Sonoma | DUNBAR 1102 | DUNBAR 1102861496 | Vegetation | 2022-06-24 18:20 | 6/20 - 6/26 | 2022-06-25 07:07 | 767 | FTS | 295321 | 2459 | 116 | 82 | 44 | 2 | 2 | 19 | 120.098
22-0078359 | Santa Clara | MILPITAS 1108 | MILPITAS 1108XR122 | Unknown | 2022-06-24 19:46 | 6/20 - 6/26 | 2022-06-24 21:23 | 97 | FTS | 236044 | 2639 | 95 | 52 | 29 | 6 | 0 | 0 | 89.4445
22-0078365 | Mendocino | HOPLAND 1101 | HOPLAND 11014626 | Unknown | 2022-06-24 20:04 | 6/20 - 6/26 | 2022-06-25 08:19 | 735 | FTS | 151198 | 425 | 12 | 8 | 6 | 3 | 0 | 0 | 355.76
22-0078370 | Sonoma | CLOVERDALE 1101 | CLOVERDALE 11011101/2 | Unknown | 2022-06-24 21:05 | 6/20 - 6/26 | 2022-06-25 01:42 | 277 | FTS | 619607 | 2642 | 182 | 123 | 38 | 7 | 0 | 1 | 234.522
22-0078452 | Alameda | RADUM 1105 | RADUM 1105806392 | Animal | 2022-06-25 09:00 | 6/20 - 6/26 | 2022-06-25 10:43 | 103 | FTS | 25441 | 247 | 19 | 13 | 8 | 0 | 0 | 0 | 103
22-0078470 | Contra Costa | MORAGA 1102 | MORAGA 1102221914 | Equipment | 2022-06-25 10:08 | 6/20 - 6/26 | 2022-06-25 15:43 | 335 | FTS | 419247 | 2437 | 95 | 65 | 36 | 8 | 0 | 0 | 172.0341
22-0078499 | Santa Cruz | BIG BASIN 1101 | BIG BASIN 1101573005 | Company Initiated | 2022-06-25 10:55 | 6/20 - 6/26 | 2022-06-25 14:43 | 228 | FTS | 11628 | 86 | 7 | 6 | 1 | 0 | 0 | 0 | 135.2093
22-0078523 | Placer | DRUM 1101 | DRUM 11011101/2 | 3rd Party | 2022-06-25 11:50 | 6/20 - 6/26 | 2022-06-25 20:32 | 522 | FTS | 102438 | 203 | 6 | 3 | 19 | 1 | 0 | 1 | 504.6207
22-0078512 | San Luis Obispo | TEMPLETON 2111 | TEMPLETON 2111686138 | Unknown | 2022-06-25 13:05 | 6/20 - 6/26 | 2022-06-25 15:52 | 167 | FTS | 12219 | 141 | 7 | 6 | 0 | 0 | 0 | 1 | 86.6596
22-0078517 | San Luis Obispo | ATASCADERO 1103 | ATASCADERO 1103A16 | Unknown | 2022-06-25 13:11 | 6/20 - 6/26 | 2022-06-25 15:07 | 116 | FTS | 26100 | 225 | 7 | 4 | 3 | 0 | 0 | 0 | 116
22-0066278 | Shasta | WHITMORE 1101 | WHITMORE 11011101/2 | Company Initiated | 2022-06-25 13:28 | 6/20 - 6/26 | 2022-06-25 14:40 | 72 | FTS | 39096 | 543 | 36 | 28 | 13 | 3 | 0 | 3 | 72
22-0078532 | Shasta | PANORAMA 1102 | PANORAMA 11021526 | Animal | 2022-06-25 14:03 | 6/20 - 6/26 | 2022-06-25 17:01 | 178 | FTS | 18334 | 103 | 8 | 7 | 2 | 0 | 0 | 0 | 178
22-0078570 | Santa Cruz | BIG BASIN 1101 | BIG BASIN 1101393582 | Vegetation | 2022-06-25 17:49 | 6/20 - 6/26 | 2022-06-25 20:23 | 154 | FTS | 94895 | 635 | 40 | 30 | 10 | 0 | 0 | 1 | 149.4409
22-0078585 | Santa Cruz | CAMP EVERS 2105 | CAMP EVERS 210510728 | Unknown | 2022-06-25 19:43 | 6/20 - 6/26 | 2022-06-26 13:45 | 1082 | FTS | 2917697 | 2993 | 235 | 179 | 45 | 4 | 0 | 1 | 974.8403
22-0078686 | Monterey | DEL MONTE 2104 | DEL MONTE 21042624 | Unknown | 2022-06-26 00:55 | 6/20 - 6/26 | 2022-06-26 04:13 | 198 | FTS | 207596 | 3227 | 163 | 123 | 90 | 1 | 0 | 1 | 64.331
22-0078689 | El Dorado | APPLE HILL 2102 | APPLE HILL 210251792 | Unknown | 2022-06-26 04:18 | 6/20 - 6/26 | 2022-06-26 09:01 | 283 | FTS | 241831 | 856 | 60 | 36 | 11 | 0 | 0 | 3 | 282.5129
22-0078699 | Mendocino | LAYTONVILLE 1101 | LAYTONVILLE 1101448108 | Unknown | 2022-06-26 06:30 | 6/20 - 6/26 | 2022-06-26 08:49 | 139 | FTS | 6533 | 47 | 3 | 3 | 0 | 0 | 0 | 0 | 139
22-0078698 | Nevada | BRUNSWICK 1105 | BRUNSWICK 11052204 | Animal | 2022-06-26 07:07 | 6/20 - 6/26 | 2022-06-26 12:41 | 334 | FTS | 287517 | 940 | 48 | 36 | 12 | 0 | 0 | 12 | 305.8691
22-0078701 | Amador | ELECTRA 1102 | ELECTRA 11024756 | Animal | 2022-06-26 07:22 | 6/20 - 6/26 | 2022-06-26 09:37 | 135 | FTS | 77575 | 650 | 44 | 23 | 16 | 3 | 0 | 0 | 119.3462
22-0078703 | Marin | SAN RAFAEL 1104 | SAN RAFAEL 1104802 | Animal | 2022-06-26 07:43 | 6/20 - 6/26 | 2022-06-26 08:14 | 31 | FTS | 43586 | 1406 | 60 | 39 | 15 | 3 | 0 | 0 | 31
22-0078705 | San Benito | HOLLISTER 2106 | HOLLISTER 21064004 | 3rd Party | 2022-06-26 07:59 | 6/20 - 6/26 | 2022-06-27 00:21 | 982 | FTS | 55770 | 312 | 17 | 12 | 3 | 1 | 0 | 0 | 178.75
22-0078706 | Contra Costa | FAIRVIEW 2207 | FAIRVIEW 22072207/2 | Unknown | 2022-06-26 08:04 | 6/20 - 6/26 | 2022-06-26 13:30 | 326 | FTS | 1386626 | 4626 | 216 | 136 | 90 | 10 | 0 | 0 | 299.7462
22-0078758 | Santa Clara | LOS GATOS 1101 | LOS GATOS 11011101/2 | Animal | 2022-06-26 18:01 | 6/20 - 6/26 | 2022-06-26 19:08 | 67 | FTS | 152152 | 2364 | 92 | 69 | 37 | 8 | 0 | 2 | 64.3621
22-0078760 | Butte | WYANDOTTE 1110 | WYANDOTTE 1110747922 | Animal | 2022-06-26 18:15 | 6/20 - 6/26 | 2022-06-26 21:58 | 223 | FTS | 287067 | 1564 | 216 | 162 | 25 | 0 | 0 | 1 | 183.5467
22-0078767 | Mariposa | BEAR VALLEY 2101 | BEAR VALLEY 21014500 | Equipment | 2022-06-26 19:19 | 6/20 - 6/26 | 2022-06-27 11:09 | 950 | FTS | 286011 | 540 | 29 | 19 | 14 | 3 | 0 | 0 | 529.65
22-0078774 | Amador | ELECTRA 1101 | ELECTRA 11017104 | Unknown | 2022-06-26 21:04 | 6/20 - 6/26 | 2022-06-27 09:37 | 753 | FTS | 469119 | 623 | 63 | 41 | 7 | 0 | 0 | 1 | 753
22-0078825 | Butte | BUTTE 1105 | BUTTE 1105134600 | Vegetation | 2022-06-26 23:50 | 6/20 - 6/26 | 2022-06-27 13:35 | 825 | FTS | 44865 | 368 | 27 | 14 | 5 | 1 | 0 | 3 | 121.9158
22-0078824 | Nevada | HIGGINS 1104 | HIGGINS 11041006 | Unknown | 2022-06-27 00:18 | 6/27 - 7/3 | 2022-06-27 05:15 | 297 | FTS | 529280 | 1872 | 130 | 90 | 19 | 1 | 0 | 4 | 282.735
22-0078830 | Sonoma | SONOMA 1107 | SONOMA 1107844168 | Unknown | 2022-06-27 03:21 | 6/27 - 7/3 | 2022-06-27 10:27 | 426 | FTS | 53250 | 125 | 2 | 2 | 4 | 0 | 0 | 0 | 426
22-0078854 | Tulare | STONE CORRAL 1110 | STONE CORRAL 1110894956 | Unknown | 2022-06-27 07:30 | 6/27 - 7/3 | 2022-06-27 09:17 | 107 | FTS | 2461 | 23 | 1 | 1 | 0 | 0 | 0 | 0 | 107
22-0078981 | Santa Cruz | BEN LOMOND 0401 | BEN LOMOND 0401944178 | Vegetation | 2022-06-27 10:38 | 6/27 - 7/3 | 2022-06-27 17:37 | 419 | FTS | 86400 | 752 | 70 | 52 | 15 | 3 | 0 | 1 | 114.8936
22-0079018 | Monterey | LOS OSITOS 2103 | LOS OSITOS 2103220608 | Animal | 2022-06-27 12:10 | 6/27 - 7/3 | 2022-06-27 13:06 | 56 | FTS | 448 | 8 | 0 | 0 | 1 | 0 | 0 | 0 | 56
22-0079117 | Napa | PUEBLO 1104 | PUEBLO 1104105708 | 3rd Party | 2022-06-27 14:10 | 6/27 - 7/3 | 2022-06-28 03:30 | 800 | FTS | 65676 | 551 | 23 | 15 | 2 | 0 | 0 | 5 | 119.1942
22-0079137 | Santa Cruz | CAMP EVERS 2106 | CAMP EVERS 210660120 | Vegetation | 2022-06-27 14:37 | 6/27 - 7/3 | 2022-06-27 18:26 | 229 | FTS | 119075 | 548 | 52 | 34 | 7 | 0 | 0 | 5 | 217.2901
22-0079189 | El Dorado | APPLE HILL 2102 | APPLE HILL 2102186912 | Vegetation | 2022-06-27 15:43 | 6/27 - 7/3 | 2022-06-27 20:28 | 285 | FTS | 348051 | 1224 | 110 | 85 | 17 | 3 | 0 | 4 | 284.3554
22-0079186 | San Luis Obispo | SAN LUIS OBISPO 1101 | SAN LUIS OBISPO 1101V12 | Unknown | 2022-06-27 15:51 | 6/27 - 7/3 | 2022-06-27 19:14 | 203 | FTS | 41209 | 203 | 5 | 2 | 47 | 0 | 0 | 1 | 203
22-0079206 | Contra Costa | BRENTWOOD 2105 | BRENTWOOD 2105B504R | Unknown | 2022-06-27 16:46 | 6/27 - 7/3 | 2022-06-27 18:00 | 74 | FTS | 4500 | 67 | 1 | 1 | 12 | 0 | 0 | 0 | 67.1642
22-0079210 | Tuolumne | CURTIS 1702 | CURTIS 170247488 | Unknown | 2022-06-27 17:06 | 6/27 - 7/3 | 2022-06-27 19:54 | 168 | FTS | 98280 | 585 | 53 | 39 | 7 | 8 | 0 | 1 | 168
22-0079214 | Santa Cruz | CAMP EVERS 2105 | CAMP EVERS 210510294 | Vegetation | 2022-06-27 17:06 | 6/27 - 7/3 | 2022-06-27 19:48 | 162 | FTS | 69822 | 431 | 39 | 29 | 11 | 0 | 0 | 0 | 162
22-0079221 | Tuolumne | MIWUK 1702 | MIWUK 17029270 | Equipment | 2022-06-27 17:46 | 6/27 - 7/3 | 2022-06-28 00:38 | 412 | FTS | 85480 | 525 | 47 | 30 | 5 | 0 | 0 | 0 | 162.819
22-0079234 | Contra Costa | CLAYTON 2212 | CLAYTON 22122212/2 | Unknown | 2022-06-27 19:12 | 6/27 - 7/3 | 2022-06-27 20:56 | 104 | FTS | 351520 | 3380 | 291 | 192 | 78 | 8 | 0 | 5 | 104
22-0079236 | Sonoma | PETALUMA C 1108 | PETALUMA C 1108618 | 3rd Party | 2022-06-27 19:15 | 6/27 - 7/3 | 2022-06-28 05:15 | 600 | FTS | 78925 | 713 | 35 | 26 | 10 | 3 | 0 | 1 | 110.6942
22-0079239 | Tuolumne | PEORIA 1705 | PEORIA 17051834 | Unknown | 2022-06-27 19:36 | 6/27 - 7/3 | 2022-06-27 21:22 | 106 | FTS | 43142 | 407 | 35 | 26 | 2 | 0 | 0 | 1 | 106
22-0079246 | El Dorado | SHINGLE SPRINGS 2109 | SHINGLE SPRINGS 210912392 | Unknown | 2022-06-27 19:51 | 6/27 - 7/3 | 2022-06-28 00:58 | 307 | FTS | 163608 | 871 | 79 | 48 | 23 | 3 | 0 | 5 | 187.8393
22-0079250 | Tulare | DUNLAP 1102 | DUNLAP 11027290 | Equipment | 2022-06-27 20:02 | 6/27 - 7/3 | 2022-06-28 14:23 | 1101 | FTS | 52416 | 56 | 0 | 0 | 5 | 0 | 0 | 0 | 936
22-0079249 | Calaveras | CORRAL 1101 | CORRAL 110136652 | Unknown | 2022-06-27 20:04 | 6/27 - 7/3 | 2022-06-28 09:55 | 831 | FTS | 159138 | 443 | 46 | 29 | 3 | 0 | 0 | 2 | 359.228
22-0079255 | El Dorado | APPLE HILL 2102 | APPLE HILL 21026552 | Unknown | 2022-06-27 21:00 | 6/27 - 7/3 | 2022-06-28 09:43 | 763 | FTS | 632027 | 3377 | 274 | 190 | 43 | 3 | 0 | 12 | 187.1564
22-0079277 | Humboldt | HOOPA 1101 | HOOPA 110137202 | Vegetation | 2022-06-28 00:17 | 6/27 - 7/3 | 2022-06-28 10:22 | 605 | FTS | 68365 | 113 | 0 | 0 | 8 | 1 | 0 | 0 | 605
22-0079278 | Lassen | MC ARTHUR 1101 | MC ARTHUR 11011544 | Unknown | 2022-06-28 03:06 | 6/27 - 7/3 | 2022-06-28 09:13 | 367 | FTS | 134411 | 367 | 15 | 12 | 20 | 3 | 0 | 0 | 366.2425
22-0079280 | Santa Cruz | PAUL SWEET 2106 | PAUL SWEET 21062106/2 | Unknown | 2022-06-28 04:02 | 6/27 - 7/3 | 2022-06-28 07:59 | 237 | C/OUT | 873239 | 4595 | 306 | 251 | 66 | 14 | 2 | 6 | 190.0411
22-0079281 | Tulare | STONE CORRAL 1110 | STONE CORRAL 1110975698 | Unknown | 2022-06-28 04:35 | 6/27 - 7/3 | 2022-06-28 06:46 | 131 | FTS | 6943 | 53 | 0 | 0 | 1 | 0 | 0 | 0 | 131
22-0079290 | Nevada | BRUNSWICK 1102 | BRUNSWICK 11021010 | Animal | 2022-06-28 06:12 | 6/27 - 7/3 | 2022-06-28 09:00 | 168 | FTS | 112224 | 668 | 43 | 31 | 3 | 0 | 0 | 5 | 168
22-0079300 | Santa Barbara | SANTA YNEZ 1102 | SANTA YNEZ 1102320270 | Unknown | 2022-06-28 06:52 | 6/27 - 7/3 | 2022-06-28 10:41 | 229 | FTS | 51597 | 228 | 4 | 1 | 9 | 0 | 0 | 0 | 226.3026
22-0079303 | Santa Clara | LOS GATOS 1107 | LOS GATOS 11071107/2 | Animal | 2022-06-28 07:07 | 6/27 - 7/3 | 2022-06-28 08:18 | 71 | FTS | 163726 | 2306 | 113 | 71 | 71 | 2 | 0 | 14 | 71
22-0079341 | Nevada | BRUNSWICK 1104 | BRUNSWICK 11041020 | Animal | 2022-06-28 08:13 | 6/27 - 7/3 | 2022-06-28 12:27 | 254 | FTS | 244333 | 1643 | 110 | 63 | 19 | 5 | 0 | 26 | 148.7115
22-0079371 | Marin | SAN RAFAEL 1108 | SAN RAFAEL 11081108/2 | Animal | 2022-06-28 08:44 | 6/27 - 7/3 | 2022-06-28 11:11 | 147 | FTS | 648121 | 4617 | 150 | 81 | 38 | 4 | 0 | 0 | 140.3771
22-0079519 | San Mateo | HALF MOON BAY 1103 | HALF MOON BAY 1103880484 | Vegetation | 2022-06-28 11:39 | 6/27 - 7/3 | 2022-06-28 19:50 | 491 | HLT | 436468 | 1946 | 59 | 47 | 55 | 10 | 0 | 4 | 224.2898
22-0079524 | Tehama | CORNING 1101 | CORNING 110182846 | Unknown | 2022-06-28 11:49 | 6/27 - 7/3 | 2022-06-28 13:03 | 74 | FTS | 9842 | 133 | 11 | 8 | 4 | 2 | 0 | 0 | 74
22-0079633 | Santa Cruz | ROB ROY 2104 | ROB ROY 210410960 | 3rd Party | 2022-06-28 13:49 | 6/27 - 7/3 | 2022-06-29 03:03 | 794 | FTS | 158797 | 2392 | 166 | 136 | 34 | 6 | 0 | 2 | 66.3867
22-0079647 | Placer | HORSESHOE 1104 | HORSESHOE 110450142 | Unknown | 2022-06-28 14:13 | 6/27 - 7/3 | 2022-06-28 16:00 | 107 | FTS | 33384 | 312 | 25 | 15 | 5 | 0 | 0 | 0 | 107
22-0079826 | Monterey | OILFIELDS 1103 | OILFIELDS 1103N42 | Animal | 2022-06-28 23:56 | 6/27 - 7/3 | 2022-06-29 02:55 | 179 | FTS | 403810 | 2268 | 84 | 57 | 47 | 2 | 0 | 2 | 178.0467
22-0079856 | Napa | PUEBLO 2104 | PUEBLO 2104391312 | Equipment | 2022-06-29 06:26 | 6/27 - 7/3 | 2022-06-29 08:49 | 143 | FTS | 2288 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 143
22-0079862 | Calaveras | CORRAL 1101 | CORRAL 11011101/2 | Unknown | 2022-06-29 06:45 | 6/27 - 7/3 | 2022-06-29 10:40 | 235 | FTS | 168658 | 2014 | 151 | 102 | 28 | 0 | 0 | 5 | 83.7428
22-0079864 | Sonoma | FITCH MOUNTAIN 1113 | FITCH MOUNTAIN 1113154 | Unknown | 2022-06-29 06:48 | 6/27 - 7/3 | 2022-06-29 09:25 | 157 | FTS | 61442 | 395 | 18 | 13 | 10 | 0 | 0 | 4 | 155.5494
22-0079926 | Santa Cruz | PAUL SWEET 2104 | PAUL SWEET 21045394 | Vegetation | 2022-06-29 08:43 | 6/27 - 7/3 | 2022-06-29 10:15 | 92 | FTS | 27324 | 297 | 1027 | 823 | 201 | 25 | 5 | 14 | 92
22-0079948 | El Dorado | ECHO SUMMIT 1101 | ECHO SUMMIT 1101927328 | Equipment | 2022-06-29 09:28 | 6/27 - 7/3 | 2022-06-29 10:36 | 68 | FTS | 11900 | 175 | 1 | 1 | 2 | 0 | 0 | 0 | 68
22-0079953 | Plumas | BUCKS CREEK 1103 | BUCKS CREEK 1103338520 | Unknown | 2022-06-29 09:41 | 6/27 - 7/3 | 2022-06-29 20:20 | 639 | FTS | 178742 | 306 | 2 | 2 | 3 | 0 | 0 | 0 | 584.1242
22-0079986 | El Dorado | APPLE HILL 2102 | APPLE HILL 21021532 | Animal | 2022-06-29 10:29 | 6/27 - 7/3 | 2022-06-29 15:05 | 276 | FTS | 723412 | 2665 | 221 | 160 | 39 | 8 | 0 | 16 | 271.4492
22-0080054 | Tehama | CORNING 1101 | CORNING 110182846 | Unknown | 2022-06-29 12:14 | 6/27 - 7/3 | 2022-06-29 14:03 | 109 | FTS | 14497 | 133 | 11 | 8 | 4 | 2 | 0 | 0 | 109
22-0080173 | Butte | WYANDOTTE 1103 | WYANDOTTE 1103640652 | Equipment | 2022-06-29 14:43 | 6/27 - 7/3 | 2022-06-30 03:51 | 788 | FTS | 224593 | 1216 | 116 | 94 | 21 | 0 | 0 | 2 | 184.6982
22-0080214 | El Dorado | APPLE HILL 2102 | APPLE HILL 21027502 | Company Initiated | 2022-06-29 15:16 | 6/27 - 7/3 | 2022-06-29 16:29 | 73 | FTS | 27448 | 376 | 31 | 22 | 3 | 0 | 0 | 2 | 73
22-0080256 | Tehama | CORNING 1101 | CORNING 110182846 | Unknown | 2022-06-29 17:07 | 6/27 - 7/3 | 2022-06-29 19:30 | 143 | FTS | 13771 | 133 | 11 | 8 | 4 | 2 | 0 | 0 | 103.5414
22-0080279 | San Mateo | EMERALD LAKE 0401 | EMERALD LAKE 0401401/2 | Equipment | 2022-06-29 18:35 | 6/27 - 7/3 | 2022-06-29 23:32 | 297 | FTS | 96359 | 1136 | 69 | 54 | 23 | 1 | 0 | 1 | 84.8231
22-0080334 | Placer | HIGGINS 1110 | HIGGINS 111051794 | Animal | 2022-06-30 00:47 | 6/27 - 7/3 | 2022-06-30 10:39 | 592 | FTS | 19336 | 84 | 6 | 5 | 3 | 0 | 0 | 0 | 230.1905
22-0080338 | Tulare | DUNLAP 1102 | DUNLAP 11027290 | Equipment | 2022-06-30 03:41 | 6/27 - 7/3 | 2022-06-30 16:39 | 778 | FTS | 28921 | 56 | 0 | 0 | 5 | 0 | 0 | 0 | 516.4464
22-0080342 | Tuolumne | CURTIS 1705 | CURTIS 17058170 | Unknown | 2022-06-30 05:28 | 6/27 - 7/3 | 2022-06-30 07:50 | 142 | FTS | 71284 | 502 | 54 | 43 | 4 | 0 | 0 | 0 | 142
22-0080356 | Alameda | VASCO 1102 | VASCO 1102546328 | Unknown | 2022-06-30 06:39 | 6/27 - 7/3 | 2022-06-30 15:34 | 535 | FTS | 73875 | 228 | 20 | 14 | 7 | 0 | 0 | 1 | 324.0132
22-0080361 | Amador | CLAY 1101 | CLAY 110113450 | Unknown | 2022-06-30 07:02 | 6/27 - 7/3 | 2022-06-30 08:35 | 93 | FTS | 41292 | 444 | 47 | 34 | 5 | 0 | 0 | 0 | 93
22-0080516 | El Dorado | SHINGLE SPRINGS 2109 | SHINGLE SPRINGS 21099372 | Animal | 2022-06-30 10:32 | 6/27 - 7/3 | 2022-06-30 13:20 | 168 | HLT | 417250 | 2506 | 207 | 138 | 31 | 2 | 0 | 38 | 166.5004
22-0080523 | Mariposa | MARIPOSA 2102 | MARIPOSA 210237288 | Unknown | 2022-06-30 11:02 | 6/27 - 7/3 | 2022-06-30 17:36 | 394 | FTS | 265162 | 673 | 48 | 36 | 15 | 5 | 0 | 0 | 394
22-0080586 | Santa Cruz | CAMP EVERS 2103 | CAMP EVERS 21035402 | Animal | 2022-06-30 12:49 | 6/27 - 7/3 | 2022-06-30 14:17 | 88 | FTS | 202724 | 2339 | 175 | 141 | 46 | 3 | 0 | 5 | 86.6712
22-0080778 | Butte | WYANDOTTE 1107 | WYANDOTTE 110738438 | 3rd Party | 2022-06-30 16:35 | 6/27 - 7/3 | 2022-07-01 10:50 | 1095 | FTS | 274720 | 737 | 73 | 54 | 9 | 0 | 0 | 3 | 372.7544
22-0080808 | Placer | PENRYN 1103 | PENRYN 1103604 | Equipment | 2022-06-30 18:12 | 6/27 - 7/3 | 2022-07-01 02:14 | 482 | FTS | 81208 | 329 | 15 | 8 | 3 | 0 | 0 | 5 | 246.8328
22-0080813 | Fresno | AUBERRY 1101 | AUBERRY 11011101/2 | Animal | 2022-06-30 19:03 | 6/27 - 7/3 | 2022-06-30 22:14 | 191 | FTS | 613946 | 3216 | 238 | 162 | 80 | 16 | 0 | 8 | 190.9036
22-0080829 | San Mateo | MENLO 1102 | MENLO 11028952 | Vegetation | 2022-06-30 21:49 | 6/27 - 7/3 | 2022-07-01 03:54 | 365 | FTS | 34744 | 302 | 10 | 9 | 8 | 0 | 0 | 0 | 115.0464
22-0080859 | Mendocino | WILLITS 1104 | WILLITS 1104934 | Unknown | 2022-06-30 23:06 | 6/27 - 7/3 | 2022-07-01 08:51 | 585 | FTS | 169641 | 427 | 31 | 20 | 15 | 0 | 0 | 1 | 397.2857
22-0080875 | El Dorado | APPLE HILL 2102 | APPLE HILL 21028372 | Unknown | 2022-07-01 01:58 | 6/27 - 7/3 | 2022-07-01 11:32 | 574 | FTS | 1414585 | 2674 | 221 | 160 | 39 | 8 | 0 | 16 | 529.0146
22-0081164 | Butte | WYANDOTTE 1110 | WYANDOTTE 1110747922 | Animal | 2022-07-01 13:51 | 6/27 - 7/3 | 2022-07-01 15:27 | 96 | FTS | 149496 | 1563 | 216 | 162 | 25 | 0 | 0 | 1 | 95.6468
22-0081236 | Fresno | AUBERRY 1102 | AUBERRY 1102R2850 | Environmental/External | 2022-07-01 15:24 | 6/27 - 7/3 | 2022-07-02 05:27 | 843 | FTS | 69468 | 224 | 28 | 18 | 7 | 4 | 0 | 1 | 310.125
22-0081260 | Santa Cruz | ROB ROY 2104 | ROB ROY 210412596 | Animal | 2022-07-01 16:35 | 6/27 - 7/3 | 2022-07-01 19:35 | 180 | FTS | 73800 | 410 | 37 | 32 | 4 | 0 | 0 | 0 | 180
22-0081293 | Santa Cruz | BEN LOMOND 0401 | BEN LOMOND 0401944178 | Vegetation | 2022-07-01 20:49 | 6/27 - 7/3 | 2022-07-02 11:59 | 910 | FTS | 115911 | 759 | 70 | 52 | 15 | 3 | 0 | 1 | 152.7154
22-0081295 | Amador | CLAY 1103 | CLAY 11037142 | Unknown | 2022-07-01 20:53 | 6/27 - 7/3 | 2022-07-02 08:15 | 682 | FTS | 34248 | 81 | 0 | 0 | 5 | 0 | 0 | 0 | 422.8148
22-0081323 | Amador | PINE GROVE 1102 | PINE GROVE 110245292 | Unknown | 2022-07-02 00:41 | 6/27 - 7/3 | 2022-07-02 03:45 | 184 | FTS | 90528 | 492 | 42 | 27 | 11 | 0 | 0 | 0 | 184
22-0081333 | El Dorado | SHINGLE SPRINGS 2108 | SHINGLE SPRINGS 210851474 | Unknown | 2022-07-02 02:11 | 6/27 - 7/3 | 2022-07-02 08:12 | 361 | FTS | 270389 | 749 | 53 | 33 | 10 | 2 | 0 | 0 | 361
22-0081331 | Contra Costa | CLAYTON 2215 | CLAYTON 2215W531R | Unknown | 2022-07-02 03:06 | 6/27 - 7/3 | 2022-07-03 10:47 | 1901 | FTS | 283637 | 869 | 69 | 41 | 14 | 1 | 0 | 0 | 326.3947
22-0081329 | Lassen | MC ARTHUR 1101 | MC ARTHUR 11011546 | Unknown | 2022-07-02 03:15 | 6/27 - 7/3 | 2022-07-02 09:57 | 402 | FTS | 43818 | 109 | 5 | 4 | 2 | 0 | 0 | 0 | 402
22-0081344 | Santa Cruz | CAMP EVERS 2106 | CAMP EVERS 210611044 | Unknown | 2022-07-02 07:51 | 6/27 - 7/3 | 2022-07-02 12:59 | 308 | FTS | 624423 | 2487 | 195 | 145 | 45 | 4 | 0 | 5 | 251.0748
22-0081358 | El Dorado | DIAMOND SPRINGS 1103 | DIAMOND SPRINGS 11039432 | Unknown | 2022-07-02 08:48 | 6/27 - 7/3 | 2022-07-02 13:10 | 262 | FTS | 145410 | 555 | 59 | 41 | 8 | 0 | 0 | 2 | 262
22-0081406 | El Dorado | MOUNTAIN QUARRIES 2101 | MOUNTAIN QUARRIES 21012422 | Vegetation | 2022-07-02 12:37 | 6/27 - 7/3 | 2022-07-02 15:12 | 155 | FTS | 86679 | 612 | 39 | 28 | 9 | 1 | 0 | 1 | 141.6324
22-0081434 | Tuolumne | STANISLAUS 1702 | STANISLAUS 17021702/2 | Equipment | 2022-07-02 17:36 | 6/27 - 7/3 | 2022-07-03 13:46 | 1210 | FTS | 4964930 | 4971 | 200 | 156 | 52 | 3 | 2 | 0 | 998.7789
22-0081437 | Placer | PENRYN 1103 | PENRYN 1103660 | Vegetation | 2022-07-02 18:20 | 6/27 - 7/3 | 2022-07-03 05:34 | 674 | FTS | 35306 | 451 | 28 | 15 | 3 | 0 | 0 | 4 | 78.2838
22-0081482 | Butte | WYANDOTTE 1102 | WYANDOTTE 110213044 | Unknown | 2022-07-03 03:10 | 6/27 - 7/3 | 2022-07-03 08:32 | 322 | FTS | 10948 | 34 | 2 | 2 | 0 | 0 | 0 | 1 | 322
22-0081484 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113641367 | Animal | 2022-07-03 06:19 | 6/27 - 7/3 | 2022-07-03 09:28 | 189 | FTS | 56511 | 299 | 15 | 10 | 3 | 0 | 0 | 4 | 189
22-0081486 | Monterey | LAURELES 1111 | LAURELES 11112028 | Unknown | 2022-07-03 07:06 | 6/27 - 7/3 | 2022-07-03 10:15 | 189 | FTS | 90387 | 487 | 31 | 22 | 7 | 0 | 0 | 0 | 185.5996
22-0081488 | Nevada | BRUNSWICK 1104 | BRUNSWICK 1104327226 | Equipment | 2022-07-03 08:00 | 6/27 - 7/3 | 2022-07-03 08:53 | 53 | FTS | 901 | 17 | 2 | 2 | 0 | 0 | 0 | 0 | 53
22-0081489 | Santa Cruz | GREEN VALLEY 2101 | GREEN VALLEY 210136820 | Unknown | 2022-07-03 08:03 | 6/27 - 7/3 | 2022-07-03 14:06 | 363 | FTS | 300872 | 1992 | 134 | 111 | 31 | 14 | 0 | 5 | 151.0402
22-0081496 | Mendocino | HOPLAND 1101 | HOPLAND 1101768 | Unknown | 2022-07-03 09:30 | 6/27 - 7/3 | 2022-07-03 12:41 | 191 | FTS | 18909 | 99 | 3 | 2 | 1 | 0 | 0 | 0 | 191
22-0081493 | Placer | BELL 1108 | BELL 110880680 | Animal | 2022-07-03 09:34 | 6/27 - 7/3 | 2022-07-03 11:24 | 110 | FTS | 16060 | 146 | 14 | 9 | 1 | 0 | 0 | 0 | 110
22-0081509 | San Luis Obispo | ATASCADERO 1102 | ATASCADERO 1102A28 | Unknown | 2022-07-03 11:40 | 6/27 - 7/3 | 2022-07-03 13:52 | 132 | FTS | 230080 | 1795 | 65 | 35 | 9 | 2 | 0 | 0 | 128.1783
22-0081517 | El Dorado | DIAMOND SPRINGS 1103 | DIAMOND SPRINGS 11039432 | Unknown | 2022-07-03 12:11 | 6/27 - 7/3 | 2022-07-03 13:48 | 97 | FTS | 53835 | 555 | 59 | 41 | 8 | 0 | 0 | 2 | 97
22-0081531 | Sonoma | MIRABEL 1101 | MIRABEL 1101201156 | Animal | 2022-07-03 15:35 | 6/27 - 7/3 | 2022-07-03 16:32 | 57 | FTS | 4503 | 79 | 5 | 4 | 1 | 0 | 0 | 0 | 57
22-0081548 | Contra Costa | TASSAJARA 2113 | TASSAJARA 2113MR276 | Unknown | 2022-07-03 18:51 | 6/27 - 7/3 | 2022-07-03 20:21 | 90 | FTS | 40410 | 449 | 30 | 24 | 10 | 0 | 0 | 1 | 90
22-0081551 | El Dorado | CLARKSVILLE 2104 | CLARKSVILLE 210419772 | 3rd Party | 2022-07-03 20:50 | 6/27 - 7/3 | 2022-07-04 12:59 | 969 | FTS | 73168 | 244 | 22 | 15 | 3 | 0 | 0 | 8 | 299.8689
22-0081556 | Santa Barbara | PURISIMA 1101 | PURISIMA 11011101/2 | 3rd Party | 2022-07-03 21:26 | 6/27 - 7/3 | 2022-07-04 02:18 | 292 | FTS | 285444 | 2403 | 82 | 61 | 39 | 2 | 0 | 0 | 118.7865
22-0081597 | San Luis Obispo | TEMPLETON 2112 | TEMPLETON 2112R28 | Unknown | 2022-07-04 08:36 | 7/4 - 7/10 | 2022-07-04 09:42 | 66 | FTS | 21780 | 330 | 8 | 6 | 9 | 0 | 0 | 0 | 66
22-0081601 | Alameda | VINEYARD 2108 | VINEYARD 2108MR172 | 3rd Party | 2022-07-04 09:15 | 7/4 - 7/10 | 2022-07-05 02:03 | 1008 | FTS | 375136 | 3026 | 173 | 116 | 38 | 2 | 0 | 0 | 123.9709
22-0081602 | Contra Costa | SOBRANTE 1102 | SOBRANTE 1102690098 | Animal | 2022-07-04 09:17 | 7/4 - 7/10 | 2022-07-04 10:15 | 58 | FTS | 33872 | 584 | 37 | 28 | 13 | 2 | 0 | 0 | 58
22-0081603 | Nevada | HIGGINS 1109 | HIGGINS 1109594 | Animal | 2022-07-04 09:19 | 7/4 - 7/10 | 2022-07-04 10:57 | 98 | FTS | 49686 | 507 | 51 | 29 | 4 | 0 | 0 | 3 | 98
22-0081605 | Calaveras | FROGTOWN 1702 | FROGTOWN 170275252 | Unknown | 2022-07-04 09:35 | 7/4 - 7/10 | 2022-07-04 13:31 | 236 | FTS | 185292 | 822 | 38 | 25 | 29 | 2 | 0 | 2 | 225.4161
22-0081607 | Sonoma | MIRABEL 1101 | MIRABEL 1101298 | Unknown | 2022-07-04 09:41 | 7/4 - 7/10 | 2022-07-04 17:40 | 479 | FTS | 116295 | 385 | 16 | 13 | 2 | 0 | 0 | 0 | 302.0649
22-0081609 | Amador | CLAY 1102 | CLAY 11021102/2 | 3rd Party | 2022-07-04 09:51 | 7/4 - 7/10 | 2022-07-04 11:22 | 91 | FTS | 273 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 91
22-0081610 | Lassen | MC ARTHUR 1101 | MC ARTHUR 11011544 | Animal | 2022-07-04 09:56 | 7/4 - 7/10 | 2022-07-04 13:10 | 194 | FTS | 70196 | 367 | 15 | 12 | 20 | 3 | 0 | 0 | 191.2698
22-0081617 | Solano | VACAVILLE 1104 | VACAVILLE 11041104/2 | Animal | 2022-07-04 11:01 | 7/4 - 7/10 | 2022-07-04 13:55 | 174 | FTS | 274347 | 2092 | 139 | 92 | 34 | 2 | 0 | 1 | 131.141
22-0081655 | Marin | STAFFORD 1102 | STAFFORD 11021258 | Unknown | 2022-07-04 16:07 | 7/4 - 7/10 | 2022-07-04 17:12 | 65 | FTS | 77610 | 1194 | 70 | 48 | 6 | 3 | 0 | 0 | 65
22-0081663 | San Luis Obispo | SAN LUIS OBISPO 1103 | SAN LUIS OBISPO 110342344 | Unknown | 2022-07-04 17:09 | 7/4 - 7/10 | 2022-07-04 18:54 | 105 | FTS | 34335 | 327 | 12 | 9 | 3 | 0 | 0 | 2 | 105
22-0081672 | El Dorado | CLARKSVILLE 2104 | CLARKSVILLE 210419772 | Unknown | 2022-07-04 21:08 | 7/4 - 7/10 | 2022-07-05 08:40 | 692 | FTS | 168848 | 244 | 22 | 15 | 3 | 0 | 0 | 8 | 692
22-0081674 | Mendocino | HOPLAND 1101 | HOPLAND 1101960 | Vegetation | 2022-07-04 21:18 | 7/4 - 7/10 | 2022-07-05 08:49 | 691 | FTS | 37314 | 54 | 1 | 1 | 1 | 0 | 0 | 0 | 691
22-0081678 | Madera | OAKHURST 1103 | OAKHURST 110310140 | Equipment | 2022-07-04 21:51 | 7/4 - 7/10 | 2022-07-05 13:00 | 909 | FTS | 417894 | 914 | 60 | 49 | 24 | 0 | 0 | 1 | 457.2144
22-0081682 | San Luis Obispo | FOOTHILL 1102 | FOOTHILL 110299432 | Unknown | 2022-07-04 22:28 | 7/4 - 7/10 | 2022-07-05 01:09 | 161 | FTS | 324711 | 2259 | 52 | 38 | 23 | 3 | 0 | 0 | 143.741
22-0081690 | Butte | ORO FINO 1102 | ORO FINO 110276008 | Equipment | 2022-07-05 02:16 | 7/4 - 7/10 | 2022-07-05 09:28 | 432 | FTS | 83904 | 377 | 35 | 22 | 4 | 0 | 0 | 0 | 222.557
22-0081697 | Santa Cruz | GREEN VALLEY 2101 | GREEN VALLEY 210112106 | Animal | 2022-07-05 05:39 | 7/4 - 7/10 | 2022-07-05 09:30 | 231 | FTS | 233772 | 1012 | 86 | 69 | 9 | 1 | 0 | 0 | 231
22-0081782 | Mendocino | CALPELLA 1101 | CALPELLA 1101753000 | Unknown | 2022-07-05 09:56 | 7/4 - 7/10 | 2022-07-05 11:42 | 106 | FTS | 32754 | 309 | 15 | 13 | 11 | 2 | 0 | 0 | 106
22-0081805 | San Luis Obispo | ATASCADERO 1101 | ATASCADERO 1101A50 | Unknown | 2022-07-05 10:43 | 7/4 - 7/10 | 2022-07-05 17:28 | 405 | FTS | 193828 | 1418 | 98 | 59 | 15 | 3 | 0 | 2 | 136.6911
22-0081815 | Santa Barbara | PUEBLO 1105 | PUEBLO 1105637242 | Animal | 2022-07-05 10:48 | 7/4 - 7/10 | 2022-07-05 14:07 | 199 | FTS | 30248 | 152 | 2 | 2 | 1 | 0 | 0 | 0 | 199
22-0081828 | Santa Cruz | ROB ROY 2104 | ROB ROY 210410960 | Unknown | 2022-07-05 11:14 | 7/4 - 7/10 | 2022-07-05 13:21 | 127 | FTS | 225767 | 2393 | 166 | 136 | 34 | 6 | 0 | 2 | 94.3448
22-0081890 | Placer | PENRYN 1107 | PENRYN 11072708 | 3rd Party | 2022-07-05 12:57 | 7/4 - 7/10 | 2022-07-06 01:33 | 756 | FTS | 159842 | 378 | 36 | 25 | 6 | 0 | 0 | 1 | 422.8624
22-0081891 | Lake | KONOCTI 1102 | KONOCTI 110264664 | Vegetation | 2022-07-05 12:58 | 7/4 - 7/10 | 2022-07-05 17:37 | 279 | FTS | 74673 | 507 | 38 | 26 | 3 | 0 | 0 | 1 | 147.284
22-0081938 | Lake | LUCERNE 1103 | LUCERNE 11031103/2 | Unknown | 2022-07-05 14:00 | 7/4 - 7/10 | 2022-07-05 15:25 | 85 | FTS | 191590 | 2254 | 230 | 161 | 36 | 1 | 0 | 0 | 85
22-0081950 | Merced | GUSTINE 1102 | GUSTINE 11029100 | Animal | 2022-07-05 14:11 | 7/4 - 7/10 | 2022-07-05 16:29 | 138 | FTS | 90528 | 656 | 13 | 10 | 13 | 0 | 0 | 0 | 138
22-0082015 | San Luis Obispo | ATASCADERO 1102 | ATASCADERO 1102A28 | Unknown | 2022-07-05 15:41 | 7/4 - 7/10 | 2022-07-05 17:52 | 131 | FTS | 226913 | 1795 | 65 | 35 | 9 | 2 | 0 | 0 | 126.4139
22-0082037 | San Luis Obispo | TEMPLETON 2111 | TEMPLETON 2111A66 | Animal | 2022-07-05 16:34 | 7/4 - 7/10 | 2022-07-05 18:56 | 142 | FTS | 138876 | 978 | 71 | 37 | 20 | 4 | 0 | 1 | 142
22-0082081 | Shasta | PANORAMA 1102 | PANORAMA 11021342 | Unknown | 2022-07-05 21:16 | 7/4 - 7/10 | 2022-07-06 03:03 | 347 | FTS | 128994 | 544 | 51 | 34 | 3 | 0 | 0 | 0 | 237.1213
22-0082116 | Fresno | COALINGA NO 2 1105 | COALINGA NO 2 110541954 | Unknown | 2022-07-06 04:38 | 7/4 - 7/10 | 2022-07-06 11:12 | 394 | FTS | 53550 | 161 | 4 | 2 | 6 | 4 | 0 | 0 | 332.6087
22-0082139 | Shasta | JESSUP 1103 | JESSUP 11031540 | Animal | 2022-07-06 06:40 | 7/4 - 7/10 | 2022-07-06 16:47 | 607 | FTS | 69668 | 665 | 68 | 54 | 7 | 0 | 0 | 0 | 104.7639
22-0082268 | Santa Cruz | BIG BASIN 1101 | BIG BASIN 1101393582 | Unknown | 2022-07-06 11:04 | 7/4 - 7/10 | 2022-07-06 15:02 | 238 | FTS | 94640 | 635 | 40 | 30 | 10 | 0 | 0 | 1 | 149.0394
22-0082479 | Humboldt | FRUITLAND 1142 | FRUITLAND 11421142/2 | Vegetation | 2022-07-06 17:07 | 7/4 - 7/10 | 2022-07-06 19:28 | 141 | FTS | 92331 | 1023 | 23 | 17 | 23 | 5 | 0 | 0 | 90.2551
22-0082494 | Marin | WOODACRE 1102 | WOODACRE 1102137662 | Animal | 2022-07-06 19:21 | 7/4 - 7/10 | 2022-07-06 20:23 | 62 | FTS | 117180 | 1890 | 90 | 49 | 28 | 6 | 0 | 0 | 62
22-0082503 | Placer | PENRYN 1105 | PENRYN 110550548 | Animal | 2022-07-06 20:37 | 7/4 - 7/10 | 2022-07-06 22:38 | 121 | FTS | 29161 | 241 | 15 | 10 | 0 | 0 | 0 | 2 | 121
22-0082506 | Monterey | RESERVATION ROAD 1102 | RESERVATION ROAD 11023032 | Animal | 2022-07-06 21:17 | 7/4 - 7/10 | 2022-07-06 22:30 | 73 | FTS | 7957 | 109 | 9 | 8 | 1 | 0 | 0 | 0 | 73
22-0082507 | Nevada | COLUMBIA HILL 1101 | COLUMBIA HILL 110135424 | Equipment | 2022-07-06 21:18 | 7/4 - 7/10 | 2022-07-07 12:25 | 907 | FTS | 68230 | 241 | 15 | 12 | 9 | 3 | 0 | 0 | 283.112
22-0082525 | Monterey | LAURELES 1112 | LAURELES 111268454 | Unknown | 2022-07-06 23:42 | 7/4 - 7/10 | 2022-07-07 02:10 | 148 | FTS | 114996 | 777 | 29 | 17 | 27 | 1 | 0 | 1 | 148
22-0082532 | Sonoma | SONOMA 1105 | SONOMA 1105138 | Equipment | 2022-07-07 03:51 | 7/4 - 7/10 | 2022-07-08 00:09 | 1218 | FTS | 237899 | 699 | 30 | 20 | 9 | 0 | 0 | 6 | 340.3419
22-0082594 | Santa Clara | MC KEE 1107 | MC KEE 1107XR010 | Unknown | 2022-07-07 08:02 | 7/4 - 7/10 | 2022-07-07 09:46 | 104 | FTS | 43784 | 421 | 21 | 15 | 3 | 0 | 0 | 1 | 104
22-0082633 | Amador | TIGER CREEK 0201 | TIGER CREEK 0201201/2 | Company Initiated | 2022-07-07 08:50 | 7/4 - 7/10 | 2022-07-07 08:57 | 7 | FTS | 98 | 14 | 0 | 0 | 3 | 0 | 0 | 0 | 7
22-0082722 | Mariposa | MERCED FALLS 1102 | MERCED FALLS 110285002 | Equipment | 2022-07-07 10:45 | 7/4 - 7/10 | 2022-07-07 11:17 | 32 | FTS | 17664 | 552 | 44 | 29 | 15 | 2 | 0 | 0 | 32
22-0082766 | Santa Clara | MC KEE 1107 | MC KEE 1107XR010 | Animal | 2022-07-07 12:08 | 7/4 - 7/10 | 2022-07-07 13:46 | 98 | FTS | 41062 | 419 | 21 | 15 | 3 | 0 | 0 | 1 | 98
22-0082760 | Mendocino | PHILO 1101 | PHILO 11011101/2 | Vegetation | 2022-07-07 12:11 | 7/4 - 7/10 | 2022-07-07 17:49 | 338 | FTS | 446585 | 2215 | 60 | 38 | 50 | 13 | 0 | 2 | 201.6185
22-0082835 | Placer | BELL 1109 | BELL 1109724884 | Unknown | 2022-07-07 14:01 | 7/4 - 7/10 | 2022-07-07 17:33 | 212 | FTS | 63196 | 329 | 24 | 17 | 5 | 0 | 0 | 3 | 192.0851
22-0082867 | Tuolumne | CURTIS 1703 | CURTIS 17036064 | 3rd Party | 2022-07-07 14:38 | 7/4 - 7/10 | 2022-07-08 01:57 | 679 | FTS | 59188 | 379 | 37 | 31 | 4 | 0 | 0 | 0 | 156.1689
22-0082868 | Santa Cruz | POINT MORETTI 1101 | POINT MORETTI 110110722 | Vegetation | 2022-07-07 14:41 | 7/4 - 7/10 | 2022-07-08 05:50 | 909 | FTS | 32406 | 260 | 18 | 14 | 4 | 0 | 0 | 3 | 124.6385
22-0082932 | Lake | REDBUD 1102 | REDBUD 1102922 | Animal | 2022-07-07 17:27 | 7/4 - 7/10 | 2022-07-07 19:18 | 111 | FTS | 37407 | 337 | 26 | 16 | 4 | 0 | 1 | 0 | 111
22-0082926 | Santa Cruz | CAMP EVERS 2105 | CAMP EVERS 210595050 | Vegetation | 2022-07-07 17:31 | 7/4 - 7/10 | 2022-07-08 00:37 | 426 | FTS | 131760 | 1966 | 146 | 110 | 33 | 3 | 0 | 1 | 67.0193
22-0082952 | Lake | LUCERNE 1103 | LUCERNE 1103630 | Animal | 2022-07-07 19:40 | 7/4 - 7/10 | 2022-07-07 20:54 | 74 | FTS | 114256 | 1544 | 147 | 97 | 21 | 1 | 0 | 0 | 74
22-0082947 | San Luis Obispo | CAMBRIA 1102 | CAMBRIA 11021102/2 | 3rd Party | 2022-07-07 19:42 | 7/4 - 7/10 | 2022-07-08 08:18 | 756 | FTS | 248484 | 1254 | 42 | 29 | 19 | 0 | 0 | 3 | 198.1531
22-0082987 | Fresno | AUBERRY 1101 | AUBERRY 1101R2579 | Animal | 2022-07-08 04:28 | 7/4 - 7/10 | 2022-07-08 06:43 | 135 | FTS | 41445 | 307 | 24 | 17 | 5 | 0 | 0 | 0 | 135
22-0082988 | Tulare | STONE CORRAL 1108 | STONE CORRAL 1108255186 | Unknown | 2022-07-08 04:35 | 7/4 - 7/10 | 2022-07-08 08:44 | 249 | FTS | 13695 | 55 | 2 | 1 | 0 | 0 | 0 | 0 | 249
22-0082991 | Solano | JAMESON 1105 | JAMESON 1105466348 | Animal | 2022-07-08 05:26 | 7/4 - 7/10 | 2022-07-08 08:26 | 180 | FTS | 46236 | 353 | 12 | 6 | 8 | 2 | 0 | 2 | 130.9802
22-0083188 | Shasta | PIT NO 1 1101 | PIT NO 1 11011101/2 | Unknown | 2022-07-08 10:33 | 7/4 - 7/10 | 2022-07-08 16:51 | 378 | FTS | 302836 | 999 | 56 | 40 | 32 | 3 | 10 | 0 | 303.1391
22-0083366 | Marin | NOVATO 1104 | NOVATO 110455398 | Unknown | 2022-07-08 14:51 | 7/4 - 7/10 | 2022-07-08 17:30 | 159 | FTS | 18377 | 161 | 1 | 0 | 16 | 0 | 0 | 0 | 114.1429
22-0083379 | Sonoma | CLOVERDALE 1101 | CLOVERDALE 1101474708 | Animal | 2022-07-08 15:12 | 7/4 - 7/10 | 2022-07-08 16:28 | 76 | FTS | 7543 | 103 | 12 | 7 | 5 | 0 | 0 | 0 | 73.233
22-0083431 | Lake | KONOCTI 1102 | KONOCTI 1102714370 | Unknown | 2022-07-08 18:25 | 7/4 - 7/10 | 2022-07-08 19:49 | 84 | FTS | 9744 | 116 | 12 | 11 | 1 | 0 | 0 | 0 | 84
22-0083441 | Nevada | NARROWS 2105 | NARROWS 21052426 | Animal | 2022-07-08 19:19 | 7/4 - 7/10 | 2022-07-08 20:40 | 81 | FTS | 166201 | 2105 | 179 | 103 | 28 | 4 | 0 | 19 | 78.9553
22-0083458 | Lake | UPPER LAKE 1101 | UPPER LAKE 1101660 | Unknown | 2022-07-08 20:09 | 7/4 - 7/10 | 2022-07-09 09:08 | 779 | FTS | 376838 | 484 | 37 | 21 | 2 | 0 | 0 | 0 | 778.5909
22-0083461 | Tuolumne | PEORIA 1701 | PEORIA 17013186 | Unknown | 2022-07-08 21:38 | 7/4 - 7/10 | 2022-07-09 01:40 | 242 | FTS | 243334 | 1259 | 74 | 57 | 14 | 0 | 0 | 0 | 193.2756
22-0083460 | San Luis Obispo | OCEANO 1104 | OCEANO 11041104/2 | 3rd Party | 2022-07-08 21:38 | 7/4 - 7/10 | 2022-07-08 22:57 | 79 | FTS | 357290 | 5414 | 219 | 176 | 62 | 18 | 0 | 32 | 65.9937
22-0083469 | Monterey | RESERVATION ROAD 1102 | RESERVATION ROAD 11023032 | Unknown | 2022-07-09 00:48 | 7/4 - 7/10 | 2022-07-09 03:06 | 138 | FTS | 15042 | 109 | 9 | 8 | 1 | 0 | 0 | 0 | 138
22-0083480 | Nevada | BRUNSWICK 1107 | BRUNSWICK 11071107/2 | Animal | 2022-07-09 06:24 | 7/4 - 7/10 | 2022-07-09 08:36 | 132 | FTS | 566873 | 5896 | 376 | 250 | 98 | 17 | 4 | 5 | 96.1454
22-0083486 | Nevada | BRUNSWICK 1105 | BRUNSWICK 11052140 | Unknown | 2022-07-09 07:14 | 7/4 - 7/10 | 2022-07-09 12:09 | 295 | FTS | 176115 | 597 | 32 | 24 | 5 | 0 | 0 | 7 | 295
22-0083484 | Santa Barbara | BUELLTON 1101 | BUELLTON 1101Y06 | Animal | 2022-07-09 07:16 | 7/4 - 7/10 | 2022-07-09 08:44 | 88 | FTS | 30536 | 347 | 5 | 5 | 10 | 0 | 0 | 0 | 88
22-0083502 | Amador | PINE GROVE 1102 | PINE GROVE 11023168 | Unknown | 2022-07-09 09:55 | 7/4 - 7/10 | 2022-07-09 15:29 | 334 | FTS | 239035 | 1070 | 88 | 57 | 14 | 0 | 0 | 6 | 223.3972
22-0083513 | Yuba | WHEATLAND 1105 | WHEATLAND 1105248490 | Unknown | 2022-07-09 11:42 | 7/4 - 7/10 | 2022-07-09 14:25 | 163 | FTS | 34556 | 212 | 12 | 6 | 3 | 0 | 0 | 4 | 163
22-0083521 | Santa Clara | HICKS 2101 | HICKS 2101XR162 | Unknown | 2022-07-09 12:40 | 7/4 - 7/10 | 2022-07-09 16:23 | 223 | FTS | 343492 | 1550 | 94 | 68 | 23 | 3 | 0 | 0 | 221.6077
22-0083573 | Monterey | SOLEDAD 2102 | SOLEDAD 21027008 | 3rd Party | 2022-07-09 18:14 | 7/4 - 7/10 | 2022-07-09 19:36 | 82 | FTS | 7790 | 95 | 0 | 0 | 5 | 0 | 0 | 0 | 82
22-0083577 | Lake | REDBUD 1102 | REDBUD 1102432 | Unknown | 2022-07-09 18:47 | 7/4 - 7/10 | 2022-07-09 22:21 | 214 | FTS | 437630 | 2045 | 168 | 110 | 22 | 1 | 0 | 0 | 214
22-0083582 | Contra Costa | LAKEWOOD 2227 | LAKEWOOD 2227W503R | Unknown | 2022-07-09 20:03 | 7/4 - 7/10 | 2022-07-09 22:17 | 134 | FTS | 233345 | 1927 | 114 | 81 | 21 | 1 | 0 | 0 | 121.0924
22-0083583 | Lake | CLEAR LAKE 1101 | CLEAR LAKE 11011302 | Animal | 2022-07-09 20:18 | 7/4 - 7/10 | 2022-07-10 08:22 | 724 | FTS | 379376 | 524 | 37 | 21 | 8 | 0 | 1 | 0 | 724
22-0083584 | Calaveras | NORTH BRANCH 1101 | NORTH BRANCH 110111158 | Unknown | 2022-07-09 20:26 | 7/4 - 7/10 | 2022-07-10 00:24 | 238 | FTS | 96628 | 406 | 34 | 21 | 12 | 0 | 0 | 3 | 238
22-0083601 | Lake | KONOCTI 1102 | KONOCTI 1102532 | Vegetation | 2022-07-09 22:27 | 7/4 - 7/10 | 2022-07-10 10:11 | 704 | FTS | 65885 | 373 | 21 | 13 | 8 | 0 | 0 | 0 | 176.6354
22-0083607 | Lassen | MC ARTHUR 1101 | MC ARTHUR 11011544 | Unknown | 2022-07-09 23:51 | 7/4 - 7/10 | 2022-07-10 15:00 | 909 | FTS | 332601 | 367 | 15 | 12 | 20 | 3 | 0 | 0 | 906.2698
22-0083609 | El Dorado | SHINGLE SPRINGS 2105 | SHINGLE SPRINGS 210551738 | Equipment | 2022-07-10 00:21 | 7/4 - 7/10 | 2022-07-10 15:31 | 910 | FTS | 331647 | 2207 | 161 | 113 | 23 | 0 | 0 | 6 | 150.2705
22-0083621 | Shasta | BURNEY 1101 | BURNEY 11012402 | Unknown | 2022-07-10 06:56 | 7/4 - 7/10 | 2022-07-10 10:51 | 235 | FTS | 147133 | 631 | 54 | 39 | 9 | 1 | 0 | 0 | 233.1743
22-0083625 | Marin | STAFFORD 1102 | STAFFORD 1102524 | Animal | 2022-07-10 07:52 | 7/4 - 7/10 | 2022-07-10 08:51 | 59 | FTS | 92866 | 1574 | 94 | 54 | 13 | 1 | 0 | 0 | 59
22-0083626 | Shasta | PIT NO 5 1101 | PIT NO 5 11011614 | Unknown | 2022-07-10 08:27 | 7/4 - 7/10 | 2022-07-10 15:50 | 443 | FTS | 443 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 443
22-0083635 | Santa Cruz | BIG BASIN 1102 | BIG BASIN 110296986 | Animal | 2022-07-10 10:41 | 7/4 - 7/10 | 2022-07-10 14:50 | 249 | FTS | 164784 | 831 | 48 | 33 | 14 | 1 | 0 | 1 | 198.296
22-0083641 | Mendocino | UKIAH 1113 | UKIAH 11131113/2 | 3rd Party | 2022-07-10 11:17 | 7/4 - 7/10 | 2022-07-10 13:22 | 125 | FTS | 151125 | 1209 | 66 | 41 | 26 | 3 | 0 | 0 | 125
22-0083648 | Shasta | RISING RIVER 1101 | RISING RIVER 11011101/2 | Unknown | 2022-07-10 12:36 | 7/4 - 7/10 | 2022-07-10 14:37 | 121 | FTS | 86173 | 725 | 46 | 44 | 14 | 0 | 0 | 0 | 118.8593
22-0083650 | Shasta | VOLTA 1101 | VOLTA 11011568 | Unknown | 2022-07-10 13:02 | 7/4 - 7/10 | 2022-07-10 16:52 | 230 | FTS | 20930 | 91 | 5 | 3 | 1 | 0 | 0 | 0 | 230
22-0083661 | Humboldt | RIO DELL 1102 | RIO DELL 11028768 | Vegetation | 2022-07-10 15:14 | 7/4 - 7/10 | 2022-07-11 00:02 | 528 | FTS | 71470 | 307 | 12 | 9 | 3 | 1 | 0 | 0 | 232.8013
22-0083660 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 21012181 | 3rd Party | 2022-07-10 15:22 | 7/4 - 7/10 | 2022-07-10 19:06 | 224 | FTS | 11424 | 51 | 0 | 0 | 2 | 0 | 0 | 0 | 224
22-0083674 | Humboldt | HOOPA 1101 | HOOPA 110193038 | Animal | 2022-07-10 18:04 | 7/4 - 7/10 | 2022-07-10 19:44 | 100 | FTS | 10100 | 101 | 2 | 2 | 12 | 11 | 0 | 0 | 100
22-0083677 | Santa Cruz | CAMP EVERS 2103 | CAMP EVERS 21032103/2 | 3rd Party | 2022-07-10 18:39 | 7/4 - 7/10 | 2022-07-10 20:09 | 90 | FTS | 219870 | 3275 | 252 | 206 | 64 | 5 | 0 | 15 | 67.1359
22-0083680 | San Mateo | EMERALD LAKE 0401 | EMERALD LAKE 0401401/2 | Unknown | 2022-07-10 18:49 | 7/4 - 7/10 | 2022-07-11 10:30 | 941 | FTS | 289177 | 1137 | 69 | 54 | 23 | 1 | 0 | 1 | 254.3333
22-0083685 | Yuba | BROWNS VALLEY 1101 | BROWNS VALLEY 110136622 | Unknown | 2022-07-10 20:49 | 7/4 - 7/10 | 2022-07-11 09:18 | 749 | FTS | 11235 | 15 | 1 | 1 | 0 | 0 | 0 | 0 | 749
22-0083686 | Humboldt | RIO DELL 1102 | RIO DELL 11028852 | Vegetation | 2022-07-10 21:07 | 7/4 - 7/10 | 2022-07-11 16:16 | 1149 | FTS | 105708 | 92 | 3 | 2 | 10 | 0 | 1 | 0 | 1149
22-0083711 | El Dorado | SHINGLE SPRINGS 2109 | SHINGLE SPRINGS 210913322 | Animal | 2022-07-11 01:55 | 7/11 - 7/17 | 2022-07-11 06:35 | 280 | FTS | 688909 | 2524 | 210 | 138 | 32 | 2 | 0 | 38 | 272.9433
22-0083715 | Contra Costa | WILLOW PASS 1101 | WILLOW PASS 11011101/2 | 3rd Party | 2022-07-11 03:23 | 7/11 - 7/17 | 2022-07-11 05:24 | 121 | FTS | 142418 | 1601 | 117 | 77 | 20 | 0 | 0 | 0 | 88.9557
22-0083723 | Nevada | HIGGINS 1107 | HIGGINS 11071070 | Vegetation | 2022-07-11 06:43 | 7/11 - 7/17 | 2022-07-11 16:24 | 581 | FTS | 27706 | 239 | 21 | 13 | 9 | 0 | 0 | 7 | 115.9247
22-0083740 | Plumas | EAST QUINCY 1101 | EAST QUINCY 11012452 | Animal | 2022-07-11 07:45 | 7/11 - 7/17 | 2022-07-11 09:17 | 92 | FTS | 91816 | 998 | 54 | 36 | 7 | 0 | 0 | 0 | 92
22-0083852 | Tehama | CORNING 1101 | CORNING 110182846 | Unknown | 2022-07-11 10:55 | 7/11 - 7/17 | 2022-07-11 11:51 | 56 | FTS | 7448 | 133 | 11 | 8 | 4 | 2 | 0 | 0 | 56
22-0083987 | Shasta | PANORAMA 1102 | PANORAMA 11021526 | Animal | 2022-07-11 13:46 | 7/11 - 7/17 | 2022-07-11 16:06 | 140 | FTS | 14048 | 103 | 8 | 7 | 2 | 0 | 0 | 0 | 136.3883
22-0084103 | San Mateo | EMERALD LAKE 0401 | EMERALD LAKE 0401401/2 | Unknown | 2022-07-11 18:14 | 7/11 - 7/17 | 2022-07-11 20:55 | 161 | FTS | 178735 | 1137 | 69 | 54 | 23 | 1 | 0 | 1 | 157.1988
22-0084104 | Santa Clara | HICKS 2103 | HICKS 21032103/2 | Animal | 2022-07-11 18:35 | 7/11 - 7/17 | 2022-07-12 03:10 | 515 | C/OUT | 308764 | 3668 | 212 | 132 | 38 | 3 | 0 | 0 | 84.1778
22-0084105 | Santa Clara | HICKS 2101 | HICKS 21012101/2 | Unknown | 2022-07-11 18:37 | 7/11 - 7/17 | 2022-07-13 01:26 | 1849 | FTS | 1310576 | 4942 | 289 | 200 | 75 | 12 | 0 | 0 | 265.1914
22-0084109 | Humboldt | GARBERVILLE 1102 | GARBERVILLE 110256048 | Vegetation | 2022-07-11 18:37 | 7/11 - 7/17 | 2022-07-12 12:27 | 1070 | FTS | 349884 | 378 | 9 | 8 | 17 | 6 | 0 | 0 | 925.619
22-0084114 | Amador | OLETA 1101 | OLETA 11011208 | Unknown | 2022-07-11 18:52 | 7/11 - 7/17 | 2022-07-12 09:39 | 887 | FTS | 442339 | 500 | 31 | 18 | 10 | 1 | 0 | 1 | 884.678
22-0084125 | Calaveras | NORTH BRANCH 1101 | NORTH BRANCH 110111158 | Unknown | 2022-07-11 20:22 | 7/11 - 7/17 | 2022-07-11 23:54 | 212 | FTS | 86072 | 406 | 34 | 21 | 12 | 0 | 0 | 3 | 212
22-0084169 | Mendocino | CALPELLA 1101 | CALPELLA 1101542 | Vegetation | 2022-07-12 02:48 | 7/11 - 7/17 | 2022-07-12 10:39 | 471 | FTS | 184161 | 391 | 26 | 18 | 2 | 0 | 0 | 0 | 471
22-0084205 | Contra Costa | CLAYTON 2212 | CLAYTON 2212204416 | Vegetation | 2022-07-12 07:12 | 7/11 - 7/17 | 2022-07-12 16:48 | 576 | FTS | 34816 | 154 | 9 | 5 | 0 | 0 | 0 | 1 | 226.0779
22-0084250 | El Dorado | SHINGLE SPRINGS 2109 | SHINGLE SPRINGS 210913322 | Unknown | 2022-07-12 09:01 | 7/11 - 7/17 | 2022-07-12 13:02 | 241 | FTS | 155445 | 645 | 57 | 36 | 4 | 0 | 0 | 5 | 241
22-0084289 | Contra Costa | BRENTWOOD 2105 | BRENTWOOD 2105B504R | Unknown | 2022-07-12 10:31 | 7/11 - 7/17 | 2022-07-12 11:50 | 79 | FTS | 3379 | 67 | 1 | 1 | 12 | 0 | 0 | 0 | 50.4328
22-0084380 | Santa Cruz | BEN LOMOND 0401 | BEN LOMOND 040116010 | Unknown | 2022-07-12 12:41 | 7/11 - 7/17 | 2022-07-12 14:35 | 114 | FTS | 15960 | 140 | 8 | 8 | 6 | 1 | 0 | 0 | 114
22-0084526 | Santa Clara | LOYOLA 1102 | LOYOLA 1102917865 | Unknown | 2022-07-12 16:01 | 7/11 - 7/17 | 2022-07-12 19:55 | 234 | FTS | 9126 | 39 | 2 | 2 | 1 | 0 | 0 | 0 | 234
22-0084523 | Humboldt | HOOPA 1101 | HOOPA 110182542 | Unknown | 2022-07-12 17:08 | 7/11 - 7/17 | 2022-07-13 13:53 | 1245 | FTS | 97815 | 244 | 10 | 6 | 8 | 0 | 0 | 0 | 400.8811
22-0084541 | Shasta | OREGON TRAIL 1103 | OREGON TRAIL 110335002 | 3rd Party | 2022-07-12 20:08 | 7/11 - 7/17 | 2022-07-13 05:00 | 532 | FTS | 314633 | 1121 | 92 | 64 | 20 | 3 | 0 | 1 | 280.6717
22-0084551 | Solano | NORTH TOWER 2101 | NORTH TOWER 2101158556/2 | Unknown | 2022-07-12 22:00 | 7/11 - 7/17 | 2022-07-12 22:38 | 38 | FTS | 123728 | 3256 | 229 | 148 | 37 | 8 | 0 | 0 | 38
22-0084570 | Calaveras | CORRAL 1103 | CORRAL 110336680 | Unknown | 2022-07-13 01:29 | 7/11 - 7/17 | 2022-07-13 04:42 | 193 | FTS | 137416 | 712 | 80 | 49 | 11 | 0 | 0 | 0 | 193
22-0084572 | San Luis Obispo | CAYUCOS 1102 | CAYUCOS 1102613456 | Unknown | 2022-07-13 02:02 | 7/11 - 7/17 | 2022-07-13 10:54 | 532 | FTS | 55328 | 104 | 1 | 1 | 0 | 0 | 0 | 1 | 532
22-0084578 | Sonoma | MOLINO 1102 | MOLINO 1102104 | Unknown | 2022-07-13 03:33 | 7/11 - 7/17 | 2022-07-13 14:18 | 645 | FTS | 594777 | 1526 | 83 | 53 | 21 | 1 | 0 | 13 | 389.7621
22-0084585 | Contra Costa | BRENTWOOD 2105 | BRENTWOOD 210598606 | Animal | 2022-07-13 06:12 | 7/11 - 7/17 | 2022-07-13 12:04 | 352 | FTS | 32357 | 298 | 15 | 7 | 12 | 0 | 0 | 0 | 108.5805
22-0084640 | Santa Cruz | CAMP EVERS 2106 | CAMP EVERS 21062106/2 | Unknown | 2022-07-13 07:43 | 7/11 - 7/17 | 2022-07-13 12:58 | 315 | FTS | 1228448 | 5760 | 498 | 376 | 104 | 13 | 0 | 24 | 213.2722
22-0084645 | Marin | STAFFORD 1101 | STAFFORD 11011102/2 | Unknown | 2022-07-13 07:47 | 7/11 - 7/17 | 2022-07-13 09:04 | 77 | FTS | 160279 | 2541 | 156 | 119 | 19 | 4 | 0 | 0 | 63.0771
22-0080184 | Contra Costa | ALHAMBRA 1102 | ALHAMBRA 11021102/2 | Company Initiated | 2022-07-13 08:47 | 7/11 - 7/17 | 2022-07-13 09:02 | 15 | FTS | 46950 | 3130 | 146 | 100 | 47 | 10 | 4 | 0 | 15
22-0084769 | Mendocino | WILLITS 1104 | WILLITS 1104934 | 3rd Party | 2022-07-13 10:45 | 7/11 - 7/17 | 2022-07-13 13:49 | 184 | FTS | 61096 | 427 | 31 | 20 | 15 | 0 | 0 | 1 | 143.082
22-0084833 | El Dorado | APPLE HILL 2102 | APPLE HILL 2102186912 | Unknown | 2022-07-13 12:01 | 7/11 - 7/17 | 2022-07-13 15:07 | 186 | FTS | 217928 | 1224 | 110 | 85 | 17 | 3 | 0 | 4 | 178.0458
22-0085016 | Mendocino | WILLITS 1104 | WILLITS 110434008 | 3rd Party | 2022-07-13 15:50 | 7/11 - 7/17 | 2022-07-13 16:54 | 64 | FTS | 35728 | 571 | 38 | 31 | 19 | 0 | 0 | 0 | 62.5709
22-0085069 | Sierra | ALLEGHANY 1101 | ALLEGHANY 1101978 | Company Initiated | 2022-07-13 18:25 | 7/11 - 7/17 | 2022-07-13 18:51 | 26 | FTS | 4212 | 162 | 2 | 1 | 3 | 0 | 0 | 0 | 26
22-0085070 | Contra Costa | NORTH DUBLIN 2103 | NORTH DUBLIN 21032103/2 | Unknown | 2022-07-13 18:36 | 7/11 - 7/17 | 2022-07-14 11:01 | 985 | FTS | 657377 | 4847 | 164 | 114 | 51 | 6 | 0 | 0 | 135.6255
22-0085081 | Calaveras | NORTH BRANCH 1101 | NORTH BRANCH 110111158 | Unknown | 2022-07-13 20:10 | 7/11 - 7/17 | 2022-07-13 22:46 | 156 | FTS | 63336 | 406 | 34 | 21 | 12 | 0 | 0 | 3 | 156
22-0085084 | Trinity | WILLOW CREEK 1103 | WILLOW CREEK 11037514 | Vegetation | 2022-07-13 20:54 | 7/11 - 7/17 | 2022-07-14 10:51 | 837 | FTS | 1063827 | 1271 | 74 | 56 | 13 | 2 | 0 | 0 | 837
22-0085120 | Solano | JAMESON 1105 | JAMESON 1105466348 | Animal | 2022-07-14 05:29 | 7/11 - 7/17 | 2022-07-14 07:30 | 121 | FTS | 32207 | 353 | 12 | 6 | 8 | 2 | 0 | 2 | 91.238
22-0085339 | Tehama | VOLTA 1101 | VOLTA 11011516 | 3rd Party | 2022-07-14 11:36 | 7/11 - 7/17 | 2022-07-14 14:16 | 160 | FTS | 20800 | 130 | 11 | 9 | 17 | 2 | 0 | 0 | 160
22-0085406 | Santa Cruz | CAMP EVERS 2105 | CAMP EVERS 210511384 | Vegetation | 2022-07-14 13:02 | 7/11 - 7/17 | 2022-07-14 16:00 | 178 | FTS | 65326 | 367 | 15 | 14 | 3 | 1 | 0 | 0 | 178
22-0085618 | Solano | PEABODY 2106 | PEABODY 21062106/2 | Unknown | 2022-07-15 00:05 | 7/11 - 7/17 | 2022-07-15 02:59 | 174 | FTS | 247376 | 2976 | 273 | 209 | 19 | 2 | 0 | 0 | 83.1237
22-0085625 | Merced | MERCED FALLS 1102 | MERCED FALLS 1102482838 | Animal | 2022-07-15 05:04 | 7/11 - 7/17 | 2022-07-15 09:27 | 263 | FTS | 371619 | 1413 | 115 | 74 | 28 | 5 | 0 | 0 | 263
22-0085631 | Marin | STAFFORD 1102 | STAFFORD 11021202 | Unknown | 2022-07-15 05:53 | 7/11 - 7/17 | 2022-07-15 07:30 | 97 | FTS | 5141 | 53 | 0 | 0 | 1 | 0 | 0 | 0 | 97
22-0085632 | Placer | PLACER 1103 | PLACER 1103429574 | Animal | 2022-07-15 05:56 | 7/11 - 7/17 | 2022-07-15 07:49 | 113 | FTS | 52933 | 521 | 28 | 15 | 9 | 1 | 0 | 0 | 101.5988
22-0085672 | Placer | PENRYN 1105 | PENRYN 11051342 | Animal | 2022-07-15 07:34 | 7/11 - 7/17 | 2022-07-15 09:10 | 96 | FTS | 58080 | 605 | 36 | 22 | 9 | 0 | 0 | 11 | 96
22-0085685 | Calaveras | NORTH BRANCH 1101 | NORTH BRANCH 110111158 | Unknown | 2022-07-15 08:12 | 7/11 - 7/17 | 2022-07-15 13:17 | 305 | FTS | 77910 | 406 | 34 | 21 | 12 | 0 | 0 | 3 | 191.8966
22-0085720 | Sonoma | MIRABEL 1101 | MIRABEL 1101298 | Unknown | 2022-07-15 08:59 | 7/11 - 7/17 | 2022-07-15 10:47 | 108 | FTS | 18908 | 229 | 12 | 10 | 2 | 0 | 0 | 0 | 82.5677
22-0085767 | Contra Costa | MORAGA 1102 | MORAGA 11021106/2 | Unknown | 2022-07-15 10:08 | 7/11 - 7/17 | 2022-07-15 14:23 | 255 | C/OUT | 547090 | 2376 | 93 | 67 | 23 | 9 | 0 | 0 | 230.2567
22-0085848 | Lake | LUCERNE 1103 | LUCERNE 11034200 | Animal | 2022-07-15 12:03 | 7/11 - 7/17 | 2022-07-15 14:31 | 148 | FTS | 55605 | 378 | 54 | 41 | 11 | 0 | 0 | 0 | 147.1032
22-0085893 | Contra Costa | ROSSMOOR 1102 | ROSSMOOR 1102457174 | Unknown | 2022-07-15 12:56 | 7/11 - 7/17 | 2022-07-15 16:44 | 228 | FTS | 795524 | 3530 | 323 | 223 | 19 | 0 | 0 | 0 | 225.3609
22-0085896 | Lake | KONOCTI 1108 | KONOCTI 11081278 | Vegetation | 2022-07-15 13:11 | 7/11 - 7/17 | 2022-07-15 14:45 | 94 | FTS | 42018 | 447 | 34 | 25 | 7 | 0 | 0 | 0 | 94
22-0085962 | Lake | MIDDLETOWN 1101 | MIDDLETOWN 1101571926 | Unknown | 2022-07-15 13:14 | 7/11 - 7/17 | 2022-07-15 16:22 | 188 | FTS | 2820 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 188
22-0085984 | San Luis Obispo | TEMPLETON 2112 | TEMPLETON 2112R80 | 3rd Party | 2022-07-15 15:49 | 7/11 - 7/17 | 2022-07-16 00:37 | 528 | FTS | 204607 | 971 | 36 | 29 | 25 | 0 | 0 | 0 | 210.7178
22-0086009 | Tuolumne | CURTIS 1704 | CURTIS 17048140 | Unknown | 2022-07-15 17:23 | 7/11 - 7/17 | 2022-07-15 19:29 | 126 | FTS | 108612 | 862 | 81 | 54 | 13 | 0 | 0 | 1 | 126
22-0086019 | Fresno | TIVY VALLEY 1107 | TIVY VALLEY 1107869946 | Unknown | 2022-07-15 17:43 | 7/11 - 7/17 | 2022-07-15 19:57 | 134 | FTS | 38324 | 286 | 33 | 25 | 3 | 0 | 0 | 0 | 134
22-0086020 | Fresno | TIVY VALLEY 1107 | TIVY VALLEY 1107584840 | Unknown | 2022-07-15 17:43 | 7/11 - 7/17 | 2022-07-15 23:14 | 331 | FTS | 121762 | 520 | 49 | 30 | 3 | 0 | 0 | 0 | 234.1577
22-0086029 | El Dorado | DIAMOND SPRINGS 1103 | DIAMOND SPRINGS 11039432 | Unknown | 2022-07-15 19:29 | 7/11 - 7/17 | 2022-07-15 23:56 | 267 | FTS | 141061 | 555 | 59 | 41 | 8 | 0 | 0 | 2 | 254.164
22-0086031 | Mariposa | BEAR VALLEY 2101 | BEAR VALLEY 21014500 | Equipment | 2022-07-15 19:38 | 7/11 - 7/17 | 2022-07-15 20:20 | 42 | FTS | 22722 | 541 | 29 | 19 | 14 | 3 | 0 | 0 | 42
22-0086035 | Nevada | HIGGINS 1109 | HIGGINS 110950078 | Animal | 2022-07-15 20:14 | 7/11 - 7/17 | 2022-07-16 18:34 | 1340 | FTS | 70892 | 407 | 26 | 20 | 4 | 0 | 0 | 8 | 174.1818
22-0086039 | Shasta | OREGON TRAIL 1102 | OREGON TRAIL 11021382 | Unknown | 2022-07-15 21:00 | 7/11 - 7/17 | 2022-07-16 00:25 | 205 | FTS | 47681 | 245 | 24 | 21 | 1 | 0 | 0 | 0 | 194.6163
22-0086054 | Monterey | LAURELES 1111 | LAURELES 11112028 | Animal | 2022-07-15 22:14 | 7/11 - 7/17 | 2022-07-16 12:30 | 856 | FTS | 57984 | 487 | 31 | 22 | 7 | 0 | 0 | 0 | 119.0637
22-0086072 | Sonoma | FULTON 1102 | FULTON 11024522 | Vegetation | 2022-07-15 23:59 | 7/11 - 7/17 | 2022-07-16 10:42 | 643 | FTS | 137651 | 468 | 14 | 11 | 6 | 0 | 0 | 2 | 294.1261
22-0086082 | El Dorado | SHINGLE SPRINGS 2108 | SHINGLE SPRINGS 210851474 | Unknown | 2022-07-16 05:33 | 7/11 - 7/17 | 2022-07-16 07:28 | 115 | FTS | 86135 | 749 | 53 | 33 | 10 | 2 | 0 | 0 | 115
22-0086083 | San Benito | TRES PINOS 1111 | TRES PINOS 11114032 | Animal | 2022-07-16 05:50 | 7/11 - 7/17 | 2022-07-16 06:43 | 53 | FTS | 8660 | 168 | 6 | 6 | 4 | 3 | 0 | 0 | 51.5476
22-0086085 | Humboldt | HOOPA 1101 | HOOPA 110137202 | Vegetation | 2022-07-16 05:52 | 7/11 - 7/17 | 2022-07-16 22:45 | 1013 | FTS | 85438 | 114 | 0 | 0 | 8 | 1 | 0 | 0 | 749.4561
22-0086095 | Santa Cruz | CAMP EVERS 2106 | CAMP EVERS 210611044 | Equipment | 2022-07-16 07:01 | 7/11 - 7/17 | 2022-07-17 22:13 | 2352 | FTS | 602693 | 2488 | 195 | 145 | 45 | 4 | 0 | 5 | 242.24
22-0086099 | Placer | LINCOLN 1104 | LINCOLN 1104685276 | Animal | 2022-07-16 07:07 | 7/11 - 7/17 | 2022-07-16 10:50 | 223 | FTS | 60923 | 431 | 32 | 22 | 4 | 0 | 0 | 1 | 141.3527
22-0086109 | Santa Cruz | CAMP EVERS 2106 | CAMP EVERS 21065020 | Unknown | 2022-07-16 07:35 | 7/11 - 7/17 | 2022-07-16 12:13 | 278 | FTS | 161391 | 839 | 71 | 48 | 10 | 0 | 0 | 7 | 192.3611
22-0086141 | Tehama | RED BLUFF 1104 | RED BLUFF 11041302 | Unknown | 2022-07-16 10:13 | 7/11 - 7/17 | 2022-07-16 14:17 | 244 | FTS | 128828 | 896 | 79 | 47 | 18 | 1 | 0 | 1 | 143.7812
22-0086161 | El Dorado | DIAMOND SPRINGS 1106 | DIAMOND SPRINGS 110656026 | Unknown | 2022-07-16 13:14 | 7/11 - 7/17 | 2022-07-16 14:39 | 85 | FTS | 19805 | 233 | 21 | 13 | 2 | 0 | 0 | 1 | 85
22-0086169 | Placer | HORSESHOE 1104 | HORSESHOE 110450142 | Unknown | 2022-07-16 14:01 | 7/11 - 7/17 | 2022-07-16 22:17 | 496 | FTS | 32529 | 312 | 25 | 15 | 5 | 0 | 0 | 0 | 104.2596
22-0086175 | Mendocino | UKIAH 1114 | UKIAH 1114528 | Unknown | 2022-07-16 15:35 | 7/11 - 7/17 | 2022-07-16 17:32 | 117 | FTS | 15093 | 129 | 4 | 1 | 7 | 0 | 0 | 0 | 117
22-0086199 | Mariposa | BEAR VALLEY 2101 | BEAR VALLEY 21014500 | Equipment | 2022-07-16 19:02 | 7/11 - 7/17 | 2022-07-16 20:41 | 99 | FTS | 47067 | 541 | 29 | 19 | 14 | 3 | 0 | 0 | 87
22-0086204 | Shasta | CEDAR CREEK 1101 | CEDAR CREEK 11011608 | 3rd Party | 2022-07-16 20:31 | 7/11 - 7/17 | 2022-07-17 01:57 | 326 | FTS | 53732 | 200 | 18 | 13 | 2 | 0 | 0 | 0 | 268.66
22-0086233 | Sonoma | SONOMA 1105 | SONOMA 1105229588 | Unknown | 2022-07-17 00:54 | 7/11 - 7/17 | 2022-07-17 09:22 | 508 | FTS | 93472 | 184 | 6 | 6 | 0 | 0 | 0 | 5 | 508
22-0086234 | Santa Cruz | CAMP EVERS 2105 | CAMP EVERS 210574170 | Vegetation | 2022-07-17 02:24 | 7/11 - 7/17 | 2022-07-17 12:45 | 621 | FTS | 258975 | 1966 | 146 | 110 | 33 | 3 | 0 | 1 | 131.7269
22-0086244 | Tehama | RED BLUFF 1104 | RED BLUFF 11041302 | Unknown | 2022-07-17 07:24 | 7/11 - 7/17 | 2022-07-17 13:50 | 386 | FTS | 268492 | 896 | 79 | 47 | 18 | 1 | 0 | 1 | 299.6562
22-0086243 | Santa Clara | HOLLISTER 2102 | HOLLISTER 2102113634 | Animal | 2022-07-17 07:41 | 7/11 - 7/17 | 2022-07-17 08:26 | 45 | FTS | 4050 | 90 | 3 | 1 | 3 | 0 | 0 | 0 | 45
22-0086246 | Shasta | VOLTA 1102 | VOLTA 11021504 | Animal | 2022-07-17 07:50 | 7/11 - 7/17 | 2022-07-17 10:38 | 168 | FTS | 182910 | 1175 | 106 | 73 | 17 | 3 | 0 | 0 | 155.6681
22-0086247 | Napa | SILVERADO 2104 | SILVERADO 2104726 | 3rd Party | 2022-07-17 08:01 | 7/11 - 7/17 | 2022-07-17 13:34 | 333 | FTS | 115551 | 347 | 19 | 11 | 13 | 3 | 0 | 0 | 333
22-0086260 | San Luis Obispo | ATASCADERO 1103 | ATASCADERO 1103A16 | Animal | 2022-07-17 09:24 | 7/11 - 7/17 | 2022-07-17 11:30 | 126 | FTS | 28350 | 225 | 7 | 4 | 3 | 0 | 0 | 0 | 126
22-0086273 | Nevada | BRUNSWICK 1106 | BRUNSWICK 110651486 | Vegetation | 2022-07-17 12:24 | 7/11 - 7/17 | 2022-07-17 19:40 | 436 | FTS | 77958 | 1066 | 82 | 53 | 9 | 0 | 0 | 6 | 73.1313
22-0086278 | Lake | KONOCTI 1102 | KONOCTI 1102714370 | Unknown | 2022-07-17 13:30 | 7/11 - 7/17 | 2022-07-17 14:55 | 85 | FTS | 9860 | 116 | 12 | 11 | 1 | 0 | 0 | 0 | 85
22-0086286 | Sonoma | BELLEVUE 2103 | BELLEVUE 2103552 | Vegetation | 2022-07-17 14:28 | 7/11 - 7/17 | 2022-07-17 16:22 | 114 | FTS | 95760 | 840 | 50 | 39 | 16 | 0 | 0 | 12 | 114
22-0086296 | Humboldt | GARBERVILLE 1102 | GARBERVILLE 11022124 | Unknown | 2022-07-17 16:06 | 7/11 - 7/17 | 2022-07-17 19:14 | 188 | FTS | 752 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 188
22-0086308 | Mariposa | BEAR VALLEY 2101 | BEAR VALLEY 21014500 | Equipment | 2022-07-17 19:09 | 7/11 - 7/17 | 2022-07-17 20:19 | 70 | FTS | 37870 | 541 | 29 | 19 | 14 | 3 | 0 | 0 | 70
22-0086312 | Mariposa | MARIPOSA 2102 | MARIPOSA 210210880 | Equipment | 2022-07-17 19:41 | 7/11 - 7/17 | 2022-07-18 02:54 | 433 | FTS | 93160 | 481 | 49 | 35 | 5 | 0 | 0 | 0 | 193.6798
22-0086317 | Santa Barbara | BUELLTON 1101 | BUELLTON 1101Y06 | Unknown | 2022-07-17 20:27 | 7/11 - 7/17 | 2022-07-17 23:32 | 185 | FTS | 64195 | 347 | 5 | 5 | 10 | 0 | 0 | 0 | 185
22-0086344 | Marin | LAS GALLINAS A 1105 | LAS GALLINAS A 11051105/2 | Vegetation | 2022-07-18 03:19 | 7/18 - 7/24 | 2022-07-18 04:53 | 94 | C/OUT | 99448 | 2837 | 157 | 86 | 51 | 9 | 0 | 0 | 35.0539
22-0086345 | Alameda | CAYETANO 2111 | CAYETANO 21112111/2 | Unknown | 2022-07-18 04:02 | 7/18 - 7/24 | 2022-07-18 07:48 | 226 | FTS | 467594 | 2069 | 48 | 28 | 26 | 4 | 0 | 0 | 226
22-0086346 | Santa Cruz | PAUL SWEET 2104 | PAUL SWEET 2104885736 | Animal | 2022-07-18 04:32 | 7/18 - 7/24 | 2022-07-18 05:38 | 66 | FTS | 28908 | 438 | 44 | 35 | 5 | 1 | 0 | 0 | 66
22-0086350 | Shasta | ANDERSON 1103 | ANDERSON 11031600 | Animal | 2022-07-18 04:58 | 7/18 - 7/24 | 2022-07-18 07:11 | 133 | FTS | 17157 | 129 | 10 | 7 | 4 | 0 | 0 | 0 | 133
22-0086357 | Monterey | GABILAN 1101 | GABILAN 1101460414 | Unknown | 2022-07-18 05:54 | 7/18 - 7/24 | 2022-07-18 08:18 | 144 | FTS | 5616 | 39 | 3 | 2 | 0 | 0 | 0 | 0 | 144
22-0086360 | El Dorado | CLARKSVILLE 2104 | CLARKSVILLE 210419772 | Unknown | 2022-07-18 06:09 | 7/18 - 7/24 | 2022-07-18 09:10 | 181 | FTS | 44164 | 244 | 22 | 15 | 3 | 0 | 0 | 8 | 181
22-0086361 | Sonoma | DUNBAR 1103 | DUNBAR 1103302 | Animal | 2022-07-18 06:20 | 7/18 - 7/24 | 2022-07-18 07:41 | 81 | FTS | 117528 | 2476 | 247 | 192 | 19 | 0 | 0 | 12 | 47.4669
22-0069306 | Calaveras | STANISLAUS 1701 | STANISLAUS 170179826 | Company Initiated | 2022-07-18 06:38 | 7/18 - 7/24 | 2022-07-18 07:22 | 44 | FTS | 86636 | 1969 | 119 | 93 | 30 | 6 | 0 | 1 | 44
22-0086367 | Calaveras | STANISLAUS 1702 | STANISLAUS 17021850 | Unknown | 2022-07-18 06:38 | 7/18 - 7/24 | 2022-07-18 11:50 | 312 | FTS | 472093 | 2453 | 92 | 69 | 27 | 3 | 2 | 0 | 192.4554
22-0086369 | Monterey | LAURELES 1111 | LAURELES 11112020 | Unknown | 2022-07-18 06:43 | 7/18 - 7/24 | 2022-07-18 09:15 | 152 | FTS | 128896 | 848 | 24 | 14 | 26 | 0 | 0 | 0 | 152
22-0086437 | Amador | OLETA 1102 | OLETA 1102186326 | Unknown | 2022-07-18 08:50 | 7/18 - 7/24 | 2022-07-18 12:23 | 213 | FTS | 205599 | 967 | 38 | 24 | 19 | 1 | 0 | 6 | 212.6153
22-0086493 | Monterey | RESERVATION ROAD 1102 | RESERVATION ROAD 11023032 | Equipment | 2022-07-18 09:41 | 7/18 - 7/24 | 2022-07-18 12:03 | 142 | FTS | 15478 | 109 | 9 | 8 | 1 | 0 | 0 | 0 | 142
22-0086510 | Nevada | NARROWS 2102 | NARROWS 210248484 | Company Initiated | 2022-07-18 09:53 | 7/18 - 7/24 | 2022-07-18 10:46 | 53 | FTS | 31588 | 596 | 38 | 24 | 18 | 6 | 0 | 10 | 53
22-0086525 | Plumas | HAMILTON BRANCH 1101 | HAMILTON BRANCH 110190334 | Equipment | 2022-07-18 10:18 | 7/18 - 7/24 | 2022-07-18 12:28 | 130 | FTS | 39182 | 303 | 17 | 14 | 7 | 0 | 0 | 0 | 129.3135
22-0086554 | Calaveras | PEORIA 1704 | PEORIA 170411232 | Unknown | 2022-07-18 10:59 | 7/18 - 7/24 | 2022-07-18 16:16 | 317 | FTS | 658020 | 2382 | 196 | 137 | 55 | 2 | 0 | 2 | 276.2469
22-0086709 | Santa Clara | LLAGAS 2107 | LLAGAS 2107374344 | Vegetation | 2022-07-18 14:51 | 7/18 - 7/24 | 2022-07-19 02:43 | 712 | FTS | 14074 | 263 | 21 | 11 | 3 | 0 | 0 | 0 | 53.5133
22-0086744 | Santa Cruz | GREEN VALLEY 2101 | GREEN VALLEY 2101942143 | Company Initiated | 2022-07-18 16:03 | 7/18 - 7/24 | 2022-07-18 17:01 | 58 | FTS | 4350 | 75 | 2 | 2 | 0 | 0 | 0 | 2 | 58
22-0086751 | Kern | MAGUNDEN 1108 | MAGUNDEN 1108250674 | 3rd Party | 2022-07-18 16:26 | 7/18 - 7/24 | 2022-07-18 17:22 | 56 | FTS | 5824 | 104 | 1 | 1 | 1 | 0 | 0 | 0 | 56
22-0086778 | Contra Costa | MORAGA 1102 | MORAGA 110242914 | Unknown | 2022-07-18 18:17 | 7/18 - 7/24 | 2022-07-18 19:37 | 80 | FTS | 39506 | 1441 | 39 | 30 | 15 | 3 | 0 | 0 | 27.4157
22-0086798 | Tulare | STONE CORRAL 1110 | STONE CORRAL 1110894956 | Animal | 2022-07-18 20:09 | 7/18 - 7/24 | 2022-07-18 23:13 | 184 | FTS | 4232 | 23 | 1 | 1 | 0 | 0 | 0 | 0 | 184
22-0086808 | Monterey | RESERVATION ROAD 1102 | RESERVATION ROAD 11021102/2 | Animal | 2022-07-18 20:35 | 7/18 - 7/24 | 2022-07-19 00:54 | 259 | FTS | 237674 | 2114 | 88 | 64 | 38 | 2 | 0 | 0 | 112.4286
22-0086815 | Sonoma | CALISTOGA 1101 | CALISTOGA 110178734 | Unknown | 2022-07-18 21:07 | 7/18 - 7/24 | 2022-07-19 11:13 | 846 | FTS | 70506 | 166 | 5 | 5 | 1 | 0 | 0 | 0 | 424.7349
22-0086855 | Yuba | WHEATLAND 1105 | WHEATLAND 1105248490 | Unknown | 2022-07-19 04:13 | 7/18 - 7/24 | 2022-07-19 06:56 | 163 | FTS | 34556 | 212 | 12 | 6 | 3 | 0 | 0 | 4 | 163
22-0086861 | Napa | PUEBLO 2104 | PUEBLO 2104656 | Unknown | 2022-07-19 05:50 | 7/18 - 7/24 | 2022-07-19 10:05 | 255 | FTS | 84915 | 333 | 12 | 7 | 12 | 0 | 0 | 0 | 255
22-0086867 | San Benito | TRES PINOS 1111 | TRES PINOS 11114032 | Animal | 2022-07-19 06:21 | 7/18 - 7/24 | 2022-07-19 07:05 | 44 | FTS | 7148 | 168 | 6 | 6 | 4 | 3 | 0 | 0 | 42.5476
22-0086882 | Tuolumne | MIWUK 1702 | MIWUK 1702823548 | Animal | 2022-07-19 07:00 | 7/18 - 7/24 | 2022-07-19 17:09 | 609 | FTS | 87810 | 841 | 66 | 49 | 12 | 0 | 0 | 0 | 104.4114
22-0086960 | Sonoma | FULTON 1107 | FULTON 1107214 | Equipment | 2022-07-19 08:53 | 7/18 - 7/24 | 2022-07-19 13:11 | 258 | FTS | 63256 | 474 | 25 | 20 | 12 | 0 | 0 | 4 | 133.4515
22-0087059 | Shasta | PANORAMA 1102 | PANORAMA 11021342 | Unknown | 2022-07-19 11:02 | 7/18 - 7/24 | 2022-07-19 13:30 | 148 | FTS | 41061 | 544 | 51 | 34 | 3 | 0 | 0 | 0 | 75.4798
22-0087137 | San Luis Obispo | TEMPLETON 2111 | TEMPLETON 2111686138 | Company Initiated | 2022-07-19 13:15 | 7/18 - 7/24 | 2022-07-19 14:05 | 50 | FTS | 4250 | 85 | 6 | 5 | 0 | 0 | 0 | 0 | 50
22-0087151 | Santa Cruz | CAMP EVERS 2106 | CAMP EVERS 210616000 | 3rd Party | 2022-07-19 13:36 | 7/18 - 7/24 | 2022-07-19 18:04 | 268 | FTS | 740990 | 2836 | 230 | 184 | 42 | 7 | 0 | 14 | 261.28
22-0087247 | El Dorado | EL DORADO PH 2101 | EL DORADO PH 210113362 | Company Initiated | 2022-07-19 15:03 | 7/18 - 7/24 | 2022-07-19 15:55 | 52 | FTS | 23400 | 450 | 9 | 8 | 12 | 0 | 0 | 0 | 52
22-0087298 | Santa Cruz | BIG BASIN 1102 | BIG BASIN 110212758 | Vegetation | 2022-07-19 16:55 | 7/18 - 7/24 | 2022-07-19 18:42 | 107 | FTS | 29639 | 277 | 17 | 16 | 6 | 0 | 0 | 0 | 107
22-0087318 | Placer | SHADY GLEN 1102 | SHADY GLEN 11022232 | 3rd Party | 2022-07-19 17:39 | 7/18 - 7/24 | 2022-07-19 20:50 | 191 | FTS | 67805 | 355 | 29 | 21 | 16 | 0 | 0 | 1 | 191
22-0087376 | Tehama | TYLER 1105 | TYLER 110585132 | Unknown | 2022-07-19 21:53 | 7/18 - 7/24 | 2022-07-20 10:08 | 735 | FTS | 168476 | 834 | 87 | 55 | 13 | 2 | 0 | 1 | 202.0096
22-0087394 | Sonoma | LAKEVILLE 1102 | LAKEVILLE 1102347280 | Unknown | 2022-07-19 22:13 | 7/18 - 7/24 | 2022-07-20 09:12 | 659 | FTS | 62498 | 97 | 2 | 1 | 1 | 0 | 0 | 2 | 644.3093
22-0087412 | Marin | BOLINAS 1101 | BOLINAS 1101504 | Unknown | 2022-07-19 23:34 | 7/18 - 7/24 | 2022-07-20 10:43 | 669 | FTS | 564492 | 844 | 17 | 8 | 10 | 1 | 0 | 0 | 668.8294
22-0087427 | Lake | HIGHLANDS 1102 | HIGHLANDS 110275140 | Equipment | 2022-07-20 05:42 | 7/18 - 7/24 | 2022-07-20 15:17 | 575 | FTS | 266239 | 2617 | 295 | 209 | 34 | 9 | 1 | 0 | 101.7344
22-0087576 | Placer | HALSEY 1101 | HALSEY 110176178 | Unknown | 2022-07-20 10:29 | 7/18 - 7/24 | 2022-07-20 13:08 | 159 | FTS | 99852 | 628 | 46 | 34 | 4 | 0 | 0 | 0 | 159
22-0087634 | Mariposa | MARIPOSA 2102 | MARIPOSA 210237288 | Unknown | 2022-07-20 11:43 | 7/18 - 7/24 | 2022-07-20 15:43 | 240 | FTS | 139200 | 580 | 46 | 35 | 13 | 5 | 0 | 0 | 240
22-0087688 | Placer | HALSEY 1101 | HALSEY 11012414 | Unknown | 2022-07-20 12:56 | 7/18 - 7/24 | 2022-07-20 15:49 | 173 | FTS | 61991 | 403 | 26 | 20 | 7 | 0 | 0 | 3 | 153.8238
22-0087757 | Sonoma | MIRABEL 1102 | MIRABEL 110286326 | Vegetation | 2022-07-20 14:24 | 7/18 - 7/24 | 2022-07-20 19:50 | 326 | FTS | 15789 | 261 | 9 | 8 | 7 | 0 | 0 | 0 | 60.4943
22-0087759 | Fresno | AUBERRY 1102 | AUBERRY 110237466 | Unknown | 2022-07-20 14:29 | 7/18 - 7/24 | 2022-07-20 17:21 | 172 | FTS | 69832 | 406 | 42 | 28 | 2 | 0 | 0 | 1 | 172
22-0087786 | Monterey | RESERVATION ROAD 1102 | RESERVATION ROAD 11023030 | Unknown | 2022-07-20 15:02 | 7/18 - 7/24 | 2022-07-20 16:40 | 98 | FTS | 20008 | 221 | 3 | 2 | 2 | 0 | 0 | 0 | 90.5339
22-0087812 | Placer | FORESTHILL 1101 | FORESTHILL 11011802 | 3rd Party | 2022-07-20 15:30 | 7/18 - 7/24 | 2022-07-21 01:48 | 618 | FTS | 220720 | 1658 | 172 | 113 | 20 | 2 | 0 | 0 | 133.1242
22-0087830 | Lake | LUCERNE 1103 | LUCERNE 11034624 | Animal | 2022-07-20 16:00 | 7/18 - 7/24 | 2022-07-20 18:15 | 135 | FTS | 51030 | 378 | 54 | 41 | 11 | 0 | 0 | 0 | 135
22-0087867 | Placer | HALSEY 1101 | HALSEY 110176178 | Vegetation | 2022-07-20 17:17 | 7/18 - 7/24 | 2022-07-20 21:11 | 234 | FTS | 40027 | 628 | 46 | 34 | 4 | 0 | 0 | 0 | 63.7373
22-0087896 | Shasta | ANDERSON 1103 | ANDERSON 11031600 | Animal | 2022-07-20 19:37 | 7/18 - 7/24 | 2022-07-20 21:29 | 112 | FTS | 7408 | 129 | 10 | 7 | 4 | 0 | 0 | 0 | 57.4264
22-0087897 | Monterey | OILFIELDS 1103 | OILFIELDS 1103N48 | Unknown | 2022-07-20 19:49 | 7/18 - 7/24 | 2022-07-20 22:17 | 148 | FTS | 41144 | 278 | 10 | 4 | 4 | 0 | 0 | 2 | 148
22-0087913 | El Dorado | CLARKSVILLE 2106 | CLARKSVILLE 210619642 | Equipment | 2022-07-20 20:57 | 7/18 - 7/24 | 2022-07-21 12:34 | 937 | FTS | 192302 | 846 | 60 | 38 | 21 | 1 | 0 | 0 | 227.3073
22-0087915 | Lassen | MC ARTHUR 1101 | MC ARTHUR 11011544 | Unknown | 2022-07-20 21:33 | 7/18 - 7/24 | 2022-07-21 02:37 | 304 | FTS | 79948 | 366 | 15 | 12 | 20 | 3 | 0 | 0 | 218.4372
22-0087934 | Santa Cruz | PAUL SWEET 2106 | PAUL SWEET 21065178 | Animal | 2022-07-20 22:56 | 7/18 - 7/24 | 2022-07-21 08:13 | 557 | FTS | 78567 | 267 | 30 | 27 | 5 | 0 | 0 | 1 | 294.2584
22-0087938 | Sonoma | FITCH MOUNTAIN 1113 | FITCH MOUNTAIN 111324550 | Vegetation | 2022-07-20 23:23 | 7/18 - 7/24 | 2022-07-21 00:53 | 90 | FTS | 19890 | 221 | 6 | 4 | 7 | 0 | 0 | 2 | 90
22-0087945 | Shasta | PANORAMA 1102 | PANORAMA 11021526 | Animal | 2022-07-21 03:58 | 7/18 - 7/24 | 2022-07-21 06:27 | 149 | FTS | 15033 | 103 | 8 | 7 | 2 | 0 | 0 | 0 | 145.9515
22-0088013 | Contra Costa | ROSSMOOR 1106 | ROSSMOOR 1106L522R | Unknown | 2022-07-21 08:23 | 7/18 - 7/24 | 2022-07-21 10:12 | 109 | FTS | 215185 | 2221 | 54 | 38 | 14 | 8 | 0 | 0 | 96.8865
22-0088027 | San Luis Obispo | PASO ROBLES 1103 | PASO ROBLES 110355374 | Unknown | 2022-07-21 08:48 | 7/18 - 7/24 | 2022-07-21 12:26 | 218 | FTS | 86146 | 517 | 13 | 8 | 5 | 0 | 0 | 0 | 166.6267
22-0088073 | Calaveras | CALAVERAS CEMENT 1101 | CALAVERAS CEMENT 110111236 | Animal | 2022-07-21 09:54 | 7/18 - 7/24 | 2022-07-22 02:38 | 1004 | FTS | 23614 | 182 | 11 | 9 | 6 | 0 | 0 | 0 | 129.7473
22-0088196 | Fresno | AUBERRY 1102 | AUBERRY 110237466 | Unknown | 2022-07-21 12:25 | 7/18 - 7/24 | 2022-07-21 15:18 | 173 | FTS | 70238 | 406 | 42 | 28 | 2 | 0 | 0 | 1 | 173
22-0088199 | Fresno | AUBERRY 1102 | AUBERRY 1102R902 | Unknown | 2022-07-21 12:27 | 7/18 - 7/24 | 2022-07-21 14:58 | 151 | FTS | 42884 | 284 | 29 | 19 | 5 | 0 | 0 | 1 | 151
22-0088246 | Napa | MONTICELLO 1101 | MONTICELLO 1101256640 | Unknown | 2022-07-21 13:22 | 7/18 - 7/24 | 2022-07-21 16:06 | 164 | FTS | 6789 | 42 | 0 | 0 | 4 | 0 | 0 | 0 | 161.6429
22-0088313 | Humboldt | GARBERVILLE 1102 | GARBERVILLE 11021102/2 | Vegetation | 2022-07-21 14:57 | 7/18 - 7/24 | 2022-07-21 17:35 | 158 | FTS | 270572 | 1936 | 41 | 26 | 60 | 11 | 0 | 0 | 139.7583
22-0088341 | Sonoma | CALISTOGA 1101 | CALISTOGA 1101242919 | Unknown | 2022-07-21 15:31 | 7/18 - 7/24 | 2022-07-21 16:54 | 83 | FTS | 1992 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 83
22-0088399 | Nevada | BRUNSWICK 1110 | BRUNSWICK 11101110/2 | Equipment | 2022-07-21 18:22 | 7/18 - 7/24 | 2022-07-22 02:47 | 505 | FTS | 506221 | 3153 | 210 | 149 | 64 | 14 | 4 | 5 | 160.5522
22-0088422 | Mariposa | MARIPOSA 2101 | MARIPOSA 210110240 | Unknown | 2022-07-21 21:06 | 7/18 - 7/24 | 2022-07-22 12:41 | 935 | FTS | 413000 | 469 | 24 | 16 | 8 | 0 | 0 | 0 | 880.597
22-0088472 | Nevada | HIGGINS 1103 | HIGGINS 1103995672 | Vegetation | 2022-07-22 00:56 | 7/18 - 7/24 | 2022-07-22 17:12 | 976 | FTS | 36772 | 217 | 14 | 9 | 2 | 0 | 0 | 0 | 169.4562
22-0088473 | Santa Clara | SARATOGA 1106 | SARATOGA 1106LC24 | Vegetation | 2022-07-22 01:58 | 7/18 - 7/24 | 2022-07-22 19:30 | 1052 | FTS | 111576 | 1154 | 64 | 43 | 18 | 1 | 0 | 0 | 96.6863
22-0088485 | Santa Barbara | CABRILLO 1103 | CABRILLO 1103Y46 | Unknown | 2022-07-22 05:57 | 7/18 - 7/24 | 2022-07-22 08:57 | 180 | FTS | 23755 | 275 | 2 | 2 | 5 | 0 | 0 | 0 | 86.3818
22-0088574 | San Luis Obispo | OCEANO 1104 | OCEANO 1104891294 | Vegetation | 2022-07-22 08:40 | 7/18 - 7/24 | 2022-07-22 13:35 | 295 | FTS | 62863 | 870 | 41 | 32 | 5 | 1 | 0 | 10 | 72.2563
22-0088601 | El Dorado | SHINGLE SPRINGS 2109 | SHINGLE SPRINGS 21099372 | Unknown | 2022-07-22 08:59 | 7/18 - 7/24 | 2022-07-22 12:29 | 210 | HLT | 299597 | 2117 | 165 | 113 | 24 | 2 | 0 | 30 | 141.5196
22-0088619 | Santa Cruz | BIG BASIN 1102 | BIG BASIN 1102351054 | Animal | 2022-07-22 09:29 | 7/18 - 7/24 | 2022-07-22 12:17 | 168 | FTS | 67548 | 831 | 48 | 33 | 14 | 1 | 0 | 1 | 81.2852
22-0085482 | Santa Cruz | BIG BASIN 1102 | BIG BASIN 1102573005 | Company Initiated | 2022-07-22 12:47 | 7/18 - 7/24 | 2022-07-22 13:05 | 18 | FTS | 720 | 40 | 4 | 3 | 0 | 0 | 0 | 0 | 18
22-0088784 | Kern | POSO MOUNTAIN 2104 | POSO MOUNTAIN 210448268 | Unknown | 2022-07-22 13:19 | 7/18 - 7/24 | 2022-07-22 17:16 | 237 | FTS | 2133 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 237
22-0085525 | Monterey | SOLEDAD 2105 | SOLEDAD 2105315500 | Company Initiated | 2022-07-22 19:22 | 7/18 - 7/24 | 2022-07-22 19:58 | 36 | FTS | 14557 | 602 | 13 | 11 | 9 | 0 | 0 | 0 | 24.1811
22-0088913 | Marin | ALTO 1125 | ALTO 11251256 | Unknown | 2022-07-22 22:15 | 7/18 - 7/24 | 2022-07-23 01:01 | 166 | FTS | 305163 | 2122 | 78 | 52 | 22 | 2 | 0 | 0 | 143.8091
22-0088914 | Monterey | KING CITY 1102 | KING CITY 1102728782 | Unknown | 2022-07-22 22:20 | 7/18 - 7/24 | 2022-07-22 22:52 | 32 | FTS | 160 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 32
22-0088928 | Santa Clara | MORGAN HILL 2105 | MORGAN HILL 2105XR564 | Unknown | 2022-07-23 02:56 | 7/18 - 7/24 | 2022-07-23 06:15 | 199 | FTS | 71043 | 357 | 19 | 15 | 10 | 2 | 0 | 0 | 199
22-0088944 | Sonoma | GEYSERVILLE 1102 | GEYSERVILLE 1102274 | Unknown | 2022-07-23 07:09 | 7/18 - 7/24 | 2022-07-23 10:20 | 191 | FTS | 77310 | 420 | 11 | 3 | 8 | 1 | 0 | 1 | 184.0714
22-0088948 | Marin | STAFFORD 1101 | STAFFORD 11011102/2 | Unknown | 2022-07-23 07:22 | 7/18 - 7/24 | 2022-07-23 14:23 | 421 | FTS | 1383109 | 3971 | 232 | 145 | 27 | 7 | 0 | 0 | 348.3024
22-0088949 | Marin | WOODACRE 1102 | WOODACRE 1102137662 | Animal | 2022-07-23 07:32 | 7/18 - 7/24 | 2022-07-23 11:02 | 210 | FTS | 322106 | 1891 | 90 | 49 | 28 | 6 | 0 | 0 | 170.3363
22-0088954 | Monterey | JOLON 1103 | JOLON 11031103/2 | Unknown | 2022-07-23 07:55 | 7/18 - 7/24 | 2022-07-23 11:53 | 238 | FTS | 4760 | 20 | 0 | 0 | 15 | 0 | 0 | 0 | 238
22-0088956 | Tuolumne | SPRING GAP 1702 | SPRING GAP 17029280 | Equipment | 2022-07-23 08:06 | 7/18 - 7/24 | 2022-07-23 18:52 | 646 | FTS | 617106 | 1536 | 35 | 23 | 18 | 2 | 0 | 0 | 401.7617
22-0088999 | Santa Cruz | CAMP EVERS 2106 | CAMP EVERS 2106737512 | Vegetation | 2022-07-23 12:08 | 7/18 - 7/24 | 2022-07-23 13:50 | 102 | FTS | 63204 | 918 | 71 | 48 | 10 | 0 | 0 | 0 | 68.8497
22-0083562 | Santa Cruz | CAMP EVERS 2106 | CAMP EVERS 210612840 | Company Initiated | 2022-07-23 13:28 | 7/18 - 7/24 | 2022-07-23 14:43 | 75 | FTS | 4500 | 60 | 9 | 8 | 2 | 0 | 0 | 0 | 75
22-0089022 | Santa Clara | MORGAN HILL 2111 | MORGAN HILL 2111XR398 | 3rd Party | 2022-07-23 14:20 | 7/18 - 7/24 | 2022-07-23 15:03 | 43 | FTS | 8253 | 400 | 23 | 20 | 10 | 0 | 0 | 1 | 20.6325
22-0089050 | Placer | DEL MAR 2109 | DEL MAR 210975802 | Unknown | 2022-07-23 18:06 | 7/18 - 7/24 | 2022-07-23 19:23 | 77 | FTS | 211981 | 2753 | 152 | 97 | 26 | 1 | 0 | 1 | 77
22-0089057 | Santa Cruz | ROB ROY 2105 | ROB ROY 210512586 | Animal | 2022-07-23 21:11 | 7/18 - 7/24 | 2022-07-23 22:01 | 50 | FTS | 53900 | 1078 | 95 | 80 | 8 | 3 | 0 | 0 | 50
22-0089059 | Calaveras | STANISLAUS 1701 | STANISLAUS 17011701/2 | 3rd Party | 2022-07-23 21:47 | 7/18 - 7/24 | 2022-07-24 14:32 | 1005 | FTS | 1547525 | 2187 | 134 | 100 | 68 | 4 | 0 | 0 | 707.6017
22-0089092 | Kings | AVENAL 2101 | AVENAL 21019070 | Animal | 2022-07-23 23:22 | 7/18 - 7/24 | 2022-07-24 04:25 | 303 | FTS | 20604 | 68 | 0 | 0 | 9 | 0 | 0 | 0 | 303
22-0089093 | Sonoma | BELLEVUE 2103 | BELLEVUE 2103552 | Vegetation | 2022-07-24 01:24 | 7/18 - 7/24 | 2022-07-24 11:06 | 582 | FTS | 69298 | 839 | 50 | 39 | 16 | 0 | 0 | 12 | 82.5959
22-0089094 | Contra Costa | WILLOW PASS 2108 | WILLOW PASS 21082108/2 | Unknown | 2022-07-24 01:35 | 7/18 - 7/24 | 2022-07-24 03:27 | 112 | FTS | 220448 | 5616 | 290 | 200 | 47 | 6 | 0 | 0 | 39.2536
22-0089102 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 210623190 | Unknown | 2022-07-24 06:10 | 7/18 - 7/24 | 2022-07-24 08:42 | 152 | FTS | 272220 | 1994 | 148 | 92 | 26 | 4 | 1 | 4 | 136.5196
22-0089101 | Madera | OAKHURST 1101 | OAKHURST 11015490 | Unknown | 2022-07-24 06:12 | 7/18 - 7/24 | 2022-07-24 10:00 | 228 | FTS | 345684 | 1554 | 175 | 128 | 31 | 2 | 0 | 0 | 222.4479
22-0089109 | Contra Costa | SOBRANTE 1103 | SOBRANTE 11031103/2 | Unknown | 2022-07-24 07:28 | 7/18 - 7/24 | 2022-07-24 11:52 | 264 | C/OUT | 259248 | 982 | 61 | 42 | 15 | 1 | 0 | 0 | 264
22-0089131 | Alameda | VINEYARD 2108 | VINEYARD 2108MR172 | Equipment | 2022-07-24 10:21 | 7/18 - 7/24 | 2022-07-25 03:13 | 1012 | FTS | 476344 | 3026 | 173 | 116 | 38 | 2 | 0 | 0 | 157.4171
22-0089157 | San Luis Obispo | TEMPLETON 2112 | TEMPLETON 2112R28 | Unknown | 2022-07-24 13:42 | 7/18 - 7/24 | 2022-07-24 17:40 | 238 | FTS | 78039 | 329 | 8 | 6 | 9 | 0 | 0 | 0 | 237.2006
22-0089171 | Humboldt | GARBERVILLE 1101 | GARBERVILLE 11011750 | Vegetation | 2022-07-24 15:32 | 7/18 - 7/24 | 2022-07-25 02:15 | 643 | FTS | 18764 | 92 | 1 | 1 | 2 | 0 | 0 | 0 | 203.9565
22-0089197 | Sonoma | GEYSERVILLE 1102 | GEYSERVILLE 1102484 | Animal | 2022-07-24 18:39 | 7/18 - 7/24 | 2022-07-24 21:00 | 141 | FTS | 53862 | 382 | 5 | 2 | 15 | 1 | 0 | 1 | 141
22-0089205 | Tuolumne | CURTIS 1702 | CURTIS 17028000 | Equipment | 2022-07-24 20:24 | 7/18 - 7/24 | 2022-07-25 08:21 | 717 | FTS | 161768 | 1152 | 107 | 80 | 16 | 1 | 0 | 0 | 140.4236
22-0089220 | Contra Costa | ORINDA 0401 | ORINDA 0401401/2 | Vegetation | 2022-07-24 22:21 | 7/18 - 7/24 | 2022-07-25 03:43 | 322 | FTS | 53846 | 293 | 17 | 11 | 2 | 0 | 0 | 0 | 183.7747
22-0089243 | Tuolumne | CURTIS 1702 | CURTIS 170234426 | Vegetation | 2022-07-24 23:39 | 7/18 - 7/24 | 2022-07-25 04:26 | 287 | FTS | 161007 | 561 | 35 | 24 | 9 | 2 | 0 | 0 | 287
22-0089253 | Santa Cruz | BEN LOMOND 1101 | BEN LOMOND 1101BL 2101 | 3rd Party | 2022-07-25 02:49 | 7/25 - 7/31 | 2022-07-25 13:33 | 644 | FTS | 297804 | 1966 | 146 | 110 | 33 | 3 | 0 | 1 | 151.4771
22-0089262 | Tehama | CORNING 1101 | CORNING 110185152 | Unknown | 2022-07-25 06:09 | 7/25 - 7/31 | 2022-07-25 09:42 | 213 | FTS | 81123 | 476 | 67 | 40 | 9 | 0 | 0 | 0 | 170.4265
22-0089264 | Sonoma | DUNBAR 1102 | DUNBAR 1102246 | Unknown | 2022-07-25 06:27 | 7/25 - 7/31 | 2022-07-25 10:15 | 228 | FTS | 117817 | 532 | 23 | 13 | 8 | 0 | 0 | 7 | 221.4605
22-0089270 | Lake | KONOCTI 1102 | KONOCTI 110264664 | Unknown | 2022-07-25 06:47 | 7/25 - 7/31 | 2022-07-25 09:58 | 191 | FTS | 96281 | 507 | 38 | 26 | 3 | 0 | 0 | 1 | 189.9034
22-0089287 | Placer | PENRYN 1106 | PENRYN 110651674 | Vegetation | 2022-07-25 07:51 | 7/25 - 7/31 | 2022-07-25 14:49 | 418 | FTS | 164246 | 907 | 64 | 39 | 6 | 3 | 0 | 0 | 181.0871
22-0089321 | Sonoma | CALISTOGA 1101 | CALISTOGA 110178734 | Equipment | 2022-07-25 09:11 | 7/25 - 7/31 | 2022-07-25 22:12 | 781 | FTS | 51694 | 166 | 5 | 5 | 1 | 0 | 0 | 0 | 311.4096
22-0089327 | Nevada | NARROWS 2105 | NARROWS 21052216 | Animal | 2022-07-25 09:25 | 7/25 - 7/31 | 2022-07-25 12:09 | 164 | FTS | 166096 | 2101 | 177 | 102 | 28 | 4 | 0 | 19 | 79.0557
22-0089340 | San Benito | HOLLISTER 2102 | HOLLISTER 2102113634 | Unknown | 2022-07-25 10:00 | 7/25 - 7/31 | 2022-07-25 11:01 | 61 | FTS | 4819 | 79 | 3 | 1 | 3 | 0 | 0 | 0 | 61
22-0089359 | Butte | SYCAMORE CREEK 1109 | SYCAMORE CREEK 11091109/2 | Animal | 2022-07-25 10:01 | 7/25 - 7/31 | 2022-07-25 16:45 | 404 | FTS | 238106 | 2372 | 158 | 104 | 30 | 1 | 0 | 0 | 100.382
22-0089355 | Solano | JAMESON 1102 | JAMESON 11028842 | Animal | 2022-07-25 10:21 | 7/25 - 7/31 | 2022-07-25 11:59 | 98 | FTS | 66354 | 783 | 72 | 52 | 22 | 0 | 0 | 2 | 84.7433
22-0089414 | Butte | BIG BEND 1102 | BIG BEND 11021102/2 | Unknown | 2022-07-25 12:04 | 7/25 - 7/31 | 2022-07-25 14:30 | 146 | FTS | 47450 | 325 | 8 | 4 | 11 | 0 | 0 | 0 | 146
22-0089503 | Napa | MONTICELLO 1101 | MONTICELLO 110137384 | Unknown | 2022-07-25 14:43 | 7/25 - 7/31 | 2022-07-25 16:49 | 126 | FTS | 63630 | 505 | 27 | 19 | 11 | 0 | 0 | 2 | 126
22-0089546 | Butte | BIG BEND 1102 | BIG BEND 11021102/2 | Equipment | 2022-07-25 16:09 | 7/25 - 7/31 | 2022-07-26 05:00 | 771 | FTS | 121377 | 635 | 28 | 17 | 18 | 0 | 0 | 1 | 191.1449
22-0089562 | Mendocino | UKIAH 1111 | UKIAH 1111433984 | Unknown | 2022-07-25 16:56 | 7/25 - 7/31 | 2022-07-25 19:47 | 171 | HLT | 180180 | 1072 | 39 | 20 | 21 | 6 | 0 | 0 | 168.0784
22-0089573 | Solano | VACAVILLE 1108 | VACAVILLE 11088762 | Animal | 2022-07-25 18:51 | 7/25 - 7/31 | 2022-07-25 19:57 | 66 | FTS | 24232 | 423 | 22 | 15 | 15 | 1 | 0 | 2 | 57.2861
22-0089576 | Humboldt | BRIDGEVILLE 1101 | BRIDGEVILLE 110169866 | Unknown | 2022-07-25 18:58 | 7/25 - 7/31 | 2022-07-26 12:04 | 1026 | FTS | 64638 | 63 | 1 | 1 | 2 | 0 | 0 | 0 | 1026
22-0089588 | Tehama | TYLER 1105 | TYLER 11051704 | Equipment | 2022-07-25 21:34 | 7/25 - 7/31 | 2022-07-26 04:28 | 414 | FTS | 119446 | 834 | 87 | 55 | 13 | 2 | 0 | 1 | 143.2206
22-0089602 | Nevada | BRUNSWICK 1110 | BRUNSWICK 11101110/2 | 3rd Party | 2022-07-25 22:25 | 7/25 - 7/31 | 2022-07-26 16:11 | 1066 | FTS | 171714 | 3076 | 203 | 143 | 63 | 14 | 4 | 5 | 55.8238
22-0089607 | Napa | SILVERADO 2102 | SILVERADO 21022102/2 | Equipment | 2022-07-26 00:19 | 7/25 - 7/31 | 2022-07-26 03:36 | 197 | FTS | 66172 | 1264 | 10 | 9 | 27 | 0 | 0 | 2 | 52.3513
22-0089608 | Monterey | GABILAN 1101 | GABILAN 11013034 | Equipment | 2022-07-26 00:27 | 7/25 - 7/31 | 2022-07-26 15:46 | 919 | FTS | 365234 | 543 | 31 | 21 | 12 | 0 | 0 | 0 | 672.6225
22-0089622 | Tuolumne | CURTIS 1703 | CURTIS 170384944 | Unknown | 2022-07-26 05:44 | 7/25 - 7/31 | 2022-07-26 07:29 | 105 | FTS | 322665 | 3073 | 201 | 148 | 44 | 1 | 0 | 5 | 105
22-0089645 | Tuolumne | CURTIS 1705 | CURTIS 170539256 | Unknown | 2022-07-26 07:21 | 7/25 - 7/31 | 2022-07-26 08:13 | 52 | FTS | 27144 | 522 | 67 | 48 | 4 | 0 | 0 | 0 | 52
22-0090027 | Plumas | CRESCENT MILLS 2101 | CRESCENT MILLS 21012562 | Animal | 2022-07-26 16:13 | 7/25 - 7/31 | 2022-07-26 18:20 | 127 | FTS | 179036 | 1533 | 66 | 49 | 25 | 1 | 5 | 0 | 116.788
22-0090046 | Mendocino | UKIAH 1115 | UKIAH 1115534 | Unknown | 2022-07-26 17:16 | 7/25 - 7/31 | 2022-07-26 19:12 | 116 | FTS | 20880 | 180 | 7 | 5 | 6 | 1 | 0 | 0 | 116
22-0090087 | Sonoma | MIRABEL 1101 | MIRABEL 1101116 | Unknown | 2022-07-26 20:50 | 7/25 - 7/31 | 2022-07-27 08:16 | 686 | FTS | 87366 | 385 | 16 | 13 | 2 | 0 | 0 | 0 | 226.9247
22-0090111 | Santa Clara | MORGAN HILL 2111 | MORGAN HILL 2111XR398 | 3rd Party | 2022-07-27 00:26 | 7/25 - 7/31 | 2022-07-28 01:23 | 1497 | FTS | 233040 | 400 | 23 | 20 | 10 | 0 | 0 | 1 | 582.6
22-0090121 | Nevada | HIGGINS 1103 | HIGGINS 110350072 | Animal | 2022-07-27 05:52 | 7/25 - 7/31 | 2022-07-27 09:39 | 227 | FTS | 146188 | 644 | 49 | 30 | 3 | 0 | 0 | 10 | 227
22-0090153 | Santa Clara | LOS GATOS 1106 | LOS GATOS 110660116 | Unknown | 2022-07-27 07:31 | 7/25 - 7/31 | 2022-07-27 10:47 | 196 | FTS | 180761 | 1135 | 91 | 72 | 23 | 3 | 0 | 3 | 159.2608
22-0090185 | Mariposa | BEAR VALLEY 2105 | BEAR VALLEY 21054170 | 3rd Party | 2022-07-27 08:30 | 7/25 - 7/31 | 2022-07-27 11:22 | 172 | FTS | 118279 | 688 | 53 | 41 | 11 | 8 | 1 | 1 | 171.9172
22-0090331 | Butte | ORO FINO 1102 | ORO FINO 11022090 | Vegetation | 2022-07-27 11:42 | 7/25 - 7/31 | 2022-07-27 13:37 | 115 | FTS | 65780 | 572 | 76 | 49 | 5 | 0 | 0 | 1 | 115
22-0090340 | Sonoma | CALISTOGA 1101 | CALISTOGA 110178734 | Company Initiated | 2022-07-27 12:25 | 7/25 - 7/31 | 2022-07-27 15:26 | 181 | FTS | 11041 | 61 | 5 | 5 | 0 | 0 | 0 | 0 | 181
22-0090474 | Plumas | HAMILTON BRANCH 1101 | HAMILTON BRANCH 1101161872 | Unknown | 2022-07-27 15:20 | 7/25 - 7/31 | 2022-07-27 18:00 | 160 | FTS | 480 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 160
22-0090520 | Placer | FORESTHILL 1101 | FORESTHILL 11011802 | 3rd Party | 2022-07-27 16:49 | 7/25 - 7/31 | 2022-07-27 19:21 | 152 | FTS | 251274 | 1658 | 172 | 113 | 20 | 2 | 0 | 0 | 151.5525
22-0090533 | Contra Costa | LAKEWOOD 1103 | LAKEWOOD 1103857172 | Animal | 2022-07-27 17:38 | 7/25 - 7/31 | 2022-07-27 18:33 | 55 | FTS | 4290 | 78 | 5 | 3 | 1 | 0 | 0 | 0 | 55
22-0090644 | Solano | VACA DIXON 1105 | VACA DIXON 11059792 | Unknown | 2022-07-28 07:26 | 7/25 - 7/31 | 2022-07-28 08:33 | 67 | FTS | 35108 | 524 | 67 | 42 | 3 | 0 | 0 | 2 | 67
22-0090813 | Sonoma | SONOMA 1105 | SONOMA 1105229588 | Company Initiated | 2022-07-28 12:00 | 7/25 - 7/31 | 2022-07-28 12:55 | 55 | FTS | 2255 | 41 | 4 | 4 | 0 | 0 | 0 | 1 | 55
22-0090893 | Placer | DRUM 1101 | DRUM 11011101/2 | Unknown | 2022-07-28 13:45 | 7/25 - 7/31 | 2022-07-28 17:23 | 218 | FTS | 36337 | 203 | 6 | 3 | 19 | 1 | 0 | 1 | 179
22-0090995 | Shasta | STILLWATER 1102 | STILLWATER 11021466 | Unknown | 2022-07-28 15:37 | 7/25 - 7/31 | 2022-07-28 19:02 | 205 | FTS | 97375 | 475 | 44 | 32 | 7 | 0 | 0 | 0 | 205
22-0091052 | Shasta | STILLWATER 1102 | STILLWATER 11021102/2 | Unknown | 2022-07-28 19:07 | 7/25 - 7/31 | 2022-07-28 22:57 | 230 | FTS | 316925 | 1420 | 120 | 82 | 16 | 0 | 0 | 0 | 223.1866
22-0091062 | Placer | WISE 1102 | WISE 11022230 | Unknown | 2022-07-28 19:57 | 7/25 - 7/31 | 2022-07-29 09:14 | 797 | FTS | 115264 | 859 | 68 | 53 | 4 | 0 | 0 | 13 | 134.1839
22-0091072 | Alameda | VASCO 1102 | VASCO 1102546328 | Unknown | 2022-07-28 20:43 | 7/25 - 7/31 | 2022-07-29 11:19 | 876 | FTS | 199728 | 228 | 20 | 14 | 7 | 0 | 0 | 1 | 876
22-0091096 | Butte | SYCAMORE CREEK 1109 | SYCAMORE CREEK 11091109/2 | Unknown | 2022-07-28 23:56 | 7/25 - 7/31 | 2022-07-29 06:08 | 372 | FTS | 493168 | 2372 | 158 | 104 | 30 | 1 | 0 | 0 | 207.9123
22-0091104 | Yolo | MADISON 2101 | MADISON 21011606 | Unknown | 2022-07-29 04:47 | 7/25 - 7/31 | 2022-07-29 09:50 | 303 | FTS | 97045 | 515 | 18 | 8 | 6 | 0 | 0 | 1 | 188.4369
22-0091109 | Shasta | MC ARTHUR 1101 | MC ARTHUR 11011488 | Unknown | 2022-07-29 05:39 | 7/25 - 7/31 | 2022-07-29 09:56 | 257 | FTS | 50115 | 195 | 6 | 3 | 0 | 0 | 0 | 0 | 257
22-0091143 | Santa Cruz | CAMP EVERS 2105 | CAMP EVERS 210510728 | Unknown | 2022-07-29 07:07 | 7/25 - 7/31 | 2022-07-29 09:35 | 148 | FTS | 389706 | 2993 | 235 | 179 | 45 | 4 | 0 | 1 | 130.2058
22-0091155 | Fresno | DUNLAP 1102 | DUNLAP 11027060 | Animal | 2022-07-29 07:27 | 7/25 - 7/31 | 2022-07-29 12:26 | 299 | FTS | 37770 | 223 | 19 | 13 | 3 | 1 | 0 | 0 | 169.3722
22-0091263 | Sonoma | BELLEVUE 2103 | BELLEVUE 2103552 | Unknown | 2022-07-29 10:14 | 7/25 - 7/31 | 2022-07-29 12:39 | 145 | FTS | 121800 | 840 | 50 | 39 | 16 | 0 | 0 | 12 | 145
22-0091323 | San Mateo | WOODSIDE 1101 | WOODSIDE 110147872 | Unknown | 2022-07-29 11:06 | 7/25 - 7/31 | 2022-07-29 13:36 | 150 | FTS | 27467 | 250 | 17 | 9 | 14 | 1 | 0 | 0 | 109.868
22-0091331 | Santa Clara | STELLING 1109 | STELLING 1109589102 | Unknown | 2022-07-29 11:38 | 7/25 - 7/31 | 2022-07-29 12:53 | 75 | FTS | 2175 | 29 | 5 | 3 | 1 | 0 | 0 | 0 | 75
22-0091424 | Santa Cruz | CAMP EVERS 2105 | CAMP EVERS 210510728 | Vegetation | 2022-07-29 13:45 | 7/25 - 7/31 | 2022-07-29 15:11 | 86 | FTS | 217998 | 2993 | 235 | 179 | 45 | 4 | 0 | 1 | 72.836
22-0091511 | Contra Costa | CLAYTON 2212 | CLAYTON 22122212/2 | 3rd Party | 2022-07-29 16:18 | 7/25 - 7/31 | 2022-07-29 17:10 | 52 | FTS | 175760 | 3380 | 291 | 192 | 78 | 8 | 0 | 5 | 52
22-0091521 | Contra Costa | CLAYTON 2212 | CLAYTON 2212614950 | Unknown | 2022-07-29 17:10 | 7/25 - 7/31 | 2022-07-29 17:43 | 33 | FTS | 1584 | 48 | 3 | 2 | 0 | 0 | 0 | 0 | 33
22-0091522 | Shasta | GIRVAN 1102 | GIRVAN 1102212096 | Unknown | 2022-07-29 17:25 | 7/25 - 7/31 | 2022-07-29 19:54 | 149 | FTS | 6854 | 46 | 4 | 2 | 0 | 0 | 0 | 0 | 149
22-0091551 | Tuolumne | CURTIS 1705 | CURTIS 170539256 | Unknown | 2022-07-29 20:02 | 7/25 - 7/31 | 2022-07-29 21:04 | 62 | FTS | 32364 | 522 | 67 | 48 | 4 | 0 | 0 | 0 | 62
22-0091554 | Placer | DEL MAR 2109 | DEL MAR 21092109/2 | Animal | 2022-07-29 20:42 | 7/25 - 7/31 | 2022-07-29 22:31 | 109 | FTS | 395999 | 4067 | 237 | 154 | 40 | 2 | 0 | 1 | 97.3688
22-0091557 | Calaveras | CALAVERAS CEMENT 1101 | CALAVERAS CEMENT 1101502 | Unknown | 2022-07-29 21:52 | 7/25 - 7/31 | 2022-07-30 08:08 | 616 | FTS | 638636 | 1039 | 58 | 43 | 24 | 0 | 0 | 0 | 614.6641
22-0091574 | Marin | STAFFORD 1102 | STAFFORD 11021202 | Equipment | 2022-07-30 01:59 | 7/25 - 7/31 | 2022-07-30 12:27 | 628 | FTS | 8294 | 53 | 0 | 0 | 1 | 0 | 0 | 0 | 156.4906
22-0091577 | Calaveras | FROGTOWN 1701 | FROGTOWN 170113412 | Unknown | 2022-07-30 03:20 | 7/25 - 7/31 | 2022-07-30 05:24 | 124 | FTS | 156858 | 1827 | 113 | 88 | 27 | 6 | 0 | 1 | 85.8555
22-0091592 | Nevada | NARROWS 2102 | NARROWS 21022220 | Vegetation | 2022-07-30 06:42 | 7/25 - 7/31 | 2022-07-30 09:45 | 183 | FTS | 83204 | 890 | 56 | 33 | 20 | 7 | 0 | 11 | 93.4876
22-0091622 | Tuolumne | CURTIS 1704 | CURTIS 17046060 | Unknown | 2022-07-30 08:47 | 7/25 - 7/31 | 2022-07-30 13:01 | 254 | FTS | 322148 | 1559 | 175 | 124 | 16 | 0 | 0 | 2 | 206.6376
22-0091625 | Placer | LINCOLN 1104 | LINCOLN 11042070 | 3rd Party | 2022-07-30 09:12 | 7/25 - 7/31 | 2022-07-30 10:36 | 84 | FTS | 22417 | 344 | 27 | 20 | 2 | 0 | 0 | 5 | 65.1657
22-0091645 | Yuba | PIKE CITY 1101 | PIKE CITY 11011720 | Company Initiated | 2022-07-30 11:05 | 7/25 - 7/31 | 2022-07-30 11:27 | 22 | FTS | 154 | 7 | 1 | 1 | 0 | 0 | 0 | 0 | 22
22-0091658 | Sierra | ALLEGHANY 1101 | ALLEGHANY 1101978 | Company Initiated | 2022-07-30 11:48 | 7/25 - 7/31 | 2022-07-30 12:07 | 19 | FTS | 3667 | 193 | 4 | 3 | 3 | 0 | 0 | 0 | 19
22-0091662 | Amador | ELECTRA 1101 | ELECTRA 11017104 | Unknown | 2022-07-30 11:48 | 7/25 - 7/31 | 2022-07-30 13:42 | 114 | FTS | 71022 | 623 | 63 | 41 | 7 | 0 | 0 | 1 | 114
22-0091670 | Placer | LINCOLN 1104 | LINCOLN 11042070 | 3rd Party | 2022-07-30 12:21 | 7/25 - 7/31 | 2022-07-30 13:43 | 82 | FTS | 28208 | 344 | 27 | 20 | 2 | 0 | 0 | 5 | 82
22-0091676 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113A70 | 3rd Party | 2022-07-30 13:09 | 7/25 - 7/31 | 2022-07-30 17:56 | 287 | FTS | 803287 | 3125 | 177 | 127 | 50 | 2 | 1 | 20 | 257.0518
22-0091695 | Shasta | WHITMORE 1101 | WHITMORE 1101903576 | Unknown | 2022-07-30 13:14 | 7/25 - 7/31 | 2022-07-30 18:49 | 335 | FTS | 32160 | 96 | 9 | 7 | 1 | 0 | 0 | 1 | 335
22-0091678 | Contra Costa | TASSAJARA 2108 | TASSAJARA 2108D520R | Equipment | 2022-07-30 13:17 | 7/25 - 7/31 | 2022-07-30 17:21 | 244 | FTS | 602375 | 4538 | 224 | 149 | 84 | 18 | 0 | 0 | 132.7402
22-0091699 | Monterey | RESERVATION ROAD 1101 | RESERVATION ROAD 1101383718 | Animal | 2022-07-30 14:57 | 7/25 - 7/31 | 2022-07-30 17:41 | 164 | FTS | 116276 | 709 | 51 | 32 | 18 | 2 | 0 | 0 | 164
22-0091710 | Plumas | GANSNER 1101 | GANSNER 11012424 | Equipment | 2022-07-30 15:52 | 7/25 - 7/31 | 2022-07-30 20:18 | 266 | FTS | 54796 | 206 | 11 | 8 | 4 | 0 | 0 | 2 | 266
22-0091742 | Plumas | BIG MEADOWS 2101 | BIG MEADOWS 21012476 | Unknown | 2022-07-30 18:09 | 7/25 - 7/31 | 2022-07-30 21:20 | 191 | FTS | 265681 | 1391 | 42 | 31 | 15 | 0 | 0 | 0 | 191
22-0091739 | Fresno | TIVY VALLEY 1107 | TIVY VALLEY 1107822606 | Unknown | 2022-07-30 20:01 | 7/25 - 7/31 | 2022-07-31 08:16 | 735 | FTS | 142030 | 836 | 64 | 46 | 13 | 0 | 0 | 0 | 169.8923
22-0091768 | Contra Costa | RESEARCH 2102 | RESEARCH 2102446423 | Unknown | 2022-07-30 21:55 | 7/25 - 7/31 | 2022-07-31 09:34 | 699 | FTS | 49629 | 71 | 2 | 1 | 2 | 0 | 0 | 0 | 699
22-0091761 | Calaveras | CALAVERAS CEMENT 1101 | CALAVERAS CEMENT 110111188 | Animal | 2022-07-31 00:52 | 7/25 - 7/31 | 2022-07-31 04:10 | 198 | FTS | 151668 | 766 | 55 | 37 | 18 | 1 | 0 | 0 | 198
22-0091775 | Placer | HALSEY 1102 | HALSEY 110239104 | Unknown | 2022-07-31 06:11 | 7/25 - 7/31 | 2022-07-31 11:23 | 312 | FTS | 77207 | 899 | 72 | 48 | 20 | 7 | 0 | 11 | 85.881
22-0091817 | El Dorado | SHINGLE SPRINGS 2109 | SHINGLE SPRINGS 210911092 | Animal | 2022-07-31 12:38 | 7/25 - 7/31 | 2022-07-31 15:15 | 157 | FTS | 85575 | 915 | 47 | 36 | 10 | 1 | 0 | 24 | 93.5246
22-0091820 | Tuolumne | PEORIA 1701 | PEORIA 170176030 | Unknown | 2022-07-31 13:27 | 7/25 - 7/31 | 2022-07-31 16:16 | 169 | FTS | 32617 | 193 | 8 | 7 | 7 | 2 | 0 | 0 | 169
22-0091830 | Mariposa | BEAR VALLEY 2105 | BEAR VALLEY 210521160 | Unknown | 2022-07-31 17:32 | 7/25 - 7/31 | 2022-08-01 09:20 | 948 | FTS | 169057 | 230 | 14 | 10 | 1 | 0 | 0 | 0 | 735.0304
22-0091840 | Monterey | SOLEDAD 2105 | SOLEDAD 21053720 | Unknown | 2022-07-31 18:54 | 7/25 - 7/31 | 2022-07-31 21:51 | 177 | FTS | 14868 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 177
22-0091849 | El Dorado | DIAMOND SPRINGS 1105 | DIAMOND SPRINGS 11052102 | 3rd Party | 2022-07-31 21:23 | 7/25 - 7/31 | 2022-08-01 09:52 | 749 | FTS | 268666 | 1092 | 98 | 51 | 24 | 7 | 0 | 2 | 246.0311

## July 2022 070122_073122
Outages | County | Circuit | CPZ | Cause | FNL | Week | End Date | Restoration Time (min) | EPSS Outage Type | Customer Minutes | CESO | Medical_Baseline | Life_Support | Critical_Customer | Schools | Hospitals | Well_Water_Dependent | CAIDI
22-0080875 | El Dorado | APPLE HILL 2102 | APPLE HILL 21028372 | Unknown | 2022-07-01 01:58 | 6/27 - 7/3 | 2022-07-01 11:32 | 574 | FTS | 1414585 | 2674 | 221 | 160 | 39 | 8 | 0 | 16 | 529.0146
22-0081164 | Butte | WYANDOTTE 1110 | WYANDOTTE 1110747922 | Animal | 2022-07-01 13:51 | 6/27 - 7/3 | 2022-07-01 15:27 | 96 | FTS | 149496 | 1563 | 216 | 162 | 25 | 0 | 0 | 1 | 95.6468
22-0081236 | Fresno | AUBERRY 1102 | AUBERRY 1102R2850 | Environmental/External | 2022-07-01 15:24 | 6/27 - 7/3 | 2022-07-02 05:27 | 843 | FTS | 69468 | 224 | 28 | 18 | 7 | 4 | 0 | 1 | 310.125
22-0081260 | Santa Cruz | ROB ROY 2104 | ROB ROY 210412596 | Animal | 2022-07-01 16:35 | 6/27 - 7/3 | 2022-07-01 19:35 | 180 | FTS | 73800 | 410 | 37 | 32 | 4 | 0 | 0 | 0 | 180
22-0081293 | Santa Cruz | BEN LOMOND 0401 | BEN LOMOND 0401944178 | Vegetation | 2022-07-01 20:49 | 6/27 - 7/3 | 2022-07-02 11:59 | 910 | FTS | 115911 | 759 | 70 | 52 | 15 | 3 | 0 | 1 | 152.7154
22-0081295 | Amador | CLAY 1103 | CLAY 11037142 | Unknown | 2022-07-01 20:53 | 6/27 - 7/3 | 2022-07-02 08:15 | 682 | FTS | 34248 | 81 | 0 | 0 | 5 | 0 | 0 | 0 | 422.8148
22-0081323 | Amador | PINE GROVE 1102 | PINE GROVE 110245292 | Unknown | 2022-07-02 00:41 | 6/27 - 7/3 | 2022-07-02 03:45 | 184 | FTS | 90528 | 492 | 42 | 27 | 11 | 0 | 0 | 0 | 184
22-0081333 | El Dorado | SHINGLE SPRINGS 2108 | SHINGLE SPRINGS 210851474 | Unknown | 2022-07-02 02:11 | 6/27 - 7/3 | 2022-07-02 08:12 | 361 | FTS | 270389 | 749 | 53 | 33 | 10 | 2 | 0 | 0 | 361
22-0081331 | Contra Costa | CLAYTON 2215 | CLAYTON 2215W531R | Unknown | 2022-07-02 03:06 | 6/27 - 7/3 | 2022-07-03 10:47 | 1901 | FTS | 283637 | 869 | 69 | 41 | 14 | 1 | 0 | 0 | 326.3947
22-0081329 | Lassen | MC ARTHUR 1101 | MC ARTHUR 11011546 | Unknown | 2022-07-02 03:15 | 6/27 - 7/3 | 2022-07-02 09:57 | 402 | FTS | 43818 | 109 | 5 | 4 | 2 | 0 | 0 | 0 | 402
22-0081344 | Santa Cruz | CAMP EVERS 2106 | CAMP EVERS 210611044 | Unknown | 2022-07-02 07:51 | 6/27 - 7/3 | 2022-07-02 12:59 | 308 | FTS | 624423 | 2487 | 195 | 145 | 45 | 4 | 0 | 5 | 251.0748
22-0081358 | El Dorado | DIAMOND SPRINGS 1103 | DIAMOND SPRINGS 11039432 | Unknown | 2022-07-02 08:48 | 6/27 - 7/3 | 2022-07-02 13:10 | 262 | FTS | 145410 | 555 | 59 | 41 | 8 | 0 | 0 | 2 | 262
22-0081406 | El Dorado | MOUNTAIN QUARRIES 2101 | MOUNTAIN QUARRIES 21012422 | Vegetation | 2022-07-02 12:37 | 6/27 - 7/3 | 2022-07-02 15:12 | 155 | FTS | 86679 | 612 | 39 | 28 | 9 | 1 | 0 | 1 | 141.6324
22-0081434 | Tuolumne | STANISLAUS 1702 | STANISLAUS 17021702/2 | Equipment | 2022-07-02 17:36 | 6/27 - 7/3 | 2022-07-03 13:46 | 1210 | FTS | 4964930 | 4971 | 200 | 156 | 52 | 3 | 2 | 0 | 998.7789
22-0081437 | Placer | PENRYN 1103 | PENRYN 1103660 | Vegetation | 2022-07-02 18:20 | 6/27 - 7/3 | 2022-07-03 05:34 | 674 | FTS | 35306 | 451 | 28 | 15 | 3 | 0 | 0 | 4 | 78.2838
22-0081482 | Butte | WYANDOTTE 1102 | WYANDOTTE 110213044 | Unknown | 2022-07-03 03:10 | 6/27 - 7/3 | 2022-07-03 08:32 | 322 | FTS | 10948 | 34 | 2 | 2 | 0 | 0 | 0 | 1 | 322
22-0081484 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113641367 | Animal | 2022-07-03 06:19 | 6/27 - 7/3 | 2022-07-03 09:28 | 189 | FTS | 56511 | 299 | 15 | 10 | 3 | 0 | 0 | 4 | 189
22-0081486 | Monterey | LAURELES 1111 | LAURELES 11112028 | Unknown | 2022-07-03 07:06 | 6/27 - 7/3 | 2022-07-03 10:15 | 189 | FTS | 90387 | 487 | 31 | 22 | 7 | 0 | 0 | 0 | 185.5996
22-0081488 | Nevada | BRUNSWICK 1104 | BRUNSWICK 1104327226 | Equipment | 2022-07-03 08:00 | 6/27 - 7/3 | 2022-07-03 08:53 | 53 | FTS | 901 | 17 | 2 | 2 | 0 | 0 | 0 | 0 | 53
22-0081489 | Santa Cruz | GREEN VALLEY 2101 | GREEN VALLEY 210136820 | Unknown | 2022-07-03 08:03 | 6/27 - 7/3 | 2022-07-03 14:06 | 363 | FTS | 300872 | 1992 | 134 | 111 | 31 | 14 | 0 | 5 | 151.0402
22-0081496 | Mendocino | HOPLAND 1101 | HOPLAND 1101768 | Unknown | 2022-07-03 09:30 | 6/27 - 7/3 | 2022-07-03 12:41 | 191 | FTS | 18909 | 99 | 3 | 2 | 1 | 0 | 0 | 0 | 191
22-0081493 | Placer | BELL 1108 | BELL 110880680 | Animal | 2022-07-03 09:34 | 6/27 - 7/3 | 2022-07-03 11:24 | 110 | FTS | 16060 | 146 | 14 | 9 | 1 | 0 | 0 | 0 | 110
22-0081509 | San Luis Obispo | ATASCADERO 1102 | ATASCADERO 1102A28 | Unknown | 2022-07-03 11:40 | 6/27 - 7/3 | 2022-07-03 13:52 | 132 | FTS | 230080 | 1795 | 65 | 35 | 9 | 2 | 0 | 0 | 128.1783
22-0081517 | El Dorado | DIAMOND SPRINGS 1103 | DIAMOND SPRINGS 11039432 | Unknown | 2022-07-03 12:11 | 6/27 - 7/3 | 2022-07-03 13:48 | 97 | FTS | 53835 | 555 | 59 | 41 | 8 | 0 | 0 | 2 | 97
22-0081531 | Sonoma | MIRABEL 1101 | MIRABEL 1101201156 | Animal | 2022-07-03 15:35 | 6/27 - 7/3 | 2022-07-03 16:32 | 57 | FTS | 4503 | 79 | 5 | 4 | 1 | 0 | 0 | 0 | 57
22-0081548 | Contra Costa | TASSAJARA 2113 | TASSAJARA 2113MR276 | Unknown | 2022-07-03 18:51 | 6/27 - 7/3 | 2022-07-03 20:21 | 90 | FTS | 40410 | 449 | 30 | 24 | 10 | 0 | 0 | 1 | 90
22-0081551 | El Dorado | CLARKSVILLE 2104 | CLARKSVILLE 210419772 | 3rd Party | 2022-07-03 20:50 | 6/27 - 7/3 | 2022-07-04 12:59 | 969 | FTS | 73168 | 244 | 22 | 15 | 3 | 0 | 0 | 8 | 299.8689
22-0081556 | Santa Barbara | PURISIMA 1101 | PURISIMA 11011101/2 | 3rd Party | 2022-07-03 21:26 | 6/27 - 7/3 | 2022-07-04 02:18 | 292 | FTS | 285444 | 2403 | 82 | 61 | 39 | 2 | 0 | 0 | 118.7865
22-0081597 | San Luis Obispo | TEMPLETON 2112 | TEMPLETON 2112R28 | Unknown | 2022-07-04 08:36 | 7/4 - 7/10 | 2022-07-04 09:42 | 66 | FTS | 21780 | 330 | 8 | 6 | 9 | 0 | 0 | 0 | 66
22-0081601 | Alameda | VINEYARD 2108 | VINEYARD 2108MR172 | 3rd Party | 2022-07-04 09:15 | 7/4 - 7/10 | 2022-07-05 02:03 | 1008 | FTS | 375136 | 3026 | 173 | 116 | 38 | 2 | 0 | 0 | 123.9709
22-0081602 | Contra Costa | SOBRANTE 1102 | SOBRANTE 1102690098 | Animal | 2022-07-04 09:17 | 7/4 - 7/10 | 2022-07-04 10:15 | 58 | FTS | 33872 | 584 | 37 | 28 | 13 | 2 | 0 | 0 | 58
22-0081603 | Nevada | HIGGINS 1109 | HIGGINS 1109594 | Animal | 2022-07-04 09:19 | 7/4 - 7/10 | 2022-07-04 10:57 | 98 | FTS | 49686 | 507 | 51 | 29 | 4 | 0 | 0 | 3 | 98
22-0081605 | Calaveras | FROGTOWN 1702 | FROGTOWN 170275252 | Unknown | 2022-07-04 09:35 | 7/4 - 7/10 | 2022-07-04 13:31 | 236 | FTS | 185292 | 822 | 38 | 25 | 29 | 2 | 0 | 2 | 225.4161
22-0081607 | Sonoma | MIRABEL 1101 | MIRABEL 1101298 | Unknown | 2022-07-04 09:41 | 7/4 - 7/10 | 2022-07-04 17:40 | 479 | FTS | 116295 | 385 | 16 | 13 | 2 | 0 | 0 | 0 | 302.0649
22-0081609 | Amador | CLAY 1102 | CLAY 11021102/2 | 3rd Party | 2022-07-04 09:51 | 7/4 - 7/10 | 2022-07-04 11:22 | 91 | FTS | 273 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 91
22-0081610 | Lassen | MC ARTHUR 1101 | MC ARTHUR 11011544 | Animal | 2022-07-04 09:56 | 7/4 - 7/10 | 2022-07-04 13:10 | 194 | FTS | 70196 | 367 | 15 | 12 | 20 | 3 | 0 | 0 | 191.2698
22-0081617 | Solano | VACAVILLE 1104 | VACAVILLE 11041104/2 | Animal | 2022-07-04 11:01 | 7/4 - 7/10 | 2022-07-04 13:55 | 174 | FTS | 274347 | 2092 | 139 | 92 | 34 | 2 | 0 | 1 | 131.141
22-0081655 | Marin | STAFFORD 1102 | STAFFORD 11021258 | Unknown | 2022-07-04 16:07 | 7/4 - 7/10 | 2022-07-04 17:12 | 65 | FTS | 77610 | 1194 | 70 | 48 | 6 | 3 | 0 | 0 | 65
22-0081663 | San Luis Obispo | SAN LUIS OBISPO 1103 | SAN LUIS OBISPO 110342344 | Unknown | 2022-07-04 17:09 | 7/4 - 7/10 | 2022-07-04 18:54 | 105 | FTS | 34335 | 327 | 12 | 9 | 3 | 0 | 0 | 2 | 105
22-0081672 | El Dorado | CLARKSVILLE 2104 | CLARKSVILLE 210419772 | Unknown | 2022-07-04 21:08 | 7/4 - 7/10 | 2022-07-05 08:40 | 692 | FTS | 168848 | 244 | 22 | 15 | 3 | 0 | 0 | 8 | 692
22-0081674 | Mendocino | HOPLAND 1101 | HOPLAND 1101960 | Vegetation | 2022-07-04 21:18 | 7/4 - 7/10 | 2022-07-05 08:49 | 691 | FTS | 37314 | 54 | 1 | 1 | 1 | 0 | 0 | 0 | 691
22-0081678 | Madera | OAKHURST 1103 | OAKHURST 110310140 | Equipment | 2022-07-04 21:51 | 7/4 - 7/10 | 2022-07-05 13:00 | 909 | FTS | 417894 | 914 | 60 | 49 | 24 | 0 | 0 | 1 | 457.2144
22-0081682 | San Luis Obispo | FOOTHILL 1102 | FOOTHILL 110299432 | Unknown | 2022-07-04 22:28 | 7/4 - 7/10 | 2022-07-05 01:09 | 161 | FTS | 324711 | 2259 | 52 | 38 | 23 | 3 | 0 | 0 | 143.741
22-0081690 | Butte | ORO FINO 1102 | ORO FINO 110276008 | Equipment | 2022-07-05 02:16 | 7/4 - 7/10 | 2022-07-05 09:28 | 432 | FTS | 83904 | 377 | 35 | 22 | 4 | 0 | 0 | 0 | 222.557
22-0081697 | Santa Cruz | GREEN VALLEY 2101 | GREEN VALLEY 210112106 | Animal | 2022-07-05 05:39 | 7/4 - 7/10 | 2022-07-05 09:30 | 231 | FTS | 233772 | 1012 | 86 | 69 | 9 | 1 | 0 | 0 | 231
22-0081782 | Mendocino | CALPELLA 1101 | CALPELLA 1101753000 | Unknown | 2022-07-05 09:56 | 7/4 - 7/10 | 2022-07-05 11:42 | 106 | FTS | 32754 | 309 | 15 | 13 | 11 | 2 | 0 | 0 | 106
22-0081805 | San Luis Obispo | ATASCADERO 1101 | ATASCADERO 1101A50 | Unknown | 2022-07-05 10:43 | 7/4 - 7/10 | 2022-07-05 17:28 | 405 | FTS | 193828 | 1418 | 98 | 59 | 15 | 3 | 0 | 2 | 136.6911
22-0081815 | Santa Barbara | PUEBLO 1105 | PUEBLO 1105637242 | Animal | 2022-07-05 10:48 | 7/4 - 7/10 | 2022-07-05 14:07 | 199 | FTS | 30248 | 152 | 2 | 2 | 1 | 0 | 0 | 0 | 199
22-0081828 | Santa Cruz | ROB ROY 2104 | ROB ROY 210410960 | Unknown | 2022-07-05 11:14 | 7/4 - 7/10 | 2022-07-05 13:21 | 127 | FTS | 225767 | 2393 | 166 | 136 | 34 | 6 | 0 | 2 | 94.3448
22-0081890 | Placer | PENRYN 1107 | PENRYN 11072708 | 3rd Party | 2022-07-05 12:57 | 7/4 - 7/10 | 2022-07-06 01:33 | 756 | FTS | 159842 | 378 | 36 | 25 | 6 | 0 | 0 | 1 | 422.8624
22-0081891 | Lake | KONOCTI 1102 | KONOCTI 110264664 | Vegetation | 2022-07-05 12:58 | 7/4 - 7/10 | 2022-07-05 17:37 | 279 | FTS | 74673 | 507 | 38 | 26 | 3 | 0 | 0 | 1 | 147.284
22-0081938 | Lake | LUCERNE 1103 | LUCERNE 11031103/2 | Unknown | 2022-07-05 14:00 | 7/4 - 7/10 | 2022-07-05 15:25 | 85 | FTS | 191590 | 2254 | 230 | 161 | 36 | 1 | 0 | 0 | 85
22-0081950 | Merced | GUSTINE 1102 | GUSTINE 11029100 | Animal | 2022-07-05 14:11 | 7/4 - 7/10 | 2022-07-05 16:29 | 138 | FTS | 90528 | 656 | 13 | 10 | 13 | 0 | 0 | 0 | 138
22-0082015 | San Luis Obispo | ATASCADERO 1102 | ATASCADERO 1102A28 | Unknown | 2022-07-05 15:41 | 7/4 - 7/10 | 2022-07-05 17:52 | 131 | FTS | 226913 | 1795 | 65 | 35 | 9 | 2 | 0 | 0 | 126.4139
22-0082037 | San Luis Obispo | TEMPLETON 2111 | TEMPLETON 2111A66 | Animal | 2022-07-05 16:34 | 7/4 - 7/10 | 2022-07-05 18:56 | 142 | FTS | 138876 | 978 | 71 | 37 | 20 | 4 | 0 | 1 | 142
22-0082081 | Shasta | PANORAMA 1102 | PANORAMA 11021342 | Unknown | 2022-07-05 21:16 | 7/4 - 7/10 | 2022-07-06 03:03 | 347 | FTS | 128994 | 544 | 51 | 34 | 3 | 0 | 0 | 0 | 237.1213
22-0082116 | Fresno | COALINGA NO 2 1105 | COALINGA NO 2 110541954 | Unknown | 2022-07-06 04:38 | 7/4 - 7/10 | 2022-07-06 11:12 | 394 | FTS | 53550 | 161 | 4 | 2 | 6 | 4 | 0 | 0 | 332.6087
22-0082139 | Shasta | JESSUP 1103 | JESSUP 11031540 | Animal | 2022-07-06 06:40 | 7/4 - 7/10 | 2022-07-06 16:47 | 607 | FTS | 69668 | 665 | 68 | 54 | 7 | 0 | 0 | 0 | 104.7639
22-0082268 | Santa Cruz | BIG BASIN 1101 | BIG BASIN 1101393582 | Unknown | 2022-07-06 11:04 | 7/4 - 7/10 | 2022-07-06 15:02 | 238 | FTS | 94640 | 635 | 40 | 30 | 10 | 0 | 0 | 1 | 149.0394
22-0082479 | Humboldt | FRUITLAND 1142 | FRUITLAND 11421142/2 | Vegetation | 2022-07-06 17:07 | 7/4 - 7/10 | 2022-07-06 19:28 | 141 | FTS | 92331 | 1023 | 23 | 17 | 23 | 5 | 0 | 0 | 90.2551
22-0082494 | Marin | WOODACRE 1102 | WOODACRE 1102137662 | Animal | 2022-07-06 19:21 | 7/4 - 7/10 | 2022-07-06 20:23 | 62 | FTS | 117180 | 1890 | 90 | 49 | 28 | 6 | 0 | 0 | 62
22-0082503 | Placer | PENRYN 1105 | PENRYN 110550548 | Animal | 2022-07-06 20:37 | 7/4 - 7/10 | 2022-07-06 22:38 | 121 | FTS | 29161 | 241 | 15 | 10 | 0 | 0 | 0 | 2 | 121
22-0082506 | Monterey | RESERVATION ROAD 1102 | RESERVATION ROAD 11023032 | Animal | 2022-07-06 21:17 | 7/4 - 7/10 | 2022-07-06 22:30 | 73 | FTS | 7957 | 109 | 9 | 8 | 1 | 0 | 0 | 0 | 73
22-0082507 | Nevada | COLUMBIA HILL 1101 | COLUMBIA HILL 110135424 | Equipment | 2022-07-06 21:18 | 7/4 - 7/10 | 2022-07-07 12:25 | 907 | FTS | 68230 | 241 | 15 | 12 | 9 | 3 | 0 | 0 | 283.112
22-0082525 | Monterey | LAURELES 1112 | LAURELES 111268454 | Unknown | 2022-07-06 23:42 | 7/4 - 7/10 | 2022-07-07 02:10 | 148 | FTS | 114996 | 777 | 29 | 17 | 27 | 1 | 0 | 1 | 148
22-0082532 | Sonoma | SONOMA 1105 | SONOMA 1105138 | Equipment | 2022-07-07 03:51 | 7/4 - 7/10 | 2022-07-08 00:09 | 1218 | FTS | 237899 | 699 | 30 | 20 | 9 | 0 | 0 | 6 | 340.3419
22-0082594 | Santa Clara | MC KEE 1107 | MC KEE 1107XR010 | Unknown | 2022-07-07 08:02 | 7/4 - 7/10 | 2022-07-07 09:46 | 104 | FTS | 43784 | 421 | 21 | 15 | 3 | 0 | 0 | 1 | 104
22-0082633 | Amador | TIGER CREEK 0201 | TIGER CREEK 0201201/2 | Company Initiated | 2022-07-07 08:50 | 7/4 - 7/10 | 2022-07-07 08:57 | 7 | FTS | 98 | 14 | 0 | 0 | 3 | 0 | 0 | 0 | 7
22-0082722 | Mariposa | MERCED FALLS 1102 | MERCED FALLS 110285002 | Equipment | 2022-07-07 10:45 | 7/4 - 7/10 | 2022-07-07 11:17 | 32 | FTS | 17664 | 552 | 44 | 29 | 15 | 2 | 0 | 0 | 32
22-0082766 | Santa Clara | MC KEE 1107 | MC KEE 1107XR010 | Animal | 2022-07-07 12:08 | 7/4 - 7/10 | 2022-07-07 13:46 | 98 | FTS | 41062 | 419 | 21 | 15 | 3 | 0 | 0 | 1 | 98
22-0082760 | Mendocino | PHILO 1101 | PHILO 11011101/2 | Vegetation | 2022-07-07 12:11 | 7/4 - 7/10 | 2022-07-07 17:49 | 338 | FTS | 446585 | 2215 | 60 | 38 | 50 | 13 | 0 | 2 | 201.6185
22-0082835 | Placer | BELL 1109 | BELL 1109724884 | Unknown | 2022-07-07 14:01 | 7/4 - 7/10 | 2022-07-07 17:33 | 212 | FTS | 63196 | 329 | 24 | 17 | 5 | 0 | 0 | 3 | 192.0851
22-0082867 | Tuolumne | CURTIS 1703 | CURTIS 17036064 | 3rd Party | 2022-07-07 14:38 | 7/4 - 7/10 | 2022-07-08 01:57 | 679 | FTS | 59188 | 379 | 37 | 31 | 4 | 0 | 0 | 0 | 156.1689
22-0082868 | Santa Cruz | POINT MORETTI 1101 | POINT MORETTI 110110722 | Vegetation | 2022-07-07 14:41 | 7/4 - 7/10 | 2022-07-08 05:50 | 909 | FTS | 32406 | 260 | 18 | 14 | 4 | 0 | 0 | 3 | 124.6385
22-0082932 | Lake | REDBUD 1102 | REDBUD 1102922 | Animal | 2022-07-07 17:27 | 7/4 - 7/10 | 2022-07-07 19:18 | 111 | FTS | 37407 | 337 | 26 | 16 | 4 | 0 | 1 | 0 | 111
22-0082926 | Santa Cruz | CAMP EVERS 2105 | CAMP EVERS 210595050 | Vegetation | 2022-07-07 17:31 | 7/4 - 7/10 | 2022-07-08 00:37 | 426 | FTS | 131760 | 1966 | 146 | 110 | 33 | 3 | 0 | 1 | 67.0193
22-0082952 | Lake | LUCERNE 1103 | LUCERNE 1103630 | Animal | 2022-07-07 19:40 | 7/4 - 7/10 | 2022-07-07 20:54 | 74 | FTS | 114256 | 1544 | 147 | 97 | 21 | 1 | 0 | 0 | 74
22-0082947 | San Luis Obispo | CAMBRIA 1102 | CAMBRIA 11021102/2 | 3rd Party | 2022-07-07 19:42 | 7/4 - 7/10 | 2022-07-08 08:18 | 756 | FTS | 248484 | 1254 | 42 | 29 | 19 | 0 | 0 | 3 | 198.1531
22-0082987 | Fresno | AUBERRY 1101 | AUBERRY 1101R2579 | Animal | 2022-07-08 04:28 | 7/4 - 7/10 | 2022-07-08 06:43 | 135 | FTS | 41445 | 307 | 24 | 17 | 5 | 0 | 0 | 0 | 135
22-0082988 | Tulare | STONE CORRAL 1108 | STONE CORRAL 1108255186 | Unknown | 2022-07-08 04:35 | 7/4 - 7/10 | 2022-07-08 08:44 | 249 | FTS | 13695 | 55 | 2 | 1 | 0 | 0 | 0 | 0 | 249
22-0082991 | Solano | JAMESON 1105 | JAMESON 1105466348 | Animal | 2022-07-08 05:26 | 7/4 - 7/10 | 2022-07-08 08:26 | 180 | FTS | 46236 | 353 | 12 | 6 | 8 | 2 | 0 | 2 | 130.9802
22-0083188 | Shasta | PIT NO 1 1101 | PIT NO 1 11011101/2 | Unknown | 2022-07-08 10:33 | 7/4 - 7/10 | 2022-07-08 16:51 | 378 | FTS | 302836 | 999 | 56 | 40 | 32 | 3 | 10 | 0 | 303.1391
22-0083366 | Marin | NOVATO 1104 | NOVATO 110455398 | Unknown | 2022-07-08 14:51 | 7/4 - 7/10 | 2022-07-08 17:30 | 159 | FTS | 18377 | 161 | 1 | 0 | 16 | 0 | 0 | 0 | 114.1429
22-0083379 | Sonoma | CLOVERDALE 1101 | CLOVERDALE 1101474708 | Animal | 2022-07-08 15:12 | 7/4 - 7/10 | 2022-07-08 16:28 | 76 | FTS | 7543 | 103 | 12 | 7 | 5 | 0 | 0 | 0 | 73.233
22-0083431 | Lake | KONOCTI 1102 | KONOCTI 1102714370 | Unknown | 2022-07-08 18:25 | 7/4 - 7/10 | 2022-07-08 19:49 | 84 | FTS | 9744 | 116 | 12 | 11 | 1 | 0 | 0 | 0 | 84
22-0083441 | Nevada | NARROWS 2105 | NARROWS 21052426 | Animal | 2022-07-08 19:19 | 7/4 - 7/10 | 2022-07-08 20:40 | 81 | FTS | 166201 | 2105 | 179 | 103 | 28 | 4 | 0 | 19 | 78.9553
22-0083458 | Lake | UPPER LAKE 1101 | UPPER LAKE 1101660 | Unknown | 2022-07-08 20:09 | 7/4 - 7/10 | 2022-07-09 09:08 | 779 | FTS | 376838 | 484 | 37 | 21 | 2 | 0 | 0 | 0 | 778.5909
22-0083461 | Tuolumne | PEORIA 1701 | PEORIA 17013186 | Unknown | 2022-07-08 21:38 | 7/4 - 7/10 | 2022-07-09 01:40 | 242 | FTS | 243334 | 1259 | 74 | 57 | 14 | 0 | 0 | 0 | 193.2756
22-0083460 | San Luis Obispo | OCEANO 1104 | OCEANO 11041104/2 | 3rd Party | 2022-07-08 21:38 | 7/4 - 7/10 | 2022-07-08 22:57 | 79 | FTS | 357290 | 5414 | 219 | 176 | 62 | 18 | 0 | 32 | 65.9937
22-0083469 | Monterey | RESERVATION ROAD 1102 | RESERVATION ROAD 11023032 | Unknown | 2022-07-09 00:48 | 7/4 - 7/10 | 2022-07-09 03:06 | 138 | FTS | 15042 | 109 | 9 | 8 | 1 | 0 | 0 | 0 | 138
22-0083480 | Nevada | BRUNSWICK 1107 | BRUNSWICK 11071107/2 | Animal | 2022-07-09 06:24 | 7/4 - 7/10 | 2022-07-09 08:36 | 132 | FTS | 566873 | 5896 | 376 | 250 | 98 | 17 | 4 | 5 | 96.1454
22-0083486 | Nevada | BRUNSWICK 1105 | BRUNSWICK 11052140 | Unknown | 2022-07-09 07:14 | 7/4 - 7/10 | 2022-07-09 12:09 | 295 | FTS | 176115 | 597 | 32 | 24 | 5 | 0 | 0 | 7 | 295
22-0083484 | Santa Barbara | BUELLTON 1101 | BUELLTON 1101Y06 | Animal | 2022-07-09 07:16 | 7/4 - 7/10 | 2022-07-09 08:44 | 88 | FTS | 30536 | 347 | 5 | 5 | 10 | 0 | 0 | 0 | 88
22-0083502 | Amador | PINE GROVE 1102 | PINE GROVE 11023168 | Unknown | 2022-07-09 09:55 | 7/4 - 7/10 | 2022-07-09 15:29 | 334 | FTS | 239035 | 1070 | 88 | 57 | 14 | 0 | 0 | 6 | 223.3972
22-0083513 | Yuba | WHEATLAND 1105 | WHEATLAND 1105248490 | Unknown | 2022-07-09 11:42 | 7/4 - 7/10 | 2022-07-09 14:25 | 163 | FTS | 34556 | 212 | 12 | 6 | 3 | 0 | 0 | 4 | 163
22-0083521 | Santa Clara | HICKS 2101 | HICKS 2101XR162 | Unknown | 2022-07-09 12:40 | 7/4 - 7/10 | 2022-07-09 16:23 | 223 | FTS | 343492 | 1550 | 94 | 68 | 23 | 3 | 0 | 0 | 221.6077
22-0083573 | Monterey | SOLEDAD 2102 | SOLEDAD 21027008 | 3rd Party | 2022-07-09 18:14 | 7/4 - 7/10 | 2022-07-09 19:36 | 82 | FTS | 7790 | 95 | 0 | 0 | 5 | 0 | 0 | 0 | 82
22-0083577 | Lake | REDBUD 1102 | REDBUD 1102432 | Unknown | 2022-07-09 18:47 | 7/4 - 7/10 | 2022-07-09 22:21 | 214 | FTS | 437630 | 2045 | 168 | 110 | 22 | 1 | 0 | 0 | 214
22-0083582 | Contra Costa | LAKEWOOD 2227 | LAKEWOOD 2227W503R | Unknown | 2022-07-09 20:03 | 7/4 - 7/10 | 2022-07-09 22:17 | 134 | FTS | 233345 | 1927 | 114 | 81 | 21 | 1 | 0 | 0 | 121.0924
22-0083583 | Lake | CLEAR LAKE 1101 | CLEAR LAKE 11011302 | Animal | 2022-07-09 20:18 | 7/4 - 7/10 | 2022-07-10 08:22 | 724 | FTS | 379376 | 524 | 37 | 21 | 8 | 0 | 1 | 0 | 724
22-0083584 | Calaveras | NORTH BRANCH 1101 | NORTH BRANCH 110111158 | Unknown | 2022-07-09 20:26 | 7/4 - 7/10 | 2022-07-10 00:24 | 238 | FTS | 96628 | 406 | 34 | 21 | 12 | 0 | 0 | 3 | 238
22-0083601 | Lake | KONOCTI 1102 | KONOCTI 1102532 | Vegetation | 2022-07-09 22:27 | 7/4 - 7/10 | 2022-07-10 10:11 | 704 | FTS | 65885 | 373 | 21 | 13 | 8 | 0 | 0 | 0 | 176.6354
22-0083607 | Lassen | MC ARTHUR 1101 | MC ARTHUR 11011544 | Unknown | 2022-07-09 23:51 | 7/4 - 7/10 | 2022-07-10 15:00 | 909 | FTS | 332601 | 367 | 15 | 12 | 20 | 3 | 0 | 0 | 906.2698
22-0083609 | El Dorado | SHINGLE SPRINGS 2105 | SHINGLE SPRINGS 210551738 | Equipment | 2022-07-10 00:21 | 7/4 - 7/10 | 2022-07-10 15:31 | 910 | FTS | 331647 | 2207 | 161 | 113 | 23 | 0 | 0 | 6 | 150.2705
22-0083621 | Shasta | BURNEY 1101 | BURNEY 11012402 | Unknown | 2022-07-10 06:56 | 7/4 - 7/10 | 2022-07-10 10:51 | 235 | FTS | 147133 | 631 | 54 | 39 | 9 | 1 | 0 | 0 | 233.1743
22-0083625 | Marin | STAFFORD 1102 | STAFFORD 1102524 | Animal | 2022-07-10 07:52 | 7/4 - 7/10 | 2022-07-10 08:51 | 59 | FTS | 92866 | 1574 | 94 | 54 | 13 | 1 | 0 | 0 | 59
22-0083626 | Shasta | PIT NO 5 1101 | PIT NO 5 11011614 | Unknown | 2022-07-10 08:27 | 7/4 - 7/10 | 2022-07-10 15:50 | 443 | FTS | 443 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 443
22-0083635 | Santa Cruz | BIG BASIN 1102 | BIG BASIN 110296986 | Animal | 2022-07-10 10:41 | 7/4 - 7/10 | 2022-07-10 14:50 | 249 | FTS | 164784 | 831 | 48 | 33 | 14 | 1 | 0 | 1 | 198.296
22-0083641 | Mendocino | UKIAH 1113 | UKIAH 11131113/2 | 3rd Party | 2022-07-10 11:17 | 7/4 - 7/10 | 2022-07-10 13:22 | 125 | FTS | 151125 | 1209 | 66 | 41 | 26 | 3 | 0 | 0 | 125
22-0083648 | Shasta | RISING RIVER 1101 | RISING RIVER 11011101/2 | Unknown | 2022-07-10 12:36 | 7/4 - 7/10 | 2022-07-10 14:37 | 121 | FTS | 86173 | 725 | 46 | 44 | 14 | 0 | 0 | 0 | 118.8593
22-0083650 | Shasta | VOLTA 1101 | VOLTA 11011568 | Unknown | 2022-07-10 13:02 | 7/4 - 7/10 | 2022-07-10 16:52 | 230 | FTS | 20930 | 91 | 5 | 3 | 1 | 0 | 0 | 0 | 230
22-0083661 | Humboldt | RIO DELL 1102 | RIO DELL 11028768 | Vegetation | 2022-07-10 15:14 | 7/4 - 7/10 | 2022-07-11 00:02 | 528 | FTS | 71470 | 307 | 12 | 9 | 3 | 1 | 0 | 0 | 232.8013
22-0083660 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 21012181 | 3rd Party | 2022-07-10 15:22 | 7/4 - 7/10 | 2022-07-10 19:06 | 224 | FTS | 11424 | 51 | 0 | 0 | 2 | 0 | 0 | 0 | 224
22-0083674 | Humboldt | HOOPA 1101 | HOOPA 110193038 | Animal | 2022-07-10 18:04 | 7/4 - 7/10 | 2022-07-10 19:44 | 100 | FTS | 10100 | 101 | 2 | 2 | 12 | 11 | 0 | 0 | 100
22-0083677 | Santa Cruz | CAMP EVERS 2103 | CAMP EVERS 21032103/2 | 3rd Party | 2022-07-10 18:39 | 7/4 - 7/10 | 2022-07-10 20:09 | 90 | FTS | 219870 | 3275 | 252 | 206 | 64 | 5 | 0 | 15 | 67.1359
22-0083680 | San Mateo | EMERALD LAKE 0401 | EMERALD LAKE 0401401/2 | Unknown | 2022-07-10 18:49 | 7/4 - 7/10 | 2022-07-11 10:30 | 941 | FTS | 289177 | 1137 | 69 | 54 | 23 | 1 | 0 | 1 | 254.3333
22-0083685 | Yuba | BROWNS VALLEY 1101 | BROWNS VALLEY 110136622 | Unknown | 2022-07-10 20:49 | 7/4 - 7/10 | 2022-07-11 09:18 | 749 | FTS | 11235 | 15 | 1 | 1 | 0 | 0 | 0 | 0 | 749
22-0083686 | Humboldt | RIO DELL 1102 | RIO DELL 11028852 | Vegetation | 2022-07-10 21:07 | 7/4 - 7/10 | 2022-07-11 16:16 | 1149 | FTS | 105708 | 92 | 3 | 2 | 10 | 0 | 1 | 0 | 1149
22-0083711 | El Dorado | SHINGLE SPRINGS 2109 | SHINGLE SPRINGS 210913322 | Animal | 2022-07-11 01:55 | 7/11 - 7/17 | 2022-07-11 06:35 | 280 | FTS | 688909 | 2524 | 210 | 138 | 32 | 2 | 0 | 38 | 272.9433
22-0083715 | Contra Costa | WILLOW PASS 1101 | WILLOW PASS 11011101/2 | 3rd Party | 2022-07-11 03:23 | 7/11 - 7/17 | 2022-07-11 05:24 | 121 | FTS | 142418 | 1601 | 117 | 77 | 20 | 0 | 0 | 0 | 88.9557
22-0083723 | Nevada | HIGGINS 1107 | HIGGINS 11071070 | Vegetation | 2022-07-11 06:43 | 7/11 - 7/17 | 2022-07-11 16:24 | 581 | FTS | 27706 | 239 | 21 | 13 | 9 | 0 | 0 | 7 | 115.9247
22-0083740 | Plumas | EAST QUINCY 1101 | EAST QUINCY 11012452 | Animal | 2022-07-11 07:45 | 7/11 - 7/17 | 2022-07-11 09:17 | 92 | FTS | 91816 | 998 | 54 | 36 | 7 | 0 | 0 | 0 | 92
22-0083852 | Tehama | CORNING 1101 | CORNING 110182846 | Unknown | 2022-07-11 10:55 | 7/11 - 7/17 | 2022-07-11 11:51 | 56 | FTS | 7448 | 133 | 11 | 8 | 4 | 2 | 0 | 0 | 56
22-0083987 | Shasta | PANORAMA 1102 | PANORAMA 11021526 | Animal | 2022-07-11 13:46 | 7/11 - 7/17 | 2022-07-11 16:06 | 140 | FTS | 14048 | 103 | 8 | 7 | 2 | 0 | 0 | 0 | 136.3883
22-0084103 | San Mateo | EMERALD LAKE 0401 | EMERALD LAKE 0401401/2 | Unknown | 2022-07-11 18:14 | 7/11 - 7/17 | 2022-07-11 20:55 | 161 | FTS | 178735 | 1137 | 69 | 54 | 23 | 1 | 0 | 1 | 157.1988
22-0084104 | Santa Clara | HICKS 2103 | HICKS 21032103/2 | Animal | 2022-07-11 18:35 | 7/11 - 7/17 | 2022-07-12 03:10 | 515 | C/OUT | 308764 | 3668 | 212 | 132 | 38 | 3 | 0 | 0 | 84.1778
22-0084105 | Santa Clara | HICKS 2101 | HICKS 21012101/2 | Unknown | 2022-07-11 18:37 | 7/11 - 7/17 | 2022-07-13 01:26 | 1849 | FTS | 1310576 | 4942 | 289 | 200 | 75 | 12 | 0 | 0 | 265.1914
22-0084109 | Humboldt | GARBERVILLE 1102 | GARBERVILLE 110256048 | Vegetation | 2022-07-11 18:37 | 7/11 - 7/17 | 2022-07-12 12:27 | 1070 | FTS | 349884 | 378 | 9 | 8 | 17 | 6 | 0 | 0 | 925.619
22-0084114 | Amador | OLETA 1101 | OLETA 11011208 | Unknown | 2022-07-11 18:52 | 7/11 - 7/17 | 2022-07-12 09:39 | 887 | FTS | 442339 | 500 | 31 | 18 | 10 | 1 | 0 | 1 | 884.678
22-0084125 | Calaveras | NORTH BRANCH 1101 | NORTH BRANCH 110111158 | Unknown | 2022-07-11 20:22 | 7/11 - 7/17 | 2022-07-11 23:54 | 212 | FTS | 86072 | 406 | 34 | 21 | 12 | 0 | 0 | 3 | 212
22-0084169 | Mendocino | CALPELLA 1101 | CALPELLA 1101542 | Vegetation | 2022-07-12 02:48 | 7/11 - 7/17 | 2022-07-12 10:39 | 471 | FTS | 184161 | 391 | 26 | 18 | 2 | 0 | 0 | 0 | 471
22-0084205 | Contra Costa | CLAYTON 2212 | CLAYTON 2212204416 | Vegetation | 2022-07-12 07:12 | 7/11 - 7/17 | 2022-07-12 16:48 | 576 | FTS | 34816 | 154 | 9 | 5 | 0 | 0 | 0 | 1 | 226.0779
22-0084250 | El Dorado | SHINGLE SPRINGS 2109 | SHINGLE SPRINGS 210913322 | Unknown | 2022-07-12 09:01 | 7/11 - 7/17 | 2022-07-12 13:02 | 241 | FTS | 155445 | 645 | 57 | 36 | 4 | 0 | 0 | 5 | 241
22-0084289 | Contra Costa | BRENTWOOD 2105 | BRENTWOOD 2105B504R | Unknown | 2022-07-12 10:31 | 7/11 - 7/17 | 2022-07-12 11:50 | 79 | FTS | 3379 | 67 | 1 | 1 | 12 | 0 | 0 | 0 | 50.4328
22-0084380 | Santa Cruz | BEN LOMOND 0401 | BEN LOMOND 040116010 | Unknown | 2022-07-12 12:41 | 7/11 - 7/17 | 2022-07-12 14:35 | 114 | FTS | 15960 | 140 | 8 | 8 | 6 | 1 | 0 | 0 | 114
22-0084526 | Santa Clara | LOYOLA 1102 | LOYOLA 1102917865 | Unknown | 2022-07-12 16:01 | 7/11 - 7/17 | 2022-07-12 19:55 | 234 | FTS | 9126 | 39 | 2 | 2 | 1 | 0 | 0 | 0 | 234
22-0084523 | Humboldt | HOOPA 1101 | HOOPA 110182542 | Unknown | 2022-07-12 17:08 | 7/11 - 7/17 | 2022-07-13 13:53 | 1245 | FTS | 97815 | 244 | 10 | 6 | 8 | 0 | 0 | 0 | 400.8811
22-0084541 | Shasta | OREGON TRAIL 1103 | OREGON TRAIL 110335002 | 3rd Party | 2022-07-12 20:08 | 7/11 - 7/17 | 2022-07-13 05:00 | 532 | FTS | 314633 | 1121 | 92 | 64 | 20 | 3 | 0 | 1 | 280.6717
22-0084551 | Solano | NORTH TOWER 2101 | NORTH TOWER 2101158556/2 | Unknown | 2022-07-12 22:00 | 7/11 - 7/17 | 2022-07-12 22:38 | 38 | FTS | 123728 | 3256 | 229 | 148 | 37 | 8 | 0 | 0 | 38
22-0084570 | Calaveras | CORRAL 1103 | CORRAL 110336680 | Unknown | 2022-07-13 01:29 | 7/11 - 7/17 | 2022-07-13 04:42 | 193 | FTS | 137416 | 712 | 80 | 49 | 11 | 0 | 0 | 0 | 193
22-0084572 | San Luis Obispo | CAYUCOS 1102 | CAYUCOS 1102613456 | Unknown | 2022-07-13 02:02 | 7/11 - 7/17 | 2022-07-13 10:54 | 532 | FTS | 55328 | 104 | 1 | 1 | 0 | 0 | 0 | 1 | 532
22-0084578 | Sonoma | MOLINO 1102 | MOLINO 1102104 | Unknown | 2022-07-13 03:33 | 7/11 - 7/17 | 2022-07-13 14:18 | 645 | FTS | 594777 | 1526 | 83 | 53 | 21 | 1 | 0 | 13 | 389.7621
22-0084585 | Contra Costa | BRENTWOOD 2105 | BRENTWOOD 210598606 | Animal | 2022-07-13 06:12 | 7/11 - 7/17 | 2022-07-13 12:04 | 352 | FTS | 32357 | 298 | 15 | 7 | 12 | 0 | 0 | 0 | 108.5805
22-0084640 | Santa Cruz | CAMP EVERS 2106 | CAMP EVERS 21062106/2 | Unknown | 2022-07-13 07:43 | 7/11 - 7/17 | 2022-07-13 12:58 | 315 | FTS | 1228448 | 5760 | 498 | 376 | 104 | 13 | 0 | 24 | 213.2722
22-0084645 | Marin | STAFFORD 1101 | STAFFORD 11011102/2 | Unknown | 2022-07-13 07:47 | 7/11 - 7/17 | 2022-07-13 09:04 | 77 | FTS | 160279 | 2541 | 156 | 119 | 19 | 4 | 0 | 0 | 63.0771
22-0080184 | Contra Costa | ALHAMBRA 1102 | ALHAMBRA 11021102/2 | Company Initiated | 2022-07-13 08:47 | 7/11 - 7/17 | 2022-07-13 09:02 | 15 | FTS | 46950 | 3130 | 146 | 100 | 47 | 10 | 4 | 0 | 15
22-0084769 | Mendocino | WILLITS 1104 | WILLITS 1104934 | 3rd Party | 2022-07-13 10:45 | 7/11 - 7/17 | 2022-07-13 13:49 | 184 | FTS | 61096 | 427 | 31 | 20 | 15 | 0 | 0 | 1 | 143.082
22-0084833 | El Dorado | APPLE HILL 2102 | APPLE HILL 2102186912 | Unknown | 2022-07-13 12:01 | 7/11 - 7/17 | 2022-07-13 15:07 | 186 | FTS | 217928 | 1224 | 110 | 85 | 17 | 3 | 0 | 4 | 178.0458
22-0085016 | Mendocino | WILLITS 1104 | WILLITS 110434008 | 3rd Party | 2022-07-13 15:50 | 7/11 - 7/17 | 2022-07-13 16:54 | 64 | FTS | 35728 | 571 | 38 | 31 | 19 | 0 | 0 | 0 | 62.5709
22-0085069 | Sierra | ALLEGHANY 1101 | ALLEGHANY 1101978 | Company Initiated | 2022-07-13 18:25 | 7/11 - 7/17 | 2022-07-13 18:51 | 26 | FTS | 4212 | 162 | 2 | 1 | 3 | 0 | 0 | 0 | 26
22-0085070 | Contra Costa | NORTH DUBLIN 2103 | NORTH DUBLIN 21032103/2 | Unknown | 2022-07-13 18:36 | 7/11 - 7/17 | 2022-07-14 11:01 | 985 | FTS | 657377 | 4847 | 164 | 114 | 51 | 6 | 0 | 0 | 135.6255
22-0085081 | Calaveras | NORTH BRANCH 1101 | NORTH BRANCH 110111158 | Unknown | 2022-07-13 20:10 | 7/11 - 7/17 | 2022-07-13 22:46 | 156 | FTS | 63336 | 406 | 34 | 21 | 12 | 0 | 0 | 3 | 156
22-0085084 | Trinity | WILLOW CREEK 1103 | WILLOW CREEK 11037514 | Vegetation | 2022-07-13 20:54 | 7/11 - 7/17 | 2022-07-14 10:51 | 837 | FTS | 1063827 | 1271 | 74 | 56 | 13 | 2 | 0 | 0 | 837
22-0085120 | Solano | JAMESON 1105 | JAMESON 1105466348 | Animal | 2022-07-14 05:29 | 7/11 - 7/17 | 2022-07-14 07:30 | 121 | FTS | 32207 | 353 | 12 | 6 | 8 | 2 | 0 | 2 | 91.238
22-0085339 | Tehama | VOLTA 1101 | VOLTA 11011516 | 3rd Party | 2022-07-14 11:36 | 7/11 - 7/17 | 2022-07-14 14:16 | 160 | FTS | 20800 | 130 | 11 | 9 | 17 | 2 | 0 | 0 | 160
22-0085406 | Santa Cruz | CAMP EVERS 2105 | CAMP EVERS 210511384 | Vegetation | 2022-07-14 13:02 | 7/11 - 7/17 | 2022-07-14 16:00 | 178 | FTS | 65326 | 367 | 15 | 14 | 3 | 1 | 0 | 0 | 178
22-0085618 | Solano | PEABODY 2106 | PEABODY 21062106/2 | Unknown | 2022-07-15 00:05 | 7/11 - 7/17 | 2022-07-15 02:59 | 174 | FTS | 247376 | 2976 | 273 | 209 | 19 | 2 | 0 | 0 | 83.1237
22-0085625 | Merced | MERCED FALLS 1102 | MERCED FALLS 1102482838 | Animal | 2022-07-15 05:04 | 7/11 - 7/17 | 2022-07-15 09:27 | 263 | FTS | 371619 | 1413 | 115 | 74 | 28 | 5 | 0 | 0 | 263
22-0085631 | Marin | STAFFORD 1102 | STAFFORD 11021202 | Unknown | 2022-07-15 05:53 | 7/11 - 7/17 | 2022-07-15 07:30 | 97 | FTS | 5141 | 53 | 0 | 0 | 1 | 0 | 0 | 0 | 97
22-0085632 | Placer | PLACER 1103 | PLACER 1103429574 | Animal | 2022-07-15 05:56 | 7/11 - 7/17 | 2022-07-15 07:49 | 113 | FTS | 52933 | 521 | 28 | 15 | 9 | 1 | 0 | 0 | 101.5988
22-0085672 | Placer | PENRYN 1105 | PENRYN 11051342 | Animal | 2022-07-15 07:34 | 7/11 - 7/17 | 2022-07-15 09:10 | 96 | FTS | 58080 | 605 | 36 | 22 | 9 | 0 | 0 | 11 | 96
22-0085685 | Calaveras | NORTH BRANCH 1101 | NORTH BRANCH 110111158 | Unknown | 2022-07-15 08:12 | 7/11 - 7/17 | 2022-07-15 13:17 | 305 | FTS | 77910 | 406 | 34 | 21 | 12 | 0 | 0 | 3 | 191.8966
22-0085720 | Sonoma | MIRABEL 1101 | MIRABEL 1101298 | Unknown | 2022-07-15 08:59 | 7/11 - 7/17 | 2022-07-15 10:47 | 108 | FTS | 18908 | 229 | 12 | 10 | 2 | 0 | 0 | 0 | 82.5677
22-0085767 | Contra Costa | MORAGA 1102 | MORAGA 11021106/2 | Unknown | 2022-07-15 10:08 | 7/11 - 7/17 | 2022-07-15 14:23 | 255 | C/OUT | 547090 | 2376 | 93 | 67 | 23 | 9 | 0 | 0 | 230.2567
22-0085848 | Lake | LUCERNE 1103 | LUCERNE 11034200 | Animal | 2022-07-15 12:03 | 7/11 - 7/17 | 2022-07-15 14:31 | 148 | FTS | 55605 | 378 | 54 | 41 | 11 | 0 | 0 | 0 | 147.1032
22-0085893 | Contra Costa | ROSSMOOR 1102 | ROSSMOOR 1102457174 | Unknown | 2022-07-15 12:56 | 7/11 - 7/17 | 2022-07-15 16:44 | 228 | FTS | 795524 | 3530 | 323 | 223 | 19 | 0 | 0 | 0 | 225.3609
22-0085896 | Lake | KONOCTI 1108 | KONOCTI 11081278 | Vegetation | 2022-07-15 13:11 | 7/11 - 7/17 | 2022-07-15 14:45 | 94 | FTS | 42018 | 447 | 34 | 25 | 7 | 0 | 0 | 0 | 94
22-0085962 | Lake | MIDDLETOWN 1101 | MIDDLETOWN 1101571926 | Unknown | 2022-07-15 13:14 | 7/11 - 7/17 | 2022-07-15 16:22 | 188 | FTS | 2820 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 188
22-0085984 | San Luis Obispo | TEMPLETON 2112 | TEMPLETON 2112R80 | 3rd Party | 2022-07-15 15:49 | 7/11 - 7/17 | 2022-07-16 00:37 | 528 | FTS | 204607 | 971 | 36 | 29 | 25 | 0 | 0 | 0 | 210.7178
22-0086009 | Tuolumne | CURTIS 1704 | CURTIS 17048140 | Unknown | 2022-07-15 17:23 | 7/11 - 7/17 | 2022-07-15 19:29 | 126 | FTS | 108612 | 862 | 81 | 54 | 13 | 0 | 0 | 1 | 126
22-0086019 | Fresno | TIVY VALLEY 1107 | TIVY VALLEY 1107869946 | Unknown | 2022-07-15 17:43 | 7/11 - 7/17 | 2022-07-15 19:57 | 134 | FTS | 38324 | 286 | 33 | 25 | 3 | 0 | 0 | 0 | 134
22-0086020 | Fresno | TIVY VALLEY 1107 | TIVY VALLEY 1107584840 | Unknown | 2022-07-15 17:43 | 7/11 - 7/17 | 2022-07-15 23:14 | 331 | FTS | 121762 | 520 | 49 | 30 | 3 | 0 | 0 | 0 | 234.1577
22-0086029 | El Dorado | DIAMOND SPRINGS 1103 | DIAMOND SPRINGS 11039432 | Unknown | 2022-07-15 19:29 | 7/11 - 7/17 | 2022-07-15 23:56 | 267 | FTS | 141061 | 555 | 59 | 41 | 8 | 0 | 0 | 2 | 254.164
22-0086031 | Mariposa | BEAR VALLEY 2101 | BEAR VALLEY 21014500 | Equipment | 2022-07-15 19:38 | 7/11 - 7/17 | 2022-07-15 20:20 | 42 | FTS | 22722 | 541 | 29 | 19 | 14 | 3 | 0 | 0 | 42
22-0086035 | Nevada | HIGGINS 1109 | HIGGINS 110950078 | Animal | 2022-07-15 20:14 | 7/11 - 7/17 | 2022-07-16 18:34 | 1340 | FTS | 70892 | 407 | 26 | 20 | 4 | 0 | 0 | 8 | 174.1818
22-0086039 | Shasta | OREGON TRAIL 1102 | OREGON TRAIL 11021382 | Unknown | 2022-07-15 21:00 | 7/11 - 7/17 | 2022-07-16 00:25 | 205 | FTS | 47681 | 245 | 24 | 21 | 1 | 0 | 0 | 0 | 194.6163
22-0086054 | Monterey | LAURELES 1111 | LAURELES 11112028 | Animal | 2022-07-15 22:14 | 7/11 - 7/17 | 2022-07-16 12:30 | 856 | FTS | 57984 | 487 | 31 | 22 | 7 | 0 | 0 | 0 | 119.0637
22-0086072 | Sonoma | FULTON 1102 | FULTON 11024522 | Vegetation | 2022-07-15 23:59 | 7/11 - 7/17 | 2022-07-16 10:42 | 643 | FTS | 137651 | 468 | 14 | 11 | 6 | 0 | 0 | 2 | 294.1261
22-0086082 | El Dorado | SHINGLE SPRINGS 2108 | SHINGLE SPRINGS 210851474 | Unknown | 2022-07-16 05:33 | 7/11 - 7/17 | 2022-07-16 07:28 | 115 | FTS | 86135 | 749 | 53 | 33 | 10 | 2 | 0 | 0 | 115
22-0086083 | San Benito | TRES PINOS 1111 | TRES PINOS 11114032 | Animal | 2022-07-16 05:50 | 7/11 - 7/17 | 2022-07-16 06:43 | 53 | FTS | 8660 | 168 | 6 | 6 | 4 | 3 | 0 | 0 | 51.5476
22-0086085 | Humboldt | HOOPA 1101 | HOOPA 110137202 | Vegetation | 2022-07-16 05:52 | 7/11 - 7/17 | 2022-07-16 22:45 | 1013 | FTS | 85438 | 114 | 0 | 0 | 8 | 1 | 0 | 0 | 749.4561
22-0086095 | Santa Cruz | CAMP EVERS 2106 | CAMP EVERS 210611044 | Equipment | 2022-07-16 07:01 | 7/11 - 7/17 | 2022-07-17 22:13 | 2352 | FTS | 602693 | 2488 | 195 | 145 | 45 | 4 | 0 | 5 | 242.24
22-0086099 | Placer | LINCOLN 1104 | LINCOLN 1104685276 | Animal | 2022-07-16 07:07 | 7/11 - 7/17 | 2022-07-16 10:50 | 223 | FTS | 60923 | 431 | 32 | 22 | 4 | 0 | 0 | 1 | 141.3527
22-0086109 | Santa Cruz | CAMP EVERS 2106 | CAMP EVERS 21065020 | Unknown | 2022-07-16 07:35 | 7/11 - 7/17 | 2022-07-16 12:13 | 278 | FTS | 161391 | 839 | 71 | 48 | 10 | 0 | 0 | 7 | 192.3611
22-0086141 | Tehama | RED BLUFF 1104 | RED BLUFF 11041302 | Unknown | 2022-07-16 10:13 | 7/11 - 7/17 | 2022-07-16 14:17 | 244 | FTS | 128828 | 896 | 79 | 47 | 18 | 1 | 0 | 1 | 143.7812
22-0086161 | El Dorado | DIAMOND SPRINGS 1106 | DIAMOND SPRINGS 110656026 | Unknown | 2022-07-16 13:14 | 7/11 - 7/17 | 2022-07-16 14:39 | 85 | FTS | 19805 | 233 | 21 | 13 | 2 | 0 | 0 | 1 | 85
22-0086169 | Placer | HORSESHOE 1104 | HORSESHOE 110450142 | Unknown | 2022-07-16 14:01 | 7/11 - 7/17 | 2022-07-16 22:17 | 496 | FTS | 32529 | 312 | 25 | 15 | 5 | 0 | 0 | 0 | 104.2596
22-0086175 | Mendocino | UKIAH 1114 | UKIAH 1114528 | Unknown | 2022-07-16 15:35 | 7/11 - 7/17 | 2022-07-16 17:32 | 117 | FTS | 15093 | 129 | 4 | 1 | 7 | 0 | 0 | 0 | 117
22-0086199 | Mariposa | BEAR VALLEY 2101 | BEAR VALLEY 21014500 | Equipment | 2022-07-16 19:02 | 7/11 - 7/17 | 2022-07-16 20:41 | 99 | FTS | 47067 | 541 | 29 | 19 | 14 | 3 | 0 | 0 | 87
22-0086204 | Shasta | CEDAR CREEK 1101 | CEDAR CREEK 11011608 | 3rd Party | 2022-07-16 20:31 | 7/11 - 7/17 | 2022-07-17 01:57 | 326 | FTS | 53732 | 200 | 18 | 13 | 2 | 0 | 0 | 0 | 268.66
22-0086233 | Sonoma | SONOMA 1105 | SONOMA 1105229588 | Unknown | 2022-07-17 00:54 | 7/11 - 7/17 | 2022-07-17 09:22 | 508 | FTS | 93472 | 184 | 6 | 6 | 0 | 0 | 0 | 5 | 508
22-0086234 | Santa Cruz | CAMP EVERS 2105 | CAMP EVERS 210574170 | Vegetation | 2022-07-17 02:24 | 7/11 - 7/17 | 2022-07-17 12:45 | 621 | FTS | 258975 | 1966 | 146 | 110 | 33 | 3 | 0 | 1 | 131.7269
22-0086244 | Tehama | RED BLUFF 1104 | RED BLUFF 11041302 | Unknown | 2022-07-17 07:24 | 7/11 - 7/17 | 2022-07-17 13:50 | 386 | FTS | 268492 | 896 | 79 | 47 | 18 | 1 | 0 | 1 | 299.6562
22-0086243 | Santa Clara | HOLLISTER 2102 | HOLLISTER 2102113634 | Animal | 2022-07-17 07:41 | 7/11 - 7/17 | 2022-07-17 08:26 | 45 | FTS | 4050 | 90 | 3 | 1 | 3 | 0 | 0 | 0 | 45
22-0086246 | Shasta | VOLTA 1102 | VOLTA 11021504 | Animal | 2022-07-17 07:50 | 7/11 - 7/17 | 2022-07-17 10:38 | 168 | FTS | 182910 | 1175 | 106 | 73 | 17 | 3 | 0 | 0 | 155.6681
22-0086247 | Napa | SILVERADO 2104 | SILVERADO 2104726 | 3rd Party | 2022-07-17 08:01 | 7/11 - 7/17 | 2022-07-17 13:34 | 333 | FTS | 115551 | 347 | 19 | 11 | 13 | 3 | 0 | 0 | 333
22-0086260 | San Luis Obispo | ATASCADERO 1103 | ATASCADERO 1103A16 | Animal | 2022-07-17 09:24 | 7/11 - 7/17 | 2022-07-17 11:30 | 126 | FTS | 28350 | 225 | 7 | 4 | 3 | 0 | 0 | 0 | 126
22-0086273 | Nevada | BRUNSWICK 1106 | BRUNSWICK 110651486 | Vegetation | 2022-07-17 12:24 | 7/11 - 7/17 | 2022-07-17 19:40 | 436 | FTS | 77958 | 1066 | 82 | 53 | 9 | 0 | 0 | 6 | 73.1313
22-0086278 | Lake | KONOCTI 1102 | KONOCTI 1102714370 | Unknown | 2022-07-17 13:30 | 7/11 - 7/17 | 2022-07-17 14:55 | 85 | FTS | 9860 | 116 | 12 | 11 | 1 | 0 | 0 | 0 | 85
22-0086286 | Sonoma | BELLEVUE 2103 | BELLEVUE 2103552 | Vegetation | 2022-07-17 14:28 | 7/11 - 7/17 | 2022-07-17 16:22 | 114 | FTS | 95760 | 840 | 50 | 39 | 16 | 0 | 0 | 12 | 114
22-0086296 | Humboldt | GARBERVILLE 1102 | GARBERVILLE 11022124 | Unknown | 2022-07-17 16:06 | 7/11 - 7/17 | 2022-07-17 19:14 | 188 | FTS | 752 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 188
22-0086308 | Mariposa | BEAR VALLEY 2101 | BEAR VALLEY 21014500 | Equipment | 2022-07-17 19:09 | 7/11 - 7/17 | 2022-07-17 20:19 | 70 | FTS | 37870 | 541 | 29 | 19 | 14 | 3 | 0 | 0 | 70
22-0086312 | Mariposa | MARIPOSA 2102 | MARIPOSA 210210880 | Equipment | 2022-07-17 19:41 | 7/11 - 7/17 | 2022-07-18 02:54 | 433 | FTS | 93160 | 481 | 49 | 35 | 5 | 0 | 0 | 0 | 193.6798
22-0086317 | Santa Barbara | BUELLTON 1101 | BUELLTON 1101Y06 | Unknown | 2022-07-17 20:27 | 7/11 - 7/17 | 2022-07-17 23:32 | 185 | FTS | 64195 | 347 | 5 | 5 | 10 | 0 | 0 | 0 | 185
22-0086344 | Marin | LAS GALLINAS A 1105 | LAS GALLINAS A 11051105/2 | Vegetation | 2022-07-18 03:19 | 7/18 - 7/24 | 2022-07-18 04:53 | 94 | C/OUT | 99448 | 2837 | 157 | 86 | 51 | 9 | 0 | 0 | 35.0539
22-0086345 | Alameda | CAYETANO 2111 | CAYETANO 21112111/2 | Unknown | 2022-07-18 04:02 | 7/18 - 7/24 | 2022-07-18 07:48 | 226 | FTS | 467594 | 2069 | 48 | 28 | 26 | 4 | 0 | 0 | 226
22-0086346 | Santa Cruz | PAUL SWEET 2104 | PAUL SWEET 2104885736 | Animal | 2022-07-18 04:32 | 7/18 - 7/24 | 2022-07-18 05:38 | 66 | FTS | 28908 | 438 | 44 | 35 | 5 | 1 | 0 | 0 | 66
22-0086350 | Shasta | ANDERSON 1103 | ANDERSON 11031600 | Animal | 2022-07-18 04:58 | 7/18 - 7/24 | 2022-07-18 07:11 | 133 | FTS | 17157 | 129 | 10 | 7 | 4 | 0 | 0 | 0 | 133
22-0086357 | Monterey | GABILAN 1101 | GABILAN 1101460414 | Unknown | 2022-07-18 05:54 | 7/18 - 7/24 | 2022-07-18 08:18 | 144 | FTS | 5616 | 39 | 3 | 2 | 0 | 0 | 0 | 0 | 144
22-0086360 | El Dorado | CLARKSVILLE 2104 | CLARKSVILLE 210419772 | Unknown | 2022-07-18 06:09 | 7/18 - 7/24 | 2022-07-18 09:10 | 181 | FTS | 44164 | 244 | 22 | 15 | 3 | 0 | 0 | 8 | 181
22-0086361 | Sonoma | DUNBAR 1103 | DUNBAR 1103302 | Animal | 2022-07-18 06:20 | 7/18 - 7/24 | 2022-07-18 07:41 | 81 | FTS | 117528 | 2476 | 247 | 192 | 19 | 0 | 0 | 12 | 47.4669
22-0069306 | Calaveras | STANISLAUS 1701 | STANISLAUS 170179826 | Company Initiated | 2022-07-18 06:38 | 7/18 - 7/24 | 2022-07-18 07:22 | 44 | FTS | 86636 | 1969 | 119 | 93 | 30 | 6 | 0 | 1 | 44
22-0086367 | Calaveras | STANISLAUS 1702 | STANISLAUS 17021850 | Unknown | 2022-07-18 06:38 | 7/18 - 7/24 | 2022-07-18 11:50 | 312 | FTS | 472093 | 2453 | 92 | 69 | 27 | 3 | 2 | 0 | 192.4554
22-0086369 | Monterey | LAURELES 1111 | LAURELES 11112020 | Unknown | 2022-07-18 06:43 | 7/18 - 7/24 | 2022-07-18 09:15 | 152 | FTS | 128896 | 848 | 24 | 14 | 26 | 0 | 0 | 0 | 152
22-0086437 | Amador | OLETA 1102 | OLETA 1102186326 | Unknown | 2022-07-18 08:50 | 7/18 - 7/24 | 2022-07-18 12:23 | 213 | FTS | 205599 | 967 | 38 | 24 | 19 | 1 | 0 | 6 | 212.6153
22-0086493 | Monterey | RESERVATION ROAD 1102 | RESERVATION ROAD 11023032 | Equipment | 2022-07-18 09:41 | 7/18 - 7/24 | 2022-07-18 12:03 | 142 | FTS | 15478 | 109 | 9 | 8 | 1 | 0 | 0 | 0 | 142
22-0086510 | Nevada | NARROWS 2102 | NARROWS 210248484 | Company Initiated | 2022-07-18 09:53 | 7/18 - 7/24 | 2022-07-18 10:46 | 53 | FTS | 31588 | 596 | 38 | 24 | 18 | 6 | 0 | 10 | 53
22-0086525 | Plumas | HAMILTON BRANCH 1101 | HAMILTON BRANCH 110190334 | Equipment | 2022-07-18 10:18 | 7/18 - 7/24 | 2022-07-18 12:28 | 130 | FTS | 39182 | 303 | 17 | 14 | 7 | 0 | 0 | 0 | 129.3135
22-0086554 | Calaveras | PEORIA 1704 | PEORIA 170411232 | Unknown | 2022-07-18 10:59 | 7/18 - 7/24 | 2022-07-18 16:16 | 317 | FTS | 658020 | 2382 | 196 | 137 | 55 | 2 | 0 | 2 | 276.2469
22-0086709 | Santa Clara | LLAGAS 2107 | LLAGAS 2107374344 | Vegetation | 2022-07-18 14:51 | 7/18 - 7/24 | 2022-07-19 02:43 | 712 | FTS | 14074 | 263 | 21 | 11 | 3 | 0 | 0 | 0 | 53.5133
22-0086744 | Santa Cruz | GREEN VALLEY 2101 | GREEN VALLEY 2101942143 | Company Initiated | 2022-07-18 16:03 | 7/18 - 7/24 | 2022-07-18 17:01 | 58 | FTS | 4350 | 75 | 2 | 2 | 0 | 0 | 0 | 2 | 58
22-0086751 | Kern | MAGUNDEN 1108 | MAGUNDEN 1108250674 | 3rd Party | 2022-07-18 16:26 | 7/18 - 7/24 | 2022-07-18 17:22 | 56 | FTS | 5824 | 104 | 1 | 1 | 1 | 0 | 0 | 0 | 56
22-0086778 | Contra Costa | MORAGA 1102 | MORAGA 110242914 | Unknown | 2022-07-18 18:17 | 7/18 - 7/24 | 2022-07-18 19:37 | 80 | FTS | 39506 | 1441 | 39 | 30 | 15 | 3 | 0 | 0 | 27.4157
22-0086798 | Tulare | STONE CORRAL 1110 | STONE CORRAL 1110894956 | Animal | 2022-07-18 20:09 | 7/18 - 7/24 | 2022-07-18 23:13 | 184 | FTS | 4232 | 23 | 1 | 1 | 0 | 0 | 0 | 0 | 184
22-0086808 | Monterey | RESERVATION ROAD 1102 | RESERVATION ROAD 11021102/2 | Animal | 2022-07-18 20:35 | 7/18 - 7/24 | 2022-07-19 00:54 | 259 | FTS | 237674 | 2114 | 88 | 64 | 38 | 2 | 0 | 0 | 112.4286
22-0086815 | Sonoma | CALISTOGA 1101 | CALISTOGA 110178734 | Unknown | 2022-07-18 21:07 | 7/18 - 7/24 | 2022-07-19 11:13 | 846 | FTS | 70506 | 166 | 5 | 5 | 1 | 0 | 0 | 0 | 424.7349
22-0086855 | Yuba | WHEATLAND 1105 | WHEATLAND 1105248490 | Unknown | 2022-07-19 04:13 | 7/18 - 7/24 | 2022-07-19 06:56 | 163 | FTS | 34556 | 212 | 12 | 6 | 3 | 0 | 0 | 4 | 163
22-0086861 | Napa | PUEBLO 2104 | PUEBLO 2104656 | Unknown | 2022-07-19 05:50 | 7/18 - 7/24 | 2022-07-19 10:05 | 255 | FTS | 84915 | 333 | 12 | 7 | 12 | 0 | 0 | 0 | 255
22-0086867 | San Benito | TRES PINOS 1111 | TRES PINOS 11114032 | Animal | 2022-07-19 06:21 | 7/18 - 7/24 | 2022-07-19 07:05 | 44 | FTS | 7148 | 168 | 6 | 6 | 4 | 3 | 0 | 0 | 42.5476
22-0086882 | Tuolumne | MIWUK 1702 | MIWUK 1702823548 | Animal | 2022-07-19 07:00 | 7/18 - 7/24 | 2022-07-19 17:09 | 609 | FTS | 87810 | 841 | 66 | 49 | 12 | 0 | 0 | 0 | 104.4114
22-0086960 | Sonoma | FULTON 1107 | FULTON 1107214 | Equipment | 2022-07-19 08:53 | 7/18 - 7/24 | 2022-07-19 13:11 | 258 | FTS | 63256 | 474 | 25 | 20 | 12 | 0 | 0 | 4 | 133.4515
22-0087059 | Shasta | PANORAMA 1102 | PANORAMA 11021342 | Unknown | 2022-07-19 11:02 | 7/18 - 7/24 | 2022-07-19 13:30 | 148 | FTS | 41061 | 544 | 51 | 34 | 3 | 0 | 0 | 0 | 75.4798
22-0087137 | San Luis Obispo | TEMPLETON 2111 | TEMPLETON 2111686138 | Company Initiated | 2022-07-19 13:15 | 7/18 - 7/24 | 2022-07-19 14:05 | 50 | FTS | 4250 | 85 | 6 | 5 | 0 | 0 | 0 | 0 | 50
22-0087151 | Santa Cruz | CAMP EVERS 2106 | CAMP EVERS 210616000 | 3rd Party | 2022-07-19 13:36 | 7/18 - 7/24 | 2022-07-19 18:04 | 268 | FTS | 740990 | 2836 | 230 | 184 | 42 | 7 | 0 | 14 | 261.28
22-0087247 | El Dorado | EL DORADO PH 2101 | EL DORADO PH 210113362 | Company Initiated | 2022-07-19 15:03 | 7/18 - 7/24 | 2022-07-19 15:55 | 52 | FTS | 23400 | 450 | 9 | 8 | 12 | 0 | 0 | 0 | 52
22-0087298 | Santa Cruz | BIG BASIN 1102 | BIG BASIN 110212758 | Vegetation | 2022-07-19 16:55 | 7/18 - 7/24 | 2022-07-19 18:42 | 107 | FTS | 29639 | 277 | 17 | 16 | 6 | 0 | 0 | 0 | 107
22-0087318 | Placer | SHADY GLEN 1102 | SHADY GLEN 11022232 | 3rd Party | 2022-07-19 17:39 | 7/18 - 7/24 | 2022-07-19 20:50 | 191 | FTS | 67805 | 355 | 29 | 21 | 16 | 0 | 0 | 1 | 191
22-0087376 | Tehama | TYLER 1105 | TYLER 110585132 | Unknown | 2022-07-19 21:53 | 7/18 - 7/24 | 2022-07-20 10:08 | 735 | FTS | 168476 | 834 | 87 | 55 | 13 | 2 | 0 | 1 | 202.0096
22-0087394 | Sonoma | LAKEVILLE 1102 | LAKEVILLE 1102347280 | Unknown | 2022-07-19 22:13 | 7/18 - 7/24 | 2022-07-20 09:12 | 659 | FTS | 62498 | 97 | 2 | 1 | 1 | 0 | 0 | 2 | 644.3093
22-0087412 | Marin | BOLINAS 1101 | BOLINAS 1101504 | Unknown | 2022-07-19 23:34 | 7/18 - 7/24 | 2022-07-20 10:43 | 669 | FTS | 564492 | 844 | 17 | 8 | 10 | 1 | 0 | 0 | 668.8294
22-0087427 | Lake | HIGHLANDS 1102 | HIGHLANDS 110275140 | Equipment | 2022-07-20 05:42 | 7/18 - 7/24 | 2022-07-20 15:17 | 575 | FTS | 266239 | 2617 | 295 | 209 | 34 | 9 | 1 | 0 | 101.7344
22-0087576 | Placer | HALSEY 1101 | HALSEY 110176178 | Unknown | 2022-07-20 10:29 | 7/18 - 7/24 | 2022-07-20 13:08 | 159 | FTS | 99852 | 628 | 46 | 34 | 4 | 0 | 0 | 0 | 159
22-0087634 | Mariposa | MARIPOSA 2102 | MARIPOSA 210237288 | Unknown | 2022-07-20 11:43 | 7/18 - 7/24 | 2022-07-20 15:43 | 240 | FTS | 139200 | 580 | 46 | 35 | 13 | 5 | 0 | 0 | 240
22-0087688 | Placer | HALSEY 1101 | HALSEY 11012414 | Unknown | 2022-07-20 12:56 | 7/18 - 7/24 | 2022-07-20 15:49 | 173 | FTS | 61991 | 403 | 26 | 20 | 7 | 0 | 0 | 3 | 153.8238
22-0087757 | Sonoma | MIRABEL 1102 | MIRABEL 110286326 | Vegetation | 2022-07-20 14:24 | 7/18 - 7/24 | 2022-07-20 19:50 | 326 | FTS | 15789 | 261 | 9 | 8 | 7 | 0 | 0 | 0 | 60.4943
22-0087759 | Fresno | AUBERRY 1102 | AUBERRY 110237466 | Unknown | 2022-07-20 14:29 | 7/18 - 7/24 | 2022-07-20 17:21 | 172 | FTS | 69832 | 406 | 42 | 28 | 2 | 0 | 0 | 1 | 172
22-0087786 | Monterey | RESERVATION ROAD 1102 | RESERVATION ROAD 11023030 | Unknown | 2022-07-20 15:02 | 7/18 - 7/24 | 2022-07-20 16:40 | 98 | FTS | 20008 | 221 | 3 | 2 | 2 | 0 | 0 | 0 | 90.5339
22-0087812 | Placer | FORESTHILL 1101 | FORESTHILL 11011802 | 3rd Party | 2022-07-20 15:30 | 7/18 - 7/24 | 2022-07-21 01:48 | 618 | FTS | 220720 | 1658 | 172 | 113 | 20 | 2 | 0 | 0 | 133.1242
22-0087830 | Lake | LUCERNE 1103 | LUCERNE 11034624 | Animal | 2022-07-20 16:00 | 7/18 - 7/24 | 2022-07-20 18:15 | 135 | FTS | 51030 | 378 | 54 | 41 | 11 | 0 | 0 | 0 | 135
22-0087867 | Placer | HALSEY 1101 | HALSEY 110176178 | Vegetation | 2022-07-20 17:17 | 7/18 - 7/24 | 2022-07-20 21:11 | 234 | FTS | 40027 | 628 | 46 | 34 | 4 | 0 | 0 | 0 | 63.7373
22-0087896 | Shasta | ANDERSON 1103 | ANDERSON 11031600 | Animal | 2022-07-20 19:37 | 7/18 - 7/24 | 2022-07-20 21:29 | 112 | FTS | 7408 | 129 | 10 | 7 | 4 | 0 | 0 | 0 | 57.4264
22-0087897 | Monterey | OILFIELDS 1103 | OILFIELDS 1103N48 | Unknown | 2022-07-20 19:49 | 7/18 - 7/24 | 2022-07-20 22:17 | 148 | FTS | 41144 | 278 | 10 | 4 | 4 | 0 | 0 | 2 | 148
22-0087913 | El Dorado | CLARKSVILLE 2106 | CLARKSVILLE 210619642 | Equipment | 2022-07-20 20:57 | 7/18 - 7/24 | 2022-07-21 12:34 | 937 | FTS | 192302 | 846 | 60 | 38 | 21 | 1 | 0 | 0 | 227.3073
22-0087915 | Lassen | MC ARTHUR 1101 | MC ARTHUR 11011544 | Unknown | 2022-07-20 21:33 | 7/18 - 7/24 | 2022-07-21 02:37 | 304 | FTS | 79948 | 366 | 15 | 12 | 20 | 3 | 0 | 0 | 218.4372
22-0087934 | Santa Cruz | PAUL SWEET 2106 | PAUL SWEET 21065178 | Animal | 2022-07-20 22:56 | 7/18 - 7/24 | 2022-07-21 08:13 | 557 | FTS | 78567 | 267 | 30 | 27 | 5 | 0 | 0 | 1 | 294.2584
22-0087938 | Sonoma | FITCH MOUNTAIN 1113 | FITCH MOUNTAIN 111324550 | Vegetation | 2022-07-20 23:23 | 7/18 - 7/24 | 2022-07-21 00:53 | 90 | FTS | 19890 | 221 | 6 | 4 | 7 | 0 | 0 | 2 | 90
22-0087945 | Shasta | PANORAMA 1102 | PANORAMA 11021526 | Animal | 2022-07-21 03:58 | 7/18 - 7/24 | 2022-07-21 06:27 | 149 | FTS | 15033 | 103 | 8 | 7 | 2 | 0 | 0 | 0 | 145.9515
22-0088013 | Contra Costa | ROSSMOOR 1106 | ROSSMOOR 1106L522R | Unknown | 2022-07-21 08:23 | 7/18 - 7/24 | 2022-07-21 10:12 | 109 | FTS | 215185 | 2221 | 54 | 38 | 14 | 8 | 0 | 0 | 96.8865
22-0088027 | San Luis Obispo | PASO ROBLES 1103 | PASO ROBLES 110355374 | Unknown | 2022-07-21 08:48 | 7/18 - 7/24 | 2022-07-21 12:26 | 218 | FTS | 86146 | 517 | 13 | 8 | 5 | 0 | 0 | 0 | 166.6267
22-0088073 | Calaveras | CALAVERAS CEMENT 1101 | CALAVERAS CEMENT 110111236 | Animal | 2022-07-21 09:54 | 7/18 - 7/24 | 2022-07-22 02:38 | 1004 | FTS | 23614 | 182 | 11 | 9 | 6 | 0 | 0 | 0 | 129.7473
22-0088196 | Fresno | AUBERRY 1102 | AUBERRY 110237466 | Unknown | 2022-07-21 12:25 | 7/18 - 7/24 | 2022-07-21 15:18 | 173 | FTS | 70238 | 406 | 42 | 28 | 2 | 0 | 0 | 1 | 173
22-0088199 | Fresno | AUBERRY 1102 | AUBERRY 1102R902 | Unknown | 2022-07-21 12:27 | 7/18 - 7/24 | 2022-07-21 14:58 | 151 | FTS | 42884 | 284 | 29 | 19 | 5 | 0 | 0 | 1 | 151
22-0088246 | Napa | MONTICELLO 1101 | MONTICELLO 1101256640 | Unknown | 2022-07-21 13:22 | 7/18 - 7/24 | 2022-07-21 16:06 | 164 | FTS | 6789 | 42 | 0 | 0 | 4 | 0 | 0 | 0 | 161.6429
22-0088313 | Humboldt | GARBERVILLE 1102 | GARBERVILLE 11021102/2 | Vegetation | 2022-07-21 14:57 | 7/18 - 7/24 | 2022-07-21 17:35 | 158 | FTS | 270572 | 1936 | 41 | 26 | 60 | 11 | 0 | 0 | 139.7583
22-0088341 | Sonoma | CALISTOGA 1101 | CALISTOGA 1101242919 | Unknown | 2022-07-21 15:31 | 7/18 - 7/24 | 2022-07-21 16:54 | 83 | FTS | 1992 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 83
22-0088399 | Nevada | BRUNSWICK 1110 | BRUNSWICK 11101110/2 | Equipment | 2022-07-21 18:22 | 7/18 - 7/24 | 2022-07-22 02:47 | 505 | FTS | 506221 | 3153 | 210 | 149 | 64 | 14 | 4 | 5 | 160.5522
22-0088422 | Mariposa | MARIPOSA 2101 | MARIPOSA 210110240 | Unknown | 2022-07-21 21:06 | 7/18 - 7/24 | 2022-07-22 12:41 | 935 | FTS | 413000 | 469 | 24 | 16 | 8 | 0 | 0 | 0 | 880.597
22-0088472 | Nevada | HIGGINS 1103 | HIGGINS 1103995672 | Vegetation | 2022-07-22 00:56 | 7/18 - 7/24 | 2022-07-22 17:12 | 976 | FTS | 36772 | 217 | 14 | 9 | 2 | 0 | 0 | 0 | 169.4562
22-0088473 | Santa Clara | SARATOGA 1106 | SARATOGA 1106LC24 | Vegetation | 2022-07-22 01:58 | 7/18 - 7/24 | 2022-07-22 19:30 | 1052 | FTS | 111576 | 1154 | 64 | 43 | 18 | 1 | 0 | 0 | 96.6863
22-0088485 | Santa Barbara | CABRILLO 1103 | CABRILLO 1103Y46 | Unknown | 2022-07-22 05:57 | 7/18 - 7/24 | 2022-07-22 08:57 | 180 | FTS | 23755 | 275 | 2 | 2 | 5 | 0 | 0 | 0 | 86.3818
22-0088574 | San Luis Obispo | OCEANO 1104 | OCEANO 1104891294 | Vegetation | 2022-07-22 08:40 | 7/18 - 7/24 | 2022-07-22 13:35 | 295 | FTS | 62863 | 870 | 41 | 32 | 5 | 1 | 0 | 10 | 72.2563
22-0088601 | El Dorado | SHINGLE SPRINGS 2109 | SHINGLE SPRINGS 21099372 | Unknown | 2022-07-22 08:59 | 7/18 - 7/24 | 2022-07-22 12:29 | 210 | HLT | 299597 | 2117 | 165 | 113 | 24 | 2 | 0 | 30 | 141.5196
22-0088619 | Santa Cruz | BIG BASIN 1102 | BIG BASIN 1102351054 | Animal | 2022-07-22 09:29 | 7/18 - 7/24 | 2022-07-22 12:17 | 168 | FTS | 67548 | 831 | 48 | 33 | 14 | 1 | 0 | 1 | 81.2852
22-0085482 | Santa Cruz | BIG BASIN 1102 | BIG BASIN 1102573005 | Company Initiated | 2022-07-22 12:47 | 7/18 - 7/24 | 2022-07-22 13:05 | 18 | FTS | 720 | 40 | 4 | 3 | 0 | 0 | 0 | 0 | 18
22-0088784 | Kern | POSO MOUNTAIN 2104 | POSO MOUNTAIN 210448268 | Unknown | 2022-07-22 13:19 | 7/18 - 7/24 | 2022-07-22 17:16 | 237 | FTS | 2133 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 237
22-0085525 | Monterey | SOLEDAD 2105 | SOLEDAD 2105315500 | Company Initiated | 2022-07-22 19:22 | 7/18 - 7/24 | 2022-07-22 19:58 | 36 | FTS | 14557 | 602 | 13 | 11 | 9 | 0 | 0 | 0 | 24.1811
22-0088913 | Marin | ALTO 1125 | ALTO 11251256 | Unknown | 2022-07-22 22:15 | 7/18 - 7/24 | 2022-07-23 01:01 | 166 | FTS | 305163 | 2122 | 78 | 52 | 22 | 2 | 0 | 0 | 143.8091
22-0088914 | Monterey | KING CITY 1102 | KING CITY 1102728782 | Unknown | 2022-07-22 22:20 | 7/18 - 7/24 | 2022-07-22 22:52 | 32 | FTS | 160 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 32
22-0088928 | Santa Clara | MORGAN HILL 2105 | MORGAN HILL 2105XR564 | Unknown | 2022-07-23 02:56 | 7/18 - 7/24 | 2022-07-23 06:15 | 199 | FTS | 71043 | 357 | 19 | 15 | 10 | 2 | 0 | 0 | 199
22-0088944 | Sonoma | GEYSERVILLE 1102 | GEYSERVILLE 1102274 | Unknown | 2022-07-23 07:09 | 7/18 - 7/24 | 2022-07-23 10:20 | 191 | FTS | 77310 | 420 | 11 | 3 | 8 | 1 | 0 | 1 | 184.0714
22-0088948 | Marin | STAFFORD 1101 | STAFFORD 11011102/2 | Unknown | 2022-07-23 07:22 | 7/18 - 7/24 | 2022-07-23 14:23 | 421 | FTS | 1383109 | 3971 | 232 | 145 | 27 | 7 | 0 | 0 | 348.3024
22-0088949 | Marin | WOODACRE 1102 | WOODACRE 1102137662 | Animal | 2022-07-23 07:32 | 7/18 - 7/24 | 2022-07-23 11:02 | 210 | FTS | 322106 | 1891 | 90 | 49 | 28 | 6 | 0 | 0 | 170.3363
22-0088954 | Monterey | JOLON 1103 | JOLON 11031103/2 | Unknown | 2022-07-23 07:55 | 7/18 - 7/24 | 2022-07-23 11:53 | 238 | FTS | 4760 | 20 | 0 | 0 | 15 | 0 | 0 | 0 | 238
22-0088956 | Tuolumne | SPRING GAP 1702 | SPRING GAP 17029280 | Equipment | 2022-07-23 08:06 | 7/18 - 7/24 | 2022-07-23 18:52 | 646 | FTS | 617106 | 1536 | 35 | 23 | 18 | 2 | 0 | 0 | 401.7617
22-0088999 | Santa Cruz | CAMP EVERS 2106 | CAMP EVERS 2106737512 | Vegetation | 2022-07-23 12:08 | 7/18 - 7/24 | 2022-07-23 13:50 | 102 | FTS | 63204 | 918 | 71 | 48 | 10 | 0 | 0 | 0 | 68.8497
22-0083562 | Santa Cruz | CAMP EVERS 2106 | CAMP EVERS 210612840 | Company Initiated | 2022-07-23 13:28 | 7/18 - 7/24 | 2022-07-23 14:43 | 75 | FTS | 4500 | 60 | 9 | 8 | 2 | 0 | 0 | 0 | 75
22-0089022 | Santa Clara | MORGAN HILL 2111 | MORGAN HILL 2111XR398 | 3rd Party | 2022-07-23 14:20 | 7/18 - 7/24 | 2022-07-23 15:03 | 43 | FTS | 8253 | 400 | 23 | 20 | 10 | 0 | 0 | 1 | 20.6325
22-0089050 | Placer | DEL MAR 2109 | DEL MAR 210975802 | Unknown | 2022-07-23 18:06 | 7/18 - 7/24 | 2022-07-23 19:23 | 77 | FTS | 211981 | 2753 | 152 | 97 | 26 | 1 | 0 | 1 | 77
22-0089057 | Santa Cruz | ROB ROY 2105 | ROB ROY 210512586 | Animal | 2022-07-23 21:11 | 7/18 - 7/24 | 2022-07-23 22:01 | 50 | FTS | 53900 | 1078 | 95 | 80 | 8 | 3 | 0 | 0 | 50
22-0089059 | Calaveras | STANISLAUS 1701 | STANISLAUS 17011701/2 | 3rd Party | 2022-07-23 21:47 | 7/18 - 7/24 | 2022-07-24 14:32 | 1005 | FTS | 1547525 | 2187 | 134 | 100 | 68 | 4 | 0 | 0 | 707.6017
22-0089092 | Kings | AVENAL 2101 | AVENAL 21019070 | Animal | 2022-07-23 23:22 | 7/18 - 7/24 | 2022-07-24 04:25 | 303 | FTS | 20604 | 68 | 0 | 0 | 9 | 0 | 0 | 0 | 303
22-0089093 | Sonoma | BELLEVUE 2103 | BELLEVUE 2103552 | Vegetation | 2022-07-24 01:24 | 7/18 - 7/24 | 2022-07-24 11:06 | 582 | FTS | 69298 | 839 | 50 | 39 | 16 | 0 | 0 | 12 | 82.5959
22-0089094 | Contra Costa | WILLOW PASS 2108 | WILLOW PASS 21082108/2 | Unknown | 2022-07-24 01:35 | 7/18 - 7/24 | 2022-07-24 03:27 | 112 | FTS | 220448 | 5616 | 290 | 200 | 47 | 6 | 0 | 0 | 39.2536
22-0089102 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 210623190 | Unknown | 2022-07-24 06:10 | 7/18 - 7/24 | 2022-07-24 08:42 | 152 | FTS | 272220 | 1994 | 148 | 92 | 26 | 4 | 1 | 4 | 136.5196
22-0089101 | Madera | OAKHURST 1101 | OAKHURST 11015490 | Unknown | 2022-07-24 06:12 | 7/18 - 7/24 | 2022-07-24 10:00 | 228 | FTS | 345684 | 1554 | 175 | 128 | 31 | 2 | 0 | 0 | 222.4479
22-0089109 | Contra Costa | SOBRANTE 1103 | SOBRANTE 11031103/2 | Unknown | 2022-07-24 07:28 | 7/18 - 7/24 | 2022-07-24 11:52 | 264 | C/OUT | 259248 | 982 | 61 | 42 | 15 | 1 | 0 | 0 | 264
22-0089131 | Alameda | VINEYARD 2108 | VINEYARD 2108MR172 | Equipment | 2022-07-24 10:21 | 7/18 - 7/24 | 2022-07-25 03:13 | 1012 | FTS | 476344 | 3026 | 173 | 116 | 38 | 2 | 0 | 0 | 157.4171
22-0089157 | San Luis Obispo | TEMPLETON 2112 | TEMPLETON 2112R28 | Unknown | 2022-07-24 13:42 | 7/18 - 7/24 | 2022-07-24 17:40 | 238 | FTS | 78039 | 329 | 8 | 6 | 9 | 0 | 0 | 0 | 237.2006
22-0089171 | Humboldt | GARBERVILLE 1101 | GARBERVILLE 11011750 | Vegetation | 2022-07-24 15:32 | 7/18 - 7/24 | 2022-07-25 02:15 | 643 | FTS | 18764 | 92 | 1 | 1 | 2 | 0 | 0 | 0 | 203.9565
22-0089197 | Sonoma | GEYSERVILLE 1102 | GEYSERVILLE 1102484 | Animal | 2022-07-24 18:39 | 7/18 - 7/24 | 2022-07-24 21:00 | 141 | FTS | 53862 | 382 | 5 | 2 | 15 | 1 | 0 | 1 | 141
22-0089205 | Tuolumne | CURTIS 1702 | CURTIS 17028000 | Equipment | 2022-07-24 20:24 | 7/18 - 7/24 | 2022-07-25 08:21 | 717 | FTS | 161768 | 1152 | 107 | 80 | 16 | 1 | 0 | 0 | 140.4236
22-0089220 | Contra Costa | ORINDA 0401 | ORINDA 0401401/2 | Vegetation | 2022-07-24 22:21 | 7/18 - 7/24 | 2022-07-25 03:43 | 322 | FTS | 53846 | 293 | 17 | 11 | 2 | 0 | 0 | 0 | 183.7747
22-0089243 | Tuolumne | CURTIS 1702 | CURTIS 170234426 | Vegetation | 2022-07-24 23:39 | 7/18 - 7/24 | 2022-07-25 04:26 | 287 | FTS | 161007 | 561 | 35 | 24 | 9 | 2 | 0 | 0 | 287
22-0089253 | Santa Cruz | BEN LOMOND 1101 | BEN LOMOND 1101BL 2101 | 3rd Party | 2022-07-25 02:49 | 7/25 - 7/31 | 2022-07-25 13:33 | 644 | FTS | 297804 | 1966 | 146 | 110 | 33 | 3 | 0 | 1 | 151.4771
22-0089262 | Tehama | CORNING 1101 | CORNING 110185152 | Unknown | 2022-07-25 06:09 | 7/25 - 7/31 | 2022-07-25 09:42 | 213 | FTS | 81123 | 476 | 67 | 40 | 9 | 0 | 0 | 0 | 170.4265
22-0089264 | Sonoma | DUNBAR 1102 | DUNBAR 1102246 | Unknown | 2022-07-25 06:27 | 7/25 - 7/31 | 2022-07-25 10:15 | 228 | FTS | 117817 | 532 | 23 | 13 | 8 | 0 | 0 | 7 | 221.4605
22-0089270 | Lake | KONOCTI 1102 | KONOCTI 110264664 | Unknown | 2022-07-25 06:47 | 7/25 - 7/31 | 2022-07-25 09:58 | 191 | FTS | 96281 | 507 | 38 | 26 | 3 | 0 | 0 | 1 | 189.9034
22-0089287 | Placer | PENRYN 1106 | PENRYN 110651674 | Vegetation | 2022-07-25 07:51 | 7/25 - 7/31 | 2022-07-25 14:49 | 418 | FTS | 164246 | 907 | 64 | 39 | 6 | 3 | 0 | 0 | 181.0871
22-0089321 | Sonoma | CALISTOGA 1101 | CALISTOGA 110178734 | Equipment | 2022-07-25 09:11 | 7/25 - 7/31 | 2022-07-25 22:12 | 781 | FTS | 51694 | 166 | 5 | 5 | 1 | 0 | 0 | 0 | 311.4096
22-0089327 | Nevada | NARROWS 2105 | NARROWS 21052216 | Animal | 2022-07-25 09:25 | 7/25 - 7/31 | 2022-07-25 12:09 | 164 | FTS | 166096 | 2101 | 177 | 102 | 28 | 4 | 0 | 19 | 79.0557
22-0089340 | San Benito | HOLLISTER 2102 | HOLLISTER 2102113634 | Unknown | 2022-07-25 10:00 | 7/25 - 7/31 | 2022-07-25 11:01 | 61 | FTS | 4819 | 79 | 3 | 1 | 3 | 0 | 0 | 0 | 61
22-0089359 | Butte | SYCAMORE CREEK 1109 | SYCAMORE CREEK 11091109/2 | Animal | 2022-07-25 10:01 | 7/25 - 7/31 | 2022-07-25 16:45 | 404 | FTS | 238106 | 2372 | 158 | 104 | 30 | 1 | 0 | 0 | 100.382
22-0089355 | Solano | JAMESON 1102 | JAMESON 11028842 | Animal | 2022-07-25 10:21 | 7/25 - 7/31 | 2022-07-25 11:59 | 98 | FTS | 66354 | 783 | 72 | 52 | 22 | 0 | 0 | 2 | 84.7433
22-0089414 | Butte | BIG BEND 1102 | BIG BEND 11021102/2 | Unknown | 2022-07-25 12:04 | 7/25 - 7/31 | 2022-07-25 14:30 | 146 | FTS | 47450 | 325 | 8 | 4 | 11 | 0 | 0 | 0 | 146
22-0089503 | Napa | MONTICELLO 1101 | MONTICELLO 110137384 | Unknown | 2022-07-25 14:43 | 7/25 - 7/31 | 2022-07-25 16:49 | 126 | FTS | 63630 | 505 | 27 | 19 | 11 | 0 | 0 | 2 | 126
22-0089546 | Butte | BIG BEND 1102 | BIG BEND 11021102/2 | Equipment | 2022-07-25 16:09 | 7/25 - 7/31 | 2022-07-26 05:00 | 771 | FTS | 121377 | 635 | 28 | 17 | 18 | 0 | 0 | 1 | 191.1449
22-0089562 | Mendocino | UKIAH 1111 | UKIAH 1111433984 | Unknown | 2022-07-25 16:56 | 7/25 - 7/31 | 2022-07-25 19:47 | 171 | HLT | 180180 | 1072 | 39 | 20 | 21 | 6 | 0 | 0 | 168.0784
22-0089573 | Solano | VACAVILLE 1108 | VACAVILLE 11088762 | Animal | 2022-07-25 18:51 | 7/25 - 7/31 | 2022-07-25 19:57 | 66 | FTS | 24232 | 423 | 22 | 15 | 15 | 1 | 0 | 2 | 57.2861
22-0089576 | Humboldt | BRIDGEVILLE 1101 | BRIDGEVILLE 110169866 | Unknown | 2022-07-25 18:58 | 7/25 - 7/31 | 2022-07-26 12:04 | 1026 | FTS | 64638 | 63 | 1 | 1 | 2 | 0 | 0 | 0 | 1026
22-0089588 | Tehama | TYLER 1105 | TYLER 11051704 | Equipment | 2022-07-25 21:34 | 7/25 - 7/31 | 2022-07-26 04:28 | 414 | FTS | 119446 | 834 | 87 | 55 | 13 | 2 | 0 | 1 | 143.2206
22-0089602 | Nevada | BRUNSWICK 1110 | BRUNSWICK 11101110/2 | 3rd Party | 2022-07-25 22:25 | 7/25 - 7/31 | 2022-07-26 16:11 | 1066 | FTS | 171714 | 3076 | 203 | 143 | 63 | 14 | 4 | 5 | 55.8238
22-0089607 | Napa | SILVERADO 2102 | SILVERADO 21022102/2 | Equipment | 2022-07-26 00:19 | 7/25 - 7/31 | 2022-07-26 03:36 | 197 | FTS | 66172 | 1264 | 10 | 9 | 27 | 0 | 0 | 2 | 52.3513
22-0089608 | Monterey | GABILAN 1101 | GABILAN 11013034 | Equipment | 2022-07-26 00:27 | 7/25 - 7/31 | 2022-07-26 15:46 | 919 | FTS | 365234 | 543 | 31 | 21 | 12 | 0 | 0 | 0 | 672.6225
22-0089622 | Tuolumne | CURTIS 1703 | CURTIS 170384944 | Unknown | 2022-07-26 05:44 | 7/25 - 7/31 | 2022-07-26 07:29 | 105 | FTS | 322665 | 3073 | 201 | 148 | 44 | 1 | 0 | 5 | 105
22-0089645 | Tuolumne | CURTIS 1705 | CURTIS 170539256 | Unknown | 2022-07-26 07:21 | 7/25 - 7/31 | 2022-07-26 08:13 | 52 | FTS | 27144 | 522 | 67 | 48 | 4 | 0 | 0 | 0 | 52
22-0090027 | Plumas | CRESCENT MILLS 2101 | CRESCENT MILLS 21012562 | Animal | 2022-07-26 16:13 | 7/25 - 7/31 | 2022-07-26 18:20 | 127 | FTS | 179036 | 1533 | 66 | 49 | 25 | 1 | 5 | 0 | 116.788
22-0090046 | Mendocino | UKIAH 1115 | UKIAH 1115534 | Unknown | 2022-07-26 17:16 | 7/25 - 7/31 | 2022-07-26 19:12 | 116 | FTS | 20880 | 180 | 7 | 5 | 6 | 1 | 0 | 0 | 116
22-0090087 | Sonoma | MIRABEL 1101 | MIRABEL 1101116 | Unknown | 2022-07-26 20:50 | 7/25 - 7/31 | 2022-07-27 08:16 | 686 | FTS | 87366 | 385 | 16 | 13 | 2 | 0 | 0 | 0 | 226.9247
22-0090111 | Santa Clara | MORGAN HILL 2111 | MORGAN HILL 2111XR398 | 3rd Party | 2022-07-27 00:26 | 7/25 - 7/31 | 2022-07-28 01:23 | 1497 | FTS | 233040 | 400 | 23 | 20 | 10 | 0 | 0 | 1 | 582.6
22-0090121 | Nevada | HIGGINS 1103 | HIGGINS 110350072 | Animal | 2022-07-27 05:52 | 7/25 - 7/31 | 2022-07-27 09:39 | 227 | FTS | 146188 | 644 | 49 | 30 | 3 | 0 | 0 | 10 | 227
22-0090153 | Santa Clara | LOS GATOS 1106 | LOS GATOS 110660116 | Unknown | 2022-07-27 07:31 | 7/25 - 7/31 | 2022-07-27 10:47 | 196 | FTS | 180761 | 1135 | 91 | 72 | 23 | 3 | 0 | 3 | 159.2608
22-0090185 | Mariposa | BEAR VALLEY 2105 | BEAR VALLEY 21054170 | 3rd Party | 2022-07-27 08:30 | 7/25 - 7/31 | 2022-07-27 11:22 | 172 | FTS | 118279 | 688 | 53 | 41 | 11 | 8 | 1 | 1 | 171.9172
22-0090331 | Butte | ORO FINO 1102 | ORO FINO 11022090 | Vegetation | 2022-07-27 11:42 | 7/25 - 7/31 | 2022-07-27 13:37 | 115 | FTS | 65780 | 572 | 76 | 49 | 5 | 0 | 0 | 1 | 115
22-0090340 | Sonoma | CALISTOGA 1101 | CALISTOGA 110178734 | Company Initiated | 2022-07-27 12:25 | 7/25 - 7/31 | 2022-07-27 15:26 | 181 | FTS | 11041 | 61 | 5 | 5 | 0 | 0 | 0 | 0 | 181
22-0090474 | Plumas | HAMILTON BRANCH 1101 | HAMILTON BRANCH 1101161872 | Unknown | 2022-07-27 15:20 | 7/25 - 7/31 | 2022-07-27 18:00 | 160 | FTS | 480 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 160
22-0090520 | Placer | FORESTHILL 1101 | FORESTHILL 11011802 | 3rd Party | 2022-07-27 16:49 | 7/25 - 7/31 | 2022-07-27 19:21 | 152 | FTS | 251274 | 1658 | 172 | 113 | 20 | 2 | 0 | 0 | 151.5525
22-0090533 | Contra Costa | LAKEWOOD 1103 | LAKEWOOD 1103857172 | Animal | 2022-07-27 17:38 | 7/25 - 7/31 | 2022-07-27 18:33 | 55 | FTS | 4290 | 78 | 5 | 3 | 1 | 0 | 0 | 0 | 55
22-0090644 | Solano | VACA DIXON 1105 | VACA DIXON 11059792 | Unknown | 2022-07-28 07:26 | 7/25 - 7/31 | 2022-07-28 08:33 | 67 | FTS | 35108 | 524 | 67 | 42 | 3 | 0 | 0 | 2 | 67
22-0090813 | Sonoma | SONOMA 1105 | SONOMA 1105229588 | Company Initiated | 2022-07-28 12:00 | 7/25 - 7/31 | 2022-07-28 12:55 | 55 | FTS | 2255 | 41 | 4 | 4 | 0 | 0 | 0 | 1 | 55
22-0090893 | Placer | DRUM 1101 | DRUM 11011101/2 | Unknown | 2022-07-28 13:45 | 7/25 - 7/31 | 2022-07-28 17:23 | 218 | FTS | 36337 | 203 | 6 | 3 | 19 | 1 | 0 | 1 | 179
22-0090995 | Shasta | STILLWATER 1102 | STILLWATER 11021466 | Unknown | 2022-07-28 15:37 | 7/25 - 7/31 | 2022-07-28 19:02 | 205 | FTS | 97375 | 475 | 44 | 32 | 7 | 0 | 0 | 0 | 205
22-0091052 | Shasta | STILLWATER 1102 | STILLWATER 11021102/2 | Unknown | 2022-07-28 19:07 | 7/25 - 7/31 | 2022-07-28 22:57 | 230 | FTS | 316925 | 1420 | 120 | 82 | 16 | 0 | 0 | 0 | 223.1866
22-0091062 | Placer | WISE 1102 | WISE 11022230 | Unknown | 2022-07-28 19:57 | 7/25 - 7/31 | 2022-07-29 09:14 | 797 | FTS | 115264 | 859 | 68 | 53 | 4 | 0 | 0 | 13 | 134.1839
22-0091072 | Alameda | VASCO 1102 | VASCO 1102546328 | Unknown | 2022-07-28 20:43 | 7/25 - 7/31 | 2022-07-29 11:19 | 876 | FTS | 199728 | 228 | 20 | 14 | 7 | 0 | 0 | 1 | 876
22-0091096 | Butte | SYCAMORE CREEK 1109 | SYCAMORE CREEK 11091109/2 | Unknown | 2022-07-28 23:56 | 7/25 - 7/31 | 2022-07-29 06:08 | 372 | FTS | 493168 | 2372 | 158 | 104 | 30 | 1 | 0 | 0 | 207.9123
22-0091104 | Yolo | MADISON 2101 | MADISON 21011606 | Unknown | 2022-07-29 04:47 | 7/25 - 7/31 | 2022-07-29 09:50 | 303 | FTS | 97045 | 515 | 18 | 8 | 6 | 0 | 0 | 1 | 188.4369
22-0091109 | Shasta | MC ARTHUR 1101 | MC ARTHUR 11011488 | Unknown | 2022-07-29 05:39 | 7/25 - 7/31 | 2022-07-29 09:56 | 257 | FTS | 50115 | 195 | 6 | 3 | 0 | 0 | 0 | 0 | 257
22-0091143 | Santa Cruz | CAMP EVERS 2105 | CAMP EVERS 210510728 | Unknown | 2022-07-29 07:07 | 7/25 - 7/31 | 2022-07-29 09:35 | 148 | FTS | 389706 | 2993 | 235 | 179 | 45 | 4 | 0 | 1 | 130.2058
22-0091155 | Fresno | DUNLAP 1102 | DUNLAP 11027060 | Animal | 2022-07-29 07:27 | 7/25 - 7/31 | 2022-07-29 12:26 | 299 | FTS | 37770 | 223 | 19 | 13 | 3 | 1 | 0 | 0 | 169.3722
22-0091263 | Sonoma | BELLEVUE 2103 | BELLEVUE 2103552 | Unknown | 2022-07-29 10:14 | 7/25 - 7/31 | 2022-07-29 12:39 | 145 | FTS | 121800 | 840 | 50 | 39 | 16 | 0 | 0 | 12 | 145
22-0091323 | San Mateo | WOODSIDE 1101 | WOODSIDE 110147872 | Unknown | 2022-07-29 11:06 | 7/25 - 7/31 | 2022-07-29 13:36 | 150 | FTS | 27467 | 250 | 17 | 9 | 14 | 1 | 0 | 0 | 109.868
22-0091331 | Santa Clara | STELLING 1109 | STELLING 1109589102 | Unknown | 2022-07-29 11:38 | 7/25 - 7/31 | 2022-07-29 12:53 | 75 | FTS | 2175 | 29 | 5 | 3 | 1 | 0 | 0 | 0 | 75
22-0091424 | Santa Cruz | CAMP EVERS 2105 | CAMP EVERS 210510728 | Vegetation | 2022-07-29 13:45 | 7/25 - 7/31 | 2022-07-29 15:11 | 86 | FTS | 217998 | 2993 | 235 | 179 | 45 | 4 | 0 | 1 | 72.836
22-0091511 | Contra Costa | CLAYTON 2212 | CLAYTON 22122212/2 | 3rd Party | 2022-07-29 16:18 | 7/25 - 7/31 | 2022-07-29 17:10 | 52 | FTS | 175760 | 3380 | 291 | 192 | 78 | 8 | 0 | 5 | 52
22-0091521 | Contra Costa | CLAYTON 2212 | CLAYTON 2212614950 | Unknown | 2022-07-29 17:10 | 7/25 - 7/31 | 2022-07-29 17:43 | 33 | FTS | 1584 | 48 | 3 | 2 | 0 | 0 | 0 | 0 | 33
22-0091522 | Shasta | GIRVAN 1102 | GIRVAN 1102212096 | Unknown | 2022-07-29 17:25 | 7/25 - 7/31 | 2022-07-29 19:54 | 149 | FTS | 6854 | 46 | 4 | 2 | 0 | 0 | 0 | 0 | 149
22-0091551 | Tuolumne | CURTIS 1705 | CURTIS 170539256 | Unknown | 2022-07-29 20:02 | 7/25 - 7/31 | 2022-07-29 21:04 | 62 | FTS | 32364 | 522 | 67 | 48 | 4 | 0 | 0 | 0 | 62
22-0091554 | Placer | DEL MAR 2109 | DEL MAR 21092109/2 | Animal | 2022-07-29 20:42 | 7/25 - 7/31 | 2022-07-29 22:31 | 109 | FTS | 395999 | 4067 | 237 | 154 | 40 | 2 | 0 | 1 | 97.3688
22-0091557 | Calaveras | CALAVERAS CEMENT 1101 | CALAVERAS CEMENT 1101502 | Unknown | 2022-07-29 21:52 | 7/25 - 7/31 | 2022-07-30 08:08 | 616 | FTS | 638636 | 1039 | 58 | 43 | 24 | 0 | 0 | 0 | 614.6641
22-0091574 | Marin | STAFFORD 1102 | STAFFORD 11021202 | Equipment | 2022-07-30 01:59 | 7/25 - 7/31 | 2022-07-30 12:27 | 628 | FTS | 8294 | 53 | 0 | 0 | 1 | 0 | 0 | 0 | 156.4906
22-0091577 | Calaveras | FROGTOWN 1701 | FROGTOWN 170113412 | Unknown | 2022-07-30 03:20 | 7/25 - 7/31 | 2022-07-30 05:24 | 124 | FTS | 156858 | 1827 | 113 | 88 | 27 | 6 | 0 | 1 | 85.8555
22-0091592 | Nevada | NARROWS 2102 | NARROWS 21022220 | Vegetation | 2022-07-30 06:42 | 7/25 - 7/31 | 2022-07-30 09:45 | 183 | FTS | 83204 | 890 | 56 | 33 | 20 | 7 | 0 | 11 | 93.4876
22-0091622 | Tuolumne | CURTIS 1704 | CURTIS 17046060 | Unknown | 2022-07-30 08:47 | 7/25 - 7/31 | 2022-07-30 13:01 | 254 | FTS | 322148 | 1559 | 175 | 124 | 16 | 0 | 0 | 2 | 206.6376
22-0091625 | Placer | LINCOLN 1104 | LINCOLN 11042070 | 3rd Party | 2022-07-30 09:12 | 7/25 - 7/31 | 2022-07-30 10:36 | 84 | FTS | 22417 | 344 | 27 | 20 | 2 | 0 | 0 | 5 | 65.1657
22-0091645 | Yuba | PIKE CITY 1101 | PIKE CITY 11011720 | Company Initiated | 2022-07-30 11:05 | 7/25 - 7/31 | 2022-07-30 11:27 | 22 | FTS | 154 | 7 | 1 | 1 | 0 | 0 | 0 | 0 | 22
22-0091658 | Sierra | ALLEGHANY 1101 | ALLEGHANY 1101978 | Company Initiated | 2022-07-30 11:48 | 7/25 - 7/31 | 2022-07-30 12:07 | 19 | FTS | 3667 | 193 | 4 | 3 | 3 | 0 | 0 | 0 | 19
22-0091662 | Amador | ELECTRA 1101 | ELECTRA 11017104 | Unknown | 2022-07-30 11:48 | 7/25 - 7/31 | 2022-07-30 13:42 | 114 | FTS | 71022 | 623 | 63 | 41 | 7 | 0 | 0 | 1 | 114
22-0091670 | Placer | LINCOLN 1104 | LINCOLN 11042070 | 3rd Party | 2022-07-30 12:21 | 7/25 - 7/31 | 2022-07-30 13:43 | 82 | FTS | 28208 | 344 | 27 | 20 | 2 | 0 | 0 | 5 | 82
22-0091676 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113A70 | 3rd Party | 2022-07-30 13:09 | 7/25 - 7/31 | 2022-07-30 17:56 | 287 | FTS | 803287 | 3125 | 177 | 127 | 50 | 2 | 1 | 20 | 257.0518
22-0091695 | Shasta | WHITMORE 1101 | WHITMORE 1101903576 | Unknown | 2022-07-30 13:14 | 7/25 - 7/31 | 2022-07-30 18:49 | 335 | FTS | 32160 | 96 | 9 | 7 | 1 | 0 | 0 | 1 | 335
22-0091678 | Contra Costa | TASSAJARA 2108 | TASSAJARA 2108D520R | Equipment | 2022-07-30 13:17 | 7/25 - 7/31 | 2022-07-30 17:21 | 244 | FTS | 602375 | 4538 | 224 | 149 | 84 | 18 | 0 | 0 | 132.7402
22-0091699 | Monterey | RESERVATION ROAD 1101 | RESERVATION ROAD 1101383718 | Animal | 2022-07-30 14:57 | 7/25 - 7/31 | 2022-07-30 17:41 | 164 | FTS | 116276 | 709 | 51 | 32 | 18 | 2 | 0 | 0 | 164
22-0091710 | Plumas | GANSNER 1101 | GANSNER 11012424 | Equipment | 2022-07-30 15:52 | 7/25 - 7/31 | 2022-07-30 20:18 | 266 | FTS | 54796 | 206 | 11 | 8 | 4 | 0 | 0 | 2 | 266
22-0091742 | Plumas | BIG MEADOWS 2101 | BIG MEADOWS 21012476 | Unknown | 2022-07-30 18:09 | 7/25 - 7/31 | 2022-07-30 21:20 | 191 | FTS | 265681 | 1391 | 42 | 31 | 15 | 0 | 0 | 0 | 191
22-0091739 | Fresno | TIVY VALLEY 1107 | TIVY VALLEY 1107822606 | Unknown | 2022-07-30 20:01 | 7/25 - 7/31 | 2022-07-31 08:16 | 735 | FTS | 142030 | 836 | 64 | 46 | 13 | 0 | 0 | 0 | 169.8923
22-0091768 | Contra Costa | RESEARCH 2102 | RESEARCH 2102446423 | Unknown | 2022-07-30 21:55 | 7/25 - 7/31 | 2022-07-31 09:34 | 699 | FTS | 49629 | 71 | 2 | 1 | 2 | 0 | 0 | 0 | 699
22-0091761 | Calaveras | CALAVERAS CEMENT 1101 | CALAVERAS CEMENT 110111188 | Animal | 2022-07-31 00:52 | 7/25 - 7/31 | 2022-07-31 04:10 | 198 | FTS | 151668 | 766 | 55 | 37 | 18 | 1 | 0 | 0 | 198
22-0091775 | Placer | HALSEY 1102 | HALSEY 110239104 | Unknown | 2022-07-31 06:11 | 7/25 - 7/31 | 2022-07-31 11:23 | 312 | FTS | 77207 | 899 | 72 | 48 | 20 | 7 | 0 | 11 | 85.881
22-0091817 | El Dorado | SHINGLE SPRINGS 2109 | SHINGLE SPRINGS 210911092 | Animal | 2022-07-31 12:38 | 7/25 - 7/31 | 2022-07-31 15:15 | 157 | FTS | 85575 | 915 | 47 | 36 | 10 | 1 | 0 | 24 | 93.5246
22-0091820 | Tuolumne | PEORIA 1701 | PEORIA 170176030 | Unknown | 2022-07-31 13:27 | 7/25 - 7/31 | 2022-07-31 16:16 | 169 | FTS | 32617 | 193 | 8 | 7 | 7 | 2 | 0 | 0 | 169
22-0091830 | Mariposa | BEAR VALLEY 2105 | BEAR VALLEY 210521160 | Unknown | 2022-07-31 17:32 | 7/25 - 7/31 | 2022-08-01 09:20 | 948 | FTS | 169057 | 230 | 14 | 10 | 1 | 0 | 0 | 0 | 735.0304
22-0091840 | Monterey | SOLEDAD 2105 | SOLEDAD 21053720 | Unknown | 2022-07-31 18:54 | 7/25 - 7/31 | 2022-07-31 21:51 | 177 | FTS | 14868 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 177
22-0091849 | El Dorado | DIAMOND SPRINGS 1105 | DIAMOND SPRINGS 11052102 | 3rd Party | 2022-07-31 21:23 | 7/25 - 7/31 | 2022-08-01 09:52 | 749 | FTS | 268666 | 1092 | 98 | 51 | 24 | 7 | 0 | 2 | 246.0311

## YTD EPSS Outages_Circuit
Circuit | Count of Outages
ALHAMBRA 1102 | 2
ALHAMBRA 1105 | 1
ALLEGHANY 1101 | 3
ALTO 1124 | 1
ALTO 1125 | 2
ANDERSON 1103 | 2
ANNAPOLIS 1101 | 1
ANTLER SUB | 1
APPLE HILL 1103 | 1
APPLE HILL 1104 | 1
APPLE HILL 2102 | 9
ATASCADERO 1101 | 2
ATASCADERO 1102 | 3
ATASCADERO 1103 | 5
AUBERRY 1101 | 4
AUBERRY 1102 | 5
AVENAL 2101 | 1
BALCH NO 1 1101 | 1
BANGOR 1101 | 2
BAYWOOD 1101 | 1
BEAR VALLEY 2101 | 4
BEAR VALLEY 2105 | 3
BELL 1107 | 1
BELL 1108 | 1
BELL 1109 | 1
BELLEVUE 2103 | 3
BEN LOMOND 0401 | 5
BEN LOMOND 1101 | 1
BIG BASIN 1101 | 5
BIG BASIN 1102 | 5
BIG BEND 1102 | 5
BIG MEADOWS 2101 | 2
BOLINAS 1101 | 1
BONNIE NOOK 1102 | 1
BRENTWOOD 2105 | 6
BRIDGEVILLE 1101 | 1
BROWNS VALLEY 1101 | 1
BRUNSWICK 1102 | 3
BRUNSWICK 1103 | 1
BRUNSWICK 1104 | 2
BRUNSWICK 1105 | 3
BRUNSWICK 1106 | 2
BRUNSWICK 1107 | 1
BRUNSWICK 1110 | 2
BUCKS CREEK 1103 | 1
BUELLTON 1101 | 3
BURNEY 1101 | 1
BUTTE 1105 | 1
CABRILLO 1103 | 1
CALAVERAS CEMENT 1101 | 4
CALISTOGA 1101 | 4
CALISTOGA 1102 | 3
CALISTOGA SUB | 1
CALPELLA 1101 | 2
CAMBRIA 1102 | 2
CAMP EVERS 2103 | 3
CAMP EVERS 2105 | 11
CAMP EVERS 2106 | 12
CANTUA 1103 | 1
CASTRO VALLEY 1110 | 1
CASTRO VALLEY 1111 | 1
CAYETANO 2111 | 1
CAYUCOS 1101 | 1
CAYUCOS 1102 | 2
CEDAR CREEK 1101 | 1
CHALLENGE 1101 | 2
CHESTER 1102 | 1
CHOLAME 2102 | 2
CLARK ROAD 1102 | 1
CLARKSVILLE 2103 | 1
CLARKSVILLE 2104 | 3
CLARKSVILLE 2106 | 2
CLARKSVILLE 2110 | 1
CLAY 1101 | 2
CLAY 1102 | 3
CLAY 1103 | 2
CLAYTON 2212 | 4
CLAYTON 2215 | 1
CLEAR LAKE 1101 | 1
CLEAR LAKE 1102 | 1
CLOVERDALE 1101 | 2
COALINGA NO 2 1105 | 2
COARSEGOLD 2102 | 1
COARSEGOLD 2103 | 1
COARSEGOLD 2104 | 2
COLUMBIA HILL 1101 | 4
COPPERMINE 1104 | 2
CORNING 1101 | 7
CORNING 1102 | 4
CORRAL 1101 | 6
CORRAL 1102 | 1
CORRAL 1103 | 1
CORTINA 1101 | 1
COTTONWOOD 1101 | 1
COTTONWOOD 1102 | 2
COTTONWOOD 1103 | 1
CRESCENT MILLS 2101 | 1
CURTIS 1702 | 3
CURTIS 1703 | 2
CURTIS 1704 | 3
CURTIS 1705 | 4
CUYAMA 1103 | 1
DEL MAR 2109 | 2
DEL MONTE 2104 | 2
DESCHUTES 1101 | 1
DESCHUTES 1104 | 1
DIAMOND SPRINGS 1103 | 3
DIAMOND SPRINGS 1105 | 2
DIAMOND SPRINGS 1106 | 2
DRUM 1101 | 2
DUNBAR 1101 | 2
DUNBAR 1102 | 2
DUNBAR 1103 | 1
DUNLAP 1102 | 7
DUNLAP 1103 | 1
EAST QUINCY 1101 | 1
ECHO SUMMIT 1101 | 1
EEL RIVER 1102 | 1
EL DORADO PH 2101 | 2
ELECTRA 1101 | 3
ELECTRA 1102 | 1
ELK CREEK 1101 | 4
EMERALD LAKE 0401 | 3
FAIRVIEW 2207 | 4
FITCH MOUNTAIN 1113 | 5
FOOTHILL 1102 | 2
FORESTHILL 1101 | 2
FORT ROSS 1121 | 1
FREMONT 1104 | 1
FROGTOWN 1701 | 1
FROGTOWN 1702 | 1
FRUITLAND 1142 | 1
FULTON 1102 | 1
FULTON 1107 | 1
GABILAN 1101 | 2
GANSNER 1101 | 2
GARBERVILLE 1101 | 1
GARBERVILLE 1102 | 4
GERBER 1102 | 1
GEYSERVILLE 1101 | 3
GEYSERVILLE 1102 | 4
GIRVAN 1101 | 2
GIRVAN 1102 | 3
GREEN VALLEY 2101 | 6
GREENBRAE 1102 | 1
GUSTINE 1102 | 1
HALF MOON BAY 1101 | 2
HALF MOON BAY 1103 | 6
HALSEY 1101 | 3
HALSEY 1102 | 2
HAMILTON BRANCH 1101 | 2
HARTLEY 1101 | 2
HICKS 2101 | 6
HICKS 2103 | 1
HIGGINS 1103 | 2
HIGGINS 1104 | 3
HIGGINS 1107 | 1
HIGGINS 1109 | 2
HIGGINS 1110 | 1
HIGHLANDS 1102 | 4
HOLLISTER 2102 | 2
HOLLISTER 2105 | 2
HOLLISTER 2106 | 4
HOOPA 1101 | 5
HOPLAND 1101 | 5
HORSESHOE 1101 | 1
HORSESHOE 1104 | 2
JAMESON 1102 | 2
JAMESON 1105 | 3
JESSUP 1101 | 1
JESSUP 1102 | 1
JESSUP 1103 | 1
JOLON 1102 | 1
JOLON 1103 | 3
KANAKA 1101 | 1
KERCKHOFF 1101 | 1
KING CITY 1102 | 1
KING CITY 1103 | 2
KIRKER 2104 | 1
KONOCTI 1102 | 5
KONOCTI 1108 | 1
LAKEVILLE 1102 | 3
LAKEWOOD 1103 | 2
LAKEWOOD 2107 | 1
LAKEWOOD 2227 | 1
LAMONT 1102 | 1
LAMONT 1104 | 2
LAS GALLINAS A 1105 | 1
LAS GALLINAS A 1107 | 1
LAS POSITAS 2108 | 1
LAURELES 1111 | 3
LAURELES 1112 | 1
LAYTONVILLE 1101 | 1
LAYTONVILLE 1102 | 1
LINCOLN 1104 | 5
LLAGAS 2101 | 1
LLAGAS 2107 | 1
LOCKEFORD 2102 | 1
LOGAN CREEK 2102 | 4
LOS GATOS 1101 | 1
LOS GATOS 1106 | 5
LOS GATOS 1107 | 1
LOS GATOS 1108 | 1
LOS MOLINOS 1101 | 1
LOS OSITOS 2102 | 1
LOS OSITOS 2103 | 4
LOYOLA 1102 | 1
LUCERNE 1103 | 4
MADISON 1105 | 2
MADISON 2101 | 10
MAGUNDEN 1108 | 3
MARIPOSA 2101 | 3
MARIPOSA 2102 | 4
MC ARTHUR 1101 | 6
MC KEE 1107 | 3
MC KEE 1111 | 1
MENLO 1102 | 2
MERCED FALLS 1102 | 2
MIDDLETOWN 1101 | 2
MIDDLETOWN 1102 | 1
MILPITAS 1105 | 1
MILPITAS 1108 | 1
MIRABEL 1101 | 6
MIRABEL 1102 | 1
MIWUK 1701 | 1
MIWUK 1702 | 3
MOLINO 1102 | 2
MONTE RIO 1111 | 3
MONTE RIO 1113 | 1
MONTICELLO 1101 | 4
MORAGA 1102 | 3
MORAGA 1105 | 2
MORGAN HILL 2104 | 1
MORGAN HILL 2105 | 3
MORGAN HILL 2109 | 1
MORGAN HILL 2111 | 4
MORRO BAY 1101 | 1
MOUNTAIN QUARRIES 2101 | 2
NAPA 1110 | 1
NAPA 1112 | 1
NARROWS 2102 | 5
NARROWS 2105 | 8
NORTH BRANCH 1101 | 4
NORTH DUBLIN 2103 | 3
NORTH TOWER 2101 | 1
NOVATO 1104 | 1
OAKHURST 1101 | 2
OAKHURST 1102 | 1
OAKHURST 1103 | 2
OAKLAND X 1104 | 1
OCEANO 1104 | 6
OILFIELDS 1103 | 4
OLEMA 1101 | 1
OLETA 1101 | 1
OLETA 1102 | 2
OREGON TRAIL 1102 | 2
OREGON TRAIL 1103 | 1
ORINDA 0401 | 1
ORO FINO 1101 | 3
ORO FINO 1102 | 4
OROSI 1102 | 2
OTTER 1101 | 2
PANORAMA 1101 | 1
PANORAMA 1102 | 6
PARADISE 1104 | 1
PARADISE 1106 | 2
PASO ROBLES 1103 | 1
PASO ROBLES 1104 | 1
PAUL SWEET 2104 | 2
PAUL SWEET 2105 | 3
PAUL SWEET 2106 | 3
PAUL SWEET 2107 | 2
PEABODY 2106 | 1
PEABODY 2113 | 1
PENRYN 1103 | 5
PENRYN 1105 | 4
PENRYN 1106 | 1
PENRYN 1107 | 1
PEORIA 1701 | 3
PEORIA 1704 | 2
PEORIA 1705 | 1
PERRY 1101 | 1
PETALUMA C 1108 | 1
PETALUMA C 1109 | 1
PHILO 1101 | 2
PHILO 1102 | 1
PIKE CITY 1101 | 2
PINE GROVE 1102 | 2
PIT NO 1 1101 | 1
PIT NO 3 2101 | 1
PIT NO 5 1101 | 1
PLACER 1103 | 1
PLACERVILLE 2106 | 5
POINT MORETTI 1101 | 2
POSO MOUNTAIN 2101 | 10
POSO MOUNTAIN 2103 | 2
POSO MOUNTAIN 2104 | 1
POTTER VALLEY P H 1105 | 1
PUEBLO 1104 | 1
PUEBLO 1105 | 1
PUEBLO 2103 | 1
PUEBLO 2104 | 5
PURISIMA 1101 | 1
PUTAH CREEK 1105 | 4
RADUM 1105 | 1
RAWSON 1103 | 1
RED BLUFF 1103 | 1
RED BLUFF 1104 | 4
REDBUD 1101 | 1
REDBUD 1102 | 3
RESEARCH 2102 | 1
RESERVATION ROAD 1101 | 1
RESERVATION ROAD 1102 | 6
RINCON 1101 | 1
RIO DELL 1102 | 2
RISING RIVER 1101 | 2
ROB ROY 2104 | 5
ROB ROY 2105 | 4
ROSSMOOR 1102 | 1
ROSSMOOR 1106 | 1
SALT SPRINGS 2101 | 1
SAN ARDO 1101 | 1
SAN CARLOS 1104 | 1
SAN JOAQUIN #3 1101 | 1
SAN JOAQUIN #3 1102 | 2
SAN JUSTO 1101 | 3
SAN LUIS OBISPO 1101 | 1
SAN LUIS OBISPO 1103 | 1
SAN LUIS OBISPO 1107 | 10
SAN MIGUEL 1106 | 2
SAN RAFAEL 1104 | 1
SAN RAFAEL 1106 | 1
SAN RAFAEL 1107 | 1
SAN RAFAEL 1108 | 1
SAN RAMON 2103 | 3
SAN RAMON 2107 | 2
SAND CREEK 1103 | 2
SANTA ROSA A 1107 | 1
SANTA YNEZ 1101 | 1
SANTA YNEZ 1102 | 4
SANTA YNEZ 1104 | 2
SARATOGA 1103 | 1
SARATOGA 1104 | 1
SARATOGA 1106 | 2
SARATOGA 1107 | 1
SHADY GLEN 1102 | 1
SHINGLE SPRINGS 1104 | 1
SHINGLE SPRINGS 2105 | 3
SHINGLE SPRINGS 2108 | 6
SHINGLE SPRINGS 2109 | 6
SILVERADO 2102 | 6
SILVERADO 2103 | 2
SILVERADO 2104 | 6
SILVERADO 2105 | 4
SISQUOC 1102 | 3
SMARTVILLE SUB | 1
SOBRANTE 1101 | 1
SOBRANTE 1102 | 2
SOBRANTE 1103 | 1
SOLEDAD 2101 | 1
SOLEDAD 2102 | 2
SOLEDAD 2105 | 3
SONOMA 1102 | 5
SONOMA 1105 | 4
SONOMA 1107 | 2
SPRING GAP 1702 | 1
STAFFORD 1101 | 2
STAFFORD 1102 | 5
STANISLAUS 1701 | 4
STANISLAUS 1702 | 2
STELLING 1109 | 1
STELLING 1110 | 1
STILLWATER 1101 | 1
STILLWATER 1102 | 3
STONE CORRAL 1108 | 3
STONE CORRAL 1110 | 3
SUNOL 1101 | 1
SYCAMORE CREEK 1109 | 2
TASSAJARA 2103 | 2
TASSAJARA 2108 | 1
TASSAJARA 2113 | 2
TEMPLETON 2110 | 2
TEMPLETON 2111 | 4
TEMPLETON 2112 | 3
TEMPLETON 2113 | 6
TIGER CREEK 0201 | 1
TIVY VALLEY 1107 | 7
TRES PINOS 1111 | 2
TYLER 1105 | 6
UKIAH 1111 | 1
UKIAH 1113 | 1
UKIAH 1114 | 1
UKIAH 1115 | 1
UPPER LAKE 1101 | 2
VACA DIXON 1105 | 3
VACAVILLE 1104 | 1
VACAVILLE 1108 | 2
VASCO 1102 | 2
VINEYARD 2108 | 3
VOLTA 1101 | 4
VOLTA 1102 | 1
WEST POINT 1102 | 1
WESTLEY 1103 | 1
WHEATLAND 1105 | 3
WHITMORE 1101 | 2
WILLITS 1104 | 4
WILLOW CREEK 1103 | 2
WILLOW PASS 1101 | 1
WILLOW PASS 2108 | 1
WISE 1101 | 3
WISE 1102 | 3
WOODACRE 1101 | 1
WOODACRE 1102 | 5
WOODSIDE 1101 | 1
WOODWARD 2108 | 1
WYANDOTTE 1102 | 1
WYANDOTTE 1103 | 1
WYANDOTTE 1107 | 1
WYANDOTTE 1109 | 2
WYANDOTTE 1110 | 2
ZACA 1101 | 1
ZACA 1102 | 1
Total Result | 964

## YTD EPSS Outages_CESO
Circuit | Months | Sum of CESO
ALHAMBRA 1102 |  | 184660
| Jun | 137710
| Jul | 46950
ALHAMBRA 1105 |  | 280468
| Jun | 280468
ALLEGHANY 1101 |  | 17185
| Jun | 9306
| Jul | 7879
ALTO 1124 |  | 3000
| May | 3000
ALTO 1125 |  | 309979
| May | 4816
| Jul | 305163
ANDERSON 1103 |  | 24565
| Jul | 24565
ANNAPOLIS 1101 |  | 104279
| Jun | 104279
ANTLER SUB |  | 71735
| Jun | 71735
APPLE HILL 1103 |  | 32500
| Jun | 32500
APPLE HILL 1104 |  | 190008
| Jun | 190008
APPLE HILL 2102 |  | 4950953
| May | 879429
| Jun | 2439011
| Jul | 1632513
ATASCADERO 1101 |  | 431740
| May | 237912
| Jul | 193828
ATASCADERO 1102 |  | 781744
| Jun | 324751
| Jul | 456993
ATASCADERO 1103 |  | 429363
| Apr | 171099
| Jun | 229914
| Jul | 28350
AUBERRY 1101 |  | 1243630
| Jun | 1202185
| Jul | 41445
AUBERRY 1102 |  | 401271
| Jun | 148849
| Jul | 252422
AVENAL 2101 |  | 20604
| Jul | 20604
BALCH NO 1 1101 |  | 93897
| Jun | 93897
BANGOR 1101 |  | 71160
| Jun | 71160
BAYWOOD 1101 |  | 75690
| Apr | 75690
BEAR VALLEY 2101 |  | 393670
| Jun | 286011
| Jul | 107659
BEAR VALLEY 2105 |  | 380256
| May | 92920
| Jul | 287336
BELL 1107 |  | 76886
| Jun | 76886
BELL 1108 |  | 16060
| Jul | 16060
BELL 1109 |  | 63196
| Jul | 63196
BELLEVUE 2103 |  | 286858
| Jul | 286858
BEN LOMOND 0401 |  | 270659
| May | 18414
| Jun | 120374
| Jul | 131871
BEN LOMOND 1101 |  | 297804
| Jul | 297804
BIG BASIN 1101 |  | 875282
| Jun | 780642
| Jul | 94640
BIG BASIN 1102 |  | 368747
| Jun | 106056
| Jul | 262691
BIG BEND 1102 |  | 285119
| May | 65383
| Jun | 50909
| Jul | 168827
BIG MEADOWS 2101 |  | 341683
| Jun | 76002
| Jul | 265681
BOLINAS 1101 |  | 564492
| Jul | 564492
BONNIE NOOK 1102 |  | 150335
| Jun | 150335
BRENTWOOD 2105 |  | 312146
| Jun | 276410
| Jul | 35736
BRIDGEVILLE 1101 |  | 64638
| Jul | 64638
BROWNS VALLEY 1101 |  | 11235
| Jul | 11235
BRUNSWICK 1102 |  | 482614
| Jun | 482614
BRUNSWICK 1103 |  | 353146
| Jun | 353146
BRUNSWICK 1104 |  | 245234
| Jun | 244333
| Jul | 901
BRUNSWICK 1105 |  | 773770
| Jun | 597655
| Jul | 176115
BRUNSWICK 1106 |  | 655543
| Jun | 577585
| Jul | 77958
BRUNSWICK 1107 |  | 566873
| Jul | 566873
BRUNSWICK 1110 |  | 677935
| Jul | 677935
BUCKS CREEK 1103 |  | 178742
| Jun | 178742
BUELLTON 1101 |  | 115323
| Jun | 20592
| Jul | 94731
BURNEY 1101 |  | 147133
| Jul | 147133
BUTTE 1105 |  | 44865
| Jun | 44865
CABRILLO 1103 |  | 23755
| Jul | 23755
CALAVERAS CEMENT 1101 |  | 849278
| May | 35360
| Jul | 813918
CALISTOGA 1101 |  | 135233
| Jul | 135233
CALISTOGA 1102 |  | 978440
| May | 571333
| Jun | 407107
CALISTOGA SUB |  | 522092
| May | 522092
CALPELLA 1101 |  | 216915
| Jul | 216915
CAMBRIA 1102 |  | 345654
| Apr | 97170
| Jul | 248484
CAMP EVERS 2103 |  | 744608
| Jun | 524738
| Jul | 219870
CAMP EVERS 2105 |  | 4317957
| May | 2840
| Jun | 3251352
| Jul | 1063765
CAMP EVERS 2106 |  | 3715238
| May | 79883
| Jun | 209706
| Jul | 3425649
CANTUA 1103 |  | 12596
| Mar | 12596
CASTRO VALLEY 1110 |  | 158288
| Jun | 158288
CASTRO VALLEY 1111 |  | 72470
| Jun | 72470
CAYETANO 2111 |  | 467594
| Jul | 467594
CAYUCOS 1101 |  | 69720
| Jun | 69720
CAYUCOS 1102 |  | 65628
| Jun | 10300
| Jul | 55328
CEDAR CREEK 1101 |  | 53732
| Jul | 53732
CHALLENGE 1101 |  | 770479
| Jun | 770479
CHESTER 1102 |  | 26600
| Jun | 26600
CHOLAME 2102 |  | 98789
| May | 63473
| Jun | 35316
CLARK ROAD 1102 |  | 4221
| May | 4221
CLARKSVILLE 2103 |  | 42969
| Jun | 42969
CLARKSVILLE 2104 |  | 286180
| Jul | 286180
CLARKSVILLE 2106 |  | 1329360
| Jun | 1137058
| Jul | 192302
CLARKSVILLE 2110 |  | 37776
| May | 37776
CLAY 1101 |  | 63558
| May | 22266
| Jun | 41292
CLAY 1102 |  | 390
| May | 117
| Jul | 273
CLAY 1103 |  | 50996
| Jun | 16748
| Jul | 34248
CLAYTON 2212 |  | 563680
| Jun | 351520
| Jul | 212160
CLAYTON 2215 |  | 283637
| Jul | 283637
CLEAR LAKE 1101 |  | 379376
| Jul | 379376
CLEAR LAKE 1102 |  | 5194
| Jun | 5194
CLOVERDALE 1101 |  | 627150
| Jun | 619607
| Jul | 7543
COALINGA NO 2 1105 |  | 67704
| Apr | 14154
| Jul | 53550
COARSEGOLD 2102 |  | 351614
| Jun | 351614
COARSEGOLD 2103 |  | 297255
| Jun | 297255
COARSEGOLD 2104 |  | 635261
| May | 429158
| Jun | 206103
COLUMBIA HILL 1101 |  | 208131
| May | 139901
| Jul | 68230
COPPERMINE 1104 |  | 81514
| May | 81514
CORNING 1101 |  | 261378
| Jun | 172807
| Jul | 88571
CORNING 1102 |  | 332387
| Apr | 43969
| May | 235314
| Jun | 53104
CORRAL 1101 |  | 581719
| May | 118732
| Jun | 462987
CORRAL 1102 |  | 66200
| Jun | 66200
CORRAL 1103 |  | 137416
| Jul | 137416
CORTINA 1101 |  | 1251
| Jun | 1251
COTTONWOOD 1101 |  | 54531
| May | 54531
COTTONWOOD 1102 |  | 178628
| Jun | 178628
COTTONWOOD 1103 |  | 77420
| Jun | 77420
CRESCENT MILLS 2101 |  | 179036
| Jul | 179036
CURTIS 1702 |  | 421055
| Jun | 98280
| Jul | 322775
CURTIS 1703 |  | 381853
| Jul | 381853
CURTIS 1704 |  | 717812
| Jun | 287052
| Jul | 430760
CURTIS 1705 |  | 181494
| Jun | 121986
| Jul | 59508
CUYAMA 1103 |  | 26090
| Apr | 26090
DEL MAR 2109 |  | 607980
| Jul | 607980
DEL MONTE 2104 |  | 520871
| Jun | 520871
DESCHUTES 1101 |  | 63641
| Jun | 63641
DESCHUTES 1104 |  | 42963
| May | 42963
DIAMOND SPRINGS 1103 |  | 340306
| Jul | 340306
DIAMOND SPRINGS 1105 |  | 386123
| May | 117457
| Jul | 268666
DIAMOND SPRINGS 1106 |  | 65565
| Jun | 45760
| Jul | 19805
DRUM 1101 |  | 138775
| Jun | 102438
| Jul | 36337
DUNBAR 1101 |  | 74424
| May | 9480
| Jun | 64944
DUNBAR 1102 |  | 413138
| Jun | 295321
| Jul | 117817
DUNBAR 1103 |  | 117528
| Jul | 117528
DUNLAP 1102 |  | 504035
| May | 166528
| Jun | 299737
| Jul | 37770
DUNLAP 1103 |  | 165415
| Jun | 165415
EAST QUINCY 1101 |  | 91816
| Jul | 91816
ECHO SUMMIT 1101 |  | 11900
| Jun | 11900
EEL RIVER 1102 |  | 38661
| Jun | 38661
EL DORADO PH 2101 |  | 342751
| Jun | 319351
| Jul | 23400
ELECTRA 1101 |  | 639821
| May | 99680
| Jun | 469119
| Jul | 71022
ELECTRA 1102 |  | 77575
| Jun | 77575
ELK CREEK 1101 |  | 494464
| Apr | 275455
| May | 169169
| Jun | 49840
EMERALD LAKE 0401 |  | 564271
| Jun | 96359
| Jul | 467912
FAIRVIEW 2207 |  | 2402733
| Jun | 2402733
FITCH MOUNTAIN 1113 |  | 322585
| May | 241253
| Jun | 61442
| Jul | 19890
FOOTHILL 1102 |  | 507735
| Jun | 183024
| Jul | 324711
FORESTHILL 1101 |  | 471994
| Jul | 471994
FORT ROSS 1121 |  | 3975
| Jun | 3975
FREMONT 1104 |  | 7871
| Jun | 7871
FROGTOWN 1701 |  | 156858
| Jul | 156858
FROGTOWN 1702 |  | 185292
| Jul | 185292
FRUITLAND 1142 |  | 92331
| Jul | 92331
FULTON 1102 |  | 137651
| Jul | 137651
FULTON 1107 |  | 63256
| Jul | 63256
GABILAN 1101 |  | 370850
| Jul | 370850
GANSNER 1101 |  | 58252
| Jun | 3456
| Jul | 54796
GARBERVILLE 1101 |  | 18764
| Jul | 18764
GARBERVILLE 1102 |  | 621564
| Jun | 356
| Jul | 621208
GERBER 1102 |  | 18980
| May | 18980
GEYSERVILLE 1101 |  | 93386
| May | 93386
GEYSERVILLE 1102 |  | 366348
| Jun | 235176
| Jul | 131172
GIRVAN 1101 |  | 291591
| May | 216130
| Jun | 75461
GIRVAN 1102 |  | 395597
| May | 105971
| Jun | 282772
| Jul | 6854
GREEN VALLEY 2101 |  | 643049
| Jun | 104055
| Jul | 538994
GREENBRAE 1102 |  | 541848
| Jun | 541848
GUSTINE 1102 |  | 90528
| Jul | 90528
HALF MOON BAY 1101 |  | 47232
| Jun | 47232
HALF MOON BAY 1103 |  | 1068270
| Jun | 1068270
HALSEY 1101 |  | 201870
| Jul | 201870
HALSEY 1102 |  | 282849
| May | 205642
| Jul | 77207
HAMILTON BRANCH 1101 |  | 39662
| Jul | 39662
HARTLEY 1101 |  | 322384
| Jun | 322384
HICKS 2101 |  | 3179434
| May | 547115
| Jun | 978251
| Jul | 1654068
HICKS 2103 |  | 308764
| Jul | 308764
HIGGINS 1103 |  | 182960
| Jul | 182960
HIGGINS 1104 |  | 728213
| Jun | 728213
HIGGINS 1107 |  | 27706
| Jul | 27706
HIGGINS 1109 |  | 120578
| Jul | 120578
HIGGINS 1110 |  | 19336
| Jun | 19336
HIGHLANDS 1102 |  | 611969
| Jun | 345730
| Jul | 266239
HOLLISTER 2102 |  | 8869
| Jul | 8869
HOLLISTER 2105 |  | 60173
| Jun | 60173
HOLLISTER 2106 |  | 152653
| Apr | 24149
| May | 31060
| Jun | 97444
HOOPA 1101 |  | 744350
| Jun | 550997
| Jul | 193353
HOPLAND 1101 |  | 322627
| Jun | 266404
| Jul | 56223
HORSESHOE 1101 |  | 383185
| Jun | 383185
HORSESHOE 1104 |  | 65913
| Jun | 33384
| Jul | 32529
JAMESON 1102 |  | 273048
| May | 206694
| Jul | 66354
JAMESON 1105 |  | 110919
| Jun | 32476
| Jul | 78443
JESSUP 1101 |  | 171400
| Apr | 171400
JESSUP 1102 |  | 148685
| Jun | 148685
JESSUP 1103 |  | 69668
| Jul | 69668
JOLON 1102 |  | 92621
| Jun | 92621
JOLON 1103 |  | 13892
| May | 9132
| Jul | 4760
KANAKA 1101 |  | 156651
| May | 156651
KERCKHOFF 1101 |  | 11580
| Jun | 11580
KING CITY 1102 |  | 160
| Jul | 160
KING CITY 1103 |  | 675008
| May | 264244
| Jun | 410764
KIRKER 2104 |  | 992190
| May | 992190
KONOCTI 1102 |  | 256443
| Jul | 256443
KONOCTI 1108 |  | 42018
| Jul | 42018
LAKEVILLE 1102 |  | 77539
| Mar | 7663
| Jun | 7378
| Jul | 62498
LAKEWOOD 1103 |  | 8268
| Jun | 3978
| Jul | 4290
LAKEWOOD 2107 |  | 349665
| Jun | 349665
LAKEWOOD 2227 |  | 233345
| Jul | 233345
LAMONT 1102 |  | 22176
| Jun | 22176
LAMONT 1104 |  | 13612
| Jun | 13612
LAS GALLINAS A 1105 |  | 99448
| Jul | 99448
LAS GALLINAS A 1107 |  | 70052
| Jun | 70052
LAS POSITAS 2108 |  | 226041
| Jun | 226041
LAURELES 1111 |  | 277267
| Jul | 277267
LAURELES 1112 |  | 114996
| Jul | 114996
LAYTONVILLE 1101 |  | 6533
| Jun | 6533
LAYTONVILLE 1102 |  | 28327
| Jun | 28327
LINCOLN 1104 |  | 279499
| May | 104281
| Jun | 63670
| Jul | 111548
LLAGAS 2101 |  | 23276
| May | 23276
LLAGAS 2107 |  | 14074
| Jul | 14074
LOCKEFORD 2102 |  | 80192
| May | 80192
LOGAN CREEK 2102 |  | 115893
| Apr | 14348
| May | 101545
LOS GATOS 1101 |  | 152152
| Jun | 152152
LOS GATOS 1106 |  | 491925
| May | 35304
| Jun | 275860
| Jul | 180761
LOS GATOS 1107 |  | 163726
| Jun | 163726
LOS GATOS 1108 |  | 7442
| Apr | 7442
LOS MOLINOS 1101 |  | 20034
| Jun | 20034
LOS OSITOS 2102 |  | 1520
| Jun | 1520
LOS OSITOS 2103 |  | 634391
| Jun | 634391
LOYOLA 1102 |  | 9126
| Jul | 9126
LUCERNE 1103 |  | 412481
| Jul | 412481
MADISON 1105 |  | 185423
| Apr | 34412
| Jun | 151011
MADISON 2101 |  | 2726756
| Apr | 238602
| May | 1817964
| Jun | 573145
| Jul | 97045
MAGUNDEN 1108 |  | 37336
| Jun | 31512
| Jul | 5824
MARIPOSA 2101 |  | 605282
| May | 192282
| Jul | 413000
MARIPOSA 2102 |  | 874580
| May | 377058
| Jun | 265162
| Jul | 232360
MC ARTHUR 1101 |  | 711089
| Jun | 134411
| Jul | 576678
MC KEE 1107 |  | 142181
| Jun | 57335
| Jul | 84846
MC KEE 1111 |  | 20536
| Jun | 20536
MENLO 1102 |  | 88372
| Jun | 88372
MERCED FALLS 1102 |  | 389283
| Jul | 389283
MIDDLETOWN 1101 |  | 236530
| Mar | 233710
| Jul | 2820
MIDDLETOWN 1102 |  | 34666
| May | 34666
MILPITAS 1105 |  | 172205
| Jun | 172205
MILPITAS 1108 |  | 236044
| Jun | 236044
MIRABEL 1101 |  | 273051
| Jun | 45979
| Jul | 227072
MIRABEL 1102 |  | 15789
| Jul | 15789
MIWUK 1701 |  | 282972
| May | 282972
MIWUK 1702 |  | 269353
| May | 96063
| Jun | 85480
| Jul | 87810
MOLINO 1102 |  | 743823
| Jun | 149046
| Jul | 594777
MONTE RIO 1111 |  | 400715
| May | 40303
| Jun | 360412
MONTE RIO 1113 |  | 67360
| May | 67360
MONTICELLO 1101 |  | 450201
| May | 286786
| Jun | 92996
| Jul | 70419
MORAGA 1102 |  | 1005843
| Jun | 419247
| Jul | 586596
MORAGA 1105 |  | 589512
| Jun | 589512
MORGAN HILL 2104 |  | 69537
| May | 69537
MORGAN HILL 2105 |  | 418687
| Jun | 347644
| Jul | 71043
MORGAN HILL 2109 |  | 504775
| Jun | 504775
MORGAN HILL 2111 |  | 2189246
| May | 119679
| Jun | 1828274
| Jul | 241293
MORRO BAY 1101 |  | 83058
| Jun | 83058
MOUNTAIN QUARRIES 2101 |  | 232290
| May | 145611
| Jul | 86679
NAPA 1110 |  | 3648
| Jun | 3648
NAPA 1112 |  | 22116
| Jun | 22116
NARROWS 2102 |  | 1539163
| May | 712544
| Jun | 711827
| Jul | 114792
NARROWS 2105 |  | 2474334
| May | 1240532
| Jun | 901505
| Jul | 332297
NORTH BRANCH 1101 |  | 323946
| Jul | 323946
NORTH DUBLIN 2103 |  | 2430266
| Jun | 1772889
| Jul | 657377
NORTH TOWER 2101 |  | 123728
| Jul | 123728
NOVATO 1104 |  | 18377
| Jul | 18377
OAKHURST 1101 |  | 849416
| May | 503732
| Jul | 345684
OAKHURST 1102 |  | 408281
| Jun | 408281
OAKHURST 1103 |  | 1448696
| Jun | 1030802
| Jul | 417894
OAKLAND X 1104 |  | 34552
| Jun | 34552
OCEANO 1104 |  | 936438
| May | 11180
| Jun | 505105
| Jul | 420153
OILFIELDS 1103 |  | 831283
| May | 45928
| Jun | 744211
| Jul | 41144
OLEMA 1101 |  | 22601
| Jun | 22601
OLETA 1101 |  | 442339
| Jul | 442339
OLETA 1102 |  | 492695
| Jun | 287096
| Jul | 205599
OREGON TRAIL 1102 |  | 262771
| Jun | 215090
| Jul | 47681
OREGON TRAIL 1103 |  | 314633
| Jul | 314633
ORINDA 0401 |  | 53846
| Jul | 53846
ORO FINO 1101 |  | 753303
| May | 257544
| Jun | 495759
ORO FINO 1102 |  | 259141
| Jun | 109457
| Jul | 149684
OROSI 1102 |  | 499805
| Jun | 499805
OTTER 1101 |  | 55483
| Apr | 55483
PANORAMA 1101 |  | 162735
| Jun | 162735
PANORAMA 1102 |  | 230128
| May | 12658
| Jun | 18334
| Jul | 199136
PARADISE 1104 |  | 188772
| May | 188772
PARADISE 1106 |  | 69866
| May | 18180
| Jun | 51686
PASO ROBLES 1103 |  | 86146
| Jul | 86146
PASO ROBLES 1104 |  | 260196
| Jun | 260196
PAUL SWEET 2104 |  | 56232
| Jun | 27324
| Jul | 28908
PAUL SWEET 2105 |  | 1163364
| Jun | 1163364
PAUL SWEET 2106 |  | 974488
| Jun | 895921
| Jul | 78567
PAUL SWEET 2107 |  | 32555
| Jun | 32555
PEABODY 2106 |  | 247376
| Jul | 247376
PEABODY 2113 |  | 767512
| Jun | 767512
PENRYN 1103 |  | 334114
| May | 152205
| Jun | 146603
| Jul | 35306
PENRYN 1105 |  | 322644
| Jun | 235403
| Jul | 87241
PENRYN 1106 |  | 164246
| Jul | 164246
PENRYN 1107 |  | 159842
| Jul | 159842
PEORIA 1701 |  | 441647
| Jun | 165696
| Jul | 275951
PEORIA 1704 |  | 880814
| Jun | 222794
| Jul | 658020
PEORIA 1705 |  | 43142
| Jun | 43142
PERRY 1101 |  | 194376
| Apr | 194376
PETALUMA C 1108 |  | 78925
| Jun | 78925
PETALUMA C 1109 |  | 8964
| Jun | 8964
PHILO 1101 |  | 471857
| Jun | 25272
| Jul | 446585
PHILO 1102 |  | 482079
| Jun | 482079
PIKE CITY 1101 |  | 176615
| May | 176461
| Jul | 154
PINE GROVE 1102 |  | 329563
| Jul | 329563
PIT NO 1 1101 |  | 302836
| Jul | 302836
PIT NO 3 2101 |  | 45375
| Jun | 45375
PIT NO 5 1101 |  | 443
| Jul | 443
PLACER 1103 |  | 52933
| Jul | 52933
PLACERVILLE 2106 |  | 1570529
| May | 600127
| Jun | 698182
| Jul | 272220
POINT MORETTI 1101 |  | 39259
| Jun | 6853
| Jul | 32406
POSO MOUNTAIN 2101 |  | 306033
| May | 10640
| Jun | 283969
| Jul | 11424
POSO MOUNTAIN 2103 |  | 18981
| Jun | 18981
POSO MOUNTAIN 2104 |  | 2133
| Jul | 2133
POTTER VALLEY P H 1105 |  | 2520
| Jun | 2520
PUEBLO 1104 |  | 65676
| Jun | 65676
PUEBLO 1105 |  | 30248
| Jul | 30248
PUEBLO 2103 |  | 99554
| Jun | 99554
PUEBLO 2104 |  | 357684
| May | 57024
| Jun | 215745
| Jul | 84915
PURISIMA 1101 |  | 285444
| Jul | 285444
PUTAH CREEK 1105 |  | 9680
| Apr | 860
| May | 8820
RADUM 1105 |  | 25441
| Jun | 25441
RAWSON 1103 |  | 113348
| May | 113348
RED BLUFF 1103 |  | 587311
| Apr | 587311
RED BLUFF 1104 |  | 792823
| May | 390795
| Jun | 4708
| Jul | 397320
REDBUD 1101 |  | 39440
| Jun | 39440
REDBUD 1102 |  | 675916
| Jun | 200879
| Jul | 475037
RESEARCH 2102 |  | 49629
| Jul | 49629
RESERVATION ROAD 1101 |  | 116276
| Jul | 116276
RESERVATION ROAD 1102 |  | 595806
| Jun | 299647
| Jul | 296159
RINCON 1101 |  | 1603636
| Jun | 1603636
RIO DELL 1102 |  | 177178
| Jul | 177178
RISING RIVER 1101 |  | 449557
| Jun | 363384
| Jul | 86173
ROB ROY 2104 |  | 572176
| Jun | 272609
| Jul | 299567
ROB ROY 2105 |  | 793099
| Jun | 739199
| Jul | 53900
ROSSMOOR 1102 |  | 795524
| Jul | 795524
ROSSMOOR 1106 |  | 215185
| Jul | 215185
SALT SPRINGS 2101 |  | 301600
| Jun | 301600
SAN ARDO 1101 |  | 2492
| May | 2492
SAN CARLOS 1104 |  | 13556
| Jun | 13556
SAN JOAQUIN #3 1101 |  | 166898
| May | 166898
SAN JOAQUIN #3 1102 |  | 132064
| Jun | 132064
SAN JUSTO 1101 |  | 47490
| Jun | 47490
SAN LUIS OBISPO 1101 |  | 41209
| Jun | 41209
SAN LUIS OBISPO 1103 |  | 34335
| Jul | 34335
SAN LUIS OBISPO 1107 |  | 939348
| May | 194739
| Jun | 744609
SAN MIGUEL 1106 |  | 43878
| May | 23718
| Jun | 20160
SAN RAFAEL 1104 |  | 43586
| Jun | 43586
SAN RAFAEL 1106 |  | 214132
| Jun | 214132
SAN RAFAEL 1107 |  | 13545
| Jun | 13545
SAN RAFAEL 1108 |  | 648121
| Jun | 648121
SAN RAMON 2103 |  | 235759
| Jun | 235759
SAN RAMON 2107 |  | 725792
| Jun | 725792
SAND CREEK 1103 |  | 224010
| Jun | 224010
SANTA ROSA A 1107 |  | 142038
| Jun | 142038
SANTA YNEZ 1101 |  | 25344
| Jun | 25344
SANTA YNEZ 1102 |  | 211663
| May | 53064
| Jun | 158599
SANTA YNEZ 1104 |  | 26417
| May | 18216
| Jun | 8201
SARATOGA 1103 |  | 81464
| Jun | 81464
SARATOGA 1104 |  | 132102
| Jun | 132102
SARATOGA 1106 |  | 157159
| Jun | 45583
| Jul | 111576
SARATOGA 1107 |  | 247585
| Jun | 247585
SHADY GLEN 1102 |  | 67805
| Jul | 67805
SHINGLE SPRINGS 1104 |  | 57330
| Jun | 57330
SHINGLE SPRINGS 2105 |  | 491583
| Jun | 159936
| Jul | 331647
SHINGLE SPRINGS 2108 |  | 1493765
| May | 1096921
| Jun | 40320
| Jul | 356524
SHINGLE SPRINGS 2109 |  | 1810384
| Jun | 580858
| Jul | 1229526
SILVERADO 2102 |  | 478626
| Apr | 87966
| May | 174664
| Jun | 149824
| Jul | 66172
SILVERADO 2103 |  | 14525
| Jun | 14525
SILVERADO 2104 |  | 2699923
| May | 1511774
| Jun | 1072598
| Jul | 115551
SILVERADO 2105 |  | 64608
| Jun | 64608
SISQUOC 1102 |  | 77578
| Jan | 24180
| Jun | 53398
SMARTVILLE SUB |  | 30623
| May | 30623
SOBRANTE 1101 |  | 59050
| May | 59050
SOBRANTE 1102 |  | 134320
| Jun | 100448
| Jul | 33872
SOBRANTE 1103 |  | 259248
| Jul | 259248
SOLEDAD 2101 |  | 59482
| Jun | 59482
SOLEDAD 2102 |  | 20520
| May | 12730
| Jul | 7790
SOLEDAD 2105 |  | 32617
| Jun | 3192
| Jul | 29425
SONOMA 1102 |  | 250125
| Apr | 100050
| May | 14835
| Jun | 135240
SONOMA 1105 |  | 432821
| Apr | 99195
| Jul | 333626
SONOMA 1107 |  | 113375
| Jun | 113375
SPRING GAP 1702 |  | 617106
| Jul | 617106
STAFFORD 1101 |  | 1543388
| Jul | 1543388
STAFFORD 1102 |  | 368069
| Jun | 184158
| Jul | 183911
STANISLAUS 1701 |  | 2288867
| May | 435033
| Jun | 219673
| Jul | 1634161
STANISLAUS 1702 |  | 5437023
| Jul | 5437023
STELLING 1109 |  | 2175
| Jul | 2175
STELLING 1110 |  | 266873
| Jun | 266873
STILLWATER 1101 |  | 136226
| Jun | 136226
STILLWATER 1102 |  | 516425
| Jun | 102125
| Jul | 414300
STONE CORRAL 1108 |  | 61930
| Jun | 48235
| Jul | 13695
STONE CORRAL 1110 |  | 13636
| Jun | 9404
| Jul | 4232
SUNOL 1101 |  | 48491
| Jun | 48491
SYCAMORE CREEK 1109 |  | 731274
| Jul | 731274
TASSAJARA 2103 |  | 501244
| Jun | 501244
TASSAJARA 2108 |  | 602375
| Jul | 602375
TASSAJARA 2113 |  | 111277
| Jun | 70867
| Jul | 40410
TEMPLETON 2110 |  | 599824
| May | 248602
| Jun | 351222
TEMPLETON 2111 |  | 333170
| May | 177825
| Jun | 12219
| Jul | 143126
TEMPLETON 2112 |  | 304426
| Jul | 304426
TEMPLETON 2113 |  | 1965580
| May | 925553
| Jun | 180229
| Jul | 859798
TIGER CREEK 0201 |  | 98
| Jul | 98
TIVY VALLEY 1107 |  | 1010588
| May | 83200
| Jun | 625272
| Jul | 302116
TRES PINOS 1111 |  | 15808
| Jul | 15808
TYLER 1105 |  | 1202931
| Jun | 915009
| Jul | 287922
UKIAH 1111 |  | 180180
| Jul | 180180
UKIAH 1113 |  | 151125
| Jul | 151125
UKIAH 1114 |  | 15093
| Jul | 15093
UKIAH 1115 |  | 20880
| Jul | 20880
UPPER LAKE 1101 |  | 635118
| Jun | 258280
| Jul | 376838
VACA DIXON 1105 |  | 256289
| May | 102522
| Jun | 118659
| Jul | 35108
VACAVILLE 1104 |  | 274347
| Jul | 274347
VACAVILLE 1108 |  | 62147
| Jun | 37915
| Jul | 24232
VASCO 1102 |  | 273603
| Jun | 73875
| Jul | 199728
VINEYARD 2108 |  | 2527157
| Jun | 1675677
| Jul | 851480
VOLTA 1101 |  | 268156
| Jun | 226426
| Jul | 41730
VOLTA 1102 |  | 182910
| Jul | 182910
WEST POINT 1102 |  | 56188
| Jun | 56188
WESTLEY 1103 |  | 18338
| Apr | 18338
WHEATLAND 1105 |  | 179054
| May | 109942
| Jul | 69112
WHITMORE 1101 |  | 71256
| Jun | 39096
| Jul | 32160
WILLITS 1104 |  | 303165
| Jun | 206341
| Jul | 96824
WILLOW CREEK 1103 |  | 1263845
| Jun | 200018
| Jul | 1063827
WILLOW PASS 1101 |  | 142418
| Jul | 142418
WILLOW PASS 2108 |  | 220448
| Jul | 220448
WISE 1101 |  | 693541
| May | 128895
| Jun | 564646
WISE 1102 |  | 303825
| May | 62260
| Jun | 126301
| Jul | 115264
WOODACRE 1101 |  | 73260
| Jun | 73260
WOODACRE 1102 |  | 1260499
| Jun | 821213
| Jul | 439286
WOODSIDE 1101 |  | 27467
| Jul | 27467
WOODWARD 2108 |  | 107794
| Jun | 107794
WYANDOTTE 1102 |  | 10948
| Jul | 10948
WYANDOTTE 1103 |  | 224593
| Jun | 224593
WYANDOTTE 1107 |  | 274720
| Jun | 274720
WYANDOTTE 1109 |  | 161553
| May | 51801
| Jun | 109752
WYANDOTTE 1110 |  | 436563
| Jun | 287067
| Jul | 149496
ZACA 1101 |  | 139703
| Jun | 139703
ZACA 1102 |  | 24944
| May | 24944
Total Result |  | 161466371

## YTD EPSS Outages_CAIDI
Circuit | Customer Minutes | CESO | CAIDI
ALHAMBRA 1102 | 184660 | 6258 | 29.5078
ALHAMBRA 1105 | 280468 | 1828 | 153.4289
ALLEGHANY 1101 | 17185 | 449 | 38.2739
ALTO 1124 | 3000 | 40 | 75
ALTO 1125 | 309979 | 2208 | 140.389
ANDERSON 1103 | 24565 | 258 | 95.2132
ANNAPOLIS 1101 | 104279 | 152 | 686.0461
ANTLER SUB | 71735 | 944 | 75.9905
APPLE HILL 1103 | 32500 | 260 | 125
APPLE HILL 1104 | 190008 | 936 | 203
APPLE HILL 2102 | 4950953 | 14476 | 342.0111
ATASCADERO 1101 | 431740 | 4876 | 88.5439
ATASCADERO 1102 | 781744 | 5385 | 145.1707
ATASCADERO 1103 | 429363 | 2870 | 149.6038
AUBERRY 1101 | 1243630 | 5682 | 218.8719
AUBERRY 1102 | 401271 | 2039 | 196.7979
AVENAL 2101 | 20604 | 68 | 303
BALCH NO 1 1101 | 93897 | 28 | 3353.4643
BANGOR 1101 | 71160 | 594 | 119.798
BAYWOOD 1101 | 75690 | 290 | 261
BEAR VALLEY 2101 | 393670 | 2163 | 182.0018
BEAR VALLEY 2105 | 380256 | 1148 | 331.2334
BELL 1107 | 76886 | 521 | 147.5739
BELL 1108 | 16060 | 146 | 110
BELL 1109 | 63196 | 329 | 192.0851
BELLEVUE 2103 | 286858 | 2519 | 113.8777
BEN LOMOND 0401 | 270659 | 2308 | 117.2699
BEN LOMOND 1101 | 297804 | 1966 | 151.4771
BIG BASIN 1101 | 875282 | 5608 | 156.0774
BIG BASIN 1102 | 368747 | 2810 | 131.2267
BIG BEND 1102 | 285119 | 1548 | 184.1854
BIG MEADOWS 2101 | 341683 | 2781 | 122.8634
BOLINAS 1101 | 564492 | 844 | 668.8294
BONNIE NOOK 1102 | 150335 | 535 | 281
BRENTWOOD 2105 | 312146 | 848 | 368.0967
BRIDGEVILLE 1101 | 64638 | 63 | 1026
BROWNS VALLEY 1101 | 11235 | 15 | 749
BRUNSWICK 1102 | 482614 | 2004 | 240.8253
BRUNSWICK 1103 | 353146 | 1276 | 276.7602
BRUNSWICK 1104 | 245234 | 1660 | 147.7313
BRUNSWICK 1105 | 773770 | 2415 | 320.4017
BRUNSWICK 1106 | 655543 | 3189 | 205.5638
BRUNSWICK 1107 | 566873 | 5896 | 96.1454
BRUNSWICK 1110 | 677935 | 6229 | 108.8353
BUCKS CREEK 1103 | 178742 | 306 | 584.1242
BUELLTON 1101 | 115323 | 882 | 130.7517
BURNEY 1101 | 147133 | 631 | 233.1743
BUTTE 1105 | 44865 | 368 | 121.9158
CABRILLO 1103 | 23755 | 275 | 86.3818
CALAVERAS CEMENT 1101 | 849278 | 2147 | 395.565
CALISTOGA 1101 | 135233 | 417 | 324.2998
CALISTOGA 1102 | 978440 | 6466 | 151.3208
CALISTOGA SUB | 522092 | 3810 | 137.032
CALPELLA 1101 | 216915 | 700 | 309.8786
CAMBRIA 1102 | 345654 | 1869 | 184.9406
CAMP EVERS 2103 | 744608 | 6065 | 122.7713
CAMP EVERS 2105 | 4317957 | 16573 | 260.5417
CAMP EVERS 2106 | 3715238 | 17834 | 208.3233
CANTUA 1103 | 12596 | 17 | 740.9412
CASTRO VALLEY 1110 | 158288 | 208 | 761
CASTRO VALLEY 1111 | 72470 | 415 | 174.6265
CAYETANO 2111 | 467594 | 2069 | 226
CAYUCOS 1101 | 69720 | 332 | 210
CAYUCOS 1102 | 65628 | 156 | 420.6923
CEDAR CREEK 1101 | 53732 | 200 | 268.66
CHALLENGE 1101 | 770479 | 1406 | 547.9936
CHESTER 1102 | 26600 | 665 | 40
CHOLAME 2102 | 98789 | 457 | 216.1685
CLARK ROAD 1102 | 4221 | 67 | 63
CLARKSVILLE 2103 | 42969 | 375 | 114.584
CLARKSVILLE 2104 | 286180 | 732 | 390.9563
CLARKSVILLE 2106 | 1329360 | 5638 | 235.7857
CLARKSVILLE 2110 | 37776 | 2361 | 16
CLAY 1101 | 63558 | 742 | 85.6577
CLAY 1102 | 390 | 9 | 43.3333
CLAY 1103 | 50996 | 187 | 272.7059
CLAYTON 2212 | 563680 | 6962 | 80.9652
CLAYTON 2215 | 283637 | 869 | 326.3947
CLEAR LAKE 1101 | 379376 | 524 | 724
CLEAR LAKE 1102 | 5194 | 49 | 106
CLOVERDALE 1101 | 627150 | 2745 | 228.4699
COALINGA NO 2 1105 | 67704 | 185 | 365.9676
COARSEGOLD 2102 | 351614 | 1365 | 257.5927
COARSEGOLD 2103 | 297255 | 1189 | 250.0042
COARSEGOLD 2104 | 635261 | 5513 | 115.2296
COLUMBIA HILL 1101 | 208131 | 848 | 245.4375
COPPERMINE 1104 | 81514 | 212 | 384.5
CORNING 1101 | 261378 | 2280 | 114.6395
CORNING 1102 | 332387 | 1003 | 331.3928
CORRAL 1101 | 581719 | 3730 | 155.9568
CORRAL 1102 | 66200 | 425 | 155.7647
CORRAL 1103 | 137416 | 712 | 193
CORTINA 1101 | 1251 | 9 | 139
COTTONWOOD 1101 | 54531 | 219 | 249
COTTONWOOD 1102 | 178628 | 1702 | 104.9518
COTTONWOOD 1103 | 77420 | 553 | 140
CRESCENT MILLS 2101 | 179036 | 1533 | 116.788
CURTIS 1702 | 421055 | 2298 | 183.2267
CURTIS 1703 | 381853 | 3452 | 110.6179
CURTIS 1704 | 717812 | 3680 | 195.0576
CURTIS 1705 | 181494 | 2048 | 88.6201
CUYAMA 1103 | 26090 | 54 | 483.1481
DEL MAR 2109 | 607980 | 6820 | 89.1466
DEL MONTE 2104 | 520871 | 6454 | 80.7051
DESCHUTES 1101 | 63641 | 588 | 108.233
DESCHUTES 1104 | 42963 | 269 | 159.7138
DIAMOND SPRINGS 1103 | 340306 | 1665 | 204.388
DIAMOND SPRINGS 1105 | 386123 | 2183 | 176.8772
DIAMOND SPRINGS 1106 | 65565 | 639 | 102.6056
DRUM 1101 | 138775 | 406 | 341.8103
DUNBAR 1101 | 74424 | 224 | 332.25
DUNBAR 1102 | 413138 | 2991 | 138.127
DUNBAR 1103 | 117528 | 2476 | 47.4669
DUNLAP 1102 | 504035 | 1206 | 417.9395
DUNLAP 1103 | 165415 | 557 | 296.9749
EAST QUINCY 1101 | 91816 | 998 | 92
ECHO SUMMIT 1101 | 11900 | 175 | 68
EEL RIVER 1102 | 38661 | 106 | 364.7264
EL DORADO PH 2101 | 342751 | 1537 | 223
ELECTRA 1101 | 639821 | 1869 | 342.3333
ELECTRA 1102 | 77575 | 650 | 119.3462
ELK CREEK 1101 | 494464 | 1572 | 314.5445
EMERALD LAKE 0401 | 564271 | 3410 | 165.4754
FAIRVIEW 2207 | 2402733 | 11343 | 211.8252
FITCH MOUNTAIN 1113 | 322585 | 1375 | 234.6073
FOOTHILL 1102 | 507735 | 4491 | 113.0561
FORESTHILL 1101 | 471994 | 3316 | 142.3384
FORT ROSS 1121 | 3975 | 25 | 159
FREMONT 1104 | 7871 | 25 | 314.84
FROGTOWN 1701 | 156858 | 1827 | 85.8555
FROGTOWN 1702 | 185292 | 822 | 225.4161
FRUITLAND 1142 | 92331 | 1023 | 90.2551
FULTON 1102 | 137651 | 468 | 294.1261
FULTON 1107 | 63256 | 474 | 133.4515
GABILAN 1101 | 370850 | 582 | 637.1993
GANSNER 1101 | 58252 | 230 | 253.2696
GARBERVILLE 1101 | 18764 | 92 | 203.9565
GARBERVILLE 1102 | 621564 | 2322 | 267.6848
GERBER 1102 | 18980 | 130 | 146
GEYSERVILLE 1101 | 93386 | 360 | 259.4056
GEYSERVILLE 1102 | 366348 | 1646 | 222.5687
GIRVAN 1101 | 291591 | 2449 | 119.0653
GIRVAN 1102 | 395597 | 2043 | 193.6353
GREEN VALLEY 2101 | 643049 | 4547 | 141.4227
GREENBRAE 1102 | 541848 | 2568 | 211
GUSTINE 1102 | 90528 | 656 | 138
HALF MOON BAY 1101 | 47232 | 82 | 576
HALF MOON BAY 1103 | 1068270 | 6210 | 172.0242
HALSEY 1101 | 201870 | 1659 | 121.6817
HALSEY 1102 | 282849 | 1797 | 157.4007
HAMILTON BRANCH 1101 | 39662 | 306 | 129.6144
HARTLEY 1101 | 322384 | 1552 | 207.7216
HICKS 2101 | 3179434 | 15899 | 199.977
HICKS 2103 | 308764 | 3668 | 84.1778
HIGGINS 1103 | 182960 | 861 | 212.4971
HIGGINS 1104 | 728213 | 4711 | 154.5772
HIGGINS 1107 | 27706 | 239 | 115.9247
HIGGINS 1109 | 120578 | 914 | 131.9234
HIGGINS 1110 | 19336 | 84 | 230.1905
HIGHLANDS 1102 | 611969 | 6461 | 94.7174
HOLLISTER 2102 | 8869 | 169 | 52.4793
HOLLISTER 2105 | 60173 | 254 | 236.9016
HOLLISTER 2106 | 152653 | 1247 | 122.4162
HOOPA 1101 | 744350 | 1060 | 702.217
HOPLAND 1101 | 322627 | 1153 | 279.8153
HORSESHOE 1101 | 383185 | 1364 | 280.9274
HORSESHOE 1104 | 65913 | 624 | 105.6298
JAMESON 1102 | 273048 | 1566 | 174.3602
JAMESON 1105 | 110919 | 1059 | 104.7394
JESSUP 1101 | 171400 | 1791 | 95.7007
JESSUP 1102 | 148685 | 2353 | 63.1895
JESSUP 1103 | 69668 | 665 | 104.7639
JOLON 1102 | 92621 | 148 | 625.8176
JOLON 1103 | 13892 | 60 | 231.5333
KANAKA 1101 | 156651 | 538 | 291.1729
KERCKHOFF 1101 | 11580 | 30 | 386
KING CITY 1102 | 160 | 5 | 32
KING CITY 1103 | 675008 | 1588 | 425.068
KIRKER 2104 | 992190 | 5094 | 194.7762
KONOCTI 1102 | 256443 | 1619 | 158.3959
KONOCTI 1108 | 42018 | 447 | 94
LAKEVILLE 1102 | 77539 | 264 | 293.7083
LAKEWOOD 1103 | 8268 | 156 | 53
LAKEWOOD 2107 | 349665 | 1905 | 183.5512
LAKEWOOD 2227 | 233345 | 1927 | 121.0924
LAMONT 1102 | 22176 | 88 | 252
LAMONT 1104 | 13612 | 63 | 216.0635
LAS GALLINAS A 1105 | 99448 | 2837 | 35.0539
LAS GALLINAS A 1107 | 70052 | 844 | 83
LAS POSITAS 2108 | 226041 | 1872 | 120.7484
LAURELES 1111 | 277267 | 1822 | 152.1773
LAURELES 1112 | 114996 | 777 | 148
LAYTONVILLE 1101 | 6533 | 47 | 139
LAYTONVILLE 1102 | 28327 | 127 | 223.0472
LINCOLN 1104 | 279499 | 1980 | 141.1611
LLAGAS 2101 | 23276 | 243 | 95.786
LLAGAS 2107 | 14074 | 263 | 53.5133
LOCKEFORD 2102 | 80192 | 324 | 247.5062
LOGAN CREEK 2102 | 115893 | 614 | 188.7508
LOS GATOS 1101 | 152152 | 2364 | 64.3621
LOS GATOS 1106 | 491925 | 3066 | 160.4452
LOS GATOS 1107 | 163726 | 2306 | 71
LOS GATOS 1108 | 7442 | 335 | 22.2149
LOS MOLINOS 1101 | 20034 | 233 | 85.9828
LOS OSITOS 2102 | 1520 | 16 | 95
LOS OSITOS 2103 | 634391 | 1035 | 612.9382
LOYOLA 1102 | 9126 | 39 | 234
LUCERNE 1103 | 412481 | 4554 | 90.5755
MADISON 1105 | 185423 | 377 | 491.8382
MADISON 2101 | 2726756 | 6782 | 402.0578
MAGUNDEN 1108 | 37336 | 312 | 119.6667
MARIPOSA 2101 | 605282 | 1219 | 496.5398
MARIPOSA 2102 | 874580 | 3901 | 224.1938
MC ARTHUR 1101 | 711089 | 1771 | 401.5184
MC KEE 1107 | 142181 | 1259 | 112.9317
MC KEE 1111 | 20536 | 604 | 34
MENLO 1102 | 88372 | 425 | 207.9341
MERCED FALLS 1102 | 389283 | 1965 | 198.1084
MIDDLETOWN 1101 | 236530 | 1117 | 211.7547
MIDDLETOWN 1102 | 34666 | 494 | 70.1741
MILPITAS 1105 | 172205 | 3689 | 46.6807
MILPITAS 1108 | 236044 | 2639 | 89.4445
MIRABEL 1101 | 273051 | 1708 | 159.8659
MIRABEL 1102 | 15789 | 261 | 60.4943
MIWUK 1701 | 282972 | 920 | 307.5783
MIWUK 1702 | 269353 | 2207 | 122.0449
MOLINO 1102 | 743823 | 3620 | 205.476
MONTE RIO 1111 | 400715 | 2335 | 171.6124
MONTE RIO 1113 | 67360 | 517 | 130.2901
MONTICELLO 1101 | 450201 | 3033 | 148.4342
MORAGA 1102 | 1005843 | 6254 | 160.8319
MORAGA 1105 | 589512 | 2277 | 258.8986
MORGAN HILL 2104 | 69537 | 385 | 180.6156
MORGAN HILL 2105 | 418687 | 5751 | 72.8025
MORGAN HILL 2109 | 504775 | 4180 | 120.7596
MORGAN HILL 2111 | 2189246 | 3882 | 563.948
MORRO BAY 1101 | 83058 | 327 | 254
MOUNTAIN QUARRIES 2101 | 232290 | 1139 | 203.9421
NAPA 1110 | 3648 | 76 | 48
NAPA 1112 | 22116 | 549 | 40.2842
NARROWS 2102 | 1539163 | 4169 | 369.1924
NARROWS 2105 | 2474334 | 13424 | 184.3217
NORTH BRANCH 1101 | 323946 | 1624 | 199.4741
NORTH DUBLIN 2103 | 2430266 | 14698 | 165.3467
NORTH TOWER 2101 | 123728 | 3256 | 38
NOVATO 1104 | 18377 | 161 | 114.1429
OAKHURST 1101 | 849416 | 3104 | 273.6521
OAKHURST 1102 | 408281 | 3185 | 128.1887
OAKHURST 1103 | 1448696 | 4871 | 297.4124
OAKLAND X 1104 | 34552 | 617 | 56
OCEANO 1104 | 936438 | 10962 | 85.4258
OILFIELDS 1103 | 831283 | 4919 | 168.9943
OLEMA 1101 | 22601 | 233 | 97
OLETA 1101 | 442339 | 500 | 884.678
OLETA 1102 | 492695 | 1933 | 254.8862
OREGON TRAIL 1102 | 262771 | 779 | 337.3184
OREGON TRAIL 1103 | 314633 | 1121 | 280.6717
ORINDA 0401 | 53846 | 293 | 183.7747
ORO FINO 1101 | 753303 | 5801 | 129.8574
ORO FINO 1102 | 259141 | 2382 | 108.7914
OROSI 1102 | 499805 | 758 | 659.3734
OTTER 1101 | 55483 | 212 | 261.7123
PANORAMA 1101 | 162735 | 1504 | 108.2015
PANORAMA 1102 | 230128 | 1500 | 153.4187
PARADISE 1104 | 188772 | 2256 | 83.6755
PARADISE 1106 | 69866 | 607 | 115.1005
PASO ROBLES 1103 | 86146 | 517 | 166.6267
PASO ROBLES 1104 | 260196 | 2368 | 109.8801
PAUL SWEET 2104 | 56232 | 735 | 76.5061
PAUL SWEET 2105 | 1163364 | 6428 | 180.9838
PAUL SWEET 2106 | 974488 | 5129 | 189.9957
PAUL SWEET 2107 | 32555 | 350 | 93.0143
PEABODY 2106 | 247376 | 2976 | 83.1237
PEABODY 2113 | 767512 | 5668 | 135.4114
PENRYN 1103 | 334114 | 2237 | 149.3581
PENRYN 1105 | 322644 | 2999 | 107.5839
PENRYN 1106 | 164246 | 907 | 181.0871
PENRYN 1107 | 159842 | 378 | 422.8624
PEORIA 1701 | 441647 | 2712 | 162.8492
PEORIA 1704 | 880814 | 3161 | 278.6504
PEORIA 1705 | 43142 | 407 | 106
PERRY 1101 | 194376 | 740 | 262.6703
PETALUMA C 1108 | 78925 | 713 | 110.6942
PETALUMA C 1109 | 8964 | 54 | 166
PHILO 1101 | 471857 | 2367 | 199.3481
PHILO 1102 | 482079 | 733 | 657.6794
PIKE CITY 1101 | 176615 | 146 | 1209.6918
PINE GROVE 1102 | 329563 | 1562 | 210.9878
PIT NO 1 1101 | 302836 | 999 | 303.1391
PIT NO 3 2101 | 45375 | 152 | 298.5197
PIT NO 5 1101 | 443 | 1 | 443
PLACER 1103 | 52933 | 521 | 101.5988
PLACERVILLE 2106 | 1570529 | 8013 | 195.9976
POINT MORETTI 1101 | 39259 | 337 | 116.4955
POSO MOUNTAIN 2101 | 306033 | 629 | 486.539
POSO MOUNTAIN 2103 | 18981 | 54 | 351.5
POSO MOUNTAIN 2104 | 2133 | 9 | 237
POTTER VALLEY P H 1105 | 2520 | 40 | 63
PUEBLO 1104 | 65676 | 551 | 119.1942
PUEBLO 1105 | 30248 | 152 | 199
PUEBLO 2103 | 99554 | 313 | 318.0639
PUEBLO 2104 | 357684 | 1047 | 341.6275
PURISIMA 1101 | 285444 | 2403 | 118.7865
PUTAH CREEK 1105 | 9680 | 40 | 242
RADUM 1105 | 25441 | 247 | 103
RAWSON 1103 | 113348 | 705 | 160.7773
RED BLUFF 1103 | 587311 | 2725 | 215.527
RED BLUFF 1104 | 792823 | 2732 | 290.1988
REDBUD 1101 | 39440 | 493 | 80
REDBUD 1102 | 675916 | 5214 | 129.6348
RESEARCH 2102 | 49629 | 71 | 699
RESERVATION ROAD 1101 | 116276 | 709 | 164
RESERVATION ROAD 1102 | 595806 | 4778 | 124.6978
RINCON 1101 | 1603636 | 2381 | 673.5136
RIO DELL 1102 | 177178 | 399 | 444.0551
RISING RIVER 1101 | 449557 | 1450 | 310.0393
ROB ROY 2104 | 572176 | 5829 | 98.1602
ROB ROY 2105 | 793099 | 5325 | 148.9388
ROSSMOOR 1102 | 795524 | 3530 | 225.3609
ROSSMOOR 1106 | 215185 | 2221 | 96.8865
SALT SPRINGS 2101 | 301600 | 917 | 328.8986
SAN ARDO 1101 | 2492 | 24 | 103.8333
SAN CARLOS 1104 | 13556 | 261 | 51.9387
SAN JOAQUIN #3 1101 | 166898 | 582 | 286.7663
SAN JOAQUIN #3 1102 | 132064 | 524 | 252.0305
SAN JUSTO 1101 | 47490 | 502 | 94.6016
SAN LUIS OBISPO 1101 | 41209 | 203 | 203
SAN LUIS OBISPO 1103 | 34335 | 327 | 105
SAN LUIS OBISPO 1107 | 939348 | 12561 | 74.7829
SAN MIGUEL 1106 | 43878 | 149 | 294.4832
SAN RAFAEL 1104 | 43586 | 1406 | 31
SAN RAFAEL 1106 | 214132 | 1912 | 111.9937
SAN RAFAEL 1107 | 13545 | 301 | 45
SAN RAFAEL 1108 | 648121 | 4617 | 140.3771
SAN RAMON 2103 | 235759 | 552 | 427.0996
SAN RAMON 2107 | 725792 | 6303 | 115.1502
SAND CREEK 1103 | 224010 | 813 | 275.5351
SANTA ROSA A 1107 | 142038 | 1214 | 117
SANTA YNEZ 1101 | 25344 | 192 | 132
SANTA YNEZ 1102 | 211663 | 1218 | 173.7791
SANTA YNEZ 1104 | 26417 | 277 | 95.3682
SARATOGA 1103 | 81464 | 1218 | 66.8834
SARATOGA 1104 | 132102 | 1008 | 131.0536
SARATOGA 1106 | 157159 | 1731 | 90.7909
SARATOGA 1107 | 247585 | 672 | 368.4301
SHADY GLEN 1102 | 67805 | 355 | 191
SHINGLE SPRINGS 1104 | 57330 | 637 | 90
SHINGLE SPRINGS 2105 | 491583 | 3383 | 145.3098
SHINGLE SPRINGS 2108 | 1493765 | 10140 | 147.3141
SHINGLE SPRINGS 2109 | 1810384 | 9578 | 189.0148
SILVERADO 2102 | 478626 | 3973 | 120.4697
SILVERADO 2103 | 14525 | 63 | 230.5556
SILVERADO 2104 | 2699923 | 6220 | 434.0712
SILVERADO 2105 | 64608 | 385 | 167.813
SISQUOC 1102 | 77578 | 305 | 254.3541
SMARTVILLE SUB | 30623 | 271 | 113
SOBRANTE 1101 | 59050 | 1348 | 43.8056
SOBRANTE 1102 | 134320 | 1168 | 115
SOBRANTE 1103 | 259248 | 982 | 264
SOLEDAD 2101 | 59482 | 172 | 345.8256
SOLEDAD 2102 | 20520 | 190 | 108
SOLEDAD 2105 | 32617 | 703 | 46.3969
SONOMA 1102 | 250125 | 575 | 435
SONOMA 1105 | 432821 | 1107 | 390.9855
SONOMA 1107 | 113375 | 250 | 453.5
SPRING GAP 1702 | 617106 | 1536 | 401.7617
STAFFORD 1101 | 1543388 | 6512 | 237.0068
STAFFORD 1102 | 368069 | 4448 | 82.7493
STANISLAUS 1701 | 2288867 | 5962 | 383.9093
STANISLAUS 1702 | 5437023 | 7424 | 732.3576
STELLING 1109 | 2175 | 29 | 75
STELLING 1110 | 266873 | 855 | 312.1322
STILLWATER 1101 | 136226 | 705 | 193.2284
STILLWATER 1102 | 516425 | 2370 | 217.9008
STONE CORRAL 1108 | 61930 | 165 | 375.3333
STONE CORRAL 1110 | 13636 | 99 | 137.7374
SUNOL 1101 | 48491 | 499 | 97.1764
SYCAMORE CREEK 1109 | 731274 | 4744 | 154.1471
TASSAJARA 2103 | 501244 | 5966 | 84.0168
TASSAJARA 2108 | 602375 | 4538 | 132.7402
TASSAJARA 2113 | 111277 | 898 | 123.9165
TEMPLETON 2110 | 599824 | 1610 | 372.5615
TEMPLETON 2111 | 333170 | 2181 | 152.7602
TEMPLETON 2112 | 304426 | 1630 | 186.7644
TEMPLETON 2113 | 1965580 | 8957 | 219.4462
TIGER CREEK 0201 | 98 | 14 | 7
TIVY VALLEY 1107 | 1010588 | 4585 | 220.4118
TRES PINOS 1111 | 15808 | 336 | 47.0476
TYLER 1105 | 1202931 | 4344 | 276.9178
UKIAH 1111 | 180180 | 1072 | 168.0784
UKIAH 1113 | 151125 | 1209 | 125
UKIAH 1114 | 15093 | 129 | 117
UKIAH 1115 | 20880 | 180 | 116
UPPER LAKE 1101 | 635118 | 1740 | 365.0103
VACA DIXON 1105 | 256289 | 3346 | 76.5956
VACAVILLE 1104 | 274347 | 2092 | 131.141
VACAVILLE 1108 | 62147 | 848 | 73.2866
VASCO 1102 | 273603 | 456 | 600.0066
VINEYARD 2108 | 2527157 | 9078 | 278.3826
VOLTA 1101 | 268156 | 1001 | 267.8881
VOLTA 1102 | 182910 | 1175 | 155.6681
WEST POINT 1102 | 56188 | 198 | 283.7778
WESTLEY 1103 | 18338 | 41 | 447.2683
WHEATLAND 1105 | 179054 | 818 | 218.8924
WHITMORE 1101 | 71256 | 639 | 111.5117
WILLITS 1104 | 303165 | 1996 | 151.8863
WILLOW CREEK 1103 | 1263845 | 1523 | 829.8391
WILLOW PASS 1101 | 142418 | 1601 | 88.9557
WILLOW PASS 2108 | 220448 | 5616 | 39.2536
WISE 1101 | 693541 | 4115 | 168.5397
WISE 1102 | 303825 | 1352 | 224.7226
WOODACRE 1101 | 73260 | 740 | 99
WOODACRE 1102 | 1260499 | 9452 | 133.3579
WOODSIDE 1101 | 27467 | 250 | 109.868
WOODWARD 2108 | 107794 | 464 | 232.3147
WYANDOTTE 1102 | 10948 | 34 | 322
WYANDOTTE 1103 | 224593 | 1216 | 184.6982
WYANDOTTE 1107 | 274720 | 737 | 372.7544
WYANDOTTE 1109 | 161553 | 753 | 214.5458
WYANDOTTE 1110 | 436563 | 3127 | 139.6108
ZACA 1101 | 139703 | 750 | 186.2707
ZACA 1102 | 24944 | 547 | 45.6015

## YTD EPSS Outages_CPZ
CPZ | Count of Outages
ALHAMBRA 11021102/2 | 2
ALHAMBRA 110581514 | 1
ALLEGHANY 1101978 | 3
ALTO 1124884949 | 1
ALTO 11251256 | 1
ALTO 1125296476 | 1
ANDERSON 11031600 | 2
ANNAPOLIS 1101528344 | 1
APPLE HILL 11038412 | 1
APPLE HILL 110413512 | 1
APPLE HILL 21021532 | 1
APPLE HILL 2102186912 | 3
APPLE HILL 210251792 | 2
APPLE HILL 21026552 | 1
APPLE HILL 21027502 | 1
APPLE HILL 21028372 | 1
ATASCADERO 11011101/2 | 1
ATASCADERO 1101A50 | 1
ATASCADERO 1102A28 | 3
ATASCADERO 1103A16 | 2
ATASCADERO 1103A46 | 3
AUBERRY 11011101/2 | 1
AUBERRY 110149122 | 1
AUBERRY 1101R2578 | 1
AUBERRY 1101R2579 | 1
AUBERRY 110237466 | 2
AUBERRY 1102R2850 | 1
AUBERRY 1102R902 | 2
AVENAL 21019070 | 1
BALCH NO 1 1101105414 | 1
BANGOR 11017446 | 1
BANGOR 1101870548 | 1
BAYWOOD 11011101/2 | 1
BEAR VALLEY 21014500 | 4
BEAR VALLEY 210521160 | 2
BEAR VALLEY 21054170 | 1
BELL 11072400 | 1
BELL 110880680 | 1
BELL 1109724884 | 1
BELLEVUE 2103552 | 3
BEN LOMOND 040116010 | 2
BEN LOMOND 04015206 | 1
BEN LOMOND 0401944178 | 2
BEN LOMOND 1101BL 2101 | 1
BIG BASIN 110110720 | 1
BIG BASIN 1101393582 | 2
BIG BASIN 1101573005 | 1
BIG BASIN 110195690 | 1
BIG BASIN 110212758 | 1
BIG BASIN 1102351054 | 1
BIG BASIN 1102573005 | 1
BIG BASIN 110296986 | 2
BIG BEND 11021102/2 | 3
BIG BEND 1102884340 | 2
BIG MEADOWS 21012016 | 1
BIG MEADOWS 21012476 | 1
BOLINAS 1101504 | 1
BONNIE NOOK 11021102/2 | 1
BRENTWOOD 2105502672 | 1
BRENTWOOD 21056512 | 1
BRENTWOOD 210598606 | 2
BRENTWOOD 2105B504R | 2
BRIDGEVILLE 110169866 | 1
BROWNS VALLEY 110136622 | 1
BRUNSWICK 11021010 | 3
BRUNSWICK 11032784 | 1
BRUNSWICK 11041020 | 1
BRUNSWICK 1104327226 | 1
BRUNSWICK 11052140 | 1
BRUNSWICK 11052204 | 1
BRUNSWICK 11052210 | 1
BRUNSWICK 110651486 | 2
BRUNSWICK 11071107/2 | 1
BRUNSWICK 11101110/2 | 2
BUCKS CREEK 1103338520 | 1
BUELLTON 1101Y06 | 2
BUELLTON 1101Y26 | 1
BURNEY 11012402 | 1
BUTTE 1105134600 | 1
CABRILLO 1103Y46 | 1
CALAVERAS CEMENT 110111188 | 1
CALAVERAS CEMENT 110111236 | 2
CALAVERAS CEMENT 1101502 | 1
CALISTOGA 1101242919 | 1
CALISTOGA 110178734 | 3
CALISTOGA 11021102/2 | 3
CALPELLA 1101542 | 1
CALPELLA 1101753000 | 1
CAMBRIA 11021102/2 | 1
CAMBRIA 1102W50 | 1
CAMP EVERS 210311056 | 1
CAMP EVERS 21032103/2 | 1
CAMP EVERS 21035402 | 1
CAMP EVERS 210510294 | 1
CAMP EVERS 210510728 | 3
CAMP EVERS 210511384 | 1
CAMP EVERS 210512590 | 1
CAMP EVERS 210533542 | 1
CAMP EVERS 21055188 | 1
CAMP EVERS 210574170 | 1
CAMP EVERS 210595050 | 2
CAMP EVERS 210611044 | 2
CAMP EVERS 210612840 | 1
CAMP EVERS 210616000 | 1
CAMP EVERS 21062106/2 | 1
CAMP EVERS 210637210 | 1
CAMP EVERS 21065020 | 2
CAMP EVERS 210660120 | 2
CAMP EVERS 2106737512 | 2
CANTUA 11039900 | 1
CASTRO VALLEY 1110MR273 | 1
CASTRO VALLEY 1111MR334 | 1
CAYETANO 21112111/2 | 1
CAYUCOS 1101W58 | 1
CAYUCOS 1102317156 | 1
CAYUCOS 1102613456 | 1
CEDAR CREEK 11011608 | 1
CHALLENGE 11011101/2 | 2
CHESTER 11021102/2 | 1
CHOLAME 2102796386 | 1
CHOLAME 2102X16 | 1
CLARK ROAD 1102212118 | 1
CLARKSVILLE 2103593454 | 1
CLARKSVILLE 210419772 | 3
CLARKSVILLE 210619642 | 1
CLARKSVILLE 21062106/2 | 1
CLARKSVILLE 211019692 | 1
CLAY 110113450 | 1
CLAY 110184572 | 1
CLAY 11021102/2 | 3
CLAY 11031230 | 1
CLAY 11037142 | 1
CLAYTON 2212204416 | 1
CLAYTON 22122212/2 | 2
CLAYTON 2212614950 | 1
CLAYTON 2215W531R | 1
CLEAR LAKE 11011302 | 1
CLEAR LAKE 1102904 | 1
CLOVERDALE 11011101/2 | 1
CLOVERDALE 1101474708 | 1
COALINGA NO 2 110541954 | 1
COALINGA NO 2 11059000 | 1
COARSEGOLD 210210890 | 1
COARSEGOLD 21035020 | 1
COARSEGOLD 21042104/2 | 1
COARSEGOLD 2104570682 | 1
COLUMBIA HILL 110135424 | 1
COLUMBIA HILL 1101764 | 2
COLUMBIA HILL 110190730 | 1
COPPERMINE 1104556430 | 2
CORNING 11011624 | 1
CORNING 110182846 | 5
CORNING 110185152 | 1
CORNING 11021622 | 1
CORNING 11021900 | 1
CORNING 110253184 | 2
CORRAL 11011101/2 | 1
CORRAL 110112606 | 1
CORRAL 110112612 | 1
CORRAL 110136652 | 2
CORRAL 110175204 | 1
CORRAL 110236666 | 1
CORRAL 110336680 | 1
CORTINA 1101528460 | 1
COTTONWOOD 11011610 | 1
COTTONWOOD 11029026 | 2
COTTONWOOD 11031616 | 1
CRESCENT MILLS 21012562 | 1
CURTIS 170234426 | 1
CURTIS 170247488 | 1
CURTIS 17028000 | 1
CURTIS 17036064 | 1
CURTIS 170384944 | 1
CURTIS 17046060 | 2
CURTIS 17048140 | 1
CURTIS 170539256 | 2
CURTIS 17058170 | 2
CUYAMA 1103622728 | 1
DEL MAR 21092109/2 | 1
DEL MAR 210975802 | 1
DEL MONTE 21042624 | 2
DESCHUTES 11011380 | 1
DESCHUTES 11049726 | 1
DIAMOND SPRINGS 11039432 | 3
DIAMOND SPRINGS 11052102 | 2
DIAMOND SPRINGS 110656026 | 1
DIAMOND SPRINGS 110676088 | 1
DRUM 11011101/2 | 2
DUNBAR 1101440 | 1
DUNBAR 1101534 | 1
DUNBAR 1102246 | 1
DUNBAR 1102861496 | 1
DUNBAR 1103302 | 1
DUNLAP 11021102/2 | 1
DUNLAP 11027060 | 1
DUNLAP 11027290 | 5
DUNLAP 11037220 | 1
EAST QUINCY 11012452 | 1
ECHO SUMMIT 1101927328 | 1
EEL RIVER 11021902 | 1
EL DORADO PH 210113362 | 1
EL DORADO PH 210152456 | 1
ELECTRA 11017104 | 3
ELECTRA 11024756 | 1
ELK CREEK 11012002 | 2
ELK CREEK 110137334 | 2
EMERALD LAKE 0401401/2 | 3
FAIRVIEW 22072207/2 | 2
FAIRVIEW 2207M501R | 1
FAIRVIEW 2207P148 | 1
FITCH MOUNTAIN 1113154 | 1
FITCH MOUNTAIN 111324550 | 3
FITCH MOUNTAIN 1113356 | 1
FOOTHILL 110299432 | 2
FORESTHILL 11011802 | 2
FORT ROSS 1121913812 | 1
FREMONT 1104645342 | 1
FROGTOWN 170113412 | 1
FROGTOWN 170275252 | 1
FRUITLAND 11421142/2 | 1
FULTON 11024522 | 1
FULTON 1107214 | 1
GABILAN 11013034 | 1
GABILAN 1101460414 | 1
GANSNER 11012424 | 1
GANSNER 1101782320 | 1
GARBERVILLE 11011750 | 1
GARBERVILLE 11021102/2 | 1
GARBERVILLE 11022124 | 2
GARBERVILLE 110256048 | 1
GERBER 11021560 | 1
GEYSERVILLE 110137454 | 3
GEYSERVILLE 1102274 | 3
GEYSERVILLE 1102484 | 1
GIRVAN 11011101/2 | 1
GIRVAN 11011330 | 1
GIRVAN 11021102/2 | 1
GIRVAN 1102212096 | 1
GIRVAN 110280726 | 1
GREEN VALLEY 210111054 | 1
GREEN VALLEY 210112106 | 2
GREEN VALLEY 210136820 | 1
GREEN VALLEY 2101942143 | 2
GREENBRAE 11021254 | 1
GUSTINE 11029100 | 1
HALF MOON BAY 1101818874 | 2
HALF MOON BAY 1103655644 | 3
HALF MOON BAY 1103880484 | 2
HALF MOON BAY 1103H82 | 1
HALSEY 11012414 | 1
HALSEY 110176178 | 2
HALSEY 110239104 | 2
HAMILTON BRANCH 1101161872 | 1
HAMILTON BRANCH 110190334 | 1
HARTLEY 1101658 | 1
HARTLEY 1101738 | 1
HICKS 21012101/2 | 1
HICKS 2101XR162 | 3
HICKS 2101XR250 | 2
HICKS 21032103/2 | 1
HIGGINS 110350072 | 1
HIGGINS 1103995672 | 1
HIGGINS 11041006 | 2
HIGGINS 11041374 | 1
HIGGINS 11071070 | 1
HIGGINS 110950078 | 1
HIGGINS 1109594 | 1
HIGGINS 111051794 | 1
HIGHLANDS 1102556 | 1
HIGHLANDS 1102623120 | 1
HIGHLANDS 110275140 | 2
HOLLISTER 2102113634 | 2
HOLLISTER 21054048 | 2
HOLLISTER 21064004 | 4
HOOPA 11013174 | 1
HOOPA 110137202 | 2
HOOPA 110182542 | 1
HOOPA 110193038 | 1
HOPLAND 11014626 | 1
HOPLAND 1101768 | 1
HOPLAND 110180620 | 1
HOPLAND 110194006 | 1
HOPLAND 1101960 | 1
HORSESHOE 11011101/2 | 1
HORSESHOE 110450142 | 2
JAMESON 11028842 | 2
JAMESON 1105466348 | 3
JESSUP 11019002 | 1
JESSUP 11021102/2 | 1
JESSUP 11031540 | 1
JOLON 11027004 | 1
JOLON 11031103/2 | 3
KANAKA 1101LR1101/2 | 1
KERCKHOFF 1101R308 | 1
KING CITY 1102728782 | 1
KING CITY 11037038 | 2
KIRKER 21042104/2 | 1
KONOCTI 1102532 | 1
KONOCTI 110264664 | 2
KONOCTI 1102714370 | 2
KONOCTI 11081278 | 1
LAKEVILLE 1102347280 | 2
LAKEVILLE 110287432 | 1
LAKEWOOD 1103857172 | 2
LAKEWOOD 2107396264 | 1
LAKEWOOD 2227W503R | 1
LAMONT 11021644 | 1
LAMONT 11044113 | 2
LAS GALLINAS A 11051105/2 | 1
LAS GALLINAS A 1107554 | 1
LAS POSITAS 2108MR190 | 1
LAURELES 11112020 | 1
LAURELES 11112028 | 2
LAURELES 111268454 | 1
LAYTONVILLE 1101448108 | 1
LAYTONVILLE 110237586 | 1
LINCOLN 11042070 | 2
LINCOLN 110451756 | 2
LINCOLN 1104685276 | 1
LLAGAS 2101XR584 | 1
LLAGAS 2107374344 | 1
LOCKEFORD 210212468 | 1
LOGAN CREEK 21022226 | 1
LOGAN CREEK 21022428 | 1
LOGAN CREEK 210237316 | 1
LOGAN CREEK 210262032 | 1
LOS GATOS 11011101/2 | 1
LOS GATOS 110660116 | 2
LOS GATOS 1106LB44 | 2
LOS GATOS 1106LB48 | 1
LOS GATOS 11071107/2 | 1
LOS GATOS 1108LB44 | 1
LOS MOLINOS 11011308 | 1
LOS OSITOS 2102258878 | 1
LOS OSITOS 21031132 | 1
LOS OSITOS 2103220608 | 1
LOS OSITOS 21033010 | 2
LOYOLA 1102917865 | 1
LUCERNE 11031103/2 | 1
LUCERNE 11034200 | 1
LUCERNE 11034624 | 1
LUCERNE 1103630 | 1
MADISON 11057712 | 2
MADISON 21011606 | 6
MADISON 2101888814 | 1
MADISON 210189332 | 3
MAGUNDEN 1108250674 | 3
MARIPOSA 210110170 | 1
MARIPOSA 210110240 | 1
MARIPOSA 210110990 | 1
MARIPOSA 210210880 | 1
MARIPOSA 210237288 | 2
MARIPOSA 2102440236 | 1
MC ARTHUR 11011488 | 1
MC ARTHUR 11011544 | 4
MC ARTHUR 11011546 | 1
MC KEE 1107XR010 | 3
MC KEE 1111711900 | 1
MENLO 11028952 | 1
MENLO 1102W80 | 1
MERCED FALLS 1102482838 | 1
MERCED FALLS 110285002 | 1
MIDDLETOWN 1101548 | 1
MIDDLETOWN 1101571926 | 1
MIDDLETOWN 1102514 | 1
MILPITAS 11051105/2 | 1
MILPITAS 1108XR122 | 1
MIRABEL 1101116 | 2
MIRABEL 1101201156 | 1
MIRABEL 1101228 | 1
MIRABEL 1101298 | 2
MIRABEL 110286326 | 1
MIWUK 1701953336 | 1
MIWUK 1702823548 | 2
MIWUK 17029270 | 1
MOLINO 1102104 | 2
MONTE RIO 1111256 | 1
MONTE RIO 111164758 | 2
MONTE RIO 1113346 | 1
MONTICELLO 1101256640 | 1
MONTICELLO 110137384 | 1
MONTICELLO 110152910 | 1
MONTICELLO 110193384 | 1
MORAGA 11021106/2 | 1
MORAGA 1102221914 | 1
MORAGA 110242914 | 1
MORAGA 11051105/2 | 1
MORAGA 1105829530 | 1
MORGAN HILL 2104152774 | 1
MORGAN HILL 21052105/2 | 1
MORGAN HILL 2105XR176 | 1
MORGAN HILL 2105XR564 | 1
MORGAN HILL 2109XR246 | 1
MORGAN HILL 21112111/2 | 1
MORGAN HILL 2111997000 | 1
MORGAN HILL 2111XR398 | 2
MORRO BAY 1101V66 | 1
MOUNTAIN QUARRIES 21012422 | 1
MOUNTAIN QUARRIES 210135466 | 1
NAPA 1110373667 | 1
NAPA 11121302 | 1
NARROWS 21022220 | 2
NARROWS 210248484 | 2
NARROWS 210276952 | 1
NARROWS 21052216 | 1
NARROWS 21052228 | 1
NARROWS 21052426 | 3
NARROWS 21052748 | 3
NORTH BRANCH 110111158 | 4
NORTH DUBLIN 21032103/2 | 3
NORTH TOWER 2101158556/2 | 1
NOVATO 110455398 | 1
OAKHURST 11015490 | 1
OAKHURST 1101636114 | 1
OAKHURST 11021102/2 | 1
OAKHURST 110310140 | 1
OAKHURST 11031103/2 | 1
OAKLAND X 1104CR101 | 1
OCEANO 11041104/2 | 1
OCEANO 1104891294 | 1
OCEANO 1104Q12 | 1
OCEANO 1104V38 | 3
OILFIELDS 110387034 | 1
OILFIELDS 1103N42 | 1
OILFIELDS 1103N44 | 1
OILFIELDS 1103N48 | 1
OLEMA 11011200 | 1
OLETA 11011208 | 1
OLETA 1102186326 | 2
OREGON TRAIL 11021382 | 1
OREGON TRAIL 110249144 | 1
OREGON TRAIL 110335002 | 1
ORINDA 0401401/2 | 1
ORO FINO 11011101/2 | 2
ORO FINO 11012022 | 1
ORO FINO 11022090 | 1
ORO FINO 11022096 | 1
ORO FINO 11022560 | 1
ORO FINO 110276008 | 1
OROSI 11021102/2 | 2
OTTER 11012052 | 1
OTTER 1101696967 | 1
PANORAMA 11011101/2 | 1
PANORAMA 11021342 | 2
PANORAMA 11021526 | 4
PARADISE 11041104/2 | 1
PARADISE 110636042 | 2
PASO ROBLES 110355374 | 1
PASO ROBLES 1104R14 | 1
PAUL SWEET 21045394 | 1
PAUL SWEET 2104885736 | 1
PAUL SWEET 21052105/2 | 1
PAUL SWEET 2105959032 | 2
PAUL SWEET 21062106/2 | 1
PAUL SWEET 21065178 | 2
PAUL SWEET 210710986 | 2
PEABODY 21062106/2 | 1
PEABODY 21132113/2 | 1
PENRYN 110351658 | 1
PENRYN 1103604 | 2
PENRYN 1103660 | 2
PENRYN 11051105/2 | 1
PENRYN 11051342 | 1
PENRYN 110550548 | 1
PENRYN 110550550 | 1
PENRYN 110651674 | 1
PENRYN 11072708 | 1
PEORIA 17013186 | 2
PEORIA 170176030 | 1
PEORIA 170411232 | 1
PEORIA 170459596 | 1
PEORIA 17051834 | 1
PERRY 1101V88 | 1
PETALUMA C 1108618 | 1
PETALUMA C 1109820458 | 1
PHILO 11011101/2 | 1
PHILO 110137222 | 1
PHILO 1102920 | 1
PIKE CITY 11011720 | 1
PIKE CITY 11011730 | 1
PINE GROVE 11023168 | 1
PINE GROVE 110245292 | 1
PIT NO 1 11011101/2 | 1
PIT NO 3 21012101/2 | 1
PIT NO 5 11011614 | 1
PLACER 1103429574 | 1
PLACERVILLE 210619732 | 1
PLACERVILLE 21062224 | 1
PLACERVILLE 210623190 | 2
PLACERVILLE 21067522 | 1
POINT MORETTI 110110722 | 1
POINT MORETTI 110136514 | 1
POSO MOUNTAIN 21011703 | 2
POSO MOUNTAIN 21012101/2 | 2
POSO MOUNTAIN 21012181 | 5
POSO MOUNTAIN 21014456 | 1
POSO MOUNTAIN 21032103/2 | 2
POSO MOUNTAIN 210448268 | 1
POTTER VALLEY P H 1105195738 | 1
PUEBLO 1104105708 | 1
PUEBLO 1105637242 | 1
PUEBLO 2103678 | 1
PUEBLO 2104279478 | 1
PUEBLO 2104378860 | 1
PUEBLO 2104391312 | 1
PUEBLO 2104656 | 2
PURISIMA 11011101/2 | 1
PUTAH CREEK 1105617260 | 4
RADUM 1105806392 | 1
RAWSON 11033314 | 1
RED BLUFF 11031103/2 | 1
RED BLUFF 11041302 | 3
RED BLUFF 1104952448 | 1
REDBUD 110191960 | 1
REDBUD 1102432 | 2
REDBUD 1102922 | 1
RESEARCH 2102446423 | 1
RESERVATION ROAD 1101383718 | 1
RESERVATION ROAD 11021102/2 | 2
RESERVATION ROAD 11023030 | 1
RESERVATION ROAD 11023032 | 3
RINCON 1101576 | 1
RIO DELL 11028768 | 1
RIO DELL 11028852 | 1
RISING RIVER 11011101/2 | 2
ROB ROY 210410298 | 1
ROB ROY 210410960 | 2
ROB ROY 210412596 | 2
ROB ROY 210512584 | 1
ROB ROY 210512586 | 2
ROB ROY 21055090 | 1
ROSSMOOR 1102457174 | 1
ROSSMOOR 1106L522R | 1
SALT SPRINGS 21011232 | 1
SAN ARDO 11017632 | 1
SAN CARLOS 11048858 | 1
SAN JOAQUIN #3 1101673480 | 1
SAN JOAQUIN #3 11021102/2 | 2
SAN JUSTO 1101201311 | 2
SAN JUSTO 11014002 | 1
SAN LUIS OBISPO 1101V12 | 1
SAN LUIS OBISPO 110342344 | 1
SAN LUIS OBISPO 11071107/2 | 1
SAN LUIS OBISPO 1107V18 | 8
SAN LUIS OBISPO 1107V58 | 1
SAN MIGUEL 1106428314 | 1
SAN MIGUEL 1106605393 | 1
SAN RAFAEL 1104802 | 1
SAN RAFAEL 110648752 | 1
SAN RAFAEL 11071276 | 1
SAN RAFAEL 11081108/2 | 1
SAN RAMON 2103MR279 | 3
SAN RAMON 21072107/2 | 1
SAN RAMON 2107MR284 | 1
SAND CREEK 11037070 | 1
SAND CREEK 1103818064 | 1
SANTA ROSA A 1107LR1107/2 | 1
SANTA YNEZ 1101Y52 | 1
SANTA YNEZ 1102320270 | 3
SANTA YNEZ 1102Y18 | 1
SANTA YNEZ 110477098 | 2
SARATOGA 1103LC40 | 1
SARATOGA 110413314 | 1
SARATOGA 1106340986 | 1
SARATOGA 1106LC24 | 1
SARATOGA 1107LC26 | 1
SHADY GLEN 11022232 | 1
SHINGLE SPRINGS 1104556218 | 1
SHINGLE SPRINGS 210511172 | 2
SHINGLE SPRINGS 210551738 | 1
SHINGLE SPRINGS 210819622 | 4
SHINGLE SPRINGS 210851474 | 2
SHINGLE SPRINGS 210911092 | 1
SHINGLE SPRINGS 210912392 | 1
SHINGLE SPRINGS 210913322 | 2
SHINGLE SPRINGS 21099372 | 2
SILVERADO 21022102/2 | 1
SILVERADO 210258626 | 2
SILVERADO 2102636 | 1
SILVERADO 210298998 | 2
SILVERADO 2103403102 | 1
SILVERADO 2103617828 | 1
SILVERADO 2104632 | 4
SILVERADO 2104708 | 1
SILVERADO 2104726 | 1
SILVERADO 21051306 | 1
SILVERADO 2105247660 | 1
SILVERADO 2105443258 | 1
SILVERADO 2105658898 | 1
SISQUOC 1102M52 | 2
SISQUOC 1102M54 | 1
SOBRANTE 11011101/2 | 1
SOBRANTE 1102690098 | 2
SOBRANTE 11031103/2 | 1
SOLEDAD 21017048 | 1
SOLEDAD 21027008 | 2
SOLEDAD 2105315500 | 2
SOLEDAD 21053720 | 1
SONOMA 1102441730 | 5
SONOMA 1105138 | 1
SONOMA 1105229588 | 3
SONOMA 1107844168 | 2
SPRING GAP 17029280 | 1
STAFFORD 11011102/2 | 2
STAFFORD 11021202 | 2
STAFFORD 11021258 | 1
STAFFORD 1102524 | 2
STANISLAUS 17011701/2 | 1
STANISLAUS 17011812 | 1
STANISLAUS 17017144 | 1
STANISLAUS 170179826 | 1
STANISLAUS 17021702/2 | 1
STANISLAUS 17021850 | 1
STELLING 1109589102 | 1
STELLING 1110LL72 | 1
STILLWATER 11011320 | 1
STILLWATER 11021102/2 | 1
STILLWATER 11021466 | 2
STONE CORRAL 1108255186 | 3
STONE CORRAL 1110894956 | 2
STONE CORRAL 1110975698 | 1
SUNOL 1101MR299 | 1
SYCAMORE CREEK 11091109/2 | 2
TASSAJARA 21032103/2 | 2
TASSAJARA 2108D520R | 1
TASSAJARA 2113MR276 | 2
TEMPLETON 2110307832 | 1
TEMPLETON 2110901690 | 1
TEMPLETON 2111686138 | 2
TEMPLETON 2111A66 | 2
TEMPLETON 2112R28 | 2
TEMPLETON 2112R80 | 1
TEMPLETON 2113641367 | 1
TEMPLETON 2113A08 | 1
TEMPLETON 2113A32 | 1
TEMPLETON 2113A70 | 2
TEMPLETON 2113R82 | 1
TIGER CREEK 0201201/2 | 1
TIVY VALLEY 1107584840 | 2
TIVY VALLEY 11077380 | 1
TIVY VALLEY 1107822606 | 3
TIVY VALLEY 1107869946 | 1
TRES PINOS 11114032 | 2
TYLER 11051704 | 4
TYLER 110585132 | 2
UKIAH 1111433984 | 1
UKIAH 11131113/2 | 1
UKIAH 1114528 | 1
UKIAH 1115534 | 1
UPPER LAKE 11011101/2 | 1
UPPER LAKE 1101660 | 1
VACA DIXON 110540092 | 2
VACA DIXON 11059792 | 1
VACAVILLE 11041104/2 | 1
VACAVILLE 11088762 | 2
VASCO 1102546328 | 2
VINEYARD 2108MR172 | 3
VOLTA 11011516 | 1
VOLTA 11011568 | 1
VOLTA 110180454 | 1
VOLTA 110185234 | 1
VOLTA 11021504 | 1
WEST POINT 110236676 | 1
WESTLEY 1103237522 | 1
WHEATLAND 1105248490 | 3
WHITMORE 11011101/2 | 1
WHITMORE 1101903576 | 1
WILLITS 110434008 | 2
WILLITS 1104934 | 2
WILLOW CREEK 11032936 | 1
WILLOW CREEK 11037514 | 1
WILLOW PASS 11011101/2 | 1
WILLOW PASS 21082108/2 | 1
WISE 11011101/2 | 1
WISE 11011404 | 2
WISE 11022230 | 1
WISE 1102307494 | 1
WISE 1102697216 | 1
WOODACRE 1101404 | 1
WOODACRE 1102137662 | 5
WOODSIDE 110147872 | 1
WOODWARD 2108R2860 | 1
WYANDOTTE 110213044 | 1
WYANDOTTE 1103640652 | 1
WYANDOTTE 110738438 | 1
WYANDOTTE 110913052 | 1
WYANDOTTE 110979932 | 1
WYANDOTTE 1110747922 | 2
ZACA 1101M82 | 1
ZACA 1102Y02 | 1
N/A | 3
Total Result | 964

## CPZs
CPZ | EPSS Device Global ID
LAYTONVILLE 1102538750 | {22042EBF-768B-4F6E-A0FB-8BA05EA6F8F6}
WOODSIDE 11011922 | {26E85C09-0B57-42B9-B352-ED273600E95D}
FAIRVIEW 220799096 | {55278842-270D-4261-9B21-666405A19DF7}
ROB ROY 210410930 | {6FDB7B55-5D84-4478-9719-37334B4F5477}
MARIPOSA 210110990 | {8667D6C6-0139-493E-962E-C5EBDBB9ECAB}
POINT ARENA 11012637 | {827A54D0-0188-46E1-B6F0-E7D696DF4D89}
BELMONT 11104845 | {D5010A07-EC1F-422A-818C-56120CF28FE6}
SWIFT 2110XR366 | {10854A52-7EF2-416D-830E-BF803A6482A0}
JOLON 11027040 | {15367F9D-D171-45F6-9CB4-6F5003394A6D}
MENLO 11029110 | {2ADB84B9-4752-4713-BF49-15F96D94E1DF}
HARTLEY 1102841676 | {5D95B927-2424-488D-993D-ADBE978C5596}
PETALUMA C 110835452 | {D67283F3-E166-4B71-B1F9-990D049050F3}
PAUL SWEET 210510290 | {33AE2657-6F42-4109-A970-89EF5E991C73}
STAFFORD 1102784704 | {5DA8991F-2CE2-4FD2-84E6-8E0B8213A71A}
WYANDOTTE 1103CB | {729134BB-0DFA-4145-807F-650A6E064048}
MARIPOSA 210237282 | {9C7CA36A-A220-4889-B18C-7665D5C736E3}
GREEN VALLEY 210112130 | {A0B73F98-66D4-44F0-A30D-DD6726111A66}
BELL 1108467470 | {35B30399-E588-44B0-B481-56F6CD9688B5}
SWIFT 2110XR332 | {DF04272D-0020-4DFE-BB56-C7BF45BF962F}
CAMP EVERS 210511010 | {F21FA11B-160D-41F2-AA17-7452280F39DA}
TEMPLETON 2113A24 | {F76D7225-917A-402F-BB98-F7057EA3149E}
VIEJO 22022179 | {BEBF2F35-AA76-45BC-AFD8-E27852839913}
MONTE RIO 11135026 | {2E6DCA70-6B36-4F65-B853-AA4AC3CF0E30}
WYANDOTTE 110737472 | {B3E100DA-AA63-42D1-94E1-A7F9E0DF29D9}
COTATI 110361736 | {BCD422E2-9AE0-44D1-BF49-26A0E5D7C844}
WEIMAR 11012740 | {DA254098-CE2F-4B1D-8DCD-E2A142ECA867}
JARVIS 1111MR121 | {F5BF7E7D-4C96-4918-ABEF-C33B63B5DD64}
GANSNER 1101590690 | {2EBA9C84-1564-4E97-B683-C3C5B09E3911}
CALISTOGA 110266730 | {2FC93923-0AF8-4A4D-9F96-EF0ED8AF2245}
PETALUMA C 1109373772 | {485D794E-EDB7-4779-A265-326DD68DD55C}
MC ARTHUR 1102542920 | {937AC6EE-B826-41A2-9509-4DF206B104A5}
SANTA ROSA A 1104220 | {97A379E6-C657-4B3B-9AC8-B4B0F3BA119F}
OAKLAND K 1104432850 | {14CA8224-5AC7-4834-81C3-26558D7F85B9}
SOBRANTE 1101L534R | {25DCD8D9-03C2-4BC1-93F7-DF5BB3FCC448}
SAN LUIS OBISPO 1107V60 | {331D14B2-6B0F-4273-9F56-8DD687C4B860}
PAUL SWEET 210398594 | {BA3D6A76-5335-48A7-9116-A38FBA76779B}
SHADY GLEN 11022232 | {362CB776-12CD-4A6D-89F4-5301B9D37C1F}
PETALUMA C 1108233646 | {380213DC-12AF-4B84-9312-495B969AE9CC}
PIKE CITY 11011730 | {5771C40B-154E-478C-BBED-0818A68D33F0}
UPPER LAKE 1101CB | {6A48DD4C-8096-4848-9316-CAF03427E24D}
WILLITS 1103964 | {B6068DE4-2B76-4559-A97F-83EC4465ECB7}
CORRAL 110236666 | {D6BA7AB0-BD1E-4258-B5D5-B64D6E99400B}
MORGAN HILL 2104CB | {107D0CE4-0125-4C25-9DF3-3408566B030B}
GIRVAN 1102212096 | {2CF3750C-AFAA-443E-A704-CD883AA64DE4}
ATASCADERO 1103A46 | {614AFF73-1972-445B-AB78-45C825B90AEF}
POSO MOUNTAIN 21014456 | {80FE859C-5651-4408-BF07-1945D67AD54A}
MONROE 2103224 | {18B04DCD-9DDD-4C1C-AC8D-731B4880D7B2}
MT EDEN 1112MR537 | {A5398856-385B-4671-B566-17D8F81D2C22}
STILLWATER 1101CB | {05FAE411-CB1F-4ADD-9163-2A2B0A61C7F7}
ALLEGHANY 11021101/2 | {303E53EF-22EF-468F-BD54-C029D47A56AA}
BIG RIVER 110155402 | {2D8E8FC7-3A5C-40AE-8F67-02A91CEAEC16}
OILFIELDS 11037064 | {8A139B57-6162-459B-9D12-F430854EC2EB}
HOLLISTER 21054724 | {8EF9C157-EB82-4F95-9143-D4D285784E19}
OAKLAND X 1104438648 | {51A41992-B3B3-41BA-BF69-679DAA3E243C}
SAN JOAQUIN #2 110310320 | {6E730337-737F-4AF4-89D0-F209BD78A056}
SYCAMORE CREEK 11112014 | {9FD8CC5B-B764-4FC0-90D0-B9293DA570EE}
FULTON 11045016 | {AC56E29F-28CE-4D76-8621-1CA9BB136C25}
HARTLEY 110194178 | {33AF121E-F118-4B6E-94DA-FB39FA49A86E}
ELECTRA 11024756 | {7D7E61A9-DD15-4C94-B46D-9A82D231AEA5}
DIVIDE 1102M46 | {CA16F48A-6A4D-4E2F-9307-EE7712739B5B}
EL DORADO PH 210219542 | {D823F384-3D02-4716-90A2-5DA25C95DCED}
COALINGA NO 1 11099210 | {1B415827-7E73-4327-8D34-697190EF078A}
MC ARTHUR 11011544 | {2548B457-03C9-4EEF-9E95-D0AA3CBA5A67}
COVELO 1101430286 | {64F3E707-0C89-449C-A14A-0CB9EA1C7E88}
MORGAN HILL 2105345099 | {2DBAAA9C-8985-4692-9A1B-CC370D239D9B}
OAKLAND K 1101CR170 | {8CEAFBDA-9CAF-47DF-A93A-B3DE193C02EB}
CHOLAME 2102X16 | {90DAAFCD-8A40-42C4-A489-C7D86439D101}
LLAGAS 2104XR148 | {C84A9225-11AD-48B0-B13C-5F9DBEE07DEA}
FOOTHILL 1102CB | {CF5272DC-8419-42E3-A72F-BD395166C5DF}
BUTTE 11032422 | {F6CF6B5A-1E51-4A8D-BE96-2DD1B8FF14FE}
BELL 110950506 | {085B8A15-383C-4AC7-8C00-A9FA8BED6EBE}
CURTIS 17039210 | {28A07299-BAB6-4846-84FA-366E13AEFEE9}
KIRKER 2103P524R | {F88B8CE0-AB57-498A-8D97-A3755A2B41A0}
NARROWS 21052228 | {460117C5-52D5-4539-942E-65301ACAACE9}
VINEYARD 2107MR332 | {5E4EB8F1-F20C-4A10-9616-09E586C03349}
MORGAN HILL 2109XR246 | {601835A0-060D-478B-8A86-7129055F5CF4}
SAN CARLOS 110479774 | {84501BB6-0E8B-48DF-8950-A9E642A52FF8}
FORT BRAGG A 1102816 | {DCB2091F-52D0-405B-8DDE-82750DB61471}
BURLINGAME 04049066 | {585506C1-ED3B-4FB3-84DA-FABB2641F074}
HALF MOON BAY 11022032 | {04338CCA-7EF9-409D-9ECF-B4834D579CE2}
SONOMA 11061678 | {80158D87-8FBA-4904-925F-F73ECFE1E50A}
MONTE RIO 1111240 | {561B7435-E1A2-417A-BAD2-8DB925A728A4}
PEORIA 1705CB | {7B5B2CF8-2901-483C-B55E-83E22B23519F}
PAUL SWEET 21065178 | {7E071814-6E26-47AC-8D93-17E4616D1F83}
OTTER 1101440 | {9B3F8B66-8E8D-4C3E-B30C-F806C7A06324}
SILVERADO 21023010 | {B8F94D37-4665-475E-83A6-71024C2C2EB0}
SANTA ROSA A 1110184 | {422CE5F4-0FBE-4EEC-A8C2-C4BEFA9D6650}
MORGAN HILL 2106XR324 | {2C56B704-0B48-474B-86AD-67CE86231708}
TULARE LAKE 1104884818 | {639991A8-D9DB-4B2A-B168-DB2687AE8157}
WESTLEY 110111736 | {A40369F9-5BFB-4A69-8B09-DA1A82DE5EFA}
MOUNTAIN QUARRIES 210192474 | {D7F1D14A-5B2A-48EF-B12A-9197AE3BCA5E}
LINCOLN 1101875554 | {BC430285-5DBF-4545-8AE8-96AF6071F68F}
WILLOW PASS 2107273996 | {85D52075-D52D-4D71-A7CF-355529F177DC}
EMERALD LAKE 0402CB | {A0667D06-51C5-41CE-85EE-7B2260B907EA}
FULTON 1104466 | {AE97AA30-6595-4674-A3E8-E3C81CE235CD}
RALSTON 1101CB | {C5ED9BB6-82EE-4A74-A509-3A42E5E8C396}
CALAVERAS CEMENT 11014786 | {CF62E6C3-07CA-4DD5-8099-332BF3F2B85C}
COALINGA NO 1 1108CB | {D0D57548-BFE1-4E51-8167-796FFB6E7A8E}
MORGAN HILL 2109XR104 | {DECA5724-8C2D-4F8F-80A8-75B013DC4D0B}
PIT NO 7 1101CB | {E4590054-53CD-4399-A96C-42C934E0E3BE}
NEWBURG 113397612 | {1B3C973B-E8C8-4CCB-9A5F-D4D21840CBA9}
EL DORADO PH 210152456 | {20EA6D57-AE8A-4389-B5E9-F8A1FC109811}
PUEBLO 110548264 | {2AEE294B-FE8D-44F1-8029-584BDB7857EF}
HORSESHOE 1104CB | {3D4378F9-B822-4985-B4DC-F977157ECBFD}
COTATI 1105136 | {47497F55-F48D-47C7-AAFC-7B07673C8B7F}
TIDEWATER 210487978 | {F47CA250-FEC5-4A9D-A7B7-CD6372963F55}
OCEANO 1102V56 | {6A98D8AD-262A-4E43-B52C-E7FA164E1E31}
PETALUMA C 110948000 | {762F2724-D687-4C14-8C14-CCCD968810AC}
OLETA 1102799924 | {B8897444-5751-4E50-98B6-2ADB95C6C270}
SAN RAFAEL 1109535284 | {292E168B-A807-4BEB-8205-853DD377A6FA}
INDIAN FLAT 1104CB | {8FE2B2A5-53AD-4D02-8B28-25A33ED98DCB}
SILVERADO 2105359428 | {9FD052B0-6B15-4CAB-B530-047A5976AD91}
HIGHLANDS 1104CB | {EC0CBAAC-D25D-4166-8326-CC1A005227F9}
ANDERSON 11029792 | {F240E67E-FE6C-498C-BF9F-54CAA8C204DD}
PINE GROVE 1102467560 | {0D3BE776-7F21-48C6-8A4E-A95714C0EA5F}
HIGGINS 110332120 | {42C0044E-B495-4983-9439-0351AC9E28F8}
RINCON 1103568 | {A91227FD-6BAA-4D3E-82C2-58CC21F46A65}
PLACER 1101CB | {D36692F8-5845-4D8F-B564-14537DDF3E03}
WOODWARD 2108290010 | {8476058D-CCFA-425A-8D9D-8591EF3E3149}
LINDEN 1103542460 | {20BF9716-345C-4355-8648-C5A90D0DDDB0}
COTTONWOOD 110131500 | {29DB4A9A-9909-45FE-9CC1-C3F1A6A44799}
TEMPLETON 2110R02 | {43D83959-6253-49E9-BD6A-065B7EF0ABAF}
BRUNSWICK 1103234378 | {69E159D4-B5BB-47CF-962F-03601F5F22F3}
NAPA 110549856 | {A567CC7C-BB96-40C6-B54C-7AC9DFF3A542}
PINE GROVE 11026080 | {B48DDE03-609C-4554-A3F2-3D029A190740}
GEYSERVILLE 1102CB | {B7169D14-D576-4EBC-83AD-DD429DE5E777}
BONNIE NOOK 1103CB | {C90BDB25-C8EE-44ED-88EB-56C4AFDDB087}
OCEANO 1104Q08 | {D6547032-0BCE-40E6-B529-0CCA8B7E9C38}
SOLEDAD 2101775342 | {F417DA2A-C751-4206-9B93-7957CC7AB9E6}
SANTA ROSA A 1104716 | {F8BEFC4B-3D6B-4BB7-B77D-7582CBA169BE}
HOLLISTER 21054048 | {522758DC-D04C-45F3-86B0-6920B5847932}
SILVERADO 2103507513 | {5DB6403E-B6A2-4C39-88E1-26D243AA9FAC}
RINCON 1102228730 | {A2A06826-B5AC-4037-94EC-F135DC826294}
ANDERSON 1103CB | {87B1630C-320C-4426-9018-625251B99E73}
OLEMA 1101334 | {A82D843B-628F-4D51-ABE5-7DA46EAA8FF0}
VOLTA 110185234 | {ED0B6774-A707-41C7-AD0B-86162B275429}
POINT MORETTI 11015078 | {FA346406-A3D0-4066-8116-4806F77ED4DD}
POINT MORETTI 110110722 | {0A8CC9D0-C5F4-40DD-BD29-00E6CE7DAA43}
GARBERVILLE 11021510 | {1339ADD4-8465-4C5F-ADF0-25D79054621F}
SOBRANTE 1102690098 | {2B19DC4F-7A35-4B7B-9AF2-F2CF56BFB136}
CASTRO VALLEY 1107MR235 | {35AEE05C-849F-43E6-A066-12B4CE5002B2}
JARVIS 1108CB | {6E2BBEB0-5FF2-432A-87B6-19D6CB26C1C6}
FITCH MOUNTAIN 1111CB | {AA2E97C7-3759-4D9E-BC19-D9ED237F5DA1}
COTATI 1102464 | {E06C85FF-5B48-4064-AE0D-D34C585D0676}
FORT BRAGG A 1102265870 | {E0FAB4E0-B6D5-48CE-BF78-A57BBF22B01A}
RESEARCH 210263274 | {17B0EA25-D73F-4786-903D-45184AAF8053}
VACAVILLE 1103CB | {404CB668-CECA-42E3-95F0-FB6161DA4FDC}
HALF MOON BAY 1103461558 | {5B63424F-7E68-45B3-A042-84BE563149F0}
MILPITAS 1109XR524 | {648B5D01-67D3-492E-989C-FF81490722DD}
NORTH DUBLIN 2103CB | {7713D0FD-BB09-40ED-B7D7-E260577647D4}
WILLITS 1104936096 | {8248C880-166C-430F-A087-7EE0312E38BC}
BURNEY 110297318 | {C4DDB13D-8C8F-4D3D-860D-833D982C6826}
REDBUD 1101754544 | {084CA147-3467-4FE1-A862-8038A9834EE2}
PLACERVILLE 2106935216 | {2AFE09FA-88B1-4B78-BACA-DA079C6170B5}
BRIDGEVILLE 1101365380 | {FC8DA5F1-E256-452E-840A-DB2CC55A41C4}
ANITA 11062462 | {89E1C548-ADAA-4B04-80A4-5DCCECCCDB3E}
LOGAN CREEK 2102806 | {8700E55C-38C6-41AB-AF2A-3B50EA0B2E05}
EL CERRITO G 1112418480 | {F4711D50-C892-433D-B1D0-EB1B6E0C6AE7}
TYLER 11051536 | {8FC5AABE-9067-41E2-B562-CCB95292040F}
FORT SEWARD 1121CB | {9D061223-5B52-4134-9A27-9EB1E4A74BC8}
BIG BASIN 110112838 | {CC60F8EB-8583-4463-B38C-D2F869F171F0}
WILLOW CREEK 11035012 | {315E4027-C3C2-48C5-87DF-DFA709D95931}
NOVATO 1104676060 | {64CF78D9-1536-455F-B223-A7030F2F7FB3}
MORGAN HILL 2110814616 | {FEA8F80B-51AF-4084-A9B9-47D11430DD95}
TIVY VALLEY 1106CB | {36113653-5563-4401-879E-ECEBC9923AFA}
PETALUMA C 1109857148 | {42F8D929-F3A9-49A8-94C4-A1A9328D939B}
CLAYTON 2212334476 | {463B1668-4DE2-4C88-A747-EE241BC43F5E}
SAN LUIS OBISPO 110596874 | {5F18F1B6-CBB8-4C1C-BF98-6DFB5D98EA76}
LOS COCHES 110255146 | {C48784E3-4EDB-45E6-AEA2-4A807640BDC5}
WISE 110163199 | {919A8A04-B874-4A68-AF90-D4143250C76A}
MIWUK 170247143 | {976CA043-61DE-4F22-87BA-0696E25C4DF1}
PLACER 1104426944 | {A52EC61D-8C7F-4197-8472-76105B9A8A93}
SANTA YNEZ 1101Y52 | {CDC11A25-DBD9-42BE-AA95-70647385571E}
FROGTOWN 17021573 | {7D119895-6544-4FC7-A1BD-CC0A5D84976F}
HIGHWAY 1102700 | {17274A38-F8A1-462F-93E6-49EE52FB630E}
VIEJO 22019704 | {49931849-9CA4-43E6-B559-5E2CB6D2E2B4}
CHESTER 1101CB | {F5B87947-B1CF-4B32-AB2B-95DA61D92836}
FLORENCE 0401110836 | {013CB3A7-7F48-4CCC-AAF7-D8407E0657E6}
TASSAJARA 210865438 | {D91BF138-6798-4927-88BC-C1A382D4C37D}
SAN LUIS OBISPO 1104V14 | {25830136-A5D5-4A08-9B85-05018D7569FD}
SISQUOC 1101CB | {335463E4-7716-4BC6-BF55-B39E4654D44F}
SAN RAFAEL 1107434 | {7DB3B65A-9BC0-48E9-AEAF-56397C577A2D}
SNEATH LANE 11071277 | {8E15B458-F29C-4328-B8BB-225EB178302D}
MIWUK 1702S2247 | {A068179F-B6CC-4678-A4EC-AF469032942C}
EL CERRITO G 1110BR238 | {D5C37EEA-D463-430D-8618-04212D08A58F}
FULTON 1102258281 | {09E88888-5AC3-4010-8136-EE66FDCF2B20}
POTTER VALLEY P H 110564118 | {BE94A233-F70C-44A4-9222-81B080FDD6FB}
LUCERNE 1106526 | {BFEEA045-A307-47A2-9C2E-0B69ACE24065}
FORT ROSS 1121560 | {C44E173D-32C1-4900-92A5-AD54BFE2000C}
SHEPHERD 2111707358 | {043E8F07-84F7-4AE7-BB3D-18F6172375EA}
DEL MONTE 21042760 | {99475FCB-F6DE-46D1-A853-CCBB82A0015E}
SAN LUIS OBISPO 1108CB | {BB99A914-387F-48D8-919A-BB8BCFE90D9F}
MESA 11016111 | {8CD02839-6B9C-4A4E-A161-AF3A96F4F1AB}
TULUCAY 1101CB | {D5040DDA-C582-40B5-8A53-2E3901DC0B08}
OREGON TRAIL 110335002 | {E6157D99-E31C-4483-8F6B-FEB133AE35BB}
OAKLAND J 1102CR184 | {F0F7E9DB-942E-4AD9-8BB3-9A4EAA06963A}
TASSAJARA 210883368 | {F3272220-83F6-47EF-AA10-7270133DA2ED}
HIGHLANDS 1103520 | {20B5CFDD-9238-415D-BF03-7EE0B92100FE}
CLOVERDALE 110184088 | {58421E59-40D9-4FE6-B6D2-E336A596F8EF}
PRUNEDALE 1107CB | {9055CD6F-1385-4DAA-B189-3CEA20BFACDF}
PANORAMA 11023320 | {A631613E-AC26-415F-BA05-B8776DE457AF}
ORO LOMA 11063650 | {2CF9B0F9-24F6-405F-A3C7-E9E2A28497C4}
LLAGAS 2106CB | {36DDC7E6-DD90-43BE-A64F-8D62BC22EEA3}
SANTA YNEZ 1102320270 | {5627B063-B665-4EAB-9B4A-39C8A753C0BC}
MIDDLETOWN 11011314 | {6605C9B9-1E01-4CAA-B9F4-139E3DFEC103}
SOBRANTE 1103215046 | {6AFEB52D-9F4A-444E-B3FC-D10C077C8013}
MONTICELLO 110165454 | {9E39C048-EF22-4DAE-9CE9-DEC0330A8321}
PENRYN 1105154362 | {A58D8351-9C68-4CA5-80CA-5BE208F9F034}
BIG BASIN 11025066 | {A725B58B-37EB-4147-83B3-63635BC09A1B}
SAN RAFAEL 1101546438 | {D3437865-FD72-4BD7-976C-C052BE1AC57C}
BERKELEY F 1103162952 | {0AD46168-2B6E-4761-82AD-462845B00603}
ROSSMOOR 1106L522R | {35E6FC31-93E6-466C-8E12-BDEF19C3F3E9}
LINCOLN 2109CB | {4E6AFF3A-F560-4015-9A7B-59C83CDB47B7}
EL CERRITO G 1105CB | {63FDD22C-1D84-438C-BDD2-97E9627809B3}
CAMP EVERS 2106287578 | {8E63B9EB-959B-406C-95DE-C4CA49EAA042}
HOLLISTER 2102113634 | {AA026DE2-36FF-41BE-B277-D062A4C54501}
EDENVALE 2113CB | {CBC2E590-65E4-4DD8-9118-7B6CB910201C}
SANTA MARIA 1108M80 | {D0FCA825-EE19-45C5-82C2-01947841A1DF}
CHOLAME 11015939 | {47231439-CE13-4A31-BF86-1A2379821F62}
ORO FINO 11022096 | {458FC9CE-4CFA-459C-BFC4-3FAD1C0058BF}
BASALT 1106316302 | {4B4F529E-61C9-4763-88C9-BA9E643D6014}
ROSSMOOR 110845268 | {7DDF8536-9630-4E95-BAC2-3F8D7B68665E}
CLAY 1102CB | {D868AF66-93C2-4B3E-8187-2C428023C31E}
LOS COCHES 11027514 | {C48784E3-4EDB-45E6-AEA2-4A807640BDC5}
MERCED FALLS 11029460 | {0E4DE50B-9CB6-46AA-9EAF-66A90C70B824}
FAIRVIEW 2207P150 | {0F676DC3-CFF5-456D-B8E2-CAA231B3A90A}
PUTAH CREEK 11038362 | {520DA4C4-E38A-4EBC-850C-F11EB0848411}
WILLOW PASS 1101CB | {7CF27098-3028-4D6C-96BA-430FB7E80045}
GREEN VALLEY 210312656 | {80B98B39-6C55-4280-B2BD-3BF57A0B5E71}
JESSUP 1103728460 | {933860CE-81EB-48DD-96BA-C0297EF47CBE}
CHALLENGE 11015460 | {B23B77B2-F3D5-42C7-AB2B-D58C03818E3A}
PASO ROBLES 1106726154 | {C43AB9E2-6528-4AA3-BC20-CCEFDDDA1380}
MADISON 21019512 | {C556C375-7B0E-4693-B801-A5D6F39CB3E2}
LOS MOLINOS 11011308 | {09A4B9E8-989B-4DA3-9154-EF01A44BB71B}
RED BLUFF 1104CB | {2E1FA774-5A9F-4570-9AF6-F0EFBD272BA5}
MARIPOSA 2101309438 | {050E06AF-91BE-429B-BDFE-3EAD80F24863}
MIDDLETOWN 1102998 | {5F8C3D5E-6EE2-44BA-8DAB-1423918270D0}
BEAR VALLEY 21014160 | {853E569F-DA3D-4A9C-B01E-E103347AC121}
VASCO 1102546328 | {940E4DBA-804F-4033-AFB1-1900E1E5DF1D}
ANITA 11052572 | {BD567EF6-1FB2-4D01-8EA9-A26EEF378E91}
PUTAH CREEK 110267858 | {14F48B8C-8A8F-4490-B11D-9FE802AC416A}
FORT ORD 1101CB | {66CA8537-4E7C-48FF-82D7-109E7EF7B7FC}
BROWNS VALLEY 11011268 | {868A573A-DC6D-45C3-92E0-27ABE99A6BF7}
TAR FLAT 04023144 | {C73A5D7F-692C-413A-8D72-DC21C7152C9F}
HILLSDALE 040485812 | {2DBE6767-7D56-4562-8F78-31E59118A4C4}
CAMPHORA 110177978 | {31472151-05E0-42A0-B884-E32FC8EACB46}
HALF MOON BAY 1102350336 | {61D17DF6-ADDA-4D95-BD25-C42B9D51757B}
WOODSIDE 1101CB | {74C9689B-27E2-45AE-B69F-F01C8E2CB358}
KERN OIL 11062794 | {6ED1033E-54FE-4DD5-BA1F-9025AD47E265}
MARTELL 1101473004 | {2C34AC51-01A3-44C9-B45A-F5786A7BA8F0}
GREEN VALLEY 2101535998 | {9588524C-2A8E-4126-AE5D-984A8FAAE76A}
LE GRAND 11107120 | {B9B7E2CF-8396-4913-AA14-43F1BD9F0A32}
JARVIS 1108MR366 | {4D5666F5-BD84-4CAA-B8A5-49AFE5BCCE43}
LAS POSITAS 2108631066 | {A35687F3-7828-400B-B177-522C0D2F58CA}
WOODSIDE 1105CB | {B0B93653-ABAA-40D2-863C-C601369FC194}
COPPERMINE 1104R3200 | {D5328BB7-8D1B-4713-8DFA-263EA71DC9E2}
CAMP EVERS 21065300 | {30210CF9-C9B7-4E0D-B350-23AD99A7DA9C}
MCKITTRICK 11013043 | {5A307946-5CD5-4050-AB0D-2E455B17B341}
FROGTOWN 170236870 | {94EE7076-462E-4300-BB9C-E1B2A1AE599F}
HOLLISTER 21054042 | {1E6DC745-CC49-441C-9C9B-BCE1C0BE079C}
WHEATLAND 1105248490 | {373720FB-6F75-4350-A081-94440166CEBB}
HUMBOLDT BAY 1101898396 | {91BBB89B-9333-4A31-8E04-1784413A7D4C}
TASSAJARA 2104CB | {B05D8AC6-2B7C-4E68-B328-BD625ED75426}
CLEAR LAKE 110181976 | {4B824BDA-3530-4F86-B304-5BB8EAFD0730}
DOBBINS 110169722 | {DCD6C7A6-BCDE-42A2-9036-021FA6ED047F}
COTATI 110387402 | {EEE52A91-AF03-4B18-9CCC-F7F6825D7052}
TEMBLOR 110459326 | {29FDF678-E116-4F18-93AB-072742A94198}
SUMMIT 110249484 | {4D17090F-B031-42D9-8E52-3D09021DC1AB}
SOBRANTE 1103CB | {D5F18742-859C-45AE-BB95-2396135F0809}
MIWUK 1701CB | {E8F5F8AF-6EC9-4C69-835B-E53C764AC834}
BRUNSWICK 1103173934 | {04D37AC0-1325-4EC9-B6FB-C903BA33F6BD}
MC ARTHUR 1101501106 | {FAF0B739-3196-4C1D-A8BD-B6B12F707FEC}
BIG BASIN 1102243760 | {7DF78B7A-3D58-4011-B365-74BA17A842F7}
BAYWOOD 1101CB | {82D72170-020E-4DD7-9C9F-960EDB0862CE}
EL CERRITO G 1110BR126 | {D5C37EEA-D463-430D-8618-04212D08A58F}
AUBURN 1101173014 | {ACC7CE4E-E9FD-4F32-956F-F6FB27435C5C}
MONTICELLO 1101718 | {CFFE2061-0111-499A-9D10-C50262E92A10}
CAROLANDS 0404CB | {F73FE32B-0064-4963-BD0F-96E252B7B701}
BEAR VALLEY 2105454432 | {11DB8C84-C8EE-401C-AB12-1A2E81A02CED}
MC ARTHUR 1101CB | {180C9221-B3D3-4A32-9DB9-CD8B7E0EF9F1}
CARBONA 110114204 | {03E03B20-8D28-451C-9701-95F4851E85CE}
MORRO BAY 1102W22 | {52C280BB-FF66-4850-B734-B05EEFB600B7}
ALTO 1124430 | {5B9950E9-6C0C-44EE-B414-F2773560C367}
CAMP EVERS 210660122 | {CCDF3A25-AE56-4EB7-B245-ECC2A1643713}
MILLBRAE 110453676 | {78D6C5D5-9F2A-45C6-A0D6-6C9E91038F45}
COTATI 1105701873 | {970A448F-8FB4-445C-86EA-CEC681F3DA87}
PENRYN 1106980728 | {1524F2FC-2DED-4951-9267-9B0CA2F011FD}
PETALUMA C 1108883512 | {177BEE80-A728-4F61-A7CE-6DDABA69C9A9}
MONROE 2107428720 | {3D15A0FB-7F79-449E-9100-AEDACD615B82}
EL DORADO PH 2102CB | {876266AC-37EA-414C-92FC-94A2ACD4EB2D}
SAN LEANDRO U 1114213524 | {A807698D-F940-498F-A1CC-0E26E202721D}
MENLO 1102223286 | {ADCE2FC0-63B1-4997-AA36-C71BC01F8536}
PIT NO 5 110190846 | {B00B32D2-7E6B-47E8-9895-8153D924AA94}
MONROE 2103408 | {D546C25E-2665-4E0F-83E6-19A6D0D70A7D}
CORTINA 11013056 | {E3B77E93-BB57-4588-891B-4456F675EF56}
MIWUK 170111800 | {CA297791-685C-4EDD-BB53-30F381A39ACF}
CLARKSVILLE 211019692 | {E7EDC231-ACD1-4AD9-A89B-5DAED0E6D6EA}
IGNACIO 1104450582 | {F91156C0-E294-4BD1-9245-277084BD5819}
CALISTOGA 1102306462 | {B6480B23-3B7E-4A3F-9C7B-82F910A25330}
UPPER LAKE 1101660 | {0F0F521B-1DED-434B-B495-1C9D87139123}
WILLITS 11021270 | {1C1CA89F-8D6E-4D8E-B038-38C87CE5A599}
PARADISE 11061212 | {3A3C4FDA-6EA3-4A05-AE15-F95A09F30BC3}
RIO DELL 11021504 | {6F9BA8E0-5DE1-4B25-826B-D7A1564B0177}
FORT BRAGG A 11021226 | {75E57175-6FC2-4C18-9858-49FEBB55AE91}
CLARK ROAD 11022044 | {62022298-C96E-4026-AE43-0F12DB277F1C}
SAN RAFAEL 11081262 | {B486F4D0-4246-4914-B521-4CE6A759247F}
CAYUCOS 11014701 | {5CFEA468-EAFA-49AC-B046-6E19D81021D8}
ORO FINO 11022090 | {D1240401-ECAA-4BD1-99E5-871723028078}
TEMPLETON 2109R50 | {E9F4AFB5-1012-46CB-93BD-65999630DF83}
FORT ROSS 1121612266 | {F813F206-BF9E-4739-A94F-434D2CFC229C}
HUMBOLDT BAY 11024724 | {0A5740C1-9196-4281-8753-B21C8EA0160F}
PETALUMA C 1108CB | {184EAEA4-EF9D-4F25-94EE-091BC560403A}
PUEBLO 2102656 | {95F0930E-F4E9-4090-B429-18E6DA1F891D}
FORT ORD 210637286 | {9AA16F48-39A4-4006-910E-3E37752DF955}
FAIRVIEW 2207M501R | {9F1312F5-B448-48CC-A9C3-FC2DE03C4391}
WILLOW PASS 210721135 | {AAC60A33-2BAE-4745-8C6C-2A17FF968240}
LLAGAS 2106XR146 | {B73F7608-4D30-4162-A279-F1B71A76D86D}
LAS POSITAS 2108MR190 | {BBAD7CA8-9930-4EC0-8393-CDE6447A6BA4}
WYANDOTTE 110313018 | {FD9CCA92-C052-4A36-88EE-05418588C974}
PANOCHE 110390540 | {2A3253A4-EBC1-4720-AE66-B68045C8C594}
MONTE RIO 11133970 | {53EC2261-1200-4127-A3BA-F52DA74219E3}
SALT SPRINGS 21023118 | {56415AA1-122C-4BC6-8C7D-172F2B1EFCC0}
CHESTER 1101922138 | {F5B87947-B1CF-4B32-AB2B-95DA61D92836}
HOPLAND 1101768 | {CF814E69-077B-44BB-9617-D51226ABE508}
COTATI 1103148 | {E6932BC8-83DE-4484-A9F8-B83591D802E2}
CURTIS 17058110 | {09598188-CE5A-44C7-8CBD-CFBA0AA34580}
CHOLAME 1101R96 | {0F26305A-B95B-48BC-93DA-531056D0E973}
VINEYARD 2110CB | {14A8794B-8A75-4FC8-9957-3059A6D6C76B}
ECHO SUMMIT 1101927328 | {14BBAC88-26D3-4F29-8425-274D619391ED}
MAXWELL 110545180 | {F3456836-F540-4C5A-8C4E-BB2A14482B86}
WOODACRE 11021280 | {2D7883CD-6608-4310-8AB5-FA60A939C766}
PETALUMA C 1109664732 | {485D794E-EDB7-4779-A265-326DD68DD55C}
CASTRO VALLEY 1107MR336 | {AD5F876C-C0A5-47C7-B722-6D39867E5D84}
SOLEDAD 2101823854 | {C9EB66D5-F17E-475C-84E3-A6D209341971}
SONOMA 1106510055 | {E5FD210F-062C-4CDB-BD2B-F92685B10DF5}
DUNBAR 1102528 | {FB8DED4F-C1A4-4542-AF21-D3D770C633DF}
MOLINO 1102111666 | {2D9442B3-0FEF-4574-B297-2133787A6E1D}
SONOMA 110749132 | {B66DFA6A-6131-4186-B4AB-0BA7B611120F}
CABRILLO 1104765792 | {A8C0DCB1-6987-421D-A6ED-00C50AACF3B4}
FROGTOWN 17027108 | {3530973A-E1ED-42D6-80CA-474C64476B90}
NOTRE DAME 1103407486 | {611B5D12-B194-497D-815D-46B8449CCF48}
HORSESHOE 11061680 | {6467CE55-E29D-44B6-B77F-76D86FE9D5B0}
SOLEDAD 2104413916 | {FD7651EF-898B-49C0-B621-C2068E1D4495}
FORT ORD 210736596 | {121773FD-4C4B-4842-BF5D-136BCB9BFB8D}
PLACER 1103429574 | {3FC818D4-1421-4E7E-A0F8-41C3D62E44F8}
BAY MEADOWS 2102CB | {7B48B738-B738-4F2B-B0D7-4D191D860D4E}
OAKHURST 110377384 | {B3D10DC1-455E-4DDF-8795-B604423C3B61}
COTTONWOOD 110335470 | {E7F7F25C-AE9C-459D-9EB5-32BCE8602EF6}
SONOMA 1104412 | {13C5D467-3A5D-46D1-9164-0C6474ACC9E0}
RINCON 1103655192 | {40BB98CB-5E98-49A0-9B1A-45D346011806}
CASTROVILLE 210436922 | {5DE92B6D-4604-444B-8D65-AB7A469C1FE2}
SAUSALITO 11021268 | {8F1701AB-AC20-48A5-8989-61140107D373}
COTATI 110259258 | {94E0088D-6FDA-42A4-A01C-471E05EB28CA}
BELLEVUE 2103648 | {BB094C57-2223-469C-ABF0-9ADC89223899}
MENLO 11029018 | {D2B478D6-3AC8-4C31-9F67-86F64FEB69F8}
SARATOGA 1107167792 | {E731F6BE-8220-43FF-B403-4FCE65138051}
GOLDTREE 1105912920 | {2BB441D5-FA7B-41CB-B4C4-3BB6BA3702C5}
FORT ROSS 1121124 | {228A6257-66FD-4F4F-AA34-7D22FE084DBC}
RED BLUFF 1105161818 | {31D1DD7F-CFDD-44BD-88FD-B9B13228B34E}
HONCUT 110275350 | {3ECFF3DB-033A-4FC4-B37B-A365EAF3EE98}
WYANDOTTE 110366146 | {44DEC261-543D-4709-894B-61B8ADC18491}
STONE CORRAL 11087100 | {7C3F27CE-B3FE-4A3A-A517-4F1EC2F3B587}
GREENBRAE 1104300 | {84506FE0-5799-4537-9C92-AE6186A1DEC5}
SAN PABLO 1106CB | {974C14BC-8049-48F9-B115-F54945EEB110}
BUTTE 1105CB | {99D60B56-5961-4789-A3E0-D520C3413381}
HARRIS 110866386 | {9A3D8818-9236-4C74-9C67-0369FA031A48}
FLINT 1102CB | {C6A91D98-B704-457B-84C0-0DADC269F3D4}
HIGHLANDS 110484640 | {E2438D63-9836-48BB-91BE-1736CBE6A21A}
WILLITS 1104188268 | {F170EA1C-ED28-4FA0-9674-709AC3DC1CC0}
MONTE RIO 1113180 | {15C2C6AB-DE9A-4E17-8C2D-97DC9B78100A}
MESA 1103206794 | {6E34D557-FB41-44E6-B10D-DE75166431A4}
VOLTA 110253130 | {1EA4A0A1-3D5B-4E8F-B75B-661AF3FEE831}
OREGON TRAIL 1104CB | {8048141D-B1E9-414C-85DA-8DE818EBAD4F}
BASALT 1106267462 | {0C9DEF06-9AAB-4128-9810-85E010FF7C1A}
CAMP EVERS 210610718 | {EB3DBCD3-2E38-4DBD-98AD-E58F823F41D1}
BLUE LAKE 11024624 | {DB40B2E8-0171-47DD-8BAC-EDA4F7194556}
PASO ROBLES 1103CB | {5A5ABA2D-583E-4687-9FE8-7872A20C2CCC}
BRUNSWICK 1102940 | {8A1F3383-8C42-4458-990C-2355B321D3F3}
SAN LUIS OBISPO 1107248566 | {93AB4944-1A1F-422D-B748-968CE7493B5C}
WOODWARD 2108CUS1164 | {61F2ACD6-570E-4D22-AC3A-276FF7469BBF}
LOS OSITOS 210366936 | {29735F50-C5F4-4F83-8013-D3D04A895748}
TULE POWER HOUSE 1101CB | {35723AC1-565E-4787-875F-B05907FDAE4F}
SAN LUIS OBISPO 1101483444 | {6095BEE0-0C36-47E1-939F-BFF38B2ABD81}
CAMP EVERS 210612760 | {77218484-2483-4A3A-8ACC-0336A0ABECA8}
SPENCE 1102990464 | {E5160FAE-67B2-410A-AE3B-822157B58701}
FORT ROSS 112137326 | {56EC8BE0-B402-4A7D-9076-C44EBD9A9DDD}
OCEANO 1104V36 | {612579F3-BEE6-43F6-ABF9-9C9C3F31A5CF}
FRENCH GULCH 1102CB | {68ED899E-4033-413B-A72A-EE83BDC8B804}
FAIRMOUNT 0401395180 | {6981AFAE-EB4D-4375-A997-CCC0FDE33FD6}
ROSSMOOR 1109CB | {A19250ED-73EF-497C-80D4-3643AA1817C6}
HALF MOON BAY 11016369 | {2DBAB1CF-D3D1-4CC0-A406-0CDA12AB2548}
ANNAPOLIS 1101CB | {26E5272A-CBC3-4332-B0D6-5C00B9086880}
STAFFORD 1102524 | {890FBE04-45F2-477D-ABCA-3FF18127DAFA}
PHILO 1102928 | {946F4845-815D-4480-AA93-F475D8FE739E}
IGNACIO 1103151462 | {A36BBD4A-24CB-4238-BDFE-096AC8C68041}
SAN MIGUEL 1106605393 | {AE0302DD-E961-46A4-9A94-0278CDDD5E25}
RAWSON 11031486 | {2BC26C95-B90F-49BD-888B-1F85DFF0BF79}
SANTA YNEZ 1101980192 | {CCDAB0AA-FC42-4576-8856-F9CCAB22AC0D}
BUTTE 11032208 | {F6CF6B5A-1E51-4A8D-BE96-2DD1B8FF14FE}
PAUL SWEET 210335240 | {BA3D6A76-5335-48A7-9116-A38FBA76779B}
HUMBOLDT BAY 1102741980 | {3D0CD5B3-E4C3-4E4C-848A-D16C0F741C16}
LOGAN CREEK 21022428 | {44523332-7517-43E5-BC5F-36858B2AD5AD}
MORAGA 1105116034 | {52D8B49E-A907-44B9-9C80-969531571B5F}
SILVERADO 2105658898 | {991CF770-C017-4F1E-B905-05B063249BE8}
DEL MONTE 21049500 | {9F487EDE-1254-4232-B1F0-1B8CB4720B05}
BERKELEY F 1105BR166 | {ABB7B77D-2EF2-4B3C-9B77-BF1774A4BD64}
DEL MONTE 21042032 | {C1DCB446-91BC-4976-8E19-E90A61136DD7}
DEL MAR 210584138 | {DD87F226-71D9-4417-928F-44802F1E6068}
LUCERNE 11034200 | {0AEE71D0-17A5-4B33-BC11-93FDB3F0422F}
LOS GATOS 1101950286 | {168FAC6E-221A-4D80-AD26-79821278B765}
FORT ORD 210779062 | {5AF19FAC-D5B1-4A0E-9483-EA04C351FFDD}
SARATOGA 1105CB | {0AC2A538-D1DE-4BF0-89DD-0FB685A31962}
MIRABEL 1101254 | {E6BD4324-CEC6-41E3-9006-EBD82C1FE66D}
CAMP EVERS 2105CB | {EE077F7F-8175-4265-8512-03731CF3E11C}
MILPITAS 1109XR208 | {1C76A5CB-14FE-4796-B246-F53503C2A0BB}
MIRABEL 1101688780 | {47D4786A-45B9-45D8-AF62-3522AA9D4ACB}
STELLING 111060090 | {1AB7CEED-5C4C-4BB2-AA34-33FF777E7C4A}
RESEARCH 2102D537R | {748A5B81-A79F-4986-90A0-2D101111DB07}
COVELO 1101536 | {7897A070-7C30-42E9-B1B0-EB5E015E733B}
MADISON 210123272 | {C4B928B0-1315-4EFF-A9DD-F47090119304}
PASO ROBLES 1104R56 | {3A535F79-B416-456C-A3C1-BEDA8326FF1E}
MORGAN HILL 2111419718 | {40B38A4F-7054-4A4B-BF09-F440B1202801}
WISE 11022230 | {46E702EC-9F9A-49D3-8D4F-660BC1315D70}
CLAYTON 2212614950 | {4884B072-CC16-4259-AE22-6A15B8CC59ED}
SAN ARDO 110265604 | {A30EDBA7-9AAC-4E4B-A35C-8F3268903239}
FROGTOWN 1702812366 | {4CE434B8-E02D-4920-A230-5B04B8D42C75}
SAN JOAQUIN #3 1103CB | {A6A3BCCC-F462-4ECA-85D9-4927341E1902}
BRUNSWICK 111094368 | {AC82A3F6-A35E-40B3-B30F-C23643AC0649}
LUCERNE 1106857174 | {64C6F4FE-9745-4B83-9BA2-6905B1D464FF}
SANTA MARIA 1110M44 | {E772CBEC-2F5A-43A3-91C3-8EE495E372D1}
SWIFT 2109XR300 | {17D989D5-D004-4CEC-9F17-89364403A1F1}
OCEANO 1102847440 | {45F26A7D-9F54-449D-A121-9094CE2E38B8}
FROGTOWN 17011623 | {32DE7714-2265-4DEA-9044-817FFC428BF4}
MONTE RIO 1113346 | {EA690835-9E38-4D73-A546-B5676BCE1BEA}
GREEN VALLEY 210136820 | {1058939C-63D6-4E6A-BE26-51405BD3A77F}
PIT NO 5 11011614 | {1BEC31F5-3F54-4C7C-921A-7E6673591BD6}
SHADY GLEN 1101898212 | {29EB973A-BC17-445F-AED1-F026327BAFBC}
ANDERSON 1101CB | {4FF91FEF-C966-4E36-B08B-C812EFC4BE16}
CURTIS 1701CB | {74641153-5847-4D3C-B484-25FD29972F96}
VALLEY VIEW 1106P182 | {772F24AF-7DA1-47C8-B6AE-4C4810E9D260}
IGNACIO 1105908 | {1C105F4C-AE80-4099-9437-85CB973612DF}
WOODSIDE 1104420146 | {39508B32-B583-4F3B-8AB5-C8A9DFC4FCD3}
FROGTOWN 170212282 | {3C80F4C0-E9A6-46C9-A594-5586FAD2CDE6}
MADISON 2101647730 | {9C777D0B-81EB-422B-9E3E-C0277E2A4B3B}
MARIPOSA 21021960 | {C88CD342-0019-4371-8FA7-CA6CF25A5380}
DRUM 11011602 | {4FA3034C-CC34-47A2-AF7A-8A1D1515E919}
CALISTOGA 1101CB | {07D5D1F0-E088-492A-95F0-C51ED4C7A4B4}
LAYTONVILLE 1102141962 | {24057538-792C-47E6-85BB-163CA71B1FC5}
WRIGHT 111084280 | {339E2C7E-2DBD-42B5-BF29-414F5F6E8F92}
SAN CARLOS 11048846 | {4B35CC98-8B7D-4556-87A5-A4000634AA4A}
SPAULDING 1101578852 | {4B4ECB86-924B-4487-850F-9E73F5ADEBBF}
HARTLEY 1101738 | {7E2F1938-FEBF-4ABD-86B8-56A7EC0C222F}
KONOCTI 1102806668 | {43499343-6FDA-499A-9065-0F9A4F778AB9}
CORNING 110238162 | {9739935D-6CDE-49DF-B214-4F89D603A9E6}
CALISTOGA 1101242919 | {A2E97EA6-1CE8-40C8-917B-02BFB4DB75BC}
WRIGHT 1110CB | {ABB28193-DF6D-40B9-BA16-1713A8EF4B58}
NAPA 1102561208 | {12961FC8-2125-43B0-A892-045A87E2B620}
OAKLAND J 1106CR330 | {4808F0D1-7684-45A4-AA78-2B2D6EF06890}
COVELO 110146208 | {1E92B113-D351-4051-A3ED-221149B2FA2D}
HATTON 1101399900 | {4ACA70E2-9D9C-40F9-8434-15B06F65DC14}
HARTLEY 1102CB | {60D33697-692D-4938-96CD-E53257AEC032}
BEN LOMOND 04015206 | {93B6E3D2-A180-4B48-A34A-CC6FAF84E787}
VIEJO 22029104 | {AD318D3F-F8E0-477A-9CA4-DF6AF7B738B6}
DIVIDE 1103CB | {BFA942F4-E00F-4B4B-9BEC-83B4F4C04B73}
WILLOW CREEK 1102CB | {0F7FFA32-0648-474C-B64E-A51E578D757F}
CALISTOGA 1102447865 | {256C107E-DF69-4B49-8315-E416EEEC567C}
MARIPOSA 21019400 | {5BCEC129-10D0-4B20-A658-76CA792FBB41}
NORTH BRANCH 1101750010 | {7465C87A-2B17-44E2-A07D-3F978BE2E64E}
ALTO 112081716 | {AB366F07-2039-406C-B0DB-849A899ADA0E}
HALSEY 11012414 | {C7CE8EEC-BFCB-464B-A0B6-4DE95EE01B52}
MOLINO 11014900 | {5231DB16-86D1-4843-83D5-814DD0192BCB}
GOLDTREE 1108939400 | {F40F9B94-B69D-4B7D-86DD-125E8D7AC87E}
SAN BENITO 2101295566 | {02E6ABF5-EA12-4934-8526-CDD1BECA0A7E}
HIGGINS 11044281 | {46E9257A-F9DC-47D6-A72D-7B5FD7E2E022}
CURTIS 1704CB | {6CFF4874-9416-4562-8168-A66869F04B91}
WILLITS 1103968 | {7E4735B5-33E8-4CD6-9F8D-A9385ABC1901}
BOLINAS 1101CB | {86BA3963-96A5-4181-83CD-FA7B5EC47222}
LAKEVIEW 11034488 | {DB6CF4A5-64C5-4D3C-8106-DF77F9284168}
LLAGAS 2107142710 | {E4B7388D-56E6-4038-9DF8-2387BF129F0C}
CASTRO VALLEY 1110MR243 | {58409F43-908C-4F7B-B13E-65AE96367D27}
MORAGA 1104CB | {65BF29A6-90D7-4E9D-9D0F-0B463AE68E56}
SAN LUIS OBISPO 1107V62 | {331D14B2-6B0F-4273-9F56-8DD687C4B860}
SILVERADO 2102772792 | {A1E340CE-2BA1-4C87-8C2A-156A4355C24F}
GREENBRAE 1103718674 | {B4FDB7D9-192B-4627-9F31-9C96B3E85045}
CASTRO VALLEY 1102MR204 | {B72D11A7-A3E3-4487-9B62-E0B9199739E9}
PIT NO 1 1101LR-RC-A | {240B9597-FDF1-4E00-A581-05E13375E11A}
DIAMOND SPRINGS 1103CB | {F21436B1-06B1-4781-A6B4-F2B85E06831B}
SHADY GLEN 1101820080 | {2295C6B5-DB5C-485B-935E-32BBB76DDD81}
LLAGAS 2107XR188 | {1B5D7998-B20D-4848-BE59-22884992869D}
SAN RAFAEL 1105408 | {25A73CC9-0B81-408B-9142-F5D6802BB119}
CLARKSVILLE 210619642 | {6458AB58-DA5E-4D0A-95E1-69BD6C7E0EA2}
KESWICK 11019712 | {7666B122-2C0C-4302-93AF-84BE4CAB5B18}
VOLTA 11021646 | {82B5D74E-1D42-49A6-873C-1363407619B8}
STELLING 1110CB | {8E953D43-E75B-4D09-B2DE-0248B8D89E29}
COVELO 1101225458 | {F774F37B-0BFB-4E5C-8B3B-83726F441387}
HOLLISTER 210441808 | {3A7DE5A9-6F9C-4704-A7B4-637F15326CD9}
BANGOR 110182350 | {61206052-9537-4FFD-A305-D8F681D781BF}
SILVERADO 2104708 | {65E252BA-B6AF-41C8-8302-CDA75AAEE4FD}
MONTE RIO 11131989 | {EA690835-9E38-4D73-A546-B5676BCE1BEA}
GLENN 11012012 | {79FEFA25-425D-4CA0-8714-2AC25C0E088A}
GARBERVILLE 11011514 | {7F9C85EF-487B-454C-8489-CDBA87D32E67}
FROGTOWN 1702307998 | {89CC7A11-127F-43C2-800C-EB67E4FC6948}
UKIAH 1111433984 | {90D9EBEA-E8B3-45BF-93FF-595A29473B29}
CLARK ROAD 11022582 | {E681E40E-5ECE-4E9E-921D-C13E15C00CCA}
CURTIS 170356972 | {F49F720E-0E74-44F4-A395-CBFF584836C4}
ANTELOPE 11013609 | {F610032A-F2E0-4366-8F75-D3F075E51CA8}
PIT NO 3 2101839220 | {5C4A4B21-8DC0-4DD4-BD69-EB88E21328E5}
CURTIS 170349746 | {7D0477A1-3B70-4629-B0DA-1E96F8ADF8DC}
BRUNSWICK 1104CB | {BEA0A501-B4D2-4CC0-BAE4-F7EC8C1D8A1B}
PAUL SWEET 210516008 | {8D1DF0FB-6A31-4B98-9D74-0EE015EF8A6D}
ALLEGHANY 1101978 | {3479738B-50FC-4140-94A7-E159A76AE25B}
MORGAN HILL 210653992 | {92AC711D-1F72-4B85-B43C-96526CED20CC}
MORGAN HILL 2105XR564 | {002F00BF-AB7A-4582-A318-84DD2A6C3219}
OLETA 1102CB | {23616425-EB34-423E-9DF9-30BB0AE7795F}
CALPELLA 1102421412 | {3A9F2D9A-7433-47D8-8578-46D205BA61B6}
MILLBRAE 1108639978 | {8FFF56B3-5742-48DE-8779-85060D8D7011}
PUEBLO 110548260 | {F405820C-EB9B-44D6-A3EF-2469BFF7A112}
TIDEWATER 210695842 | {DECD64D5-E92D-44EE-BF28-1EF0D6E10478}
SAN RAFAEL 1106837 | {3CC0B2ED-4CCD-4757-94A4-43056A68F6C1}
BIG RIVER 11011052 | {774F8E82-5627-4004-BA65-1CFB3311B274}
WYANDOTTE 1110873858 | {B9243DFE-989F-4BFE-A52A-70EF1DB7EE8E}
MONTE RIO 1111969182 | {CFD49D25-5A97-4913-B570-E644DBC2B01E}
FLINT 1101958726 | {F60C4C6E-928C-45EE-B5E3-FE18B260D743}
MONTE RIO 1113320 | {EF630F9A-72E2-42EA-B074-23D3C9859856}
WISE 11022234 | {2EBA7959-7933-4246-BD38-55C2DE2602D7}
KANAKA 110165606 | {342DEF5A-AA53-475D-8D7B-ABE1A3F6B4E9}
WYANDOTTE 1107829470 | {112CEC5D-7594-450C-A06E-88C65F1E5892}
INDIAN FLAT 11044580 | {215B4A0E-B4E1-4DEB-8481-0B3FF4DD4D17}
FORT BRAGG A 1102418 | {2F10EC8A-D66D-41A3-A96A-C091A52D1815}
BURNS 2101CB | {77124F72-2A10-485B-AF25-5FB9845AECBA}
VIEJO 22032016 | {4DC9724F-62CE-4CE8-B9B2-FC8D42753B78}
SHINGLE SPRINGS 210819622 | {95880633-835C-41AD-A217-FF4EBDC70BBD}
NARROWS 210242584 | {BB1737E9-F6A8-464E-B585-0852853AAD83}
MADISON 21017702 | {DCC4F33D-94BC-4C20-B81E-44479B092EB6}
LOYOLA 1102LL12 | {FC7EF3C1-E676-4F19-A408-525DCCC4AA40}
COVELO 11012467 | {149E5268-4926-4B7A-B9E2-928EA9B5F83B}
MIWUK 170238218 | {A068179F-B6CC-4678-A4EC-AF469032942C}
CAMP EVERS 2105BL 2101 | {096C1652-B7E1-4420-B7F5-3A29C5C5F06A}
EAST QUINCY 1101424048 | {13F95C63-620B-4827-AE11-2F38727C8122}
MESA 1103M92 | {2DBCA866-9F0D-46E8-B9B3-4863FA94560D}
LINCOLN 110451756 | {302C4176-4830-4D29-8953-2FECE7A076EF}
BROWNS VALLEY 110193870 | {77D006A2-E276-4C22-A5B0-EE84D8EA3177}
FROGTOWN 1702204480 | {F66F5E9F-01CE-4986-95ED-652F7B3AA4E8}
PIT NO 3 21011480 | {E236376B-9C17-4833-888F-1B5788910DB2}
NARROWS 2104CB | {F4FF7575-EB60-4F06-920B-F33332AB37E0}
UKIAH 1114822 | {2D9FE14A-68D2-46A5-B4CD-1EF83FC0FBCE}
WOODACRE 110191900 | {315B41A4-2763-4241-B96A-998B94A74075}
APPLE HILL 21021532 | {4A1B7FA4-9EA2-489A-952B-02F0D69E191E}
MIDDLETOWN 1101932140 | {302C19E7-740B-49C6-83EC-9E70AC44D5CB}
SARATOGA 1107LC12 | {574B3F5C-C8A6-43BF-A24C-78D062C2D75A}
MIDDLETOWN 1101644756 | {67FA5D3B-5BFA-40EE-AABA-659446964531}
NOVATO 1104889406 | {B0ADA7D3-946E-4D87-A626-5D6D71C05975}
MIRABEL 110286326 | {F24A6BFB-F462-4C79-8226-3FA35A366957}
LUCERNE 11062355 | {BFEEA045-A307-47A2-9C2E-0B69ACE24065}
BRUNSWICK 1103164092 | {58929914-99C2-4C8E-B85B-CC617974C9CA}
PLACERVILLE 210623190 | {83B5D9E2-BFF1-452F-91D8-11E4F5A6B453}
VOLTA 11029742 | {A7123BEC-B365-4766-B96E-6C5017CAB086}
OAKLAND K 1102CB | {D1E9CD4E-4BC6-42D5-802C-68BF9527A1E0}
DESCHUTES 11011652 | {FDD63F63-31B3-4440-A376-DFAEA489B8E7}
BRUNSWICK 1106CB | {05FDE184-0042-4792-8C58-B7C18CC19C9C}
MORGAN HILL 2105CB | {30C139BA-309C-45BA-85AD-14DDE6598AF6}
CAMP EVERS 210660124 | {498D8DB9-5CC7-45E0-BE16-B8DB75429782}
CALISTOGA 1102929461 | {54FC9C79-A744-48AC-829D-6AD9866F8972}
POINT ARENA 1101CB | {72A22D65-E2E8-42C5-897F-8C8D23CE5089}
STAFFORD 11021048 | {B779C83B-3DC2-4512-9F97-360CB13A0909}
JESSUP 1103770356 | {CD04E6E9-9DF1-41F0-9406-3CAF5658019D}
APPLE HILL 110412832 | {0010E3CC-5B34-4785-98D9-D2D98BC731B3}
EL CERRITO G 1108BR254 | {1BE7584A-89AA-4EFA-BCE7-9E7AC1997D2C}
WOODSIDE 11018972 | {31C2E01B-7B87-407B-9DC8-52C242320576}
MORGAN HILL 2105XR176 | {33647C9D-A594-482D-97B0-F9F1AC5928F8}
LAKEWOOD 2224W544R | {56915414-A928-48BE-9033-58A50A467962}
JAMESON 11028842 | {A9A36598-2BF7-4270-99BF-EC9B9E23BB29}
SARATOGA 1107899344 | {BBDA6BAB-A6E1-4EF2-A377-B93BB222DBB3}
MESA 1103236053 | {C0ABDB73-42C4-4D60-9BB1-4077EF0BE355}
DIVIDE 1103567884 | {8595AA03-4461-43F0-83E3-96D1A07CC7F4}
PENRYN 11072410 | {88D11C1E-94DA-491E-B166-BE630EDE0741}
IGNACIO 1104469764 | {B15C4D34-840D-4CC7-96CF-D3ABBE50E477}
NEWBURG 11326576 | {2C9C3EB7-00FC-4934-A962-9B300983DC9F}
VACAVILLE 1104CB | {CBB1E17F-BE5D-42E9-AB86-48D61CF7F4ED}
EL DORADO PH 2102542272 | {5B8E36B2-B12B-4F00-8166-D1E50ADA08E5}
LOW GAP 11014086 | {71DE392B-20E6-4124-9FFE-851197719244}
EL DORADO PH 210119752 | {8256574C-8B3C-4A26-BCE0-BA059359AE5F}
SARATOGA 11076867 | {1EECCE5A-2560-4A1B-BCA1-BF5B03357FA1}
PENRYN 110351658 | {9E584244-489D-49B0-8EC4-8B40DD374169}
MADISON 2101725408 | {A1A5DB3C-6B99-4418-9DB8-859C77A01E6D}
SHADY GLEN 1101585766 | {0FE524F2-DA0B-43E6-AE33-7B106122C864}
OTTER 110263868 | {11A5B6DF-81F1-427D-A78C-DE7EF2F392AC}
PENRYN 11051378 | {1E1BA976-38CE-4912-807F-3A5F3BFF5CD1}
PAUL SWEET 2109634576 | {270FCA15-092A-4BC1-985F-1AAFCAC44027}
LLAGAS 2101984552 | {07E209B8-80A2-40A5-8228-12D4DFF42801}
HARTLEY 1102490 | {81602399-62C7-41C1-B875-F30FCB0774B7}
MORGAN HILL 2111123422 | {C3FC7DAB-5E2B-4C00-BE86-ED9552703F1E}
SAN LUIS OBISPO 1108144690 | {FA97EBC4-7DF7-4291-B59F-FFD92DA4891B}
VOLTA 110254932 | {3AA926AF-5D59-48E9-968A-65279153CE9D}
HIGGINS 11041374 | {5975A3D8-5B89-4D93-9C6D-113094290849}
IGNACIO 11011779 | {64639A8A-2672-4BE4-8EBB-2985CB356A36}
ROSSMOOR 1104892332 | {D2330A0C-459B-4F6C-BE3B-0AABB85A2AF8}
COVELO 110196896 | {C93D43A5-1B00-47F7-99CB-5288FDBDDC41}
RED BLUFF 1105CB | {FEC690E3-0920-4E0A-BCDB-0BA1BA1CD1E2}
JAMESON 110265516 | {A9A36598-2BF7-4270-99BF-EC9B9E23BB29}
VOLTA 11021502 | {1EA4A0A1-3D5B-4E8F-B75B-661AF3FEE831}
CEDAR CREEK 1101CB | {4A950894-EB8D-4B95-B3B2-200DB270C21B}
MARTELL 11016074 | {52B817B8-3607-4215-94CE-6DB0D80039B6}
POINT MORETTI 110110724 | {F7013B1A-D0D7-4319-B5E7-A5441451D41D}
GARBERVILLE 1103CB | {81BF210B-E399-451E-B158-93FB561813DD}
MC ARTHUR 110151398 | {85EE7B40-6D93-48B5-9C94-EBAACB072BA9}
HATTON 1102648928 | {96F3BFFE-8B25-45FE-9E94-B3CC1506798D}
LAKEWOOD 2107CB | {C476BEC6-6566-47F3-B164-264FA9A69083}
PETALUMA C 1109259100 | {CBE2D558-4F9F-4EDA-8260-3A87B72F1065}
PAUL SWEET 210878006 | {62614D7C-C46B-4061-8F81-503DEACC476D}
OLETA 1101754718 | {F9BCD513-5384-4FF0-AB87-CE22E82C21EE}
NORTH BRANCH 1101TS1115 | {441CFEC9-1CA0-48DF-94A7-C868FF359EA8}
HALF MOON BAY 1103869962 | {F951C9B5-DFF6-4F18-959A-6543A104D243}
CALISTOGA 1102960240 | {41CC5656-0DD4-454D-8539-FF84073137C6}
FORT ORD 11019518 | {66CA8537-4E7C-48FF-82D7-109E7EF7B7FC}
KONOCTI 1102716 | {D5E7700A-E368-40EA-8C45-A0E9AA2F6F54}
HATTON 110256680 | {15F21C1B-A03A-4E01-B20D-69BB0B19F555}
ROB ROY 2105931192 | {1C63E144-CC28-45E6-852A-59F6783E5E65}
SNEATH LANE 110796530 | {387BB7F7-C1FA-403D-B1F2-AEFE2A510405}
CASTRO VALLEY 1102CB | {4C70CAF0-3BFD-4092-B38C-A567700FFBF5}
PARADISE 1106CB | {54AC0ECA-BD93-49A2-9B30-909ADBE15177}
VOLTA 110280982 | {2D79CCBE-1B8B-472A-B9BB-B34254CCD666}
VINEYARD 2108MR172 | {D247C9D4-2385-4C86-98D9-FAEFF0DAB6B3}
GIRVAN 1101CB | {DEF16B60-E22C-4BAF-BEFC-F4B0E169B38F}
CASTRO VALLEY 1102MR359 | {F23FD02C-15E0-46F5-9C74-B690AB0C4482}
APPLE HILL 1104814656 | {E9B2D551-2CAF-489B-9D1C-4D1BCFDB0559}
CORTINA 110130016 | {E3B77E93-BB57-4588-891B-4456F675EF56}
LOS MOLINOS 110171402 | {09A4B9E8-989B-4DA3-9154-EF01A44BB71B}
MOLINO 1102905231 | {96DF56B4-09D9-4632-A84A-99B69DBE4320}
CARLOTTA 112142896 | {98A83A4A-2877-4301-8F63-D1E33C62F68A}
HERDLYN 110299602 | {BD7C976E-7CD9-4ACD-A152-480ECCDE08A2}
VIEJO 220292792 | {C8ECEDCB-3AAA-445C-9FF2-2773F53D5EAE}
MONTE RIO 111264682 | {DD8BA615-FFBA-48E9-84EA-5D20532CD959}
PANORAMA 1102508502 | {6303BED6-9051-4E72-A1E9-A3825361F885}
DESCHUTES 1104269170 | {2ABC92FF-56CD-4099-9E14-FDA9128A7AC4}
RUSS RANCH 110196276 | {35E834E5-9FE3-4B04-BFD2-7F38E4FACAB8}
SOLEDAD 2105125484 | {E0D1D31B-EE07-4A3C-BA17-91B209FA1390}
SAN LEANDRO U 1114458451 | {0A24ED8E-78C9-4838-A7F9-84D3780435AE}
BRUNSWICK 110651486 | {20D517CB-EFEF-4E5D-A065-4994CEAE6929}
MESA 1103126697 | {431342B2-8FA7-4C4E-B028-5E0C383A0588}
COTATI 110536536 | {554E4D6F-0779-4CD2-B95F-DB489BEA9C8F}
VIEJO 22032628 | {4DC9724F-62CE-4CE8-B9B2-FC8D42753B78}
SARATOGA 1107LC26 | {AB3D61A8-2047-43B4-8648-838CA93AAC23}
KIRKER 210475648 | {C74DE802-BF47-4D57-912D-652414113F12}
CORONA 1103176 | {C751DAA9-A68F-4E3E-9A3D-8380575CF487}
MC KEE 1111711900 | {E158EBD1-D391-40F7-8D5C-4284F51B8199}
KERN OIL 11043843 | {9F23EB64-F3B4-4CBF-BA80-2578C2F13B01}
CLAY 11031821 | {AE111B59-4073-4BA6-A6F7-C46E4FCA24F4}
HIGGINS 1110197930 | {C6E8B2FD-D557-459C-B9FB-FFB281472FF9}
OAKLAND J 1118CR198 | {218F069D-01B3-4618-A6DA-CD10F8EDDF5D}
MORAGA 1101CB | {6B23A69C-24B9-4566-AFFA-1FAEC2B2E50D}
PUTAH CREEK 1102710384 | {807BE66E-A7AB-4BA1-B8B2-4ADCA53B3B50}
PUTAH CREEK 11028352 | {89E381E1-F842-49C9-837A-CF37A4D6EF66}
SAN LUIS OBISPO 1108337126 | {F9425320-A467-49B9-AA89-B48ACFF8F012}
WYANDOTTE 11091040 | {10790C99-0AC4-4885-95AD-50DB99DD62BD}
CANTUA 11029310 | {47A2D34B-B373-4F5E-9E14-A9EF32FD99D4}
BRIDGEVILLE 1102839652 | {6A116841-A841-40C3-9B48-86C4D5331427}
PANORAMA 11022009 | {A631613E-AC26-415F-BA05-B8776DE457AF}
CAYETANO 2111MR444 | {9023C050-E4CF-4D3E-B644-63B7AF1F7B04}
KETTLEMAN HILLS 110149656 | {E3191191-EC32-4B60-A32F-F8582A37B6F0}
MENDOCINO 1102CB | {988CA71C-AB6C-46A7-920F-6295BBF50876}
NAPA 1112CB | {C2E68366-657D-4902-BBD7-D59A6C76C29A}
LOS COCHES 110275272 | {EE0BDD3D-35F5-4175-A0F2-FD670912F53D}
OCEANO 1104V38 | {F2D88342-EA4A-4DE6-A5A2-0FD601C586EE}
HOOPA 11013290 | {FBCD7012-56B0-4DB8-BFD1-768DDA012D1B}
LAURELES 1112438 | {1F7CD2D0-886C-4D05-8112-AF25ABC480A2}
SALMON CREEK 1101676 | {4DCB6ED2-9B7F-4AF7-86F4-3A84466B49F2}
MORGAN HILL 2105XR070 | {D4E598FB-500D-4E86-913F-DD1E461E4E23}
MIWUK 1702823548 | {DE713724-4753-42EE-87B5-64C0693236F8}
CLAYTON 2215184604 | {E913837A-6C3A-41F3-92AB-2B49EC8EE227}
MARIPOSA 2101929360 | {050E06AF-91BE-429B-BDFE-3EAD80F24863}
HILLSDALE 0401CB | {3840BE80-21EA-4670-95C2-6EA58C09B292}
PIT NO 1 11011552 | {47AA609B-0BD3-40D9-878F-3D1F5D334A7D}
GARBERVILLE 11022124 | {4AC60F3F-45CC-4080-B7C8-2A403EC32A74}
SERRAMONTE 11046055 | {5AC2A44E-A5CE-4631-A5D0-59B8F85FCDA2}
VIEJO 22022014 | {8E85DA31-E8CD-4D80-BE55-60AFA6937F74}
ROSSMOOR 1101CB | {E76B2183-0811-41C5-8C57-31DB4D93EC1E}
ALTO 1121508 | {F8ED8086-0E7D-4BB7-85C2-CAA1D3DA55CE}
NORTH BRANCH 1101752104 | {13E5BBB0-001E-4A48-B4D2-914C2E42F6A2}
RADUM 1105806392 | {597A5CEE-82F6-4D96-ADE3-E225B0B39A15}
BUCKS CREEK 1103338520 | {788A24F0-B95A-4429-91A6-A78EF0DB40D4}
KERCKHOFF 1101R308 | {88F7D35A-B742-45DC-AA55-32394737AD92}
HATTON 11012204 | {19B86573-307E-4C6E-966B-96848CB70151}
MC ARTHUR 110137388 | {94162D16-0097-44C8-A147-FCAA580DD744}
SANTA NELLA 11013680 | {D9B42920-8795-457D-8506-B9A1003BB3E6}
ELECTRA 11017104 | {21E26CE5-9BFF-45A6-8272-2A9D442E9691}
SONOMA 1102CB | {2300EEC9-D815-4DFC-98C2-FB3F79503060}
WISE 1102CB | {605358FE-4007-4349-A521-8A072F22F69A}
UKIAH 1114528 | {7CFF91C6-6122-459F-BD71-B9F17BE39EB0}
JESSUP 11011496 | {7E13CC3A-AEA1-4A09-9EEC-1D6C86F4363F}
VOLTA 1102453266 | {98C4DD6D-D3EE-4676-9123-391728297153}
FORT BRAGG A 1102CB | {A11A44BE-5FF6-4EAE-B643-DC3914767492}
BEN LOMOND 0401944178 | {EB10C4EE-4491-4EBB-BF92-473E5065B27C}
PERRY 1101W52 | {EFFF9048-E08F-4C22-B5E1-9B1A32E0D054}
SAN LEANDRO U 1114MR545 | {4B9E4541-F21D-43AC-ADB7-3A92CC33D20B}
SANTA ROSA A 1104210 | {53C74AF7-2A69-47CF-8DFD-9E70E0E39334}
DIVIDE 110245067 | {EF9A6FA5-0241-4F64-89EA-1575EA9DAF76}
HALF MOON BAY 1101903182 | {AD0B095F-6CFC-4F63-886D-7CEABBD6DA89}
MONTICELLO 110193384 | {D1302290-4599-4ADB-94B8-46B42AAD5681}
BRIDGEVILLE 1101CB | {FC8DA5F1-E256-452E-840A-DB2CC55A41C4}
RESEARCH 2101D576R | {06DF90B3-08E5-4846-BD76-E525F02721A2}
WOODSIDE 11018522 | {0C4874FF-D222-478C-B9D7-BED0F08FA35C}
LAYTONVILLE 110189606 | {17A00714-8A49-49C0-B860-6006F3A8F3AD}
BRUNSWICK 1105963830 | {EDC3C6AA-B200-49D0-AFDA-73B9844EB8E4}
COTTONWOOD 1101CB | {509EDC5C-5C13-447D-BAA5-6AE957D846E4}
FITCH MOUNTAIN 1113443164 | {82F1B323-9F47-4844-B053-6FD72157B262}
RIO DELL 11026151 | {68D3E51B-D82F-468F-8693-722B02390473}
EMERALD LAKE 0401CB | {BF748DD1-7EA7-463E-91B5-1F0876DD9BB0}
CAYETANO 2109CB | {CB1F79C6-162B-44E7-BDF1-619119F35335}
TYLER 11051704 | {E58E84BF-2C2E-494E-AE66-0D141BD137C3}
SANTA YNEZ 110477098 | {30375F5B-5F9A-4C1C-992C-DEDED43F1FC3}
APPLE HILL 210251792 | {60540539-B6BA-4E80-BC6C-988DA579218B}
WRIGHT 1110288242 | {ABB28193-DF6D-40B9-BA16-1713A8EF4B58}
STAFFORD 1102CB | {C9CC8490-6E43-45D4-87C2-A85ACD7797AC}
LAKEVILLE 1102347280 | {CFC0ACB5-498C-4299-AD8A-6B456236AB7F}
DESCHUTES 1104CB | {D7FE7EC5-7478-43B3-9A24-52065EFA1755}
VIEJO 2204CB | {DB34AA1E-C0F6-41DF-BFC5-43E5CD8E6B2B}
SAN MIGUEL 1106N34 | {19CBB8DD-B0DD-40C9-99D6-9DC6A38717ED}
WYANDOTTE 1106304014 | {29C2B584-F455-4FA3-B4A4-3F4E989317C3}
APPLE HILL 21028372 | {87934A6A-C9D7-420E-9278-5C4F8DB79DED}
KIRKER 2104442850 | {93786D8B-5CA8-445E-A8E7-839499543A43}
JESSUP 110194468 | {D2D6973F-363A-4DAC-B85F-5E6E9B82592B}
CAMP EVERS 210510214 | {F835FBEC-BE60-4F27-B7FA-FBF03B1492E9}
BELLEVUE 2101CB | {09987E11-E541-4564-AE03-05F03FAC13CB}
PIT NO 1 11019702 | {240B9597-FDF1-4E00-A581-05E13375E11A}
LOGAN CREEK 210247194 | {8700E55C-38C6-41AB-AF2A-3B50EA0B2E05}
SAN LUIS OBISPO 1104350030 | {5E4CECE6-B405-46DF-AB3E-BC23B1171AD2}
WYANDOTTE 110613016 | {73895C48-E496-423A-BB9D-D8E6858BCD72}
HICKS 2101XR600 | {7AD08992-20DE-491C-B310-C51F11D11659}
PASO ROBLES 1104R14 | {8D8A441E-1C9B-4D22-BCF5-1C9794F2F9D9}
CURTIS 1703CB | {C4B116D3-EE04-4D0A-96A8-6CF57FE78721}
BRUNSWICK 110767218 | {22F4E53D-20D9-4A9C-BDCD-9693C219E892}
FRUITLAND 1141200856 | {549199A2-4261-43E8-8700-8DDEE28DEA6C}
ATASCADERO 1102A28 | {7017AD32-E07A-4554-A2AD-C732D91DBE2C}
CHOLAME 2102X24 | {042A33DE-71B1-40FB-B0CF-6D56CCA576B0}
ALTO 1121CB | {AC60738C-EEA0-4867-B6FF-D969AE620995}
VACAVILLE 110941782 | {D12E3D2F-1998-4DA6-942A-7BE316909F83}
CALISTOGA 1101894 | {D294E12F-4C7C-4C89-818B-50A112502FCB}
OILFIELDS 11032757 | {63E72A21-A36A-4936-B748-71270400CC57}
SONOMA 110213367 | {2300EEC9-D815-4DFC-98C2-FB3F79503060}
MONTE RIO 1111292 | {E76F208E-D030-4954-AE4B-2E5BE9D9580C}
SARATOGA 1104209146 | {DAB08854-D3B6-4F8F-8E8C-51427B3E01B1}
LOYOLA 1102LL64 | {8FF2C357-E560-4F49-BD6C-1A85C9D294D8}
CUYAMA 21013533 | {AE254590-1F13-4FEF-92B1-1F8EB5A8892D}
PLACERVILLE 21061104 | {DC8F828A-9D78-4250-9936-BA54E6245EA8}
MOLINO 1102CB | {3827F6F2-326F-4FCC-9EC1-DB4311EC910A}
DEL MAR 1103CB | {8F0FCBB5-348C-4DDA-9D44-60778A054848}
NOVATO 110387834 | {F95FECA9-BE51-4923-A755-70AE69DDB475}
PACIFICA 1102660408 | {002FC16A-D8E0-4EC1-BCF1-D174F5CB0D0E}
DEL MONTE 21032000 | {A7511424-C0A7-4DC4-BAD6-B60505BBA431}
SAN RAFAEL 11011210 | {C15D2B27-11D0-43EC-9B15-374D2297640F}
REEDLEY 1104887932 | {DE4A3F35-1098-43E3-AFD1-E0057FBA11D6}
SOBRANTE 1102CB | {FAE87638-3327-4270-9C08-0DC3E3B13CC0}
HIGGINS 11032194 | {04FFA86D-12A8-4DCB-A786-7ABADD4FCF1A}
BRUNSWICK 11052130 | {12398A09-47B6-4618-B7A8-07F9B9DF4D2E}
HATTON 1101CB | {19B86573-307E-4C6E-966B-96848CB70151}
PERRY 1101CB | {30D7373B-D31B-4D5D-82BF-42F5B4929DAA}
SHEPHERD 2111443696 | {E96DE61C-94D8-44EC-B1DA-8923104268C8}
SAN JOAQUIN #3 1101CB | {5A8D30A3-8AE5-4F6B-B53A-735A17ABC0FB}
WOOD 0401CB | {8F0A48D9-A322-4FA2-98F5-9BA99B0B225E}
MORGAN HILL 2109145998 | {DE740AD5-7224-4449-BB36-490304754B67}
MONTE RIO 111164758 | {173229A0-9A6C-4AB5-8BBC-51112D47DF20}
GATES 1106879496 | {3E771B8A-A2BC-4AF3-89F7-B4D332DE2C00}
REEDLEY 11067270 | {549C94F0-8520-4315-9A40-1509DB31AB52}
LOS OSITOS 2102624200 | {55FFD10E-AE85-4366-9D32-F7DB90B5CFE9}
COTTONWOOD 1101384360 | {509EDC5C-5C13-447D-BAA5-6AE957D846E4}
WOODSIDE 11029046 | {BF6AF21E-B6B4-453B-837A-E823913B38FF}
GRASS VALLEY 110358498 | {EB087661-42A5-46E0-BB53-1DC1A49FC6AA}
SNEATH LANE 1102CB | {40980895-4B8E-4C74-B15F-E13FF900DC4F}
SILVERADO 2103CB | {66AAADD9-54A2-4D43-B82B-F401906AF14B}
EEL RIVER 11024396 | {890D4B8A-DB25-4CCA-9D69-562BFAFFB09E}
WILLOW CREEK 110129362 | {1D151194-CF04-464D-9004-1F697BF4DA48}
RACETRACK 170310870 | {2C817939-22E6-4D0A-962C-2F9F458E8593}
OILFIELDS 1103N64 | {CDC6585C-22C0-4542-A949-CDEE5502EA22}
SILVERADO 2104722 | {73D28043-CFDC-4F62-93B5-37CC33588BEA}
MENLO 11029152 | {844542AF-23E3-4A9F-A1D2-E72C86286BF7}
OLETA 1101296804 | {85FEEB3E-959D-465E-A93D-BA3999C78268}
PALMER 1101M88 | {A85BAC06-7F10-4768-B721-E152D18C46EA}
BIG RIVER 1101CB | {BCC029FE-B790-4D1A-9B12-5D2C7AA3930D}
HALF MOON BAY 1103CB | {D0EDFCD8-2A8A-490D-A06D-0BAFCCC6E362}
PUTAH CREEK 11058812 | {D437F6E1-386B-4A56-A527-2C85C72A2065}
CLAYTON 2212523764 | {F3AF2874-1B26-4F8E-A2D1-24B02ACC6A03}
OAKLAND K 1102378866 | {D1E9CD4E-4BC6-42D5-802C-68BF9527A1E0}
SHADY GLEN 110151696 | {0FE524F2-DA0B-43E6-AE33-7B106122C864}
OREGON TRAIL 110346860 | {4F1FF48F-FF8A-488F-A383-0E93A88F3890}
NARROWS 21022728 | {1F33AC4D-BB0A-424C-BF6E-423FE06FB054}
BRUNSWICK 111095576 | {AC82A3F6-A35E-40B3-B30F-C23643AC0649}
FROGTOWN 170211212 | {275411B9-F65E-4C2D-AC92-04E91C75A810}
OAKHURST 1102333062 | {4739024B-FF85-45D7-AECF-B2FD3D7B777B}
MORAGA 1101669542 | {B9A70335-64B1-4C3F-8843-DB3BDADB4C77}
ATASCADERO 1101A02 | {F4592309-FF5C-4AE7-B40E-CF8D73FD01E6}
MIDDLETOWN 1101548 | {F67E867C-FC38-4763-8DCC-25139EFCB73A}
LAS GALLINAS A 1106685852 | {FB62643F-8EA7-437D-B912-4A4CCD18E192}
MARTELL 110368192 | {2D2F9EB5-C573-4256-A9F2-6087D93C70C6}
SOLEDAD 2105404754 | {36177CF1-DF55-4FEE-893C-1AD0F53C4183}
DAIRYVILLE 1101CB | {7E805BB6-FA35-4404-BBBB-4801C3E98DDD}
LOS OSITOS 210364348 | {8276CB14-B72D-46E3-83F9-1F1DCC6858E6}
TIVY VALLEY 11067150 | {90E00265-C0CF-4482-89EA-4364E2D4853A}
PUTAH CREEK 110258340 | {EC7E3E82-534C-45F0-825C-A06402B7C3CE}
POINT MORETTI 1101415734 | {EF958110-BB67-48F0-BCC0-A7C84F7DFFDE}
TEMPLETON 2112R28 | {F888EA83-160B-4C8A-947C-3FEEFB60DC7F}
OLETA 1102793776 | {23616425-EB34-423E-9DF9-30BB0AE7795F}
DEVILS DEN 1102CB | {A92A6C8C-B557-4608-A4A1-975F3E0D9109}
CAMP EVERS 2103449218 | {A1366627-BA9B-4DAB-8067-98E47F041CB9}
WINDSOR 1103171410 | {CF3D4281-EA2F-4415-B4CD-AC674F9B4864}
WYANDOTTE 11102590 | {EF5D8957-32CC-44F0-808E-217DC0A13E35}
SAN JOAQUIN #3 1102CB | {F2F4DFE2-A71E-4AEB-AA05-9FF7D56E28F8}
HONCUT 1102301886 | {95CFDCE9-A6F6-4428-B8F8-A23AC65977EB}
DIAMOND SPRINGS 1104CB | {6872443C-7FE4-416F-92B9-65D58A293737}
CHOLAME 2102X08 | {7DB68BFD-2EE5-4737-904D-3F4AB911B6ED}
MIDDLETOWN 110148212 | {87D28769-5329-4925-BD5B-DA686EE4E76D}
GEYSERVILLE 1102350 | {95D38DE9-E8FF-48E8-A441-5433C36DE660}
LAYTONVILLE 110264908 | {9B107EC7-49C5-413B-94F9-4B15782C698B}
RISING RIVER 11011530 | {BE242D62-FFF6-4E73-8F41-DCC9F0527F50}
MONTE RIO 1113250 | {F3C44BD4-C837-40EB-9584-B17B6404063F}
MOUNTAIN QUARRIES 21011130 | {F71097AE-E6F3-430F-8B2D-241E8D88F4AE}
CABRILLO 11031437 | {02264660-E3C6-4806-AC6E-28401EBDA58A}
GOLDTREE 1105551904 | {FF54465D-5764-4C87-9FA1-2FCC27FF3FF8}
GATES 110699914 | {0403AD0A-8957-4413-B5CA-AB406F66F7FB}
OAKLAND J 1116CR328 | {38D3BFB4-B810-445A-BCA4-713A479E6C8D}
SHINGLE SPRINGS 210851476 | {5930D652-4C2C-456B-9C55-1601828B7C0A}
SUMMIT 110147786 | {3E9B0952-44E2-4D0F-8A1E-44C0D690C0BA}
EL CERRITO G 1112664184 | {253DD6AB-E4CF-46A7-A9CA-31B26BCFBF2A}
GABILAN 11013090 | {43462865-0ED2-47A6-A8E8-8B52D18F5577}
BIG BASIN 110276752 | {5E67FDC7-6621-4E4B-BC49-469EB29666B6}
PEORIA 170492888 | {B68E2FC5-9A54-49EB-9258-EB6EA1DB9D61}
SANTA MARIA 1108M122 | {8C8E266A-9290-4622-A640-18215AFA35B2}
WALDO 0401965216 | {B6A1E84D-F904-4E0D-8713-BF77906CA63F}
SYCAMORE CREEK 110979474 | {BEF311A1-A486-4265-8EB8-C5A6755295FB}
BASALT 1106783176 | {0C9DEF06-9AAB-4128-9810-85E010FF7C1A}
TASSAJARA 2106203380 | {C6A4A4CF-A03A-49E5-B0DC-3DB8EE99EA58}
SANTA NELLA 11043130 | {D412B745-D070-4998-9104-DFC87BB22A4F}
BASALT 110138824 | {36CB0205-94DA-45AD-B087-D2736F00D26A}
MONROE 2107230 | {3D15A0FB-7F79-449E-9100-AEDACD615B82}
HAMILTON BRANCH 11012082 | {C6BC6538-2EB6-4DA5-9982-6A2D9BE60DD8}
STONE CORRAL 11107320 | {D090E99D-0335-45D1-8BE3-75B46FB44EC9}
HUMBOLDT BAY 1102309413 | {0A5740C1-9196-4281-8753-B21C8EA0160F}
STONE CORRAL 11087310 | {9C22AB4D-7471-42A3-9430-CD197230D588}
HAMMONDS 110212100 | {FD894490-402E-4AE2-A8E0-2A3DAB4F2C46}
GARBERVILLE 11022010 | {0FD31FD2-8045-433E-9D12-C8669CFF0383}
DESCHUTES 11041582 | {1467DC6C-6C30-498B-9696-60E37D99774A}
NORTH BRANCH 110111158 | {441CFEC9-1CA0-48DF-94A7-C868FF359EA8}
SANTA NELLA 1101CB | {D9B42920-8795-457D-8506-B9A1003BB3E6}
SAN RAMON 210853732 | {009FED72-F984-488A-870A-FBDD7926AC29}
LOS MOLINOS 1101CB | {2F05D844-382F-480E-A414-A8255A95CC97}
HIGHLANDS 1103917328 | {420FCC10-4F1B-4366-A6B1-9FFE71DCA9D4}
CORTINA 1101107710 | {30FD709D-FDD9-476F-A094-8F17316D4F25}
VACAVILLE 110847860 | {59386278-9020-4BB7-BD46-9280C84FE5FF}
NAPA 1112315244 | {91380486-2659-460E-8E8C-74182A1F6A64}
MARIPOSA 2102241564 | {D6398899-238B-49AC-A776-D1F3468DFF9B}
WYANDOTTE 110613046 | {29C2B584-F455-4FA3-B4A4-3F4E989317C3}
BELMONT 11038958 | {B68C4BA8-94F5-4FA3-9062-8EFAD0B4F95D}
ORO FINO 110276008 | {EEE4445E-754A-4610-952B-CBD9BE00EDE8}
WILLOW CREEK 11015002 | {F93B7399-B5D7-47F7-B54D-9C6933AF7A2F}
MIRABEL 1101CB | {0DAF681A-D0A6-472F-BDFE-814CD10BFA9B}
LAKEWOOD 2110139484 | {B6F65C5B-8596-4980-BF5A-72D64E484475}
PENRYN 1107346 | {CD96B61F-E4EC-4F93-8ED7-3657DC7B6074}
COALINGA NO 1 11089714F | {D0D57548-BFE1-4E51-8167-796FFB6E7A8E}
OAKLAND J 1102CR252 | {FD5FE64E-C40E-49F6-A1B2-6062B4E7CFF6}
CALISTOGA 11015934 | {39A37840-00F8-46CB-8218-BB0855552677}
GATES 110692202 | {0403AD0A-8957-4413-B5CA-AB406F66F7FB}
STILLWATER 1102CB | {942A5D01-90B2-440A-92F6-C8D3C90D4346}
STANISLAUS 170237276 | {C3619A95-0ECC-48A6-ABDA-B7A0B8AC9A76}
VACA DIXON 110540092 | {D4665A08-FBB8-4B23-A149-E42CE69C940B}
AUBERRY 1101R2578 | {E7B58C7C-DEE3-44AF-9DC1-540E49CB1676}
UKIAH 11151216 | {190ED11E-6BBE-4AB9-A430-D568E91970DF}
MONTICELLO 1101256640 | {50BA7E67-5EAD-4941-88EC-76A715C41286}
DUNBAR 1103681238 | {E1077E4E-022A-4658-906D-61D41C4EF125}
CHOLAME 2102X18 | {D9DC2012-D30B-464F-B310-3196684B5ECE}
POTTER VALLEY P H 110576498 | {0A0C5F0B-CE32-47C8-9E33-CC208CAF8F95}
MAGUNDEN 1108250674 | {9C5EB345-7F42-4EDD-AEC2-EDD4964080F0}
CALAVERAS CEMENT 110111188 | {B3717E2C-44BF-4A63-A354-45BBFC0B5253}
ZACA 1101Y70 | {C56ADC1A-9E36-443A-A4AD-EABCB05C5CD5}
UKIAH 1111144510 | {2D399A89-FF4A-4D16-963F-99FB5F6695E4}
OAKLAND D 0407CB | {D6B258F1-A023-49ED-A291-5DC1514DFA3F}
PLACERVILLE 111219712 | {E3DC7090-B1A0-4812-A562-44F0E2AEC108}
CASTRO VALLEY 1108MR337 | {3ECE28A7-9E9D-4AFE-8619-84A42C55B001}
ALTO 11221212 | {480E1BDA-E928-4338-A7BA-DDA1B7A106EF}
OLEMA 110175686 | {702CCB2B-B1B0-4591-B980-760D81375AFB}
COARSEGOLD 210310820 | {87310FC6-15ED-48C6-A2E1-D0212614AC1A}
PAUL SWEET 210216006 | {ACD82200-9A89-4E0D-B5FF-D276794568F7}
LOGAN CREEK 2102767046 | {0DB23F18-2307-44BE-917D-7278F1DC4733}
ALHAMBRA 11058302 | {EAE1D7B0-E463-4F79-B04B-CDCA7EEEF36C}
PERRY 1101200598 | {F3BB7464-D4D3-443C-A678-902DB9A05DA5}
KANAKA 1101CB | {0C0686BD-4FFD-40DF-98D5-F53EB4C7C859}
PURISIMA 1101Y44 | {867AA1B1-4446-48B6-9D80-8E314456C23F}
CRESCENT MILLS 21012056 | {BEDEF3DF-E1F0-4BAB-9E81-90CA4240CF80}
CUYAMA 1104CB | {C3CB332E-B41D-4DA6-9C37-1357A17FBA81}
BRUNSWICK 111063100 | {F62664EC-2775-4F42-885E-6C5354881CBF}
MARIPOSA 210110240 | {4272B914-DD96-40AD-9866-404625A4A67D}
CARLOTTA 112144150 | {47D7E27E-F1F2-4AFA-B2C6-25B11F5B475A}
SOLEDAD 21017048 | {820718CC-7467-4DD2-B2F8-381F3D5B3CFD}
MENDOCINO 1101450 | {8EF50422-5CB8-4728-A990-D408AE9FCE63}
SARATOGA 1103CB | {9466ABB8-FD29-43E6-AC42-34C6719BD0EC}
ELK 11011260 | {AE0E521E-C3FF-493C-8531-F1F586FF92F5}
PENRYN 11072708 | {B656F43A-A721-479D-8405-E771FFE89131}
LAS GALLINAS A 1107554 | {DA43FDAA-0AFD-4DA3-9BAB-E9F0ED9A89B4}
SPRING GAP 170210720 | {A2735C5A-AC0C-48E2-9CB7-2F6A791B6D33}
PUEBLO 1105348368 | {CC4E6B7C-3A75-42D2-8AEA-EBA3500E2172}
MONTE RIO 11131313 | {2E6DCA70-6B36-4F65-B853-AA4AC3CF0E30}
REEDLEY 1104243924 | {15D80CB3-430C-4D10-9907-2D2A3FAA2A64}
MOUNTAIN QUARRIES 21011102 | {4F7ECBF9-F29B-4CC1-9A4D-006B1538826F}
SAN MIGUEL 1105765824 | {5DAC96E6-D800-4242-8BE0-8DEA9CB14558}
CALISTOGA 1102963232 | {5EEDD19C-D1E4-417C-AEDF-CB3B24F7FA99}
COTTONWOOD 11031348 | {7B732F61-9830-429D-98CB-A07442DFF2C3}
LLAGAS 2106XR296 | {36DDC7E6-DD90-43BE-A64F-8D62BC22EEA3}
SILVERADO 2105861266 | {AA30177A-A383-43BF-A978-435A7E84A10D}
MORAGA 1102161484 | {BF062587-F543-4494-9BCB-AB97B3FA4161}
ALLEGHANY 1101VR816 | {FD2262BF-C160-4434-8E95-55FF0A0B15F6}
BRUNSWICK 11021010 | {CA5C38FD-CE12-4872-96AA-D926F4220C4F}
WYANDOTTE 1109758802 | {EC08C284-9906-406B-94E5-ADD7510D64ED}
BALCH NO 1 1101406582 | {F32CC135-97A4-4BFA-A01E-518E8F21967F}
CLAYTON 221798080 | {02D34549-5AC7-4AFF-A057-7824A31FF47B}
SANTA YNEZ 1104Y28 | {D5DD389C-0EE7-4085-B05C-70F106F6B79D}
CARRIZO PLAINS 11013527 | {DF118858-83A9-4B97-BE1A-B9801D7678FF}
ROSSMOOR 1106CB | {DFA21900-F572-4D0B-90D6-E67080E9EF87}
FITCH MOUNTAIN 1111610 | {1D8E3949-43DF-43FB-98A9-8DD711C7AB01}
AUBERRY 1101233716 | {4B373C79-EE2B-4490-BA99-503E66D60707}
VACAVILLE 111113652 | {A457A03A-C6E6-47D1-86AC-AE763850EDD5}
PACIFICA 1102267868 | {275774F1-4908-4480-8C4A-1E1AEF9EEB75}
TEMBLOR 11049126 | {C2992F46-2554-463F-8E87-219C3C230B9E}
CURTIS 1702295684 | {A1BFE45A-13E7-4FF1-9988-30B11E2FBC1C}
MIWUK 170193062 | {B18F77BC-A9DA-4B29-AB14-C0D1FCA97447}
ALTO 112332448 | {C469F866-3A91-4B43-94B4-8116C5F6A5C8}
CORRAL 110336680 | {EB467927-3D28-42DC-B202-516334CB2DF4}
EL CERRITO G 1113BR282 | {F1CD3584-0342-4B1C-AC95-933DCB32DB86}
VACAVILLE 1111905076 | {3A0CCFE3-C12C-4384-B593-6A5D6B4AD5AF}
OAKHURST 1101CB | {2CDF7848-B063-4FC4-9C52-AE29AA49D3FF}
LAKEWOOD 210757670 | {8B044506-1700-4270-904E-C6B876F0B7BE}
TIGER CREEK 0201320746 | {C7F675D5-2B2A-49BD-AF13-9888C7E4FCA2}
MIDDLETOWN 1103CB | {EF7692CE-6490-45CF-89E0-AAC63F03AECA}
MENLO 11037902 | {8A15255F-3865-4264-A6D3-8F9EE2AA73EF}
CAMP EVERS 21035402 | {CEB97A6E-057E-4617-8BF5-91D85F0FC1F8}
PINECREST 04011818 | {D8E71690-B481-4860-BE72-8B484DD0017D}
IGNACIO 1105775176 | {E636DD2B-323A-4E65-AE99-16FA1288A9E0}
LOS GATOS 110760092 | {FE58AABB-4F2E-4F6C-8A2E-70A2F4BDC1F4}
GIRVAN 110280726 | {1C2C814F-78D0-401D-8386-69906E2875F3}
CALISTOGA 1101537148 | {950B7723-A5B4-41CD-A0A5-13F29B883B0B}
WINDSOR 1103CB | {AC54FADD-7787-4603-A3A1-1A1440375EA4}
SAUSALITO 11021224 | {BE77E89E-D575-4124-AA7C-BF07ADE3CD3D}
BURNEY 1101CB | {DD5BA261-28C3-4395-8BF5-3D293075C1EE}
TIDEWATER 2106C540R | {2DE5693C-879D-4FCD-88B6-818902BD649A}
CASTRO VALLEY 1111MR334 | {144B3CD2-37D4-4FA9-8973-1F3A9C9CD174}
BERKELEY F 0402502466 | {5BAFA9F8-CA96-406F-9803-715FC721E178}
SARATOGA 1105LC14 | {D8F111B1-64B9-41D7-9211-8173FEC05653}
VASCO 1103964102 | {DA001B7B-04D4-4B91-80D8-0CD4D55EE955}
BRENTWOOD 21056512 | {DA007DA4-760F-4151-A582-C98D9C468550}
GEYSERVILLE 1101711966 | {1896BE4A-1AA3-4F21-93D4-ED4B47D95FC3}
CLARK ROAD 1102407706 | {2CB09E0C-64E6-4F21-99AA-BAB6BE3DC5D0}
OCEANO 1104337754 | {EF084BAC-E8B6-45D7-885C-1A50430DEB23}
VIEJO 220235388 | {5487E49D-3A5D-43A1-BCCA-6878D14EA68E}
SAUSALITO 1102964592 | {EE9BA2A3-B7F1-4ADE-BF30-423061F0C66F}
WHEELER RIDGE 11012878 | {F5B58D0D-3D6A-436B-9C40-AFEED4581FEF}
CABRILLO 1103Y46 | {02264660-E3C6-4806-AC6E-28401EBDA58A}
JESSUP 11031518 | {16E5A2EC-59F7-4145-9776-574EFD44BE58}
DEL MONTE 210386496 | {572A903E-D7FD-4349-978F-5FBD205DDA11}
MARIPOSA 210197142 | {5AF7FF1D-FC61-4F2B-B337-918BFB6B463C}
COTATI 1105213984 | {681EF2A3-DED2-470D-950D-0263CA946ECD}
HALF MOON BAY 11028910 | {72FA64D8-3A63-4420-A7D7-130A2E3D886E}
RACETRACK 1703759144 | {BD9AA387-4336-4A73-8479-F487626759F8}
MORRO BAY 1102W24 | {4C9F3CAE-E991-4EA7-BCAB-BA03C4CEAE92}
RESERVATION ROAD 1101975548 | {F1FA9138-E071-404A-A9E5-572EE0A580EB}
LAURELES 11116421 | {03861487-35BB-45AB-853E-5E8CD2B590E5}
LOS OSITOS 21037014 | {1106E17B-9FEA-4422-BC78-03AC3BC8E250}
DIAMOND SPRINGS 110719702 | {635CA5E5-8968-4E76-BA11-3BE643BA9E35}
LAS GALLINAS A 110436840 | {B49A679E-AF73-47B6-A79D-47CB4D4EEA89}
CARBONA 110145186 | {D5A2A0ED-5854-48FF-9353-DEF3C343CB3C}
WYANDOTTE 11031504 | {ED98A6D0-06D7-43E4-A03B-484FE67F86A6}
REEDLEY 1112477952 | {EE0E49AF-2EA8-49CD-B4D9-4F587BDF49BA}
VINEYARD 2107978364 | {3BBA2979-D28D-4292-8651-8D6BC40655D3}
ELK CREEK 11012008 | {49F083FF-CCD6-4656-915A-45D76A900BBC}
POINT ARENA 11013702 | {5DD49BEE-09C2-4674-9D89-3A76B7F55110}
CURTIS 1702CB | {7226EEDE-AAEC-45AB-A41D-23DA3572485A}
CORRAL 11012128 | {B16B71D1-22D0-45E3-8592-F21047B1C034}
MONTE RIO 1112938174 | {D361D503-3790-453C-B66D-A7A3345502F7}
SAN LUIS OBISPO 1107V02 | {1413E321-0BD6-4E14-989C-C8FF6A4A6DD1}
VOLTA 11011596 | {2F8DBBAA-A379-4ECE-8007-F482E8F75EAA}
GUALALA 1112CB | {8A730939-42F5-47D3-8D16-1FB3EEA2BAEF}
NOVATO 1104422246 | {45CE06EC-53C4-4919-88F0-CCEFB9190769}
LAS GALLINAS A 1107662 | {18214BA8-F1AB-49DB-836F-E6DF072AD66A}
SUMMIT 11022302 | {4DAC7BB8-BA46-4649-99C3-6D0CB53CFA90}
WILLIAMS 110230232 | {ADFD680A-942E-4051-AFFB-E1BB46F8DE19}
COVELO 1101664688 | {1E92B113-D351-4051-A3ED-221149B2FA2D}
SOBRANTE 1101934036 | {21AC5929-6E59-49F5-90AA-DFB268A45B54}
GARBERVILLE 11024744 | {221BC5D9-51C0-467D-BFB7-19AAD7C5E6CD}
LE GRAND 11045010 | {2DA20832-0986-4675-BA93-1E55E4E2B6B0}
TEMPLETON 2112R80 | {3E696401-4261-4D08-869B-B3D4019E7D36}
GERBER 11023771 | {51D7DA46-9CAC-46EE-9575-3C307DF390C6}
DUNLAP 1102CB | {A6D1F5C5-C503-4CFC-844D-2877BC97AA39}
DEL MONTE 21043066 | {F5363A17-6294-4FBA-A5E9-297DB437E9E9}
PINE GROVE 110245292 | {EB0CF7B2-4A78-45DE-8AED-51D903B9E71F}
PUEBLO 1102662 | {1AE19971-F682-43DD-B35E-DF767DF7D39D}
ROSSMOOR 110542088 | {2CF05CCD-DA30-4E66-88FB-8AE7485C3DA7}
REEDLEY 1104274990 | {1B9CB438-3D64-400D-8827-441645AF1444}
KERN OIL 110646960 | {1BEA114F-1545-4690-B5EF-CA295187FA4B}
KERCKHOFF 1101CB | {5CEBE369-1234-4C2E-B50B-4FF49A63CB11}
PENRYN 1103CB | {87180880-8EB9-4F8B-82CC-028E4C7029F0}
PEORIA 170169124 | {8AAD3A20-76BA-4DD7-9403-7AA47644DC04}
FULTON 11075058 | {72AE5EDE-AC15-4265-AF32-67B0F370C217}
VIEJO 2203CB | {4DC9724F-62CE-4CE8-B9B2-FC8D42753B78}
SUNOL 1101CB | {6830085F-FF28-4A85-9104-F5B6CFD24479}
RACETRACK 17038120 | {B167BE1C-A9FE-47A6-A4DC-3662D3CE2EC1}
SHINGLE SPRINGS 210913322 | {C2386B39-9DEB-4629-9750-D5EE983424AF}
FRUITLAND 1142615540 | {C9D02877-D683-4E00-8203-11814AA4CD46}
WYANDOTTE 110940608 | {CDE1CEEE-8C9B-4065-8C9F-F4DC3E571419}
LAKEVILLE 1101CB | {DCB62918-25E3-416E-A1A9-9199A2CE1F5F}
SHEPHERD 2111688294 | {043E8F07-84F7-4AE7-BB3D-18F6172375EA}
RESEARCH 2102CB | {16057A1D-A77A-4434-99E8-5E9C232075A4}
MENLO 1103866118 | {8A15255F-3865-4264-A6D3-8F9EE2AA73EF}
SHINGLE SPRINGS 210551738 | {82A82E49-B7B9-4B20-91CE-19896367619D}
COTATI 11055156 | {ACC3FA28-9FAB-4AE9-AABE-1ABF0B659322}
CLOVERDALE 1101964556 | {C8B8F7FB-319D-436A-B288-8DB11A5DC4AF}
CAMP EVERS 210595050 | {CA99B367-8DC7-4E82-BCC3-DFC89B2C9160}
MIDDLETOWN 1103830 | {F5CA881C-11A8-4857-9165-F7C1423FEF9F}
GIRVAN 11029012 | {10010FC4-3D49-44D1-8CB1-63E2C5CA1480}
CAMP EVERS 2104CB | {84EE2558-0006-42C6-8836-08F2D7F2DAA3}
CAMP EVERS 21055188 | {8C44BEAB-509E-4818-A7FB-FBD552205E02}
COLUMBIA HILL 110190730 | {8D36000E-CB6A-4063-B9B3-E1FA6651AB85}
JANES CREEK 110141990 | {B4EC8E85-89E6-4E1E-A58C-F910365EBD5D}
GREENBRAE 11041302 | {84506FE0-5799-4537-9C92-AE6186A1DEC5}
ELECTRA 1101175840 | {46D2F232-282F-454C-99DD-05E7F6733AC1}
MORGAN HILL 2108CB | {4DF45F56-E0C5-4EB4-A8CE-218D259985D0}
MIWUK 170153038 | {AA9722DD-9A20-411C-A91B-FCD027C3242A}
BELL 111050522 | {E670C03E-CA4E-48A0-8E3D-40CC604AC7DD}
TEMPLETON 2113A10 | {E6F3FB48-7B73-44A2-9D22-75A3F05024E8}
PUEBLO 1105642 | {2AEE294B-FE8D-44F1-8029-584BDB7857EF}
ROB ROY 2105CB | {65F8EE18-25DB-48C0-8EE8-63D74E373DA3}
CORRAL 110112304 | {C6783DDC-8CCC-4EFE-8097-5CE8336375DE}
ARLINGTON 0401404226 | {B073565E-E5DC-4302-BADE-27F696E6F580}
TASSAJARA 2109CB | {E1A9F699-2041-4569-A9A7-03860994D8BC}
KETTLEMAN HILLS 1101CB | {E3191191-EC32-4B60-A32F-F8582A37B6F0}
CHOLAME 2102X02 | {042A33DE-71B1-40FB-B0CF-6D56CCA576B0}
PLACERVILLE 210619552 | {0286A39D-02E8-4B52-9BF3-B9BA1A908257}
STANISLAUS 17011331 | {34B1CFFF-1F43-44C3-AF15-E50BDC16F6A4}
TOKAY 1101CB | {11EDF2B5-A0C5-48FD-9A56-5F2C5A063907}
CALISTOGA 1102714556 | {AEB996A6-B3E6-422B-A668-DF66D3A05824}
NEWBURG 11313446 | {8A80C7E5-86DA-415B-A0BF-702ACAC61E9A}
HALF MOON BAY 1101818874 | {94188B54-65D0-48E4-B281-167ED6270B8E}
ALTO 1125530664 | {DA893851-A239-41E8-8E7B-70F066561313}
BRUNSWICK 11062392 | {F0B6C592-2F67-4F88-A13D-794768FAAAF8}
PIT NO 3 21011386 | {4A0A56A3-602B-4EA0-9D5D-4F9EBD3DE945}
SONOMA 1106296492 | {55EA2698-B693-4D7C-84A6-FBA73C981197}
SAN ARDO 11017094 | {A9BAF716-D950-4219-B81C-E6209F590D56}
SILVERADO 2104324994 | {E948BFE3-2646-4701-991A-B5E0EF4D54D5}
TEMPLETON 2109R78 | {23FDF1DB-782E-4000-92DD-5A064AF483AC}
CORRAL 1103936674 | {6A75A276-6764-44DB-AA5D-741492F8A6AA}
CALAVERAS CEMENT 110111236 | {765E2074-110B-4FD6-8019-AD09D7431DAB}
GREEN VALLEY 21036661 | {80B98B39-6C55-4280-B2BD-3BF57A0B5E71}
RINCON 110275816 | {2FAB6430-43D4-439B-B7B8-4BB8DFD0CD27}
TIVY VALLEY 1106D8492 | {90E00265-C0CF-4482-89EA-4364E2D4853A}
HICKS 2101XR548 | {21823ADE-60D1-49AF-96C7-A6BCD78F0512}
DUNBAR 11034882 | {2B1CF1D9-BF9E-474F-B027-6D9BAFB42F24}
HIGHLANDS 110486807 | {4153AD52-F0C3-4F94-B9A7-DBFADEA8B1B3}
HOPLAND 1101154790 | {90407EF8-546C-4CC0-BAC4-A3C598D39737}
ARCATA 11211206 | {AF459D89-AFC9-4CD3-8D0B-AF684DED3FA0}
TULUCAY 1101628 | {E6EA8FFD-93FC-4EE2-B4B3-05C67BB86274}
MOLINO 1101322 | {87C4E1DE-229A-456D-853B-731F9308D34F}
COTTONWOOD 110359128 | {7A360B24-DB74-4302-B7FF-A7991F9BEB20}
BELLEVUE 1102463316 | {D29926DB-AE31-4DF0-BAC8-C7164572C130}
WOODSIDE 110551262 | {B0B93653-ABAA-40D2-863C-C601369FC194}
VALLEY VIEW 1106P180 | {27893E9C-0A5B-4290-96D8-63CEC0636192}
JESSUP 11013383 | {4BBBA9F5-2A5C-430F-82E9-5C32AA8B7737}
PUTAH CREEK 110396792 | {520DA4C4-E38A-4EBC-850C-F11EB0848411}
CAMP EVERS 21067603 | {4EC0C5CA-D3E9-47E9-809A-55A51CA9C021}
MOUNTAIN QUARRIES 21011346 | {B959CC4A-E894-449B-BBA9-D2734BD80359}
EDES 1112CR312 | {C2D0F25E-59C9-41E0-A6F7-60C91C33934C}
MENLO 11029092 | {CB7FED94-E514-4F6A-B3B1-FDD03272551C}
EL CERRITO G 1113CB | {F1CD3584-0342-4B1C-AC95-933DCB32DB86}
FITCH MOUNTAIN 1113677510 | {034C6230-F1B3-44AD-89C0-4E5511DEDDB5}
RINCON 11035152 | {1D81D8F5-A042-428A-8894-895D8E08C89E}
GOLDTREE 1105CB | {2BB441D5-FA7B-41CB-B4C4-3BB6BA3702C5}
GREENBRAE 1104751 | {84506FE0-5799-4537-9C92-AE6186A1DEC5}
NEWBURG 113190242 | {3A3BBF86-310F-432E-A06D-A8536237FB4D}
OAKLAND X 1101CR224 | {42F99BA0-D146-40B7-AEEE-A7B52478E064}
LAYTONVILLE 1101518 | {48D8AB29-32BE-434B-A269-6B6F081BC956}
COVELO 1101112804 | {5A8F3694-A0F4-41C3-88AB-492CAEAEF38E}
WESTLEY 11039900 | {0DB6DB9D-7804-4D10-B639-1A5CA91DDA98}
HERDLYN 1102CUS1379 | {6D42CB7A-C91F-4DBB-9706-F92EF8B0963E}
DEL MONTE 21043088 | {FB7A8750-C967-4B2F-BC27-F33BBB5DCEFD}
TASSAJARA 2106CB | {0F972632-618F-44CB-A965-3BB4F6195935}
FRUITLAND 11426064 | {4A1EC5D3-CF7E-4E3A-B115-9A4757B7DAC6}
HAMILTON BRANCH 11012436 | {637602BE-E394-4D87-B06C-9852D4AA6AF2}
LOYOLA 1102LL62 | {AB8403D1-2343-4452-8395-9C954CC8DC13}
HICKS 2103LB50 | {ED3D87A2-B26D-4CB8-8B3D-56CD442881C5}
ALLEGHANY 1101808 | {FD2262BF-C160-4434-8E95-55FF0A0B15F6}
SANTA ROSA A 1111758024 | {FFCF3ECB-BCF6-4D7C-80BD-D22A2A7318FC}
FORT ROSS 112170288 | {19BB688C-7539-4331-8ED9-2B0221333B05}
ARCATA 11216004 | {7105441B-4177-4883-821E-B79840B9E771}
RED BLUFF 1104135854 | {7A5937DD-12B9-45A4-A4A3-79E6F1361431}
IONE 110113446 | {E7CD9906-89BD-49E9-822A-3B11AFC2B697}
STANISLAUS 17017144 | {EBD937A8-0F05-49AA-848E-8FB362E60B61}
HOLLISTER 210491424 | {951B1516-4326-49B7-849D-E72573882819}
DIAMOND SPRINGS 11039432 | {A12D2A90-44E6-4ECA-BE2F-8893B2D17E74}
CORRAL 110133616 | {ADB98FB7-737B-452B-893E-B8C57E3FA760}
PUEBLO 2102943820 | {BC3FC9AC-589D-48EE-984C-94B4C353EDD1}
CURTIS 17019230 | {BD6EE575-4256-4E66-B07C-5D3BE152301A}
MENDOCINO 110137462 | {CBF297F1-D8F4-467D-B156-4EC62C764040}
OROSI 1102617446 | {38342D33-FCBD-48C5-A427-7A9D99AAC119}
PRUNEDALE 1110CB | {43A69DC1-4C36-4A90-B444-3F421C39E759}
WISE 1102307494 | {DAD370F0-D502-456B-9D6C-C04B93F7ABC9}
OTTER 110298036 | {05EEF29D-5376-4D63-9244-FB865CD63617}
EL DORADO PH 2102771208 | {40FC7F52-2B65-471F-ACDA-BEA2893716D4}
IONE 110112236 | {9D5BFE02-DE54-49D0-8A6C-80BCABF7CBD7}
COVELO 1101679050 | {211F2948-077B-47E2-AE1D-731B8C6DAA7F}
ROB ROY 2105796388 | {239842ED-B895-435E-91C3-BDF520C0114A}
DEL MONTE 21029060 | {6CCE4F90-013B-444F-9BDA-6C6A4EE75374}
MIRABEL 1102524356 | {93EAC16B-EBC7-4B14-81C7-36C500A3A6BF}
HARTLEY 1101CB | {9A7B1854-4374-4D14-BB43-EA4EAD6446AB}
MONROE 2103222 | {D546C25E-2665-4E0F-83E6-19A6D0D70A7D}
WISHON 1101514298 | {CACEDC8F-E904-428B-BE98-B04E14D43479}
RED BLUFF 11011334 | {0CEFEC1C-E5A7-4802-97C4-53CDE555B5DF}
SILVERADO 210437632 | {13A712E3-B547-41AB-8639-0CAD4756D0FC}
SAND CREEK 110397354 | {1C32E9CE-3898-49FE-891B-A309867CC97B}
VINEYARD 2107MR649 | {E0DA3FA9-134E-46BA-BA63-A138252A7798}
DUNLAP 11027060 | {DC0C9AE9-E0EC-4108-AF9E-4DDFE694FC71}
STONE CORRAL 11087592F | {9C22AB4D-7471-42A3-9430-CD197230D588}
GOLDTREE 1108CB | {0CEB70F5-2209-4B8B-BEA6-B7EBAFD3DEEB}
SAN LUIS OBISPO 1107456456 | {FE7ADF6B-5FAD-4650-8E18-1F81A8FDEE84}
ALTO 1124703432 | {60AD6E98-4C8E-4B03-A21E-57588A85616E}
SAN ARDO 1101824808 | {D178EAD0-51DA-46C3-AC83-7A5FC311BC88}
MIRABEL 1101831090 | {1FA8A5B8-216C-48A5-8B5C-D037DBE66063}
PENRYN 110790970 | {9DF5CB55-1623-4B4B-9F53-43CFDE7622F1}
OAKLAND J 1102951816 | {F44E0750-FE39-44A0-8598-B8A75709D6C1}
PARADISE 1105CB | {4E875C07-9BF0-416D-8352-B1380CD2F62E}
BASALT 110635550 | {31C38397-CC97-43EB-A38A-D18D8FE5AEB7}
ROSSMOOR 1106349024 | {D175B824-8D4A-4E43-87C6-A3785AB99098}
COTATI 110494186 | {2F39A049-2BA5-4A00-94B6-4F8A51F9E4CE}
MARICOPA 1102CB | {3886D126-B275-4867-A304-EDF3653324EA}
VIEJO 220436948 | {942157E7-82C2-4FD2-994B-E6CDBC22CA49}
REDBUD 11022013 | {D29B0306-223B-4BFF-9389-253396BA7A0F}
FREMONT 1104MR707 | {62124451-9B9F-46EB-B50A-534B1B0CB257}
TEMPLETON 2113848137 | {FB380A98-AA0D-4842-98E9-EA318AC8BB0D}
CABRILLO 1103Y12 | {723FB00A-7C12-42CB-85FE-70F2D7BE445E}
ECHO SUMMIT 1101265728 | {14BBAC88-26D3-4F29-8425-274D619391ED}
DEVILS DEN 1101824190 | {2555B82F-7B04-4543-97DE-389AB426740D}
BIG BEND 1101180398 | {8A0E1297-B2C6-4E29-9AF9-DF1E115646B0}
SAN RAFAEL 1106588020 | {93B83BF6-0390-40F7-ADB3-1AD8B7256ABB}
REDBUD 1101323962 | {ADA3ACDD-1F23-47D9-8D0C-75E817018764}
BLUE LAKE 110256630 | {3C7601AF-6F6C-4334-9C5E-41DFDCEC0722}
PANOCHE 11034008 | {0C7E1298-8ED7-4AF4-8E12-9D89E23F7125}
TYLER 1105CB | {AAAE8701-80F0-46AE-8702-4013E06C972E}
HIGGINS 111051794 | {B86F1700-5A54-45AD-BE5A-60237D0F62CD}
VIEJO 22029112 | {BEBF2F35-AA76-45BC-AFD8-E27852839913}
WILLOW CREEK 1101CB | {D8B02D5B-6C13-4C05-89BB-FB46690FC150}
HORSESHOE 110451536 | {DCF001D4-BEE1-4DF1-BC31-9FDF6ADCEBFC}
JAMESON 11057652 | {15E7F33B-BC99-41F7-80A1-54BDC820E172}
BIG MEADOWS 2101CB | {48DFC761-81AC-4E6E-A815-DEA2190E6576}
RAWSON 11033314 | {7BD4E626-0623-483B-B7FA-C43993C96595}
ROB ROY 210410954 | {A588ED32-95D8-43A3-8FC4-5077DBA91F77}
BELL 1109724884 | {C6312B9E-C10C-4771-B9EE-B7179EF46C16}
SILVERADO 210258626 | {05AC1C5B-D6E1-429E-A072-263D6E199803}
MONTICELLO 1101720 | {07BF8128-F528-4070-AA6F-0E3ACF3A793A}
OCEANO 1104Q12 | {1F61853A-FECA-4E03-86FF-C3BDC269D699}
WILLOW PASS 2107CB | {24C8C7E8-733A-453C-8A4F-FE8CF59DAF59}
STONE CORRAL 1110894956 | {28CCBA34-60FA-4FD7-81DE-39D9BA572A75}
BEN LOMOND 040116010 | {52BA473C-1BA5-4952-86A7-343CF045CF65}
FORT ORD 21079614 | {5AF19FAC-D5B1-4A0E-9483-EA04C351FFDD}
HUMBOLDT BAY 1102104220 | {92404771-2B96-4EE9-9A7E-4C0DA339A55A}
DUNBAR 1103799422 | {587017B7-CF95-40B8-A31E-326EDAB4E012}
POSO MOUNTAIN 2104CB | {AA81189C-0FB0-446B-B000-4E0A59F32937}
HATTON 11022010 | {07CA7935-70B1-4CBA-B069-3C5BAF9F4438}
TASSAJARA 2112D569R | {182E7891-748D-4B1C-AB5C-2655C693C420}
OCEANO 1104104102 | {6F967F18-8991-4C9D-8139-526CA500F4D2}
HALF MOON BAY 11039112 | {F951C9B5-DFF6-4F18-959A-6543A104D243}
CORONA 1103776806 | {02DCFD19-ACE4-4ED7-8974-B818BB682331}
SUMMIT 110186658 | {CD142DCA-BFBC-491B-9C29-D02961854E56}
EL DORADO PH 210113362 | {5789A00B-A217-4C31-8B0F-242AC56113D1}
GUALALA 1111CB | {73132ABD-89F1-46DF-ADF4-0148C2A7C9B0}
NEWBURG 1131CB | {C04ABA60-50E1-4D28-B0FC-7F9C72775B5F}
ALTO 112265474 | {C2F314B0-1B7A-4CC5-862B-042BD22A1A33}
NAPA 111289474 | {D8230112-C16E-4959-B193-6B3851D10773}
CHOLAME 2102X06 | {2CD93861-C1D5-4471-A09B-75955F723957}
SAN LUIS OBISPO 1101592368 | {6095BEE0-0C36-47E1-939F-BFF38B2ABD81}
CORNING 110185162 | {9C401B14-4A54-4DA8-B9DB-3EDB68F74D1D}
BASALT 1106CUS167 | {4B4F529E-61C9-4763-88C9-BA9E643D6014}
COARSEGOLD 21025722 | {28AC0DE3-760D-482C-B0A3-0B7999D74D44}
VOLTA 110153118 | {0F8042BD-810A-4C9D-833A-F377AF6EE4DF}
SARATOGA 1115LC20 | {3FC7657A-E97F-4835-8F9A-E34BACD9F92C}
SONOMA 11054456 | {4BB2B9D0-8D98-43BA-87AD-9BC7CE46F8C2}
SNEATH LANE 110210255 | {40980895-4B8E-4C74-B15F-E13FF900DC4F}
GUALALA 11121294 | {6177229C-DB60-448B-B309-D4C2F1A2330C}
PERRY 1101W12 | {743AA0A1-467D-436E-BBF0-31F00EC2544E}
RINCON 1102782389 | {06E2A336-248D-48CA-909C-FCEA57AB6ED4}
MOLINO 1101891 | {366DDD05-C36C-4018-8E0C-E1718F820EB6}
WOODACRE 11011456 | {1ACD7F45-5073-4366-9697-A511E06B0768}
RIO DELL 1101CB | {6FEFE5FA-547D-43B0-B009-E716079C25C4}
MIWUK 170179118 | {7A676B71-51F1-4DF0-A596-B3D6F63218D3}
SISQUOC 1104301229 | {4D6D6BF4-E19B-4629-9318-504AFE626164}
VIEJO 22039094 | {BCAEB21F-2017-4B30-B93C-AB6BCBE099D0}
WILLITS 1103538 | {0092EF79-68EA-4B6C-8B69-750DA296468A}
CLAYTON 2215CB | {17D49159-2A99-4FB5-B2DC-0815D2D13280}
CALAVERAS CEMENT 110136880 | {2CE7DA92-EEC1-4680-BEC4-A1E05BA2B50C}
DIAMOND SPRINGS 1106762780 | {5E624FA1-8898-49A2-BC33-0C0CCA1E740F}
PEABODY 2113945670 | {463CEDCD-A864-4BE7-A495-4562C479EEC4}
COARSEGOLD 2102383092 | {426A5610-C0CB-4740-A0E9-5755646CBB70}
CURTIS 170247488 | {A13891AD-BB5A-427E-8F5C-CEB24021177B}
ALHAMBRA 110581514 | {AC26085C-F280-4A6A-A0D9-361E1E9983F9}
KETTLEMAN HILLS 21049020 | {B053CDDE-1D32-495C-9C06-5A87198FD76A}
TEMPLETON 2109P32 | {BE3D916E-88E2-482C-892F-AF61F2F67735}
BRUNSWICK 11041020 | {DBDF15C5-1C5A-46A1-9C80-FCF08A12927F}
TASSAJARA 2113MR457 | {B9D0F1F0-F20F-489B-8E21-22409D603A4D}
DUNBAR 1103302 | {34794EA8-41B0-4C58-A267-88FB7ED2F311}
FRUITLAND 11426054 | {4DE5CD9A-1BC1-4D9F-A13E-0336C2BFEF7C}
PIERCY 2110CB | {6C9416AC-4CC1-4577-A462-96F88C7F1AEF}
COARSEGOLD 2104791582 | {8C9C1F4D-9C24-4A9A-947D-D1CEA924DCBB}
CAMP EVERS 210611044 | {90D97D29-641D-4D44-ABC6-DEB499FDF2DF}
DEL MONTE 2102615458 | {6CCE4F90-013B-444F-9BDA-6C6A4EE75374}
SILVERADO 210234959 | {03890B2D-86C2-4585-9C1D-5FAACC6CEB0E}
BIG BEND 1101CB | {25C4070D-0704-4FE8-B250-876F6C426225}
CEDAR CREEK 11011656 | {383E38F1-9CAC-409E-B20B-DAC5E1331447}
SAN CARLOS 0404CB | {997E35A5-4F56-4E03-9F74-715398B359A5}
PASO ROBLES 1103N58 | {ABB59667-7D2C-427E-8CD5-70D7C7F4474B}
FELLOWS 210382182 | {A2B8C63A-2E3C-415F-A84C-6AAC2DF68E0B}
SILVERADO 2103315138 | {66AAADD9-54A2-4D43-B82B-F401906AF14B}
WYANDOTTE 110738438 | {112CEC5D-7594-450C-A06E-88C65F1E5892}
BASALT 1106CB | {230E7534-26E2-46DC-BF08-6106FB749B89}
VALLEY VIEW 1106P128 | {30491B06-175D-4B50-9477-0E42FFDBA4F5}
CAMBRIA 1101CB | {5CB94E28-BCD0-4946-A0EA-D8080443F8CB}
ALHAMBRA 1101CB | {8AE2EF2A-3822-4BB8-8505-AA1FB37F605D}
ALTO 112191428 | {987386B4-3AF7-40EE-94AC-C1508EDFA8F3}
PETALUMA C 1109128 | {003177BD-8A4D-4A57-8E37-AC044D50D3EA}
MONTE RIO 11125040 | {2864C93C-BF52-4E0B-A5D1-FA5019DBF7C4}
WOODACRE 110196844 | {829ACA47-635E-4880-92A0-8C929EC179A6}
COARSEGOLD 21036110 | {04B6E7EF-7D58-4AD6-8C95-F9DC0FD8A439}
BASALT 1101CB | {36CB0205-94DA-45AD-B087-D2736F00D26A}
OAKLAND K 1101CR178 | {3AC71A95-3DF9-478B-ACCE-8AC300269CEA}
SAN LEANDRO U 1114501762 | {C98515D1-8118-4F7F-9133-7ABF5BE205C0}
MARIPOSA 2101752630 | {482F0B3D-137A-48C9-9E82-504F3E80E798}
KING CITY 1102728782 | {0D58B496-6AB1-442B-8B1C-174456B4DA3C}
DUNLAP 1103CB | {2C485712-3D09-43E6-B47A-A2006FA28A66}
SAN MIGUEL 1104R54 | {44EB9D6F-C95C-4275-8EE8-1FAA212EEB1F}
TEJON 1102732836 | {A9055457-4647-4903-9845-7B35001BBD43}
SAN RAFAEL 1107CB | {AC6B2CFB-8470-47A8-8CFF-360D120857F5}
MIDDLETOWN 1101128648 | {B7C3ED67-9905-41F0-81DC-45B8DE5466D9}
EL DORADO PH 21026645 | {876266AC-37EA-414C-92FC-94A2ACD4EB2D}
MONTE RIO 1113652 | {1A58D4D4-08C9-4897-B970-7F34BB31F59C}
LINCOLN 110195756 | {46334C59-6E86-4DFA-8790-B3204A43F682}
CLARKSVILLE 211011112 | {6508E8D3-0E1A-4D53-A06C-C666BBE3F64E}
FOOTHILL 1101CB | {A0154153-BF56-4706-9955-FEBD0CFAAAA7}
CALAVERAS CEMENT 110113424 | {B1720971-4842-488B-929E-F65E96985B19}
PASO ROBLES 1104P02 | {8D8A441E-1C9B-4D22-BCF5-1C9794F2F9D9}
CORTINA 110130192 | {E3B77E93-BB57-4588-891B-4456F675EF56}
SAN RAMON 211995606 | {0CC5B62D-8E39-47F2-A113-AB2F434531F0}
CALISTOGA 1101843761 | {0B54DF53-2082-4B6F-9020-553C5C7EBC03}
DEL MONTE 21042762 | {32A9C949-424C-43B5-963D-82C15E14F50A}
LAMONT 110217566 | {97C1B34A-95F8-4CCE-8DCC-4962D06B743A}
PANOCHE 11034010 | {8C4CDF18-070E-4712-A105-26C4CB39CA5E}
TEMBLOR 110414233 | {99CF017F-6ED0-462F-8AD1-7CD56A44DE93}
TIVY VALLEY 110737522 | {DA50CC20-DF93-4A26-9942-3A43E97DCAC4}
VIEJO 22029100 | {BEBF2F35-AA76-45BC-AFD8-E27852839913}
PUEBLO 110256136 | {1AE19971-F682-43DD-B35E-DF767DF7D39D}
PACIFICA 1102320094 | {3BE78651-BE87-4B28-8A48-F46DBB91FDDB}
NOVATO 1101CB | {6FEEE710-65A0-4303-87FF-23996199A852}
WHEELER RIDGE 110137662 | {E4E8B6C8-61FB-4D05-90A7-1AEC2AB09918}
SAN RAMON 2102CB | {AFA2F3E5-5A6D-403E-A015-1BB8AB0D90BE}
COTATI 1104426 | {B13BE392-390E-4E3B-A432-5336348FF9E8}
WOODSIDE 110176194 | {D1B97B5C-C0C0-4C1A-A0E9-54FF1BD58307}
PENRYN 11072704 | {3C765F3F-8878-4C34-98CF-2D3F31F6AD44}
EL DORADO PH 21016852 | {550714A4-7303-4842-936D-572C7CE200C4}
NARROWS 21011202 | {63551680-2169-45C3-BF85-1608C868FCAF}
CRESTA 1101103126 | {8CC5C28A-D4E3-4E7C-8DC9-1431E561B6CC}
DIAMOND SPRINGS 1106CB | {C99F1365-4BA0-493A-A0A5-5D7F7D14700C}
HOPLAND 110180620 | {CEE02838-136E-45AF-B305-63BB762F2ACE}
HORSESHOE 1106CB | {E78C9DEE-4564-4CED-86F6-578EC71D6FE0}
KING CITY 11067032 | {EC91064F-2715-4BD5-A3A7-0B8166F6F214}
FULTON 110257686 | {08567963-8339-4FA1-9F78-3A951553BB03}
CUYAMA 11033539 | {086ABE98-CA07-4B5E-94A2-D2E7EF6983E6}
TASSAJARA 2113MR276 | {3C13801D-CC64-4F61-AF69-C39F394BB25E}
COTATI 110257108 | {E06C85FF-5B48-4064-AE0D-D34C585D0676}
FORT BRAGG A 1102416218 | {39C594BB-A2EE-491E-843C-6A3739AD958F}
GARBERVILLE 1101574630 | {7F9C85EF-487B-454C-8489-CDBA87D32E67}
SILVERADO 21022495 | {E417384C-CD10-4D00-B136-62F02EAF1C4A}
DESCHUTES 1104715242 | {F164BF8B-3484-47A3-8EEF-5FFD77D4911A}
SANTA YNEZ 1104Y66 | {B46D742B-3DDA-4738-A51C-19ABAD3AA23C}
BASALT 1104CB | {1D69793B-6513-4BDE-BB21-BAE25C357436}
CHESTER 1102CB | {655104DB-DE28-4723-9C66-99BF732C7F54}
VIEJO 22029089 | {BA7590D4-FA7A-4E66-A4E2-9385E2F5FD08}
APPLE HILL 2102836878 | {5DC9E720-795B-432E-BA68-667FD0BD630A}
BELL 11072400 | {DB8C8898-F3FD-4C6D-9D99-FE8F56C2485D}
PENRYN 1103604 | {E0C71142-0733-49C8-8AA5-49865B61A687}
CLARK ROAD 1102CB | {E6C812B7-52C7-47F0-B595-32AF66AB7A9D}
GEYSERVILLE 1101482 | {FC698F49-08CB-4375-B278-3C062280B4C5}
OAKLAND J 1102CR102 | {0FCC4668-DE07-42BB-BC4D-4288336A5D5A}
PAUL SWEET 210980246 | {8C8A8C09-E52E-42BB-8F77-24A43F9E99B3}
BAY MEADOWS 210248770 | {89242FEE-8748-42BC-8EA8-CDD97EA44EAD}
RIO DELL 1102772210 | {F40CB029-270F-46C5-9305-F30A68FC7241}
COARSEGOLD 210410030 | {A8CB9256-CE86-4125-B378-C2EE50D5BB11}
ALHAMBRA 110213333 | {CC913DB3-6A51-493D-BE11-D5EAF399B0A8}
CLARKSVILLE 21066832 | {C549AB23-FF4D-4476-A6BB-298E3FC3CA01}
CHALLENGE 11021902 | {1446E22C-05D8-4F82-9637-10F46D2B1E35}
BELMONT 11038956 | {1467F520-572F-46EC-93E0-707DAECC5FB0}
WHEELER RIDGE 11014164 | {E4E8B6C8-61FB-4D05-90A7-1AEC2AB09918}
ARCATA 1121716954 | {6E3AE2B4-F135-43F0-832F-E39BC5035CBC}
EL CERRITO G 1110BR240 | {D5C37EEA-D463-430D-8618-04212D08A58F}
SOBRANTE 110142914 | {D5713EAC-4361-483E-B20A-724A36C5F247}
PLACER 110451732 | {F20DF12E-C49B-40A8-AAFB-7DBBC88F8ED9}
NARROWS 210276952 | {070E580D-ED42-47CA-BF5A-6C96D8E39FC5}
CLEAR LAKE 1101832686 | {4352C464-74E0-4EAA-9A4D-DC58892F06BA}
BRENTWOOD 2110CB | {656225FC-E476-48B0-B77B-181188E8D8F8}
CLOVERDALE 110294476 | {80FED0BE-D166-42DD-AD9D-F9569A62BF53}
TIDEWATER 210614072 | {A74482B6-4F98-4489-A417-0B9C2832ACBF}
ALTO 1123CB | {C4F18DDE-7DF7-43C4-9D20-1B47C5ED6CA4}
DEL MONTE 2102878376 | {6CCE4F90-013B-444F-9BDA-6C6A4EE75374}
MILPITAS 1109XR374 | {0C3DEB50-B6B5-4438-9654-82B0930BBF12}
OAKHURST 110310190 | {15EFA531-A43D-4849-828D-DC9485A13753}
PIT NO 5 1101884224 | {3B84F04D-9352-4AA9-91C7-0899748ED548}
MORRO BAY 1102V84 | {C6CF638E-9C90-41DD-9ABD-A01972E6D396}
DEL MONTE 210138582 | {2F70F4D8-3BA3-4012-9A01-B8B771F3D276}
MIDDLETOWN 1101352182 | {AEB7C7BA-C773-4591-86C0-9A5CE1531025}
REDBUD 1102432 | {D29B0306-223B-4BFF-9389-253396BA7A0F}
NEWBURG 1133CB | {DD9AEFE6-8781-45D2-A01C-A8D7D2CCC603}
MORRO BAY 1101V64 | {02238211-B668-4889-9A10-D952B009B264}
BOLINAS 11011064 | {196072E3-9BAD-4649-BDA0-FE3AF88F88C8}
HOOPA 110193038 | {1C7B29C1-9766-4E63-AFC2-ED97D59270C9}
APPLE HILL 210239544 | {67403348-AD5A-4D81-B973-25AED6358693}
SAN LUIS OBISPO 1105796050 | {81973749-CAB3-49C6-B105-0C3D389524EF}
SHEPHERD 2111537008 | {E96DE61C-94D8-44EC-B1DA-8923104268C8}
HICKS 2103CB | {F9C1F2D6-7B0F-4CCE-9FBD-177508C9BBDA}
MORGAN HILL 2105XR268 | {4F22013A-C8F8-4C93-9CF0-829946636F4D}
CUYAMA 11031635 | {7338276C-0737-41F2-B421-53D877AA647D}
PETALUMA C 1108208 | {D6A4485E-AC24-4E5F-8B68-E6B52EAE7CCB}
FREMONT 1104MR339 | {02184DCE-4986-4759-8E54-71AE9F6D44F7}
BELL 1108351852 | {50A19D76-23E4-4194-A546-FA4EB9B67EC9}
POSO MOUNTAIN 210448268 | {59412086-F782-4166-B6FC-4A718057E9E9}
BIG RIVER 11011286 | {DFBBBB18-D02D-419D-977F-28C5BC8837E8}
SAN CARLOS 0406CB | {E4554E11-1488-4093-BA83-414508537E1C}
TAMARACK 1101CB | {1755A18B-6E24-4507-ACE5-9CCC118C7159}
FULTON 1102885254 | {2F7CFFF4-26D8-43F1-AB7C-C43D0BC5D438}
OLEMA 1101320 | {53821A46-8FEE-4585-B4C8-79B31D43CD6A}
MENLO 110276134 | {6CA76C53-8C3A-4667-92BB-084EB68DB35C}
TASSAJARA 210812712 | {99848A3D-3AE5-4D01-A9C7-8BD9676BEFEE}
WEST POINT 110136674 | {B0AD76E8-C8B6-4D91-BE40-831E99BE5659}
FRENCH GULCH 11012905 | {CEDB41D0-D0A4-4C87-B076-5057F893A246}
HIGGINS 11039753 | {5963F19C-E1BE-46EC-9E26-B117A913E935}
OLEMA 1101758594 | {EB266F6D-17EC-430D-AF10-380B2A2664C8}
CAMP EVERS 2106CB | {F50933AC-5B82-417B-BA6F-799563320ECE}
SAN LUIS OBISPO 1103V82 | {FCC7352B-1F1B-4520-9419-DD9582012EFB}
AUBERRY 1101R2579 | {1328D5B4-6BC6-4A19-8B7D-C1E2266894DF}
OCEANO 1106V26 | {2FEE1CE0-BC95-467C-8CDD-CAD4D3CD2579}
MADISON 21011943 | {DCC4F33D-94BC-4C20-B81E-44479B092EB6}
MIDDLETOWN 1102514 | {51EF8730-4C17-4517-B094-A50393B56842}
GEYSERVILLE 1101122 | {69EA27A3-0D2B-4A2D-A229-63A3090F6AF6}
VOLTA 110180454 | {8854FD88-45EB-44A4-AE38-EE1BF37E09D7}
RIDGE 0401CB | {A69D2BA4-3D74-416C-A5CD-5CA28C67DFB5}
BROWNS VALLEY 110197188 | {D76845FE-B268-426A-A73C-E770602E73F9}
LUCERNE 1103CB | {F830099C-EEA2-4CF4-B68F-D2F012925468}
MOLINO 1101338 | {4502A0E5-A181-4FD0-A72F-EAB91B5F9EA1}
VACAVILLE 1112CB | {5828CFD8-0F34-469A-AB4B-4395B45CE3D2}
BOGARD 1101CB | {5CFCF023-4A49-452A-9B13-3F245544233B}
MAXWELL 11023306 | {F1C1856B-ECB8-4CF9-A778-CDB8457E4724}
FRUITLAND 1142899734 | {84FB064E-BD98-4DA8-AF4F-2B45B0138D7B}
CALAVERAS CEMENT 1101544800 | {B4FC0E10-1DBC-4446-A2DE-836BB2DB31D0}
RISING RIVER 11011532 | {D3F18D5E-2734-47E6-AA3E-0F1256C05891}
BELMONT 11103975 | {650AE2A0-8481-4167-A199-68E796B3390A}
DIAMOND SPRINGS 1106176130 | {6647B708-EB30-40C8-9FB8-1AD5D9953BA6}
PUEBLO 210375612 | {0A48EF8D-B34A-44FD-9901-4812541B4E91}
MARTELL 110198374 | {277F84D3-A270-449A-A58E-FDC1A84261F4}
PLACER 1101208930 | {53E235AC-648B-4E69-8BA8-94C5D0F7B09F}
STELLING 11109265 | {D66F2372-56F2-4D8A-9310-F85A981AACD1}
FORT BRAGG A 110465894 | {DDA08885-FEC3-49A8-9C1B-A5CDAFE21444}
MORGAN HILL 2105XR494 | {2DBAAA9C-8985-4692-9A1B-CC370D239D9B}
JESSUP 110296554 | {14C3CF81-5A6E-4ADC-BDB6-EF5B849D6F19}
WHEELER RIDGE 110170228 | {E4E8B6C8-61FB-4D05-90A7-1AEC2AB09918}
SANTA MARIA 1108M18 | {516D977A-EB39-4268-8E04-4AF0198F88DB}
MOLINO 1101600112 | {561785C2-9342-42A6-8DBE-3ACD64E05D9A}
ROB ROY 210512582 | {9F9A8C20-EA90-4789-ADB1-26DC34BBE385}
BIG RIVER 1101954 | {A36BE560-E1CB-4559-8E7E-01132EBA1D0A}
TIVY VALLEY 1107599142 | {B0EAA688-0840-4FBA-BE74-3B15BA6BD7F3}
AVENAL 21019070 | {BA67822C-2303-4723-983B-9142A9A0088D}
NEWBURG 1132665674 | {F0A8EA1C-5D25-4DA2-A0EA-6346825293B2}
REDBUD 1101CB | {3ED5FB3A-A2CD-4F13-ABBF-430305FFB318}
WYANDOTTE 11061512 | {29C2B584-F455-4FA3-B4A4-3F4E989317C3}
OLEMA 11011252 | {46D411EC-386C-4DB1-B30F-D2D2AC060A49}
OROSI 11037901F | {029EB0AA-88F8-4BF4-93B1-3A5396293CB7}
PARADISE 1104CB | {60D04F67-B0A9-4BD6-8DCF-759CBE65FF11}
PASO ROBLES 1108P28 | {674E461B-DF8C-43E8-8C03-AA3C3BF037C3}
OAKLAND J 1102CR250 | {FD5FE64E-C40E-49F6-A1B2-6062B4E7CFF6}
WOODCHUCK 2101R1790 | {BDADDF4D-CB81-46CE-9E7F-46F136FB9606}
CAMP EVERS 21065020 | {D340DCCD-95D6-4317-9003-DD8DEDE9B1C0}
CASTRO VALLEY 1108MR205 | {E6DE5FA6-EF94-448F-BB17-EE24C05283D8}
BRIDGEVILLE 110137484 | {24C71D6A-46DB-4BB7-8807-9800CAD347CE}
PAUL SWEET 210510918 | {8D1DF0FB-6A31-4B98-9D74-0EE015EF8A6D}
PIT NO 5 11011658 | {B21A40B5-551B-4708-A4A5-34576C3781E9}
COTTONWOOD 110168190 | {B9D0806A-E952-4DB8-821A-8A74AB16F016}
PACIFICA 110410195 | {C0B7FBD5-C48E-49C2-A7B2-8E06D90A6C57}
SANTA NELLA 110111370 | {D9B42920-8795-457D-8506-B9A1003BB3E6}
LOCKEFORD 2102206884 | {2D298F6A-BEA8-4B07-AC26-301AFF0706CC}
ROSSMOOR 110798488 | {748E6AB1-94A7-498F-8F09-FF430BCD1517}
SAN MIGUEL 1104R88 | {C7BB1503-DD28-48B3-9C96-3F6DD2B88AD1}
HICKS 2111255740 | {EB7674B7-CCD0-4EFE-8467-AE9A3DE4BA98}
GUSTINE 11029100 | {FC926262-8B0E-4F06-BF55-D74DA7FE90D8}
VINEYARD 2107MR801 | {E0DA3FA9-134E-46BA-BA63-A138252A7798}
SAN RAMON 2107CB | {772B9C3A-4112-4E6C-8E48-73C0CBC8A027}
MIDDLETOWN 1102CB | {7E69B413-A223-4CCD-AF98-CC3C74EA7FDA}
BANGOR 1101614048 | {808B9A32-C42D-445B-9979-179B0B7A37BE}
UKIAH 1114844294 | {E31B357F-7D66-4467-A543-DD5E914AB51D}
CLOVERDALE 1102307342 | {A0D136BC-BED5-4E61-825E-2EC84D15BD33}
OAKHURST 11015490 | {19617CFD-32A5-4AA4-9E54-43F64E95D667}
BELLEVUE 2103552 | {22D41C36-E42C-48E6-9A63-86DF5176F2CA}
LOS OSITOS 21033010 | {528CF887-3009-4BDA-941C-23A6FE9B29B6}
POINT MORETTI 110136516 | {6763B940-A4FC-4294-830C-EA07CE726C5F}
PASO ROBLES 110764703 | {BF9A1CFA-5044-466A-9DCB-672D048DD99A}
DIAMOND SPRINGS 1104705100 | {B2C0084B-109E-44CB-BAED-2939A6DED126}
STAFFORD 110242542 | {C9CC8490-6E43-45D4-87C2-A85ACD7797AC}
PINE GROVE 11011021 | {5E0ECFE9-34C5-4F2B-8405-6E29B71598DF}
GRAYS FLAT 0401CB | {0DD81C15-0750-470B-8405-5D786A5E8465}
SOLEDAD 2101955138 | {9A077527-882A-4F06-B221-C25746AA1F96}
PETALUMA C 1108636 | {BE0D8CE5-BE7F-4D94-B792-C4D840A2819E}
SNEATH LANE 1101CB | {E63B66A6-F711-492C-AE55-754D3FBB9FA4}
TIVY VALLEY 1106R1450 | {90E00265-C0CF-4482-89EA-4364E2D4853A}
TIGER CREEK 0201CB | {42CE80CD-1575-4D75-9DA9-13CC191BD6F8}
FULTON 1107286 | {72AE5EDE-AC15-4265-AF32-67B0F370C217}
DUNBAR 1101725292 | {86609C6B-F85A-40FF-9C70-59FE9D214477}
SISQUOC 1102M52 | {B8793525-C43B-4B72-9E84-4F6812828DC2}
MARTELL 1101803328 | {2C34AC51-01A3-44C9-B45A-F5786A7BA8F0}
FRENCH GULCH 11011464 | {CEDB41D0-D0A4-4C87-B076-5057F893A246}
ATASCADERO 1102A26 | {DA2C7B5E-6C7B-401F-B35E-CA8BB5D3B738}
STONE CORRAL 1110189488 | {DB3D7864-7F45-444C-BD96-835D23E12B3A}
OLETA 11022642 | {2ADCBD92-66F4-407E-9ADA-EA48C32C4604}
ALTO 1125510 | {3D1372A7-8F04-4F4C-824F-7EEDAB15603F}
EL CERRITO G 1105BR160 | {473DFDCA-EA19-476B-B0A4-B163B0B91B7F}
TEMPLETON 2108A40 | {FFDFCD62-3D83-4DB1-8291-20A4384347C8}
ZACA 1102Y02 | {615A0700-A424-4825-ACAC-C9AB34833626}
RESERVATION ROAD 11023032 | {966AAD61-7205-4A6B-9491-7F1C72E1ED94}
COLUMBIA HILL 11012212 | {BA4E3F60-A7E4-477D-9CC6-E4ABC3E72986}
HALF MOON BAY 11038898 | {F439C87D-AAE9-43A5-B8D6-BA1AB4C5C362}
MESA 1103Q18 | {C0ABDB73-42C4-4D60-9BB1-4077EF0BE355}
EL CAPITAN 110311670 | {BCF947C4-6F66-4253-A6FE-897D9621AEC6}
MORGAN HILL 2111XR398 | {C3FC7DAB-5E2B-4C00-BE86-ED9552703F1E}
JAMESON 1102CB | {CCF6C8D4-166E-445A-ACEB-16D79D2A6A88}
DUNBAR 1102246 | {ECF0597E-C523-4664-9DE2-2ED0EC5C00F2}
MIWUK 1702576504 | {0C4CD1BE-E231-46BA-AA07-10AAA7A9A5DB}
HARRIS 11082062 | {0E0C2894-9F4C-4F14-AF8A-F5A44822C594}
GONZALES 1101522356 | {B8E5DB63-2FB3-475E-A16D-C9AC460D90A7}
SALT SPRINGS 21023142 | {31EFB8EC-9037-4E2A-A03A-16D15C4387DC}
HAMILTON BRANCH 11012046 | {385C1178-1E10-4C92-A2B8-B11436713899}
EAST QUINCY 1101951424 | {83723391-EB93-4D6A-A5B4-68EA4AD17B8A}
SAN CARLOS 11049010 | {98FA686F-C0FD-4E53-94B4-4278583D2FA4}
HALF MOON BAY 11018902 | {C41F4E5E-7BB3-4EF6-9D85-B639632114A4}
MILLBRAE 1104217 | {78D6C5D5-9F2A-45C6-A0D6-6C9E91038F45}
SILVERADO 210248380 | {65C50E41-4A19-4EF0-8E02-55AD7C68E0C7}
COTTONWOOD 11021578 | {0E682A09-C0D8-404A-8B27-2B967048024C}
PASO ROBLES 1103P08 | {1FA86F64-861A-4311-896C-8F2E15FE3A38}
LAKEWOOD 1104W528R | {6E990274-D878-48AF-B3D8-9102E49E31C0}
EUREKA E 110435934 | {B435E505-091B-4464-AF4F-65421296FB23}
CALISTOGA 1101134232 | {07D5D1F0-E088-492A-95F0-C51ED4C7A4B4}
OCEANO 1104Q10 | {FB18C056-8E7F-47BF-BAE4-63685AFB3AD7}
OLEMA 110137074 | {117C09FD-AE60-4D22-843F-8781BD8BA585}
VIEJO 22049440 | {35D3CEF8-0523-4ECA-BC11-26CD68907349}
ORINDA 0402402/2 LR | {5BBA7E94-488D-470E-9522-5BF71768AFC8}
TIDEWATER 2106703654 | {2DE5693C-879D-4FCD-88B6-818902BD649A}
CLEAR LAKE 1102223792 | {EE43D8DE-EC78-4D51-AA66-FA42E0AD335E}
AUBURN 1102251946 | {F47804CC-754A-4FCA-B217-8CAF682A164E}
OAKLAND K 110217430 | {02500171-BA04-46CD-BDC9-060AD340AEF8}
OROVILLE 1102CB | {581D49A7-9F4F-4C9A-B76D-C943A94B162C}
DUNBAR 1103CB | {587017B7-CF95-40B8-A31E-326EDAB4E012}
SAN MIGUEL 1104R58 | {5D373241-D81F-4822-B649-3A4A39407074}
COTTONWOOD 1102544790 | {7F934250-B67B-44F2-9547-08902728DC9E}
SNEATH LANE 110748338 | {83D7785E-7AE6-4CFF-B401-9FB72EBCD47F}
ROB ROY 21055090 | {97F0E264-6757-4E01-B858-9C73FC0BF875}
MONTE RIO 1112120 | {A3E8D9EB-1B5A-4CFD-AE2F-C1E7C6E04114}
STANISLAUS 17024905 | {7A6C2092-3A26-4926-BE3F-3A04290F7325}
WYANDOTTE 11091520 | {FC542AC7-29DE-47A0-A073-41001E21B2E1}
OAKHURST 1103CB | {0FC43676-7F71-4151-8B57-A856F18A7815}
FORT ORD 21069138 | {2DB40D5F-4BD1-40A5-9FBF-211C9D3CC0A4}
SAN RAFAEL 1109519234 | {BFF521B9-A860-4F51-B554-94546E79EB8D}
WEIMAR 11012058 | {7EF077DC-E313-42E9-8185-688E5BE27A63}
CLAYTON 221738248 | {2E89F027-67FF-4082-9169-E158A83D0166}
PENNGROVE 11013476 | {9D558E42-88D5-42F3-808F-02B4EF74376D}
HOLLISTER 21054060 | {F5425C52-6CB2-4CD9-81A3-7FCEE48AC283}
COTATI 1104232 | {0D1EAD50-F416-4D20-B817-3BDC9FDA64E8}
VIEJO 22029120 | {3A16450D-C56F-42B5-80F8-8369EAD6F0C2}
MARTELL 1101250060 | {8F8995FB-51DC-4122-872F-27F17EF06719}
CORNING 110253184 | {15DF5EF9-6694-4A35-B7F3-919A8A286CFC}
LOS MOLINOS 1102CB | {3C29BFDD-B708-4EA4-82F6-BE02F2280B00}
COTATI 1103310 | {40F0C968-F731-4A61-A453-D93A6C5B08AE}
EDENVALE 2113XR106 | {CBC2E590-65E4-4DD8-9118-7B6CB910201C}
REDBUD 11021212 | {5D4D8690-5B01-4EDA-9ADD-A0F82EE8F0D4}
ALTO 11251158 | {DC93F2BF-1FFD-4AAB-B042-E35ACAAAB3A8}
WEST POINT 110236676 | {1445490F-C0B5-460E-8F6D-3B7658CD2546}
BRENTWOOD 2105500796 | {B557525E-C955-4555-A43D-602C62B6D5B3}
FROGTOWN 1702592404 | {2DE456BF-71ED-4278-9F9A-6A3D0E617A94}
MC ARTHUR 11011492 | {4752BF93-70F8-42FC-8D3A-033549B0C98A}
ARBUCKLE 1104669720 | {4F1CDC69-EA0B-4135-93B4-1C48EA3748CD}
CLARKSVILLE 2105385236 | {760BF466-E4DF-4A5C-B2C4-51F0ABE15277}
FITCH MOUNTAIN 1111792628 | {89345583-C072-4A34-9FA1-B63C26C09270}
BERKELEY F 1103813976 | {8BB0C622-0BA1-48A6-BC5B-DC08A0DC776B}
LAURELES 11116617 | {03861487-35BB-45AB-853E-5E8CD2B590E5}
DIAMOND SPRINGS 110650324 | {DCB9D4A3-4396-4AF7-B5A4-4405D20B6E8E}
PLACERVILLE 1112566624 | {69C7055C-8321-466E-890B-DA1A435F5398}
OCEANO 1105V48 | {70C30D54-868D-4F87-BAB6-E123ACDD12E7}
CAMP EVERS 210612840 | {F761DD80-845B-4F29-ADA0-4CE9C4A1F615}
SILVERADO 2105167360 | {0F3794E1-7800-452D-B826-F4E0E0581557}
ANDERSON 1101337668 | {4FF91FEF-C966-4E36-B08B-C812EFC4BE16}
HOOPA 110182542 | {AF113D3A-C32B-4AE6-9683-F0B931A2BCC2}
REEDLEY 11047340 | {1B9CB438-3D64-400D-8827-441645AF1444}
BRUNSWICK 1105CB | {E1779AD2-4579-4092-9EC8-FEE4F5C13371}
HIGHWAY 1102815524 | {17274A38-F8A1-462F-93E6-49EE52FB630E}
KESWICK 11011590 | {F2F9B8C7-DF20-4B0C-A519-3E0E16F2B19B}
SO. CAL. EDISON #3 1101CB | {FEFF3CD8-2343-48D8-93C4-6004850FEF87}
HARTLEY 1101698 | {14B018BB-E4F3-4418-8464-262A2B2FE900}
HOLLISTER 2102406496 | {17B07670-0E53-4796-89E8-790E1D545BFE}
COTATI 1102462 | {2E0FB866-9F6A-4839-A968-F9A8CD3FA6CE}
CABRILLO 1104497036 | {27DCEC24-FA17-48AC-A20B-BD915C784084}
LUCERNE 11031280 | {A05AE75B-B8B1-4EF0-A327-427A302D4FDB}
CABRILLO 1104Y24 | {A2EAD6B1-6208-4216-A913-DC206F2BE25D}
PENRYN 1106CB | {C3E0B410-F242-443E-BF4E-9C519E692FDB}
CLARK ROAD 11022070 | {DBD4B653-AFBF-40EB-8724-1790AF913C8C}
ANNAPOLIS 1101202158 | {0B0F8D7C-2C4F-4CBA-AE85-A14338AA03E0}
SAN LEANDRO U 1109CR284 | {42064D42-EDBF-4ED5-8222-65863B241E1D}
DUNBAR 1102CB | {46D8BBC2-519D-4FA1-BC3E-5FF3581AAFDB}
ARCATA 1122CB | {4D343D95-65B7-4F09-8335-963B7DE7388B}
RED BLUFF 110176020 | {737A9C64-4C75-4B29-81A5-32595FB9B2D8}
DEL MONTE 210448004 | {C1DCB446-91BC-4976-8E19-E90A61136DD7}
LOW GAP 11014160 | {8F7144B3-988A-433A-A6F7-A1F0E4529E41}
SAN LEANDRO U 1109CR344 | {D888F259-DA4B-44A5-A254-AC7BF27B35F0}
WYANDOTTE 1107CB | {0E127264-C3E4-4550-BC79-8854D7BB9B29}
PACIFICA 110110067 | {2C30988A-F66E-4A90-B5B0-67ED6781F8F5}
COTATI 1105616 | {4B1C4FCD-287E-4417-8568-2D11E983B37F}
COARSEGOLD 2102CB | {5FCD3F70-B3EF-41B7-B59A-4AF393BD948D}
WEST POINT 1101L1969 | {10618A90-ED86-44CD-8B76-773E3BF2AE42}
COALINGA NO 2 110541882 | {90AEEBB8-CCE7-458F-AF2F-7D8FEF1C57D6}
GUSTINE 1102999258 | {09DAC264-33D4-48C8-811A-344E9E34B63F}
MONTE RIO 11135024 | {3F69DD3E-C46A-485A-8A4E-8252A760746F}
SYCAMORE CREEK 11112602 | {5CDF71A4-CDCE-4614-B4AE-BACB8DC21516}
SILVERADO 2104371746 | {49BFB9F2-5C6B-4B7C-8CFC-569E7EA29701}
SAUSALITO 1101CB | {89972505-5E8F-4A2D-AA5C-D59B16608028}
SEACLIFF 040112946 | {9DDD43C5-588F-4D1E-AFA3-8A122C419F83}
JARVIS 1108548648 | {4D5666F5-BD84-4CAA-B8A5-49AFE5BCCE43}
HATTON 110137088 | {C7A22305-CC6A-494A-88D7-7F9AE8676071}
MARIPOSA 2102527766 | {E89F466E-8BA2-4F18-BDD7-EDCC9695F74F}
LAYTONVILLE 1102572 | {33062E2A-6001-4611-8363-46C244F6285A}
WHEELER RIDGE 1101234580 | {6E248E69-5334-44F4-BB88-9697823ED075}
RACETRACK 170455798 | {7E0EED7A-2775-40CE-B357-57739361FC2E}
SAN MIGUEL 1107CB | {9AFFCF48-B4BB-4816-B96D-D0BF56E32579}
ARCATA 112293912 | {B31BB8D7-E9FC-4E78-862F-0335ED33A574}
SILVERADO 2103403102 | {CFFB1C96-B030-4780-B25A-3AB8C753331F}
HALSEY 11022514 | {D24FE68D-C3B0-43F0-8A16-C357F1C466D0}
OAKHURST 1103719490 | {0997B2C6-B46C-4942-8B54-4BA0035375E3}
OAKLAND J 11067867 | {4808F0D1-7684-45A4-AA78-2B2D6EF06890}
KONOCTI 11024300 | {74BC573A-BB75-4EEC-A68D-D9673A89AFF2}
COARSEGOLD 2104828842 | {8C9C1F4D-9C24-4A9A-947D-D1CEA924DCBB}
LOS OSITOS 21037082 | {E273F09C-00C1-48A4-A71E-352A62A15E75}
STOREY 11095680 | {4558735C-9506-4B45-82B0-A917961DD704}
SISQUOC 1104675420 | {4D6D6BF4-E19B-4629-9318-504AFE626164}
MENLO 1102628458 | {8DAF1791-FC97-4AAB-A29C-384C99616E7D}
CASTRO VALLEY 1110MR525 | {A785A044-2D61-4F74-B02F-A90F8B32D4AB}
FORT SEWARD 11211690 | {E448EB4C-7ECC-4C43-A720-97024B873C96}
POINT MORETTI 110139126 | {1E00CF74-EEE2-4457-A6AF-F5C49F5CE48D}
PASO ROBLES 1103N54 | {3D8A845E-016A-4676-A95E-AFB35541512A}
CALAVERAS CEMENT 110111238 | {16B948B9-B372-45A4-B29D-56B8F2A70B74}
TECUYA 1101CB | {65DD5366-DF6E-489A-A139-9549CF95748E}
RED BLUFF 11041630 | {89D48A42-926D-430B-837E-EDF8AFB821B9}
BEN LOMOND 04015144 | {8CE26437-AB3D-4CA1-B3DD-136FBC93120B}
SARATOGA 1106CB | {D3EE6D7F-47FA-4D89-A2C1-869E892A4C05}
SANTA MARIA 1110M76 | {E772CBEC-2F5A-43A3-91C3-8EE495E372D1}
SAND CREEK 1103CB | {E54C0E82-949E-4C90-9607-A30CD2E7D9C4}
SAN RAFAEL 1108516 | {F2E5D603-195F-45A5-9636-597C9B053516}
JOLON 11027002 | {0490EF9F-4327-4CEC-AB8A-ADCAD043B99F}
BELMONT 111039182 | {2B049CE5-6DAC-4065-B555-915EF340A6E9}
BERKELEY F 1105CB | {34B1FBA6-E642-41FD-8BD2-ADAC657BB906}
WILLITS 11032506 | {3B860DB0-A747-4B2B-900E-A58BF536B758}
PLACERVILLE 1112778710 | {69C7055C-8321-466E-890B-DA1A435F5398}
ALTO 1124432 | {5A7E1969-E475-4A2E-A5C6-85EFB5802FE4}
LAS GALLINAS A 1106228906 | {65BDBB0B-2F19-42BF-A514-6268B91E4F4B}
LAS GALLINAS A 110599904 | {C483C6B2-63CC-448F-80AD-EB7838DB89B8}
VOLTA 11011640 | {DF67F6ED-C0C1-4634-A8E7-5650468AFAD4}
HORSESHOE 110150140 | {223CF293-20C5-4942-B371-E6A6292ECAF4}
MARTELL 1101131918 | {2C34AC51-01A3-44C9-B45A-F5786A7BA8F0}
JOLON 1102CB | {370C8631-3D98-4FD6-A4A1-B8DD1604CB6A}
LAKEVILLE 1102272 | {5BFD6D0E-9A91-4B87-9163-8304DBF587CD}
PUEBLO 1102671 | {1AE19971-F682-43DD-B35E-DF767DF7D39D}
LINCOLN 1101CB | {BC430285-5DBF-4545-8AE8-96AF6071F68F}
KERN OIL 11063301 | {BC48BC1B-FF6D-435C-9294-117A7961E04E}
GARBERVILLE 110256048 | {BF5AD074-5FDE-42FF-9EE4-EC1E7EF14392}
RIO DELL 110275970 | {C155999E-0638-4738-B652-2E7910103A63}
CORNING 110290036 | {3333A9F4-A222-4545-831F-9DC4F4A4E477}
CURTIS 170268380 | {45D5D58B-80DE-4D2E-89C9-FED8B8DCC26F}
OAKLAND X 1105CR242 | {4B545AE9-A885-48BD-BBDD-C323FFCD6AA5}
HALF MOON BAY 1103655644 | {8768B1B0-4DEA-4BD5-97FA-A78DED5BFD8E}
EL CERRITO G 1110BR236 | {DBB65B1C-D816-44BD-B6A7-C95BB0A659FA}
PANORAMA 1101CB | {39175FAF-A6C7-4043-8D47-1A655E22AF59}
CORRAL 1101D1495 | {B16B71D1-22D0-45E3-8592-F21047B1C034}
CORNING 110187304 | {A9C774C3-1428-4B46-A99D-50AD5766C649}
WOODSIDE 11042337 | {4CEFDA18-FC78-4DED-AF3C-6DA953E1658C}
FORT ORD 210531972 | {29DAE9CE-CAE3-4935-AB0F-06DB01859441}
ECHO SUMMIT 1101481660 | {3CE51A5B-7612-4EAB-BF43-95EB9AC2B5AB}
HARTLEY 110186876 | {0628807D-B297-4343-8118-F7F853EA05DA}
WYANDOTTE 1107219854 | {0E127264-C3E4-4550-BC79-8854D7BB9B29}
SILVERADO 2104726 | {8A2A1266-ADC7-4421-959B-BF4457BE3602}
OILFIELDS 1103N62 | {47FD814D-36E3-4524-B471-B70B44EFD5A6}
SAN CARLOS 110436864 | {9E2BE648-1876-419E-9EA6-9561CF55CBC8}
HIGHLANDS 1102623120 | {B5C2A169-B3BF-48D4-8260-06DB123C1FCF}
CASTRO VALLEY 111010315 | {C6807FEA-40B3-41BE-80F1-095A0F67FBA5}
KESWICK 11011588 | {E337A679-257A-4862-A121-8FE4E1C11ADC}
FITCH MOUNTAIN 111324918 | {30AC1F79-37C1-4981-9C64-81FC3670878D}
MORAGA 1101108540 | {372C45CD-D068-4E6E-9903-0ED38EA6950C}
HUMBOLDT BAY 11027600 | {712389D7-97A8-43EF-99E1-6A4B64E5B114}
SAN RAFAEL 11061230 | {3CC0B2ED-4CCD-4757-94A4-43056A68F6C1}
BRIDGEVILLE 1102353222 | {DC0A7D01-2EED-443F-A8C6-2C05CEB2611C}
GEYSERVILLE 1101354 | {377EDE62-95BF-4247-B5CE-2FDAD489198A}
DUNBAR 1103839384 | {587017B7-CF95-40B8-A31E-326EDAB4E012}
MONTICELLO 1101130412 | {50BA7E67-5EAD-4941-88EC-76A715C41286}
SANTA NELLA 1104611232 | {9B89E5D4-E3CF-421E-9973-405ECEC9F5B3}
WEIMAR 11022038 | {BD845FF4-9DE1-4881-9265-8047FD3823B1}
MIWUK 170110600 | {38AAAE1F-7053-4022-8941-265790AA8F13}
LLAGAS 2101XR264 | {6D5B6410-E4BE-4661-9810-568D00627E89}
ALTO 11256405 | {DA893851-A239-41E8-8E7B-70F066561313}
RINCON 1103649194 | {2A534FE3-EF17-402C-9700-8C33AB455C66}
RESERVATION ROAD 11023030 | {B5391BD5-06CA-49EB-98DD-175A1FD20C36}
SOLEDAD 210435306 | {B67EAAD0-18CE-4C8C-8264-33FF5297FE06}
GABILAN 1101566352 | {0B568E58-6FDD-401E-8368-A329B6DA6B93}
VACAVILLE 1108CB | {59386278-9020-4BB7-BD46-9280C84FE5FF}
FORT BRAGG A 11044690 | {9AB01B94-B2A5-4A8A-9109-9F42C093DB3E}
GEYSERVILLE 1102504260 | {95D38DE9-E8FF-48E8-A441-5433C36DE660}
RACETRACK 1703CB | {155070BB-C96B-485B-99BD-6B770FC28FA3}
SILVERADO 2105764650 | {A2AE86BF-29D9-46AB-AC07-62E08E2FA633}
ROSSMOOR 1106L541R | {F81A28E8-7235-47FA-8A4D-F6D87B334C4A}
PACIFICA 11026783 | {19E4E8D4-9C4C-4C6B-8FB5-CC59DB118DCE}
FAIRVIEW 2207P148 | {61CE2DCB-0D53-494B-8C34-3F4D665DD273}
SAND CREEK 1103818064 | {904E4C44-1C98-4593-BD77-E458AD2081ED}
BRENTWOOD 2105B534R | {9C413BEB-102E-4BE4-83F6-909D0B4AB75B}
MILLBRAE 110810045 | {D144CF0B-F99D-4FA8-AE9A-F2C7682917BD}
RESERVATION ROAD 1101383718 | {1ABACE31-DB52-4FF0-A8F2-ED3023CBC398}
NORTH DUBLIN 2101CB | {298F8E6C-8C4E-4458-91EA-603E3295125F}
MONTE RIO 1113539938 | {3188B2E2-9541-4BE0-B86F-D0DD55D6F8F8}
DESCHUTES 11011380 | {53F1163A-2879-44DA-A8DC-132948A94C1B}
COVELO 1101694140 | {1E92B113-D351-4051-A3ED-221149B2FA2D}
COALINGA NO 2 1105134928 | {90AEEBB8-CCE7-458F-AF2F-7D8FEF1C57D6}
TEMBLOR 11043013 | {99CF017F-6ED0-462F-8AD1-7CD56A44DE93}
OCEANO 1104891294 | {D8E625A6-002E-4883-8F5B-8B2346405940}
SISQUOC 1103867486 | {E782E12A-3164-4752-BB70-4CC8003C0253}
RINCON 1102666 | {2FAB6430-43D4-439B-B7B8-4BB8DFD0CD27}
WYANDOTTE 11061046 | {830E8D18-621D-4CC3-9150-C991F796F6A1}
WILDWOOD 110198896 | {BF76B4C8-9530-427B-8649-806B9F48C554}
SARATOGA 11075696 | {01343684-2E22-4CD1-B45D-70EFDFE53735}
SAN LUIS OBISPO 1102348318 | {22E96A5A-3667-455E-A58A-C0A9770DDF94}
EAST QUINCY 11012452 | {59C7C56F-8F8D-453D-B2CA-2A56446D1413}
OCEANO 1103V22 | {77F4F191-CCC6-4075-AD1D-AD57A94CE7F5}
SAN BENITO 2104785888 | {A0912651-34EB-4686-B7CD-51CC5436D4BA}
JAMESON 110513392 | {41D42D82-88D5-42DA-AE8F-BA1A622569DC}
ANTLER 11011378 | {C885D848-026E-4C6E-A0E7-D886450B2EC9}
WOODCHUCK 2101R1115 | {58CC59BD-D32A-413F-871C-B048589E5421}
SAN BENITO 210192468 | {309BC145-CE1F-4552-9344-E193E2F32C60}
FOOTHILL 2101251688 | {2342B1BA-896A-4C52-9E39-F87AA4527061}
SWIFT 2110616022 | {F246BE39-0175-4986-BDB0-A6E32868FF88}
HIGHLANDS 1102556 | {36BC008E-75DD-4032-9E44-5DB50949C39A}
CASTRO VALLEY 1105MR201 | {7DC88504-8437-4262-8C77-15F7F25CD1D4}
HOOPA 110137202 | {8651217A-D767-4452-8107-AA225147083B}
MIRABEL 1102976908 | {EFEDE1C8-AA0B-47C4-96EE-71FB2C33E43D}
MEADOW LANE 2106C537R | {9FDBE41D-F5FA-4A91-8801-9FABAD55128D}
BASALT 11065030 | {31C38397-CC97-43EB-A38A-D18D8FE5AEB7}
KING CITY 1106202402 | {63D615E0-331C-41EF-8235-4A9E59F47BD7}
STANISLAUS 1701CB | {918E0B8F-0C42-4226-8DC0-E78B4BED7E6D}
CORTINA 110189686 | {E3B77E93-BB57-4588-891B-4456F675EF56}
RINCON 1102644432 | {AE3754A4-9F35-4D54-A758-926320A19A34}
PHILO 1102920 | {BC0A2CA4-638F-47ED-8CA5-834F5A792974}
ATASCADERO 1103492068 | {80C03548-09A3-4516-9CD7-A85242729AF9}
TEMPLETON 2112238418 | {F888EA83-160B-4C8A-947C-3FEEFB60DC7F}
OREGON TRAIL 11043310 | {DC4CEBC1-24E2-4325-802B-4D3154343BA7}
VACA DIXON 1105965390 | {DF536E94-F9F9-48D4-A625-EBCDF4893D0B}
ANTLER 11011612 | {EAAD5F12-9AE3-4341-A497-B18C1046E2B5}
SANTA YNEZ 1101CB | {08A02557-738F-41D7-89E3-E3805DA8D735}
CAMP EVERS 210611006 | {386E8549-812B-4BD5-AF30-4B8F8F3211D4}
GREEN VALLEY 210112824 | {4709726B-1243-485D-89BF-CB13962C950E}
OAKLAND J 1118CR332 | {218F069D-01B3-4618-A6DA-CD10F8EDDF5D}
VIEJO 22019698 | {7C0AA1F8-3024-4D35-BAB8-1475B467A597}
SILVERADO 2105990552 | {6A947491-FB60-4043-BF5D-F50FFBCF57D9}
KING CITY 1106666728 | {E021D476-E098-4CDE-B403-FDCFAAF2A5C3}
SAN LUIS OBISPO 1102597518 | {22E96A5A-3667-455E-A58A-C0A9770DDF94}
CLARKSVILLE 21036842 | {74B1A787-27C8-4482-8395-8E75B6FF6455}
AUBERRY 1101R2845 | {AF3C9CC3-4B67-4003-BBC4-2AADCCAC2E66}
NOTRE DAME 1103CB | {E3ECAAF0-99B5-4E63-AE53-35BCAA42BD12}
COVELO 1101562360 | {149E5268-4926-4B7A-B9E2-928EA9B5F83B}
WOODSIDE 11049032 | {4CEFDA18-FC78-4DED-AF3C-6DA953E1658C}
OREGON TRAIL 11041574 | {6C99A7DB-F466-44F8-AE24-87D735D842AA}
MESA 1103M90 | {6E34D557-FB41-44E6-B10D-DE75166431A4}
SAN RAFAEL 11071276 | {78640A7E-4385-4C01-A0A7-78496A91C391}
TASSAJARA 2113MR280 | {B9D0F1F0-F20F-489B-8E21-22409D603A4D}
PAUL SWEET 2103458558 | {BA3D6A76-5335-48A7-9116-A38FBA76779B}
PAUL SWEET 210349370 | {751E8B54-6492-47D2-8237-81A7BF27A640}
VIEJO 220298146 | {BEBF2F35-AA76-45BC-AFD8-E27852839913}
DEVILS DEN 11029340 | {85D70EAB-58A6-4861-89D2-07CC374A0ABB}
ELK CREEK 11012032 | {93B1D857-8A90-4B8A-BADD-0500DBB7E745}
WILLITS 1103966 | {BD0977E2-D82F-4AAC-B014-EDCBC19E0BA7}
FREMONT 11041516 | {CA0B1D0C-E4E8-4109-942A-39C0D83AA3E4}
PANORAMA 11021342 | {6303BED6-9051-4E72-A1E9-A3825361F885}
SWIFT 2109XR386 | {63AAF8AC-A447-481C-8FD7-216A552C90BD}
FITCH MOUNTAIN 111349826 | {9C1AE994-AAFB-42C4-B159-C85E938EE24E}
BIG MEADOWS 21012248 | {1667C171-4E6E-402D-B45F-3BA2B8FB113A}
WILLOW CREEK 110347966 | {2ADAB335-F68D-4E0E-93A5-403C7C54DA76}
HARTLEY 1101471 | {7E2F1938-FEBF-4ABD-86B8-56A7EC0C222F}
LOS GATOS 1106LB44 | {5D70BF4D-C1AE-452C-84AB-8E4767458B84}
BIG BASIN 1101391980 | {6AB8FDF6-DF60-4669-94F5-76C04F7F5767}
GIRVAN 11019732 | {AC347828-D402-4D52-85C5-6B49A3874218}
SAN RAFAEL 11051278 | {DF15C3A9-3287-472A-8D42-2F8516FD478B}
HOOPA 1101561116 | {340CBFFC-8113-455B-B1D8-1918397994A0}
CLEAR LAKE 110237580 | {2BE21FFC-75C5-4000-AF51-9092A99D4F5A}
CALISTOGA 1102141073 | {418B82F8-6C32-40A7-BAFC-4E4E4E20312E}
ZACA 1102Y48 | {6170E12A-002A-40B3-A4BB-42077F0D87F0}
EDENVALE 210589634 | {3428AB16-83A3-41CA-A97D-9F45E561A9E9}
LAMONT 11021644 | {3E9A4648-30CB-4190-9869-1F4B7575C98E}
WEST POINT 11021341 | {7DA2EEB5-1A19-437C-8020-DD813277F9CC}
OLETA 11021228 | {944D67B9-350E-45E5-9370-1645B5E16FDD}
HOLLISTER 210683518 | {B3B33B44-B27E-4997-ADCB-104657A7A68D}
GUALALA 111223444 | {CAD50E3B-E1AA-4BD0-B856-9F05498FC7E2}
LAKEWOOD 222466408 | {E8CA3C31-B411-4BE0-B116-25507E333F7F}
SILVERADO 2102437194 | {7001DE25-A96B-4176-B38D-AB056F29A6CA}
FRUITLAND 11418860 | {901979A9-33A5-4FBB-9019-2CBDDF98F849}
OCEANO 1105V16 | {70C30D54-868D-4F87-BAB6-E123ACDD12E7}
RESERVATION ROAD 1102CB | {FE25DCBF-8FD2-4D0B-8589-850A3EE5ED4C}
HALSEY 110239104 | {033C2E2D-A850-40FA-9417-37D899E25ED1}
GREENBRAE 1104107508 | {3BE2CA95-ED55-4C1C-B1D4-36EDBF365BB4}
DOBBINS 1101CB | {3EEFA179-0D60-4808-A6C9-A2D8F6C0C66D}
WOODACRE 1102CB | {61FE98E8-80EF-4BDB-989C-5A04CDB81F15}
CLEAR LAKE 110192870 | {91E6CF65-65E6-49D9-99AE-7F739C671773}
TEMBLOR 110437694 | {29FDF678-E116-4F18-93AB-072742A94198}
EDES 1112484536 | {63D64072-C2FD-480F-8116-E56FEE7BD425}
JESSUP 110338864 | {05238085-585C-432C-A137-934EA80FC572}
PLACERVILLE 111019582 | {1EC71CEE-6F35-4B51-874D-1E06DFFEACB0}
LAURELES 111268454 | {2A037456-E4D6-4133-B41E-0D0ADCC9AA87}
POSO MOUNTAIN 2101CB | {53C5BA88-884F-48FE-B87C-D7D9589897A5}
APPLE HILL 210277546 | {71852C93-FB23-454D-AA22-159ABBF0F364}
PEORIA 170587222 | {08C43BB5-02C4-4FB7-9500-39371503D9F3}
CARRIZO PLAINS 1101711854 | {412EB69B-2273-4C1E-A820-027827AE03FC}
OLETA 1101994386 | {C597D1DF-05AF-4117-9139-6F79BFFC0A15}
BEAR VALLEY 210110019 | {01E04AB3-4BC7-461C-86D6-3A3D5CD166F9}
TYLER 110585132 | {C22EF53B-7E85-45CF-AC1D-13B919BBB848}
PINE GROVE 110235576 | {C8B6F5A4-B7EB-4267-93EF-866DFF4F4584}
LOS GATOS 1106CB | {D03187F3-5053-4E30-B164-D057F0065569}
GARBERVILLE 11026084 | {0A529EA6-6476-4FE6-9A4C-9E2DBC5F560C}
LOGAN CREEK 21022226 | {0DB23F18-2307-44BE-917D-7278F1DC4733}
PACIFICA 1102CB | {3BE78651-BE87-4B28-8A48-F46DBB91FDDB}
SHINGLE SPRINGS 21107742 | {3C509C6A-BB81-43C3-A023-21038DF3E84A}
VOLTA 110297816 | {A7123BEC-B365-4766-B96E-6C5017CAB086}
FRANKLIN 1104P146 | {4B04C7BE-F037-4E43-AD43-455E3B1A9C74}
BIG MEADOWS 21012016 | {6B2D5F4D-4DFC-49DF-85DE-2AF9D30D36A6}
CASTRO VALLEY 1110MR341 | {A785A044-2D61-4F74-B02F-A90F8B32D4AB}
MOLINO 110279306 | {B81A8616-55B2-41F9-9829-B699E6A06290}
CLAY 1101CB | {CC3A7F8F-5717-4639-B6A5-ECE8361467E4}
FORT SEWARD 1122CB | {DDBF5221-9BD5-419F-9A17-E9260A89D7CD}
LAKEVILLE 1101108774 | {B6A7196F-7623-49FA-8ADD-1DAFF9EDFE0B}
OREGON TRAIL 11031448 | {0C0482CD-DD8D-411C-9735-C68EC442433B}
EL CERRITO G 1108CB | {1BE7584A-89AA-4EFA-BCE7-9E7AC1997D2C}
HATTON 11012654 | {38794799-8756-4269-B41E-6206BA101157}
LE GRAND 11107130 | {3A9B1AE1-6BF6-4F46-86D7-C0F6964F286A}
HIGGINS 11077559 | {735D1686-195C-449F-AFF7-F3F9879F6190}
TYLER 1105816852 | {E58E84BF-2C2E-494E-AE66-0D141BD137C3}
MC ARTHUR 11011488 | {62976FAC-DE1E-4247-A5CB-A153442821DF}
FORT ORD 21069658 | {6B4BEF51-729A-495B-8FC4-CA82105C9822}
CAMP EVERS 210511384 | {8B06F25F-237B-4FE8-8F99-17C1FF96A7BD}
MIDDLETOWN 1101614 | {8C7E457A-F935-48E0-AE77-B73661F39EFF}
SNEATH LANE 11061339 | {66ED3CF0-2002-44E6-BE2F-18363B4298A8}
JAMESON 1102865502 | {A17489AD-F8E6-4EDF-87DF-CA9C33FE9292}
PAUL SWEET 2103CB | {BA3D6A76-5335-48A7-9116-A38FBA76779B}
BAY MEADOWS 210257886 | {D73C61C6-F360-40B2-9388-D54915745260}
SANTA YNEZ 1104685160 | {D82CFC78-0AF6-4ED3-B064-C26DDC2F5970}
HALF MOON BAY 11038920 | {326D13C2-6BC0-4D12-9CFE-64D0722362EA}
BIG BASIN 110296986 | {87B7E394-3606-4372-9564-36FE0E57DA45}
EL CERRITO G 1110173396 | {DFE6BFCE-280C-433D-BB23-93842B63AE53}
LOS OSITOS 21037062 | {113FEF80-B5A7-4041-A279-F58DE4B71B87}
DUNBAR 1102861496 | {200F9B52-1051-48E9-985E-1C9F81A1D6A9}
ECHO SUMMIT 1101927812 | {14BBAC88-26D3-4F29-8425-274D619391ED}
SAN CARLOS 1104699632 | {29D0150D-9878-4E59-901F-2306DBADDF8B}
CLAYTON 2215500240 | {6A2904BE-6CF6-42DD-B2C9-F94DF16B8A15}
PAUL SWEET 2104CB | {9E32E9CD-A939-47B7-8D32-52540B68C5C6}
GUALALA 1111887180 | {F1237B34-AE98-483F-8E45-6E7314FDEDD2}
ATASCADERO 1101A36 | {1A2AEC20-7798-471E-990E-3BD9D80801FA}
VIEJO 220486890 | {82047029-EAC1-4E39-B4D2-10647DA90BC3}
FITCH MOUNTAIN 1112CB | {B406A001-5E88-43B9-9966-330465F8E093}
UPPER LAKE 1101412 | {CEA08BFB-7016-4016-B5B7-B9CA2EAF8E9F}
EL CERRITO G 1112779030 | {1F8F52CE-D6F8-4FF1-8C8D-BAA757FE8A8B}
SANTA MARIA 1110M04 | {E772CBEC-2F5A-43A3-91C3-8EE495E372D1}
LAKEWOOD 210769586 | {9E806E71-872A-40DE-ABFF-C0053F485B27}
HATTON 1102CB | {DF6AF33C-27E3-43A2-A515-B3B27F7B49FE}
ZACA 1102CB | {06AE963E-8682-491C-931E-D311BC02A28D}
CAMP EVERS 210410442 | {51C72ADA-5E33-425F-A574-21BEA172A863}
MIWUK 170236888 | {5E0E9C3F-102B-4736-867B-523AEBC69611}
SANTA ROSA A 111038858 | {422CE5F4-0FBE-4EEC-A8C2-C4BEFA9D6650}
CUYAMA 1103934590 | {85AC51B2-8F96-41CA-A563-24966A62ABEE}
WOODCHUCK 2101R9223 | {FE71AAF6-F6E9-485B-A3C2-10412CBC3ED0}
GARBERVILLE 11011770 | {BBD56973-ABAA-4951-A1EE-E863C47010B2}
HIGHLANDS 11034630 | {C0802380-5040-4C58-8433-9FF2FB3282BB}
CLAYTON 2215W573R | {C86C14F4-2F7A-4D9D-966F-4FE249C0F52F}
CAYETANO 2109MR572 | {DE968837-AFA5-4F15-89D0-BA934A29FE50}
GREEN VALLEY 21016625 | {C8470ABD-D047-4E6E-A601-35B08D6D1BD2}
HIGHWAY 110181590 | {5C6F4134-089B-4151-9D4E-9160DBB180EF}
CALISTOGA 1101267806 | {BE08BC28-7DA9-44D8-9CEB-E52E9B54BB88}
BLUE LAKE 1102CB | {DB40B2E8-0171-47DD-8BAC-EDA4F7194556}
HALF MOON BAY 11026153 | {72FA64D8-3A63-4420-A7D7-130A2E3D886E}
JOLON 1103CB | {13EB3903-13F9-40C3-94BE-AF1022EEB8B5}
CLOVERDALE 110276878 | {1AAF0353-36A0-471D-9307-CCC6B1BFBE5C}
LOYOLA 1102550291 | {379AF1A9-16E4-4C0C-BE5C-4BB0C4F98451}
HICKS 2101XR250 | {7AD08992-20DE-491C-B310-C51F11D11659}
PINE GROVE 11021765 | {B84BB2A7-38F5-4777-ACCF-AE61211F946D}
SWIFT 2107XR086 | {7CB97158-4C16-4CA5-9FF2-9C62CE30BD07}
DEL MONTE 21039106 | {900D5BA1-EA68-418C-9CFF-B7A1E9A4FECC}
LUCERNE 11062327 | {BFEEA045-A307-47A2-9C2E-0B69ACE24065}
MIRABEL 11014859 | {1B23A4BA-CD57-4FC0-AB6D-FA127475AD96}
FORT ORD 2108CB | {AF7D3D91-B816-4BC0-A0EF-CC9A68E30A8C}
SONOMA 1107CB | {B66DFA6A-6131-4186-B4AB-0BA7B611120F}
COTATI 110599720 | {711CF875-45FB-4C9E-91F5-632D204CB23D}
OAKHURST 1103464622 | {E28BFF8D-F8E2-40AB-836D-4CDEF3E6FE3D}
LLAGAS 2104XR294 | {F11F1581-106D-4267-B291-AD8060715445}
PACIFICA 1101CB | {0685C5F8-0970-41C6-89BD-EFB0337B96FB}
VIEJO 2202CB | {204F3E15-8D98-42F3-A6B0-F8D2FC5C7EAD}
CLARK ROAD 110247006 | {6FBCFF19-8461-4946-AD7D-C380516CF011}
JESSUP 110141356 | {7C8CD245-F5C5-41C8-8C39-1CC5C953323C}
DESCHUTES 1104378894 | {BC7A1387-B3D8-4140-98B2-87298F0B6696}
HAMMONDS 1102CB | {FD894490-402E-4AE2-A8E0-2A3DAB4F2C46}
CLEAR LAKE 110145252 | {4B824BDA-3530-4F86-B304-5BB8EAFD0730}
TEMPLETON 2110N32 | {33400389-0E2B-42A8-BC66-48CCE49F1F75}
OLETA 1101440008 | {C597D1DF-05AF-4117-9139-6F79BFFC0A15}
RAWSON 11039052 | {2BC26C95-B90F-49BD-888B-1F85DFF0BF79}
FULTON 1105172 | {63777790-64ED-4263-AFF5-02757B725BB7}
JAMESON 11057792 | {41D42D82-88D5-42DA-AE8F-BA1A622569DC}
MONTE RIO 1113CB | {C3FAC8CF-A105-47CA-BAFD-6A205D726950}
FRUITLAND 114137410 | {CF682344-0C1A-411D-B173-CAE04AD6EAA0}
MOUNTAIN QUARRIES 210135466 | {F283C4DF-68EA-4D46-BF4A-0E3EBCA0E4FA}
CASTRO VALLEY 1110CB | {FFE0EC6C-F31E-4ACF-B207-C8795D8C3898}
IGNACIO 1105318 | {25FEAA66-B3E3-4A2E-9CFA-07C2BE62DF67}
MENLO 1102560798 | {9F355D1B-96B2-4F1B-AC5A-69166E99F7CE}
WRIGHT 11103220 | {ABB28193-DF6D-40B9-BA16-1713A8EF4B58}
CASTRO VALLEY 1105MR215 | {7DC88504-8437-4262-8C77-15F7F25CD1D4}
PUEBLO 2103253312 | {D97500C1-9AD3-4748-953B-EC7E95FBED39}
VACA DIXON 11059792 | {E29DDFD8-87C7-4111-AD68-0CCC26FD3BAF}
RALSTON 110148936 | {EA4820C6-602A-444A-A1BC-AC0CC345F5D7}
CLOVERDALE 1101112 | {EFFBC73B-5CF0-4391-8D52-00A9D7379A46}
BELL 1108533042 | {3E1C7211-235E-420D-A32C-57DAE88986D6}
PAUL SWEET 21025291 | {ACD82200-9A89-4E0D-B5FF-D276794568F7}
FULTON 11054106 | {957874C2-FA06-452C-924E-A5E4C30E68F3}
MIDDLETOWN 11014646 | {9CD0DE6C-67D0-4975-9926-0CEC6137D8E0}
FITCH MOUNTAIN 111324550 | {C4DDBB89-4E15-4D06-A02D-161343869D3B}
SAUSALITO 1101688590 | {FB370B4C-A340-488C-B2BF-3C5B30E54274}
MIDDLETOWN 1101829164 | {302C19E7-740B-49C6-83EC-9E70AC44D5CB}
SALMON CREEK 1101668 | {4AA7E9BF-D824-42F7-B4F3-AF51F29BCC9C}
PENRYN 1106212772 | {2BBB97CC-A78B-43EC-BEB0-66A2E29BC2E3}
DOLAN ROAD 1101156268 | {A6335D58-E606-4A31-A5A5-958C5FE37A92}
LAKEWOOD 2107GY401/2 | {C476BEC6-6566-47F3-B164-264FA9A69083}
WOODSIDE 11012299 | {0C4874FF-D222-478C-B9D7-BED0F08FA35C}
LONE TREE 2105CB | {BF1E0B7F-6FE5-43AC-AD5E-51535747C12F}
CLOVERDALE 11024646 | {08D74C7F-8D6E-4EDB-8355-DEA79828121D}
SAN CARLOS 1104833770 | {184D8D5D-E270-4177-8D06-41B2ADC4598A}
SAN RAFAEL 1107328 | {64A83390-336F-46D2-AA1C-9D91A30B0162}
DIXON LANDING 2101XR340 | {78E11C69-9A86-4183-B3C4-869A091C2B3F}
MERCED FALLS 110222774 | {A07075F3-76AA-4FC7-9158-0930DA76C5B7}
SYCAMORE CREEK 11092458 | {6DD04BFB-4C98-43A2-94E5-EF1AAF874533}
ROSSMOOR 1109847274 | {03879870-FD7D-4E28-B553-CE6842933DB3}
BLUE LAKE 11013578 | {2B080883-3F89-467A-86D3-526324676232}
GERBER 11021560 | {51D7DA46-9CAC-46EE-9575-3C307DF390C6}
LOS GATOS 1107812664 | {5685685F-A6FF-42EC-B764-0A6E777F0FC6}
CAMP EVERS 210510912 | {62DB6A1E-C643-412E-AD78-478695BE02E4}
HICKS 1116733078 | {128CFE15-7FAD-449A-AC53-530ECD1ABDFD}
CLAYTON 2213CB | {BE7BFFAE-6862-4503-AA75-EA4658F3F71F}
BIG BASIN 11015000 | {BFEB630C-08C1-40BC-9696-C350A5A8EA12}
UKIAH 1111477890 | {C19836E9-D34E-4A81-923F-AE30E5CB731B}
PAUL SWEET 2103811390 | {BA3D6A76-5335-48A7-9116-A38FBA76779B}
VOLTA 110165764 | {375728DD-644E-4E4B-9A8F-230DD2D4E917}
SAN JOAQUIN #2 1103157026 | {5512EE79-F6AF-4543-8A7B-B7E11740B6C7}
FORT ROSS 1121CB | {6432AE5E-F371-470F-8E71-1BA304A7A433}
SNEATH LANE 110275844 | {AC57E8D0-E406-43BB-B0B4-92AB46A557F5}
RINCON 1104207458 | {1E4D7366-24E5-4493-933B-743F7C171401}
SAN LUIS OBISPO 1103191498 | {53668CA1-F0BD-426B-87AA-933BC191323C}
SAUSALITO 11022033 | {F71841C2-A9F6-40EF-B1D5-2F1AAA2168CF}
FROGTOWN 17016807 | {32DE7714-2265-4DEA-9044-817FFC428BF4}
OAKLAND X 1104645092 | {14DC5424-B005-4065-8948-2B6A676B0C25}
PEORIA 1704877670 | {2FC56DAF-3BEA-4D4D-AF4F-08FDD13FFBA2}
KONOCTI 1102410004 | {3DD38877-E68D-4183-8213-2DCDEB2FC639}
SOLEDAD 21053076 | {36177CF1-DF55-4FEE-893C-1AD0F53C4183}
HALF MOON BAY 11038894 | {65F40270-9C1F-4F03-A2E4-A1FA52E4266C}
WOODWARD 2108CB | {8314795F-0D04-45BD-AE69-B7277494B0E9}
MILPITAS 110962157 | {9C37E848-C9FB-4404-B824-088800AAA1AF}
BRUNSWICK 11038918 | {D34CE8D2-4E63-4899-B49E-7C6D0FD502F0}
PACIFICA 1103885952 | {572B383E-2937-4EFC-BA24-50423EE8A457}
PENNGROVE 1101554 | {29853D86-D10B-44F9-9B31-548850DBE0F0}
MERCED FALLS 1102CB | {3C66AA6E-AAFB-4AC9-BCE9-F89CAFA6091F}
TEMPLETON 2112CB | {5E55D6F2-0179-4A06-BFE4-E717E82210A3}
BIG BASIN 1102307348 | {684496E5-6AA8-4CE0-BD15-F571AD20F865}
CASTRO VALLEY 1111CB | {75D298E6-3FF1-47B6-9B91-A2291860E391}
MIDDLETOWN 1101959140 | {7B530842-C667-418B-ADA6-859E3E2891D3}
BUELLTON 1101Y34 | {9919F67F-7D4E-4CC7-938A-6CB755805F83}
MORAGA 1103CB | {A7850717-18DF-4BF5-B934-11A86FF92EB5}
BIG RIVER 110169032 | {B18E180C-39A4-4EFB-8DCB-B1B629947F6E}
CHESTER 11022614 | {C8BA9CFD-3C7E-444F-AD17-DFDE1ACC00EB}
BUCKS CREEK 1103CB | {2C93052B-CAB6-4039-91C2-ECB9C837F00A}
UKIAH 1114544 | {4F4D60A8-18DF-4AD7-9533-2FDA5C5224B4}
RIO DELL 110192712 | {56AAB81A-EA84-498C-8B2D-C89BEB9CDBC9}
MORGAN HILL 21103093 | {FEA8F80B-51AF-4084-A9B9-47D11430DD95}
MEADOW LANE 2106970936 | {9FDBE41D-F5FA-4A91-8801-9FABAD55128D}
TASSAJARA 21123202 | {FFB25F94-DDAE-4CA7-A7FA-E0E40AD2E7D0}
CALISTOGA 1101257964 | {0D63E34E-7108-465F-BC13-5DF2F623AD72}
CAMP EVERS 2103CB | {22D220C5-2768-4212-BADC-DEEFF16BE912}
WYANDOTTE 1105CB | {2426BD3B-3A69-4A04-A051-7581B14322B3}
STAFFORD 1101CB | {42AA63AD-C552-4EF9-BEF2-2D7A46307F74}
DEL MONTE 21039452 | {572A903E-D7FD-4349-978F-5FBD205DDA11}
CURTIS 1705CB | {87827028-00DC-43D6-989D-C6C9D1E3E860}
GANSNER 11012006 | {AD16C82F-076B-43F6-B112-51D5058EB123}
VINEYARD 2108609690 | {D247C9D4-2385-4C86-98D9-FAEFF0DAB6B3}
COTTLE 170178452 | {D07798BA-B7E6-4FB9-A5A9-A05BC7F2FB6F}
Deer Creek PH 0401CB | {F552B7B1-BED9-44D6-8E42-3FC8759927EC}
OAKHURST 1102204618 | {4739024B-FF85-45D7-AECF-B2FD3D7B777B}
GRASS VALLEY 11031700 | {34D5CE89-BFD0-4BEE-AD2A-0183175AD2BA}
SILVERADO 210298998 | {B9DFD3D4-5938-44FA-A6FD-F2608641C707}
HIGGINS 1103789714 | {5963F19C-E1BE-46EC-9E26-B117A913E935}
EL CERRITO G 1105BR164 | {14BEC098-B04A-4CB2-9AA3-38D63A101CE1}
LOS GATOS 1101CB | {168FAC6E-221A-4D80-AD26-79821278B765}
PARADISE 110439214 | {1CCA13E6-0B87-4BF0-8C65-1F382E0EC595}
LLAGAS 21013835 | {07E209B8-80A2-40A5-8228-12D4DFF42801}
LAYTONVILLE 110237586 | {389365FD-B3C9-4F63-9935-3457B5B05A11}
BONNIE NOOK 1102CB | {3EE03E8E-7174-416B-B7B0-D49DC8F3C48B}
BELMONT 1110522372 | {650AE2A0-8481-4167-A199-68E796B3390A}
FAIRVIEW 2207M514R | {659FD2EB-053C-425F-AF25-D9C58353B44F}
JARVIS 1111907698 | {756FEBB5-79F7-43A0-8D9C-AD33FFCC0DB1}
MONTE RIO 1112CB | {78AB2FDD-E1CA-4DC9-8362-0759A43BD212}
CORRAL 110112606 | {83EA1908-090F-4204-B568-C4FACFA08477}
RISING RIVER 1101CB | {9F15BDD3-391E-4F68-AFF5-FA940D11CF0D}
CLOVERDALE 1102801904 | {AC125630-32B8-4336-8024-7175EE6E43AB}
WEIMAR 11012764 | {CBE676E4-58AB-460F-8EF4-93AB8DD21D9C}
DUNBAR 1101835658 | {E3222172-78EF-43FF-8CE5-0E25731FEA0D}
WOODCHUCK 2101R2770 | {FE71AAF6-F6E9-485B-A3C2-10412CBC3ED0}
GANSNER 110199388 | {13627031-EE44-4823-A048-AA36CB9BE013}
KING CITY 11027024 | {3218C69B-BAC7-4C6F-9235-42A08CF69E6B}
APPLE HILL 21026552 | {4065F493-7B96-40A7-8EE5-29CF10B90CA4}
MORRO BAY 1102CB | {4C9F3CAE-E991-4EA7-BCAB-BA03C4CEAE92}
CAYUCOS 1101W58 | {5CFEA468-EAFA-49AC-B046-6E19D81021D8}
STAFFORD 11011082 | {FF138367-96EF-4586-B73C-AE42FDD878F0}
WILLOW CREEK 11014904 | {2D4A5008-1C90-406A-A2B7-E4FA7A353F8A}
SAN BENITO 2101355426 | {309BC145-CE1F-4552-9344-E193E2F32C60}
CORTINA 1101302192 | {E3B77E93-BB57-4588-891B-4456F675EF56}
PLACER 1103238990 | {E0134993-C6C7-47B2-B903-8846B3C865A5}
PAUL SWEET 2105893980 | {33AE2657-6F42-4109-A970-89EF5E991C73}
BRUNSWICK 11052140 | {B6A93F55-534E-4C9A-8EB8-6367DF5FB505}
OAKLAND X 1104CR288 | {E0AFB0D0-4FAA-4A38-B181-558E89FECB34}
SHINGLE SPRINGS 211051800 | {027EA52B-9771-4584-AAFD-2CA838E196C2}
INDIAN FLAT 11044440 | {215B4A0E-B4E1-4DEB-8481-0B3FF4DD4D17}
BIG MEADOWS 21012510 | {2FDD93D7-D61D-44CD-93DA-C1ACCE10D2C0}
MAPLE CREEK 1101555034 | {D3EDA1A2-8AF8-4A2A-853E-161161439812}
SONOMA 1107844168 | {DFD9B477-AC78-4483-B663-8671DA768CEC}
CORNING 11021900 | {097280CB-BBAB-443B-A213-61E2653EB02B}
GEYSERVILLE 1102484 | {1E362916-4E6D-4E8A-A229-F0750B3C8096}
LAYTONVILLE 1102682 | {9C0210C9-FBB0-4C91-A32D-9DD4D26081CB}
SALMON CREEK 1101660 | {DD137AF2-2749-480C-8784-159970C4FC2E}
FULTON 11024994 | {EA9B2479-0C7B-4A59-82AF-47AD3E8F521E}
TEMPLETON 2110R90 | {EAF87279-EF23-4A44-B5E2-CCA62D5C53AA}
DEL MAR 11032702 | {FAA4BB2F-A14A-4ACA-9B63-02DFB58C1EE6}
GREENBRAE 110182270 | {FE2E59EB-BA50-4D05-88C6-174D3F07D4AE}
MIRABEL 1101298 | {1B23A4BA-CD57-4FC0-AB6D-FA127475AD96}
CLAYTON 2212681608 | {1FCED433-5B38-45B2-A635-D0F6F632FB56}
HONCUT 1102976552 | {3DAB252C-5A42-4BD0-ADD0-23CE62160133}
CLAYTON 2215W531R | {32128C45-30E5-4BD3-83C6-38B6DDD0B832}
POINT MORETTI 11015074 | {744CBA45-CA46-417A-809B-2361EA738493}
SNEATH LANE 110168070 | {AE75174C-F0FD-4D78-8720-D705019718D7}
FOOTHILL 2101549904 | {BEF6045A-3518-436C-A876-62625F5A4B60}
GOLDTREE 1107477878 | {E099D2A0-66BE-4A41-88A9-690DFD5F2504}
CAMP EVERS 210312990 | {EA67021F-EC51-4B91-B55C-AC9EF715A21B}
ROBLES 0401CB | {14E1D31A-B903-4B3D-95CF-6D667219B97B}
COTATI 1105104502 | {1E254E89-80C2-40C5-86C1-3418E85098A5}
MC KEE 1107XR032 | {22D0F857-9929-4CD2-9E4F-9210026EF7ED}
ROB ROY 210412596 | {272F711A-D76D-479D-B7FF-5C57D964944A}
PLACERVILLE 210639576 | {86E99440-83ED-4726-A6BC-38E34FEB5B33}
STOREY 110921859 | {F6521ECD-18B4-4A6C-9FB9-B5018A20E90A}
EDENVALE 2105XR350 | {8A7625DF-9660-4682-92E4-DE9581577DA5}
STELLING 1111LM10 | {E9E9A7BE-6BF1-4820-BD71-A61CE1AF4848}
SAN RAFAEL 1101312 | {559ECC42-B403-4A94-88A4-68DFDA9F0CD1}
DUNBAR 1103160 | {98861C56-51D3-43DB-9804-E460E1D0C1F4}
COTATI 1102CB | {991C05ED-971F-4D32-B6E6-51948C4F329B}
DIAMOND SPRINGS 110519910 | {B086CF84-D2F5-42B5-8FBA-007201735811}
HILLSDALE 040198526 | {E5751866-C01F-4B6F-A700-E0FAA4499012}
BRUNSWICK 11062796 | {EF5B06D7-E629-41B9-B306-6C2CC9919130}
MC ARTHUR 1102LR-RC-B | {E9334D2F-2952-4052-8ADD-E3F42DB77666}
JESSUP 1102CB | {232A469F-DE89-4EE3-AC4B-F74419E6464C}
UKIAH 1113691436 | {6C8F23E8-D864-4646-ABCC-F348028A767E}
COTATI 1105844060 | {8FC5790B-23DE-4032-81D7-65E070CCE3DA}
LOS GATOS 110760118 | {996F801A-49DB-4E12-9C16-86F37BF363D7}
CALPELLA 1101908688 | {BFCBEF1F-58BB-48DD-A44F-6E7737CC17D3}
PANORAMA 11021632 | {CE87ED54-B441-462F-AE1C-C4DF9A1FDFBB}
PLACER 110451734 | {0E740EDA-2722-48A5-9962-250FDAF0A7CF}
NARROWS 21052420 | {94CC379D-BE20-48E1-8496-01F284C7FE9E}
STELLING 110913228 | {76970631-2436-4433-8ABE-AE41F160A6E0}
PACIFICA 1102934870 | {CFE1B2DE-63B7-4084-B6EA-A58F62A2EB56}
PANORAMA 1102280170 | {D4F4CD74-DB1C-49F4-9D89-1A434E6A2652}
TASSAJARA 2112D514R | {3FFF1795-1315-4A71-8E91-178B9A0CCDE5}
ROB ROY 2104CB | {869A1D07-AF0C-4C1B-B4FB-3299F6D51C09}
DOLAN ROAD 110169466 | {8DAD43E1-C0B6-4B91-89E1-55DFB8ABD7AF}
PETALUMA C 110835448 | {184EAEA4-EF9D-4F25-94EE-091BC560403A}
COTTLE 1708968888 | {9FFC0599-7BDD-4120-9A8C-31EF3E3F7596}
BALCH NO 1 1101R372 | {A73833CF-1AF8-4A38-AFD0-B16A74E1496D}
SAN RAFAEL 1106CB | {A84CB2C0-9849-4D74-A8E8-7B5529F6398B}
MIWUK 17029270 | {AA0F2742-8D52-435A-9889-3CD8160159B6}
WILDWOOD 110185112 | {47D06C81-6B61-4B8B-8054-D7C4BE7B9ED2}
PETALUMA C 1108594 | {184EAEA4-EF9D-4F25-94EE-091BC560403A}
PASO ROBLES 1107P22 | {1C337801-E008-421B-9399-975B6DF38CC5}
PEORIA 1701CB | {3B5F2B21-B073-4B15-A884-38AC36D267F6}
CURTIS 170390320 | {419BA50F-A9D8-4C0B-BAD7-EA55841BE036}
PUEBLO 2103678 | {80E79C4D-3B76-415E-BA02-A8236360DA4C}
IGNACIO 1101CB | {A57172F7-A24B-4226-8C15-DA9E4C31AFEB}
LAS GALLINAS A 1105904 | {BA4CC229-6FEC-4C97-A427-8049E1A3A120}
CASTRO VALLEY 1105853216 | {D3473D96-EE5A-4DC3-BCCA-A509A72B1AB7}
MORGAN HILL 2110CB | {E4018ACB-C125-496A-B5B0-B421A786B3CA}
AVENAL 210144778 | {25E0F7F5-6399-4822-97AD-9B04397D81D8}
NOVATO 11041282 | {3B8D2573-46CC-4384-8812-825E9555364D}
MC ARTHUR 110153120 | {4F05ED84-FE56-4A90-8DC4-86D939A68626}
DIAMOND SPRINGS 11062100 | {6647B708-EB30-40C8-9FB8-1AD5D9953BA6}
DIVIDE 110348160 | {6ECC9377-E065-4FCE-971C-2036CD830EDE}
SAN RAFAEL 110648752 | {85056666-4A2B-4DAF-B399-DC93301E78AA}
REDBUD 1101400 | {928EDF6A-AE60-4D52-BF0A-EE27518314CC}
WEST POINT 1101CB | {B92F58F2-6135-47A4-8467-3E84B6151393}
ROSSMOOR 110665858 | {DE34AA94-F995-444B-B0E9-519FC6F293D6}
WILLITS 1104627552 | {E29C36BB-A169-479C-AE48-87F28EBCCCAD}
VOLTA 11011568 | {34779DE5-8611-43F9-82BD-96A7D918E1B2}
NARROWS PH 1151CB | {3969D241-789E-4335-9A13-4750E3876C2B}
LINCOLN 11011398 | {4AE4954C-B74F-45AB-A357-66A3AEBC8125}
PALMER 110198478 | {68615336-79DC-4EC6-9727-806E7A643D26}
BUELLTON 1102CB | {2D7A19FE-1388-4016-A42B-7364F42C4D40}
EL CERRITO G 1108BR346 | {47E84AA2-B51F-4F91-9057-B9557EEB1018}
BIG MEADOWS 21012476 | {A5EA53CA-65A7-43BC-BB3E-43041FB8E51A}
CORRAL 110136652 | {B537B104-D44A-45F9-BCC9-AE639B2EEDC6}
MORAGA 1104750618 | {D6B675EC-0BB2-4404-B1DC-E66B91C5F9F8}
PEORIA 170575274 | {EA8957E8-4D9E-4768-B294-C26CA1256456}
ESTUDILLO 0401850884 | {F934F942-DE0D-4D16-AAE7-D119512DF37A}
COARSEGOLD 21046210 | {37CEC619-9FFE-4BA7-9FD0-D8641CD59BBA}
NOVATO 110456282 | {45CE06EC-53C4-4919-88F0-CCEFB9190769}
PLACERVILLE 1110CB | {8F8EF18B-7E0A-4A9F-9597-8CCBE4E9FBDC}
GUALALA 1111289822 | {CEF9E817-A890-4D55-A76F-8D46E6790C4E}
TEMPLETON 2113CB | {DD694EAA-A9BC-4C03-B675-60DCE9DF4147}
OREGON TRAIL 1103CUS391 | {E6157D99-E31C-4483-8F6B-FEB133AE35BB}
WOODWARD 2108CUS5875 | {41DA8C6A-A66B-4741-8630-05B8383240D3}
EEL RIVER 11024600 | {6D6CFD45-47DB-4466-97E2-D7B4460098A9}
POSO MOUNTAIN 21012181 | {908C371E-60A0-479A-AB4A-419AF9711AF4}
CORNING 11021622 | {96C223CD-EECE-427E-9B50-0567153A92FD}
CABRILLO 1104597930 | {DB4CB1A3-78E1-4EA1-92B3-6161B305FA89}
NARROWS 21022220 | {15BB893C-861D-4514-BB53-2456F70C5D54}
MERCED FALLS 11027905 | {3C66AA6E-AAFB-4AC9-BCE9-F89CAFA6091F}
PUEBLO 1105696 | {78AAB710-6DDE-407F-827D-71666B977FA6}
ALTO 1124207690 | {2C543D7C-5902-4DC9-BE9B-719A66315791}
WYANDOTTE 110796390 | {B74488FF-9B39-410B-9AAC-30106EC9509F}
SILVERADO 2104515946 | {05AA93CC-3E16-4AA0-9C09-002C77C18466}
CLARK ROAD 1102212118 | {1264D9D2-8375-4858-AD32-A3365D0B100E}
DEL MONTE 21052644 | {317B7582-B045-4053-8009-5D848CC65A15}
HIGGINS 11071070 | {735D1686-195C-449F-AFF7-F3F9879F6190}
BELMONT 110268446 | {E797AB19-3600-4F18-89F8-9B9F590AAC2A}
WEST POINT 11014706 | {E8E54876-15CA-4535-8C00-844AA0076F05}
CURTIS 17039240 | {11F969DC-9C50-4BBE-BE33-15DB7CEEDE86}
SILVERADO 2102285782 | {7650C201-F544-4286-9EA7-A492BFABD887}
ROSSMOOR 1107857172 | {82E77E65-B48A-4043-92C4-BD82ECD8745E}
OAKLAND K 1103CR422 | {834BDB9E-9A30-4D9F-8424-760E012D4EC8}
OAKLAND X 1106121588 | {93028691-B011-4DD4-9BFD-411C56E1FD61}
KING CITY 1103139682 | {9E61253D-F8F8-496C-8DCF-19A52D48CF04}
SAND CREEK 11037110 | {D40D6BB9-1863-4357-9803-EF56709C4086}
BASALT 11062103 | {31C38397-CC97-43EB-A38A-D18D8FE5AEB7}
SAN LUIS OBISPO 1108809986 | {BB99A914-387F-48D8-919A-BB8BCFE90D9F}
BRUNSWICK 1103852240 | {D2CFCF41-58C5-4503-B8F1-FDC586F0302A}
ARVIN 110169618 | {2B1BA581-45FA-4D2D-868E-E1CB0E681EBA}
LAMMERS 1101932641 | {1FC74B38-2F9A-4123-9EBB-CB817D34D821}
RINCON 110499918 | {93D64AED-6AD4-4AFF-BDFB-1B1DAAB3072F}
RIO DELL 11027124 | {AA9B3AC3-107D-4281-A065-CEC882DC5747}
SALMON CREEK 1101571972 | {AC8C3E38-A041-499C-9BB2-FE26BAA0252C}
MARIPOSA 2101439030 | {B1C3BF34-DFE5-420F-B7AD-C0CAC681FC7D}
MORRO BAY 1101V66 | {DC1CD14A-C73E-417C-A65E-B1AE2FBC8341}
ROSSMOOR 1105CB | {2CF05CCD-DA30-4E66-88FB-8AE7485C3DA7}
WISE 1102449556 | {51CECB7D-FE74-4A7F-A054-30E9A1B3F446}
CORRAL 1101639614 | {6157CE71-7864-4436-AA7C-5C09CBEE33F6}
PLACERVILLE 2106909258 | {BA672D72-863E-4FB8-9458-911126FD31A4}
VOLTA 11021504 | {2D79CCBE-1B8B-472A-B9BB-B34254CCD666}
MENLO 1102362896 | {414B8FEF-04D8-45C9-AB62-09E735CC943C}
JAMESON 1105CB | {41D42D82-88D5-42DA-AE8F-BA1A622569DC}
KESWICK 110148480 | {9C6E3EC5-697A-453D-8DEA-C3F8B751E8D1}
BELLEVUE 2103388 | {018227D6-38CC-4EE9-BD26-7E3FF5AE9B25}
BUELLTON 1102Y50 | {BE22BF5B-77AE-4173-893E-2D7D15CAA658}
OROVILLE 1102434320 | {010ABE92-9760-4A20-97C4-698DB24D3E2F}
TASSAJARA 211238868 | {3FFF1795-1315-4A71-8E91-178B9A0CCDE5}
AUBERRY 1101CB | {50F15232-B267-496F-ACCD-C66670CD5E1D}
CORRAL 1102CB | {A70761E3-E888-44FB-B083-651B5C823F25}
SANTA ROSA A 1104CB | {BAA473AF-66C6-4355-8E90-0CDB40A98A03}
PEORIA 170413490 | {D6A9F596-51F2-4D36-A52E-B2F47C72F950}
CLAYTON 2216C544R | {DB6FE7F1-AC75-4C7E-83AC-CE5B6DE225C5}
ELK CREEK 110193504 | {C805E056-6565-4701-B47E-65A72A694487}
LOS OSITOS 2102258878 | {03FDC6F0-8EFF-4D98-B64E-FE44DDCDA68D}
BURNEY 11011358 | {2A928B3F-2AFB-4E95-9D5F-1D4611A31405}
PARADISE 1105828400 | {2883212B-8F3D-451B-836C-9588E5771E60}
SAN CARLOS 0402CB | {5D32D1B4-08FE-48B9-8413-A6C8374335DE}
GIRVAN 11011330 | {614F599C-8E41-4F43-93F2-0A1EC10532ED}
SOLEDAD 2105526864 | {1D34DC58-836D-4803-AFE9-57F78BAE9DE7}
GREEN VALLEY 210111054 | {D718FE21-E107-484D-ACA1-7018B98129C1}
CLARK ROAD 110281296 | {154C476C-5A31-47D9-B01B-5C020A5462D1}
VALLEY VIEW 1105P126 | {1A179874-1BC4-4379-BC93-DB3AE752926F}
AUBERRY 110149122 | {6985CB9B-1F8C-4CB7-A5AE-AEFA2BA7C828}
CAL WATER 11023802 | {A5C90C7D-4BB3-40A3-8AA7-071C177614C2}
HATTON 11029642 | {96F3BFFE-8B25-45FE-9E94-B3CC1506798D}
CLAY 11035386 | {85E341A9-44AE-48B4-AEF5-91CF5EF041CB}
BUELLTON 1101Y06 | {B215B9B7-F7F3-4553-8BC7-ED531B03358B}
CAYUCOS 1101CB | {E8519C3F-CC2F-4A8E-BB1B-BC611BF917C3}
LOS GATOS 1106LA42 | {07C3F785-A0A2-4537-8DD2-EA76577441A5}
SONOMA 1105138 | {7B41A8E9-FC21-424B-BE2E-1E6F807F59E5}
ELECTRA 110136816 | {7E08659E-39A5-4373-949B-319BDC171EA7}
FELLOWS 21041073 | {837EBEEA-6D15-4355-A56E-82983C8D6DE0}
WOODWARD 21085060 | {8476058D-CCFA-425A-8D9D-8591EF3E3149}
LOS GATOS 1102CB | {9CE095E8-15BC-49D7-95AC-553D14C8CC1F}
SAN LUIS OBISPO 1101V12 | {D3B095E1-F799-4165-8E63-ACB7F609DF06}
MIWUK 17021808 | {F7C0AC68-FB70-41DD-B222-3064175EA9BE}
ARCATA 112233062 | {B31BB8D7-E9FC-4E78-862F-0335ED33A574}
VACAVILLE 1109592742 | {695B9A66-1C5D-4614-8CBB-D52A4B4D47A7}
SILVERADO 2102942170 | {B9DFD3D4-5938-44FA-A6FD-F2608641C707}
PUEBLO 110459106 | {A4183870-AFD5-4FAE-BBEF-716EC88D1AB1}
SAN RAFAEL 1109CB | {B783060E-D866-4158-B26D-888D25122311}
LOS OSITOS 2103220608 | {B9039DB0-DC75-45BF-9F2C-149A67BBE1F8}
RINCON 1101839669 | {C0A31C4D-93ED-42DB-A4BA-1A3FEE5BD36B}
KETTLEMAN HILLS 11019180 | {F47F682D-7138-4134-B3BE-7095779FF947}
LINCOLN 11042070 | {FDA2EA55-8785-46E8-B115-1C92328E3E9B}
SAN JUSTO 11014002 | {3BA4B8C1-556E-4444-9F96-4ADCA52FD345}
HAMILTON BRANCH 110153192 | {D03C18EE-E1AA-4630-B396-89DAD0F5DDA8}
BEAR VALLEY 210576694 | {DBF29453-0B03-42AD-A97A-1CA961543977}
LAKEWOOD 2110D578R | {ED726999-1701-4168-B617-29D7FAC0197C}
GREEN VALLEY 210182789 | {5C8DA4CC-DB0C-4E65-BF7D-024442DE4F36}
POSO MOUNTAIN 21013990 | {00D1CA6B-BA0D-48A2-AF6B-44F02D16A6FD}
HALF MOON BAY 110148868 | {0C9E66AB-FF7E-4958-AED9-234BEE09CC6F}
AVENAL 21019810 | {25E0F7F5-6399-4822-97AD-9B04397D81D8}
DESCHUTES 110449024 | {271E2474-ABAF-41B6-966B-4F5B19FF11CA}
HALF MOON BAY 1101821698 | {4C57C032-9144-4113-A71E-DB2019EE4077}
SAN MATEO 04048554 | {5D607F0F-481D-4D2A-862A-231FF7901489}
DUNBAR 1102386158 | {672F5B11-4A5D-4A77-BAE9-574FB74B1678}
FULTON 1104CB | {86598FBB-5AAE-49A3-956D-D4079C4EFDE4}
UKIAH 1111CB | {FBA231AA-2A4C-4C3A-9CF9-4FC7651694D6}
SHADY GLEN 1101145584 | {1877CBCE-9492-4F47-B598-89710F79592C}
RACETRACK 17032553 | {155070BB-C96B-485B-99BD-6B770FC28FA3}
WYANDOTTE 1109170732 | {EEE67C1F-6C23-4D81-9B06-45B190348549}
ELECTRA 1102285758 | {7D7E61A9-DD15-4C94-B46D-9A82D231AEA5}
ROSSMOOR 1106166550 | {4AEDCE3D-BF5C-4D21-A955-F5F1D5680D0E}
DIVIDE 110398166 | {4AF5ECF8-33C4-4E7E-9141-A6CD2D4FF4E6}
BRUNSWICK 110750010 | {5FEB44CD-F1A7-4044-A3E4-77CA9BA8E902}
EAST QUINCY 1101186938 | {627D9E79-9527-4BAE-9B90-33425D67192A}
SAN ARDO 11017945 | {D178EAD0-51DA-46C3-AC83-7A5FC311BC88}
MIDDLETOWN 1102878 | {EAAE6801-22BE-4013-9B3B-D2D2C906D6CC}
BRUNSWICK 1103639148 | {F18B8210-FBEC-4E04-A79C-5C0A5F7DDB09}
MADISON 2101117644 | {03566FC1-B4DF-4D1E-A42B-48526D62FDEC}
MONROE 210290988 | {0EBA2BBA-1703-4B1A-B59D-EED82556C743}
HARRIS 11085984 | {9A3D8818-9236-4C74-9C67-0369FA031A48}
DUNLAP 11027849F | {DC0C9AE9-E0EC-4108-AF9E-4DDFE694FC71}
ALLEGHANY 1102CB | {303E53EF-22EF-468F-BD54-C029D47A56AA}
OROVILLE 11042588 | {6CD595E0-0633-4F8D-A21D-706EDE410B88}
CHOLAME 2102X22 | {8576EB3F-3AE6-4C28-B63E-BF3A9FDC680A}
HOLLISTER 21024780 | {17B07670-0E53-4796-89E8-790E1D545BFE}
EEL RIVER 1102630456 | {BA4CF323-BCF8-49E7-A1D7-D6A1F53933B5}
MERCED FALLS 11029470 | {C35DFEFE-AAAB-47B8-ACD8-3B6A331D2855}
FORT ROSS 1121134 | {D2E66D36-59AC-4BEC-BEE9-31C660B6B4ED}
MONTE RIO 1113477 | {3F69DD3E-C46A-485A-8A4E-8252A760746F}
DIXON LANDING 2109MR211 | {270CEB57-AF3B-4573-86AD-B73952A8BF6B}
SONOMA 1105435024 | {2B737C15-F621-4E73-AF75-8131ECC2AA24}
FELLOWS 2104274456 | {7F80779C-1619-4C01-8BF5-4EDD2481CA9B}
OILFIELDS 110383158 | {B2FF44F5-E554-4874-9716-21C58C3BA291}
MILLBRAE 11045521 | {29B1D2E9-693D-479C-A160-99B72B4A4B3F}
LOS GATOS 1101LB40 | {2E2463B4-F331-472F-B632-0DB9F9C1E4AF}
MOLINO 11034894 | {AC40E023-4A81-4908-BE46-066808454E49}
OTTER 11022002 | {BF5568ED-9C16-497C-B05F-AE0C967E64B7}
SAN RAFAEL 1105645362 | {CC6A4E26-740D-42F4-A649-35571E3A45ED}
MARTELL 110111244 | {E154310E-F1E3-4CE7-BE08-29FE6DF23F68}
SNEATH LANE 110210287 | {40980895-4B8E-4C74-B15F-E13FF900DC4F}
HIGHLANDS 1103287766 | {AD7457DE-7857-4646-BC27-24CDE616604D}
WYANDOTTE 1110CB | {B4858E1E-C2DC-43E7-A857-62EE09547E47}
FITCH MOUNTAIN 1113406 | {31A95017-FE64-4D4F-A4CA-39176F23B79F}
ALHAMBRA 1105CB | {36DDF29F-B22D-4B8A-AF4A-BB933D5333CF}
CALAVERAS CEMENT 1101585 | {765E2074-110B-4FD6-8019-AD09D7431DAB}
OAKHURST 110363334 | {778182E4-2AE7-465E-B2C9-C1ED6A0D9207}
LOW GAP 11012094 | {7F4B9844-ADF3-422F-9AC4-7D66BD72A184}
LAS GALLINAS A 1104CB | {B49A679E-AF73-47B6-A79D-47CB4D4EEA89}
HATTON 11022070 | {E55048C4-CAB1-4B6B-99F6-30BB24FEA325}
ALTO 11251226 | {E82C2F97-5C09-4976-BD47-A486EC875FA4}
NORTH DUBLIN 2101MR765 | {436DC1C4-F56A-4204-87B1-78F6DDDDA501}
FORT BRAGG A 11013113 | {C40FEC6C-4399-4FDE-8ABD-E729D917D61E}
HARTLEY 1101789752 | {D05A5F97-BA6C-4210-AA67-0AC96ADACE28}
MORGAN HILL 2105XR578 | {534A451C-57DA-44B8-B8BC-2F5C24A553D0}
SAN CARLOS 0405CB | {55F8A6BE-5507-412F-A65C-4CFD7B83CA1D}
WILLITS 110391810 | {75E7E1B3-D461-49A0-A0AB-E84CDEE528DF}
ALTO 1124870444 | {856EAD72-BC3F-4C54-B04F-3629A4B87A87}
CMC 1101CB | {BCDF55E9-752A-4470-8F8D-971D8F755C6B}
CAMP EVERS 210595394 | {CA99B367-8DC7-4E82-BCC3-DFC89B2C9160}
GRASS VALLEY 11012208 | {15B21A5E-7758-402F-AB04-357FA8BC8C24}
MARTELL 1101532836 | {2C34AC51-01A3-44C9-B45A-F5786A7BA8F0}
WOODSIDE 110147872 | {3F2B4E81-3F76-4F92-B31C-17D1A0284314}
CAMP EVERS 210355638 | {4C9A65DC-55B1-4CE2-AD64-FA340511DC8F}
SISQUOC 1103M98 | {72D51786-0F19-4A21-BD91-493BA8FA331E}
TIVY VALLEY 11077380 | {755777FC-6215-430E-868E-B21D92A14A1A}
WILLITS 1104504 | {A1E50B4A-662D-4B26-9A77-844EAB929468}
UKIAH 1115CB | {A99474C6-C1F9-4A19-8465-2D8ED25CEFB7}
BEAR VALLEY 21014500 | {D468A32E-4500-4D2C-80DA-85F74A9A6EF3}
HIGHLANDS 110275140 | {D71C2E21-7CE4-4721-8677-0076FC6B52D7}
APPLE HILL 1103CB | {DD461B3A-397C-4A3A-A4DD-6F0A05715903}
COARSEGOLD 21045525 | {7CAE9E3D-9A6E-4166-92A3-E494C4AA002D}
HALF MOON BAY 1103880484 | {2C061CFF-5BC9-419E-A2B7-324612618450}
SANTA YNEZ 110488746 | {3F797584-019D-48E0-A377-BC3C335B4E76}
POSO MOUNTAIN 21011703 | {703579BF-EEA4-4200-951E-8470D02B6E41}
CALISTOGA 1102177784 | {854EA7F2-5906-4478-AEB7-CF15AD49AC3F}
CAL WATER 1102135060 | {A5C90C7D-4BB3-40A3-8AA7-071C177614C2}
NORTH BRANCH 110113496 | {931E0ACF-1FAB-493D-95FA-FA513D1003B5}
BIG BASIN 110212758 | {99A79B5B-089E-4FC6-A0B0-CC4BF6257CED}
CLAYTON 2217C500R | {2E89F027-67FF-4082-9169-E158A83D0166}
FREMONT 1104CB | {62124451-9B9F-46EB-B50A-534B1B0CB257}
PACIFICA 110252715 | {9452BDE0-DE70-4463-B819-B9B0CA79D823}
SILVERADO 2104CB | {BCC000F2-427B-4C85-BE86-EBEAE729A62B}
CORRAL 110112612 | {30A29F57-3EDB-40DD-A238-DD66DF206CFB}
CLAY 110113442 | {31882BA6-5D81-4512-9217-A61120B12235}
PUEBLO 210398394 | {49549F40-A326-4458-963A-8F0223D6E156}
GEYSERVILLE 110137454 | {8E06DD08-111B-4D73-B845-1ABBADC77B32}
GRASS VALLEY 11012766 | {9368A9FD-8241-4EF3-80EC-43B66D341976}
ALTO 1120CB | {D4FBBC03-A778-4C54-9456-3A890F4850F6}
SHINGLE SPRINGS 210511162 | {F8F7136D-4B7B-4975-BCB7-4503BD4299E2}
WOODWARD 2108441553 | {8314795F-0D04-45BD-AE69-B7277494B0E9}
SPRING GAP 170286032 | {17340C5D-4E9A-414F-A76B-922497EBB75D}
POTTER VALLEY P H 1105990354 | {18F7A415-6C0E-4E68-A9B1-1EAFDA3A8A3D}
PURISIMA 1101104948 | {9148C0D8-07A2-46DD-848B-3477C31F1CBB}
OAKLAND K 1104CR326 | {993BD642-B43F-4A07-B618-DAD20FD40FEE}
ATASCADERO 1102CB | {E22A44CE-34F2-45EB-BA42-C88A6CDC3537}
SAN RAFAEL 110168970 | {0E23B264-3DB8-4CEC-B1FE-F1CB20A30CF5}
PARADISE 110343008 | {5B855AD3-6AFC-4928-AA0B-CD83074FF6CB}
WINDSOR 1102596 | {59925254-34DF-4AF0-8CD9-F41C717859C6}
CAMPHORA 1101613562 | {C4E21E20-1077-4DDF-9A14-C3E5D8A4A595}
AUBERRY 1102R2850 | {CFE5622E-640A-4701-B25A-30E645D814D9}
TEMPLETON 2110317796 | {F014BBB3-CA2E-47B6-9852-740165FD3020}
ROB ROY 210512474 | {FFC04C14-5557-4FC3-9795-3587569ECB50}
WEST POINT 110234416 | {0EFB4216-A177-4018-B731-828073FEC64E}
HOLLISTER 21044046 | {38133BFE-606B-4796-A7F0-653C5DE724A7}
MONTE RIO 111159046 | {96597AB7-8D9B-480E-B290-054AD97D3E7A}
NOTRE DAME 11022420 | {1BA9278D-6A82-456C-AB93-CADDEAC99F13}
EEL RIVER 11024814 | {CCE91D7C-BCE4-4F01-BD5F-6C83E3A409D2}
LOGAN CREEK 21022540 | {8700E55C-38C6-41AB-AF2A-3B50EA0B2E05}
PARADISE 11032486 | {5B855AD3-6AFC-4928-AA0B-CD83074FF6CB}
TRES PINOS 11114064 | {68C1BEAC-9E07-4A35-9BA1-6FC5E18C5BE8}
DESCHUTES 1104622260 | {77B43BDD-8E2B-4B03-A902-769AAAC5407C}
JESSUP 1103CB | {995D3FA2-A637-43AE-9B3D-DDCFC4316118}
WOODSIDE 110179892 | {B37068EA-10E5-4EBE-BB13-FA7A8D9F573E}
NOTRE DAME 11042408 | {BE4941E8-75D1-4DE2-AD8F-78922C143536}
JAMESON 1105371694 | {CBED1D90-C1D1-43D3-861C-32471E7EFC40}
DOLAN ROAD 1101173702 | {F06F081F-C9F5-4637-B24B-42F86E64048D}
SAN LUIS OBISPO 1107834556 | {4DD1224C-2170-47BC-A673-A91A93C1B650}
SAN RAFAEL 1110189400 | {852F6C12-DBB5-4040-A2CA-B7AA0AE353A3}
CAYETANO 2109MR186 | {96E83343-B1D6-4373-84A9-0E60E5A945BA}
STONE CORRAL 1108CB | {9C22AB4D-7471-42A3-9430-CD197230D588}
STELLING 1110881330 | {BB7AB05A-F6F1-4C97-8DCE-5C8338B638FC}
ROB ROY 210512584 | {12D75819-A6BC-4E85-B057-219FF075B3A4}
GREEN VALLEY 2103283170 | {80B98B39-6C55-4280-B2BD-3BF57A0B5E71}
KIRKER 2103850957 | {F88B8CE0-AB57-498A-8D97-A3755A2B41A0}
CLAYTON 2211CB | {6C43A4A0-2BED-42F1-970F-3C9A6C36E609}
CAROLANDS 040387173 | {4FDA6CDB-0E5F-4B76-BABA-C5F84B9DCB82}
LAKEVIEW 11064796 | {81284E87-D055-48A1-8D04-42381F10289D}
IGNACIO 1105683542 | {BB37B807-9B57-4D41-8EE3-98B7B9A98DE4}
LAKEVILLE 1105CB | {F1AD241F-1F58-4A6B-9791-DB826ADDDA3E}
VALLEY VIEW 1103P156 | {6F4A4EA4-DB8C-41B8-B673-0FAE8635F67C}
PARADISE 11032534 | {5CECBD86-FB53-4749-ACB8-FF49C0BE2397}
FORT ORD 1101131442 | {66CA8537-4E7C-48FF-82D7-109E7EF7B7FC}
KONOCTI 1102532 | {43499343-6FDA-499A-9065-0F9A4F778AB9}
DOBBINS 11015202 | {65B27162-E2B7-4CEC-9138-2917B0C9553F}
ALTO 11221260 | {7808A995-1603-4DBC-94EF-C3DF7EAAE7DD}
VINEYARD 2110102887 | {14A8794B-8A75-4FC8-9957-3059A6D6C76B}
WYANDOTTE 1102CB | {835C2D90-E2D1-4649-9C53-DD5E51FB29AE}
SHINGLE SPRINGS 210819672 | {37338E68-AEEA-49C6-B1EE-76E1EAD86B81}
SILVERADO 2102808 | {F03C5A67-D53B-453A-A832-9C316BDAD400}
CALISTOGA 1101727772 | {15B270FB-A708-4F25-A097-2249C81A7EB5}
HONCUT 110137322 | {4580F407-B405-4F86-9F13-8318C1F1927B}
DIVIDE 1102M144 | {A0FD2E34-A735-4A8C-A9DC-394B15A3212D}
WYANDOTTE 1105329930 | {C09D41C2-6107-4911-B847-897C1DB6C91E}
REEDLEY 1112226548 | {C2478E24-1A2A-421D-B2B6-2DBB6FC30E5C}
SAN RAMON 2119107418 | {0CC5B62D-8E39-47F2-A113-AB2F434531F0}
SONOMA 1105575872 | {D464C20D-2D07-4CD1-B506-ECBC5597DD8D}
SAN ARDO 1102896438 | {2EE6ABE7-4F0E-471D-A95F-6A7A117EE231}
COPPERMINE 1104613086 | {3C011A8C-6358-4933-B5ED-50C9AF8F36E1}
MC KEE 1107XR462 | {AA6D8683-68CA-48B3-8BCC-B0F7A769A3DF}
COPPERMINE 1104556430 | {B8BBE87E-B0E7-4F0B-A461-482C2514F445}
TIVY VALLEY 11067210 | {D8E13D73-EB68-4157-8FED-21C11BDD3D42}
ARBUCKLE 1101932352 | {B2E83566-334B-4D06-8145-C26AD63C12BB}
GEYSERVILLE 110135492 | {A4A124EA-8920-4709-8090-23E3A2E000DC}
DIVIDE 110323614 | {AB1CE55B-42CF-42B2-8A5C-221DBBC685D8}
VACAVILLE 1109799940 | {D12E3D2F-1998-4DA6-942A-7BE316909F83}
PEORIA 1704CB | {57BF0C33-990B-4465-98B9-17EDC5A10F72}
LE GRAND 1104RUSE | {2DA20832-0986-4675-BA93-1E55E4E2B6B0}
PUEBLO 2103329486 | {0A48EF8D-B34A-44FD-9901-4812541B4E91}
OAKLAND K 1101CB | {BAD456A1-64C0-4C58-9244-4CB0B49EFF5E}
WOODSIDE 1104CB | {C0699A77-D9F1-4326-8400-EC5E43167E10}
OTTER 11022166 | {C47B4B77-9CC6-4665-96AD-097EBCE52988}
FORT BRAGG A 1104872358 | {F09AC1B9-9514-473B-B8B0-A2B230C8B557}
HALF MOON BAY 1103623460 | {1E711061-9006-460A-8EEE-DB532A4DAE2D}
GANSNER 1101336664 | {13627031-EE44-4823-A048-AA36CB9BE013}
OCEANO 1106CB | {2FEE1CE0-BC95-467C-8CDD-CAD4D3CD2579}
AUBERRY 1101R314 | {4F5EBE36-6D68-4A47-AF49-0D6F0830F1BC}
FITCH MOUNTAIN 1111821431 | {85F11AC0-E7F5-415C-8928-2202FEFE7CC2}
AUBERRY 1101323028 | {90ABCC1D-5DD8-43C1-9AC0-715DCF2D275E}
SANTA YNEZ 1102CB | {248D5525-98DB-494D-8A88-8F5511E7C8B0}
LAMONT 11044575 | {28DDAF39-AE68-4213-B81B-B1ED800C91E5}
NEWBURG 1132CB | {2C9C3EB7-00FC-4934-A962-9B300983DC9F}
STANISLAUS 17011812 | {34B1CFFF-1F43-44C3-AF15-E50BDC16F6A4}
GEYSERVILLE 1102501402 | {450BD680-08E6-46D0-AD80-CB37688E8C0C}
HALF MOON BAY 110258448 | {51B7F99B-37F1-44D1-A380-3A17DA62C971}
ZACA 1101CB | {84844AA6-33FE-4B77-BE7F-2142383F94DA}
DIAMOND SPRINGS 11057722 | {9B3053D4-0FCD-415D-AE49-1C1AC44BB827}
CAMPHORA 110122412 | {3C98E34E-9E87-4EA2-902E-6CB817DB7650}
CASTRO VALLEY 1110MR748 | {C6807FEA-40B3-41BE-80F1-095A0F67FBA5}
WEST POINT 11024790 | {4C31F9F3-FF43-4013-B249-266EFA0B514A}
COTTONWOOD 1103CB | {7A360B24-DB74-4302-B7FF-A7991F9BEB20}
OCEANO 1102749231 | {8546FDA1-23F8-40F3-9B1E-5EFFE01FDD01}
WOODSIDE 11018912 | {429461DA-3754-40D0-8283-6B07C0ED0208}
WOODSIDE 1104555372 | {73C37461-BB3B-432F-BC96-82FA7CA2E859}
NEWBURG 113277894 | {80EB220B-EDCA-49B1-8388-856A3CF42050}
MADISON 210134164 | {C4B928B0-1315-4EFF-A9DD-F47090119304}
ELK CREEK 11012002 | {E8F1018C-E626-4FA1-B3DB-30BAFE068623}
BRUNSWICK 1105875388 | {12398A09-47B6-4618-B7A8-07F9B9DF4D2E}
MIRABEL 1102334 | {0A4816B0-BB69-491B-8E9D-476A9DF6F15C}
LLAGAS 21014523 | {4A87133B-C25C-4081-8935-66AE4E30F1EA}
HARTLEY 11014710 | {801F0074-FB1F-4C52-9EC5-EE9281D564FB}
TASSAJARA 2108954811 | {F949AA4B-CECE-442A-AA8D-703A33BB749B}
COARSEGOLD 210210330 | {FE7641C5-7812-4FD4-8B21-6308923D8DFD}
BANGOR 1101870548 | {16EDAC9B-8C49-4185-9FE4-CF4748324FBE}
EMERALD LAKE 04028872 | {18156E3B-3444-414F-97B1-9EC6878D0720}
PEORIA 17056697 | {50E0B9CF-D877-44E3-8923-B1CAE75FDAA7}
CLARKSVILLE 210951796 | {4682A97D-092B-40D3-AAD7-69641B1B3CC1}
PANORAMA 1101713592 | {70311009-6B82-4803-BF61-8884A737A669}
PAUL SWEET 2108467366 | {62614D7C-C46B-4061-8F81-503DEACC476D}
MARTELL 1103CUST | {4DC1CEF2-A050-43F8-AD47-CFA46D056F9F}
PAUL SWEET 210875588 | {62614D7C-C46B-4061-8F81-503DEACC476D}
MONTE RIO 11131067 | {3F69DD3E-C46A-485A-8A4E-8252A760746F}
PASO ROBLES 110638682 | {931CA1B4-3667-4C96-9792-EB8AF0018AF4}
LLAGAS 2101XR586 | {07E209B8-80A2-40A5-8228-12D4DFF42801}
VIEJO 220285904 | {2C01517C-E612-4085-8398-17DFB2943C5D}
GREEN VALLEY 2103478624 | {80B98B39-6C55-4280-B2BD-3BF57A0B5E71}
PASO ROBLES 1107164828 | {BF9A1CFA-5044-466A-9DCB-672D048DD99A}
ELK CREEK 11012106 | {9C349921-70C5-4A1B-82FC-D82E641B2142}
COTATI 11052121 | {554E4D6F-0779-4CD2-B95F-DB489BEA9C8F}
SAN ARDO 11017632 | {05828C1E-8E18-466B-88E7-9FC0E3CD182B}
ROB ROY 210410714 | {0A7E84D0-9946-4059-AC56-BD0EC9107E3A}
FORT BRAGG A 11013100 | {0D62503E-67CB-4A8E-BC3C-093230B8FF31}
SARATOGA 1107CB | {1EECCE5A-2560-4A1B-BCA1-BF5B03357FA1}
GARBERVILLE 11028652 | {56012ECF-3863-4B00-9D44-45818E54BBA2}
FULTON 1107145720 | {6604208B-F35A-44BE-998D-E714E06DE284}
CHALLENGE 1101CB | {6A653745-C5CA-4E78-9C62-82F0E53CCD59}
ROSSMOOR 1102CB | {92F6E341-F0BC-4716-8F01-EF905EEF4BF1}
HIGHLANDS 1103CB | {F4CEECFF-9688-4F5E-82B6-98F3F42878F8}
ALTO 1125CB | {F6FBF85B-F199-40F3-8A70-868561B74EE6}
PINE GROVE 110194936 | {0F46298C-BD7C-494E-910E-FE65C6C90770}
SALMON CREEK 110188998 | {2FFE3F5E-20F1-4C4A-B741-4DF0040A4D91}
HIGGINS 11102408 | {71CA17E4-B079-4EB2-8611-562BAD82EEBD}
GREEN VALLEY 210310932 | {71F18CE4-D284-4752-9621-5F4A7D3D2F8E}
TASSAJARA 210791094 | {9BFCBF13-2D3A-4A17-97C5-BD97C03AE6D0}
MADISON 2101351038 | {9C777D0B-81EB-422B-9E3E-C0277E2A4B3B}
SONOMA 1104914376 | {9E74C19B-FD10-4380-8F7F-0DF0A358D1AB}
CORTINA 110137554 | {E3B77E93-BB57-4588-891B-4456F675EF56}
RINCON 1103925054 | {A6030DDB-D47E-40D8-89FA-641FC9E29ED5}
HIGGINS 1107836688 | {B73B7429-00D8-4172-979B-F99C3A58EB55}
NARROWS 210551582 | {D508D44B-0B7F-43CB-B9DA-F37161CA8F62}
LUCERNE 110647198 | {DA9B8D37-5C46-437A-B55A-1CC1BE987A25}
SUNOL 1101MR297 | {144B98B4-D8D8-4444-BA16-D1CC613F7105}
SISQUOC 1103858898 | {258E8CE1-3F22-41A9-95CF-5107746239B3}
IGNACIO 1104CB | {4117016E-C4E1-43D1-8702-FC75C137797F}
CRESCENT MILLS 21012562 | {50FC30D9-9631-47C1-AB52-87E3C16BC0D9}
SAN LUIS OBISPO 1101CB | {AD6746AA-B778-4E12-B7CD-DBCB8C9B3412}
SPENCE 1102321000 | {E93A7BD3-7283-4B37-990A-F7132697460F}
TEJON 1103145334 | {13DF9C76-E2F4-4659-999F-3B0C5114903E}
OAKLAND X 1106735592 | {FEA3C3F3-959E-472A-9376-926585E20D05}
EL CERRITO G 1112BR152 | {7A0FE4A4-8FE2-4A7A-9013-EEA423D246F9}
PHILO 110137222 | {B4EDF571-A5E6-4473-9456-D58C67AB0D1F}
COTTONWOOD 11011510 | {DB300DCA-6215-4B3C-914F-828156445EA8}
SAN MIGUEL 1106CB | {DC9AC6DA-C366-497D-A431-13D5888CCACE}
CAYETANO 2109MR198 | {DE685544-4F9C-41AF-85C6-DB5D3F282705}
SHINGLE SPRINGS 2110CB | {064C2459-8C22-4F74-A2C9-18905DBD3086}
CAMP EVERS 210616000 | {1BABBDF2-DCB6-4552-BE33-67EDAC391159}
TEJON 11023760 | {6C424A0E-18F6-4E95-BDD7-E63E2F8C4F83}
MEADOW LANE 2106CB | {71331D65-41F4-43C6-916A-15339389D82C}
BIG BASIN 1102CB | {7DF78B7A-3D58-4011-B365-74BA17A842F7}
TIDEWATER 210665866 | {2DE5693C-879D-4FCD-88B6-818902BD649A}
LONE TREE 2105708440 | {9DEE5B21-E20C-4F89-8E48-13FACA2394A8}
KIRKER 2105A536R | {EABC5EEA-8AF0-4E4A-8184-A7D17C84C76E}
MARIPOSA 2102594143 | {D6398899-238B-49AC-A776-D1F3468DFF9B}
RED BLUFF 11011556 | {4D690574-08A4-46C5-A589-9057A98DE023}
STONE CORRAL 1108001 | {9C22AB4D-7471-42A3-9430-CD197230D588}
DAIRYVILLE 11014679 | {7E805BB6-FA35-4404-BBBB-4801C3E98DDD}
SONOMA 11033138 | {989A9D45-A06C-4EF7-99F0-5A8D5A73FF7C}
MARTELL 1101CB | {2C34AC51-01A3-44C9-B45A-F5786A7BA8F0}
ARBUCKLE 110447282 | {44D6ED2F-777A-4FEB-A593-3F9A2FF8D4A7}
LAYTONVILLE 11011760 | {54DB955F-557A-474F-9DB9-2B3A7068B309}
HALF MOON BAY 110264293 | {AE99FE40-5E2F-4EF7-A496-F7D5D1016060}
SAN RAFAEL 11042235 | {33CCC2F4-F827-4C07-9171-27096EF33E3C}
WHITMORE 11011598 | {0A7498D4-3D67-421B-B0F9-EE472ACD2B71}
FORT ORD 21059140 | {29DAE9CE-CAE3-4935-AB0F-06DB01859441}
CLEAR LAKE 11024708 | {7C347C2A-D137-4C7B-9A15-013D3BAB11C4}
EDES 1112417626 | {8BEFF91A-7C09-4291-9AE2-AE9219165D14}
JESSUP 11019752 | {A6F4671E-7001-4E04-8749-D198C4CDD6BE}
DIAMOND SPRINGS 110699658 | {AE525890-6C02-4814-857B-4FEF1E7D58A9}
PUTAH CREEK 1102CB | {EC7E3E82-534C-45F0-825C-A06402B7C3CE}
CAROLANDS 04049026 | {EE04BD96-5787-4D66-B00B-BC1201689111}
CARBONA 1101CB | {03E03B20-8D28-451C-9701-95F4851E85CE}
HICKS 1116LB16 | {128CFE15-7FAD-449A-AC53-530ECD1ABDFD}
REDBUD 110191960 | {44037CD8-DFED-4315-85FD-100A68145FAE}
HAMILTON BRANCH 110187784 | {512E7C3F-C5ED-477A-A43F-85AACCF18F8D}
FAIRVIEW 2207CB | {659FD2EB-053C-425F-AF25-D9C58353B44F}
PLACERVILLE 210692012 | {C89C3F78-8047-4151-A21B-FC3CD22D755E}
CUYAMA 21021000 | {78102D0F-3634-4153-BADD-EC52C2E98E32}
DIAMOND SPRINGS 1104147386 | {6872443C-7FE4-416F-92B9-65D58A293737}
COTATI 1102825 | {94E0088D-6FDA-42A4-A01C-471E05EB28CA}
PUEBLO 1105716 | {A6A5315D-8A62-41D0-A9DC-ABFF612B9C6E}
RIO DELL 110270960 | {B2A085D5-4C4C-4026-B04B-46CF38E6CB2B}
SYCAMORE CREEK 11112268 | {BCBFDCD7-6D09-427B-8565-FE77C2D532E0}
PARADISE 1105121988 | {BE2BD7AC-D920-438D-9D8D-1EC5AAEC4CAF}
SHINGLE SPRINGS 210851474 | {D915D781-6781-4960-807E-BD1A4FE75E6E}
HIGHLANDS 1103568 | {DE7AF2D5-E911-47A4-AE78-DD80A28A5D4B}
DUNBAR 1102261774 | {04FFFA70-53BF-428C-99F6-1A2E798AF420}
HARRIS 1109CB | {0E899392-4139-4EF4-8C02-780C18A47141}
PUTAH CREEK 110264044 | {17B7D6FE-5F00-4D1F-ABC4-4972705BA2FB}
BEAR VALLEY 21054170 | {ABA71BA3-C71D-490E-AEB5-C37239F168A1}
LAKEWOOD 222464093 | {6C96515F-B6CE-4B5E-91AB-166552C2F0C4}
BRUNSWICK 11052100 | {EB9602B6-3B78-44B7-9264-163222D3097C}
ATASCADERO 1103A80 | {01E75A4D-5E59-4C31-876B-BB494E0AE408}
OREGON TRAIL 11021382 | {5E999E0A-FF01-4E2B-B970-E4BD7149EAE7}
FORT BRAGG A 1102956 | {63294CD0-4D7E-4FB1-9784-991B87B370C8}
CURTIS 17026008 | {B65A3679-2982-4589-9816-E14BDF4C9657}
FITCH MOUNTAIN 1113482752 | {BE29C1CC-62E1-4311-8E3E-30A3FF867046}
MONROE 2103CB | {D546C25E-2665-4E0F-83E6-19A6D0D70A7D}
BELLEVUE 2103CB | {D7E9D0AF-E912-4093-ACB1-C01E71ABC496}
CLARK ROAD 1101CB | {F673F67C-7B92-4672-819A-41DD2FB01076}
PEORIA 170176030 | {CF97D77D-981C-448C-B149-87042BADEDF7}
LOS GATOS 1106917258 | {F0513295-9AFE-47CC-93E8-DF299D8C11AB}
OAKLAND X 1104CR022 | {2A115028-6F68-4B14-BB47-6F364E8C5941}
OTTER 11022012 | {5B008FE4-7524-4C11-8819-B0F9661FD099}
FAIRVIEW 2207M520R | {659FD2EB-053C-425F-AF25-D9C58353B44F}
NARROWS 21052216 | {94CC379D-BE20-48E1-8496-01F284C7FE9E}
COLUMBIA HILL 1101764 | {9DC430E4-865B-40A1-B9ED-F689C9145BC5}
NARROWS 210551580 | {2611646A-C593-4185-9486-0AA063D164D0}
PEABODY 211375820 | {463CEDCD-A864-4BE7-A495-4562C479EEC4}
MOLINO 1102658 | {F138D9D4-46B7-40FF-98A4-3E0C55CB9A57}
MC ARTHUR 11011546 | {F58DF78A-C4B0-4969-9413-98D7022EFF8F}
MOLINO 11015034 | {5092CF9F-9D4A-405D-A02E-8142B89FC3A4}
ORO FINO 11022556 | {6018A7D7-F178-44F7-B593-CA41A45039FD}
HALF MOON BAY 1103531594 | {F951C9B5-DFF6-4F18-959A-6543A104D243}
CALISTOGA 1102131531 | {9728A510-4796-446C-AFFA-E71EAF88F06E}
SAN LEANDRO U 1109936988 | {0A0CA719-3BA2-4B10-8DAF-28B4D94E2A5D}
ARCATA 11224218 | {BD7155EF-64EF-4144-9B75-F7FC5FD58146}
TEMPLETON 2111R86 | {C1DF3268-8D83-469E-AB38-F1D09D72570E}
PUEBLO 1104105708 | {F4390A92-E1EF-4E00-AAD7-21DFA3AD530E}
CUYAMA 21013542 | {F9E131D2-E655-4DF9-A7E0-8C8B213A0782}
NOTRE DAME 1104937710 | {3CF079B2-DF24-4674-AF57-026F1C1899BA}
MENLO 110358562 | {7E0C3FCE-17F5-4308-9D58-E63D0E2C9C4E}
CORNING 110193362 | {A9C774C3-1428-4B46-A99D-50AD5766C649}
JANES CREEK 11044844 | {26E770F4-F25D-4CF1-B69E-D7AF03209DEC}
JESSUP 11019002 | {94370961-147A-42F3-9849-8A0C21F665DA}
HALF MOON BAY 11036014 | {C9FA3CBF-AF0B-40A6-8062-0EE0474AC48A}
PINE GROVE 11023172 | {0A126708-7779-4E45-A8D5-6CB2B8C285C8}
GARCIA 0401666 | {2B626DC9-13BD-4F58-BFDD-9C1FE143AC91}
VALLEY VIEW 1106865650 | {D9DED303-0FA6-4611-A466-91E33B741947}
SAN LUIS OBISPO 1104V10 | {553967E8-15E4-4695-8C2C-6D609687BE1B}
RESERVATION ROAD 1101CB | {D8F287F2-9F47-4079-84BA-BB2B78537313}
PIKE CITY 1101CB | {1B4AEF1E-3888-4CF0-B5B2-91A85959940F}
LOS OSITOS 21031132 | {4039D191-A1E0-4943-9C3A-CC09D2E36841}
MARICOPA 1101931236 | {4BEF20F2-8B61-45E8-BE0E-DD28930DE8C2}
GREEN VALLEY 210110976 | {5C8DA4CC-DB0C-4E65-BF7D-024442DE4F36}
SONOMA 1106CB | {80158D87-8FBA-4904-925F-F73ECFE1E50A}
WYANDOTTE 11095973 | {10790C99-0AC4-4885-95AD-50DB99DD62BD}
ROB ROY 21058281 | {ABFDD865-4FD2-4A37-B95C-CF3A9E9EFA30}
TEMPLETON 2111A66 | {CD2443C5-9F0F-40FA-9737-DB91D76D5878}
OROVILLE 1104CB | {DF8BB72F-C21D-4A12-8CBC-5B84FF3140AA}
GREEN VALLEY 21035140 | {80B98B39-6C55-4280-B2BD-3BF57A0B5E71}
ELK 1101900 | {32CDF0E8-BDA5-4E37-8B42-CD1492E2A580}
BURNEY 11011322 | {A45048C4-5E06-4803-9C40-C46808E3753F}
MILPITAS 1108XR122 | {AD2D545D-446E-4C20-A74F-6B44E5722705}
PAUL SWEET 210855904 | {62614D7C-C46B-4061-8F81-503DEACC476D}
COTATI 1104CB | {D0082608-F94E-4A4E-A9EF-A114F6AAC5C3}
KONOCTI 1108950 | {D3BC4C4A-6AD6-4D57-ADFE-ACA0E6607A3B}
MARIPOSA 210110070 | {26575688-884D-4CC7-8C04-F1F692E3F0D5}
BUELLTON 1101Y26 | {4514D6A6-77B8-4164-AACC-ADDF4E8C95FD}
SONOMA 11033052 | {4B7DC187-5EE3-45A7-A2F4-3F80A5EC9C80}
CAYUCOS 1102CB | {80B87962-AD85-4936-A71D-968069A54623}
PLACERVILLE 21069712 | {C89C3F78-8047-4151-A21B-FC3CD22D755E}
KONOCTI 1108CB | {E3192F4B-E306-4B2D-9341-C84584505AEB}
GABILAN 1101989608 | {E7781237-9688-49BD-8E68-B925FC8E3926}
SILVERADO 2102922022 | {11969599-658C-4879-9EBE-BD3B4F21FB32}
BEAR VALLEY 2105CB | {3A07F3B8-E9B8-45C5-8744-6792C16A4186}
WILLOW CREEK 11033090 | {999C3E0D-1E31-46AC-B115-3B4EB4A2A32A}
OLEMA 11011200 | {A8B14B0D-3BCA-44F1-B75C-F9F858D43D86}
HAMILTON BRANCH 110137534 | {B799CE92-A5F5-41AF-A189-4F32E6DC30EA}
BRUNSWICK 110584480 | {EB9602B6-3B78-44B7-9264-163222D3097C}
FITCH MOUNTAIN 1113775992 | {D0DDB5C0-186A-4907-865A-9BE93C7A605E}
PUTAH CREEK 11033783 | {520DA4C4-E38A-4EBC-850C-F11EB0848411}
LAURELES 11112028 | {F252A13D-948A-43C3-954E-C03439B944E1}
TASSAJARA 2108437582 | {D91BF138-6798-4927-88BC-C1A382D4C37D}
CORTINA 110130262 | {30FD709D-FDD9-476F-A094-8F17316D4F25}
MESA 1103198354 | {E778BF74-7BEA-4E28-9448-C0888C04BB6B}
PRUNEDALE 11103716 | {7B756F98-069D-434F-A340-DDF69576DD23}
ELK 11014628 | {894D739D-783F-4BF2-8769-235C809A09C6}
DUNBAR 1102694641 | {9330F6B0-760C-4338-A4C1-C3EAEF5F2D51}
BRUNSWICK 11032784 | {A034BC39-5C36-44F2-830F-5D5EFC9DEDAA}
COTTONWOOD 11039072 | {CCBE325F-DB08-456F-8920-C4494B0832D2}
UKIAH 1113548420 | {CD90789A-8C40-4BA6-B727-13DE18B4CBFD}
POSO MOUNTAIN 2101720132 | {D06620A3-21E5-4CBD-8A5D-D10ADF106C84}
PUEBLO 2102595938 | {3F0F141A-08D9-4BE0-A763-3CF7287B44A5}
EEL RIVER 1102680 | {4D91C2EE-0E70-4830-92FF-2507FF07CCFB}
CAROLANDS 040197209 | {542C89B5-8855-4F9C-96E0-4B73D5C44BAD}
SHINGLE SPRINGS 2109CB | {8CA8A29D-825E-4F83-82F2-58C55E66E077}
LAYTONVILLE 1102500 | {9FACD320-0A6B-4701-A9D9-81FE9755F114}
PINE GROVE 11021222 | {B84BB2A7-38F5-4777-ACCF-AE61211F946D}
BIG BEND 1102884340 | {DF76653F-9A84-406D-B399-26AC3048352B}
BRENTWOOD 2111CB | {E5AF8736-114E-4C01-9F04-EE6BE2C6FDFA}
SILVERADO 2103617828 | {F7F03C40-551D-4024-8031-59C5BBC7C6D4}
RINCON 1103472 | {003E8DD3-C7CE-4179-B86D-B637E24AA54E}
SAN ARDO 110283166 | {A30EDBA7-9AAC-4E4B-A35C-8F3268903239}
CLAY 1102CUST | {D868AF66-93C2-4B3E-8187-2C428023C31E}
JESSUP 11031540 | {47DC31DB-63D1-4B41-9B4B-82351A2B9DE8}
ANDERSON 1101909424 | {4FF91FEF-C966-4E36-B08B-C812EFC4BE16}
MESA 1103M68 | {A25F3E5B-484A-4624-AB7F-2585CAD6EACC}
SISQUOC 1102M26 | {92EB9460-E02A-4A24-A181-995BD1F9489E}
HIGGINS 1110861610 | {C6E8B2FD-D557-459C-B9FB-FFB281472FF9}
FRUITLAND 114293234 | {F2F5CD46-ED54-485C-8E9F-F1D6186FA89B}
ARCATA 112233060 | {21ADCA93-F696-42D2-B9AB-0580CBDEB386}
PENRYN 110651674 | {2BBB97CC-A78B-43EC-BEB0-66A2E29BC2E3}
PEABODY 2106CB | {369633AA-CFA4-4128-87F4-3265F391CCA6}
POINT ARENA 110137426 | {92C865B2-0C37-47A7-A1CF-103D45B5F3C3}
SILVERADO 2105268508 | {AA30177A-A383-43BF-A978-435A7E84A10D}
MORGAN HILL 2110716210 | {FEA8F80B-51AF-4084-A9B9-47D11430DD95}
WYANDOTTE 11071026 | {F4C4052A-4712-4518-990B-FE0E43960860}
FLINT 110140666 | {F60C4C6E-928C-45EE-B5E3-FE18B260D743}
JESSUP 110238330 | {05EBFD7E-35A6-4E40-95CF-51485C56D3C6}
ALLEGHANY 1101CB | {326E3BAE-F690-4463-8FFC-C774FBAA59CE}
MESA 1103M70 | {6E34D557-FB41-44E6-B10D-DE75166431A4}
CURTIS 170411290 | {5B03EFF1-F12F-4656-8D60-84D55FFB9841}
PACIFICA 1102968736 | {6BD2C65D-7217-43E0-B7BC-E7737DB1CECA}
CORNING 110185152 | {789DE4DB-ACCC-46BB-B059-D9142CE79F75}
SILVERADO 2103920793 | {86671C53-A1BD-408B-B0CD-99AC0557F97B}
PENRYN 11052406 | {A6C70D14-E593-46FB-BE1A-9881978863D6}
LAKEWOOD 211021345 | {B6F65C5B-8596-4980-BF5A-72D64E484475}
MORAGA 110183424 | {E1CFB432-A326-40CC-8BB1-1B7A06DF46E8}
SAUSALITO 1101221834 | {89972505-5E8F-4A2D-AA5C-D59B16608028}
SNEATH LANE 1106CB | {66ED3CF0-2002-44E6-BE2F-18363B4298A8}
MILLBRAE 110465748 | {78D6C5D5-9F2A-45C6-A0D6-6C9E91038F45}
SAN ARDO 110273254 | {DAB3BC36-43FB-41D1-88AE-89CBCEF6CBDB}
SISQUOC 1103M14 | {BE479CE6-8809-4A3B-A6FB-86A2FCDE06C2}
HARRIS 11087920 | {9A3D8818-9236-4C74-9C67-0369FA031A48}
SUMMIT 110148632 | {CD142DCA-BFBC-491B-9C29-D02961854E56}
MOUNTAIN QUARRIES 210151584 | {0BE1E4C9-DDDF-49C0-980B-2AA7763D326F}
STONE CORRAL 1110975698 | {475C3D60-9DB4-42CF-BD54-DCB20C6AF853}
MILPITAS 1109903328 | {6577B24E-0FC5-4239-89A4-458F673DCDA9}
SANTA ROSA A 1107CB | {66A6713B-EEF9-4672-883A-89D2D2628FA8}
BUTTE 11052576 | {9A0BA931-124F-4B29-B938-98D870112FD7}
RESERVATION ROAD 1102303870 | {EC6A2D53-31D4-4E66-874C-302D8025180C}
SAN RAFAEL 11011250 | {0DD641FC-11BF-40FB-8EF7-3A88160AB0B4}
PARADISE 1104920400 | {1341CA63-432E-4CD8-BB46-467A27C9C55D}
JANES CREEK 1104CB | {74133F88-7C2E-41BF-994B-5D7BF579CEB8}
BEAR VALLEY 210538882 | {C5D51BCC-B370-48A3-8349-FB710857EC4B}
NEWMAN 110590430 | {AD5BB80F-100E-443D-B968-9FD3EF2DDDC6}
EDES 1112CR282 | {C2D0F25E-59C9-41E0-A6F7-60C91C33934C}
OAKLAND J 1105153228 | {FD68B15D-2380-4995-ADA8-EF407A4F9E9B}
SAN CARLOS 1103586832 | {976CCE27-9CBA-45DD-8002-F8BFB98C14D4}
HORSESHOE 11011682 | {346A62D2-9F89-49F3-B966-B00C57570576}
BUTTE 1105751990 | {EA7C07F2-4273-40BB-B6F5-36B0C70D1D31}
FORT BRAGG A 110195294 | {68CC0E2F-7024-44BE-85E9-7639B7540AB9}
FLORENCE 0401CB | {9898F55D-4181-4FB3-A3AA-B13258B3B860}
HIGHLANDS 110265650 | {D6E00327-F4CB-4F20-A907-68904C3BB997}
COTATI 110578286 | {E3F3EE76-01DA-4EFD-A1DD-D7EE0921249A}
MIDDLETOWN 11021312 | {EAE1C088-E6A0-4B00-80D2-C64BBF575702}
SAN RAMON 2107MR284 | {1E4505DC-D80E-4F9F-A5C6-1B2DD1F7142B}
PENRYN 110550550 | {38FA411E-5935-4516-9773-4CAD949A1A2A}
HOPLAND 1101558 | {7D091198-DCC2-4EA1-AD83-C691E4F808C9}
MOLINO 1104186 | {95E199CC-8537-4A38-8A02-CCF54B07F2E5}
SONOMA 1105404 | {A0925B55-2E02-42A8-B141-C53A4CA4086F}
WELLFIELD 1102CB | {B75AE0C3-AE32-4560-9D2E-0C12544F84C7}
BRUNSWICK 110756240 | {779A3152-24AF-4508-86CF-CDD542CFE4FC}
UKIAH 1111422886 | {2D399A89-FF4A-4D16-963F-99FB5F6695E4}
KING CITY 11037038 | {6DF33D7E-A953-44F1-82DC-C36E39D2281E}
TEMPLETON 2109R52 | {881400C0-59DE-4789-9E3A-A9795EA7ADF7}
LINCOLN 11042072 | {A71D3F90-1807-4414-8E54-A388088D7CB1}
MONTICELLO 1101654 | {11F49F82-D386-49B9-BCC1-D0FA0566ECA0}
BELLEVUE 1102182 | {2902212F-4C02-4AB4-BB89-DFDC181B544C}
CALISTOGA 1102769230 | {2E19A9CF-57F8-4CF7-B698-92E35CE7A12C}
COTTONWOOD 1102CB | {7F728486-5D30-4578-BA26-525DB688C650}
COALINGA NO 2 110541954 | {90AEEBB8-CCE7-458F-AF2F-7D8FEF1C57D6}
DEL MONTE 210332886 | {95BA16F1-C0BE-4BE8-9C3E-AD056E7BB712}
CLOVERDALE 1102736078 | {BF061E01-5578-402B-9978-43AB1F8350D8}
SONOMA 1102113082 | {4BCD6EE2-7FEC-4152-907C-A38A16D3BF51}
PIKE CITY 11011720 | {07E52C28-7426-408F-9FC2-C4593A9ACBA6}
SAN LUIS OBISPO 1107136678 | {20AA80FC-38F3-451E-A79F-A0EADE4A8B5E}
SARATOGA 1106LC24 | {27F30433-27B7-407B-8F57-C7D8C59F953A}
TULARE LAKE 110876864 | {7219D019-06C4-402F-BD2E-8145F907D9F0}
SANTA YNEZ 1104512912 | {7679D85F-4172-4810-B5B5-B8198D816699}
VINA 11012681 | {427F674F-2998-4807-8909-FFE2EF8784B5}
SANTA ROSA A 110432180 | {B37312AE-80D7-4090-A893-C81D3025336C}
HALF MOON BAY 11029114 | {EC65686F-B15A-4CBF-8005-BF1274876E69}
HIGGINS 1110CB | {E56A3B9A-F6B2-438C-8FDC-DFADF12A0423}
LAKEWOOD 210738404 | {E6E0CE7A-9AFF-4A02-92C6-B06263224357}
JAMESON 1105913400 | {E925FB90-0D67-4350-9303-9E202A799552}
FROGTOWN 1701L3361 | {32DE7714-2265-4DEA-9044-817FFC428BF4}
ANNAPOLIS 1101528344 | {7D61C9A3-0A8E-455B-9684-CECD384B35D0}
CLEAR LAKE 1101529830 | {91E6CF65-65E6-49D9-99AE-7F739C671773}
CANTUA 11019880 | {B55C2E19-B2B9-47FB-B0FA-5E9F76A070B4}
EEL RIVER 11033820 | {A8C66523-6BAD-4410-B093-1D69B3A4DEED}
VIEJO 22029118 | {BA7590D4-FA7A-4E66-A4E2-9385E2F5FD08}
FORT BRAGG A 11041316 | {BC4F0196-621B-4CEE-9F22-55FAA9EB12A8}
HOLLISTER 21044782 | {C12B46D7-11F2-4E48-9DFC-9E2CC790DCEA}
PUEBLO 110447912 | {C8E61154-612A-4546-9186-D3C997DC10CD}
TIDEWATER 2104226374 | {19823827-C5EA-4E2D-9FF7-7BB963BC816B}
OILFIELDS 1103N48 | {63E72A21-A36A-4936-B748-71270400CC57}
GEYSERVILLE 11014570 | {7BF9631F-F2B9-4D9F-A7A1-8FB9FBCDDF84}
PAUL SWEET 21045394 | {D6E3B990-3B6A-4843-9D6C-590EB1D40E85}
TEMPLETON 2109R92 | {03B90DE8-00D2-4B58-B65C-ED90C57EE070}
NOTRE DAME 11042537 | {BE4941E8-75D1-4DE2-AD8F-78922C143536}
MARIPOSA 21029590 | {43662797-F521-40C6-867F-8BCF69F03BE0}
NOTRE DAME 1104CB | {4C7176B3-82BB-4EC7-9074-E6E03166E224}
TIDEWATER 210618982 | {2DE5693C-879D-4FCD-88B6-818902BD649A}
PUEBLO 1104580658 | {9B7A438C-25F0-43CD-AA1E-F241960C452C}
WOODSIDE 1104456052 | {B5C1CCF7-3737-412C-9D78-BAC61B5ECBAC}
BELL 110950520 | {C66EE736-987A-4FEF-A8AF-F6DA5647068C}
MOUNTAIN QUARRIES 21012422 | {D7F1D14A-5B2A-48EF-B12A-9197AE3BCA5E}
OCEANO 1104CB | {EF084BAC-E8B6-45D7-885C-1A50430DEB23}
CAMP EVERS 210392582 | {FE8FB0E1-1FAA-49D9-87B9-90771C18AB33}
MARTELL 110191216 | {111B8F03-A7A2-4ADC-B553-BFBB68F5B187}
PLACERVILLE 1109868678 | {C4A51841-0308-49DA-9C27-2509F9C64A2D}
FITCH MOUNTAIN 1111752596 | {1E79F907-28BC-4BCD-8BF6-A38789A74B9B}
CLAYTON 221296224 | {3D0FC142-36D5-4662-84E1-74BFFF12E068}
ALTO 11251256 | {68422AE1-2121-4A4F-B961-26CF0C3DA27B}
FULTON 1102CB | {6ABCE308-047E-4F2E-99AB-65F7E6BEAD99}
SAN MIGUEL 1104CB | {D0F2F587-0747-4792-A057-16325E08E5A6}
PIERCY 2110XR258 | {EB657CB8-596F-4421-86E3-2C8A72D44EE1}
HIGGINS 1103995672 | {FCC40ADF-1FB7-4F80-97A9-6981FCDC8244}
OLETA 1101CB | {3D156343-1F71-46EE-A300-26BD3EB64071}
BUTTE 1105134600 | {4548E819-63FB-46B6-BCF4-A22534DF16A5}
FULTON 11025102 | {A7116264-DEE4-49AB-8F9D-DDEB0877D031}
LAS GALLINAS A 1107CB | {920034E3-10FC-4029-9455-A3F8C0B7BFF2}
TEMBLOR 1104CB | {C2992F46-2554-463F-8E87-219C3C230B9E}
HOPLAND 1101865263 | {CA6D1DF8-31DD-4CE3-9F89-D88B37750187}
MAXWELL 11053008 | {3FFCF8AB-2F3C-40D6-BE9B-68EE284722AE}
RINCON 1101580 | {45DAEF94-8CBC-41FA-B3AC-23C4DF1DF209}
PUTAH CREEK 110246012 | {8A0CE410-7B0B-44D2-93E6-B3B628B03752}
OCEANO 1105V44 | {CED5D6B7-0919-4723-BD8E-41D37DAA2E37}
MOLINO 1101CB | {F8D0A5CD-F859-4FB9-9BDE-10A27882B6F9}
FROGTOWN 17027134 | {0486726A-698F-459A-9224-3E1921E2AC68}
VIEJO 2201563516 | {DE1EEE83-8C6C-447F-B024-0ED2E3DD3250}
DUNBAR 1103234 | {E64AC1A3-7B00-44C4-B413-8ED8E1419B88}
OAKLAND J 1105CR256 | {FA7AC1D5-82AB-4E51-B874-C59D71756955}
WOODWARD 2108283708 | {8476058D-CCFA-425A-8D9D-8591EF3E3149}
CAMBRIA 1101858200 | {1CB4B3DE-6FA2-40BE-AA6D-BEA2EDAB4893}
APPLE HILL 210297982 | {1FCD571D-957E-4FF9-863E-0126FD4A401D}
WILLOW CREEK 11037514 | {2ADAB335-F68D-4E0E-93A5-403C7C54DA76}
CABRILLO 1104431976 | {A8C0DCB1-6987-421D-A6ED-00C50AACF3B4}
DOLAN ROAD 1101882610 | {6AB13B35-5C7E-47B3-B58A-5166F0A77CC1}
KONOCTI 11084039 | {D3BC4C4A-6AD6-4D57-ADFE-ACA0E6607A3B}
LAS AROMAS 0401LA401R | {6DF01F7D-D94B-4655-BAF6-B3A3B3F7FF40}
MONTICELLO 110137384 | {9EBC498A-4473-4FB2-A278-0770D844069B}
LLAGAS 2104735530 | {AF07F25E-155C-4D19-8872-642A3CCD5556}
CURTIS 17028000 | {C413BF51-2D4A-4E14-8A5C-AF93355185D2}
DEL MAR 1103624 | {C849372A-DDB7-468F-9EC0-AE7D09002A23}
SANTA YNEZ 1102Y18 | {CB331419-4415-4607-87D8-B05BBD8C7F9E}
FOOTHILL 2101645910 | {DA93CD43-4632-46CD-9EF3-906DC0AD12DA}
PAUL SWEET 2105959032 | {DC6678BB-B73F-4EC1-B958-DDA4A1A4DD5B}
LLAGAS 2107CB | {DD8395FC-A049-4EDA-8DC5-FEEBE3B0FF15}
GEYSERVILLE 1102274 | {F335CD9B-C6EC-489A-8E1A-57248916AA35}
DEL MONTE 210436720 | {9F487EDE-1254-4232-B1F0-1B8CB4720B05}
VALLEY VIEW 1103218424 | {0AF2BCCE-C158-41A1-A8FA-127B4D2028A8}
ELECTRA 1101CB | {0D0FEEBA-0BD3-4962-B35B-0A3278052F45}
OAKLAND J 1106CR164 | {4808F0D1-7684-45A4-AA78-2B2D6EF06890}
GUSTINE 110264140 | {643C42D4-351A-432E-B651-277EC983F63B}
RALSTON 1102CB | {A920E716-9436-4401-AAF8-C3A905DCBD43}
UKIAH 1114943840 | {D98BCE06-B639-4635-9566-7FA7CFE5BC8F}
TEMPLETON 2113A12 | {F518F823-D39A-4E63-8BF7-DA50E4754F15}
WILLOW CREEK 11013050 | {339F8F9F-E6E2-48FC-94D7-73A8490708ED}
GARBERVILLE 1101438596 | {39301543-F3C9-446A-ABF8-E960F80CEDFE}
JESSUP 110168362 | {4BBBA9F5-2A5C-430F-82E9-5C32AA8B7737}
WYANDOTTE 110913052 | {790FA841-FFAA-4636-AEC1-FF360B754DBB}
MC KEE 1103333750 | {58E90993-9BBD-4F51-9BA9-AD36025808B4}
DEL MONTE 2103CB | {B9CA7C26-A10E-4143-8CC2-799A8D4A9979}
PINE GROVE 11023168 | {EAFDD43F-F7FF-4388-8EDB-D22261F3737C}
PUEBLO 1104536006 | {EB53C457-3734-430A-A35B-404EF848B72E}
CALISTOGA 1102270153 | {5E03CEC5-E2EB-42D8-9EED-F70D1DF93EB6}
LINCOLN 1104818790 | {C5EA5C15-1CF5-4589-BD9C-EEF6FE17F558}
BRUNSWICK 1104761310 | {5D7A1019-73A7-4921-AA73-859EBCF0FBCE}
SAN RAFAEL 1109418 | {466136A5-5029-445B-8434-F48A32643962}
DUNBAR 1101534 | {5426272A-AD0A-4461-A119-14316B37A620}
MOLINO 110276066 | {8614D223-F481-4626-858F-622D47A98A6F}
EDES 1112CB | {8BEFF91A-7C09-4291-9AE2-AE9219165D14}
ORO FINO 110239154 | {EE93E5CE-FD33-44EC-A329-FBA8C511073C}
SAUSALITO 11011270 | {D140947F-0C1B-40AD-B2F0-4E3897A9B1FE}
LOYOLA 1102LL86 | {2FF7416F-A3A8-49DE-8B6E-03DC5E89A659}
GANSNER 1101CB | {40645203-FB29-4536-8849-C6C7781BFE2D}
EL CERRITO G 111257953 | {253DD6AB-E4CF-46A7-A9CA-31B26BCFBF2A}
CAROLANDS 0403CB | {4FDA6CDB-0E5F-4B76-BABA-C5F84B9DCB82}
SAN LEANDRO U 1114653758 | {535694D1-FE48-4344-BC96-5C27E6A571BF}
ARVIN 110115909 | {2B1BA581-45FA-4D2D-868E-E1CB0E681EBA}
SAN BERNARD 1101830398 | {0FCD66A3-9E49-49FB-A934-531E12B8CE6F}
BRIDGEVILLE 110255612 | {16121076-8F7B-4A07-9991-9C360FE94AC6}
ARVIN 110194892 | {2B1BA581-45FA-4D2D-868E-E1CB0E681EBA}
CHOLAME 1101CB | {35294033-F688-4422-9C73-F70641476C8E}
ELECTRA 110161816 | {467D6E51-4EB9-458F-952D-00686C463F1F}
JOLON 11027068 | {69E872AF-88D3-4B73-8E65-0B02DC82EDCF}
MILPITAS 1108CB | {7055FF43-DD9D-44C9-B3AE-9B73AF61A173}
TEMPLETON 2110941946 | {BC8B43E1-B72C-41FC-BFAC-30FCC8E9DB81}
NEWBURG 113137512 | {BE4D7FC4-1B1E-43C1-A168-77B9EA7D5DB3}
MESA 1101CB | {C61DB78B-3364-4B90-90AD-4E89668B63A7}
CASTRO VALLEY 1105132304 | {DF750B9C-4007-427B-BA49-F0504B484D45}
PURISIMA 1101CUSTREC | {0E276FF7-E726-49F1-899E-4DA4E59DCF2F}
WESTLEY 11039010 | {0DB6DB9D-7804-4D10-B639-1A5CA91DDA98}
NEWBURG 11326982 | {61AD59B6-3DE5-4155-9391-74B53A84E200}
NOVATO 1104904966 | {335D8DF9-D334-4C80-A8EC-F250AAC0E6C3}
MESA 11038647 | {6E34D557-FB41-44E6-B10D-DE75166431A4}
JAMESON 1103CB | {D66EDA38-27E9-4939-96F7-B9EFA1F3B789}
PAUL SWEET 2102CB | {E84E756D-50CD-4E19-9CC3-E6F7306D45B8}
PAUL SWEET 210710986 | {281B3385-4F71-4EC0-B77E-390E15EC23C1}
MARTELL 1101915018 | {277F84D3-A270-449A-A58E-FDC1A84261F4}
PLACERVILLE 1112CB | {69C7055C-8321-466E-890B-DA1A435F5398}
HIGGINS 11095703 | {824F13D7-3113-4AA8-8BC2-89229A42D634}
WEST POINT 11024788 | {7DA2EEB5-1A19-437C-8020-DD813277F9CC}
DOBBINS 11011264 | {81A1F156-C98B-4850-992A-A7159456D080}
AUBURN 1102CB | {8B190E99-2FFD-4283-B3F1-C9A94DD8C8D7}
ALTO 11243121 | {5B9950E9-6C0C-44EE-B414-F2773560C367}
ANDERSON 11031600 | {38F7B678-11EB-498C-AD48-774BD4B8786F}
WILLOW CREEK 1103181562 | {A739E4CD-6027-447C-8193-CB877EF24141}
OAKLAND K 1104CR204 | {A0999EEF-D902-4C4C-8260-3134A0D51FA5}
SAN ARDO 1101610148 | {A9BAF716-D950-4219-B81C-E6209F590D56}
DUNLAP 110239190 | {03B91929-B748-41B7-BED2-9D46A08F08B1}
LUCERNE 110638632 | {11292177-63B4-4D1D-9B97-B2A90B30A4AD}
VALLEY VIEW 1105368066 | {1A179874-1BC4-4379-BC93-DB3AE752926F}
SANTA ROSA A 110439786 | {697A1F90-C46B-4A32-BA8E-838CA80BD5D2}
FAIRVIEW 2207M526R | {9791B2E1-CE42-470F-873B-7EBAB5F5B113}
EEL RIVER 11021902 | {AD459C08-CBDF-43AA-86A2-CD8C1B5B6101}
FRANKLIN 1104P136 | {F15BB3D1-0A60-48BB-96E4-777A07B496BE}
DIVIDE 11021385 | {A0FD2E34-A735-4A8C-A9DC-394B15A3212D}
CAMP EVERS 210411048 | {3BCDAF7C-1C90-48AD-8ECA-3702D1B4C97A}
BRUNSWICK 1105452800 | {E1779AD2-4579-4092-9EC8-FEE4F5C13371}
GARBERVILLE 11016014 | {B179FF8C-723A-4A8D-97B0-90D4F52587A2}
BUTTE 1105398234 | {B2540AD5-03FB-488F-9579-CE16933A52B5}
MARIPOSA 2101CB | {050E06AF-91BE-429B-BDFE-3EAD80F24863}
HIGHWAY 1101738 | {27D0C7EA-6E05-4947-A47E-355769B9A693}
DIAMOND SPRINGS 110676088 | {423A8C76-9A51-45A6-B374-FEBC31B925B4}
CLAYTON 221465785 | {10733B2C-A5C3-4A9E-8D35-517FAE09EA04}
CLOVERDALE 1102262 | {79D04444-8804-48FE-A949-F2CD7D36457D}
CHESTER 1101656108 | {F5B87947-B1CF-4B32-AB2B-95DA61D92836}
PANOCHE 11034036 | {AD986AF1-07AD-469F-94A3-573792C7B7E5}
MORAGA 1101822414 | {6B23A69C-24B9-4566-AFFA-1FAEC2B2E50D}
ROB ROY 210410298 | {F407D1C7-AF54-4B98-B726-B5AC300E0031}
GARBERVILLE 11022540 | {09BB38E4-7FE7-4BD1-9CFE-F62698521734}
CALPELLA 11011204 | {48F0B79D-EE60-460B-8BC5-9B5CCB492CAC}
BURLINGAME 0404CB | {585506C1-ED3B-4FB3-84DA-FABB2641F074}
SAND CREEK 11037070 | {863BED83-C87B-4B95-B9B9-262F78012E12}
CAMBRIA 1102CB | {A36DF7B8-003C-42F6-A33B-327B9F3DECA5}
ANITA 110648098 | {89E1C548-ADAA-4B04-80A4-5DCCECCCDB3E}
FULTON 1107126742 | {C134E3B9-E693-4C16-B3A4-BFE77C3B9516}
FAIRVIEW 2207M500R | {659FD2EB-053C-425F-AF25-D9C58353B44F}
CLAYTON 221714102 | {2E89F027-67FF-4082-9169-E158A83D0166}
MONTE RIO 1112387984 | {EB3C763F-69B5-439D-A5E0-81FC232FC4F9}
WEIMAR 1102CB | {576CF59E-86D2-4E41-A7A3-27CEB8B77F40}
SANTA YNEZ 1104564710 | {36F02C24-D26B-4B85-8C08-B8C39025E135}
CHOLAME 1101X26 | {B37DAD9A-6324-4833-89D5-DCF19FFFD67A}
MILPITAS 1105CB | {CA512FE5-1127-458F-8A35-7AA6286C673F}
PARADISE 1104954322 | {E166525C-A57D-4F06-BD7C-C2B52E2E9B6B}
POINT ARENA 1101478 | {E4F90CB8-51CF-477D-BA6B-9F60A2DBE5A1}
APPLE HILL 2102186912 | {FB182C0F-B71E-4B89-801E-E64DB8A5CDBB}
PARADISE 1104961990 | {238415DA-D1C0-4791-91CD-7DCD23357CC1}
TEMPLETON 2109P14 | {03B90DE8-00D2-4B58-B65C-ED90C57EE070}
POINT ARENA 110183354 | {B01D0AA7-5805-4227-AB93-F941564BB56C}
HARTLEY 1101658 | {D05A5F97-BA6C-4210-AA67-0AC96ADACE28}
PERRY 1101V88 | {081215BD-B859-40D1-BF5E-3B29C95FC4FD}
SAN LUIS OBISPO 1104982992 | {48D82405-914A-45BE-AD86-2A9FA02155BB}
ATASCADERO 1102A88 | {7017AD32-E07A-4554-A2AD-C732D91DBE2C}
CHESTER 11022564 | {C8BA9CFD-3C7E-444F-AD17-DFDE1ACC00EB}
FULTON 110777670 | {5B55A465-FAC4-48C8-B9A5-F80EA4DBED38}
BIG BASIN 110212124 | {5E67FDC7-6621-4E4B-BC49-469EB29666B6}
ROSSMOOR 11018132 | {71494031-9F05-4CC0-A953-4E31E51E28B7}
ELK 11011300 | {731B8D8A-0D26-4FAC-B904-5F57E7A23907}
WEIMAR 1101CB | {C6D2DBB1-9437-46D3-8E37-6D1AD2333690}
SILVERADO 2105337226 | {0739C7E7-C007-4087-BADB-1D9A705F476F}
MILPITAS 110913377 | {D897A506-3C26-4AA6-AE93-1BA5129BA14D}
LOS OSITOS 2103174580 | {215C3316-AD64-4D86-B319-9811218FF7C5}
VALLEY VIEW 1103P160 | {2371EFC2-B46C-4698-931C-537DFFB0D5A5}
TULUCAY 1101137224 | {D5040DDA-C582-40B5-8A53-2E3901DC0B08}
SILVERADO 21051306 | {A2AE86BF-29D9-46AB-AC07-62E08E2FA633}
COTTONWOOD 11011610 | {FD19D23C-6A96-40C9-9542-F7EF9A6AB34E}
BURNEY 1102CB | {36A5A14C-2F20-494D-A5FC-CDF9488C4EA1}
HERDLYN 1102973026 | {6D42CB7A-C91F-4DBB-9706-F92EF8B0963E}
LLAGAS 2105XR234 | {90264C2C-3ED3-42D6-BFF5-F41E927FBBE3}
RINCON 1104CB | {DDE06CFF-C1C8-453E-9DCE-C51203C62E9C}
ALTO 1122591122 | {E26D9B6D-6B45-4494-94E9-E5BD7162DD89}
OAKLAND K 1103CR202 | {9BD2CCED-08C0-4120-A490-E52866AF5C8D}
SAN LUIS OBISPO 1107V18 | {196F79B3-5D9F-4F99-B311-272A909D0DD7}
PAUL SWEET 2104273794 | {9E32E9CD-A939-47B7-8D32-52540B68C5C6}
CALISTOGA 1101886282 | {22798A75-B031-4EAD-AEE6-E26CAD1C77A1}
UPPER LAKE 11011276 | {5F898AAB-A822-418A-A7D3-2566EAF134B5}
JAMESON 1103118944 | {A2248A11-F35A-465F-8815-05FAE8AEC21C}
MADISON 1105495270 | {2C14C00C-0CAD-4E64-99CF-10447EDEECD2}
BIG RIVER 11013002 | {E6F8FC53-7441-41DA-90B5-FEDD62BCC4B4}
MOLINO 1104380 | {5465105C-2E1E-47CE-8A44-120776A3EE22}
SANTA ROSA A 111179354 | {77B8D94F-2EC6-49F7-A5A0-3C2CCD32D5EE}
CORNING 110164090 | {9C401B14-4A54-4DA8-B9DB-3EDB68F74D1D}
OAKHURST 1102455174 | {4739024B-FF85-45D7-AECF-B2FD3D7B777B}
RACETRACK 1704CB | {128383E7-96CF-4707-8041-13E4B9B7C999}
ROSSMOOR 110654472 | {DE34AA94-F995-444B-B0E9-519FC6F293D6}
BELL 110880680 | {3A2A466A-E07F-43BB-BFCA-7454C5908F19}
STELLING 1108LM42 | {54B1742D-9454-4E0A-BDA8-E9A3850417C6}
TULUCAY 1101926496 | {5DBAA811-6F22-4836-935F-F9F50494B3FC}
FRANKLIN 1101P132 | {6376A175-D3DE-423C-8B8A-9B6318316FA7}
HIGHLANDS 1102628 | {805F8CD4-618B-4641-8C2C-AEC1BF35DB49}
EEL RIVER 110249130 | {ADA0B946-8139-4D75-A3D4-894703D1FC57}
WHITMORE 110145262 | {D9E3C410-A0BF-4EA8-96F2-E696EF9ADFFA}
FORT BRAGG A 110233064 | {13E2F68D-5FE0-429F-8E83-F4D9D6BCB638}
OILFIELDS 11037006 | {28C87B96-17F1-4B77-AC44-88E083C74B6C}
GARBERVILLE 11022500 | {37DB383D-2CA0-40C2-9028-FCF646539713}
SHADY GLEN 1101100230 | {2295C6B5-DB5C-485B-935E-32BBB76DDD81}
MOLINO 1101324 | {AA518DB7-54A4-4551-9B95-ACDCCF557961}
LAKEVILLE 1101266 | {B6A7196F-7623-49FA-8ADD-1DAFF9EDFE0B}
LAKEWOOD 210964992 | {C65A3889-43E9-4E24-9131-D549D4446C2C}
SALMON CREEK 1101242382 | {196179E3-0F18-4F79-A1AB-13E8430D60AE}
RAWSON 1103CB | {2BC26C95-B90F-49BD-888B-1F85DFF0BF79}
EL DORADO PH 210126000 | {563CD71D-CD80-49B9-9B00-20025334D5E0}
BELMONT 11109088 | {D5010A07-EC1F-422A-818C-56120CF28FE6}
OLEMA 1101337220 | {92ED973C-FC6F-4281-87E0-2EC9DA3D68C7}
MADISON 2101845694 | {9F1D585F-4585-484D-A04F-23919C37AC0A}
CLOVERDALE 110282888 | {B5A8374E-B790-43DB-958F-6C84A7C12E44}
CASTRO VALLEY 1105MR579 | {7DC88504-8437-4262-8C77-15F7F25CD1D4}
PLACER 1103284874 | {390506AD-DEF8-4149-9470-E4570BC394B3}
SAN RAFAEL 1106991658 | {3CC0B2ED-4CCD-4757-94A4-43056A68F6C1}
WOODCHUCK 2101R4610 | {58CC59BD-D32A-413F-871C-B048589E5421}
ROSSMOOR 1109961536 | {6DCAEE0E-EF55-4731-9878-3906C6B80014}
GARBERVILLE 11011604 | {905A282A-4E87-42B0-8385-244613D03E1D}
HICKS 111660050 | {AA1A8D76-D2A1-485C-9B69-D74FAC1101F8}
HIGHWAY 1101992028 | {5C6F4134-089B-4151-9D4E-9160DBB180EF}
FROGTOWN 17028482 | {DEF24EAD-1BE2-4F6F-8D2A-6151341F3B41}
COVELO 1101516510 | {EADD8CA4-64AF-4618-B2F5-C69C9631D28B}
PASO ROBLES 1108R10 | {F6C975A3-F727-462F-BF14-05FA1E630EB4}
BELL 11082226 | {FF6B966D-B6C9-448E-9EAD-BA4CD433B469}
CEDAR CREEK 1101451856 | {1E7F5746-1B26-4A75-989E-3A819FF5E822}
INDIAN FLAT 110478148 | {8FE2B2A5-53AD-4D02-8B28-25A33ED98DCB}
LOS GATOS 1102526868 | {40479F22-BBD2-4DBE-B231-5BD9D16BE0F7}
RAWSON 110385334 | {4FE71C2A-D73C-4875-8301-3BC6248AF0F6}
ANITA 1106552724 | {66BDFA7D-F7B6-403B-BF76-C55BF0419221}
PIT NO 5 11011618 | {83B8DDA8-0AE6-4FAA-9DFB-D57952CAA5C2}
HUMBOLDT BAY 110242066 | {712389D7-97A8-43EF-99E1-6A4B64E5B114}
PUEBLO 2102769868 | {D239647B-6B20-452B-9F55-A164C653DDB1}
HIGHLANDS 1103726580 | {D271DF75-70E3-4A5D-9E2E-6D2BE449ADB2}
TEJON 1102CB | {FFCCB51D-8ABA-4A3C-849A-11EC19C62E8E}
TULUCAY 1101323426 | {D5040DDA-C582-40B5-8A53-2E3901DC0B08}
WOODCHUCK 2101CB | {3E054CBA-7126-44DC-A6B7-5F7D5EF697FD}
ELK 110191336 | {51F158BA-B081-4FAF-A03B-EC569F9C35AD}
MENLO 110235722 | {56AE0E26-A1EF-48A8-89D1-72A26BF969A5}
ORINDA 04013442 | {5E439C6C-9351-476C-9634-FD9D0D59EEC5}
MIWUK 1702667248 | {A068179F-B6CC-4678-A4EC-AF469032942C}
IGNACIO 1105490728 | {ACF50790-A77B-4E22-9362-2A36912CA1D3}
SILVERADO 2104806 | {B06F68AD-C4A0-4C48-AC8B-ACB86AC8FCA9}
BELLEVUE 2103646 | {BEA97E4E-CFBB-4EAF-9EAB-B9D9096C26BD}
PEABODY 211340338 | {463CEDCD-A864-4BE7-A495-4562C479EEC4}
NORTH DUBLIN 2101MR333 | {298F8E6C-8C4E-4458-91EA-603E3295125F}
SALINAS 11043018 | {37BE6D71-E3BC-4DC2-9D89-ECD973BA9436}
MADISON 21016617 | {FAFBD2A1-FFC3-48C9-9B09-E9ECE3AD7FAB}
CAMP EVERS 210612518 | {8A35F12A-0761-4DDF-88CA-C8A70AB35338}
SAN LUIS OBISPO 1105994498 | {81973749-CAB3-49C6-B105-0C3D389524EF}
DEL MAR 21051268 | {DD87F226-71D9-4417-928F-44802F1E6068}
PRUNEDALE 111022104 | {EA4AEF31-2B29-42E0-BD25-BED069AD0B05}
DESCHUTES 1101CB | {FE5A37BD-E086-417E-B0C1-D984D30B636B}
BRUNSWICK 1102CB | {0BF84A9F-DBEC-4CA7-98FB-695194286708}
PENNGROVE 1101170 | {1A72E14C-38B8-4F2E-A8C3-6BC5686CFD94}
SAN ARDO 11027030 | {531BE6B3-C431-4299-B6F9-340C07FC847B}
MC KEE 1107827486 | {625462C6-F8FB-4C1B-B9B9-64AC08211124}
PLACERVILLE 2106CB | {86E99440-83ED-4726-A6BC-38E34FEB5B33}
OAKLAND K 1102172340 | {D34997DF-D716-4F24-A200-9AE2C7E61290}
COARSEGOLD 210310300 | {D52EB2EB-C85C-45E0-96F5-17449635DB4E}
CASTRO VALLEY 1110610800 | {217855BB-2EFA-4F5A-897E-1A1792604994}
HICKS 2101CB | {29DF4083-4850-493D-A17C-7E1454C0761F}
BERKELEY F 1105189500 | {5B19BE61-6886-4FC7-B0FB-4DA13CF3F560}
PETALUMA C 1108630 | {707F90B6-29D2-416E-88CB-4A65D150CEBD}
GANSNER 11012424 | {7FF9C2B4-7885-497B-BE5B-64337D7948AA}
WYANDOTTE 11021502 | {A54ECB41-5029-41D9-AD67-64342065DC6F}
GARBERVILLE 110197300 | {BA71994D-6A0B-4F0B-9E44-79C1DD5F42DD}
PANORAMA 1102CB | {BF983BB2-B79A-4F98-B895-74C5BCEB2BA3}
ECHO SUMMIT 110155262 | {D6DB5AF9-E5B0-458F-9897-3AC3E052AB08}
NOTRE DAME 110287268 | {1BA9278D-6A82-456C-AB93-CADDEAC99F13}
LOS MOLINOS 110163998 | {13B78A6A-8DA9-4023-969C-3CD765D0B389}
SOLEDAD 2102858388 | {14F60B66-6FBD-423A-A8D4-1F6DF8B5B464}
SAN LUIS OBISPO 1104777686 | {4B433B40-0A9F-4E4A-AD28-C0C25FE24FB2}
SPRING GAP 1702CB | {64CDB5CA-B54E-4043-BB09-802AFEE142DC}
HIGGINS 1104842642 | {77DD24A4-3555-45C1-AFB0-D6E3B0D6C267}
MORGAN HILL 2111CB | {8D6AF672-1092-41FD-91A5-035B7D768884}
OAKHURST 1102683678 | {4739024B-FF85-45D7-AECF-B2FD3D7B777B}
GOLDTREE 110814115 | {F40F9B94-B69D-4B7D-86DD-125E8D7AC87E}
SANTA NELLA 11017200 | {54EB001A-C75B-4E5F-A364-1EC2210A8870}
CURTIS 170463502 | {A5122D22-FC3B-40AD-B1C9-1922AC7D5EB3}
SPENCE 1104965598 | {E9D1075E-68D1-4D19-916B-47C6CD439F6E}
HALF MOON BAY 1102CB | {EC65686F-B15A-4CBF-8005-BF1274876E69}
WILLITS 1102CUS8736 | {9734DBF0-6F90-4CE9-BF04-F2CD4B5AEADC}
FROGTOWN 1702832694 | {94EE7076-462E-4300-BB9C-E1B2A1AE599F}
TEMPLETON 2113A32 | {B5262924-E8BA-494C-94F2-552AF4F4F88E}
VACA DIXON 110118292 | {C14F8C7D-2418-4308-A5BD-32845AC90D2E}
FULTON 11024334 | {F2C72F8A-06E0-42ED-81D6-01D05809B312}
LOS GATOS 1106LA46 | {1AF8FBF6-3836-4778-B451-B0D01E1343B6}
GEYSERVILLE 1102537096 | {450BD680-08E6-46D0-AD80-CB37688E8C0C}
REDBUD 1101708166 | {3492968E-3545-4212-B771-A444F5766479}
MOLINO 110241392 | {447B8131-1050-400E-81F0-E893F64CB384}
SAN ARDO 11027066 | {8AD3688B-AF38-466D-9653-33A0316A94CF}
WHEATLAND 110591170 | {B814ECD9-6160-4057-8AF0-345725EF4AA1}
PERRY 1101W26 | {07DF4B2B-054C-4E25-84AF-DE6FF88C6FF3}
MOUNTAIN QUARRIES 21012504 | {3A3CE7E6-6AA4-47AB-A29B-08143EBEB1C1}
MORGAN HILL 2106XR224 | {2C56B704-0B48-474B-86AD-67CE86231708}
NARROWS 21052426 | {8D49CCC1-AF4C-4146-915D-64772DC7F3D1}
HONCUT 110255206 | {95CFDCE9-A6F6-4428-B8F8-A23AC65977EB}
OREGON TRAIL 11021584 | {A1D13A32-B522-454E-9EB3-1DBA73C91901}
NAPA 1112850068 | {B5EEBD8D-5229-462C-9EA8-5264059F4EB6}
HICKS 2111XR210 | {CF04DCF7-F474-48E8-8533-36C336A15BD2}
MORAGA 1105E512R | {D2286737-B438-4EE0-BE89-B719D260A085}
KONOCTI 1102965078 | {D74BE118-5F8F-4569-9B30-2D3A4418CF36}
SHINGLE SPRINGS 210981390 | {DF428FBA-A19F-4678-A15D-08B87DAE1997}
ORTIGA 11063770 | {F76B220C-9B12-4060-8FD5-AA7B30439772}
GABILAN 1101460414 | {0008E3B5-1496-4F6F-834B-CA7B37853F9B}
GOLDTREE 1107CB | {011DEA9E-857C-400B-8F07-19E7424464B0}
FORT ROSS 1121204 | {031CA341-2C0B-4194-9FCE-C18FD57B6895}
LUCERNE 1106988590 | {03794043-4739-4484-8FAE-7CD50FBF19C7}
KONOCTI 1102948 | {3EE95B4C-7440-4D46-99D3-576CFD7E946C}
SUNOL 1101MR387 | {475B4CFB-84F1-46E3-9FF3-409BD1FA54D8}
PEABODY 211340336 | {463CEDCD-A864-4BE7-A495-4562C479EEC4}
POINT ARENA 1101476 | {E7660F7E-BB9F-4573-B70D-C3EB843F48E4}
LOYOLA 1102429970 | {13464ED5-9F48-4024-B104-3201B180FAC2}
BURNEY 11012402 | {2E555E2F-D45B-427A-941D-A906BDE558FE}
OILFIELDS 1103N44 | {47FD814D-36E3-4524-B471-B70B44EFD5A6}
RINCON 1101205854 | {F4C78492-32F9-47FB-AA37-4818CAE3C60E}
HIGGINS 1109CB | {97806AE4-5D72-4FCC-8179-00CDE6E08736}
HAMILTON BRANCH 1101CB | {CF1292FF-09D7-4946-B3C9-5DF5A5CB48C9}
VINA 110135730 | {DE33B171-715A-4B55-A52C-48E0D345F70B}
PERRY 1101W10 | {E1CC4B8A-EEA0-444B-A148-93C085F63A52}
STONE CORRAL 11107481F | {2BE56CEB-D130-4F64-98EE-3834ECE93155}
WOODSIDE 1104520832 | {2CDC70D4-A195-46DD-838C-5A22FD1041DB}
FORT ORD 210566836 | {29DAE9CE-CAE3-4935-AB0F-06DB01859441}
STANISLAUS 1702CB | {5ACF71BC-5CB9-4FB2-84D8-E7796B319ECF}
MERCED FALLS 1102482838 | {A07075F3-76AA-4FC7-9158-0930DA76C5B7}
GOLDTREE 1105588830 | {2BB441D5-FA7B-41CB-B4C4-3BB6BA3702C5}
SHINGLE SPRINGS 210912392 | {B7DD70D5-00B7-466E-B95D-1B12C82EB1E1}
PLACERVILLE 210658118 | {86E99440-83ED-4726-A6BC-38E34FEB5B33}
LAKEWOOD 211094814 | {B6F65C5B-8596-4980-BF5A-72D64E484475}
BRUNSWICK 11042112 | {5D7A1019-73A7-4921-AA73-859EBCF0FBCE}
KERCKHOFF 1101R353 | {B451B784-A247-4476-BBFC-D28DAAEE5803}
SAN RAMON 2107MR287 | {D3A467BA-261C-4588-AB1E-18C43ECC4A45}
TEJON 1103286542 | {E47780AD-DBC7-46C5-8517-B5A92A1EF564}
FORESTHILL 1101CB | {ED9435F9-E06B-4A98-B053-EB0C1DC8369F}
CAL WATER 1102329532 | {A5C90C7D-4BB3-40A3-8AA7-071C177614C2}
HARTLEY 1102524 | {45C1901D-E49E-428E-8B0F-B20AF66CAD20}
FITCH MOUNTAIN 11134566 | {7C0F49AE-FCF7-4330-B22C-F61243651B62}
CLAYTON 2212158138 | {86E6EBE9-AB18-4CA9-B6B7-D151B1A6516B}
LAKEWOOD 222475242 | {5BA403AB-BCA6-4612-86C3-4865011547A8}
FORESTHILL 11022106 | {01403AE6-90D4-4B19-983B-B7AD8BDC29F6}
PINE GROVE 1102269286 | {163AD319-AD93-4675-83CD-83770D9870B7}
TEMPLETON 2109313404 | {3A9A14B5-4831-413C-90EB-22B1436113DC}
APPLE HILL 21027502 | {730CDBAB-B217-4D30-9612-715B7140F38A}
RIO DELL 11024230 | {83499CD2-C0F0-4DE8-A7FA-CECB9345AEE8}
UKIAH 1115168892 | {E7C123E6-BA30-4506-A3E6-3FDF5CDF33DB}
TEMPLETON 2113R82 | {F7BD212B-7F44-4A16-B423-2BCFB7829D6C}
TYLER 11041522 | {0D1643DB-604E-4FBB-B45F-DBA97992B887}
NORTH DUBLIN 2103727584 | {7713D0FD-BB09-40ED-B7D7-E260577647D4}
HOOPA 11013174 | {340CBFFC-8113-455B-B1D8-1918397994A0}
PLACERVILLE 1110421358 | {3AD84F54-48F7-4505-9D9D-4F3421C728D6}
HIGGINS 1103CB | {5963F19C-E1BE-46EC-9E26-B117A913E935}
EL DORADO PH 210119612 | {5BE9A1BF-757A-4781-BCE2-C4049CA25F7D}
WILLITS 1104934 | {62A0A3F9-A1CB-414A-866A-2AE63E42851C}
MIDDLETOWN 1102302610 | {7E69B413-A223-4CCD-AF98-CC3C74EA7FDA}
MARTELL 1101185268 | {2C34AC51-01A3-44C9-B45A-F5786A7BA8F0}
MILLBRAE 110480106 | {BCA1AB36-1D1B-41D7-93BD-733AB9EA3274}
POSO MOUNTAIN 2103CB | {FFDB1F5B-AEE3-4CB6-9A6F-D3D25805592F}
CALAVERAS CEMENT 1101502 | {1D87D320-3344-47D1-AB52-86F36B13B2E4}
GOLDTREE 110815803 | {F40F9B94-B69D-4B7D-86DD-125E8D7AC87E}
CURTIS 170384944 | {46CEA7E9-BB3A-493A-8627-27189E1BD87C}
BRUNSWICK 1103262343 | {8DEE04BC-1F93-42B1-9D32-1482C9BA3DA3}
PUEBLO 1105684564 | {97C6787C-1A07-4147-A43F-2ED249921F2B}
ALLEGHANY 1101806 | {A90B9AA9-7F37-4154-B2B2-B43A5EF8D800}
LAKEWOOD 2223W540R | {FC9703D5-A1AE-46C7-92F8-123F1090FAA0}
LAS PULGAS 0401CB | {32DE72AC-BD44-46F9-BF98-F2D8B456CA9C}
PASO ROBLES 1104R12 | {4348EB98-7F3C-44FD-A7F0-CBA935871986}
TEMPLETON 2110CB | {43D83959-6253-49E9-BD6A-065B7EF0ABAF}
PINE GROVE 110283098 | {6F523CC1-7B62-49B9-AAF8-BD03742BA043}
HALF MOON BAY 11012500 | {75B0B322-68D2-4160-BC4E-E90092A2B4DE}
HARRIS 1108395498 | {956DFF7A-2597-4885-8155-9B37AFB45D53}
JESSUP 11039281 | {995D3FA2-A637-43AE-9B3D-DDCFC4316118}
COALINGA NO 1 110878186 | {3697C802-0557-4876-8B2E-ADF61773B7C5}
PRUNEDALE 111020059 | {CE89D4FD-128E-4AE3-8F53-291BB3498CD8}
HIGGINS 1107CB | {AD1702BF-568D-4020-87DE-29F495495BCD}
MC KEE 1112XR098 | {B0BB35CF-4475-436C-B6E7-59AB619EAF5A}
HALSEY 11011704 | {CDE691D3-842E-414A-AF2C-C34EFCC94439}
ELK CREEK 110137334 | {D0CAFA51-0A62-4D26-BA1A-5435FD46CC21}
PUEBLO 21031970 | {D374E70A-F10D-42BF-BFC9-DC52D8E99DC6}
DEL MAR 210551692 | {DD87F226-71D9-4417-928F-44802F1E6068}
CLARKSVILLE 210575884 | {398A55C4-A233-41E8-986A-9CEE99885341}
BRIDGEVILLE 110169866 | {3BB5B038-4064-4F43-B944-1BDE53135960}
PUTAH CREEK 1105617260 | {3FECE4A6-EA4F-4BAE-A132-55F5821EF41C}
SAN RAFAEL 1106155772 | {5D059BF5-F769-4312-8893-6A2C828C685C}
MOLINO 1103314 | {A09A7EB0-8666-4C35-B46E-B45A92DE6F58}
CAROLANDS 04049024 | {ADC13D99-F0AF-402E-9F6C-0B91201427B3}
RINCON 1101CB | {F102360D-42FF-446F-88B4-F431C95B2DC4}
TEMPLETON 2113641367 | {FE304B9F-DFAE-423B-9FF6-FD34CCDB383B}
LLAGAS 2104603392 | {28E6C6D7-8DD9-401F-863B-133430EA57C4}
CAYETANO 2109884904 | {4B1B4811-B2BF-45DA-954C-55F605B422B6}
OLEMA 11011686 | {701C0938-AA90-48C8-9BEF-CBE33E0DD08B}
SALT SPRINGS 2101TS4913 | {9EF30C64-8412-466B-8695-929E20570E0C}
DUNBAR 110379086 | {EDA68B39-7DBD-43E4-954E-1185A3CE9473}
ALLEGHANY 11011101/2-A | {B02385C8-6373-4D81-ABD4-7C98960F9245}
OAK 0401R7252 | {0F16EE83-C04F-42F2-82FB-83FAA303C2EB}
MONROE 210392868 | {18B04DCD-9DDD-4C1C-AC8D-731B4880D7B2}
SAND CREEK 11037140 | {2D5FBF93-4F75-44A4-A3B6-356A65A990D3}
EDENVALE 1102XR064 | {7567099C-0C78-4F90-B664-1299D6F2A2C9}
PRUNEDALE 110722232 | {9055CD6F-1385-4DAA-B189-3CEA20BFACDF}
CLAYTON 2216CB | {DB6FE7F1-AC75-4C7E-83AC-CE5B6DE225C5}
PARADISE 11052214 | {2883212B-8F3D-451B-836C-9588E5771E60}
BUELLTON 1102Y20 | {2A274649-29BE-484B-9512-4089BA59299F}
TEMPLETON 2110N30 | {BC8B43E1-B72C-41FC-BFAC-30FCC8E9DB81}
CRESCENT MILLS 21012232 | {6FD1FEB7-53BB-4905-92FA-6BF228EE659D}
SAN LUIS OBISPO 110788962 | {3B54DCC0-9E34-4A0D-BB42-D31181D2C4D7}
CHOLAME 2102796386 | {C3648DC1-A8A4-411C-BC09-DF15A6A8CCC0}
CLEAR LAKE 1102904 | {F2BFF36E-7C09-45BB-8051-33603CB60365}
SAN CARLOS 11048942 | {7C12A412-D2AF-4E21-A226-597936BFB6C3}
PETALUMA C 1108296 | {87D8E969-EF8D-4B9C-90F3-5A57DD740C7C}
COTATI 110379140 | {8B07F2D1-E8C2-46BF-BEB1-6EA256DCFEAC}
ANDERSON 11011390 | {F53F100A-A47D-4F77-AE95-9A2266045C73}
DESCHUTES 11011580 | {064EA007-8A62-40F7-BDB2-55C9C2572F4C}
WHEELER RIDGE 110190844 | {E4E8B6C8-61FB-4D05-90A7-1AEC2AB09918}
FRUITLAND 114195324 | {270A551E-565A-4C78-BA5D-427CE889B75E}
HOPLAND 1101CB | {7E6065FF-2C07-4696-A18E-5408BD7025E6}
STELLING 1109CB | {AA91D649-E1C5-491C-8F61-6E488119CD9F}
SWIFT 2102889948 | {BE64DC1C-3443-4966-940E-5A564C032974}
SALT SPRINGS 21028442 | {02C4638B-890A-4131-8AEF-2E0622DB34D6}
TAR FLAT 0402588710 | {15F62F46-8DEB-4CCA-80E4-1A07793D2B95}
CAYUCOS 1102W16 | {27A305FA-41EE-4706-9CA1-3C6F18524B78}
MIWUK 1701176798 | {E8F5F8AF-6EC9-4C69-835B-E53C764AC834}
TULUCAY 1101504524 | {4EA48B47-47EA-4694-BDCC-7065AA75E603}
PARADISE 110636042 | {6ADE7913-72DA-4404-B5CD-572436E5CF98}
CASTRO VALLEY 1110MR379 | {8CF3EAE2-3D5E-46D8-99A9-0040E44D6238}
POTTER VALLEY P H 11051904 | {99C448A1-95CE-4373-846C-DC41955DCE78}
GREENBRAE 1103CB | {9E4C5477-E966-43D5-8E24-BB781F7AED7E}
ELECTRA 1101L1697 | {21E26CE5-9BFF-45A6-8272-2A9D442E9691}
CASTRO VALLEY 1107MR587 | {35AEE05C-849F-43E6-A066-12B4CE5002B2}
CORTINA 110130014 | {30FD709D-FDD9-476F-A094-8F17316D4F25}
PUEBLO 2102391312 | {413AA2AE-389A-445A-BDEE-AA83E1C4150B}
MIRABEL 1102503000 | {C5E1652A-2EB6-4FD0-B328-E1AC1FDEB33B}
BELL 1109CB | {4EF25014-B554-454F-9BE5-F3AB9DDDB6E9}
DUNBAR 110347964 | {565357B0-3D43-4998-81C7-7EBC74E038B1}
BUELLTON 1101Y36 | {9CBEE47E-1598-4921-97C7-5CC747F89863}
COARSEGOLD 2103CB | {2E4BA31C-6FC8-4D7D-B79B-DB347A05F67C}
CAYETANO 2111CB | {439ED568-0BDE-4626-B59A-7C48F17E3B78}
DRUM 1101CB | {4FA3034C-CC34-47A2-AF7A-8A1D1515E919}
SAN LUIS OBISPO 1102357407 | {607A19A7-FE06-4D0F-B488-D2CD33F1131A}
WILLITS 110391948 | {69FCB8B8-95BC-4541-BD6A-BC578FAA27C9}
ANITA 1106CB | {89E1C548-ADAA-4B04-80A4-5DCCECCCDB3E}
COALINGA NO 2 110770250 | {C9B31884-8FA9-436F-9425-CE594852B802}
BRUNSWICK 1107357568 | {D067704F-EA17-4E88-B020-8A7104433E44}
SANTA YNEZ 1104CB | {36F02C24-D26B-4B85-8C08-B8C39025E135}
OAKLAND X 1106CR020 | {6992E765-02F8-45C7-B571-2F9E479DE26D}
BRUNSWICK 110456468 | {A316ED50-5AA1-4ED8-AC7C-24B23FF6CC3D}
ARLINGTON 0401CB | {B0F9DF73-E5FE-4D63-9A97-F698C647DBAA}
PAUL SWEET 210212850 | {F743E5C1-4CE6-4D65-B6FE-D0B8E82E2CBD}
SHADY GLEN 1101CB | {2295C6B5-DB5C-485B-935E-32BBB76DDD81}
EUREKA E 1104CB | {6272DCE1-80F1-4C3A-8B1B-A5CE246BB5C1}
FRUITLAND 1141866852 | {7AAAEF20-BCE1-42D0-9686-CF0447F71CAB}
OAKHURST 110310140 | {9D3389CA-CFE2-49B7-8B13-3D1B7ACB399D}
OAKHURST 1102CB | {D0015396-1CC9-4783-A5A2-48EC4AF3208B}
FELLOWS 210442100 | {D4386F50-ABF5-43E7-8326-09F92A4E0719}
PEABODY 210818182 | {BC2B156B-5F07-4313-BE60-34EF88AFE911}
SILVERADO 2105768606 | {095C5936-5504-4C4B-8302-1844A5C0B939}
DUNLAP 11027050 | {1A4C84BC-5487-41C8-8DEF-67BCD120C5BE}
HOLLISTER 21014792 | {6C3CFC54-A1A4-4370-AEA1-A2570E0F37DE}
LOS MOLINOS 1101297862 | {09A4B9E8-989B-4DA3-9154-EF01A44BB71B}
CORNING 110154906 | {9E4CA485-3B3D-4A5A-B314-7734F5C8C14A}
CALAVERAS CEMENT 110147968 | {AFAF5A37-E0AD-4142-ABDE-E616F0022060}
VALLEY VIEW 1106P176 | {B787A327-E708-4D5C-865B-C65998470D53}
SAN JUSTO 110136902 | {37C0E6FA-9A39-4134-9B6F-8111077BFC3C}
AVENA 17025494 | {3E1C42BA-A837-4BE0-A8EE-C29428358DD7}
SAN BENITO 210136912 | {90A67B0B-7B04-4738-A6BC-63EA48062380}
MOLINO 11015042 | {D5D881FC-5E37-43D0-8EE8-25189C47D57C}
GATES 11069090 | {0403AD0A-8957-4413-B5CA-AB406F66F7FB}
RED BLUFF 11041566 | {EFAF3860-6049-4F8E-AF4B-3D1B6758C8FE}
SAN LUIS OBISPO 1107CB | {FE7ADF6B-5FAD-4650-8E18-1F81A8FDEE84}
OROSI 1102CB | {283D946E-F745-4F7C-ACE9-D6EB2A3744AC}
PENRYN 1107CB | {44D8E601-5E0A-4B0D-A783-27A4770DE5A5}
TIDEWATER 210638108 | {2DE5693C-879D-4FCD-88B6-818902BD649A}
PUTAH CREEK 1105748272 | {6B7B9ED0-0961-41C2-AC06-403CFA67D331}
GUSTINE 11026926 | {70573641-CA59-4111-9B6C-A1864C98CC90}
CLARKSVILLE 2106CB | {C9DBAC79-A55E-4BD0-B21C-240D7C28DE49}
FITCH MOUNTAIN 1113824468 | {DEA1978F-46CC-423B-B61B-1E6D21D8F6B2}
FULTON 1107604 | {E553BB4B-1179-4653-BCDF-D0DE748C3124}
KONOCTI 11022293 | {3EE95B4C-7440-4D46-99D3-576CFD7E946C}
PUEBLO 110247720 | {1AE19971-F682-43DD-B35E-DF767DF7D39D}
MESA 110187454 | {8CD02839-6B9C-4A4E-A161-AF3A96F4F1AB}
KONOCTI 11081278 | {7B7F4A99-FA71-47CD-9812-ECE462607E94}
CAYUCOS 1102317156 | {BC053071-09B8-414B-AB18-6F0D45277D55}
MENDOCINO 1101CB | {D8D35F92-2CE4-473E-A048-B7A252678CA3}
GARBERVILLE 11012026 | {E7486DD4-0A7D-467A-B7E3-9401480FC5B2}
CAL WATER 1102690954 | {F35BC96C-F1E1-4513-95B9-90DB5E55FEE2}
FORT ORD 210695186 | {0139AD78-6D54-4C40-B88F-B8F196A0FC71}
BIG RIVER 110179628 | {20E18CC8-D4A7-4B74-B6A8-456036AC47A2}
MARIPOSA 210110170 | {36E417A9-B355-4038-92B6-BA6B805D598D}
BRUNSWICK 1110832231 | {4FDE05D2-6E18-49FB-9864-F184CF9B6861}
SAN RAFAEL 1105534 | {6C0139D5-EF28-447A-8798-DD6F8DC2F6B3}
DESCHUTES 11041370 | {7B256BE5-97E8-449E-A46C-21FA2871BA72}
MCKITTRICK 11013092 | {5A307946-5CD5-4050-AB0D-2E455B17B341}
APPLE HILL 2102852976 | {67403348-AD5A-4D81-B973-25AED6358693}
BURNS 210112870 | {77124F72-2A10-485B-AF25-5FB9845AECBA}
CAROLANDS 04018506 | {3FD84351-2DE6-42C2-8803-7A388D0F1725}
EAST MARYSVILLE 1108900690 | {D1622BED-440D-498A-AED4-D8C420D1B767}
RUSS RANCH 1101CB | {E22153F3-5B56-4AEB-89D0-5F7BDC6E5F58}
SAN BENITO 210275262 | {5F376FC3-2A9D-4ADF-B538-90322F89F684}
MONTICELLO 1101CB | {CCC05F57-600B-48FA-93EA-7CC307C90265}
SAN RAFAEL 11051806 | {3E85D65E-30F3-42DB-9ECD-6ED09FB2A985}
COARSEGOLD 210210890 | {426A5610-C0CB-4740-A0E9-5755646CBB70}
TEJON 11024525 | {58DF11D2-6D0E-4BD8-9469-17767B55297B}
DOBBINS 110183186 | {79296F22-0716-473A-A665-0DFCBF4642CD}
LAKEVILLE 1102CB | {B8DFA050-8FBD-478F-9E02-70E1BAA0DD09}
KONOCTI 1102985276 | {D903B690-6B65-4C8C-B64F-F1B088DE29C9}
LUCERNE 1106709252 | {DE7938AC-4236-44EA-970B-170B6BDC431A}
STELLING 1110LL72 | {510ED089-9B5B-49AE-8C69-BD6EC85BCAAA}
MADISON 2101484892 | {64480341-2026-4E64-974C-9602D07F2EA7}
CORRAL 1101CB | {67B48D0E-E0F7-48F9-B3C0-C31311AFB61B}
GREENBRAE 110276992 | {AEDCB032-1AC1-4F9E-A5A8-36B12E3777AB}
EDENVALE 2105CB | {8A7625DF-9660-4682-92E4-DE9581577DA5}
SOLEDAD 2105315500 | {9FC0A9A6-641B-4A0C-A239-731EDA3A94A8}
PEORIA 1701169700 | {E1710560-8ED7-4937-8CD5-CC64CD263529}
FORT BRAGG A 1102667996 | {267610AC-9BEB-429F-830E-E78C6931DCD3}
MIWUK 1702CB | {5DE457D9-5E7A-46A3-820A-688DCA33A9BB}
BANGOR 1101CB | {C9648835-EB5A-442A-856F-5456F572C3DC}
TEMPLETON 2111R76 | {E068C598-6807-40BC-B63F-804DC57F436F}
EDES 1112CR306 | {8BEFF91A-7C09-4291-9AE2-AE9219165D14}
TIVY VALLEY 1107822606 | {2CCB588B-990A-4DA3-9CC6-802905504EF9}
BROWNS VALLEY 1101CB | {3F3AA0D2-CD3D-432D-9160-6EFA10A51D9D}
WYANDOTTE 11101952 | {40F33AAB-5B9C-4B70-A571-E111B152C68A}
KERN OIL 1106CB | {6ED1033E-54FE-4DD5-BA1F-9025AD47E265}
DEL MONTE 2104181640 | {F5363A17-6294-4FBA-A5E9-297DB437E9E9}
WILLITS 11032500 | {8AA8B63D-CAA4-4D23-B89B-112BF8794298}
BIG BASIN 1101CB | {94CF54F7-C6CD-4453-B5AE-8C10C6BEE2CA}
TEMPLETON 2113A30 | {982A8403-6DD7-4479-B96A-84BF654A0654}
SUMMIT 110148636 | {BC06A3DB-78BE-4381-AABB-ACBB02D3E9CD}
SERRAMONTE 110467957 | {5AC2A44E-A5CE-4631-A5D0-59B8F85FCDA2}
SPRING GAP 17029280 | {EF855D85-A8A9-46E0-809B-873120E44CEB}
DIVIDE 1102CB | {EF9A6FA5-0241-4F64-89EA-1575EA9DAF76}
UKIAH 1114206824 | {47F1875F-3F15-4519-A49C-1F4ECD7BF06F}
CALISTOGA 110178734 | {6508E901-1F5A-48C3-8B34-5971800F66D8}
ROSSMOOR 1101L503R | {93932C89-B87A-4F1E-B65E-D8FDB2772713}
SHINGLE SPRINGS 2105CB | {F8F7136D-4B7B-4975-BCB7-4503BD4299E2}
BIG MEADOWS 21012246 | {FF704EC9-7B07-4166-A0E1-5C891877A473}
COALINGA NO 2 11059000 | {09F38874-A51D-4724-BABB-AF0D78EDB524}
LAS GALLINAS A 1105126886 | {5D12B5EC-5DC5-4C0D-85E8-621A855AB9FB}
CANTUA 1103792930 | {ADBA8581-1EDE-4FED-96B1-1470CDDF965C}
BAY MEADOWS 21029162 | {7B48B738-B738-4F2B-B0D7-4D191D860D4E}
GONZALES 110165704 | {71137ABD-E3E9-4FF8-AD99-B6537D8F36C1}
PARADISE 110439216 | {7AEC9581-2505-41E3-BEE2-C11F0B787970}
RED BLUFF 110451238 | {E9A98F80-2CD6-4193-969F-CD417879D03A}
TASSAJARA 2112676362 | {F9AD6B4B-3819-4B81-9BE7-73908ECEFCE0}
DESCHUTES 11011654 | {1A40C8BC-051A-4DE6-8C9D-412DD5FF54A2}
JANES CREEK 11011184 | {82D90921-E507-4935-9634-C0CEB766B38E}
OREGON TRAIL 110249144 | {C5CBE785-E536-4CC4-8B58-7E4F16DB8A71}
CURTIS 170411300 | {1342493A-4682-4997-B671-32B9B4D877B0}
MORAGA 110531512 | {412508C2-76EC-400C-8C7E-53EB1141C78F}
FORT BRAGG A 110436526 | {741F819D-F84A-48D0-B917-155D72B8DC6A}
MCKITTRICK 11011639 | {0CBC2090-103A-4482-AE0F-2EF4734EAF78}
VALLEY HOME 17031558 | {1005EDC8-1357-436D-879A-4415102F0FE3}
KERN OIL 110476778 | {1080A12B-50AC-4BDF-B6F3-449377032E50}
GREEN VALLEY 210190860 | {1058939C-63D6-4E6A-BE26-51405BD3A77F}
COTTONWOOD 110385050 | {7567B55E-AD2E-47FA-B262-240B7B9C7A1E}
CALPELLA 1101CB | {C851DF07-17A8-4945-A053-68AC77422563}
FLINT 110150960 | {347D4345-ECE4-4101-A340-58299F24E405}
PAUL SWEET 2106974130 | {69E6957D-6712-43BD-9A8F-B645CA82F0D2}
IGNACIO 1105CB | {71399AD4-B98F-4687-A48B-364B35890C76}
EL DORADO PH 2101CB | {9026688D-0DDE-43F9-BDC1-1D8B37EA23F4}
SARATOGA 1103LC40 | {A0069F30-9735-482E-85CC-36443E960AEF}
PENRYN 11072706 | {A3F26B0A-1692-42C7-87B6-33C42D499946}
LAKEWOOD 211082806 | {B6F65C5B-8596-4980-BF5A-72D64E484475}
BRUNSWICK 110378862 | {B83D09DE-3D47-4840-BFDB-F992D85178B8}
VASCO 1103CB | {D777EA4E-3A7C-4425-B34B-DA242E9EFE4C}
LOS GATOS 1107914254 | {F9DF48B9-C722-406C-B401-60189B57E89A}
SOLEDAD 2101107872 | {13A55BCC-4738-480A-B6AB-19B8FE7F095B}
IGNACIO 11011264 | {2723FD74-E215-4B66-BA9E-051AE21C4595}
PAUL SWEET 2106CB | {3E23A7A3-C33C-44B7-A4F6-DB4402C4D050}
CAMP EVERS 210637210 | {4EC0C5CA-D3E9-47E9-809A-55A51CA9C021}
SHINGLE SPRINGS 110419502 | {68D0B16F-430E-46D7-92D4-FB0EB0D57376}
CAL WATER 1102CB | {A5C90C7D-4BB3-40A3-8AA7-071C177614C2}
GUALALA 1112662 | {4C471213-8F1E-4783-A9BD-8E19C8202DBB}
SNEATH LANE 110134438 | {5A5EFB63-6847-4F33-8DBE-F9C3D6DCF54A}
MIDDLETOWN 1101851636 | {302C19E7-740B-49C6-83EC-9E70AC44D5CB}
MADISON 21011606 | {892EE518-0261-403B-AEBB-DE522B481F93}
IGNACIO 1104316 | {4117016E-C4E1-43D1-8702-FC75C137797F}
SHINGLE SPRINGS 210935598 | {4BF4ABD1-69F5-49AA-B8C3-8117FD378308}
EDES 1112CR100 | {63D64072-C2FD-480F-8116-E56FEE7BD425}
MIWUK 1701953336 | {778380F2-BA49-477B-8F0F-740FAC39A283}
ROSSMOOR 1106384042 | {7E910363-02B7-4903-815B-B702BBD4A69D}
TIDEWATER 2106C514R | {8FCD9F0C-12A9-46C8-B7B1-BF847BD03786}
BRENTWOOD 2105B504R | {9A8233B7-234B-46CF-8EEF-6B74776F9D38}
LAKEVILLE 1102280 | {F573D52A-B881-4B76-BAE1-75A508AA556E}
BOLINAS 110146152 | {14035AAB-B6A7-4C8F-9B08-2EC08FB0B5E9}
WILLOW CREEK 1103205028 | {14EDF25B-565E-45F6-929A-4EE758947CA8}
BIG BASIN 110110720 | {1594C1F1-1EBD-4EB0-9A76-086953E0C574}
MORAGA 1105829530 | {7BAB3DC6-3A7A-45FE-9661-6992831DBB83}
ATASCADERO 1103A06 | {80C03548-09A3-4516-9CD7-A85242729AF9}
HOLLISTER 2105903238 | {0363382A-DCEC-4F0E-A9CA-F2D9B0CACBC3}
TRINIDAD 110246990 | {4BDA4000-EE02-4CE4-AF17-6468A5212F43}
SAN JOAQUIN #3 1103403515 | {4CAF538D-CE7F-452E-B2C8-DD5DB29918D4}
CLARKSVILLE 210955666 | {58AFEF14-24B5-49DA-AC14-3989473D0CBD}
MONTE RIO 1111256 | {7E7B289D-4C56-4E03-B7F0-62BB352D64F7}
SHINGLE SPRINGS 210519522 | {8C6D6A40-340A-49FE-9A00-F50F1736F18B}
PRUNEDALE 11073712 | {9CE15D70-9BD3-4411-955B-AE06E56BCA8C}
GEYSERVILLE 1101480 | {B067E8FC-275B-40E3-B858-2220AFBD2EF2}
PEORIA 1705999 | {50E0B9CF-D877-44E3-8923-B1CAE75FDAA7}
CLOVERDALE 1102429006 | {7E3BECFF-8D7D-4E66-87B8-14F0BE7604FC}
HORSESHOE 1101CB | {88F5CEC0-E8A5-4F1C-9B7B-06545C0D954B}
FULTON 1102904058 | {A7116264-DEE4-49AB-8F9D-DDEB0877D031}
SHADY GLEN 1102CB | {A8C871E9-A558-4EBE-96DF-EF0BB9E9DE44}
PASO ROBLES 1104CB | {ADE2AF2F-AC34-4AA3-BF28-71F3B3370640}
NOVATO 110449280 | {DFA09063-555C-4B48-ABDD-D054FE284D1C}
CORTINA 110130006 | {E3B77E93-BB57-4588-891B-4456F675EF56}
STILLWATER 11021644 | {2295AFD6-60F9-4656-92BA-00A16BCFB50A}
FORT ORD 2105CB | {29DAE9CE-CAE3-4935-AB0F-06DB01859441}
SILVERADO 2105131568 | {8DF4CE8D-8809-41EC-B891-BD4155C95E45}
LAYTONVILLE 1102CB | {90C83132-41C0-4461-99CD-C9A5052731EB}
OAKLAND D 1112CR192 | {D247477D-6B8D-41FB-AD66-DBEF58C5249C}
OCEANO 1102M60 | {DCC941F4-38E3-4AD8-A417-5C522DBC4598}
VACAVILLE 110838316 | {05D49B9F-74A5-4524-8EF5-6986AE7D334D}
CLARKSVILLE 211011142 | {3A0A47C5-9EE4-402A-889E-C298AEE1970F}
ANDERSON 1102CB | {4CF4EB85-76D9-4518-B772-23773872AF10}
TASSAJARA 2112CB | {4D869EED-AD00-4E5D-B02B-0CB786403D3A}
ECHO SUMMIT 1101741586 | {52018984-7699-4174-8C0E-5E599E3F4F55}
MORRO BAY 1101W04 | {102F8E07-1864-431F-B2B2-B6070F04A552}
HIGGINS 1104324510 | {477268D6-DE4E-4795-ABA6-DB4CC4C4808D}
CLOVERDALE 1101474708 | {70DF189A-0B8F-41F8-947D-2C012503D21C}
KANAKA 110183288 | {A419DB79-B16D-4DB7-B7A8-B2FF0808C0AC}
OCEANO 1102862544 | {C1E44C7D-7EA2-436F-89F7-DC91E773D74E}
MADISON 2101CB | {EA6111A8-7AB9-443D-A740-55705E7BEA72}
SAN LUIS OBISPO 1104798282 | {4B433B40-0A9F-4E4A-AD28-C0C25FE24FB2}
WOODSIDE 11028862 | {4C49C25B-7AC8-408B-8A99-E4CB51688164}
AUBERRY 1102R1013 | {71E8F95F-8504-4520-9C3B-8AB71CD7CDDD}
BURNEY 11019042 | {76D3EBDD-5C29-47DF-9912-445D8BE3DBA6}
HUMBOLDT BAY 1101CB | {91BBB89B-9333-4A31-8E04-1784413A7D4C}
TASSAJARA 2107CB | {9B0F8112-6AAA-47D5-A7C6-B8C0314DE7DA}
BIG MEADOWS 21012474 | {CAAE778D-9C35-4E23-898C-4B832CDD3B89}
CASTRO VALLEY 1108MR578 | {DE9C2D91-5A65-4F2B-B56E-B99E45AB3C86}
WRIGHT 11109090 | {ABB28193-DF6D-40B9-BA16-1713A8EF4B58}
BASALT 1106657038 | {0C9DEF06-9AAB-4128-9810-85E010FF7C1A}
HIGHLANDS 1103973816 | {45E82633-486E-4610-936E-63E014462202}
SUNOL 1101MR169 | {61DFA90A-EDB2-455B-85E4-E1B3C2D31605}
FORT ORD 21069136 | {AB7BD794-6A54-404B-96D0-00596CF55B93}
JESSUP 1101271314 | {A7720DBE-D298-421E-A3B2-FE12C335EE16}
BIG BASIN 11028403 | {1695E978-9BD4-42EE-A017-6DD99E4F027F}
LAURELES 11112020 | {03861487-35BB-45AB-853E-5E8CD2B590E5}
BERKELEY F 1105BR168 | {34B1FBA6-E642-41FD-8BD2-ADAC657BB906}
SOLEDAD 21053720 | {1D34DC58-836D-4803-AFE9-57F78BAE9DE7}
TIDEWATER 210657926 | {2DE5693C-879D-4FCD-88B6-818902BD649A}
SEACLIFF 0401CB | {4EF4529F-4E08-426D-A25B-A1F6BCFED593}
PUEBLO 11053022 | {6A034A59-B030-4B42-9C02-B5134DF1FD0A}
PANORAMA 11029762 | {C1937D12-32A7-40CA-876D-66A02478084B}
CORONA 11034446 | {D1AA7A01-6717-4A8D-8AC5-0F1F18BEAC1F}
LAS GALLINAS A 11041220 | {FE680FDB-B6EA-4407-A9C1-F85BBCDCB812}
CORRAL 110314716 | {69E7CCAD-089B-4A0D-AFD3-F9DC2B18E72C}
CLAY 110314674 | {6FB5453C-8E3A-4B58-AB8D-8BEBE74026D5}
SAUSALITO 11021500 | {7E93EFF6-2E9C-40C7-BE6F-763B6DBD01F0}
CARLOTTA 1121686774 | {B05654BB-E8D8-4BA7-B923-D4499F5C765C}
TEMPLETON 2109P68 | {DD7BFBA2-59F2-4AF7-93E5-DA92AEFE3901}
SAN RAFAEL 1110854822 | {19311019-956D-4A95-87DB-92D336722225}
HALSEY 11026129 | {033C2E2D-A850-40FA-9417-37D899E25ED1}
COARSEGOLD 2104570682 | {9485A7D0-401F-403C-A8F4-B704232548DB}
TEMPLETON 2112R98 | {F888EA83-160B-4C8A-947C-3FEEFB60DC7F}
SANTA NELLA 1101CUS8000 | {D9B42920-8795-457D-8506-B9A1003BB3E6}
DEVILS DEN 1101CB | {E637B763-1297-4DA3-B168-C020DBAC2EB8}
GREENBRAE 1103343788 | {F008DFF3-E06F-4A9D-BE65-7AFC32973FC7}
DEL MAR 211064434 | {67D76908-7B70-4DAD-A31C-C1F7E75F3357}
CLARKSVILLE 210951742 | {678500B4-CC40-4993-94C8-A8D3584C2E9B}
MOLINO 1101152 | {366DDD05-C36C-4018-8E0C-E1718F820EB6}
ALTO 112087204 | {D4FBBC03-A778-4C54-9456-3A890F4850F6}
CAYUCOS 1102W18 | {D1A948DB-B3D6-469B-ACB6-5B79CAB78401}
BEAR VALLEY 210513430 | {F76AEDBB-91E0-4407-A41D-F6794405D1E1}
TEMPLETON 2111CB | {1A1B9828-BB7B-4831-9B29-12F7B7720C90}
CURTIS 17036064 | {1D6F2813-1DE7-4CF3-9F1D-B6618158D284}
MERCED FALLS 11027006 | {3C66AA6E-AAFB-4AC9-BCE9-F89CAFA6091F}
CUYAMA 1103684566 | {D1C13827-3D8F-47CF-923A-969F7154F0AA}
PLACERVILLE 1111508410 | {15D1F2F0-3D88-4B18-AFEC-B03FE833977B}
ANITA 11062074 | {F3D6F39A-52C7-4EF2-B536-42290D3060B9}
PERRY 1101V74 | {03363AA4-45D4-475B-A70A-74AAA6293936}
GARBERVILLE 11011750 | {08393BA3-C925-468F-82DD-D9087C4038E5}
HOOPA 1101405280 | {2415EF23-20CC-449E-97C7-29435A19FAB5}
MIDDLETOWN 1101439572 | {302C19E7-740B-49C6-83EC-9E70AC44D5CB}
CALISTOGA 1101157668 | {6BBCCA3D-69FC-4060-8327-3D48C3973D5D}
VIEJO 2204385618 | {84E279B4-A57A-4132-ABEC-C7AA0EE5903D}
CLOVERDALE 1102CB | {A0D136BC-BED5-4E61-825E-2EC84D15BD33}
SHINGLE SPRINGS 210911092 | {AE69F8EF-4AC2-40EB-85B9-DBE37E3684F9}
BELL 1107CB | {CD565697-14B6-4AA0-954C-46CA84031737}
CORNING 110139100 | {A9C774C3-1428-4B46-A99D-50AD5766C649}
JANES CREEK 1102CB | {00625706-EEB8-45CB-9368-35DB90D22760}
CARLOTTA 1121CB | {3CA4A42E-51F1-49B1-95E4-11CB39229D26}
PALMER 1101M82 | {51B50550-2616-4B8D-8593-9330C414F251}
UKIAH 111472990 | {7D69F374-F9B0-4F64-806B-E0305A606677}
BASALT 1106724 | {31C38397-CC97-43EB-A38A-D18D8FE5AEB7}
SARATOGA 1105431214 | {0AC2A538-D1DE-4BF0-89DD-0FB685A31962}
CURTIS 17039330 | {BE967458-9C2E-4DBF-9D1D-857D10B2BFD4}
SAN JUSTO 1101CB | {01D6D09A-4701-4A4A-B6BC-8E8154C01835}
CORONA 1101248 | {028C9314-BFED-46A4-8526-CFB499FC78E8}
STONE CORRAL 1108255186 | {0CA201EF-0A9B-4A84-97A7-EB95F1056EB9}
WEIMAR 11012084 | {1AAC91CD-F390-4834-9229-DA9482F10795}
PARADISE 1102CB | {1EC0BC1C-A2F0-4199-81E1-7326C8A938B8}
OLETA 110241396 | {6992FFBA-72E0-4D3C-898B-1A95BB5A0A16}
MOLINO 1102384 | {7FCADEEB-07B1-4335-8044-26A9BB50B5B5}
SAN CARLOS 11039148 | {976CCE27-9CBA-45DD-8002-F8BFB98C14D4}
SARATOGA 1103LC16 | {D8FA53F1-4F5D-4A3B-A2ED-DEA75FD0EA10}
ROSSMOOR 1109890534 | {24E172FD-D392-49B4-BDCF-9D27B2C7E92E}
SHINGLE SPRINGS 21099372 | {27097EEC-9CFC-4746-AAF9-881A597C47F0}
FAIRVIEW 2207P304 | {31523F0A-9FD2-41D0-8A36-117080631D88}
VACAVILLE 1111772224 | {7CDC7EE7-6A7B-4AD7-84A2-1F7D5EB3BFDB}
FRENCH GULCH 11022902 | {CBEFA52C-F905-473F-B9BB-602279DBF4B7}
HIGHLANDS 110476156 | {CEFF2CE3-E3F4-40F0-B7FB-D65976C4211A}
GONZALES 110422418 | {33EF8994-00DA-4C8F-AF23-8D41C5EB4753}
LOW GAP 110186816 | {35FAF06A-E239-4015-A854-21F6A4EC4F03}
PEABODY 2108CB | {BC2B156B-5F07-4313-BE60-34EF88AFE911}
CURTIS 170510590 | {EA84943C-5C73-4028-8D85-A074BC119CA8}
PETALUMA C 1109CB | {42F8D929-F3A9-49A8-94C4-A1A9328D939B}
KERN OIL 11044479 | {5ACED025-283C-4765-A990-89285810D6DA}
POINT ARENA 1101474 | {89838C41-7EDA-4C42-BDDA-1698278E3E6F}
LINCOLN 2109265752 | {4E6AFF3A-F560-4015-9A7B-59C83CDB47B7}
NOTRE DAME 1104176446 | {BE4941E8-75D1-4DE2-AD8F-78922C143536}
HALF MOON BAY 1103H80 | {196D5A62-8277-4556-8937-1330E86D299E}
BLUE LAKE 110266454 | {DB40B2E8-0171-47DD-8BAC-EDA4F7194556}
ALLEGHANY 1101183068 | {AFD265E6-8D27-44C3-AE65-AB550E02658A}
PURISIMA 110154728 | {B456B97B-6207-41D3-9457-CFE202A63FCC}
BEAR VALLEY 210190550 | {CE2E0286-475F-4451-81F2-51329124240C}
ROSSMOOR 110192164 | {E76B2183-0811-41C5-8C57-31DB4D93EC1E}
WOODWARD 2108R2860 | {41DA8C6A-A66B-4741-8630-05B8383240D3}
LAKEWOOD 2107474346 | {6A1EF0E0-D264-48CD-9270-B2391364A929}
WOODWARD 210892960 | {8476058D-CCFA-425A-8D9D-8591EF3E3149}
PLACERVILLE 210619732 | {A0663868-57FC-4799-ACA3-0DE33205B8E0}
ROB ROY 2104464844 | {A306B6A6-F4A4-47EC-B2AB-9B74651A417E}
LOW GAP 110137498 | {BD574B29-15C8-4B0E-8A1E-85F74B10E15F}
BIG BASIN 1101136050 | {E247FC6E-157B-4272-AEDD-8C777FFAAD92}
LOS OSITOS 2103606732 | {215C3316-AD64-4D86-B319-9811218FF7C5}
BELMONT 1103543076 | {84C88409-8465-4D6B-B014-0E4B9C728457}
RIO DELL 1102CB | {68D3E51B-D82F-468F-8693-722B02390473}
SALT SPRINGS 210117012 | {6DEB16A6-E94C-4F55-B525-DA7D39192AB7}
CAMP EVERS 210533542 | {AA5C701E-0F96-4151-A44F-2E6809287FB2}
SARATOGA 110460104 | {DAB08854-D3B6-4F8F-8E8C-51427B3E01B1}
WOODWARD 2108979850 | {61F2ACD6-570E-4D22-AC3A-276FF7469BBF}
MOUNTAIN QUARRIES 21011184 | {955B96CF-04BC-4DDA-A99C-F3551BD93482}
LAKEWOOD 2107396264 | {9DA5BB29-24BB-43F8-B179-1425D3AF09F1}
BERKELEY F 1103620294 | {A3A50FD3-D864-4F5A-8B1F-9F554249643F}
SUMMIT 110168706 | {A427B0F7-F35D-4F9B-B915-6E1C81266A58}
LOS COCHES 1102CB | {C48784E3-4EDB-45E6-AEA2-4A807640BDC5}
CLEAR LAKE 1101486 | {4B824BDA-3530-4F86-B304-5BB8EAFD0730}
HOLLISTER 21054018 | {201D4860-5BDE-4AE7-B543-F824A85004DC}
NOTRE DAME 11042028 | {68FC6E44-EFD8-4B52-B283-8EF4B688F460}
LAS GALLINAS A 1106685656 | {7BDFA48E-615C-4CCB-95C0-B267A54E309F}
ALHAMBRA 110595016 | {9A4542AE-EE8F-4BB7-BE2E-76002D6DCF25}
COTATI 110283200 | {E06C85FF-5B48-4064-AE0D-D34C585D0676}
WOODACRE 1102137662 | {C3672683-8002-442C-8DD0-CA97E76D56C3}
PUEBLO 2102600010 | {C5942BEA-FB0B-4F3F-A02A-15F17AB72955}
SISQUOC 110245261 | {B8793525-C43B-4B72-9E84-4F6812828DC2}
MADISON 2101760730 | {0CB657DB-6DA6-4A9D-A1FF-01F4FF1F9C5B}
TASSAJARA 2112791386 | {0D1DD5D5-DD54-49CD-8DC6-C13ECFED047D}
WILLOW CREEK 11032936 | {2C99C690-D2AE-47A9-8969-EBD60FC1E2F7}
CALISTOGA 1101959538 | {07D5D1F0-E088-492A-95F0-C51ED4C7A4B4}
WYANDOTTE 11101954 | {652E0C25-B4E5-4F56-A678-A27ED9716769}
EDENVALE 2105XR392 | {8483E0B5-64AC-44E8-8893-21CFBA8E4B48}
WINDSOR 1102382 | {8BAFFC14-6408-458C-A293-E7A624D7DE6D}
COARSEGOLD 210490356 | {B3FDA245-0020-4744-99E0-2E32EA3113C6}
COALINGA NO 2 11059260 | {B78C04E8-BE41-498A-893C-A7AC253857A0}
SAN RAMON 2103MR279 | {EC3D5092-5EAD-44A6-A8B2-0227C409E453}
DUNBAR 1101904852 | {EE9E2000-1BCF-4D6D-94B0-B0FE09254374}
CLAY 11037142 | {9E89ADDE-355B-4153-8A3A-140410223CE4}
SOBRANTE 1101CB | {AC34AADC-41EC-4F75-A750-22A938BF80E6}
GABILAN 11013034 | {D9D7498B-EECD-46C9-B5F7-8D9ED4F7E924}
TAMARACK 1102482896 | {FB391052-56E6-4289-94C4-964DB7340649}
MORAGA 1105CB | {40049C8F-DAE2-4759-A9B6-0D8AA42C6AC2}
MESA 1101M86 | {8CD02839-6B9C-4A4E-A161-AF3A96F4F1AB}
WILLITS 11044650 | {CBE7DCF1-ECDA-4517-A76B-79D934ABEB82}
GRASS VALLEY 1103CB | {EB087661-42A5-46E0-BB53-1DC1A49FC6AA}
STELLING 111060094 | {FAA8803D-2611-43AC-BDBE-E6661DD92FFB}
SILVERADO 2104646776 | {2B351D0D-34E9-4ED5-B9F6-58321332BC38}
FORT BRAGG A 1101CB | {34DFDDBB-39B7-422C-B7C0-767BF9731AB2}
BOLINAS 1101806 | {52879B9D-A33B-4D4E-99FA-0487B37405B8}
HALF MOON BAY 1101CB | {D114DA17-C3D8-4F00-837D-4551FAA55B77}
WEST POINT 1102CB | {EC11255E-1283-4994-89AE-376C709CBC76}
OILFIELDS 1103N04 | {011DA57D-3361-4E85-BC2A-97718564E64F}
COTATI 1103CB | {181E81CC-8A10-40D6-ABD4-3AD397DDF786}
SALMON CREEK 1101CB | {227E29C2-4875-4BDB-945B-C5CAEB5F0B81}
GUALALA 1111445166 | {69ECBFC6-9041-42D6-B70D-8E6BF5F8976F}
LOS GATOS 110660116 | {86E17BC0-A879-45C0-9429-4A0FD02BA21E}
MARIPOSA 210210880 | {AF85260C-2339-49D2-94BE-A2E04CBD4128}
CAMP EVERS 2106130936 | {B2374312-6A96-4C62-9249-47729A4C1D06}
SALT SPRINGS 21013116 | {DE9905F1-4C65-4778-858E-371103A18BB4}
ANTELOPE 11012656 | {0223D8A4-0FAE-4E90-8B93-4043739FD071}
PUEBLO 1104CB | {065E1455-5FE2-4E00-BCA8-63E4665BA32B}
LAKEVILLE 1102530 | {20EEDFE7-15DE-4AF7-B5E5-DDB50839E523}
PETALUMA C 1109270 | {3706FF29-9CD7-48BA-89F8-13A11ECD321F}
HIGGINS 1110429714 | {E56A3B9A-F6B2-438C-8FDC-DFADF12A0423}
GOLDTREE 1105944608 | {2BB441D5-FA7B-41CB-B4C4-3BB6BA3702C5}
LAKEWOOD 2224568670 | {6C96515F-B6CE-4B5E-91AB-166552C2F0C4}
PAUL SWEET 210737234 | {137C6E91-EFA6-4F4A-9FB1-51BD0ED5008F}
PIT NO 3 21011482 | {23C4AB75-7BD7-4D2C-8DD3-FAC1E53F0F0D}
MADISON 2101888814 | {7332DE5F-6F7A-45B8-8DD4-5630772AAE8E}
HAMILTON BRANCH 11013049 | {B799CE92-A5F5-41AF-A189-4F32E6DC30EA}
PETALUMA C 110856774 | {E5F8D630-F65C-4493-B471-181129A51D2B}
BIG BASIN 1102351054 | {2DB85505-B58C-4180-BE1F-5ECE90BED242}
LE GRAND 1104257152 | {2DA20832-0986-4675-BA93-1E55E4E2B6B0}
HERDLYN 1102CB | {6D42CB7A-C91F-4DBB-9706-F92EF8B0963E}
CLARKSVILLE 2105CB | {9208AF25-E3F3-4F0D-8CE3-550040B29414}
SAN ARDO 110294020 | {A30EDBA7-9AAC-4E4B-A35C-8F3268903239}
BURNEY 110237284 | {B2408DFF-DEFE-41B8-ADEE-8F62D90930D1}
PUEBLO 2103CB | {BBAA1B5B-10DE-4ADA-9508-3668952B4672}
RIO DELL 11028768 | {F40CB029-270F-46C5-9305-F30A68FC7241}
KIRKER 2103CB | {F88B8CE0-AB57-498A-8D97-A3755A2B41A0}
BUCKS CREEK 1102CB | {777DE2C4-ED25-41C9-82DD-E42386BC34EE}
TASSAJARA 2108CB | {7E453EBB-15B5-4455-9C0F-35AB481A3035}
SAN RAFAEL 11081457 | {9D9542F3-BF28-42DE-B61B-60FE0E01870B}
CALPELLA 1101345230 | {CE47E68B-6431-42EF-95CF-00E7CF465463}
MOUNTAIN QUARRIES 2101CB | {D8BA8AE4-C717-4377-92D2-0F59CC0A31DF}
CABRILLO 1103CB | {F3B21B24-5FCC-4918-B9AB-A8B8CD51F711}
FROGTOWN 1702739858 | {1A9CCDAC-B50D-483B-87EA-5C0A6CCF7B4E}
DIVIDE 1101CB | {24B4C5D2-9190-403A-BD5D-182F06265073}
CLOVERDALE 1102670 | {40B1E31D-7977-4CD1-A0DB-03E15686CC3E}
FULTON 1107214 | {82FFCF9A-29C9-4CD0-A5CE-AFFBFF95F55A}
SUMMIT 11016627 | {CD142DCA-BFBC-491B-9C29-D02961854E56}
BELL 1107643778 | {B62CEF1F-B5AF-4B96-9E64-FF58A6B33C79}
ARCATA 1121CB | {B9FFA3B9-62B6-4B90-9671-6A7AB6EDF708}
CORTINA 110149858 | {CE64727D-AFA9-4CB2-B083-0E8C4E6C1F9B}
SANTA ROSA A 1104642 | {DA22FBE8-4AE4-4189-B8A0-D6F473C1FE0F}
CARRIZO PLAINS 1101384116 | {DF118858-83A9-4B97-BE1A-B9801D7678FF}
HICKS 2103XR248 | {F3C9E330-5EFE-42AE-9971-7797E81AA91A}
UKIAH 1111807988 | {183B4AB8-E049-4175-AED7-96F466044CA0}
EEL RIVER 1102CB | {27E2901A-1EBE-4CC0-B5CB-538A633C6C56}
TEMPLETON 2112116402 | {3329F03A-165F-42EE-9423-F38D6F793EB9}
MARIPOSA 210237288 | {38642A96-8776-4716-B709-CC59463C3DA7}
MONROE 210765424 | {3D15A0FB-7F79-449E-9100-AEDACD615B82}
SNEATH LANE 11016525 | {609F8931-DB33-4C51-8B0A-74D7E061F069}
RALSTON 1101100040 | {803AEA1D-DC84-436D-9016-11A398DCA769}
LINCOLN 1101744292 | {BC430285-5DBF-4545-8AE8-96AF6071F68F}
PIT NO 5 1101CB | {B85628F4-AFE8-455E-8E14-4DB09FEDE759}
GEYSERVILLE 1102331444 | {B7169D14-D576-4EBC-83AD-DD429DE5E777}
KONOCTI 110275382 | {3635FD5D-8230-40C4-B52D-81B9839A55A9}
OILFIELDS 1103451760 | {5FF9C387-FCBA-4CB4-A5E3-8021D551E54B}
MENLO 11028952 | {56C84CD8-CFAF-4218-882A-B93134A396EB}
MARTELL 110292172 | {90FE2AC1-F695-42FF-8EBC-FB82E3B206C0}
SAN RAMON 2106CB | {9140C526-29BF-4637-A62D-8BE823C11E2E}
MORGAN HILL 2111919856 | {9425E865-2193-4800-9F65-36F91B76A0A9}
WILLOW CREEK 1101729000 | {2D4A5008-1C90-406A-A2B7-E4FA7A353F8A}
TULUCAY 11012280 | {D5040DDA-C582-40B5-8A53-2E3901DC0B08}
STOREY 11095580 | {F6521ECD-18B4-4A6C-9FB9-B5018A20E90A}
BRUNSWICK 1107969778 | {779A3152-24AF-4508-86CF-CDD542CFE4FC}
PHILO 11013700 | {1642E076-5F84-4CD5-A49F-E61735A3F10D}
VASCO 1102MR178 | {C757B1E5-E864-41C5-8F1F-450BE13C3852}
KONOCTI 1102CB | {CB616978-006D-49B9-885E-104BFB9EEDAF}
ANDERSON 1103226050 | {F12B9CD1-046D-40CE-8D1D-9858A5F6226D}
GABILAN 1101270626 | {6D5B17B5-960C-48B4-806D-BF9DA1A8A3B0}
POTTER VALLEY P H 110537476 | {216E9E12-5043-456A-946D-A8BF7CCC2C71}
PACIFIC GROVE 04222608 | {45F66B28-3708-48B3-AEFE-0F1CE66015AD}
TASSAJARA 2108189700 | {8C428159-8CA3-458B-A6CE-F60FA4399D97}
CASTRO VALLEY 1102840916 | {B3742266-0A6B-41B7-BDF6-4E4FF8E74B2F}
WYANDOTTE 110777578 | {E0470028-6FEE-4E7A-BA03-DFBD06B93819}
OCEANO 1104Q04 | {EF084BAC-E8B6-45D7-885C-1A50430DEB23}
OAKLAND J 1102159816 | {859F64C2-C27C-450D-B243-6E6F38B09662}
TRIDAM POWERHOUSE 2101CB | {865551D3-0A3E-4056-A08C-B0CD8C35D70A}
BALCH NO 1 1101105414 | {AE86CCC0-9A32-4ECB-B70D-2CCE4DDF5F1F}
RED BLUFF 11041302 | {D6DFAF59-685A-49A8-AAFF-CFC87952A858}
WILLITS 110337504 | {00459A21-49A7-4C9F-B533-C9081A2B5652}
HALF MOON BAY 11026097 | {04338CCA-7EF9-409D-9ECF-B4834D579CE2}
MORGAN HILL 2109CB | {40746EE4-53DF-4A3F-B597-DD5CDFE06F6F}
GREEN VALLEY 2101128618 | {47221F99-4C03-4459-B587-C3379C27406E}
KONOCTI 11084041 | {D3BC4C4A-6AD6-4D57-ADFE-ACA0E6607A3B}
CURTIS 170511790 | {705B5A79-F7F3-41CE-925F-797105088580}
CORNING 110135974 | {A9C774C3-1428-4B46-A99D-50AD5766C649}
ALTO 1124635972 | {09E5B2C8-C5E7-4FCA-92E9-55DF7D2FE60B}
CORRAL 110214028 | {485BC0B3-AC72-4623-B01D-27E2B69AFA49}
RIO DELL 11028852 | {5E0A571A-4E57-4C9B-881D-B7EA8F011B21}
ANTELOPE 1102CB | {C3268251-FFC0-4729-94B8-55800124A207}
OILFIELDS 1103N42 | {CDC6585C-22C0-4542-A949-CDEE5502EA22}
HARTLEY 1101336932 | {CE237446-8B77-4B6F-A151-0796DF2727A1}
LOS GATOS 1107CB | {F9DF48B9-C722-406C-B401-60189B57E89A}
MADISON 11057712 | {2C14C00C-0CAD-4E64-99CF-10447EDEECD2}
LUCERNE 1106439842 | {97FE1380-8BE3-42D2-B6E3-D4904D2C8F20}
PEORIA 170510580 | {59D5B837-86E5-4FF6-AEF5-91D544FDF3B9}
LUCERNE 1106CB | {64C6F4FE-9745-4B83-9BA2-6905B1D464FF}
SANTA ROSA A 1111147198 | {67140A91-07CE-4EA7-9BA4-49867563AE33}
UKIAH 1113968652 | {81BDBB43-850C-4250-9194-B1A69ADA9BF8}
BANGOR 1101626862 | {F430F9BA-4822-49EF-972E-D271E55910BA}
JARVIS 1101467034 | {C606228A-087B-437D-9A9F-1FD57375B95A}
FITCH MOUNTAIN 1113154 | {E5E424DC-C8C0-4A20-B0C0-11A950F19719}
SAN RAFAEL 1105344 | {73B969AA-9422-4313-8799-666FFF6134B7}
SAUSALITO 1102758798 | {535449DD-A4B3-4AA9-AB71-3DA62C691B7C}
LE GRAND 11104600 | {B9B7E2CF-8396-4913-AA14-43F1BD9F0A32}
GATES 1106755338 | {BD3133DA-EDF7-4B1E-B188-9C3D48C9C62F}
TEMPLETON 2109868666 | {23FDF1DB-782E-4000-92DD-5A064AF483AC}
MIRABEL 1102503294 | {F1ABA083-74D1-4C3F-BF47-7B099CCA3C8E}
RALSTON 11022028 | {24F66B4A-94A3-4B18-925C-2BF0060C2435}
UKIAH 1113CB | {57AE83F3-7C35-4A08-BEA4-B10AAC4F4015}
HOLLISTER 21044068 | {71FF4B1A-5585-49E7-A745-ED1E027013C4}
PARADISE 110353544 | {5B855AD3-6AFC-4928-AA0B-CD83074FF6CB}
HICKS 1116CB | {887C42B0-874F-48B4-B368-C0A3D7EE375F}
MARTELL 110299214 | {9F8CA5FE-A9BA-4EDC-994E-2CFB4235B5A0}
SHINGLE SPRINGS 210961892 | {FE625157-4A14-40D2-B1D3-1A0A93F86C88}
MOUNTAIN QUARRIES 21016953 | {6752B4B6-FF0C-4C57-ADC9-D57090816B6D}
SWIFT 2102XR440 | {BE64DC1C-3443-4966-940E-5A564C032974}
PUEBLO 2102378860 | {0747EA03-0104-4C39-B232-B182B2FD4D1E}
HALF MOON BAY 1103389114 | {2F83CE4E-0855-4D8B-B1C5-D4FFD94A6F8F}
CROWS LANDING 110190600 | {5A5D22BF-24BA-433C-9E32-EE55B80DC70A}
BLUE LAKE 110294240 | {6705332E-2929-4E9F-8E1A-9444B006678B}
PASO ROBLES 1103351084 | {7E3660A3-92BC-4694-A2D5-248E2793B9A8}
MESA 1103M72 | {C0ABDB73-42C4-4D60-9BB1-4077EF0BE355}
FITCH MOUNTAIN 1113CB | {0452ACFB-6610-4670-BD1F-C0548BB4EE02}
SANTA ROSA A 111095984 | {116DE352-2E18-465B-A34B-4DEAE4404EE5}
GERBER 1102190339 | {51D7DA46-9CAC-46EE-9575-3C307DF390C6}
BRIDGEVILLE 1102CB | {5393CBB1-CE75-4399-B6C7-25EB732D48AF}
ELK 110137434 | {6922CCC5-514B-4036-B876-FA769B5FF66C}
TRES PINOS 1111203126 | {BD94B291-9C0B-4C28-8C7B-50F4F86D7051}
SAN RAFAEL 1108322 | {9D9542F3-BF28-42DE-B61B-60FE0E01870B}
SAN ARDO 1101650772 | {B23131D9-B581-40FA-88C0-EEDBAEACA625}
PUTAH CREEK 110242982 | {EC7E3E82-534C-45F0-825C-A06402B7C3CE}
MC KEE 1107CB | {0AA07E65-EBF5-454E-BE3D-8A46CCE84946}
PENRYN 11032198 | {15328E03-B147-4A5F-A6DD-FF57B3032B26}
WATSONVILLE 21015470 | {2C7BC800-10C3-4DC0-9802-A63A1E430DC6}
PUEBLO 2102618 | {2D821F7B-3CD2-4C8D-9060-9FD2240F0305}
CASTRO VALLEY 11107742 | {217855BB-2EFA-4F5A-897E-1A1792604994}
PUEBLO 2103489964 | {5AAB74F0-F546-46F3-9229-78031722C605}
CURTIS 170234426 | {897848FB-F125-46A8-B9E9-7A6CE5229B91}
MADISON 210189332 | {D7243FB0-38B4-4640-8C10-2CD25C9CD868}
PAUL SWEET 2104867374 | {9E32E9CD-A939-47B7-8D32-52540B68C5C6}
PANOCHE 1103107270 | {9F8F9B54-61D9-473A-8686-65EC8068C547}
VALLEY VIEW 1105305072 | {A9274254-950F-4772-BD6F-0C6FB4FEF4A4}
MOLINO 11043281 | {5465105C-2E1E-47CE-8A44-120776A3EE22}
COTATI 1103446 | {181E81CC-8A10-40D6-ABD4-3AD397DDF786}
CAMP EVERS 210311046 | {DC46DF0C-E79C-47C3-8E88-AF56F3C9F267}
HOLLISTER 21044403 | {71FF4B1A-5585-49E7-A745-ED1E027013C4}
DEL MONTE 21049496 | {F5363A17-6294-4FBA-A5E9-297DB437E9E9}
OILFIELDS 1102CB | {59A6DBF3-2585-475E-ABD4-6C09185E8D33}
MOLINO 1104468882 | {8788BBFA-A2B3-4787-825E-E3E47FE6B9D7}
ALHAMBRA 1102CB | {CC913DB3-6A51-493D-BE11-D5EAF399B0A8}
SPRING GAP 1702188426 | {430BD33F-FEB4-414F-BF1F-8CCB997A468A}
LAS AROMAS 04013342 | {4892CAAF-65E7-4660-A10F-F15BB35B52DD}
APPLE HILL 2102CB | {5DC9E720-795B-432E-BA68-667FD0BD630A}
SONOMA 1107126 | {8F27A86E-670B-4331-ABF1-9BA9A6222879}
PRUNEDALE 110725695 | {9055CD6F-1385-4DAA-B189-3CEA20BFACDF}
MILPITAS 1109XR370 | {D897A506-3C26-4AA6-AE93-1BA5129BA14D}
LINCOLN 1104997576 | {302C4176-4830-4D29-8953-2FECE7A076EF}
PUEBLO 110298730 | {1AE19971-F682-43DD-B35E-DF767DF7D39D}
PASO ROBLES 1103N02 | {75A395F4-172A-4FF6-844A-F6A1B941CE83}
ROB ROY 2105439972 | {C5524593-3C0F-436B-8CBC-A27F9517C316}
HALSEY 11015731 | {FA7F836A-C8A0-42D3-8E43-389B5B7AEC7D}
HALF MOON BAY 110155210 | {2DBAB1CF-D3D1-4CC0-A406-0CDA12AB2548}
SONOMA 1107294 | {35F57AD2-0209-4C33-8C6F-331DBFF4518F}
LUCERNE 1103721 | {4100FBA2-C458-44C1-B317-2EE92F5C04AB}
SAN JOAQUIN #2 1103CB | {65F04F88-77E2-416B-8718-E84D34A90738}
SAUSALITO 1101331806 | {8796524B-A1FD-4229-B2E4-3A9BEDC52EE3}
TRINIDAD 110233936 | {8F30516F-9B17-41F9-982D-7C654517E070}
FLINT 110138570 | {68DF9E12-6736-4943-BDEF-9FA6962872B3}
OAKLAND K 1102CR014 | {B5EF99C1-ABA3-48FB-9EE2-B54D16D47CE4}
CASTRO VALLEY 1110MR273 | {C6807FEA-40B3-41BE-80F1-095A0F67FBA5}
SAN ARDO 11027000 | {A30EDBA7-9AAC-4E4B-A35C-8F3268903239}
MONTICELLO 1101630 | {EC7479AE-9F4D-4362-8AF7-E7B5EDC2ECC7}
OLEMA 1101416 | {ED6FC814-3841-4AC9-A379-44E5BC33C241}
SAN BENITO 210488772 | {1ED2FD17-894E-4836-A934-5237FD5BF8EA}
FORT ORD 11019516 | {66CA8537-4E7C-48FF-82D7-109E7EF7B7FC}
SANTA ROSA A 1111CB | {4D91C141-515F-4F14-8290-C8268E13D106}
LAURELES 11122142 | {5E20B311-BB0A-4C97-B880-E9EFFB1FD21F}
PLACERVILLE 1109CB | {C4A51841-0308-49DA-9C27-2509F9C64A2D}
COTTONWOOD 11031616 | {DB1CB0BF-953F-4047-B280-2F768227CB6A}
WOODSIDE 1102CB | {1A7707ED-44BC-402D-AC12-5D698199529B}
NOTRE DAME 11022038 | {1BA9278D-6A82-456C-AB93-CADDEAC99F13}
ROSSMOOR 1104CB | {2B644C8A-1232-4056-B6E3-B09CD0D7D415}
LLAGAS 2107374344 | {40BE7D0D-D7B9-4C64-B06B-437270976420}
SANTA ROSA A 111098988 | {422CE5F4-0FBE-4EEC-A8C2-C4BEFA9D6650}
COPPERMINE 110438474 | {E99FC5E0-5A56-4D2F-900E-4A688BBB4069}
MARTELL 1101766574 | {2C34AC51-01A3-44C9-B45A-F5786A7BA8F0}
SAN LUIS OBISPO 1107V58 | {3B54DCC0-9E34-4A0D-BB42-D31181D2C4D7}
MESA 1103M64 | {88268CAB-906C-4CD2-A318-8F214ED37905}
DOBBINS 110191464 | {93C56D43-333C-4331-959E-24C064CB9C39}
PUEBLO 1105426584 | {78AAB710-6DDE-407F-827D-71666B977FA6}
DAIRYVILLE 1101147562 | {7E805BB6-FA35-4404-BBBB-4801C3E98DDD}
WILDWOOD 11011454 | {D78DCFCA-A3F5-48E7-AD4B-409B173DF385}
DUNBAR 1103596218 | {E64AC1A3-7B00-44C4-B413-8ED8E1419B88}
STELLING 111160020 | {04E89A01-7DB9-4E29-BE3B-E16251E3C1EC}
BRENTWOOD 211199210 | {E5AF8736-114E-4C01-9F04-EE6BE2C6FDFA}
LOCKEFORD 210212468 | {34045FAB-FD0E-4469-952F-B8E16E6D8945}
PACIFIC GROVE 04222614 | {45F66B28-3708-48B3-AEFE-0F1CE66015AD}
SONOMA 1102441730 | {4F0353F4-993B-4228-9665-B8F36201BBD8}
APPLE HILL 1104236062 | {78CB65A8-D5F1-4141-9775-453719688C2B}
RED BLUFF 1101CB | {DB04D68A-27FA-4FDB-A3B9-5AB0FF58478F}
GRASS VALLEY 1102CB | {343B25CA-8FEF-457F-8025-88904C29692A}
BERESFORD 04039154 | {59262E1A-A9BD-4C08-8147-3EF20A86F7EA}
LAURELES 1111CB | {6ADA1603-F38C-494F-A594-401AD43EFE67}
MONTE RIO 1113524 | {8C8983C8-884C-4E70-BBB6-36F59CD80D78}
HAMMONDS 110212140 | {FD894490-402E-4AE2-A8E0-2A3DAB4F2C46}
FRENCH GULCH 11011892 | {EEFD67FE-817D-4F21-AFBD-03D493187270}
LUCERNE 1103630 | {F34B7A71-9435-4BB4-952A-AC8430FF4984}
RISING RIVER 11019032 | {8F4CC463-393C-4538-A842-1BB0282A8F17}
HALF MOON BAY 110265568 | {A98607D5-0034-49E5-BBAB-142F1C1E415F}
COTATI 1103132 | {D681E6AF-06CA-4983-B4FB-ED08B0DAD260}
MC ARTHUR 110290546 | {E9334D2F-2952-4052-8ADD-E3F42DB77666}
CALAVERAS CEMENT 1101CB | {16B948B9-B372-45A4-B29D-56B8F2A70B74}
PEABODY 2113CB | {463CEDCD-A864-4BE7-A495-4562C479EEC4}
JAMESON 1105466348 | {8E99B7C2-09C6-4CCD-84A3-45313788DF3F}
WHITMORE 11011594 | {CA013557-36E2-4043-ADB2-0CAC45D0FC29}
BELMONT 110347804 | {84C88409-8465-4D6B-B014-0E4B9C728457}
ANTELOPE 1101318686 | {946AC549-8FBD-4BEB-87DA-8E29BFBBE9D4}
CAMP EVERS 210311056 | {C4E0B9E0-CB11-4C51-9BF2-0A1F8C067741}
OILFIELDS 1103370932 | {28C87B96-17F1-4B77-AC44-88E083C74B6C}
BUTTE 11032104 | {FB7A2293-9439-48C4-B179-5F6C84D82D44}
SNEATH LANE 110611792 | {66ED3CF0-2002-44E6-BE2F-18363B4298A8}
PENRYN 110551676 | {6FA4A1F6-3AB8-4114-8002-DF4E0174192B}
MESA 1103M62 | {A1CF0EFC-4EE4-402B-B14C-F1C9D9E90F01}
PASO ROBLES 1107CB | {BF9A1CFA-5044-466A-9DCB-672D048DD99A}
HAMMONDS 11019760 | {EAC018D0-6E0A-45C6-BAE5-BAE564C53C44}
TEMPLETON 2113A08 | {ED2FD62D-73A2-48E2-BABA-F5CBA9685A6D}
NARROWS 21052748 | {EEAC938D-675B-4361-87B7-7942FA5DF8E7}
ARBUCKLE 1104969486 | {09231E8B-9807-445C-B8AC-5325493AFFCC}
ROSSMOOR 110181770 | {167EB25B-4A6A-4910-B109-DED2BEFF695B}
BRUNSWICK 110765574 | {22F4E53D-20D9-4A9C-BDCD-9693C219E892}
CORTINA 11013058 | {E3B77E93-BB57-4588-891B-4456F675EF56}
CALISTOGA 1102706 | {AEB996A6-B3E6-422B-A668-DF66D3A05824}
ALLEGHANY 1101804 | {B02385C8-6373-4D81-ABD4-7C98960F9245}
ORO LOMA 11069790 | {C28605C3-668C-4B5C-ADA0-9056DAF39EFD}
UKIAH 1115534 | {CD599840-F925-4A8F-AC72-601D0F3A1898}
BOLINAS 110137034 | {92DF57CB-130C-4B97-B59B-998A6C49E6E1}
DEL MONTE 21042624 | {F5363A17-6294-4FBA-A5E9-297DB437E9E9}
SAN JOAQUIN #3 110210342 | {F2F4DFE2-A71E-4AEB-AA05-9FF7D56E28F8}
KONOCTI 11084037 | {D3BC4C4A-6AD6-4D57-ADFE-ACA0E6607A3B}
LOW GAP 1101750090 | {7EAB9CA9-F4EA-480A-8BE4-2E97F9009D2B}
DEL MAR 210938684 | {970BC050-24B8-4916-A013-B639A58BC60E}
FELLOWS 21041052 | {B4133E9A-3C47-443C-9B0E-8525C1EE28EC}
JESSUP 110276068 | {B75A956B-8FBE-4735-92D0-A851A9ED4A9E}
FRANKLIN 1104CB | {DDFFEADB-3F2B-4296-80F5-9B1536EA3D55}
TIDEWATER 210447828 | {19823827-C5EA-4E2D-9FF7-7BB963BC816B}
OAKHURST 11035120 | {36CCC1E6-2517-4B50-80DA-A74340CF2F3A}
CLEAR LAKE 1101444 | {55694D06-24E9-4D6D-8BD5-E5D434DB5805}
GEYSERVILLE 1102756 | {5A3AA98B-24A2-41A0-8E61-B5A0B5E2F3E7}
NAPA 11121302 | {605680BF-CE15-4E43-86C0-2D915CDAFCDB}
ANDERSON 11011752 | {ABE6F062-1CE8-44B2-8445-67D100174B10}
VIEJO 22049540 | {D3AE8800-862E-498F-9908-541EA621BA7E}
MIWUK 1701360164 | {E8F5F8AF-6EC9-4C69-835B-E53C764AC834}
MIDDLETOWN 1101171414 | {4E6A64C0-71D5-4A3E-830D-222E13830247}
PRUNEDALE 1110826224 | {664C5E09-6BFA-4699-B652-D7925B82EDA0}
TASSAJARA 21032705 | {C740351C-623B-4A79-8F81-B59FA4E58E72}
MADISON 210120052 | {3606619A-937D-46E3-AFC7-2B9E8CB032C3}
STAFFORD 11021202 | {07D78386-6A73-46DA-81CA-B20D2445579F}
CLARKSVILLE 210551478 | {0F59AF2F-5869-40D3-A6B5-13E6D7B47101}
WOODSIDE 11049030 | {24F38127-D3B0-46CD-A96D-4474F1F7C2CF}
MORGAN HILL 2106CB | {2C56B704-0B48-474B-86AD-67CE86231708}
HIGHLANDS 110487040 | {4153AD52-F0C3-4F94-B9A7-DBFADEA8B1B3}
WYANDOTTE 11095575 | {CDE1CEEE-8C9B-4065-8C9F-F4DC3E571419}
LAS GALLINAS A 1105532 | {B4DFAE90-941A-416C-9750-49FB5BAA5F55}
WHITMORE 1101CB | {E0835FD3-053C-4202-87EB-465B52D17969}
GIRVAN 11011636 | {2A2FAB19-EBE2-405E-9DCE-8FB9750FB831}
MORGAN HILL 210542348 | {2DBAAA9C-8985-4692-9A1B-CC370D239D9B}
RAWSON 1103428534 | {4FE71C2A-D73C-4875-8301-3BC6248AF0F6}
HUMBOLDT BAY 11024714 | {712389D7-97A8-43EF-99E1-6A4B64E5B114}
SAN LEANDRO U 1109CR182 | {A2C189F4-1155-43D0-9466-3E701D18918E}
ALLEGHANY 11011101/2-B | {FD2262BF-C160-4434-8E95-55FF0A0B15F6}
MENDOCINO 110148750 | {EF680142-96BC-4632-8839-A0A3D923AC61}
HIGHLANDS 110439458 | {F73918F2-BDFA-403D-8839-D569F0C45575}
ROB ROY 210571630 | {7097C41D-4FD9-4503-BEF9-0B96E72F7C88}
AUBERRY 110237466 | {72B3FD6E-4E00-4CD9-8668-70733AC266B2}
MENLO 1102331044 | {86766416-7CB2-4969-8319-B838E7BDEB74}
STELLING 1110733294 | {877E8EF7-F426-4EC0-9032-6E0C314907A6}
CAMP EVERS 210512590 | {9C7B2B92-FC22-48B4-B1A3-9DC57E45ACA3}
CHOLAME 21025597 | {C3648DC1-A8A4-411C-BC09-DF15A6A8CCC0}
PANORAMA 11021526 | {D4F4CD74-DB1C-49F4-9D89-1A434E6A2652}
HORSESHOE 1101416226 | {DDC5A35F-31F2-4622-90DD-F12D8635E350}
EL DORADO PH 210113532 | {1AECFC8B-BC7B-4454-BB87-FD8F012E171A}
MORGAN HILL 2106XR002 | {2D5D4B5A-C41C-47E0-8A3E-3313CAAFF1F2}
LUCERNE 110676850 | {97FE1380-8BE3-42D2-B6E3-D4904D2C8F20}
BELLEVUE 2103364 | {105045E7-1917-46B4-B5AB-FC5617125FFB}
TEMPLETON 2108CB | {3F210877-7C55-4139-88CB-B237BD20F584}
FRENCH GULCH 11021462 | {673B1BD0-3EFA-4599-AB2C-B37C28829526}
CLARKSVILLE 2109CB | {7686CD28-0AD3-49A6-802B-4CD3DF814107}
MONTE RIO 1111506 | {C4F8319D-D897-4280-8AA8-30DB11490475}
RADUM 1105MR782 | {597A5CEE-82F6-4D96-ADE3-E225B0B39A15}
PASO ROBLES 110195810 | {EDB8367F-06AF-4145-97CC-734EE720D9A7}
SHINGLE SPRINGS 1103CB | {21717BF3-E14B-476C-94A8-5495C36BA027}
UKIAH 1114408 | {51D9F3E7-D9FC-4F6D-B9B5-400B76D74D25}
SAN RAFAEL 1108CB | {8BC2020E-62FB-478E-A2C9-53FD6549A421}
IONE 1101CB | {9D5BFE02-DE54-49D0-8A6C-80BCABF7CBD7}
CHALLENGE 1102CB | {C71A58EE-DA31-4CE3-8F9B-4D615671BE3A}
CALPELLA 1101542 | {C7347FC3-B613-4AAE-82AC-3F7111D01C04}
PERRY 110185870 | {30D7373B-D31B-4D5D-82BF-42F5B4929DAA}
MAXWELL 1105910362 | {F3456836-F540-4C5A-8C4E-BB2A14482B86}
DUNBAR 1102448 | {19F00F46-8DF2-4369-8C23-B78BEB3B793E}
MC ARTHUR 11011490 | {36BB4228-C5D9-43D2-9CAD-2C575004638F}
SONOMA 1106376 | {3704160C-56F4-464C-949D-B0353C9BFECB}
MONTICELLO 11011780 | {4904A78C-4F30-4D7A-889F-B688535D7066}
ROB ROY 210511028 | {FFC04C14-5557-4FC3-9795-3587569ECB50}
ROSSMOOR 110493664 | {D2330A0C-459B-4F6C-BE3B-0AABB85A2AF8}
SHADY GLEN 110248894 | {1F323A0D-3C08-4F07-A424-801F7C955EF5}
SUNOL 110148180 | {4F589EB1-04B1-4740-ACAC-1766B4EEFC97}
LAMONT 11044113 | {66C7A1C8-61A2-402A-9225-A301C2795EB0}
KERN OIL 1104CB | {9F23EB64-F3B4-4CBF-BA80-2578C2F13B01}
PENRYN 1103660 | {E80D319C-D01D-4A69-9210-7A23DDD13D1F}
OAKLAND X 1106CB | {FEA3C3F3-959E-472A-9376-926585E20D05}
TASSAJARA 210875010 | {FFB03A86-39E6-48B0-9234-84638A1DF85F}
LOS GATOS 110760024 | {0DA35336-0B04-4E75-961E-D514D30699B0}
PANORAMA 11019092 | {18BCFDD7-AD26-4B95-9A8E-1B5EFFBCB7AF}
ANDERSON 110299392 | {82EAFCF1-F1E6-41E8-A0B3-25F73ADE0F7A}
OAKLAND J 1105CR132 | {99760D35-3D8A-43D4-9A8C-B787B6697406}
RESEARCH 2102644462 | {27A7DE88-D994-4126-81BF-F7729B85F967}
BLUE LAKE 11021024 | {3C7601AF-6F6C-4334-9C5E-41DFDCEC0722}
CLARKSVILLE 2103CB | {582D525E-AEFD-49AD-B483-1141532B60A7}
MCKITTRICK 1101CB | {5A307946-5CD5-4050-AB0D-2E455B17B341}
DUNLAP 11037170 | {733D4902-C475-4A3B-A2B1-E7586C4C7AE4}
SISQUOC 1102113874 | {92EB9460-E02A-4A24-A181-995BD1F9489E}
SAN ARDO 1102323708 | {531BE6B3-C431-4299-B6F9-340C07FC847B}
OROSI 11027948F | {283D946E-F745-4F7C-ACE9-D6EB2A3744AC}
RINCON 1103CB | {2A534FE3-EF17-402C-9700-8C33AB455C66}
PAUL SWEET 2102168368 | {720DB739-6D0D-4A39-B396-1773770EDF72}
BELLEVUE 2103478 | {105045E7-1917-46B4-B5AB-FC5617125FFB}
NOTRE DAME 1102CB | {1BA9278D-6A82-456C-AB93-CADDEAC99F13}
MC KEE 1108XR302 | {41444F7B-0DEF-4E7D-BF1A-12A503159CC6}
BEAR VALLEY 2105293732 | {ABB0CC40-D4C3-4C01-9BEA-4570C6C0972F}
DIVIDE 1101M78 | {D82C0681-14F5-4168-A5B8-47CCE62ECA70}
GOLDTREE 1108961060 | {F40F9B94-B69D-4B7D-86DD-125E8D7AC87E}
SEACLIFF 0402CB | {F85FD245-E951-4FD5-89D8-9A5F2519071F}
PUTAH CREEK 1105665952 | {B44C5067-6D0E-4713-9558-13070DEDA962}
SERRAMONTE 110412705 | {5AC2A44E-A5CE-4631-A5D0-59B8F85FCDA2}
CLOVERDALE 1102672 | {B86F1274-5A5C-436E-B792-43E98848CB75}
PALMER 1101CB | {EC1B6C10-3B8B-426D-86D3-39EE85F08618}
CLOVERDALE 110247214 | {08D74C7F-8D6E-4EDB-8355-DEA79828121D}
CAROLANDS 0402CB | {6CB7829C-D7F4-4692-906A-EB06183783C1}
MARTELL 1102CB | {74DC8F54-4589-4421-89BC-E98BD5920B33}
VACAVILLE 11046542 | {82F07A4A-6ADB-4C33-B8E8-182597EEA877}
OILFIELDS 1103643162 | {28C87B96-17F1-4B77-AC44-88E083C74B6C}
CAMP EVERS 210510294 | {9A213A9A-1023-49F7-ABDF-C909666FFA23}
STOREY 11095270 | {A7B17A78-9253-49C0-9DCD-46F08F0C14C3}
MIRABEL 1101774276 | {403F76F2-1613-4EA6-AE9B-C646D2E770BD}
HERDLYN 1102B569R | {6D42CB7A-C91F-4DBB-9706-F92EF8B0963E}
TIVY VALLEY 1107248306 | {BE7D1774-079A-4F76-A335-3394843B4D82}
LAKEWOOD 2223CB | {DAC222F6-911D-41F8-A045-FDB37DA63ECF}
WEST POINT 110112256 | {10618A90-ED86-44CD-8B76-773E3BF2AE42}
ROSSMOOR 1102457174 | {1EF93EFB-6EC5-43CC-BDCD-9E975921D8A6}
WHEELER RIDGE 110183646 | {E4E8B6C8-61FB-4D05-90A7-1AEC2AB09918}
CARNERAS 1103430670 | {4F63DE1D-7CBF-4AAC-B035-BBB7D4E5B891}
CAMP EVERS 210510786 | {5510A025-B5B2-46F0-8DC5-ADBD6BE8276E}
FULTON 1107CB | {72AE5EDE-AC15-4265-AF32-67B0F370C217}
PEORIA 17041837 | {B68E2FC5-9A54-49EB-9258-EB6EA1DB9D61}
GRASS VALLEY 1101750804 | {B0F41A34-F762-41B4-ACDB-9C11F27E225A}
HIGHLANDS 11031282 | {ADF7CDB1-D7EE-4238-AD1F-3FDE0907FF69}
BRUNSWICK 1105297538 | {E1779AD2-4579-4092-9EC8-FEE4F5C13371}
ECHO SUMMIT 1101889106 | {F991AA46-5F55-4799-A06C-6C07D5355682}
OAKHURST 110311900 | {0DA18697-929C-4AB7-9F79-F379F7D7D5E9}
BELL 111056214 | {451291E3-291B-4A82-B036-A633A631A6D2}
PLACERVILLE 11118582 | {3783BA8A-4769-47A2-BDB8-6B31F03E9521}
HIGGINS 110432747 | {6831EC63-2DE1-4FA9-8E52-ECEB96F95CDF}
SONOMA 11071309 | {35F57AD2-0209-4C33-8C6F-331DBFF4518F}
ELECTRA 11011238 | {79D3DE13-EDFE-4798-9C48-8D9438D496D5}
CAMBRIA 1102W50 | {98891E8E-A196-4377-815F-B850671211F6}
OAKLAND K 1101CR346 | {BAD456A1-64C0-4C58-9244-4CB0B49EFF5E}
VINEYARD 2107MR747 | {E0DA3FA9-134E-46BA-BA63-A138252A7798}
MORGAN HILL 2104152774 | {425217ED-9250-4ACE-9F11-E30531EC148C}
OAKLAND X 1107CR428 | {44E2AC7C-1F72-42EE-8609-62087EC4A35D}
CAROLANDS 040484797 | {F73FE32B-0064-4963-BD0F-96E252B7B701}
LOS GATOS 110760114 | {9B2D8A48-20CB-454C-BA37-343177467945}
CAMP EVERS 210510996 | {9C524D92-A5C3-4391-A08F-2E5640BEA3EC}
MONROE 2103848530 | {AD6C9BC3-922D-4820-9E11-0EE6E0677452}
ATASCADERO 1103A18 | {1D2DA1C9-B2A9-4713-BA25-DD6CA0F657BB}
DEL MONTE 2103468158 | {6129877C-0FCC-4F26-BBF6-7A6117D5D7AC}
BURNEY 1102272636 | {C4DDB13D-8C8F-4D3D-860D-833D982C6826}
LUCERNE 11031663 | {F34B7A71-9435-4BB4-952A-AC8430FF4984}
BIG BASIN 110210254 | {4260F392-8CF2-458A-B972-28FCF38AA586}
PINE GROVE 1102696442 | {7DC1A977-4A68-4FDA-A273-23C4AF2AACBE}
CLARKSVILLE 2103547420 | {9CDC45A1-1E7F-49E1-BDE9-134E92A79E35}
PAUL SWEET 210312075 | {BA3D6A76-5335-48A7-9116-A38FBA76779B}
MIWUK 17028130 | {BED4FF87-AC4B-4CCF-ACF6-259B2364BA72}
HERDLYN 1102608254 | {CE97333C-59D7-4EFC-8B71-0C4A3CF5BCEE}
WESTLEY 1101463982 | {E05B0763-14F9-4FE9-A6CE-D2FD7DA8396A}
CAROLANDS 04038980 | {4FDA6CDB-0E5F-4B76-BABA-C5F84B9DCB82}
APPLE HILL 210289934 | {4065F493-7B96-40A7-8EE5-29CF10B90CA4}
ELK 11011298 | {EAE624C5-B9BF-4507-A953-B6224BD5618E}
MAXWELL 1105429752 | {F3456836-F540-4C5A-8C4E-BB2A14482B86}
MORAGA 1101121620 | {27593588-F872-4832-9B66-0B2A2D32D4A3}
MORGAN HILL 2111XR062 | {7A50E1CD-B005-4744-BD76-86E8006C9FCE}
SAN CARLOS 11049052 | {3B6CB851-40C4-4A4E-8C82-B4A7B88943F2}
HOLLISTER 21024908 | {17B07670-0E53-4796-89E8-790E1D545BFE}
COARSEGOLD 2104905960 | {D13472F2-B468-44F9-94C6-B98D2DACFC98}
ALTO 112088190 | {FB7430F5-69AD-42E3-8B5B-42F0E8A7B1F0}
DEL MONTE 21029680 | {6CCE4F90-013B-444F-9BDA-6C6A4EE75374}
FULTON 1102287172 | {1B09A511-4056-470A-B00D-4FB4522380B2}
WRIGHT 111011942 | {ABB28193-DF6D-40B9-BA16-1713A8EF4B58}
OAKHURST 1101910120 | {2CDF7848-B063-4FC4-9C52-AE29AA49D3FF}
JESSUP 11012839 | {4BBBA9F5-2A5C-430F-82E9-5C32AA8B7737}
BRUNSWICK 11052210 | {061B0891-9632-4691-9CF7-EFB012B2AC41}
SPENCE 1102276712 | {4738DB4A-9FDF-4C6A-833D-7B9AB689B6AF}
PEORIA 170459596 | {73788ED7-3EB0-46BC-B768-F67E7458E32E}
BIG BASIN 110165444 | {E247FC6E-157B-4272-AEDD-8C777FFAAD92}
FORT BRAGG A 11014622 | {FD379B27-6785-4E43-84D1-7E22C4EB286F}
POINT ARENA 110198224 | {72A22D65-E2E8-42C5-897F-8C8D23CE5089}
DOLAN ROAD 1101672110 | {18BD8A9E-072B-4ADD-8F74-F890B89581F0}
OAKLAND J 1102CR254 | {67E8FE67-3DED-400C-8861-70D52FCAFB0E}
BIG MEADOWS 21012586 | {70718D9A-2BF1-4C9C-AEE6-9A1119246050}
PUEBLO 2102279478 | {8B54D8DE-AFC7-4F5A-B048-1B02D25789A8}
HOLLISTER 21064004 | {95C4B2EA-7339-48DF-9F61-FADDFD6FCDFA}
BELMONT 11104946 | {D5010A07-EC1F-422A-818C-56120CF28FE6}
APPLE HILL 11038412 | {07722CD6-14E4-4447-AD94-AC55195AC8E1}
LAKEWOOD 2109432198 | {0F07F3E8-FB27-41AD-9B59-87BC4E61A218}
MORAGA 1103E510R | {4C3B8436-25B4-4A62-8D40-AF9B1B8FB54A}
WYANDOTTE 110979932 | {67B8C4D8-FEA1-4243-99E7-B5C8BD7D2FA9}
NOVATO 1101405812 | {6FEEE710-65A0-4303-87FF-23996199A852}
BRIDGEVILLE 1102384530 | {9FA1CD0C-6EDB-4698-8640-F0D7CDEF944B}
STANISLAUS 17021850 | {B87C881C-26C5-430F-BDD9-C06CB7701154}
ANITA 11062496 | {CA64925E-CB77-4A47-8864-C246E9A1F937}
MONTE RIO 1113678 | {F763F6AF-FC97-4F89-AD25-F9455AF541C2}
BERRENDA A 1101CB | {FD8A5294-9952-41B0-9949-0D7EF73FF10D}
LAKEWOOD 2227W503R | {0052F236-02DD-4D59-831D-9E6CA4EBFC49}
STANISLAUS 170179826 | {2EBFCB83-8CD9-4937-9DF1-5F0721235A72}
HICKS 111512494 | {48560C68-AA30-4BF0-B246-3EDAD7DA0E36}
BRUNSWICK 11102664 | {52CBF115-6640-4F98-9743-613A61123F02}
PEORIA 170590374 | {8B476FB2-9EFB-4231-AA3D-ADAA150B87C8}
OAKLAND X 1106CR266 | {9B2F70E2-3822-4ABC-9A9F-F92985EE671F}
VASCO 1102208712 | {C757B1E5-E864-41C5-8F1F-450BE13C3852}
COALINGA NO 1 11089240 | {D0D57548-BFE1-4E51-8167-796FFB6E7A8E}
TASSAJARA 2103CB | {C740351C-623B-4A79-8F81-B59FA4E58E72}
HALF MOON BAY 11018940 | {2DBAB1CF-D3D1-4CC0-A406-0CDA12AB2548}
MARICOPA 1102453320 | {34FDF5FD-B2A0-4EFC-9338-7E46284554C8}
NAPA 11025039 | {CBD8A59E-6463-47E4-AF46-087923E514DE}
AUBERRY 1101R324 | {5D27142C-8E39-486F-97D4-ACA358D18034}
SUNOL 1101605520 | {80474683-8128-4BE5-9DA4-10CEDF2ABB74}
SAN RAFAEL 11071415 | {AC6B2CFB-8470-47A8-8CFF-360D120857F5}
MEADOW LANE 2106C558R | {9FDBE41D-F5FA-4A91-8801-9FABAD55128D}
MIRABEL 11022043 | {76DCCACD-E9DC-40E0-8CEA-2EC1A63EA736}
MORRO BAY 1101W20 | {F3373B43-A9DC-45C9-B2E8-745D10B70AD6}
ESQUON 11012054 | {25AD8CDA-2DAA-40D1-AF6C-EC42757AE02A}
BELMONT 11028918 | {8299BD19-90A4-4D64-8B9E-E4A475CD494E}
TEMBLOR 110437696 | {29FDF678-E116-4F18-93AB-072742A94198}
FULTON 110555802 | {957874C2-FA06-452C-924E-A5E4C30E68F3}
LOS GATOS 110160052 | {D47892F1-0CB0-45EA-A4B1-629482BAEB79}
EL CERRITO G 1110CB | {D5C37EEA-D463-430D-8618-04212D08A58F}
RED BLUFF 1105146070 | {2E98A968-0F7D-44C0-B9F5-8D4D032F12CD}
SPRING GAP 17029690 | {06F65D45-2D82-470F-9B27-5D880652F1A1}
COALINGA NO 1 11089860 | {D0D57548-BFE1-4E51-8167-796FFB6E7A8E}
WEST POINT 110277204 | {6211F369-8BB0-4A6F-AF12-1490B4F377A4}
DEL MAR 210975802 | {AAD63AEA-E006-40EA-8F1E-5C283AEC521A}
ARBUCKLE 110194064 | {B2E83566-334B-4D06-8145-C26AD63C12BB}
FULTON 110258990 | {D9F1E4D5-6C65-4B74-B28E-1D1E2528E5E8}
TEMPLETON 21085777 | {FFDFCD62-3D83-4DB1-8291-20A4384347C8}
OILFIELDS 110387034 | {FB7AE1AC-8576-424E-830B-24A6DA8C1F01}
SHINGLE SPRINGS 2108449638 | {2803490A-7633-47C3-B696-C54B5F6A03E3}
SONOMA 110478372 | {883C1192-DE93-49B0-9D61-992A9165A32C}
BRUNSWICK 11062416 | {EDF4431E-F5AF-4806-91E5-400DCB7DFCFA}
KIRKER 2104CB | {F61A533E-D44D-4AFC-AE85-9F4FD0A8F945}
RALSTON 11021601 | {EF774119-F7FE-47E7-8D97-134D999F3AC9}
HALF MOON BAY 1103157944 | {753853E4-C224-414D-99C3-DFD71085C7CD}
RACETRACK 170310850 | {56B3B60A-49BB-43A9-9EE8-443CF9005AA3}
SOLEDAD 21027008 | {7065F476-A653-46B8-B768-E4B58582997C}
MOLINO 110251788 | {E88FFA7F-5F70-49D0-8DB1-373E7BB1124C}
ANTELOPE 11011631 | {F610032A-F2E0-4366-8F75-D3F075E51CA8}
MIWUK 1702531976 | {29DBEF63-7B51-4C6A-A786-292EB9177451}
KONOCTI 1108430588 | {6FEDFF27-6826-4700-BE39-BD65EAE2E31A}
STILLWATER 11011320 | {7010B5A1-248E-4D8C-92BA-99C3D3CD7971}
OAKLAND K 1103CB | {9BD2CCED-08C0-4120-A490-E52866AF5C8D}
LOYOLA 1102LL66 | {9C5A5E3E-259E-4BA4-92AC-E564F3B34976}
LAS GALLINAS A 1107980 | {18214BA8-F1AB-49DB-836F-E6DF072AD66A}
CAMP EVERS 2105426822 | {B7A521A6-441C-41FF-9BF3-E1AC07BB086B}
DESCHUTES 1104116082 | {C3EF95F9-70F4-48A0-B2DD-F52E93DD3550}
UKIAH 1111789282 | {0679194D-94A5-4BEE-A3BC-BCA5B0434E05}
BIG BASIN 110195690 | {0F585841-A965-44FC-98CB-5C72CA920770}
MENLO 11038982 | {122C7DAC-AC52-4005-A738-CAEFD4E1581A}
NOVATO 1104CB | {1842CB75-05D4-4BC6-974F-EF96026B2FE8}
WEST POINT 110113444 | {1F21142A-72EE-4D4A-A8F0-E9702D60226C}
ARBUCKLE 1104656592 | {20D0259F-0F20-437E-ADAA-0E44C8DDA743}
OREGON TRAIL 1103CB | {57A4B509-FD84-475C-B34A-463055A0DAF6}
TEMPLETON 2113A70 | {7937BCC6-E91C-41D5-AE9E-FB212F98DDB6}
HOLLYWOOD 0401CB | {854414CD-0C09-471D-91AA-83170F69D473}
CAYUCOS 1101W14 | {978A144F-73B7-480C-94FC-939745BD7BEE}
LOGAN CREEK 210262032 | {BEFCE23A-309D-4D6F-8ABD-50878BF1EA08}
SANTA YNEZ 1104117616 | {C577CDCB-ED67-4302-B33F-D351377518F3}
CLAYTON 2212204416 | {D1603D4D-EDBC-4667-A394-6A5E09388F26}
ROSSMOOR 110136572 | {DFEFEF45-5177-43DB-BC8B-7506E80A5515}
ELECTRA 1102CB | {F6B2F362-298B-4DEB-8C9E-04B14858212A}
REEDLEY 11047892F | {1B9CB438-3D64-400D-8827-441645AF1444}
MOLINO 1102189602 | {13620D12-1AF7-40E5-A78C-3494982800C1}
LOS COCHES 1101625902 | {24A896E9-4BBF-4DA8-BD42-A7972EEB8C30}
ATASCADERO 1103A14 | {3081AC44-490C-41E8-9095-7905CD98E81E}
STONE CORRAL 11107778F | {D090E99D-0335-45D1-8BE3-75B46FB44EC9}
BRUNSWICK 1107CB | {22F4E53D-20D9-4A9C-BDCD-9693C219E892}
HIGHWAY 1101CB | {5C6F4134-089B-4151-9D4E-9160DBB180EF}
SAN MATEO 0408CB | {72F4A567-A9CD-48CF-9E88-AA2F9E6053A6}
GRASS VALLEY 1101CB | {B0F41A34-F762-41B4-ACDB-9C11F27E225A}
RIDGE 0402CB | {DCA9ACB4-28D7-4107-A085-304473A5BF3B}
FELLOWS 21041098 | {99CA2E77-9D49-4EAD-A742-E8CB938D605F}
OAK 0401CB | {E8FD31A9-7950-4D14-9414-D1A0A0556AE8}
ECHO SUMMIT 11012500 | {52018984-7699-4174-8C0E-5E599E3F4F55}
BELL 110750172 | {6BF0E854-A546-4347-BF88-873ABBCE7D58}
EL CERRITO G 1112649732 | {7A0FE4A4-8FE2-4A7A-9013-EEA423D246F9}
BONNIE NOOK 1101CB | {9FFB5CDC-505F-4B8E-9B6D-E79E68D9EC60}
MORGAN HILL 21094145 | {DECA5724-8C2D-4F8F-80A8-75B013DC4D0B}
PLACERVILLE 111219742 | {CDEEAA53-79F0-44F1-8538-90E3C7AEC3A1}
CLARKSVILLE 210419652 | {24BA7214-EA0E-4940-8D9A-B12BFFD010BB}
ELK 1101311906 | {818DDDEB-2E77-45C3-96C4-F6724182B49A}
CALPELLA 1101619542 | {979C5268-1F54-4BBC-B316-05EF7B718423}
COARSEGOLD 210410110 | {B491FAF3-D57C-4407-A408-814947D65184}
ANDERSON 1101583708 | {C1AE4ED5-9E2B-4787-958E-F3CEA46DF77D}
CAMP EVERS 2105601610 | {D1A3ADE9-9226-4429-A4DD-15AB5B88142C}
FAIRVIEW 22078275 | {659FD2EB-053C-425F-AF25-D9C58353B44F}
JARVIS 1108MR367 | {4D5666F5-BD84-4CAA-B8A5-49AFE5BCCE43}
SHINGLE SPRINGS 211051790 | {189FDEE6-C0C8-4312-8E54-D1B717348AC0}
OLETA 1101239062 | {266221BA-D2B4-4469-81F2-F0DF035CF024}
VOLTA 110149742 | {2B3F7DCA-485E-4940-AF70-C148286D4D0A}
IONE 1101L3141 | {9D5BFE02-DE54-49D0-8A6C-80BCABF7CBD7}
MIRABEL 1102206 | {3FDFEE62-2564-4B56-8AC9-FC80D427FADF}
COVELO 110137328 | {D4E144DE-8AEF-45D3-9080-EB1CCEA62B46}
EL CERRITO G 1112BR196 | {00AF1949-B9F3-40C7-B655-E7207FF7DB49}
POTTER VALLEY P H 1104546986 | {0F563298-4ED3-47AC-A822-118BBD6BD4FC}
VACAVILLE 1111CB | {1F08C74E-1D18-453D-9F09-2E91ADE9AFB1}
SANTA ROSA A 1111114 | {7B87BD32-83E4-4831-8C0E-079887A90817}
BIG BEND 1101641808 | {A3F84BA5-8D5A-4B0D-AFE9-3E2A03521912}
VACAVILLE 11088762 | {ADB960B7-1B6C-413D-B1F8-E0FB7A88FA0F}
HOLLISTER 210542224 | {102DDCC7-B669-4F67-96A4-A65E2BB45451}
MORGAN HILL 2111XR354 | {8D6AF672-1092-41FD-91A5-035B7D768884}
SOLEDAD 21057056 | {36177CF1-DF55-4FEE-893C-1AD0F53C4183}
SAN BERNARD 1101641042 | {46FF504D-69DB-445C-A616-F2DCD009D8E4}
WHEATLAND 11042700 | {4B414DEC-F869-45CA-863F-BA162E505527}
GUSTINE 11029628 | {FC926262-8B0E-4F06-BF55-D74DA7FE90D8}
RINCON 1103198 | {7F16B5BC-4060-4BCC-9EE1-D9EAFE5FD541}
BURNEY 11011340 | {9FEEDD46-3D3C-44E2-AC09-40EF72D10F0B}
PAUL SWEET 21075134 | {A3EE8121-F4DD-4843-8E3D-4FC7281FCDB4}
SANTA ROSA A 1104991788 | {A7207572-E958-47AE-A2AE-E5F117C7F1E9}
CASTRO VALLEY 11088971 | {D8E4C9CA-7EEB-49BA-880B-C873380BC8EB}
SHINGLE SPRINGS 2110386572 | {FC00237C-3D62-4C01-88CF-5974E60BEBEE}
CLARK ROAD 110290548 | {1DE99E4E-7765-44B0-9832-275F1EB7F7A4}
CALISTOGA 1102634 | {1FCE58DF-672D-489A-B6FD-E3E4E442C0A2}
WESTLEY 1103237522 | {248AE4B1-0618-414C-9295-0197646733FC}
SWIFT 2110853720 | {8EF7F2A5-231D-429F-AB3F-65E0BD44BC33}
CLARKSVILLE 210419662 | {A9104265-B4F6-48EE-93C6-57B36F6C317A}
VASONA 1102944560 | {D5583FAD-E457-4793-A47C-008117308B38}
OROSI 1103CB | {029EB0AA-88F8-4BF4-93B1-3A5396293CB7}
PIT NO 5 11011660 | {06EBCEE6-C636-4CF7-B3B5-D5C157499FDB}
PEORIA 170413494 | {1EA8CF8C-ECB4-4CEA-BCE6-3A74137F1411}
PEORIA 170411232 | {320BFDAF-F5A8-4096-BB62-ECF18634253B}
FROGTOWN 1702224708 | {35EE754C-7E3A-4C6F-81A6-D14B057757B0}
HILLSDALE 0401289582 | {3BC63369-8BB7-498F-AC59-3790414C1555}
ANTLER 1101CB | {5E7DC64A-0B4A-4299-87CB-EE1D39916B3F}
WYANDOTTE 11071510 | {9879E6FE-604B-48B5-AF02-92364DF9D405}
HARRIS 1108CB | {9A3D8818-9236-4C74-9C67-0369FA031A48}
WILDWOOD 1101384582 | {DE2BE838-418E-479A-846C-D45336A92EC1}
MORAGA 1105553110 | {40049C8F-DAE2-4759-A9B6-0D8AA42C6AC2}
CASTRO VALLEY 1110264914 | {FFE0EC6C-F31E-4ACF-B207-C8795D8C3898}
PEORIA 170570198 | {21D2A9B2-3258-44D7-A4FD-EDFB8BC88DE8}
CALPELLA 1102CB | {2993BF9E-90A5-4634-AB04-8D39B8C96792}
CLARK ROAD 11022068 | {31C399B4-B5E1-4797-80CF-566E803A98B5}
SAN MIGUEL 1104895760 | {5D373241-D81F-4822-B649-3A4A39407074}
FOOTHILL 110299432 | {7C9F6E98-6AD1-45C0-AA12-C5A39FC092A4}
MORAGA 1102CB | {882C20B1-4F53-4E74-914C-118DECC8B0F8}
LOS GATOS 110160136 | {A1B517D1-7F5E-496E-A188-34F488988F32}
PIKE CITY 1102CB | {C855B1F9-E043-4F7B-B17F-9A4E0F007042}
CLAYTON 2214CB | {10733B2C-A5C3-4A9E-8D35-517FAE09EA04}
BANGOR 110131502 | {6925CBA3-93E0-44A7-B2DC-50805D93ECF4}
GIRVAN 1102296428 | {F8758432-B450-4943-97B4-52B80EF2F512}
BRUNSWICK 11062104 | {BDBA1A41-9235-4F2C-87B2-104E0BB64232}
NORTH BRANCH 1101CB | {BE4CA008-D653-4EED-9B85-D4D7237516F5}
UKIAH 1114CB | {D98BCE06-B639-4635-9566-7FA7CFE5BC8F}
VALLEY VIEW 1103P158 | {6F4A4EA4-DB8C-41B8-B673-0FAE8635F67C}
AUBERRY 110137536 | {AF3C9CC3-4B67-4003-BBC4-2AADCCAC2E66}
MONTICELLO 1101666 | {5E2D609D-433E-4CA6-9935-5DD068ECF7FE}
SAN LUIS OBISPO 1104V46 | {73F7E742-5FE2-48F8-9BFF-7AB912085CD1}
RADUM 1105420576 | {87051ACA-C17E-4D55-A6B8-1444F89F63EA}
CAMP EVERS 210574170 | {BA541186-8D15-43B9-BDFB-BAD6936C2F64}
APPLE HILL 110413512 | {C961DA87-D3C6-40FA-87BC-1A5AB7DF3FCD}
PEORIA 170449256 | {F440C80E-DEF5-43B1-88DC-EE268B4D5DB0}
HIGGINS 110950078 | {13205944-27DE-4E69-8D25-637FC945A119}
PASO ROBLES 1107826368 | {3681E2B2-3C69-41BC-898C-6BA327012404}
BIG RIVER 1101262924 | {BCC029FE-B790-4D1A-9B12-5D2C7AA3930D}
LLAGAS 2107870396 | {4DC0A76E-797A-4818-B053-21B7BC501B6E}
PEORIA 17051834 | {843F968C-C902-4C08-BE12-AD0D025C5DF3}
PUEBLO 2102CB | {EB7314AB-7754-4D90-B11B-A641443B251F}
MC KEE 1107XR010 | {450C95A5-CC86-42A5-8643-E83181385ECD}
WOODACRE 1102851 | {61FE98E8-80EF-4BDB-989C-5A04CDB81F15}
HOLLISTER 2102855412 | {1326B156-0483-47A9-A035-C6F98F761263}
PEABODY 211357908 | {463CEDCD-A864-4BE7-A495-4562C479EEC4}
CHESTER 11022612 | {C8BA9CFD-3C7E-444F-AD17-DFDE1ACC00EB}
WILLOW PASS 210879972 | {1FEB7E65-DDE1-46AE-83AD-B5F30417F926}
PINE GROVE 110113408 | {207F56DE-FF3F-4FB6-9F25-8FC555D28285}
LAS GALLINAS A 11051218 | {D824A6B2-681A-48EF-8928-B97846B95D59}
DESCHUTES 11019722 | {02E1E6D5-2F65-4901-878D-9181104BB0F8}
BEAR VALLEY 210110000 | {0D159A34-F101-472F-9F8B-631446B0CF4C}
DIAMOND SPRINGS 110777086 | {01A8C6BD-323D-44E5-A686-1246351A46F2}
PUEBLO 1104968601 | {17489714-54AD-404A-B125-398990CB9745}
ROB ROY 210410960 | {2E6975B3-903D-45C9-9C7D-960FEDF8E472}
ROSSMOOR 1104L530R | {2B644C8A-1232-4056-B6E3-B09CD0D7D415}
TIVY VALLEY 1107584840 | {69DA4F1C-E07E-4189-8040-902C89E5A469}
CAYUCOS 1102613456 | {6A688077-C692-4875-BCC4-AA060549E3B3}
DUNLAP 11027360 | {81D716EF-AF38-46F5-8FD2-48383247DE01}
LAS POSITAS 2110MR195 | {8911B60E-25FD-4A9D-AB0E-C717D3E4437C}
MORRO BAY 1102868170 | {0C127574-7596-4A86-A384-D65556DA9180}
HIGHLANDS 11021304 | {DF76C57E-BBD1-4728-AA99-EBD33D60311E}
PASO ROBLES 110355374 | {7E3660A3-92BC-4694-A2D5-248E2793B9A8}
CLOVERDALE 1101409224 | {B0E9356B-01BC-40EC-86CF-A93C8EF70CFD}
GREEN VALLEY 2101509068 | {CDC61CD0-0FE2-4F7D-9501-2D67363E1B49}
EDENVALE 2105739448 | {0DDD3612-D5D8-453A-817C-994BF75B062F}
CABRILLO 1103Y10 | {133D318F-822E-44D3-9638-08188E1B8D58}
WILLOW PASS 2107537100 | {24C8C7E8-733A-453C-8A4F-FE8CF59DAF59}
STELLING 1110568350 | {D66F2372-56F2-4D8A-9310-F85A981AACD1}
ROSSMOOR 1107CB | {DC54959B-747A-4CC9-B9A5-4B8CDE5FA47E}
MARIPOSA 210190180 | {DD0025EB-B991-46AA-8D21-AE164B513DA5}
BRUNSWICK 1104285704 | {252458C9-C847-447C-8725-6EE8EF8017F8}
CHOLAME 1101X14 | {47231439-CE13-4A31-BF86-1A2379821F62}
WYANDOTTE 1103640652 | {59B1EFCE-EA13-4733-ADA9-7461CE4DCF90}
VOLTA 110293418 | {06F73A44-E6BF-4E7C-AE40-21A987895C90}
SAN BENITO 2101506268 | {D701BA36-CC53-4635-AF00-A21AD8BDB3B2}
LOS MOLINOS 11023302 | {3C29BFDD-B708-4EA4-82F6-BE02F2280B00}
TRINIDAD 1102314118 | {4BDA4000-EE02-4CE4-AF17-6468A5212F43}
PACIFICA 1104230272 | {233FC7C5-A8F9-452B-B547-9495E8EC73B6}
HICKS 2103XR262 | {F9C1F2D6-7B0F-4CCE-9FBD-177508C9BBDA}
MOLINO 1102381468 | {60856F33-F69F-483D-A29E-5E684F09BD0B}
MORGAN HILL 2111997000 | {60A77C46-059F-42FD-9344-179C8ED541A4}
GARBERVILLE 1101323694 | {624B3FD3-11BE-4D35-879D-7A58EF854DA3}
HONCUT 1102478754 | {B9E11B31-9989-4FA2-87A7-5FB52DF0CB03}
BEAR VALLEY 210521160 | {BAB6581B-1DEF-4E8B-AEF9-096FA24A0638}
OAKLAND X 1104391688 | {CE464302-D75F-4110-A0B1-1E7596A4CF84}
PEABODY 210813412 | {BC2B156B-5F07-4313-BE60-34EF88AFE911}
RALSTON 11029126 | {EF774119-F7FE-47E7-8D97-134D999F3AC9}
PACIFICA 1103915474 | {572B383E-2937-4EFC-BA24-50423EE8A457}
PINE GROVE 1101CB | {5E0ECFE9-34C5-4F2B-8405-6E29B71598DF}
BEN LOMOND 1101BL 1101 | {97243609-0190-4CA4-910D-8656166A7529}
RED BLUFF 11051564 | {9D2C06EE-ACC3-496B-9742-675775229618}
TRES PINOS 11114032 | {BD94B291-9C0B-4C28-8C7B-50F4F86D7051}
WILLITS 1102350324 | {E32B6BE0-3764-43AD-A424-17E7100BD267}
MADISON 210163762 | {FAFBD2A1-FFC3-48C9-9B09-E9ECE3AD7FAB}
GANSNER 110137550 | {2D495744-1EEC-4B5A-AB6C-8BE5D83F4E62}
SAN MIGUEL 1106N38 | {7351BABC-DA39-4A67-B463-17C1BA8F0959}
SALT SPRINGS 210297924 | {77733CA8-C469-4656-B2CC-06892BE8F14F}
CUYAMA 2101952122 | {A7BC3A91-18C0-47E6-A9C8-4D7D73EA0E4E}
JOLON 11027070 | {3C29C0B2-611E-468C-9FBC-81B8ED82FB52}
GREEN VALLEY 21039959 | {71F18CE4-D284-4752-9621-5F4A7D3D2F8E}
PUEBLO 1105637242 | {76F5AEE6-B528-46EE-B628-BA0E8A65C596}
MOLINO 1102104 | {7D5BEB0A-06FF-4975-900C-BDCD4AFAA92D}
POINT ARENA 110147952 | {6151271A-BC5B-476A-8700-C63C19F32AF9}
HORSESHOE 1101603250 | {6501F20E-BB6C-44CD-B10D-FA9DBEF23636}
LUCERNE 1106664 | {7BCF996F-5D44-49DD-8430-629850EC151D}
KING CITY 11047092 | {8B5FDE5B-06CB-46AA-8A11-AB1CDB733591}
COARSEGOLD 2104CB | {9126AC99-906D-4CEE-8034-3EECC4C90F16}
MT EDEN 1112MR365 | {A5398856-385B-4671-B566-17D8F81D2C22}
CORRAL 110275622 | {C5570B1A-B071-4827-88D1-68633BB92AFE}
DOBBINS 11011808 | {E4399593-CC75-4E6C-A098-AD618A358CCA}
STELLING 1111LM40 | {E9E9A7BE-6BF1-4820-BD71-A61CE1AF4848}
HIGHWAY 1101200662 | {27D0C7EA-6E05-4947-A47E-355769B9A693}
HOPLAND 11014626 | {03A33F3F-5506-459A-89E7-ACD76DFFDD38}
ROSSMOOR 1101L501R | {192A3563-130E-4748-AE0C-092D67B95727}
PAUL SWEET 2106607772 | {5CFD19E5-804C-4EC5-B475-DE099B6B0FA7}
KANAKA 1101859138 | {779CCD7D-EBF1-49D9-866C-F06EC359F475}
SILVERADO 210581662 | {6A947491-FB60-4043-BF5D-F50FFBCF57D9}
ORO LOMA 11173740 | {C820BB58-E1B1-4D66-A2E0-22C9B53183CD}
ALTO 11231222 | {52729A7B-7BFA-4980-A850-5BD8CF10E4D2}
PAUL SWEET 2108CB | {62614D7C-C46B-4061-8F81-503DEACC476D}
SAND CREEK 1103799118 | {7DAACA3F-4C0E-44A3-94C1-301E31E8EF8D}
CLAY 11037124 | {90124199-1243-4A62-BE12-797EFE6331CC}
LOS MOLINOS 110154804 | {09A4B9E8-989B-4DA3-9154-EF01A44BB71B}
WILLITS 1102CB | {9734DBF0-6F90-4CE9-BF04-F2CD4B5AEADC}
OREGON TRAIL 11031500 | {31065709-9564-4E9B-B7A7-65368041A59F}
OLETA 11011208 | {5372D86A-A2C3-481F-93D2-142C67A2BDD1}
SAN RAFAEL 110668694 | {71ACD594-F55A-4D07-9FE3-9B0665AF5F6F}
COTTONWOOD 11031344 | {B1A37D66-F35D-4EB7-8214-339B94F2CF9F}
OILFIELDS 1103CB | {BEB06E83-3CCD-4D08-B66B-707C171E4243}
GANSNER 1101372132 | {2D495744-1EEC-4B5A-AB6C-8BE5D83F4E62}
FORT ORD 210779670 | {018C3E1E-E9D7-4770-B296-F1B4D7801EF4}
IGNACIO 1105784032 | {087FC024-1431-4D83-A955-1FB7C9160A67}
DUNLAP 11037080 | {3474C71F-C417-4DFD-9033-1EBD72D1A9BF}
GARBERVILLE 110139524 | {E1AC8377-8E8C-4414-AED8-68291E68F4CE}
BRUNSWICK 1110528196 | {AC82A3F6-A35E-40B3-B30F-C23643AC0649}
LINCOLN 1104275986 | {9DA634BB-F98A-454F-AA17-CE93C4AB5C34}
CANTUA 11039900 | {ADBA8581-1EDE-4FED-96B1-1470CDDF965C}
BELL 1108339792 | {C5B6945A-DE5A-4681-9AEF-7B6CF23C0D53}
APPLE HILL 21029722 | {CD700C3D-374F-40E3-8624-DAD7800FADA7}
MENDOCINO 110131322 | {DE700694-1BC1-42F0-BD3F-498F1D5E0950}
JAMESON 11059472 | {4372CAAD-3581-4B8A-AB27-A49D177EEFCE}
DIAMOND SPRINGS 1105CB | {76BB324A-98B3-4C58-A6D4-32DC864FAEB9}
JESSUP 110269928 | {7CA3CBB2-5BD4-44E1-9364-BA8EE2FC0FBD}
FORT ORD 21069634 | {0139AD78-6D54-4C40-B88F-B8F196A0FC71}
MARIPOSA 2102440236 | {D55632F8-2CFE-45BD-8046-185433E1F9AE}
PHILO 11021308 | {EADE9BC7-FA33-4E78-987B-E6772CEF7A88}
ORO FINO 110265932 | {EE93E5CE-FD33-44EC-A329-FBA8C511073C}
VALLEY HOME 17031532 | {F0B34ED0-42FC-4061-AC8E-1112027FAE68}
ALTO 1122CB | {F8F75874-EBBE-4BAE-AEB7-B4201B2B809B}
BIG MEADOWS 21012260 | {18489341-7942-4EE1-95D9-22D6837A669D}
CANTUA 11019890 | {B55C2E19-B2B9-47FB-B0FA-5E9F76A070B4}
CARLOTTA 11214914 | {A5C24938-2037-405D-99A3-0ABBFC2B130E}
PEORIA 170190090 | {CA1036D4-6988-4718-9A58-7F114C1260AF}
JESSUP 11021314 | {05CEA4F2-3636-4573-A883-9C548FA0A079}
PLACERVILLE 1111CB | {15D1F2F0-3D88-4B18-AFEC-B03FE833977B}
WYANDOTTE 110931758 | {4018E6B5-9FD7-42B6-984E-3899183793C0}
STAFFORD 11021258 | {67620093-3D29-47F3-861E-D41DF7A61FA6}
EL DORADO PH 2101729064 | {1AECFC8B-BC7B-4454-BB87-FD8F012E171A}
OLEMA 1101602 | {B7FC1F3D-8C95-48C1-8180-E56EBBA37A96}
SAUSALITO 110284278 | {EEE9A4DD-4FFF-4813-917D-2CD2DA44AB21}
IGNACIO 11031068 | {F489C694-D583-42AD-BB91-0D15DCF9AC70}
SPRING GAP 1702693441 | {F823B297-BE7E-454D-B946-D904DF33E9F1}
LOS GATOS 1108LB86 | {179FE519-944E-4835-9C33-84ABCACF7D82}
BRUNSWICK 1103851116 | {B83D09DE-3D47-4840-BFDB-F992D85178B8}
GABILAN 11013722 | {6D5B17B5-960C-48B4-806D-BF9DA1A8A3B0}
PENRYN 1105196418 | {C6ED3044-D174-430F-8880-19A3EDFC2300}
SILVERADO 21051308 | {E61E149E-984B-41E5-BBE8-57BFA4C46C56}
EL DORADO PH 2101668674 | {9026688D-0DDE-43F9-BDC1-1D8B37EA23F4}
CLAYTON 2217CB | {2E89F027-67FF-4082-9169-E158A83D0166}
ALHAMBRA 110582622 | {43B3FCFC-E570-42A3-9958-1934EF46169A}
MIWUK 1701992162 | {8E98014F-A627-491D-9EDE-59105F8979E1}
SAUSALITO 1102678 | {F71841C2-A9F6-40EF-B1D5-2F1AAA2168CF}
OILFIELDS 1103441010 | {28C87B96-17F1-4B77-AC44-88E083C74B6C}
CLARKSVILLE 210351564 | {1D188BFE-6402-4FA3-8FCB-922AC5F45D03}
BUELLTON 1101CB | {3DA79F67-E6AE-44CC-8D0A-A38C65F29240}
EL DORADO PH 2102994396 | {876266AC-37EA-414C-92FC-94A2ACD4EB2D}
OTTER 11012052 | {64CB4C99-55F9-4CDD-8DE2-173258603853}
SYCAMORE CREEK 11112544 | {D9A2A699-962C-4607-98AB-EA01299FAAB8}
SNEATH LANE 1107CB | {88158706-37CE-4050-9559-5A1E15835B03}
GONZALES 11013094 | {B8E5DB63-2FB3-475E-A16D-C9AC460D90A7}
RED BLUFF 110529222 | {F0D0C191-AC63-4C53-85CC-9DDB5D220867}
MARICOPA 11023558 | {341A5947-0E50-4A7D-9C85-BBC1E06228CA}
SHADY GLEN 110132726 | {486AA3F8-488C-4B89-9A1D-60C9962E4FCD}
NEWBURG 113190644 | {51231194-526E-42DD-B60A-6D3E3BD144D9}
BIG BASIN 110169550 | {6AB8FDF6-DF60-4669-94F5-76C04F7F5767}
WILLITS 1103826 | {72556B33-F33B-4E33-8959-39723007B093}
LAKEWOOD 2110W577R | {84A8C5F2-D0FD-4CA4-8FD3-BE277808997E}
FELLOWS 2103CB | {A2B8C63A-2E3C-415F-A84C-6AAC2DF68E0B}
WYANDOTTE 1109CB | {A372AD67-1459-47B8-8964-55AFC8B0D599}
SUMMIT 1101CB | {CD142DCA-BFBC-491B-9C29-D02961854E56}
HICKS 1116583284 | {EC9FDCBC-C8AE-4588-B594-E3F1FCB0DA2A}
OLEMA 110150396 | {F7C05161-6A07-4797-A2B5-C7A055E43654}
TULUCAY 11019999 | {D5040DDA-C582-40B5-8A53-2E3901DC0B08}
ELECTRA 110213414 | {BE69B59B-6EEF-4362-A602-62B1E76AF725}
CAMP EVERS 2104189010 | {CE6EDBCF-B1D7-4C02-8D27-0FDA223000E1}
TEMPLETON 2110R06 | {29732AB3-8644-4D02-B399-63E828AF790C}
MONTE RIO 1113532 | {3A330D41-F506-49D1-A8AC-21EA6FC6FDFA}
PACIFICA 11015001 | {4118C23A-F427-46E8-85D2-FD56A1055C29}
SEACLIFF 0402558727 | {46C46D9E-FFCC-4964-94A9-7BEF756B6617}
CORRAL 110313474 | {6748E8F4-5236-4133-9E21-482CCE2EC069}
DEL MAR 11032716 | {EF81CA1C-18C9-4299-AF2A-DDBDF91E767C}
CLOVERDALE 1102156 | {0AFDFC2C-BE93-4295-B473-DFD529280FFF}
EL CERRITO G 1105BR316 | {3F882A80-2491-48FC-AFA8-BDC3FFEA4D12}
BRUNSWICK 11032200 | {8832E15C-A8F3-49CE-9AF2-19EADE479033}
CAMP EVERS 210660120 | {CCDF3A25-AE56-4EB7-B245-ECC2A1643713}
TIDEWATER 2104CB | {F47CA250-FEC5-4A9D-A7B7-CD6372963F55}
COTATI 11058459 | {1E254E89-80C2-40C5-86C1-3418E85098A5}
PERRY 1101618168 | {03363AA4-45D4-475B-A70A-74AAA6293936}
OAKLAND X 1105184672 | {274ECA5A-0B48-43A3-88F5-9E1AB810108B}
VIEJO 22032636 | {2745EA16-9172-4362-B554-6BC9B1A69619}
POINT ARENA 11014923 | {827A54D0-0188-46E1-B6F0-E7D696DF4D89}
COTTONWOOD 110331548 | {5C7585A0-7AA3-4054-BF6B-A9176A3B037F}
HIGGINS 1109594 | {824F13D7-3113-4AA8-8BC2-89229A42D634}
DEL MAR 21051270 | {DD87F226-71D9-4417-928F-44802F1E6068}
VOLTA 11011516 | {3F11AD42-8CBD-4A85-ACAE-76F96892C309}
PENRYN 1105CB | {52904CB5-03B8-4344-8C19-2DFFF3E5223D}
WYANDOTTE 110213916 | {6520C128-A5D2-408B-801E-4626440008FB}
LINCOLN 210993464 | {4E6AFF3A-F560-4015-9A7B-59C83CDB47B7}
FULTON 1107914380 | {6CE1CBF7-A8F6-461B-83E4-323985F1F354}
CAROLANDS 04018888 | {8A7276CB-0C27-49CE-BD2E-58CE1319B4D3}
LAKEWOOD 2110CB | {8D56729D-62B8-4F70-8336-DC0D3C2D910B}
UPPER LAKE 110142378 | {B4FEFEF6-4949-40A0-B2AB-64F4BB223B69}
PLACERVILLE 21062224 | {BA672D72-863E-4FB8-9458-911126FD31A4}
RESERVATION ROAD 110222136 | {C1E68105-3858-4273-9D69-DD27BF248870}
OAKLAND K 1103CR188 | {C758376E-2F53-4EBD-9E43-CD37C030EEDD}
SAN RAFAEL 1104802 | {E7743FFE-2947-47FD-B4E6-A754209900CE}
BIG BEND 1102CB | {05EF3BA2-F04A-49CF-AF87-10424EDE6926}
OILFIELDS 110293788 | {207F72FF-9E9B-497E-A35C-453C13449996}
SAN RAFAEL 110863598 | {62B0F5C5-018B-42C2-9DA1-D8CCE6714B61}
EMERALD LAKE 04028858 | {6E19C0A5-86DD-49E4-909F-112A4E9E5B6E}
MENLO 1102154024 | {C583B40D-86CD-4D00-B0BD-8B42D03F7715}
SARATOGA 110413314 | {DAB08854-D3B6-4F8F-8E8C-51427B3E01B1}
SAN LEANDRO U 1109CR002 | {0A0CA719-3BA2-4B10-8DAF-28B4D94E2A5D}
PLACERVILLE 1112774186 | {69C7055C-8321-466E-890B-DA1A435F5398}
ROSSMOOR 1103W514R | {D9FD5122-71C5-470A-9067-11BD4B38DBDB}
ELK CREEK 11012004 | {DECCC899-88C1-4943-B78C-B486089CB76D}
HOLLISTER 2105CB | {ED3912F5-3969-4789-A9D3-65A01A62E3A0}
ARCATA 11220664 | {82E30D47-3E2A-4E87-8D66-B620821B7943}
PIT NO 1 110170952 | {8AC91F5C-D86E-4B8D-B342-7C652EFA0FA1}
PUEBLO 2102895310 | {C669F706-9156-43FF-93FE-C8CD4A8C9FE9}
GEYSERVILLE 110249056 | {450BD680-08E6-46D0-AD80-CB37688E8C0C}
CAMP EVERS 210510728 | {61BEE218-5ECD-4073-AA08-F1DB60558A8D}
CAL WATER 11023428 | {66B5382A-A6B4-4150-9067-49730EEFBF01}
LAURELES 111110141 | {03861487-35BB-45AB-853E-5E8CD2B590E5}
CORRAL 1101CUS9215 | {488178E5-61FC-444B-88C1-9B8C60F860FF}
HOPLAND 110194006 | {8550FAE9-8660-4D0D-A46A-9FC5A8080BAF}
SNEATH LANE 110715341 | {935F9503-A6EA-4581-B689-528244098488}
LOS GATOS 1101502026 | {E1FA2A15-AD3C-4DAF-93F8-E10F60AD1FB4}
CORTINA 1101CB | {E3B77E93-BB57-4588-891B-4456F675EF56}
OLETA 11011217 | {266221BA-D2B4-4469-81F2-F0DF035CF024}
CLARK ROAD 110292622 | {381D7853-5A02-4486-A50E-C31E33DE4E4C}
SANTA ROSA A 1110CB | {422CE5F4-0FBE-4EEC-A8C2-C4BEFA9D6650}
APPLE HILL 1104275024 | {60D1E266-474C-4944-877D-C3B4C2A1D233}
HARRIS 11095982 | {0E899392-4139-4EF4-8C02-780C18A47141}
CASTRO VALLEY 1102837904 | {D1EA05C6-0F55-455A-AD0C-597319479076}
ELECTRA 11026014 | {0CAC2312-4B19-49F7-9A0A-4917B3A62B39}
WYANDOTTE 110697550 | {29C2B584-F455-4FA3-B4A4-3F4E989317C3}
ANDERSON 1101514412 | {4FF91FEF-C966-4E36-B08B-C812EFC4BE16}
TEMPLETON 2109P60 | {B41EAAD7-8D6D-4395-8298-54FCF68764D6}
MORRO BAY 1102517286 | {0C127574-7596-4A86-A384-D65556DA9180}
CUYAMA 21013039 | {AE254590-1F13-4FEF-92B1-1F8EB5A8892D}
POTTER VALLEY P H 1105640888 | {DDBE967D-510E-4AA9-8699-FA1CD4531A33}
SAN LUIS OBISPO 110342344 | {EB029C6B-1104-4127-A12F-6B1C6DB20B5A}
PUEBLO 2102773926 | {F9DE541A-2DEB-4CE3-95CE-87C59E155BAE}
STANISLAUS 1702L3151 | {B87C881C-26C5-430F-BDD9-C06CB7701154}
CASTRO VALLEY 1102960346 | {2E3992ED-F001-40B5-B77A-1BD22BF80B0A}
OCEANO 1105V20 | {70C30D54-868D-4F87-BAB6-E123ACDD12E7}
EL DORADO PH 210163464 | {9722F7CD-905A-4FAD-885D-DF51D2B7EB29}
STANISLAUS 170237278 | {DBBC669E-53C3-46F8-B180-51E0DC203C00}
UPPER LAKE 1101452 | {B4FEFEF6-4949-40A0-B2AB-64F4BB223B69}
FAIRVIEW 2207P142 | {0B7F62BF-A04D-4B9C-AA26-AFE69516CA65}
VIEJO 2201CB | {11A2851C-72B1-4A62-98D6-D6E2FFA710C1}
MORAGA 110381146 | {14C57C49-3FAA-493A-A967-CDA87ADFA83B}
DEL MAR 21061686 | {1E127AF9-846D-4194-872F-DBA8A5888781}
STAFFORD 11026121 | {890FBE04-45F2-477D-ABCA-3FF18127DAFA}
TEMPLETON 2111R38 | {E068C598-6807-40BC-B63F-804DC57F436F}
MC ARTHUR 1102CB | {29D96E6F-9A6D-4E41-9CE1-0E9E869E48D9}
SAN RAFAEL 1104CB | {33CCC2F4-F827-4C07-9171-27096EF33E3C}
PRUNEDALE 110722448 | {9055CD6F-1385-4DAA-B189-3CEA20BFACDF}
CURTIS 17058170 | {944E3EC7-4285-4D17-99A0-D6960B77E4D2}
TULUCAY 1101613014 | {D5040DDA-C582-40B5-8A53-2E3901DC0B08}
KESWICK 1101CB | {9C6E3EC5-697A-453D-8DEA-C3F8B751E8D1}
WOODSIDE 1102472928 | {DEE5BC84-14D0-4B16-967C-4B20A0B07E86}
MILPITAS 1108342498 | {AD2D545D-446E-4C20-A74F-6B44E5722705}
SMARTVILLE 1101CB | {90A2FAB3-9517-4F41-ABE9-643E537A58ED}
WELLFIELD 11022842 | {94668338-D057-4AD5-892F-BB0D86C28946}
MILPITAS 1109XR044 | {AAFA242E-CE7C-45BF-A927-201DEB4735C4}
SAN RAFAEL 1104717160 | {33CCC2F4-F827-4C07-9171-27096EF33E3C}
TEMPLETON 2108A64 | {FFDFCD62-3D83-4DB1-8291-20A4384347C8}
CHOLAME 2102127926 | {042A33DE-71B1-40FB-B0CF-6D56CCA576B0}
ROSSMOOR 1106L552R | {52DEF6FB-138D-4E67-B717-53642F74F0D5}
DUNBAR 1101440 | {5AA0A9EA-0FB6-4230-B4CC-9462B9350D46}
FORT ORD 2107CB | {5AF19FAC-D5B1-4A0E-9483-EA04C351FFDD}
PIT NO 3 2101CB | {5C4A4B21-8DC0-4DD4-BD69-EB88E21328E5}
VALLEY VIEW 1105P190 | {75634943-F60A-4935-9A1D-02ADD9591487}
VACAVILLE 111112342 | {3A0CCFE3-C12C-4384-B593-6A5D6B4AD5AF}
RINCON 1101146053 | {3AEF342C-12B8-4583-92B0-7B9C6AC3A567}
LUCERNE 11034624 | {4100FBA2-C458-44C1-B317-2EE92F5C04AB}
SANTA ROSA A 1111526 | {77B8D94F-2EC6-49F7-A5A0-3C2CCD32D5EE}
WINDSOR 11035060 | {5C89CE05-2636-4AC9-BAFC-5707AC921B94}
OREGON TRAIL 11041634 | {6281842D-96D3-4641-90CC-4C58A4D89E7E}
RINCON 1103474 | {6A5817A5-7FC3-45B7-8DC9-2BBA0FD82034}
SAN ARDO 110193072 | {D178EAD0-51DA-46C3-AC83-7A5FC311BC88}
OAKLAND X 1104CR101 | {0E163071-14D9-42E7-B9B8-B27ACF143A75}
PAUL SWEET 210437482 | {9E32E9CD-A939-47B7-8D32-52540B68C5C6}
GEYSERVILLE 1102220154 | {450BD680-08E6-46D0-AD80-CB37688E8C0C}
REDBUD 1102523244 | {6D1DA35B-F9DF-481E-9974-60E83F30F3F5}
CAL WATER 1102920714 | {75FA50A9-2878-4633-B714-48E51CCA6E1E}
DUNBAR 1101872066 | {7BA4959A-2F94-4080-BC9D-0C53D9644F4F}
PUEBLO 1105CB | {88C9735D-F7D9-42F3-A471-0E595E4AABD3}
GLENN 110137496 | {8F5BCB3D-C3E9-4C76-9B76-7B4ACEC2657C}
CLAYTON 22159765 | {E913837A-6C3A-41F3-92AB-2B49EC8EE227}
DIVIDE 1102M130 | {EF9A6FA5-0241-4F64-89EA-1575EA9DAF76}
EL DORADO PH 210136764 | {1AECFC8B-BC7B-4454-BB87-FD8F012E171A}
CHESTER 1102546744 | {655104DB-DE28-4723-9C66-99BF732C7F54}
CLARKSVILLE 210413352 | {76CF34A1-3FD0-4E72-BAFC-6CFED61FA5FB}
ORO FINO 11012022 | {81205B01-8688-4570-8F47-B08F18EDCF16}
PARADISE 1103CB | {916B572F-25AB-43E4-8DCE-50B2436F4EE2}
CALISTOGA 1102CB | {B6480B23-3B7E-4A3F-9C7B-82F910A25330}
DIAMOND SPRINGS 1106279670 | {1FAA72D4-5699-41F5-A2F3-C539D6B6ADA9}
FORT BRAGG A 110235592 | {88ABC052-C1CA-454C-9520-7292289269D5}
WISE 11011404 | {924DEF09-31E0-4543-805A-687FEB1C84E6}
BERKELEY F 0402CB | {9CBBDE0D-F420-4BB3-A85F-B498925D2703}
DEL MONTE 2103617344 | {A04AFFEA-C849-4263-A535-5ECE95BFA747}
MARIPOSA 2101151918 | {AA9A1768-272F-4017-B4A9-F1105C658F25}
BRIDGEVILLE 110237486 | {DC0A7D01-2EED-443F-A8C6-2C05CEB2611C}
FITCH MOUNTAIN 1113352 | {F0A897EB-747B-40C7-9836-35FB75DF52B9}
OLETA 110151740 | {FCFE42BE-9C18-409B-9916-4C477F3B3051}
VALLEY VIEW 1106P166 | {064EA0EC-DFDE-4FA8-8393-49958A6F3357}
PEORIA 17013186 | {52FB3514-9C62-49DD-A158-2A9A7CF95D5B}
JESSUP 11021550 | {B661BE4F-F0A3-491F-90E4-A5B76D06F645}
HUMBOLDT BAY 1102CB | {712389D7-97A8-43EF-99E1-6A4B64E5B114}
ROSSMOOR 1108CB | {812F7F32-99CA-4B11-A2F5-E536332A91A6}
LAS GALLINAS A 1106206332 | {825543F8-A353-4A25-8EB9-38A89B92A91D}
KETTLEMAN HILLS 2104CB | {854D235B-BDF1-4D5B-90C0-9DFFA17AD61B}
PUEBLO 110475462 | {937DE59D-E2A4-4423-B890-4B26446D8098}
CAROLANDS 040387073 | {4FDA6CDB-0E5F-4B76-BABA-C5F84B9DCB82}
SWIFT 2107XR526 | {F1466976-3470-44F4-BFAC-1A77DCF2CCD2}
STONE CORRAL 11087759F | {9C22AB4D-7471-42A3-9430-CD197230D588}
EDES 1112CR308 | {63D64072-C2FD-480F-8116-E56FEE7BD425}
CLAYTON 2215812394 | {5C22565B-317C-4A78-8439-2CD9CE62BBBD}
COPPERMINE 1104R755 | {7AEDC5DF-B44F-49B0-91EC-479413610904}
ALTO 1125902 | {A0846B72-320F-48B2-9E0D-A5F9C3A78393}
REDBUD 1101454 | {ADA3ACDD-1F23-47D9-8D0C-75E817018764}
MARIPOSA 2102CB | {D6398899-238B-49AC-A776-D1F3468DFF9B}
SAN BENITO 2101CB | {D701BA36-CC53-4635-AF00-A21AD8BDB3B2}
CLARKSVILLE 2104CB | {24BA7214-EA0E-4940-8D9A-B12BFFD010BB}
MC KEE 1103XR028 | {58E90993-9BBD-4F51-9BA9-AD36025808B4}
ALTO 112278672 | {792237E5-EE75-4319-AAE8-4FDB93CD8345}
FORESTHILL 11011802 | {9A3F5548-F595-4F3F-89FC-9574388096DE}
DUNBAR 1103831696 | {C2CDF183-5E41-4942-843C-F50DAE0D8FDD}
POINT MORETTI 110110726 | {F7013B1A-D0D7-4319-B5E7-A5441451D41D}
PIT NO 3 21011360 | {060881A6-D014-4A68-9103-99AC74B02ACB}
MORRO BAY 1102V86 | {4C9F3CAE-E991-4EA7-BCAB-BA03C4CEAE92}
CLARKSVILLE 2103593454 | {1F682AD1-C38A-4DAB-9AB0-5C203E1BC633}
PURISIMA 110149394 | {3CCA61DC-2699-479D-8396-73463C6B90FD}
FULTON 11011734 | {30FC3806-038C-4AC3-A393-91BFE1889F67}
COTATI 1105893 | {554E4D6F-0779-4CD2-B95F-DB489BEA9C8F}
NAPA 1112943158 | {C39D5E34-C18E-41D1-A210-D8B55CE52048}
CLEAR LAKE 1101CB | {4B824BDA-3530-4F86-B304-5BB8EAFD0730}
MONROE 2107380760 | {744357E4-A039-4634-8800-C090FE5B1DFD}
PEORIA 17046090 | {7EE01833-70BE-4E5D-9E9A-D8D904929AC9}
PASO ROBLES 1106R70 | {931CA1B4-3667-4C96-9792-EB8AF0018AF4}
SAN RAMON 2117CB | {C84D6789-7EC5-4B63-96CB-78D964DC0C39}
FORESTHILL 11011820 | {D7E3765B-F7D8-4BEF-8206-669D15220FDF}
HOLLISTER 210228421 | {17B07670-0E53-4796-89E8-790E1D545BFE}
EL CERRITO G 1111760530 | {EC819229-CAFA-4A70-A2A2-F76BBD0A5610}
COARSEGOLD 21035020 | {19623F95-3D51-435E-B42C-17FE4878C880}
WILLITS 1104CB | {19EB4414-DC45-4E37-BE88-7022C918AAEC}
GREENBRAE 11037315 | {9E4C5477-E966-43D5-8E24-BB781F7AED7E}
LAYTONVILLE 1101CB | {65E5FC7F-8C6A-45F6-95D3-74B8F1E3F473}
SALMON CREEK 1101460 | {227E29C2-4875-4BDB-945B-C5CAEB5F0B81}
ATASCADERO 1101CB | {98F44516-A7DA-4F88-98E1-7BF277BBBD67}
PETALUMA C 1109738866 | {0A86DDE1-72D3-4AA4-946A-5E91F4735FDF}
MARTELL 11033152 | {138F1A45-4EE4-407C-9580-B6FBC2BCEC83}
NARROWS 21057203 | {8D49CCC1-AF4C-4146-915D-64772DC7F3D1}
GEYSERVILLE 1101975350 | {1C85BACB-B649-4EAE-8382-1B9833570386}
CLARKSVILLE 210419772 | {484A22B9-C40C-4E37-BA87-C46E298525CF}
SAN CARLOS 1103313472 | {5D822BC7-216C-455F-A29D-9BF065B0A46B}
SAN RAFAEL 1101310 | {1A3DCF6A-D8D9-4366-A0A3-6456AFF85AD5}
MIRABEL 1101116 | {1FA8A5B8-216C-48A5-8B5C-D037DBE66063}
SAN RAFAEL 110139156 | {332AA22A-A859-478E-AF82-419A23B67FF8}
LAKEWOOD 22247381 | {5BA403AB-BCA6-4612-86C3-4865011547A8}
SISQUOC 1104CB | {4D6D6BF4-E19B-4629-9318-504AFE626164}
WILSON 110348236 | {A1AC7D41-B778-451D-ABF3-8E1F77E14CAD}
FORT BRAGG A 1103CB | {C8B7B79F-9539-45C9-8977-9A8FC5806A25}
ATASCADERO 1103A16 | {DCD0DC19-914F-4CFB-A070-C04552F2A497}
SILVERADO 2102CB | {E417384C-CD10-4D00-B136-62F02EAF1C4A}
GREEN VALLEY 21034929 | {80B98B39-6C55-4280-B2BD-3BF57A0B5E71}
GARBERVILLE 1102343364 | {221BC5D9-51C0-467D-BFB7-19AAD7C5E6CD}
SAN LUIS OBISPO 1103153199 | {47D9D526-74AC-4FE6-92E3-2FC62834180F}
CLEAR LAKE 11011302 | {4A405FCD-64B2-4AE1-B455-764875D385D0}
BASALT 11061781 | {230E7534-26E2-46DC-BF08-6106FB749B89}
MORGAN HILL 2105XR602 | {DF06274D-82A7-4C1B-8F47-D036189DB7AF}
HIGGINS 1110166282 | {F3D6F46D-CE49-42B8-ABD9-DE4AEFF8E29E}
PAUL SWEET 2109CB | {8C8A8C09-E52E-42BB-8F77-24A43F9E99B3}
TAMARACK 1102CB | {A8FAA54E-764C-43E1-B056-AE15ABB7C1D1}
STONE CORRAL 110878844 | {9C22AB4D-7471-42A3-9430-CD197230D588}
FELLOWS 21031100 | {A2B8C63A-2E3C-415F-A84C-6AAC2DF68E0B}
MONTE RIO 1113202 | {06C5DDF3-68CB-4362-94D6-24163B7FDD9B}
ALTO 1125296476 | {0ECD6D03-E99B-4280-9CB5-4AEDBF369158}
ZACA 1101Y72 | {1D20AD79-1B20-4BDE-B0E8-CF4AA41EFB2A}
JOLON 11027004 | {4198C21C-60CC-4B51-804E-CE0EA277ED81}
LOS GATOS 1108CB | {52AE67FA-770A-4A3A-8316-07026BFE1782}
MORAGA 1103838598 | {4C3B8436-25B4-4A62-8D40-AF9B1B8FB54A}
BAY MEADOWS 21029062 | {89242FEE-8748-42BC-8EA8-CDD97EA44EAD}
SISQUOC 1102CB | {92EB9460-E02A-4A24-A181-995BD1F9489E}
IGNACIO 110584764 | {E1F2559F-5071-40B5-BFDE-D70EABF698BC}
CALISTOGA 1101122350 | {EF1FA2C3-57EE-4BD3-91A2-9186818DE5AD}
AUBURN 1101CB | {0654A595-233E-4128-BBD6-123F6D88D1DE}
BASALT 110175886 | {0FAE99A3-272C-4D4D-AE6A-B1955441A366}
VIEJO 2203573610 | {4DC9724F-62CE-4CE8-B9B2-FC8D42753B78}
MORGAN HILL 2104XR018 | {98ADBEF9-BACB-4586-BAAB-FCF78599AE57}
OLEMA 1101CB | {BE6F7E5F-020B-49FB-90DC-2F40A691D506}
GREEN VALLEY 210397492 | {80B98B39-6C55-4280-B2BD-3BF57A0B5E71}
HOLLISTER 2105480430 | {2A202711-DF81-4789-BFD4-DC7744D8ADFB}
PUEBLO 2103355186 | {2B71AD28-97C6-40FE-8942-41E801469F28}
TEMPLETON 2112485608 | {F888EA83-160B-4C8A-947C-3FEEFB60DC7F}
FREMONT 1104MR584 | {B59BCFB8-3D30-441A-916B-9810D227F102}
VIEJO 22032634 | {4DC9724F-62CE-4CE8-B9B2-FC8D42753B78}
SALT SPRINGS 21011216 | {CFBBFBB1-419F-4DD9-BB1F-9B2617993BDF}
FRANKLIN 1101P138 | {DB131498-A71D-4A26-A77E-BBAB941A8DB9}
KERN OIL 1106412184 | {1BEA114F-1545-4690-B5EF-CA295187FA4B}
MONTE RIO 1111CB | {149DEC4B-D1C4-4F4B-922B-9B5C5A4AE0D1}
STANISLAUS 170275348 | {763723A0-FD03-42C3-9B8B-0F105886147F}
RED BLUFF 11031702 | {A3CC161F-1B95-41A3-B30A-2B1FE8B4155F}
KERN OIL 1106397902 | {CFE459FE-1CFA-431D-B9D9-918FFFA04245}
PENRYN 110550548 | {00BC1CA8-06FB-48A4-95C2-0F674B5818F3}
JARVIS 1111MR122 | {1A5CD57B-504B-4150-A099-4F8257FEDA9C}
HIGGINS 11041006 | {6831EC63-2DE1-4FA9-8E52-ECEB96F95CDF}
STELLING 1110396595 | {9194A519-A8B3-47FA-9F1B-13F504BA79E3}
ANTLER 11011376 | {96A0A843-7251-461B-B57C-57ECCA82B23A}
FELLOWS 21041074 | {99CA2E77-9D49-4EAD-A742-E8CB938D605F}
PUEBLO 1105419634 | {D8943DC9-C3F8-4085-8F3C-401265EC905F}
TEMPLETON 21132949 | {7937BCC6-E91C-41D5-AE9E-FB212F98DDB6}
LAKEWOOD 211093966 | {00D76738-D88D-4571-9934-906827AF7F21}
GREEN VALLEY 2101380922 | {167D6A57-A795-4EF1-A1DB-E61FA7A54614}
SHEPHERD 2111327814 | {043E8F07-84F7-4AE7-BB3D-18F6172375EA}
SILVERADO 2102714 | {65C50E41-4A19-4EF0-8E02-55AD7C68E0C7}
TIVY VALLEY 1107869946 | {8685FED6-DA63-4202-8ADA-3D58BFE83B0E}
PRUNEDALE 11073062 | {9055CD6F-1385-4DAA-B189-3CEA20BFACDF}
GIRVAN 1102CB | {F8758432-B450-4943-97B4-52B80EF2F512}
FORESTHILL 110150486 | {FE85142D-4AEA-430F-BD77-45CC919584AA}
BIG RIVER 1101952 | {1DB69746-E909-4FD7-90E8-E346F8AB657A}
UPPER LAKE 110175370 | {5002339C-3B44-461E-A16D-6DB263D4D731}
MONROE 2107436 | {3D15A0FB-7F79-449E-9100-AEDACD615B82}
HAMILTON BRANCH 110190334 | {6FA22C4C-B16C-4BDC-8F70-7E0F32F87C45}
PANORAMA 11021249 | {6303BED6-9051-4E72-A1E9-A3825361F885}
AVENAL 2101602496 | {25E0F7F5-6399-4822-97AD-9B04397D81D8}
ALHAMBRA 1105295792 | {AC26085C-F280-4A6A-A0D9-361E1E9983F9}
OLETA 11021204 | {946E6116-FB8B-4590-A386-CB8F9AFD8BF3}
MONTE RIO 1112212 | {C70CA0FD-CD6F-47B4-AE85-ADF07161D721}
STILLWATER 110248952 | {096694C8-1954-4FED-B3CE-6072F54B2C4B}
BOLINAS 1101504 | {24FD9F9F-3AE5-44A3-85E5-C29F5C852455}
PAUL SWEET 2102337544 | {593613BC-2474-4D8A-8E89-2D049FCAFE94}
COTATI 1105328 | {711CF875-45FB-4C9E-91F5-632D204CB23D}
PARADISE 1105960434 | {4F7F1505-2A84-49CE-A88A-5D1C68BB7B5C}
BRUNSWICK 1110CB | {AC82A3F6-A35E-40B3-B30F-C23643AC0649}
PINE GROVE 11013166 | {FB4870D6-B142-4F5B-9D0C-2C983965E8D9}
LLAGAS 2101XR584 | {4A87133B-C25C-4081-8935-66AE4E30F1EA}
HATTON 11012026 | {593FA41B-396B-4601-BD50-0DE927CB7E5A}
REDBUD 1102CB | {5D4D8690-5B01-4EDA-9ADD-A0F82EE8F0D4}
COTATI 1103675834 | {D681E6AF-06CA-4983-B4FB-ED08B0DAD260}
NARROWS 2101CB | {7B0321EB-AC29-4857-8514-66B11EFDEF70}
CUYAMA 1103622728 | {EC646814-C576-4C16-B414-32B05AD6EA11}
FORT BRAGG A 1104529076 | {ED095E9E-F3A0-4C4B-ADA3-9E3DFB5A9FCD}
DUNBAR 1101CB | {099221CD-5C0A-49E5-8576-2B334B5F477C}
CORRAL 1101173174 | {488178E5-61FC-444B-88C1-9B8C60F860FF}
ELK CREEK 11012212 | {812EE935-23AB-45F1-A410-24F4ACD87AAD}
TEJON 11022455 | {A9055457-4647-4903-9845-7B35001BBD43}
LOW GAP 1101449990 | {9677DC50-AB85-42C6-9822-52AD410900D7}
CLAY 110359714 | {CC378BAE-BD49-4ABE-8599-52019F7E517A}
ROSSMOOR 110479146 | {D2330A0C-459B-4F6C-BE3B-0AABB85A2AF8}
NOTRE DAME 1103317782 | {E54B3868-C992-4672-B01F-A1BD60263D71}
BEAR VALLEY 2101CB | {01E04AB3-4BC7-461C-86D6-3A3D5CD166F9}
OAKHURST 110310570 | {3D247DD8-C725-4A26-BE65-60FA26890CB2}
EEL RIVER 11028416 | {6D6CFD45-47DB-4466-97E2-D7B4460098A9}
FORT BRAGG A 1104CB | {743824B8-B7E6-418C-AF37-30E4E0572D08}
BELLEVUE 2103940234 | {018227D6-38CC-4EE9-BD26-7E3FF5AE9B25}
CASTRO VALLEY 1107MR586 | {AD5F876C-C0A5-47C7-B722-6D39867E5D84}
WYANDOTTE 110641650 | {87BD5616-A670-4B3C-B36B-8B72CB70DFA6}
GREENBRAE 1102CB | {AEDCB032-1AC1-4F9E-A5A8-36B12E3777AB}
FROGTOWN 170274648 | {C985F098-6ECF-4C69-B902-1B5157262ED5}
LLAGAS 2104XR242 | {AF07F25E-155C-4D19-8872-642A3CCD5556}
NARROWS 2102CB | {30B38EC8-F2E7-47AF-8BC7-D7EB75673131}
MOLINO 1102535 | {3827F6F2-326F-4FCC-9EC1-DB4311EC910A}
PEORIA 170567898 | {50E0B9CF-D877-44E3-8923-B1CAE75FDAA7}
ELK 11011272 | {62C9F82C-9B7A-4C03-B528-D0CC602C0334}
SILVERADO 2104940 | {64400634-E6FB-4B73-87DB-F50EC6751223}
CLARKSVILLE 210419632 | {E10F57CA-31E3-4642-897F-6FA410857C1A}
ALPINE 1101CB | {147B95CE-2512-4395-8036-5E41FB98DF5E}
HOOPA 11013304 | {40D83712-E530-4392-B692-30F2EF646603}
SONOMA 1106746130 | {55EA2698-B693-4D7C-84A6-FBA73C981197}
PAUL SWEET 2105197474 | {33AE2657-6F42-4109-A970-89EF5E991C73}
ALTO 1124246034 | {7D95830D-A648-4B7C-9FF3-8B171C1CA56A}
DOLAN ROAD 110122158 | {95DA73C9-4DB4-4C31-AFD8-C43A5BC36425}
SAN MIGUEL 1105CB | {9DE0BAA2-B8C4-4631-BEBA-CFB3AF750506}
BELL 1108CB | {35B30399-E588-44B0-B481-56F6CD9688B5}
MC ARTHUR 110168442 | {85EE7B40-6D93-48B5-9C94-EBAACB072BA9}
COTATI 1102468 | {E06C85FF-5B48-4064-AE0D-D34C585D0676}
PAUL SWEET 210410916 | {9E32E9CD-A939-47B7-8D32-52540B68C5C6}
GONZALES 1104415382 | {1F605782-8F30-4773-8038-34124B7BD9C5}
MARTELL 1103CB | {4DC1CEF2-A050-43F8-AD47-CFA46D056F9F}
PACIFICA 1101777484 | {4118C23A-F427-46E8-85D2-FD56A1055C29}
HARRIS 1109700 | {6EE208A5-6ADB-44F7-95B4-016C09D6A385}
MOLINO 1101277292 | {73A79C1D-983A-4279-A3FD-02A1B497A62F}
CLOVERDALE 1102674 | {D3629DD4-F83C-4237-B37C-A36F4F11F0E0}
SOLEDAD 2102304826 | {D719DAC6-D0A1-4861-8256-3730BB387183}
LAYTONVILLE 1101402 | {03DB1220-E098-4294-96C0-8000CD99CD41}
POINT MORETTI 11015104 | {2D522AA5-8F8F-4B96-B755-D0E01134E6CB}
COTATI 1105103816 | {775E53AE-0A4A-4EB7-B07F-0C65E0B68CCC}
SILVERADO 2104632 | {841AD544-FFC0-4D92-904D-46B27F7D9430}
KONOCTI 1102714370 | {8A5CF734-63C5-45CD-9511-BDF8DA98EA25}
DEL MONTE 21032144 | {572A903E-D7FD-4349-978F-5FBD205DDA11}
BERKELEY F 1103BR110 | {C6EF6B66-22B5-4479-8720-12455A79DA2B}
LOCKEFORD 210220355 | {34045FAB-FD0E-4469-952F-B8E16E6D8945}
SAN LEANDRO U 1114523960 | {A807698D-F940-498F-A1CC-0E26E202721D}
SHINGLE SPRINGS 1104CB | {40341932-C636-415B-BE6F-5D9D8CD0A383}
LOS OSITOS 2103695270 | {40F1B87F-AB3F-4DE0-8638-58D9EA205806}
RACETRACK 170311270 | {502CBD17-B1A2-4DA5-B36F-93229EF4E9F0}
SILVERADO 2105CB | {6A947491-FB60-4043-BF5D-F50FFBCF57D9}
BRUNSWICK 110350070 | {DB1F9D2B-D359-4F2E-9F3F-F43B886E9D0B}
SAUSALITO 0401CB | {FA2ACC7B-DB5F-4398-838B-151CA038E350}
FRANKLIN 1104P122 | {0A789542-40BD-495E-8D9A-5D7EB997F537}
CLAY 110184572 | {537E07C0-FB8F-462B-87E9-2D8AA468190F}
CHOLAME 1101R22 | {7FDC77D6-0D2A-45F5-A1E8-7D8DC458C0F0}
SAN BENITO 2104CB | {BECA105B-BD3C-4CFB-85DF-E12EFB68ADA7}
APPLE HILL 110497086 | {E9B2D551-2CAF-489B-9D1C-4D1BCFDB0559}
REDBUD 1102510 | {01484F25-B16D-4119-BFC6-A19899DBC158}
GIRVAN 110255307 | {F8758432-B450-4943-97B4-52B80EF2F512}
PRUNEDALE 110736920 | {3866DD60-BF41-471C-88D6-BF070A4B7C9F}
FROGTOWN 1702L5407 | {3530973A-E1ED-42D6-80CA-474C64476B90}
HORSESHOE 110151538 | {87800A96-4222-40F6-B470-AA1E26FEFB33}
MIRABEL 110257840 | {BDF5B432-76F8-4E7C-875F-0CD4088812BE}
RED BLUFF 1102CB | {C7F1169F-7F4A-4C3C-8022-D0BF917F0199}
BIG RIVER 11012989 | {2D8E8FC7-3A5C-40AE-8F67-02A91CEAEC16}
MIRABEL 1102332 | {98884EB6-8FFE-4527-976C-FBFB7D667FB9}
CLAY 110334338 | {AE111B59-4073-4BA6-A6F7-C46E4FCA24F4}
SILVERADO 2105309298 | {095C5936-5504-4C4B-8302-1844A5C0B939}
FITCH MOUNTAIN 1113356 | {F1192C47-0912-4CBD-BF6E-19925F71459A}
EDENVALE 2105XR336 | {2039711E-7AA5-4D64-B713-BB2955894DC0}
VASCO 1102886522 | {4653D811-6732-4F47-994C-B6C9ADAB66CF}
PUEBLO 21031968 | {49549F40-A326-4458-963A-8F0223D6E156}
AUBERRY 1102R309 | {6CB8407B-8DEC-4DDB-A06C-70CFC4C2C27B}
REDBUD 110244119 | {D29B0306-223B-4BFF-9389-253396BA7A0F}
CAMP EVERS 210584166 | {EE077F7F-8175-4265-8512-03731CF3E11C}
SHADY GLEN 1101941844 | {D1463BB4-C6D8-4652-B8D6-F5D55EAF695A}
MORGAN HILL 2110XR326 | {FEA8F80B-51AF-4084-A9B9-47D11430DD95}
HIGHLANDS 1102CB | {12D5CC7A-B2CA-4EEF-8AD4-C988E70110AA}
PASO ROBLES 1103N50 | {382A16B7-3BCC-4C59-941A-61838BC92D6A}
SAN ARDO 110291894 | {3A8CC481-FD54-4503-B6C3-B374A7E06AA7}
ECHO SUMMIT 1101344250 | {501D001C-604C-4CB0-BC61-4A03C3824F33}
HARRIS 1109183860 | {62242811-5FAB-4F8A-8BA0-8F1F1D633349}
FORESTHILL 1101890670 | {ED9435F9-E06B-4A98-B053-EB0C1DC8369F}
SONOMA 1107606 | {8F27A86E-670B-4331-ABF1-9BA9A6222879}
CRESCENT MILLS 21012230 | {729A138E-F406-4953-BD8A-A6BF7C82CC1C}
PUEBLO 21021326 | {F776B1CF-724B-4DB6-A87F-FF45F4D5AD0B}
OLEMA 1101512 | {818B580F-3855-41D8-9229-869A2B79816E}
EL CERRITO G 1105BR304 | {9DF9A52F-32F8-4676-BE5E-F9A3D03712AF}
PRUNEDALE 1110607060 | {A8CB8177-0C64-42D1-A7A3-6215FC559483}
SARATOGA 1115463510 | {D41C5049-957B-48AE-B573-6564E214A3B4}
PALMER 1101M84 | {F73EB641-FFE0-4811-B0D3-9263F0EA89B1}
OCEANO 1106V32 | {2FEE1CE0-BC95-467C-8CDD-CAD4D3CD2579}
SONOMA 1102118 | {4BCD6EE2-7FEC-4152-907C-A38A16D3BF51}
SAN MATEO 04109068 | {5F8605AA-7B64-48E3-B49A-133A5E452602}
MOLINO 1102495692 | {6A15A22F-857C-4EC7-B263-5C7A16EAE30B}
SYCAMORE CREEK 1109CB | {6DD04BFB-4C98-43A2-94E5-EF1AAF874533}
ANTLER 11011520 | {F81A30D4-0CE7-4E7B-A7EB-CF369AB53D11}
DUNBAR 1102264 | {18F70BF8-C85A-4C7D-8180-406A04F2532F}
MONROE 2107434 | {3D15A0FB-7F79-449E-9100-AEDACD615B82}
UKIAH 11152504 | {3A01C04B-1C28-4E51-9D30-D6AD9F524D9D}
CLARKSVILLE 2110CB | {45555E2C-8D80-4EF7-9197-7511D877BC26}
FELLOWS 2104CB | {99CA2E77-9D49-4EAD-A742-E8CB938D605F}
ALTO 11201214 | {B3DBF89F-E691-4A93-8B05-2E162DB10E10}
WILLITS 1104329646 | {B6D81FD3-E8F1-4789-8A3D-786E0C133AC6}
OAKHURST 11035480 | {194E4857-C055-4CC4-9616-06A060725A90}
ROB ROY 210538430 | {FFC04C14-5557-4FC3-9795-3587569ECB50}
DUNBAR 1101137736 | {7EED3CE2-525A-40E2-A0FE-AAB7CF9E89BB}
DIVIDE 110266960 | {EF9A6FA5-0241-4F64-89EA-1575EA9DAF76}
CLAY 11031230 | {D62CDDF4-E093-4960-B995-54A7DAF191D3}
FLINT 1101750 | {070C906B-0802-4429-8F7B-A68007FED9B4}
MERCED FALLS 11024000 | {8DA8BDD3-B9B9-42D9-AC7D-1174537479B6}
LAMONT 11024222 | {97C1B34A-95F8-4CCE-8DCC-4962D06B743A}
WOODACRE 1101404 | {9E6A6B97-69AF-4332-A126-23324C3DC522}
CALAVERAS CEMENT 11011419 | {31F34B0C-04AD-46C5-88A1-857D16F62C5A}
DEVILS DEN 11019470 | {EA4C9C10-BAD2-4A0F-9CF7-5CA727AB7653}
DOLAN ROAD 1101857972 | {EB37E4EB-78C1-4046-AF1B-2299D2328F22}
CASTRO VALLEY 1111227862 | {75D298E6-3FF1-47B6-9B91-A2291860E391}
COARSEGOLD 21025380 | {28AC0DE3-760D-482C-B0A3-0B7999D74D44}
OCEANO 1102CB | {53EA2B69-06B5-416F-96AE-9EC7627A84C5}
SISQUOC 1101M96 | {ABA8F0B5-44C5-49D7-B132-C788FC15DD52}
ELK CREEK 11012228 | {AC290F88-25E1-47EB-BF8A-1F1AD055C84D}
CLARKSVILLE 210319572 | {AE109701-21ED-44EA-AA47-DDDDD6EEFB68}
CEDAR CREEK 11011362 | {81F58F11-9F6E-4CC2-A527-0CBBB670DE91}
VOLTA 1102765366 | {2D79CCBE-1B8B-472A-B9BB-B34254CCD666}
CORNING 110182846 | {0237A482-F336-4387-BDDB-C855D376A309}
ORO FINO 1102CB | {4BB60C53-9CA3-4098-8B28-FE44C4ECF9D3}
COTTONWOOD 11031508 | {86195D79-B13D-4A31-9815-45E1A5BFFF0A}
TAR FLAT 0402CB | {15F62F46-8DEB-4CCA-80E4-1A07793D2B95}
WILDWOOD 11011576 | {57B8A89B-DB5A-4A47-A82F-ABC7F06A8571}
GARBERVILLE 1102CB | {76599403-EF2F-43B7-895E-85F706D26E36}
FORT ORD 21069656 | {8BA4213A-D34B-4B87-B8F6-E146FF0B7281}
CLARKSVILLE 21096502 | {A0936C28-A756-47FA-9C1E-76F4B7CFFF7E}
HIGGINS 1108CB | {F3F43510-36DF-4FCC-ACB0-6058CB728BA2}
MIDDLETOWN 1101481876 | {302C19E7-740B-49C6-83EC-9E70AC44D5CB}
NARROWS 2105CB | {2611646A-C593-4185-9486-0AA063D164D0}
BRUNSWICK 110532536 | {547CB5AE-3FC8-46F0-9836-780E7F4C0AE3}
GARBERVILLE 1102176634 | {221BC5D9-51C0-467D-BFB7-19AAD7C5E6CD}
PLACER 1101106534 | {62739046-02AD-4CE7-A6F9-18132F783A35}
LUCERNE 110638436 | {790F1996-ADCE-423E-BD1D-F157FD535C39}
SAN LUIS OBISPO 1104V40 | {84A17C4B-1356-4E5D-9790-C7A137661BEE}
VOLTA 110237350 | {82B5D74E-1D42-49A6-873C-1363407619B8}
PIT NO 1 1101CB | {185974AB-4212-4B5F-B111-C93E97C24964}
MORRO BAY 1102W34 | {52C280BB-FF66-4850-B734-B05EEFB600B7}
HIGGINS 1104533648 | {7316CABA-ACE0-4406-9BB2-A4017DAD0078}
KETTLEMAN HILLS 2104358094 | {838618F9-BF36-4DB4-B2E1-2625851B3DC1}
SISQUOC 1102M54 | {96906956-5C77-4774-B51C-564876632563}
SILVERADO 2105247660 | {99F7BEAE-C3B5-4D12-B703-F0449CE0ADD3}
CANTUA 1101CB | {B55C2E19-B2B9-47FB-B0FA-5E9F76A070B4}
WHEELER RIDGE 1101CB | {E4E8B6C8-61FB-4D05-90A7-1AEC2AB09918}
DIAMOND SPRINGS 1107CB | {01A8C6BD-323D-44E5-A686-1246351A46F2}
PRUNEDALE 111022160 | {55A8BEF6-0A82-4DF2-9C14-9045CBA42576}
CALPELLA 1101931142 | {E12D2ABA-05E0-44D9-A574-E03478B74646}
HALSEY 110176178 | {7B5F2382-5AE2-4C66-951C-F3B7A019CDB8}
PUTAH CREEK 110546162 | {B44C5067-6D0E-4713-9558-13070DEDA962}
SANTA ROSA A 1104173590 | {BF693435-FC48-417F-BBCC-18F887A0E298}
NARROWS 21021254 | {F3B439DF-7706-4C2F-8999-BCA70EF18266}
SANTA YNEZ 1104Y04 | {1E768305-B6AF-4963-B2D5-92FDAB6A5028}
MORRO BAY 110187487 | {DC1CD14A-C73E-417C-A65E-B1AE2FBC8341}
CLARK ROAD 1102514690 | {680899C8-622A-4D07-B62D-BFF41E670A32}
TRES PINOS 1111CB | {81D7ACD1-11AF-45F6-91F4-8D9CD5CC46FD}
WISE 11022054 | {E6EC7043-C8B2-457F-AB90-031C70C010CA}
PENNGROVE 1101190 | {FC0AD92E-E9B6-43B4-B87B-301D88F19DDA}
ANNAPOLIS 110176842 | {2E3AB06D-E271-44D1-BCDE-8DE501692F34}
PAUL SWEET 2102774760 | {494C5866-0CBE-4898-9CD2-71A0E0DFEC0C}
PACIFICA 1103CB | {5EC3A666-1799-428B-8C0E-2A981579542E}
MORGAN HILL 2110654924 | {674F8E15-1E29-4545-B316-3ABCD054D65C}
MORGAN HILL 2105XR152 | {91E130A2-6B12-4607-8077-CCA3F4CE535A}
VOLTA 1102CB | {DC239059-B1DA-4C89-A482-3310C8764DA5}
AUBERRY 1102CB | {004C66A4-EFD9-4F4F-AA71-77719D3D9AC9}
SAN CARLOS 110475210 | {30A0D7F0-FF87-4B5E-B98B-6A0711429281}
HONCUT 11026130 | {3DAB252C-5A42-4BD0-ADD0-23CE62160133}
CURTIS 170190120 | {9E6CCAD4-16BF-438A-8FB8-933F07D27C09}
CURTIS 17046060 | {677BC4CE-74C4-4870-9B50-45491FB41EEF}
VOLTA 11021650 | {FEE27DB0-3817-4D7E-9EF5-189449263C1D}
FULTON 110746958 | {01F2557C-4641-4BA6-8DDF-FA4264339C1A}
COTATI 1105CB | {03190DAD-5324-4E1C-86DE-04D88D55A9A0}
HOLLISTER 2102676164 | {5ED88047-4B28-4CB1-8810-2C6A7B9E00CC}
BASALT 1105CB | {6CFDCF11-C002-42A5-AACA-1A265A50033F}
HATTON 110240461 | {E55048C4-CAB1-4B6B-99F6-30BB24FEA325}
BAY MEADOWS 110565187 | {4460A2C3-E57A-4228-8E6E-BAA1830E8AC4}
LINCOLN 1104685276 | {62CF7EB0-1F27-4DAA-93C0-D5A9F63BB597}
MORAGA 1104N532R | {8FCB98A6-A5C4-47A0-A545-FF069C01B16A}
CHOLAME 210249414 | {946E7382-BCE9-4876-B322-206F92E831CA}
FRUITLAND 1142CB | {C08075C5-E7BA-4353-AF25-7A00C76C5CA3}
HIGHLANDS 1103828 | {F617C2F6-F9CA-4233-ADD2-A5EEE40355DB}
MADISON 210144634 | {3606619A-937D-46E3-AFC7-2B9E8CB032C3}
SONOMA 1103581588 | {989A9D45-A06C-4EF7-99F0-5A8D5A73FF7C}
APPLE HILL 110313312 | {4D62B52A-6FFC-40E3-9CBB-F053155CEAAC}
STAFFORD 1102361952 | {07D78386-6A73-46DA-81CA-B20D2445579F}
WILLITS 110434008 | {5B3D2F2F-DF90-45C0-963C-1589633A1498}
CASTRO VALLEY 1102MR518 | {B72D11A7-A3E3-4487-9B62-E0B9199739E9}
TEMBLOR 11041034 | {C2992F46-2554-463F-8E87-219C3C230B9E}
WYANDOTTE 1110747922 | {60F5524C-0FF9-43B2-B1B9-D30D40C3AD67}
HALF MOON BAY 110329454 | {6106A145-F67B-4637-A42F-8BCEA85E7B24}
SAN RAFAEL 11071166 | {64A83390-336F-46D2-AA1C-9D91A30B0162}
NARROWS 21022718 | {81AACB66-94AE-4D98-92C9-EDFFCF82F0F9}
FORESTHILL 110137238 | {05132EF1-E962-492C-8CE4-DD542C3B3D15}
SAN LEANDRO U 1114MR544 | {399AB5C7-22B7-4F32-8432-A7E05E9E2D06}
WILDWOOD 1101CB | {47D06C81-6B61-4B8B-8054-D7C4BE7B9ED2}
ORO FINO 1101CB | {4F055C2B-F555-47EE-931F-D64958E5EDAE}
PENRYN 1105168616 | {91345D7C-F3FB-4825-B072-AFC3A521036D}
RIO DELL 110138332 | {A95F636D-9823-4D40-A219-A36C35F660D1}
AVENA 170212876 | {3E1C42BA-A837-4BE0-A8EE-C29428358DD7}
VALLEY VIEW 1106CB | {D9DED303-0FA6-4611-A466-91E33B741947}
ROSSMOOR 110639424 | {DFA21900-F572-4D0B-90D6-E67080E9EF87}
OILFIELDS 110241992 | {30F0CC79-17F2-4C3C-8FCB-5EFF56537510}
LAKEWOOD 211090650 | {8D56729D-62B8-4F70-8336-DC0D3C2D910B}
CLEAR LAKE 1101740076 | {AF3B7AFC-B2F6-4613-A8C9-551A8B6F40B8}
SAN RAFAEL 1105CB | {BA67EE88-1E6D-48B2-9DBA-46721926CAE7}
WOODSIDE 11018884 | {E37F33F6-1C0A-4C76-AC62-7F0B65A2F196}
PAUL SWEET 210438286 | {9E32E9CD-A939-47B7-8D32-52540B68C5C6}
CALISTOGA 110143924 | {07D5D1F0-E088-492A-95F0-C51ED4C7A4B4}
JARVIS 1108767280 | {518B32E2-92EA-4E90-A3AC-D00B405E1539}
CLAY 11029999 | {D868AF66-93C2-4B3E-8187-2C428023C31E}
PARADISE 1105499094 | {4E875C07-9BF0-416D-8352-B1380CD2F62E}
FORT ORD 210633694 | {95AB47FE-6B9D-4A04-9C44-EED36F1BA13B}
CORRAL 110359770 | {A87A01D7-FDFF-4B8F-B41F-FAA11796C3AB}
CAROLANDS 04018886 | {029D0D55-2BAE-4088-B646-F2DDA198BF80}
BANGOR 11017446 | {1FB07492-7817-4281-B458-54D457C1DE65}
OCEANO 110376678 | {2258BA59-F952-4D7E-A5B4-7204CE2B68CB}
PAUL SWEET 210349246 | {BA3D6A76-5335-48A7-9116-A38FBA76779B}
MOUNTAIN QUARRIES 21011350 | {6752B4B6-FF0C-4C57-ADC9-D57090816B6D}
SARATOGA 1107413816 | {717BE6DE-1A86-4939-B958-630A186C1AF4}
MILPITAS 1109XR372 | {D897A506-3C26-4AA6-AE93-1BA5129BA14D}
TEMPLETON 2110211842 | {816EE1E7-10CB-4545-BFF4-506903516309}
SMUD 15805CB | {87AE3F12-9778-4DE4-AC04-CB4537906F79}
MOLINO 1102344 | {A98FD5E2-DDE3-4E25-9F0F-483626AE2A81}
GIRVAN 11021028 | {F99AC090-1DE1-40AB-890A-9A8208858415}
SONOMA 1104414 | {13C5D467-3A5D-46D1-9164-0C6474ACC9E0}
LOYOLA 1102CB | {27A786CD-A523-48EE-89CB-20E33A9B5F17}
ALHAMBRA 110281034 | {CC913DB3-6A51-493D-BE11-D5EAF399B0A8}
POINT ARENA 11011296 | {827A54D0-0188-46E1-B6F0-E7D696DF4D89}
MOLINO 1102318 | {937FE0BF-1949-4B31-99B0-C96DCB7F5DAB}
HICKS 1116647210 | {9B3BCE26-3F49-48E0-A9CF-1FFE9B2444C4}
WYANDOTTE 11095607 | {790FA841-FFAA-4636-AEC1-FF360B754DBB}
MORGAN HILL 2105XR312 | {03C8F227-2007-4B73-A689-5FDF30542245}
RINCON 1104786782 | {DDE06CFF-C1C8-453E-9DCE-C51203C62E9C}
WALDO 0402258792 | {41C45E4C-83D0-45DA-8DDC-FF29D2FC8610}
IGNACIO 11051943 | {E636DD2B-323A-4E65-AE99-16FA1288A9E0}
CURTIS 170539256 | {60313232-3855-4646-B9A6-D03E4546E4FB}
OLETA 1101190308 | {C597D1DF-05AF-4117-9139-6F79BFFC0A15}
CMC 1102CB | {8AF78B6A-BE16-4226-B393-4AC8AD7FF084}
SANTA ROSA A 1108626 | {B916F1BC-FDC7-4604-9F1E-064F6D66F284}
COALINGA NO 1 1109696152 | {D2837AC8-6682-41DA-9CAE-EF262EB89AC9}
VIEJO 22019490 | {D5629837-45B4-4B33-A660-AFDD9F409AB3}
BOLINAS 1101530 | {E368881D-C918-4559-9B53-61F2E5E1FBD8}
ROSSMOOR 1104305926 | {E7EBB058-9B4D-4CDE-B87B-5DAAEF3E4493}
CLAY 1103CB | {12C9081C-95BF-4D8B-9422-8F9EBEEF2908}
BRUNSWICK 1103904574 | {1762E3E3-DCB4-41D0-A815-060A5A457F0D}
HOLLYWOOD 0401811742 | {492D154A-EE0E-4F92-B9B9-FEA1E967CA18}
LAKEVILLE 1102367100 | {4BF5FD3C-5BBE-425E-88E7-6C08A33E293B}
OAKLAND K 1104CR210 | {5D6DF9FD-08CF-4E49-97A3-2B3AF27CC711}
BRUNSWICK 11051030 | {B6CCA276-60FE-4AA5-8337-7F4B8BC06A51}
PENRYN 11051342 | {C5308B22-07AE-4998-BAA1-CBC87B70637B}
FORESTHILL 1102CB | {D5AE9DC8-C124-4C49-BB35-C0CDE45BC05E}
SANTA MARIA 1108M16 | {31A32213-8989-4C12-A58B-F9184AC14DCF}
GANSNER 1101489276 | {248F09B8-1D5D-4034-96B7-C372BB4594AA}
WRIGHT 11103800 | {ABB28193-DF6D-40B9-BA16-1713A8EF4B58}
SHADY GLEN 11012768 | {CDB0DAC7-54D4-481D-AA9B-BDB5A3BBD3C1}
PARADISE 1105829194 | {DA9F7CD6-6FE2-485B-BB50-5251F27CEFD7}
SAN ARDO 1102502 | {DAB3BC36-43FB-41D1-88AE-89CBCEF6CBDB}
CURTIS 170210940 | {16922C05-7DEF-4043-B388-9531C1140314}
KING CITY 1106958502 | {2515B17E-1532-47B4-AD33-23C2F28EDE84}
PARADISE 1104457900 | {60D04F67-B0A9-4BD6-8DCF-759CBE65FF11}
OILFIELDS 1103N40 | {5FF9C387-FCBA-4CB4-A5E3-8021D551E54B}
VALLEY VIEW 1105CB | {7F8D329C-2906-4CB9-89A6-48A9455878D0}
COTATI 11025080 | {E06C85FF-5B48-4064-AE0D-D34C585D0676}
SHINGLE SPRINGS 210511172 | {91D53CD4-6008-41E0-B5BC-B59F60B0DDAC}
COALINGA NO 2 1105897858 | {BB2EB972-0241-4416-BB6F-CD01FA83C53E}
FRUITLAND 114263170 | {BDFC6231-C003-4BB6-9C95-EEAEA882FC5D}
TEMPLETON 2110901690 | {C383B6E8-D569-48F8-A225-7445F785217A}
PINE GROVE 110213438 | {D284AD02-1208-4AE0-8968-E88D8134BCC9}
SAN RAMON 2101CB | {D5C8CF3A-0CA8-4CD2-870D-AC7D1B010386}
POSO MOUNTAIN 2103388671 | {B9DBC9F0-4947-4732-B802-049D3AB22FD5}
BUTTE 11052224 | {99D60B56-5961-4789-A3E0-D520C3413381}
CAMP EVERS 21035404 | {08861202-71CD-43A7-A4E9-A7647717C791}
WEST POINT 11021305 | {0EFB4216-A177-4018-B731-828073FEC64E}
WILLITS 1103CB | {30B0A48E-C3E5-42AA-9273-8BF1B6001968}
TASSAJARA 2112725488 | {3FFF1795-1315-4A71-8E91-178B9A0CCDE5}
PAUL SWEET 210910216 | {8C8A8C09-E52E-42BB-8F77-24A43F9E99B3}
LOGAN CREEK 210237316 | {8700E55C-38C6-41AB-AF2A-3B50EA0B2E05}
UPPER LAKE 1101861806 | {911C4C68-2E5A-42A2-8C57-88BC3B5D0196}
SAN RAMON 2107MR441 | {92E22518-527B-4324-B90B-D5A4496A4612}
GREEN VALLEY 2101135762 | {E176FCE3-EE7E-480F-BF55-388C6C19C1B5}
SAN JOAQUIN #3 1101673480 | {1AD6607D-F312-473D-9241-E313EE11C5E3}
HICKS 1116983580 | {26706A0A-D462-4709-8596-704DD2D34F48}
VIEJO 220393964 | {4DC9724F-62CE-4CE8-B9B2-FC8D42753B78}
CONTRA COSTA 211496897 | {E98A5614-0363-4815-B36D-4D8FAB4E4D57}
MORGAN HILL 2110XR164 | {11D639D0-BAAC-4BDC-B7F6-D7D6C9CC18B0}
PETALUMA C 1108632 | {276EDBF0-4288-4842-B2CC-B94871DC6986}
PHILO 1101CB | {A45E0124-BCF3-4DBF-9317-CD21317A326D}
OTTER 1102CB | {D42BED5F-FA94-4772-B8B5-334F2629EC25}
TEMPLETON 2109R34 | {D690C4D2-AB5F-4E55-BE78-1BFC0A0158F8}
GREENBRAE 11021254 | {343DAC73-DC1A-4C06-8C35-1C7245E7BB91}
SAN MIGUEL 1104R66 | {3F83E7A1-428B-491F-A667-31D49B0E1C27}
GRASS VALLEY 11032180 | {5AF8F290-EBD8-4203-A9EE-DEB7B6BE68A5}
TEMPLETON 2113A20 | {63FF5E85-7320-4916-95DB-09A821D7A9F8}
BOLINAS 11011236 | {6AEEBA49-CC4B-431B-92AA-34EB4CB9F64F}
FULTON 1105142 | {63777790-64ED-4263-AFF5-02757B725BB7}
COTTONWOOD 11029026 | {BD544C17-FF5A-4B33-BB2A-02C4080D2F78}
ORO FINO 11022236 | {C813897C-7FF0-4426-960C-CC77387AFFF1}
BLUE LAKE 1101CB | {E31E0DBD-FA9C-4715-8BFA-E451681E5B43}
SAN BENITO 2101310344 | {D701BA36-CC53-4635-AF00-A21AD8BDB3B2}
LOS COCHES 110256346 | {C48784E3-4EDB-45E6-AEA2-4A807640BDC5}
PASO ROBLES 1106CB | {569EC071-DD47-42F2-9569-DF5DC93512CB}
SYCAMORE CREEK 1111976428 | {78341850-739C-48F1-B508-024DE20CD1AD}
PLACERVILLE 21067522 | {A7A5500C-8FAC-46D4-9BD4-7B5D3F1E7024}
CAROLANDS 0401CB | {AFAFA564-C801-46B9-B877-3979D8BE4904}
ROSSMOOR 1106266602 | {C56741FC-B98A-4CE9-A61D-A05F5CB14F16}
HARRIS 11098862 | {0E899392-4139-4EF4-8C02-780C18A47141}
SISQUOC 1104M58 | {4D6D6BF4-E19B-4629-9318-504AFE626164}
ECHO SUMMIT 1101507864 | {501D001C-604C-4CB0-BC61-4A03C3824F33}
TIDEWATER 210618972 | {2DE5693C-879D-4FCD-88B6-818902BD649A}
WESTLEY 110111730 | {5D9D0169-9A60-4F2E-81FE-3563A32A79B5}
ALTO 1124428 | {84CE664B-0611-4200-83BA-04B0E42A1B56}
SAN ARDO 1101CB | {D178EAD0-51DA-46C3-AC83-7A5FC311BC88}
HIGGINS 1104498932 | {D5E00AD4-7C48-4E87-BBB1-92F5DE277EEA}
MC ARTHUR 110138998 | {FAF0B739-3196-4C1D-A8BD-B6B12F707FEC}
OCEANO 1106V28 | {5A21115A-46BA-4632-AD7D-E9A81D89A695}
LAKEWOOD 2224CB | {5BA403AB-BCA6-4612-86C3-4865011547A8}
BERESFORD 0403435168 | {9E0ECC0E-D080-43C9-A87B-75BDCB2E0E91}
MIDDLETOWN 1102632616 | {AB543CBF-7DF0-478A-B296-EEDA3DC9B71E}
CHOLAME 1101X12 | {B37DAD9A-6324-4833-89D5-DCF19FFFD67A}
PALMER 1101CUSTREC | {EC1B6C10-3B8B-426D-86D3-39EE85F08618}
LAKEWOOD 2223W532R | {DAC222F6-911D-41F8-A045-FDB37DA63ECF}
SAN BERNARD 1101438074 | {BF5DD9D5-AD1F-4BC7-AC27-542684EB7C5A}
WALNUT CREEK 0404CB | {D56BF5EB-906E-4B51-BA5A-E962F016AADF}
BRUNSWICK 1103CB | {D972EC75-3864-4C3E-9FB0-5B538887AB46}
MOUNTAIN QUARRIES 21011180 | {32A5B84F-F8E0-4F0E-B3CD-BEC3B55A0617}
COLUMBIA HILL 110135424 | {474A8BDA-95BF-4717-B362-885E409D4F7A}
HOPLAND 11011100 | {49DD2761-248F-4D1E-809D-C19E1A64F359}
WILLITS 1103409216 | {9EA45B12-9DAE-41DD-A093-6F45C691C648}
CORRAL 110213498 | {A0B72D64-342D-4CD8-B398-D7C01DA365B3}
OILFIELDS 1103233424 | {D1CD6BAF-3C2D-48BC-989C-18A0A5CF3122}
COPPERMINE 1104R3170 | {4532B921-F6B7-42D7-8837-06939F7F1ED4}
CAMP EVERS 21055146 | {592F5AE1-0E6F-42C9-A6FF-0D40652C51A7}
LOS GATOS 1106697500 | {5B274F91-3DCC-4D8C-9FA0-4D35A285F7F0}
BIG RIVER 11012183 | {A36BE560-E1CB-4559-8E7E-01132EBA1D0A}
CAMP EVERS 210511004 | {91583C6E-961C-4B38-9535-F88F266F69EA}
LINCOLN 1101860022 | {BC430285-5DBF-4545-8AE8-96AF6071F68F}
REEDLEY 11127919F | {0ED60982-9EAF-4A20-AAB0-618C5740E1E9}
COARSEGOLD 2104359656 | {0C333A4E-D2B9-4524-B156-EC4BB8B8BEEC}
COTATI 1103252 | {5C4483AA-BF97-4BA1-AC7C-28760FD1BF47}
BERKELEY F 1105BR100 | {34B1FBA6-E642-41FD-8BD2-ADAC657BB906}
SAN RAMON 2107818336 | {92E22518-527B-4324-B90B-D5A4496A4612}
CLOVERDALE 1102172096 | {40B1E31D-7977-4CD1-A0DB-03E15686CC3E}
CABRILLO 1104Y08 | {A8C0DCB1-6987-421D-A6ED-00C50AACF3B4}
MIRABEL 1102CB | {C5E1652A-2EB6-4FD0-B328-E1AC1FDEB33B}
GUALALA 111135562 | {FD400AC6-30E3-4FB9-965E-48825707A861}
EL CERRITO G 1105BR194 | {08B99221-B59C-4635-A155-E118204BFD80}
LOS OSITOS 2103258688 | {095C4297-BB9B-47AE-9B30-7513251297A3}
SUNOL 1101MR650 | {531B9791-D7B4-4DAF-8D61-5A68DAA7C3F6}
FREMONT 1104645342 | {5FF4B67A-802C-4B9E-AA95-209BF5DD22D4}
PAUL SWEET 2105CB | {8D1DF0FB-6A31-4B98-9D74-0EE015EF8A6D}
PERRY 1101986322 | {C7DAE941-6DB3-4215-863D-56303A6DD35B}
ALTO 1120500 | {E6E93162-4459-4248-A579-2775F57735F8}
PIERCY 2111CB | {F69D714C-099F-426C-95FD-DACECE33C433}
BRENTWOOD 210598606 | {659CB7C9-DF34-4927-8487-32FE0AC742E7}
CAMP EVERS 21055232 | {592F5AE1-0E6F-42C9-A6FF-0D40652C51A7}
ROSSMOOR 1108543356 | {812F7F32-99CA-4B11-A2F5-E536332A91A6}
BIG BASIN 11022253 | {7DF78B7A-3D58-4011-B365-74BA17A842F7}
WILLOW CREEK 110191926 | {ABEF63BB-FD93-485F-8439-718A3A0F3B42}
PEABODY 2113873304 | {463CEDCD-A864-4BE7-A495-4562C479EEC4}
PARADISE 11042206 | {1341CA63-432E-4CD8-BB46-467A27C9C55D}
PLACERVILLE 1111610322 | {E8C6131A-05FF-4431-8BF6-8D1D5F5027F9}
WOODWARD 210878448 | {54379B90-C0BC-4B7C-8E22-0C10DD6F3A72}
SANTA YNEZ 1104Y30 | {1B8DB8B3-1D13-4E12-A58F-43F8C34F8820}
WILLOW PASS 2108CB | {1FEB7E65-DDE1-46AE-83AD-B5F30417F926}
RINCON 1102640 | {2FAB6430-43D4-439B-B7B8-4BB8DFD0CD27}
PUEBLO 1104640 | {425E28B1-6940-4649-A8D4-A58D56D174C1}
RINCON 1101576 | {F4C78492-32F9-47FB-AA37-4818CAE3C60E}
MORAGA 1102221914 | {1B687BB2-4458-48CF-B4BC-EAC2F2DF6A24}
LAS GALLINAS A 1104304 | {7112559E-7269-4FF3-BE61-B0339A94698E}
APPLE HILL 1104CB | {C95685B7-B649-4BB7-AFD8-6C20EE89F893}
KING CITY 1106500 | {1EC73396-F2A3-41B2-A894-659988450DE2}
CAYETANO 2111MR329 | {439ED568-0BDE-4626-B59A-7C48F17E3B78}
CLEAR LAKE 1101881362 | {55694D06-24E9-4D6D-8BD5-E5D434DB5805}
AUBURN 11028611 | {F47804CC-754A-4FCA-B217-8CAF682A164E}
CAMP EVERS 2106478670 | {D340DCCD-95D6-4317-9003-DD8DEDE9B1C0}
GEYSERVILLE 1101CB | {377EDE62-95BF-4247-B5CE-2FDAD489198A}
SONOMA 1105539450 | {83741DC0-AB8A-4A6A-AF87-708226B87F58}
FORT BRAGG A 110231304 | {BF12DE8B-4E1C-4761-B900-F5DD3C822515}
LAURELES 1111432 | {C78621C3-DA62-4FAA-872F-5C934F1DDE39}
ELK CREEK 1101CB | {C805E056-6565-4701-B47E-65A72A694487}
MILPITAS 1109CB | {D897A506-3C26-4AA6-AE93-1BA5129BA14D}
VIEJO 22022606 | {DA30E872-22F6-4600-80CD-C659254182C9}
BURNEY 110257046 | {2AA24801-8300-4851-B080-261023387F10}
BELL 1110CB | {451291E3-291B-4A82-B036-A633A631A6D2}
BELMONT 11109090 | {650AE2A0-8481-4167-A199-68E796B3390A}
SILVERADO 2105900104 | {6E66B86C-1327-427E-BBA9-5D2C3C6622A5}
POINT MORETTI 110135874 | {7580C145-BC76-4DF0-BE7D-C5FC1E8761E1}
FORESTHILL 110175340 | {9A3F5548-F595-4F3F-89FC-9574388096DE}
VIEJO 22029488 | {8E85DA31-E8CD-4D80-BE55-60AFA6937F74}
WOODSIDE 11018974 | {95843233-31DE-4B8A-A7FD-7E8E48EA1CD1}
BUTTE 1105612016 | {B2540AD5-03FB-488F-9579-CE16933A52B5}
SAN MIGUEL 1104954082 | {D0A5F575-D022-443D-85F2-E2AC3A537B53}
DESCHUTES 11049718 | {F164BF8B-3484-47A3-8EEF-5FFD77D4911A}
SHINGLE SPRINGS 21092679 | {B7DD70D5-00B7-466E-B95D-1B12C82EB1E1}
SAN LUIS OBISPO 1103486690 | {EB029C6B-1104-4127-A12F-6B1C6DB20B5A}
ALTO 1124CB | {2C543D7C-5902-4DC9-BE9B-719A66315791}
WEST POINT 110293116 | {2DE74D61-95A1-4D32-9CCA-28AB5E692CE7}
PLACER 1102CB | {498BEDF6-2946-45C8-8A10-174F646330D4}
WEST POINT 110272036 | {4D3D5180-6A6C-4C43-B692-915E3881962C}
EAST QUINCY 1101CB | {7BDDAA75-E6EC-4597-A704-7B9866E3D480}
GARBERVILLE 110237054 | {BF5AD074-5FDE-42FF-9EE4-EC1E7EF14392}
OAKHURST 1102538042 | {CD5EC07C-7621-403E-BE45-2B4B105F5053}
SHINGLE SPRINGS 211051462 | {064C2459-8C22-4F74-A2C9-18905DBD3086}
TAR FLAT 0401CB | {EA023699-472E-4198-908E-801A3A6750F5}
JARVIS 1110CB | {F27BF583-4544-41F4-91D5-3B4970C09DAF}
WILLOW PASS 1101152874 | {11BE008D-2713-4231-8C63-A8180087E277}
LAS POSITAS 2107MR199 | {D8477CE0-E0EF-439F-B1B0-3F9E81D16F6C}
MARICOPA 11023082 | {F0D3E110-E06F-4F39-B085-758DD01FFE6B}
HIGHLANDS 1101CB | {F7C77AB2-FB1A-424C-8DCB-D1ED89130316}
HIGHLANDS 110448262 | {05A2F271-E60C-4560-A544-2497E351C8FC}
HIGGINS 110350072 | {740DE1B6-71C4-4F89-BFF6-C379E023E99F}
OAKHURST 110110090 | {8E59087F-9FB7-4FCF-A3C3-5164FC72FB46}
HONCUT 11015581 | {4580F407-B405-4F86-9F13-8318C1F1927B}
BRENTWOOD 2105502672 | {B557525E-C955-4555-A43D-602C62B6D5B3}
BELMONT 1110330790 | {E5D2E9A8-3F25-4DA6-AD92-5C753B714148}
WILLITS 1103696 | {EC79F2BF-D405-4EF8-A570-37C7BDE7D1BE}
IGNACIO 1103CB | {09D14343-CC3E-46D9-99DC-4193E90EB264}
CURTIS 170565908 | {2ED0FFD8-DF5F-45A0-8687-5F34F37A5A97}
VIEJO 2204746866 | {DB34AA1E-C0F6-41DF-BFC5-43E5CD8E6B2B}
RALSTON 1101420730 | {C5ED9BB6-82EE-4A74-A509-3A42E5E8C396}
FAIRVIEW 2207P302 | {31523F0A-9FD2-41D0-8A36-117080631D88}
VALLEY HOME 170339660 | {A2F287EF-C287-4618-B3E6-557974E96CE4}
BELL 11082202 | {C705CC3B-4CE7-4574-9451-1595DBBA258B}
LAS PULGAS 0401104588 | {1A6E13FA-4170-41DB-90FF-CC50D93E5B35}
STILLWATER 110148950 | {2473E4CF-72E3-4517-88B6-37E3090DCE92}
BRUNSWICK 1103956424 | {3FB24E68-4827-4A80-90A1-2EAF2EBC79EB}
COVELO 11014678 | {95061D3B-1DD0-4E52-A655-6CA082C84028}
MERCED FALLS 110285002 | {9E750160-198E-4DE4-9B67-A39CCFF98BD9}
MC ARTHUR 110137344 | {385A8486-C3EA-4FD6-BFA5-2F73ECF426BB}
SUMMIT 1101742 | {3E9B0952-44E2-4D0F-8A1E-44C0D690C0BA}
DUNLAP 11037220 | {5755A55C-8127-474D-99F5-38E2401D21A6}
GEYSERVILLE 1101166 | {BFE1D441-2168-4D90-8012-C988D5F78BF2}
FORT BRAGG A 11014698 | {C40FEC6C-4399-4FDE-8ABD-E729D917D61E}
HALF MOON BAY 1103341542 | {D82172A1-B65E-4492-A8B4-CC58BA0F7717}
WYANDOTTE 1105601234 | {2426BD3B-3A69-4A04-A051-7581B14322B3}
PUEBLO 11042802 | {EB87F1B0-DF58-4672-B521-8B7DD265BE37}
NARROWS 210248484 | {F3B439DF-7706-4C2F-8999-BCA70EF18266}
HATTON 110240465 | {DF6AF33C-27E3-43A2-A515-B3B27F7B49FE}
SAN LUIS OBISPO 1105CB | {81973749-CAB3-49C6-B105-0C3D389524EF}
PIERCY 2110866388 | {901C47B4-25C2-4C9B-9657-50A16616D760}
GARBERVILLE 1102802246 | {DAE65BBD-586B-4687-A386-299C8E68232F}
TEMPLETON 2113175566 | {570CCEFD-E2D9-4041-AF4C-E6667A3EAF28}
SONOMA 1103470636 | {989A9D45-A06C-4EF7-99F0-5A8D5A73FF7C}
LUCERNE 1103245134 | {C983D5DD-ECD3-42F8-923D-50B966424F38}
MERCED FALLS 110238748 | {E473F3E7-4790-4E95-BFB6-2DFAB51C8E70}
CLOVERDALE 1101CB | {1FD9348C-4D4E-4981-80D7-DF41347DC4BB}
FRENCH GULCH 1101CB | {20DFFDEF-5135-4324-A022-CDDC3E81B3A6}
HAMILTON BRANCH 110137436 | {32D1F0F9-DFF9-4513-A71D-93DBB94A9BB3}
LOW GAP 1101CB | {5346AC49-CDE1-40C3-A681-DA76F08A9FA4}
SAN ARDO 11017054 | {D178EAD0-51DA-46C3-AC83-7A5FC311BC88}
ROSSMOOR 1109892648 | {07D08030-E53C-4555-923F-76DCDA7152BE}
SUNOL 1101MR298 | {90446565-9C4E-4EC0-BE56-9B48C2C5DA8B}
IGNACIO 11041274 | {4117016E-C4E1-43D1-8702-FC75C137797F}
SANTA YNEZ 1101673618 | {AB14F8FE-EE00-4DB6-A9D1-E7044AA1EEF8}
SAN RAMON 2106MR285 | {BEA60D98-CFF5-4E7B-A41B-182A021D5BAE}
COVELO 1101CB | {F774F37B-0BFB-4E5C-8B3B-83726F441387}
FRUITLAND 11422006 | {0E6F84FB-9664-4CC2-ABC9-E723037587E4}
NORTH TOWER 2101CB | {17DE99B2-61AF-4462-979F-1C1B612D667F}
BURNEY 110145984 | {1877F2B7-68C6-4031-8C15-9D4F18F07556}
DEVILS DEN 1102460850 | {1ABBA2B1-53B5-449A-A275-B6A0999D81FE}
AUBERRY 1101R2839 | {1D410A42-CC20-42CD-9AF0-41D38F1027D3}
COARSEGOLD 210210050 | {246AEE64-BD98-43AF-876E-DF5040419CD3}
PEABODY 210813402 | {BC2B156B-5F07-4313-BE60-34EF88AFE911}
RINCON 1102644 | {A2A06826-B5AC-4037-94EC-F135DC826294}
KETTLEMAN HILLS 210464373 | {B01E9D88-F481-4C05-8823-888D25A886D7}
HALF MOON BAY 11028848 | {B38DB0B8-9B03-4771-A545-1316F725B1B3}
CARBONA 1101975330 | {33A7055F-6DBB-40BD-9D42-63496DE4F455}
ROB ROY 2104974520 | {A306B6A6-F4A4-47EC-B2AB-9B74651A417E}
ESQUON 1101717130 | {25AD8CDA-2DAA-40D1-AF6C-EC42757AE02A}
TIVY VALLEY 1107CB | {B007F88B-9403-4642-A8D2-16BDDDACB785}
SILVERADO 210578326 | {6A947491-FB60-4043-BF5D-F50FFBCF57D9}
DOLAN ROAD 1101590402 | {B7B666E0-E3B4-4668-B112-954F6AFA2706}
SAN RAFAEL 110991742 | {BFF521B9-A860-4F51-B554-94546E79EB8D}
PETALUMA C 1108618 | {F9D85BA5-F081-4C89-8A4E-6F66CE119492}
WYANDOTTE 1106CB | {29C2B584-F455-4FA3-B4A4-3F4E989317C3}
WOODSIDE 11049116 | {37A21F97-AEE6-4520-B851-056330FD3EDF}
HIGGINS 1107746082 | {AD1702BF-568D-4020-87DE-29F495495BCD}
WOODSIDE 110239574 | {BF6AF21E-B6B4-453B-837A-E823913B38FF}
DIAMOND SPRINGS 1106930190 | {DCB9D4A3-4396-4AF7-B5A4-4405D20B6E8E}
WILLOW CREEK 110237374 | {E5474BC9-1FBC-47D7-924C-371BAFB1C79B}
FROGTOWN 1702737236 | {F66F5E9F-01CE-4986-95ED-652F7B3AA4E8}
COTATI 1102370 | {E06C85FF-5B48-4064-AE0D-D34C585D0676}
SOBRANTE 1102L510R | {2F07459D-47C1-4462-B0ED-65839CB76ED4}
SAN ARDO 1102CB | {A30EDBA7-9AAC-4E4B-A35C-8F3268903239}
STONE CORRAL 111075288 | {2BE56CEB-D130-4F64-98EE-3834ECE93155}
CASTRO VALLEY 1102MR248 | {30E66223-084D-4B40-9C14-1E91EC3B3A23}
WYANDOTTE 110932586 | {81BB6A5C-2DB9-49AA-A7A4-75F68838201B}
CHALLENGE 11021064 | {B35DE979-0877-4DCD-A99D-B482E8F19A15}
BRUNSWICK 110663124 | {C847E025-6E0A-40C2-B74F-54E4CBC5EB88}
HALF MOON BAY 11036018 | {2DDD3645-3AB5-4B35-8936-1A369FDDE7B2}
BRENTWOOD 2105219013 | {659CB7C9-DF34-4927-8487-32FE0AC742E7}
BRENTWOOD 210596324 | {9A8233B7-234B-46CF-8EEF-6B74776F9D38}
EDENVALE 2105469810 | {8B87811F-B323-4484-BBE4-38B55670D94B}
ATASCADERO 1101A50 | {C74334F6-C157-4384-BFB7-ED7E4C2B59D6}
MADISON 210112321 | {0CB657DB-6DA6-4A9D-A1FF-01F4FF1F9C5B}
REEDLEY 11127240 | {0ED60982-9EAF-4A20-AAB0-618C5740E1E9}
CABRILLO 1104838078 | {27DCEC24-FA17-48AC-A20B-BD915C784084}
ROB ROY 21045304 | {B079AC67-F69E-4839-9DB7-69A2C23DFB56}
WOODWARD 2108R867 | {8314795F-0D04-45BD-AE69-B7277494B0E9}
STANISLAUS 17026028 | {0ADE0ABE-2B1D-4CB6-BB2E-0E310321E755}
SAN RAMON 2119CB | {0CC5B62D-8E39-47F2-A113-AB2F434531F0}
HOPLAND 1101960 | {1163B195-EACD-43BD-86EC-77A4B82C1934}
CLAYTON 221442582 | {10733B2C-A5C3-4A9E-8D35-517FAE09EA04}
FLINT 1101CB | {68DF9E12-6736-4943-BDEF-9FA6962872B3}
MORGAN HILL 2111XR292 | {7A50E1CD-B005-4744-BD76-86E8006C9FCE}
OCEANO 1103839302 | {7E0AB3E6-06DD-4E76-83F1-F36EBF375722}
BRUNSWICK 11062790 | {C10441DE-4140-4067-AC0A-82D10F063DBA}
TEMPLETON 2112R26 | {3E696401-4261-4D08-869B-B3D4019E7D36}
CORRAL 110214026 | {9D2DD8C8-FD4B-4B60-ACA0-0CCE69EA2F96}
BRUNSWICK 111061602 | {52CBF115-6640-4F98-9743-613A61123F02}
ANTLER 11011384 | {C5E3EE8D-D562-41BA-8596-EEF5987F2F11}
CALAVERAS CEMENT 11012646 | {3FB47D58-B406-4320-8238-19B8B73E9349}
ZACA 1102Y54 | {49C145C8-C8F5-459A-817E-3F37A5597C7A}
SAN RAFAEL 1106910 | {5D059BF5-F769-4312-8893-6A2C828C685C}
POTTER VALLEY P H 110495878 | {8D4490B9-6B4D-4F2D-8A60-88D879FECDA8}
SYCAMORE CREEK 1111CB | {D9A2A699-962C-4607-98AB-EA01299FAAB8}
PUEBLO 210378504 | {EDE87926-F33E-4FF5-A8C5-E53D4266C7FF}
CALISTOGA 1101890 | {37250BD0-D9D0-484F-9AA1-8C286761C77F}
VINA 11011570 | {427F674F-2998-4807-8909-FFE2EF8784B5}
PRUNEDALE 11103080 | {CE89D4FD-128E-4AE3-8F53-291BB3498CD8}
OAKLAND J 11181846 | {218F069D-01B3-4618-A6DA-CD10F8EDDF5D}
PURISIMA 1101Y40 | {0E276FF7-E726-49F1-899E-4DA4E59DCF2F}
HIGGINS 1104CB | {46E9257A-F9DC-47D6-A72D-7B5FD7E2E022}
TULARE LAKE 110854074 | {56DB22B5-CE56-48B6-8FE4-9109734E0A42}
HAMILTON BRANCH 1101161872 | {7FEFC5CA-2496-46DE-BE2F-DEB25BC01D17}
CLAY 110113450 | {27131A9E-D142-4A6D-93D0-301DB39F0FC8}
AUBERRY 1102R902 | {5ED2B13E-98E4-45F9-A6A0-57DA496030DD}
SARATOGA 1106340986 | {76A04BD1-4382-473D-8157-2FE1C012AABD}
CLEAR LAKE 1101699062 | {91E6CF65-65E6-49D9-99AE-7F739C671773}
OAKLAND J 1105CR150 | {B40886D4-E154-4D0B-BB2B-061EFDC2739B}
FOOTHILL 2101CB | {FE508189-9BB7-482A-98AE-78BDA64DB21B}
SILVERADO 2102636 | {163BDA39-807E-4AA9-AD15-91460635EEBA}
GIRVAN 1101323094 | {70CD880F-1DDD-4F51-9E9A-370D1CA1A5D7}
CRESTA 1101546650 | {A1AFFBEB-1EC0-4B98-95D8-379CD77E7C39}
ROB ROY 2104588930 | {A306B6A6-F4A4-47EC-B2AB-9B74651A417E}
CHOLAME 2102CB | {042A33DE-71B1-40FB-B0CF-6D56CCA576B0}
SAUSALITO 1102410 | {535449DD-A4B3-4AA9-AB71-3DA62C691B7C}
WOODWARD 2108703608 | {8314795F-0D04-45BD-AE69-B7277494B0E9}
SAN LUIS OBISPO 1102V96 | {9A70A0FE-6E60-48F9-B727-E7F0BBC33E9E}
PLACER 1103CB | {E0134993-C6C7-47B2-B903-8846B3C865A5}
VALLEY VIEW 1106496670 | {772F24AF-7DA1-47C8-B6AE-4C4810E9D260}
COLUMBIA HILL 1101CB | {472D2B95-5CE0-4AF5-93B6-7762ECA68067}
MADISON 210137082 | {8E6B668B-C3B5-476E-8081-82E065E91883}
HARRIS 1109355914 | {C9FD0E2E-E3CC-4613-86C7-481937B54700}
HALF MOON BAY 110260703 | {EC65686F-B15A-4CBF-8005-BF1274876E69}
LINCOLN 11042308 | {FB48CF9D-FE80-482F-938D-2D781F244FF8}
HERDLYN 1102609338 | {20393823-B77E-489E-817E-F72A23CAEA43}
SHINGLE SPRINGS 210819762 | {37338E68-AEEA-49C6-B1EE-76E1EAD86B81}
VIEJO 22012064 | {410C255F-3E61-44D1-A47D-CA8172B6BCA6}
WISE 1102465074 | {551FC8A6-8E47-4C6B-BA77-51B1DF1DDFC3}
COTATI 1103216 | {9A3F5ECF-0D58-446E-BB8C-0FCF9D3017A7}
HOLLISTER 21054040 | {9EFCEC97-B945-4717-BB02-DD9746AC6A53}
DUNBAR 1103416 | {E1077E4E-022A-4658-906D-61D41C4EF125}
HILLSDALE 040277056 | {6CAF4EA6-4ABD-4B11-B8DA-EB2F88BE9114}
MARIPOSA 21014410 | {6FC28AC3-D7E2-4D2C-9C34-2FD4A55CB839}
HALF MOON BAY 1103825502 | {753853E4-C224-414D-99C3-DFD71085C7CD}
PLACERVILLE 1112239390 | {69C7055C-8321-466E-890B-DA1A435F5398}
WILLOW CREEK 1103CB | {A739E4CD-6027-447C-8193-CB877EF24141}
EEL RIVER 1102530 | {B0F5DD9B-BA5B-4914-9A80-5D9AD769A95A}
JESSUP 1102158468 | {B661BE4F-F0A3-491F-90E4-A5B76D06F645}
PACIFICA 1104CB | {EC3F19B1-655E-438D-8AA0-F3D32FED5878}
MORRO BAY 110247584 | {0C127574-7596-4A86-A384-D65556DA9180}
FITCH MOUNTAIN 1111424 | {12685307-B1B3-4B99-A51F-5759145ED4DA}
MIRABEL 1101228 | {42913E65-3605-4DBB-8857-B0B0965C9EAC}
ROSSMOOR 110982962 | {72BC10DA-E2B4-4F9E-B1C6-B2A54D23C7DA}
UKIAH 1114911132 | {4F4D60A8-18DF-4AD7-9533-2FDA5C5224B4}
MENLO 11038512 | {8F9D0578-4CB4-4781-89AC-7B1C36D45FF0}
TASSAJARA 2103883664 | {A01F7105-694F-4AF2-BE95-1454C7C5E566}
SNEATH LANE 11015311 | {5A5EFB63-6847-4F33-8DBE-F9C3D6DCF54A}
TASSAJARA 2108D520R | {D91BF138-6798-4927-88BC-C1A382D4C37D}
PARADISE 11042034 | {F797DCB1-C578-4B28-B5FA-B1147A5E9141}
MONTICELLO 110152910 | {151C0216-83E8-4EAF-9D71-0D50917A8A0E}
HORSESHOE 11012714 | {3E108A7D-3BD7-484D-A219-8780A55EB7A1}
HARTLEY 110167994 | {7E2F1938-FEBF-4ABD-86B8-56A7EC0C222F}
SANTA TERESA 2101CB | {7514A62B-2474-4201-A784-F02F06FF897E}
MONROE 210781174 | {3D15A0FB-7F79-449E-9100-AEDACD615B82}
CLARKSVILLE 210951744 | {D119674C-FF38-4F45-A342-82E8B18FF02E}
PUEBLO 21033020 | {5A0D0FE3-BCFE-4A12-87C6-884B98130563}
LOS GATOS 1106LB48 | {ED4FFAA8-32ED-4B25-8B3D-9D1525DB179F}
GEYSERVILLE 1102868292 | {B7169D14-D576-4EBC-83AD-DD429DE5E777}
TULUCAY 1101684 | {5DBAA811-6F22-4836-935F-F9F50494B3FC}
SALT SPRINGS 21024796 | {62775B3C-DB61-48AD-B027-A91400EE7920}
ATASCADERO 1103CB | {80C03548-09A3-4516-9CD7-A85242729AF9}
CASTRO VALLEY 1108MR233 | {D8E4C9CA-7EEB-49BA-880B-C873380BC8EB}
BRUNSWICK 11052204 | {EDC3C6AA-B200-49D0-AFDA-73B9844EB8E4}
DEL MONTE 21049096 | {53A81FCC-6CE7-4EE5-B8F1-AB89BF2F3989}
PUEBLO 2102850102 | {5456D4F0-1D4A-4239-AAEE-AF57D0A5D9CB}
ROB ROY 210512586 | {ABFDD865-4FD2-4A37-B95C-CF3A9E9EFA30}
DOLAN ROAD 11013012 | {E78B7822-B984-42F9-85C5-3ACE6CA5BD79}
LAKEWOOD 222454676 | {21362692-484C-4985-A610-FAAF4CA90541}
PLACERVILLE 1110953474 | {8F8EF18B-7E0A-4A9F-9597-8CCBE4E9FBDC}
SHINGLE SPRINGS 2108CB | {31F15014-5008-45D5-9481-1A850055776D}
LOS OSITOS 2102148504 | {36658DA5-CDD3-486F-B061-605207C26350}
CHOLAME 2102X20 | {3EDA206D-0CFD-4058-8D33-8D070063612D}
EEL RIVER 1103CB | {A1A1D221-0393-4995-8057-AA9153B871D9}
LAMONT 11029785 | {3E9A4648-30CB-4190-9869-1F4B7575C98E}
NAPA 1102942 | {CBD8A59E-6463-47E4-AF46-087923E514DE}
HARTLEY 11011306 | {CE237446-8B77-4B6F-A151-0796DF2727A1}
DIAMOND SPRINGS 1107217974 | {01A8C6BD-323D-44E5-A686-1246351A46F2}
ARCATA 11225384 | {F8ACD64A-30F6-4E37-A172-24BA9176BE45}
CORRAL 1103CB | {03D991AF-6109-4C4F-9E0E-284738E05B02}
LAS GALLINAS A 1106CB | {0EC84767-A265-4D35-8CD0-07F4DBFC6169}
WATERSHED 0402CB | {1B6353F3-7152-4A32-A40C-9970C5A62BA9}
MOLINO 110266006 | {4AE7AB5F-C633-47AF-9F7F-61FE17B35998}
FITCH MOUNTAIN 1111592 | {AA2E97C7-3759-4D9E-BC19-D9ED237F5DA1}
BELLEVUE 210342412 | {AB1749CC-E955-4627-948C-09860E609DAF}
OAKHURST 1102963056 | {D0015396-1CC9-4783-A5A2-48EC4AF3208B}
BANGOR 11011804 | {F430F9BA-4822-49EF-972E-D271E55910BA}
SALMON CREEK 1101196 | {05737260-3AA4-4F7E-BF36-A5BD94AF80DD}
SUMMIT 1102CB | {5BBF8789-23F7-470F-B0A3-CCE750BDABFE}
CEDAR CREEK 11011664 | {81F58F11-9F6E-4CC2-A527-0CBBB670DE91}
CHALLENGE 11025462 | {9343C558-C255-4E56-87AF-7724333414B9}
GARBERVILLE 1101CB | {E1AC8377-8E8C-4414-AED8-68291E68F4CE}
GEYSERVILLE 110289714 | {450BD680-08E6-46D0-AD80-CB37688E8C0C}
BANGOR 11011958 | {4EADDDA4-9026-4CB9-B9C4-03D97B5E8FF0}
GARBERVILLE 110135706 | {BBD56973-ABAA-4951-A1EE-E863C47010B2}
WISE 1101CB | {919A8A04-B874-4A68-AF90-D4143250C76A}
VIEJO 2203947314 | {2745EA16-9172-4362-B554-6BC9B1A69619}
EL DORADO PH 2101887684 | {1AECFC8B-BC7B-4454-BB87-FD8F012E171A}
PARADISE 1105878870 | {4F7F1505-2A84-49CE-A88A-5D1C68BB7B5C}
OAKLAND K 1104CR208 | {61E67233-CD4F-4206-8138-63FBDA895D1D}
OTTER 1101CB | {BB161BB9-B628-4038-939A-BDBCD448B75E}
GREEN VALLEY 210112106 | {C8470ABD-D047-4E6E-A601-35B08D6D1BD2}
BRUNSWICK 110750008 | {779A3152-24AF-4508-86CF-CDD542CFE4FC}
JESSUP 1101CB | {A7720DBE-D298-421E-A3B2-FE12C335EE16}
PEORIA 17048040 | {B68E2FC5-9A54-49EB-9258-EB6EA1DB9D61}
GEYSERVILLE 1102522 | {C28A65D7-37D3-4F6C-9C48-AF74AD2858BE}
JARVIS 1108289662 | {D0FD43E9-668D-474E-A42F-940591FD44BD}
OLEMA 110149756 | {818B580F-3855-41D8-9229-869A2B79816E}
LOS GATOS 1107772050 | {2D8F3B80-1078-4F21-A2C2-0C45F69D55BE}
DIXON LANDING 2101XR580 | {78E11C69-9A86-4183-B3C4-869A091C2B3F}
OLEMA 11011318 | {48696EF7-D14F-4A4B-98EA-50D58AFE2188}
MOLINO 1104368158 | {4E9FB77B-2DAB-4C16-84CB-10ABD5B12CA4}
ELK 1101CB | {73B4F2ED-84BD-4C50-9DB1-F9DAD696FAA9}
HALF MOON BAY 110376762 | {07C4DB8D-20E6-4803-A265-29C92D756E21}
OAKLAND X 1104CB | {14DC5424-B005-4065-8948-2B6A676B0C25}
FULTON 1101CB | {30FC3806-038C-4AC3-A393-91BFE1889F67}
SANTA ROSA A 111199050 | {4D91C141-515F-4F14-8290-C8268E13D106}
MONTICELLO 11014360 | {5B3909F8-EEF1-46D6-9827-15D3DCA91BD0}
LAYTONVILLE 11022502 | {71012A72-9F3A-4416-A409-5A697A15AF1C}
COARSEGOLD 210410400 | {7CAE9E3D-9A6E-4166-92A3-E494C4AA002D}
EDENVALE 2105696340 | {3428AB16-83A3-41CA-A97D-9F45E561A9E9}
MOLINO 1102178 | {E011217D-F6B4-46C8-AC6E-B5F7ADEBD850}
TEMPLETON 2110307832 | {EAF87279-EF23-4A44-B5E2-CCA62D5C53AA}
OAKLAND K 1101CR174 | {BAD456A1-64C0-4C58-9244-4CB0B49EFF5E}
MONTICELLO 11011589 | {9EBC498A-4473-4FB2-A278-0770D844069B}
CAMP EVERS 2106737512 | {38594324-B008-4F93-A718-0D73EA72DED9}
VINEYARD 2107246084 | {5E4EB8F1-F20C-4A10-9616-09E586C03349}
VALLEY VIEW 1103CB | {6F4A4EA4-DB8C-41B8-B673-0FAE8635F67C}
CHOLAME 2102867686 | {97118B4A-2A8C-456A-94EA-FB99937C6D68}
GUALALA 1111402866 | {DDD68DD3-36B2-4580-BE12-D96815D31D50}
BIG BASIN 110212992 | {1695E978-9BD4-42EE-A017-6DD99E4F027F}
UKIAH 1111379946 | {405F1015-C662-4950-99EE-1E4A689283D9}
NEWBURG 11322074 | {61AD59B6-3DE5-4155-9391-74B53A84E200}
PASO ROBLES 1102R64 | {B7E49A70-A833-4F14-A4E0-7628D7D12C4C}
SANTA YNEZ 1101277014 | {C3C0680A-C277-44D4-BC9F-C389F4D7DF4D}
OAKHURST 1101636114 | {C6D08398-1977-4CDB-B9B0-E15E9BAE5667}
CALPELLA 1101753000 | {E12D2ABA-05E0-44D9-A574-E03478B74646}
DIAMOND SPRINGS 11071402 | {04F6A01A-981F-4306-9D80-21027E2CEC32}
SYCAMORE CREEK 1111153260 | {39E14DE7-CA2E-4F61-9B12-2EF706A95B5E}
LAURELES 1112562376 | {3DF232B2-C195-4351-91B0-CBF56F76D173}
SILVERADO 210478268 | {49BFB9F2-5C6B-4B7C-8CFC-569E7EA29701}
KONOCTI 110264664 | {B904F4CF-C6EC-4D85-9269-44343E279155}
MONTE RIO 111137520 | {C0868086-2AE3-4A05-90EB-BF1D6E5F34F7}
CLOVERDALE 1102570 | {32B34880-BC93-4771-BC39-2E887BB96BE8}
STANISLAUS 17021804 | {7A6C2092-3A26-4926-BE3F-3A04290F7325}
KESWICK 11011586 | {89760509-9943-408B-8BC5-66753273219C}
LINCOLN 1101210168 | {CF1461D3-D5B5-459F-A63E-DFDD8EE92A51}
FLORENCE 0401CR220 | {D87265E8-5674-4799-A45E-7F1EC7B446CA}
CHOLAME 2102X10 | {DC85B463-1C28-4036-85F0-A9C121ABE158}
CALISTOGA 110135588 | {027DEE93-00CD-47B3-9E09-CCA2A54DDEE2}
HALSEY 1102CB | {0961801B-845E-4B14-847B-854C50E3739F}
WOODACRE 1101CB | {0C1EAF38-D291-4410-BD5A-7EDE35C497EC}
WILLITS 110337506 | {0E5984A8-2AB8-4609-A4AD-A7903A25522F}
MENLO 11031721 | {8A15255F-3865-4264-A6D3-8F9EE2AA73EF}
BEAR VALLEY 21059480 | {83E15892-C159-48B2-98C7-95188F40B517}
SANTA NELLA 1101594884 | {D9B42920-8795-457D-8506-B9A1003BB3E6}
SWIFT 2102CB | {BE64DC1C-3443-4966-940E-5A564C032974}
GEYSERVILLE 110179788 | {CD516753-E346-488C-8A28-4021B3A7E490}
MORGAN HILL 2108XR328 | {D422348E-558F-4EA6-B8E7-CD115687A21D}
LAKEWOOD 2223289858 | {FC9703D5-A1AE-46C7-92F8-123F1090FAA0}
DUNLAP 11037040 | {079BD93C-880F-493A-A5F3-34E94A52D05E}
CALAVERAS CEMENT 110180930 | {31F34B0C-04AD-46C5-88A1-857D16F62C5A}
SAN RAFAEL 1109692576 | {324DF6E6-DDC1-4554-BC31-1F7629DC4812}
RINCON 1102CB | {5988784C-46D2-4999-AEE8-C136D520A366}
WISE 1102697216 | {64620CA8-4B52-4298-8F14-91A606AD81F8}
DIAMOND SPRINGS 1107203504 | {C468F999-9DD1-4480-AEEA-A7CA15687805}
EL CERRITO G 1113BR120 | {F1CD3584-0342-4B1C-AC95-933DCB32DB86}
WOODSIDE 11043583 | {4CEFDA18-FC78-4DED-AF3C-6DA953E1658C}
BRENTWOOD 2105389881 | {9C413BEB-102E-4BE4-83F6-909D0B4AB75B}
MC ARTHUR 1101648698 | {21F41FBB-70A7-4D16-B9FC-2C23C6369432}
OCEANO 1106Q02 | {2FEE1CE0-BC95-467C-8CDD-CAD4D3CD2579}
ELECTRA 1101105880 | {3B44BEAE-4498-4CF7-B761-D8F28E5D84CB}
SAN CARLOS 1104636064 | {9E2BE648-1876-419E-9EA6-9561CF55CBC8}
OAKLAND X 1104CR214 | {A4D00FB7-3066-4764-B528-AB78985E682B}
COTATI 110475972 | {B13BE392-390E-4E3B-A432-5336348FF9E8}
BRUNSWICK 110651484 | {D517BDE5-67A5-45A9-903B-DF9F687C44D8}
LAURELES 1112CB | {F70B7F2A-1768-433D-8A85-4CF42DC91D6A}
MIDDLETOWN 1102414 | {01278228-324E-4DE9-A0E4-67F4CFACFDAB}
CUYAMA 1103CB | {086ABE98-CA07-4B5E-94A2-D2E7EF6983E6}
OAKLAND K 1104CB | {3C8EEA5A-CE4E-4740-9897-693B2E67E957}
MORRO BAY 1102V80 | {C6CF638E-9C90-41DD-9ABD-A01972E6D396}
LAKEWOOD 110492910 | {6E990274-D878-48AF-B3D8-9102E49E31C0}
BIG BASIN 1101595388 | {E247FC6E-157B-4272-AEDD-8C777FFAAD92}
OREGON TRAIL 1102CB | {D8B4A6F8-9874-47E2-910D-F4C8426E6854}
PEABODY 210818192 | {BC2B156B-5F07-4313-BE60-34EF88AFE911}
OAKLAND X 1105CB | {44B8C422-CD6C-4697-80AE-EEAF985A6D84}
DIAMOND SPRINGS 11052102 | {51B4FBA6-E864-4F62-B988-2A8243E75100}
CANTUA 1102CB | {593FAF9F-F993-4666-8339-2025B1146F35}
WYANDOTTE 110213044 | {6DDE6DFF-A5B7-42A5-A5E6-915A880E38B9}
DIAMOND SPRINGS 110518935 | {51B4FBA6-E864-4F62-B988-2A8243E75100}
CORRAL 110175204 | {C6783DDC-8CCC-4EFE-8097-5CE8336375DE}
WYANDOTTE 1109702710 | {EEE67C1F-6C23-4D81-9B06-45B190348549}
WOODWARD 2108935396 | {54379B90-C0BC-4B7C-8E22-0C10DD6F3A72}
CAMP EVERS 210694770 | {1BABBDF2-DCB6-4552-BE33-67EDAC391159}
MIRABEL 110238514 | {76DCCACD-E9DC-40E0-8CEA-2EC1A63EA736}
OAKLAND X 1106950688 | {AF2EF2E2-3FD9-4033-9703-73840E59FAC3}
TEMPLETON 2108A38 | {FFDFCD62-3D83-4DB1-8291-20A4384347C8}
HICKS 2101984788 | {21823ADE-60D1-49AF-96C7-A6BCD78F0512}
PACIFICA 1103398620 | {572B383E-2937-4EFC-BA24-50423EE8A457}
BERKELEY F 1105BR106 | {34B1FBA6-E642-41FD-8BD2-ADAC657BB906}
MOLINO 1102509516 | {1740079B-33AB-4B93-9EE4-D9DB46F4F893}
PAUL SWEET 210612828 | {35A821AF-CADB-4929-9F1D-038A70D8EFD3}
SONOMA 11045661 | {9E74C19B-FD10-4380-8F7F-0DF0A358D1AB}
IGNACIO 11011300 | {64639A8A-2672-4BE4-8EBB-2985CB356A36}
FROGTOWN 170275252 | {7D119895-6544-4FC7-A1BD-CC0A5D84976F}
RED BLUFF 1103CB | {7FAC2369-AB0B-45B1-8121-0A58A05D1C75}
ATASCADERO 1103440856 | {CE1B4F1D-0818-4F54-96A6-5CB8D8BF7895}
COALINGA NO 1 11089850 | {D0D57548-BFE1-4E51-8167-796FFB6E7A8E}
CALISTOGA 1102184814 | {AEB996A6-B3E6-422B-A668-DF66D3A05824}
SONOMA 1105229588 | {13B9141B-C5BC-4FB2-B1B5-84BF6E8CCF1E}
ATASCADERO 1101A22 | {1A2AEC20-7798-471E-990E-3BD9D80801FA}
SAN MIGUEL 1106428314 | {44EE4AB8-A105-4D73-948F-79D5A2357B21}
FULTON 11024522 | {4783296A-689D-4C7A-9F23-C015688BF301}
DEL MAR 2109CB | {A3D1D6B2-C2DB-46A7-9A60-CC55ABB31E62}
RESEARCH 2102183888 | {0695BA0D-172B-47D5-B979-B42944990BF9}
WOODSIDE 11059160 | {B0B93653-ABAA-40D2-863C-C601369FC194}
MONROE 2107146 | {3D15A0FB-7F79-449E-9100-AEDACD615B82}
BAYWOOD 1101V102 | {6A94C75C-2B9D-417A-8946-7997EE49AE89}
BOLINAS 11011232 | {6FB5348B-5DA9-49B1-98A7-B3620A483016}
CLAY 110398680 | {710E8DB6-BDC1-4CFF-BF25-79C21CA3FC16}
BEAR VALLEY 2105916436 | {C5D51BCC-B370-48A3-8349-FB710857EC4B}
RALSTON 1101836528 | {D07EF46B-1212-40DA-B007-3854AE9B04F4}
COTATI 1102282 | {25F749B3-A74D-4E71-A304-4CB2AAD2E132}
PINE GROVE 1102CB | {29253623-89FE-435D-961C-4E4487404246}
FROGTOWN 170113412 | {32DE7714-2265-4DEA-9044-817FFC428BF4}
SALT SPRINGS 21011232 | {9EF30C64-8412-466B-8695-929E20570E0C}
BIG BASIN 1101654386 | {E247FC6E-157B-4272-AEDD-8C777FFAAD92}
EUREKA E 110498682 | {DD1791F2-46B7-4249-A231-CD7E88BA8BFB}
SALMON CREEK 1101654 | {FFF2586F-2F7B-403E-A22A-6FE170AFE85E}
APPLE HILL 110412842 | {04FA73EB-B797-476B-86A7-C1CFAD605BCA}
PUEBLO 1102CB | {1AE19971-F682-43DD-B35E-DF767DF7D39D}
SARATOGA 1103LC82 | {9466ABB8-FD29-43E6-AC42-34C6719BD0EC}
COARSEGOLD 210210610 | {8FCA88A2-5287-4980-B557-B7704EA7B310}
SANTA MARIA 1110M138 | {E772CBEC-2F5A-43A3-91C3-8EE495E372D1}
BELL 111050182 | {6B9F0345-026B-4979-BA83-3B077A617109}
CASTRO VALLEY 1105MR236 | {C255CD66-4CFB-4E6F-AE78-6A76CA6EB0AA}
LOS GATOS 1101206248 | {A1B517D1-7F5E-496E-A188-34F488988F32}
TEMPLETON 2110R94 | {C64A1C77-F715-47FB-B91C-102C85AEBD60}
SAN LUIS OBISPO 1104CB | {12F1A144-2063-4E28-8860-F6ADF2052849}
HORSESHOE 11061826 | {E78C9DEE-4564-4CED-86F6-578EC71D6FE0}
SHINGLE SPRINGS 1104556218 | {38C837DF-F86F-4C34-B834-12EBAE0AE6ED}
CAROLANDS 04038508 | {4FDA6CDB-0E5F-4B76-BABA-C5F84B9DCB82}
SAN LUIS OBISPO 1103CB | {80BB619F-1520-4563-BF62-E97585F4D6B9}
VINEYARD 2107CB | {E0DA3FA9-134E-46BA-BA63-A138252A7798}
HERDLYN 1102575178 | {6D42CB7A-C91F-4DBB-9706-F92EF8B0963E}
CLOVERDALE 1102383183 | {FC7CF79F-4C61-4A20-81A3-5285A1A20685}
VOLTA 1102641544 | {06F73A44-E6BF-4E7C-AE40-21A987895C90}
DIAMOND SPRINGS 1103467046 | {F21436B1-06B1-4781-A6B4-F2B85E06831B}
BANGOR 11011806 | {ABE5C26B-A76B-46B8-A04C-0EC15FF8F909}
BEAR VALLEY 21059570 | {C6F77565-3ECF-49F4-A49E-50D716B67BE9}
BUTTE 1105235788 | {E9B89DB3-0831-46EE-9118-671FF72DAA2A}
BROWNS VALLEY 110136622 | {EF947682-77F0-46FF-B597-C974CCFEC84A}
EEL RIVER 1102409694 | {FB6BD3A7-81A9-4DC9-861C-0BEFD220DE29}
COARSEGOLD 210210040 | {68513B5A-56EB-4D19-97D2-4A9509C9FEBC}
FAIRVIEW 2207752858 | {659FD2EB-053C-425F-AF25-D9C58353B44F}
HALSEY 1101CB | {FA7F836A-C8A0-42D3-8E43-389B5B7AEC7D}
HICKS 2103XR068 | {F9C1F2D6-7B0F-4CCE-9FBD-177508C9BBDA}
NOVATO 110455398 | {335D8DF9-D334-4C80-A8EC-F250AAC0E6C3}
ECHO SUMMIT 11018922 | {3CE51A5B-7612-4EAB-BF43-95EB9AC2B5AB}
WINDSOR 11025066 | {8BAFFC14-6408-458C-A293-E7A624D7DE6D}
EUREKA E 110429676 | {B8F6F54B-5EF0-44B9-9BD5-BD98BEED42D3}
FITCH MOUNTAIN 1111555644 | {AA2E97C7-3759-4D9E-BC19-D9ED237F5DA1}
GANSNER 110152664 | {248F09B8-1D5D-4034-96B7-C372BB4594AA}
SHADY GLEN 1101578248 | {0FE524F2-DA0B-43E6-AE33-7B106122C864}
MIDDLETOWN 1101CB | {302C19E7-740B-49C6-83EC-9E70AC44D5CB}
WINDSOR 1103701650 | {4CA5D300-8532-4AF9-BD85-CE58373188C7}
MAPLE CREEK 11016906 | {8625CA5E-81C0-4BA4-B083-5D0354E4556D}
IGNACIO 11041290 | {EEF03FEE-E315-4DF5-BC12-E5292370248B}
CURTIS 17048140 | {44BC81C9-8540-477A-9326-99FB3CD481E2}
SHINGLE SPRINGS 11038752 | {4A6A0D61-C41A-479C-A0D9-3D6225EB935A}
WOODCHUCK 2101R2640 | {918E67A3-B8AA-4550-95DB-73823B8E223E}
FROGTOWN 170232556 | {9BE6D037-BD8E-46AF-A32B-7F2BB00D9E6A}
LLAGAS 2104524360 | {F11F1581-106D-4267-B291-AD8060715445}
ANITA 11062418 | {BF1D640B-1AB6-49FB-AB3D-0A09BCB77224}
COALINGA NO 1 11089080 | {C2C023AD-0CC1-4E83-AF7F-98D1E04D84AD}
OAKLAND K 1104CR206 | {FDBE20C4-A243-4218-824C-85EFE8D9D967}
RESERVATION ROAD 1102189936 | {966AAD61-7205-4A6B-9491-7F1C72E1ED94}
FORT ROSS 11214614 | {36E821CE-0F96-4DE1-8152-1087521FEC6A}
AUBERRY 1101R2838 | {48B8D134-2217-4EE4-BD7C-3270CBBFB37D}
FRUITLAND 11413902 | {986A9626-2000-4CDA-907D-688340426BF2}
LOYOLA 110260128 | {A6F27353-D8D5-4597-90A2-CB1701C67449}
BELL 1108127062 | {EA7A922D-E9BD-484D-B6ED-929B9EBF7C80}
VINEYARD 2110946322 | {14A8794B-8A75-4FC8-9957-3059A6D6C76B}
OAKLAND K 1101CR172 | {2F486204-BB5C-45FC-9D31-305D5B069E7B}
DEL MAR 2110CB | {67D76908-7B70-4DAD-A31C-C1F7E75F3357}
HORSESHOE 110450142 | {72194304-B9B5-4008-9268-F14D384C2205}
PURISIMA 1101CB | {72519E2E-220A-434F-A310-3B8078E34E61}
REEDLEY 1104218022 | {CFE218EA-E766-4A80-8978-21707A20B8F1}
HOLLISTER 2102CB | {D8069B78-C4A1-4306-A859-EF54203AE5F4}
SWIFT 2110XR254 | {F246BE39-0175-4986-BDB0-A6E32868FF88}
TEJON 11023751 | {F982DA9B-E6B3-4123-BDDF-635E01BF398E}
COTATI 1104374 | {2F39A049-2BA5-4A00-94B6-4F8A51F9E4CE}
WYANDOTTE 11031508 | {1F5D8008-7EA4-4278-A040-64AB0E7AD925}
REDBUD 1102922 | {4E034B59-FA2C-499F-8D52-06EA3D1E77EE}
POINT MORETTI 110112122 | {9CD1A9B9-F6CA-4FBA-A861-B1CC3280E49B}
MIWUK 1701767890 | {BB39A9FB-82F3-4CEE-812A-8BCB11B79244}
MONTE RIO 1111140 | {C6591A95-C17A-4B6F-BCDF-C2C9AE4418F5}
LINCOLN 2109924404 | {D78EA46A-E23B-4345-8961-C542C9C645D9}
BUTTE 1105518014 | {EA7C07F2-4273-40BB-B6F5-36B0C70D1D31}
CALISTOGA 1102279135 | {0AB6C849-088B-4982-95AE-9F5B40F2ED13}
OLETA 110163500 | {0DE3898A-1208-4EC8-ABE1-FA05111C0DC6}
PALO SECO 0401CB | {0E3E2146-50FB-4065-BA86-A817B98C8BBE}
LAYTONVILLE 1101448108 | {301116D8-18DF-4DD2-820F-B08551F93AB9}
BIG BASIN 1101393582 | {498E3237-3BEA-4CD5-BBB3-313CDEBA801E}
SALT SPRINGS 210237300 | {77733CA8-C469-4656-B2CC-06892BE8F14F}
DIAMOND SPRINGS 110656026 | {95AAF818-10A5-460C-909E-8A1D81C4AEC8}
PHILO 11022600 | {AD82FA7A-9F47-4C04-A20C-1CCF257103DF}
PETALUMA C 1109820458 | {E3B7A6D0-5E5C-4112-ADBA-8CB389502FA6}
FREMONT 1109MR735 | {E8F7F7CC-6E45-4B77-9E47-6A6BC522B971}
LAKEVILLE 110287432 | {F16EF0FE-506D-4026-9FF6-A9B4826F67BC}
MARICOPA 110265196 | {341A5947-0E50-4A7D-9C85-BBC1E06228CA}
STANISLAUS 17021888 | {63080617-6586-4F7A-B820-64DDE42B59AD}
BEN LOMOND 04015400 | {81F477DE-A079-435A-9F55-2410FEC944BA}
DIAMOND SPRINGS 1107336076 | {01A8C6BD-323D-44E5-A686-1246351A46F2}
VOLTA 1101CB | {F21A680A-E282-4C69-AC36-05BB391457FE}
LLAGAS 2101XR244 | {133545C9-FF59-4E89-AB9A-6D025A3D74E4}
AUBERRY 1101D4982 | {90ABCC1D-5DD8-43C1-9AC0-715DCF2D275E}
ROSSMOOR 110168920 | {167EB25B-4A6A-4910-B109-DED2BEFF695B}
PERRY 110179696 | {240D21FA-CC4D-471E-B74F-148F84FE5FB1}
STILLWATER 11021466 | {430AA5A2-7BC0-4425-A05E-76360F269642}
LAKEWOOD 1102CB | {957F3B05-D3E6-46BF-B6B1-74EF9A986684}
TIDEWATER 210638866 | {2DE5693C-879D-4FCD-88B6-818902BD649A}
MIDDLETOWN 1101433160 | {67FA5D3B-5BFA-40EE-AABA-659446964531}
FROGTOWN 1702CB | {646B02DA-833B-4BEB-8A59-9FDCAF947841}
POINT MORETTI 110136514 | {6B3803C4-78D9-4845-848A-F16561C51AFC}
MC ARTHUR 11021324 | {76F913B6-6D49-4D3C-ACC8-2AE24DFE45A2}
WHEATLAND 11041348 | {86B4B4F4-9AA5-4F80-9B50-3C90FCAE3FE6}
SAN LUIS OBISPO 1103365572 | {AF070101-B27C-4E73-95B1-32ABEB0162BE}
ORINDA 0401401/2 LR | {B68800AA-8665-4562-B46C-56262DD45B63}
LOGAN CREEK 210269358 | {8700E55C-38C6-41AB-AF2A-3B50EA0B2E05}
HARRIS 11084674 | {1983F28A-08C9-48B3-9CC8-597EC6A45F0E}
PUEBLO 2103694 | {37307117-7712-4B70-890E-D9B3D42408D3}
FROGTOWN 1702815616 | {6E88E73E-9065-4C4A-A6A9-B27FFCD67E9B}
RACETRACK 17036014 | {97ACC61C-80B7-431D-B04B-B9076E222D13}
CLAYTON 2213167700 | {C972F264-64D1-4FA4-8935-EB84A5191895}
PEORIA 170184318 | {CB8A5610-26AF-406C-A01C-6D3A6199376B}
BEN LOMOND 110196738 | {EA87785F-FD13-47C1-AD0C-AE56EB6FAE60}
MONTE RIO 11135020 | {C3FAC8CF-A105-47CA-BAFD-6A205D726950}
NEWMAN 110542128 | {AD5BB80F-100E-443D-B968-9FD3EF2DDDC6}
PUTAH CREEK 11052777 | {D437F6E1-386B-4A56-A527-2C85C72A2065}
CORNING 11011624 | {DFFCBFCC-EE62-47E7-8ED4-582D4BFF492D}
OAKHURST 1101352740 | {2CDF7848-B063-4FC4-9C52-AE29AA49D3FF}
UPPER LAKE 1101472084 | {0F086603-31D0-422E-BBA1-3A12831F4713}
LOS OSITOS 21027592 | {3616477B-E0BC-4A69-8662-9C027B6A345B}
HICKS 2101XR162 | {4BEE9D9E-BAC4-46AE-B4EA-D5A6948A1B98}
SILVERADO 2105533226 | {4F585A0F-3E69-42C6-8427-3D94B7790006}
ALTO 11243745 | {5A7E1969-E475-4A2E-A5C6-85EFB5802FE4}
SHINGLE SPRINGS 210985766 | {762F5F25-9174-4408-84A6-399ADE39F207}
CAMBRIA 1101175422 | {90731576-6ADC-4169-86FA-CAE47F468CEA}
ATASCADERO 1101747522 | {98F44516-A7DA-4F88-98E1-7BF277BBBD67}
CAMP EVERS 210310946 | {A1366627-BA9B-4DAB-8067-98E47F041CB9}
GRASS VALLEY 11032110 | {B3488AFC-B0D0-44AE-ACC7-3FB60ED8C1AA}
ROSSMOOR 1105W564R | {2CF05CCD-DA30-4E66-88FB-8AE7485C3DA7}
PLACER 1104CB | {E502BFEB-ED5D-48C9-9524-9ECF207993E0}
LOS COCHES 11027046 | {C48784E3-4EDB-45E6-AEA2-4A807640BDC5}
SALMON CREEK 110137368 | {5DC6F02B-24BF-4504-9E01-B7C3B166BE28}
PIT NO 1 11013312 | {603720E6-C08C-4450-9A1D-FFFC2D98E7C9}
CORNING 1102915324 | {097280CB-BBAB-443B-A213-61E2653EB02B}
LOS GATOS 1106LA64 | {CFFA07B9-8209-4D21-824C-C9A2945C083F}
PUEBLO 1105115766 | {F405820C-EB9B-44D6-A3EF-2469BFF7A112}
PINE GROVE 11013170 | {207F56DE-FF3F-4FB6-9F25-8FC555D28285}
TEMPLETON 2109CB | {3D2DC8C9-F0E2-4189-8946-5553A87031B9}
HALF MOON BAY 1102863822 | {EC65686F-B15A-4CBF-8005-BF1274876E69}
MAPLE CREEK 1101CB | {D3EDA1A2-8AF8-4A2A-853E-161161439812}
EL CERRITO G 1113BR280 | {F1CD3584-0342-4B1C-AC95-933DCB32DB86}
LAURELES 11122768 | {30178FDC-BE0A-4074-95F8-23AFFDDFE15C}
SALT SPRINGS 210110416 | {3B618A90-1F99-49FA-8702-76A28A158E81}
KONOCTI 1102354890 | {4DDD6757-963A-43B8-ACBB-E2723C52F74B}
MENLO 1102W80 | {82B72724-3F36-4DE0-AF4C-310E9BC3E997}
DEL MONTE 210342226 | {8CF433ED-5D30-4AF4-B399-FAE6BF4CEC35}
LLAGAS 2106338878 | {CACB58CA-BF41-44AD-B0DF-195DBC524D67}
HALF MOON BAY 110398440 | {0D33DD6E-C54D-4E64-89FF-46D8E0E605B6}
PINE GROVE 110152088 | {1330A2A7-6F05-480E-914F-CD520FD996F9}
SAUSALITO 0402CB | {5AB6048B-BE9B-45DA-8B88-CE5B5004DC6C}
DEL MONTE 21032642 | {572A903E-D7FD-4349-978F-5FBD205DDA11}
OAKLAND X 1106CR008 | {A1C4F4D6-01EE-430E-BE68-0AE547BD756D}
OLETA 1102186326 | {A68CE267-B165-491B-AEAA-6DAE490DB1B3}
PLACERVILLE 210611132 | {23693049-039B-4514-94EB-4E3AE6138ACB}
RED BLUFF 110585632 | {2E98A968-0F7D-44C0-B9F5-8D4D032F12CD}
SAN RAMON 2108CB | {B814E637-1BB9-4F04-B0A4-F99C92D5342E}
OLETA 110113478 | {C597D1DF-05AF-4117-9139-6F79BFFC0A15}
FROGTOWN 1701CB | {CC00F970-8F13-4247-87D9-81AC67764BAD}
COARSEGOLD 210410335 | {9126AC99-906D-4CEE-8034-3EECC4C90F16}
WOODWARD 2108D412 | {8314795F-0D04-45BD-AE69-B7277494B0E9}
SAN LUIS OBISPO 1108V92 | {BB99A914-387F-48D8-919A-BB8BCFE90D9F}
PACIFICA 110266732 | {2E2285AC-DBD4-4A01-BBCE-F25D437434C6}
DOLAN ROAD 110157184 | {18BD8A9E-072B-4ADD-8F74-F890B89581F0}
ROSSMOOR 1103CB | {A42F88CD-4606-4D31-BD89-060DAE686890}
CLAYTON 2212CB | {E96A0569-DCDE-4681-A6D1-E506A3CBE6D9}
SUNOL 1101MR299 | {266E069D-C6A8-4558-8F2F-10A212B5E8EA}
PASO ROBLES 1103N52 | {35122D11-1E93-423C-905C-FD3596B054C4}
EL DORADO PH 210219562 | {40FC7F52-2B65-471F-ACDA-BEA2893716D4}
HUMBOLDT BAY 11027598 | {50FDFAC9-1C29-47B2-BBE8-2C25E0E08184}
SAN JOAQUIN #3 110110060 | {861A08FD-0602-4F14-A0F0-3B7AAA5D878A}
PAUL SWEET 2104885736 | {9BB76603-65A7-482F-A2CE-E72536A0A1DF}
MC KEE 110870535 | {41444F7B-0DEF-4E7D-BF1A-12A503159CC6}
PETALUMA C 1108600 | {B9E22F01-648D-4F6F-B1E0-311BE99AC492}
PUEBLO 2102698 | {EFBE7067-1C69-45D8-A9C8-472AE1406928}
SALMON CREEK 1101194 | {4BB38AE8-B760-4E43-B459-E75BDA0EF348}
TEMPLETON 2109R74 | {6A908DD9-6B72-4423-AA27-E74CEDA485AB}
PEORIA 170488630 | {6F5293E8-A883-45E5-9872-AC9FAE469C47}
CALISTOGA 1102640833 | {8A508CC4-F811-46AA-A430-C9F69A63B403}
PASO ROBLES 110789148 | {1C337801-E008-421B-9399-975B6DF38CC5}
ALTO 1124810594 | {D958A2D4-CE6E-4B3C-AC0F-6AE22C6D92E7}
BOLINAS 1101528 | {E52E3AA8-626F-4DCF-BFEC-F21E6141C71E}

## YTD EPSS Ignition Data
fixed_index_no | ILIS Report No | ignition_start_create_timestamp | dev_plbk_instruction | epss_circuit_opnum | circuit | circuit_protection_zone | fire_size | Response Time
642 | 22-0064281 | 2022-05-20 12:18 | FTS | 152201101-1730 | PIKE CITY 1101 | PIKE CITY 11011730 | 10-99 | 123
659 | 22-0060644, 22-0065198 | 2022-05-23 18:10 | FTS | 182721104-77098 | SANTA YNEZ 1104 | SANTA YNEZ 110477098 | <0.25 | 50
654 | 22-0065353 | 2022-05-23 21:53 | FTS | 014052103-CB | NORTH DUBLIN 2103 | NORTH DUBLIN 2103CB | 10-99 | 24
657 | 22-0065403 | 2022-05-24 00:27 | FTS | 043432102-636 | SILVERADO 2102 | SILVERADO 2102636 | 0.26-9.99 | 39
815 | 22-0072928 | 2022-06-10 21:46 | FTS | 042251101-94006 | HOPLAND 1101 | HOPLAND 110194006 | 0.26-9.99 | 24
816 | 22-0073081 | 2022-06-10 23:06 | FTS | 083242105-XR268 | MORGAN HILL 2105 | MORGAN HILL 2105XR268 | 0.26-9.99 | 194
848 | 22-0073996 | 2022-06-14 16:12 | FTS | 083252106-5178 | PAUL SWEET 2106 | PAUL SWEET 21065178 | <0.25 | 48
980 | 22-0078308 | 2022-06-24 23:08 | FTS | 042601101-37222 | PHILO 1101 | PHILO 110137222 | <0.25 | 59
981 | 22-0078516 | 2022-06-25 19:34 | FTS | 082021106-697500 | LOS GATOS 1106 | LOS GATOS 1106697500 | <0.25 | 63
982 | 22-0078562 | 2022-06-25 22:44 | FTS | 083622106-60124 | CAMP EVERS 2106 | CAMP EVERS 210660124 | 0.26-9.99 | 75
991 |  | 2022-06-26 21:47 | FTS | 063601111-CB | VACAVILLE 1111 | VACAVILLE 1111CB | <0.25
1014 | 22-0079791 | 2022-06-28 19:52 | FTS | 182541103-A18 | ATASCADERO 1103 | ATASCADERO 1103A18 | <0.25
1070 | 22-0081828 | 2022-07-05 11:45 | FTS | 83692104-10960 | ROB ROY 2104 | ROB ROY 210410960 | <0.25 | 31
1071 | 22-0081891 | 2022-07-05 13:03 | FTS | 43311102-64664 | KONOCTI 1102 | KONOCTI 110264664 | 0.26-9.99 | 36
1096 | 22-0082760 | 2022-07-07 12:15 | FTS | 42601101-CB | PHILO 1101 | PHILO 1101CB | <3 meters of linear travel | 57
1163 |  | 2022-07-15 06:42 | FTS | 103201101-CB | CHALLENGE 1101 | CHALLENGE 1101CB | <0.25
1256 | 22-0089321 | 2022-07-25 09:16 | FTS | 42711101-78734 | CALISTOGA 1101 | CALISTOGA 110178734 | 0.26-9.99 | 31