## Quarterly Submission Guide
| Yes | No | <-- for dropdowns
Wildfire Safety Division Attachment 2.3
Wildfire Mitigation Plan Quarterly report - non-spatial data template
Resolution WSD-011 Attachment 2.3
Instructions for use |  |  |  | Relevant options for mitigations table: Table 12
1 | Fill out the tan cells (color represented here) starting with the cell below (D17: Utility). The Utility name will populate the Table tabs to follow. Date modified will vary by table
2 | For each Table tab, after a modification is made, denote the date of the change in cell C4 for each Table tab. |  |  |  | Initiative categories | WMP Maturity model Categories | Driver options
3 | Some columns have an additional header in row 5 to serve as clarification for several columns. With the exception of projected data, row 5 will be highlighted in blue (color represented here)
4 | Some required metrics are future projections. For these, row 5, above the projections will be highlighted light green (color represented here) |  |  |  | Vegetation inspection | Risk Assessment & Mapping | 1. Ignitions | Contact with vegetation
| In future submissions, report updated projected numbers if / when projections have changed, and report actuals once the quarter / year has passed. |  |  |  | Vegetation management project | Situational Awareness & Forecasting |  | Other contact with object
5 | For data required annually rather than quarterly (see Tables 7.3 - 10), report for entire year even if part of the year is projected. Once year has passed, update cell with actuals |  |  |  | Asset inspection | Grid Design & System Hardening |  | Equipment failure
6 | Some tables will have additional instructions provided in a Notes box located in cells D2 - D4 |  |  |  | Grid hardening | Asset Management & Inspections |  | Wire-to-wire contact
Notes will explain terms, signal where projections are required, and provide other useful information.
7 | For the initial quarterly submission, utilities are required to submit data on annual metrics for 2015 - 2020, which should represent the most updated data from the 2020 WMP for years 2015-2019 |  |  |  | Other | Vegetation Management & Inspections |  | Contamination
* | Do not add or manipulate the template for any of the tabs |  |  |  |  | Data Governance |  | Vandalism / Theft
[6 empty] | Emergency Planning & Preparedness | 2. PSPS | PSPS - for sectionalization, etc.
Update the below table to establish which year, quarter of the WMP cycle this submission this represents.
Utility |  | Pacific Gas & Electric Company |  |  |  | Stakeholder Cooperation & Community Engagement
First year of 3-year WMP cycle |  | 2020
Submission year |  | 2021
Submission quarter |  | Q2 of 2021
Date Modified |  | 2021-08-02

## Table 1
Utility | Pacific Gas & Electric Company | Notes:
Table No. | 1 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
Date Modified | 2021-08-02
Note: These columns are placeholders for future QR submissions.
Table 1: Recent performance on progress metrics | [7 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Progress metric name | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
1. Grid condition findings from inspection - Distribution lines in HFTD | 1.a. | Number of circuit miles inspected from patrol inspections in HFTD - Distribution lines | 14387.9332 | 14356.0438 | 13003.3088 | 26291.4698 | 12705.0356 | 1: 4956.6152; 2: 6521.2204; 3: 6623.6717; 4: 1273.9693; Note: These columns are placeholders for future QR submissions. 1: 9676; Note: These columns are placeholders for future QR submissions. 2: 12532 | # circuit miles | Totals represent the number of poles patrolled in relationship to total poles in HFTD and converted to circuit miles. Note the circuit miles is an approximation since the patrol program is measured by pole count only.
| 1.b. | Number of circuit miles inspected from detailed inspections in HFTD - Distribution lines | 5350.1353 | 5899.5323 | 6570.7741 | 6782.3004 | 25223 | 1: 165.5898; 2: 6937.3393; 3: 5953.6485; 4: 61.3913; Note: These columns are placeholders for future QR submissions. 1: 863; Note: These columns are placeholders for future QR submissions. 2: 14062 | # circuit miles | Totals represent the number of poles inspected in relationship to total poles in HFTD and converted to circuit miles. Note the circuit miles is an approximation since the inspection program is measured by pole count only.
| 1.c. | Number of circuit miles inspected from other inspections (list types of "other" inspections in comments) in HFTD - Distribution lines | 1415.4965 | 3485.7618 | 3804.6946 | 1294.9429 | 1652.0647 | 1: 259.5034; 2: 960.0238; 3: 180.1236; 4: 509.0795; Note: These columns are placeholders for future QR submissions. 1: 122; Note: These columns are placeholders for future QR submissions. 2: 632 | # circuit miles | Totals represent the number of inspections from Pole Test and Treat program in relationship to total poles in HFTD and converted to circuit miles. Note the circuit miles is an approximation since the program is measured by pole count only.
| 1.d. | Level 1 findings in HFTD for patrol inspections - Distribution lines | 9 | 9 | 77 | 229 | 0 | 1: 4; 2: 16; 3: 431; 4: 4; Note: These columns are placeholders for future QR submissions. 1: 68; Note: These columns are placeholders for future QR submissions. 2: 12 | # findings
| 1.e. | Level 1 findings in HFTD for detailed inspections - Distribution lines | 3 | 6 | 1067 | 239 | 352 | 1: 135; 2: 208; 3: 1497; 4: 28; Note: These columns are placeholders for future QR submissions. 1: 51; Note: These columns are placeholders for future QR submissions. 2: 447 | # findings
| 1.f. | Level 1 findings in HFTD for other inspections (list types of "other" inspections in comments) - Distribution lines | 0 | 0 | 0 | 0 | 0 | 1: 0; 2: 0; 3: 2; 4: 1; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 0 | # findings | "Other" inspection methods include Pole Test and Treat and overhead IR.
| 1.g. | Level 2 findings in HFTD for patrol inspections - Distribution lines | 25 | 23 | 34 | 94 | 131 | 1: 16; 2: 14; 3: 30; 4: 3; Note: These columns are placeholders for future QR submissions. 1: 64; Note: These columns are placeholders for future QR submissions. 2: 47 | # findings
| 1.h. | Level 2 findings in HFTD for detailed inspections - Distribution lines | 487 | 576 | 651 | 648 | 10349 | 1: 74; 2: 1405; 3: 1538; 4: 18; Note: These columns are placeholders for future QR submissions. 1: 2982; Note: These columns are placeholders for future QR submissions. 2: 47504 | # findings
| 1.i. | Level 2 findings in HFTD for other inspections (list types of "other" inspections in comments) - Distribution lines | 4 | 1 | 4 | 28 | 2 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 10; Note: These columns are placeholders for future QR submissions. 2: 2 | # findings | "Other" inspection methods include Pole Test and Treat and overhead IR.
| 1.j. | Level 3 findings in HFTD for patrol inspections - Distribution lines | 92 | 83 | 55 | 316 | 462 | 1: 33; 2: 101; 3: 42; 4: 1; Note: These columns are placeholders for future QR submissions. 1: 3; Note: These columns are placeholders for future QR submissions. 2: 7 | # findings
| 1.k. | Level 3 findings in HFTD for detailed inspections - Distribution lines | 16735 | 19911 | 19667 | 16216 | 219664 | 1: 1267; 2: 39221; 3: 29915; 4: 197; Note: These columns are placeholders for future QR submissions. 1: 599; Note: These columns are placeholders for future QR submissions. 2: 10609 | # findings
| 1.l. | Level 3 findings in HFTD for other inspections (list types of "other" inspections in comments) - Distribution lines | 622 | 1775 | 1208 | 255 | 444 | 1: 37; 2: 113; 3: 82; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 0 | # findings | "Other" inspection methods include Pole Test and Treat and overhead IR.
1. Grid condition findings from inspection - Distribution lines total | 1.a.ii. | Number of total circuit miles inspected from patrol inspections - Distribution lines | 41094.9594 | 39822.6237 | 39966.6637 | 55931.77 | 55583.0052 | 1: 12536.2868; 2: 11649.4964; 3: 13067.4628; 4: 19631.0591; Note: These columns are placeholders for future QR submissions. 1: 13022; Note: These columns are placeholders for future QR submissions. 2: 21649 | # circuit miles | Totals represent the number of poles patrolled in relationship to total poles in Non-HFTD and converted to circuit miles. Note the circuit miles is an approximation since the patrol program is measured by pole count only.
| 1.b.ii. | Number of total circuit miles inspected from detailed inspections - Distribution lines | 14885.9002 | 15602.6283 | 15882.3415 | 16002.1839 | 35989.2651 | 1: 162.5379; 2: 7700.9472; 3: 11401.9412; 4: 4203.1861; Note: These columns are placeholders for future QR submissions. 1: 947; Note: These columns are placeholders for future QR submissions. 2: 15346 | # circuit miles | Totals represent the number of poles patrolled in relationship to total poles in Non-HFTD and converted to circuit miles. Note the circuit miles is an approximation since the patrol program is measured by pole count only.
| 1.c.ii. | Number of total circuit miles inspected from other inspections (list types of "other" inspections in comments) - Distribution lines | 9772.36 | 9098.1252 | 7982.0498 | 4986.4074 | 6733.7729 | 1: 1928.6223; 2: 1853.2088; 3: 1960.3699; 4: 2218.7724; Note: These columns are placeholders for future QR submissions. 1: 1429; Note: These columns are placeholders for future QR submissions. 2: 3516 | # circuit miles | Totals represent the number of inspections from Pole Test and Treat program in relationship to total poles in Non-HFTD and converted to circuit miles. Note the circuit miles is an approximation since the program is measured by pole count only.
| 1.d.ii. | Level 1 findings for patrol inspections - Distribution lines | 33 | 22 | 50 | 86 | 269 | 1: 50; 2: 38; 3: 94; 4: 68; Note: These columns are placeholders for future QR submissions. 1: 62; Note: These columns are placeholders for future QR submissions. 2: 49 | # findings | Non HFTD areas only
| 1.e.ii. | Level 1 findings for detailed inspections - Distribution lines | 22 | 33 | 414 | 5708 | 517 | 1: 59; 2: 91; 3: 445; 4: 148; Note: These columns are placeholders for future QR submissions. 1: 149; Note: These columns are placeholders for future QR submissions. 2: 405 | # findings | Non HFTD areas only
| 1.f.ii. | Level 1 findings for other inspections (list types of "other" inspections in comments) - Distribution lines | 1 | 0 | 0 | 1 | 14 | 1: 3; 2: 3; 3: 5; 4: 4; Note: These columns are placeholders for future QR submissions. 1: 1; Note: These columns are placeholders for future QR submissions. 2: 1 | # findings | Non HFTD areas only. "Other" inspection methods include Pole Test and Treat and overhead IR.
| 1.g.ii. | Level 2 findings for patrol inspections - Distribution lines | 156 | 90 | 96 | 132 | 310 | 1: 132; 2: 98; 3: 113; 4: 100; Note: These columns are placeholders for future QR submissions. 1: 163; Note: These columns are placeholders for future QR submissions. 2: 197 | # findings | Non HFTD areas only
| 1.h.ii. | Level 2 findings for detailed inspections - Distribution lines | 1153 | 1302 | 1077 | 1107 | 1894 | 1: 490; 2: 972; 3: 2380; 4: 1167; Note: These columns are placeholders for future QR submissions. 1: 3942; Note: These columns are placeholders for future QR submissions. 2: 21656 | # findings | Non HFTD areas only
| 1.i.ii. | Level 2 findings for other inspections (list types of "other" inspections in comments) - Distribution lines | 65 | 117 | 68 | 104 | 1 | 1: 5; 2: 1; 3: 11; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 939; Note: These columns are placeholders for future QR submissions. 2: 221 | # findings | Non HFTD areas only. "Other" inspection methods include Pole Test and Treat and overhead IR.
| 1.j.ii. | Level 3 findings for patrol inspections - Distribution lines | 317 | 239 | 195 | 405 | 1018 | 1: 228; 2: 149; 3: 195; 4: 54; Note: These columns are placeholders for future QR submissions. 1: 6; Note: These columns are placeholders for future QR submissions. 2: 7 | # findings | Non HFTD areas only
| 1.k.ii. | Level 3 findings for detailed inspections - Distribution lines | 35673 | 38733 | 31487 | 19278 | 39564 | 1: 1438; 2: 13837; 3: 49162; 4: 19010; Note: These columns are placeholders for future QR submissions. 1: 1051; Note: These columns are placeholders for future QR submissions. 2: 4505 | # findings | Non HFTD areas only
| 1.l.ii. | Level 3 findings for other inspections (list types of "other" inspections in comments) - Distribution lines | 3527 | 5948 | 3554 | 3763 | 1179 | 1: 950; 2: 2; 3: 1468; 4: 811; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 1 | # findings | Non HFTD Areas only. "Other" inspection methods include Pole Test and Treat and overhead IR.
1. Grid condition findings from inspection - Transmission lines in HFTD | 1.a.iii. | Number of circuit miles inspected from patrol inspections in HFTD - Transmission lines | 2585 | 3696 | 3048 | 3251 | 0 | 1: 663; 2: 1572; 3: 1259; 4: 1239; Note: These columns are placeholders for future QR submissions. 1: 2140; Note: These columns are placeholders for future QR submissions. 2: 1939 | # circuit miles
| 1.b.iii. | Number of circuit miles inspected from detailed inspections in HFTD - Transmission lines | 2978 | 1867 | 2515 | 2312 | 5563 | 1: 22; 2: 1048; 3: 1624; 4: 229; Note: These columns are placeholders for future QR submissions. 1: 685; Note: These columns are placeholders for future QR submissions. 2: 2520 | # circuit miles
| 1.c.iii. | Number of circuit miles inspected from other inspections (list types of "other" inspections in comments) in HFTD - Transmission lines | 1323 | 1323 | 1323 | 1323 | 1323 | 1: 331; 2: 331; 3: 331; 4: 331; Note: These columns are placeholders for future QR submissions. 1: 331; Note: These columns are placeholders for future QR submissions. 2: 331 | # circuit miles | "Other" inspection methods include Pole Test and Treat and overhead IR.
| 1.d.iii. | Level 1 findings in HFTD for patrol inspections - Transmission lines | - | - | - | - | 25 | 1: 0; 2: 1; 3: 133; 4: 10; Note: These columns are placeholders for future QR submissions. 1: 18; Note: These columns are placeholders for future QR submissions. 2: 1 | # findings
| 1.e.iii. | Level 1 findings in HFTD for detailed inspections - Transmission lines | 252 | 53 | 173 | 107 | 65 | 1: 0; 2: 10; 3: 11; 4: 5; Note: These columns are placeholders for future QR submissions. 1: 3; Note: These columns are placeholders for future QR submissions. 2: 47 | # findings
| 1.f.iii. | Level 1 findings in HFTD for other inspections (list types of "other" inspections in comments) - Transmission lines | - | - | - | - | 123 | 1: 38; 2: 21; 3: 108; 4: 37; Note: These columns are placeholders for future QR submissions. 1: 52; Note: These columns are placeholders for future QR submissions. 2: 23 | # findings | Includes any notification not found by patrol or detailed inspection.
| 1.g.iii. | Level 2 findings in HFTD for patrol inspections - Transmission lines | - | - | - | - | 549 | 1: 18; 2: 39; 3: 18; 4: 12; Note: These columns are placeholders for future QR submissions. 1: 37; Note: These columns are placeholders for future QR submissions. 2: 71 | # findings
| 1.h.iii. | Level 2 findings in HFTD for detailed inspections - Transmission lines | 3292 | 2346 | 2683 | 7664 | 48251 | 1: 116; 2: 3170; 3: 3872; 4: 631; Note: These columns are placeholders for future QR submissions. 1: 728; Note: These columns are placeholders for future QR submissions. 2: 8643 | # findings
| 1.i.iii. | Level 2 findings in HFTD for other inspections (list types of "other" inspections in comments) - Transmission lines | - | - | - | - | 2981 | 1: 359; 2: 735; 3: 743; 4: 204; Note: These columns are placeholders for future QR submissions. 1: 289; Note: These columns are placeholders for future QR submissions. 2: 522 | # findings | "Other" inspection methods include Pole Test and Treat and overhead IR.
| 1.j.iii. | Level 3 findings in HFTD for patrol inspections - Transmission lines | - | - | - | - | 56 | 1: 1; 2: 0; 3: 0; 4: 1; Note: These columns are placeholders for future QR submissions. 1: 1; Note: These columns are placeholders for future QR submissions. 2: 3 | # findings
| 1.k.iii. | Level 3 findings in HFTD for detailed inspections - Transmission lines | 662 | 554 | 999 | 710 | 4835 | 1: 25; 2: 2615; 3: 3476; 4: 465; Note: These columns are placeholders for future QR submissions. 1: 385; Note: These columns are placeholders for future QR submissions. 2: 4195 | # findings
| 1.l.iii. | Level 3 findings in HFTD for other inspections (list types of "other" inspections in comments) - Transmission lines | - | - | - | - | 539 | 1: 37; 2: 142; 3: 246; 4: 40; Note: These columns are placeholders for future QR submissions. 1: 73; Note: These columns are placeholders for future QR submissions. 2: 61 | # findings | "Other" inspection methods include Pole Test and Treat and overhead IR.
1. Grid condition findings from inspection - Transmission lines total | 1.a.iv. | Number of total circuit miles inspected from patrol inspections - Transmission lines | 8385 | 11523 | 10015 | 11198 | 7671 | 1: 2594; 2: 5742; 3: 4122; 4: 4208; Note: These columns are placeholders for future QR submissions. 1: 3657; Note: These columns are placeholders for future QR submissions. 2: 4546 | # circuit miles
| 1.b.iv. | Number of total circuit miles inspected from detailed inspections - Transmission lines | 9944 | 6807 | 8315 | 7131 | 10658 | 1: 36; 2: 1548; 3: 3847; 4: 1094; Note: These columns are placeholders for future QR submissions. 1: 1063; Note: These columns are placeholders for future QR submissions. 2: 3427 | # circuit miles
| 1.c.iv. | Number of total circuit miles inspected from other inspections (list types of "other" inspections in comments) - Transmission lines |  | 4393 | 4393 | 4393 | 4393 | 1: 1098; 2: 1098; 3: 1098; 4: 1098; Note: These columns are placeholders for future QR submissions. 1: 1098; Note: These columns are placeholders for future QR submissions. 2: 1098 | # circuit miles | "Other" inspection methods include Pole Test and Treat and overhead IR.
| 1.d.iv. | Level 1 findings for patrol inspections - Transmission lines | - | - | - | - | 63 | 1: 1; 2: 4; 3: 160; 4: 14; Note: These columns are placeholders for future QR submissions. 1: 62; Note: These columns are placeholders for future QR submissions. 2: 21 | # findings
| 1.e.iv. | Level 1 findings for detailed inspections - Transmission lines | 985 | 317 | 623 | 351 | 72 | 1: 0; 2: 59; 3: 45; 4: 94; Note: These columns are placeholders for future QR submissions. 1: 16; Note: These columns are placeholders for future QR submissions. 2: 51 | # findings
| 1.f.iv. | Level 1 findings for other inspections (list types of "other" inspections in comments) - Transmission lines | - | - | - | - | 355 | 1: 106; 2: 89; 3: 228; 4: 105; Note: These columns are placeholders for future QR submissions. 1: 156; Note: These columns are placeholders for future QR submissions. 2: 74 | # findings | "Other" inspection methods include Pole Test and Treat and overhead IR.
| 1.g.iv. | Level 2 findings for patrol inspections - Transmission lines | - | - | - | - | 1503 | 1: 79; 2: 218; 3: 131; 4: 114; Note: These columns are placeholders for future QR submissions. 1: 97; Note: These columns are placeholders for future QR submissions. 2: 332 | # findings
| 1.h.iv. | Level 2 findings for detailed inspections - Transmission lines | 9569 | 8779 | 10613 | 15588 | 54638 | 1: 249; 2: 6846; 3: 12375; 4: 7029; Note: These columns are placeholders for future QR submissions. 1: 1546; Note: These columns are placeholders for future QR submissions. 2: 7342 | # findings
| 1.i.iv. | Level 2 findings for other inspections (list types of "other" inspections in comments) - Transmission lines | - | - | - | - | 10621 | 1: 704; 2: 1336; 3: 1762; 4: 465; Note: These columns are placeholders for future QR submissions. 1: 958; Note: These columns are placeholders for future QR submissions. 2: 491 | # findings | "Other" inspection methods include Pole Test and Treat and overhead IR.
| 1.j.iv. | Level 3 findings for patrol inspections - Transmission lines | - | - | - | - | 158 | 1: 5; 2: 5; 3: 7; 4: 18; Note: These columns are placeholders for future QR submissions. 1: 1; Note: These columns are placeholders for future QR submissions. 2: 5 | # findings
| 1.k.iv. | Level 3 findings for detailed inspections - Transmission lines | 951 | 1065 | 2223 | 1614 | 5925 | 1: 117; 2: 4878; 3: 9034; 4: 3690; Note: These columns are placeholders for future QR submissions. 1: 780; Note: These columns are placeholders for future QR submissions. 2: 3748 | # findings
| 1.l.iv. | Level 3 findings for other inspections (list types of "other" inspections in comments) - Transmission lines | - | - | - | - | 2740 | 1: 112; 2: 189; 3: 506; 4: 107; Note: These columns are placeholders for future QR submissions. 1: 118; Note: These columns are placeholders for future QR submissions. 2: 74 | # findings | "Other" inspection methods include Pole Test and Treat and overhead IR.
2. Vegetation clearance findings from inspection - total | 2.a.i | Number of spans inspected where at least some vegetation was found in non-compliant condition - total | 2402 | 3010 | 3372 | 5072 | 37914 | 1: 9637; 2: 11055; 3: 15783; 4: 15773; Note: These columns are placeholders for future QR submissions. 1: 8543; Note: These columns are placeholders for future QR submissions. 2: 10588 | # of spans inspected with noncompliant clearance based on applicable rules and regulations at the time of inspection | See comments for this section.
| 2.a.ii | Number of spans inspected for vegetation compliance - total | 1443176 | 1562166 | 1458738 | 1496906 | 1525349 | 1: 428110; 2: 417774; 3: 335799; 4: 468295; Note: These columns are placeholders for future QR submissions. 1: 445641; Note: These columns are placeholders for future QR submissions. 2: 419031 | # of spans inspected for vegetation compliance | See comments for this section.
2. Vegetation clearance findings from inspection - in HFTD | 2.b.i | Number of spans inspected where at least some vegetation was found in non-compliant condition in HFTD | 204 | 442 | 912 | 1919 | 14469 | 1: 4385; 2: 6844; 3: 8078; 4: 5691; Note: These columns are placeholders for future QR submissions. 1: 4307; Note: These columns are placeholders for future QR submissions. 2: 5635 | # of spans inspected with noncompliant clearance based on applicable rules and regulations at the time of inspection | See comments for this section.
| 2.b.ii | Number of spans inspected for vegetation compliance in HFTD | 170577 | 337899 | 323228 | 428070 | 457740 | 1: 137694; 2: 165572; 3: 122804; 4: 120114; Note: These columns are placeholders for future QR submissions. 1: 152931; Note: These columns are placeholders for future QR submissions. 2: 163509 | # of spans inspected for vegetation compliance | See comments for this section.
3. Community outreach metrics | 3.a. | # Customers in an evacuation zone for utility-ignited wildfire | - | - | - | - | - | [12 empty] | # customers (if customer was in an evacuation zone for multiple wildfires, count the customer for each relevant wildfire) | See comments for this section. | bar: 1 to Note: These columns are placeholders for future QR submissions. 2
| 3.b. | # Customers notified of evacuation orders | - | - | - | - | - | [12 empty] | # customers (count customer multiple times for each unique wildfire of which they were notified) | See comments for this section. | bar: 1 to Note: These columns are placeholders for future QR submissions. 2
| 3.c. | % of customers notified of evacuation in evacuation zone of a utility-ignited wildfire | - | - | - | - | - | [12 empty] | Percentage of customers notified of evacuation | See comments for this section. | bar: 1 to Note: These columns are placeholders for future QR submissions. 2
Updated comments for Table 1 (8/2/2021): Inspections and findings data correspond with the uptick of inspections that are being done in Q2. Please refer to the commitment list in the 2021 WMP for more information. Comments for Table 1: Item 1. Description – Grid Condition Findings From Inspection – Distribution: · Level 1 findings are defined as Priority A tags. Level 2 findings are defined as Priority B and E tags. Level 3 findings are defined as priority F and H tags. · PG&E does not track inspection data by circuit mile. Circuit miles shown are estimated based as a fraction of total circuit mileage and are assumed proportional to the percentage of structures inspected for each inspection category. Item 1. Description – Grid Condition Findings From Inspection – Transmission: · Findings by inspection/patrol type are not available before 2019; all findings were assigned to Detailed Inspections. · Level 1 findings are defined as Priority A tags. Level 2 findings are defined as Priority B and E tags. Level 3 findings are defined as priority F tags. · PG&E does not track inspection data by circuit mile. If a structure/circuit was patrolled multiple times in a year, mileage is only counted once for that year. Fraction of total mileage was assumed proportional to the percentage of structures inspected. Item 2. Description – Vegetation Clearance Findings From Inspection: · The number of spans inspected with noncompliant clearance is based on applicable rules and regulations at the time of inspection. · PG&E does not track the precise data requested as PG&E’s vegetation management data is generally tracked by tree. Therefore, the closest available data has been provided with an estimated translation to the “Percentage of right-of-way with noncompliant clearance” data that was requested. PG&E vegetation management pre-inspectors identify a tree that is currently violating minimum clearance distances, or may violate minimum clearance in the near future, with a special designation of being a Hazard Notification (HN). Not all HNs represent actively non-compliant trees, as in many cases the tree is currently compliant but may be at risk of violating minimum clearances before the normal tree work cycle can be completed. Nonetheless, HNs are the best estimate PG&E has for the number of trees that were identified as being inside or near the minimum clearance requirements and have been provided above as the “Trees identified as being currently, or at risk in the near future, of being out of compliance” data. · This estimate for the number of electric overhead spans has been determined by assuming an average span length (distance between poles) of 275 feet. Item 3. Description – Community Outreach Metrics: # Customers in an Evacuation Zone for Utility-Ignited Wildfire; # Customers Notified of Evacuation Orders: · PG&E does not issue wildfire evacuation notices to customers and does not maintain metrics on the number of customers in an evacuation zone or the number of customers notified of evacuation orders. In an effort to gather this data, PG&E’s Public Safety Specialists reached out to safety personnel from 38 counties to determine if any evacuation data was available for the utility-ignited wildfires as defined in Table 2. Most replies from county personnel provided limited or incomplete data or indicated that the requested data was not available. Because of this, PG&E is unable to report on evacuation related requirements in this table. PG&E anticipates this to be a recurring challenge going forward. Item 4. Assumptions for Inspection Data in 1.a,1.b,1.c · See note below regarding Table 8 (historical grid data unavailable for 2014-2018); circuit mileage is assumed to be the same as our 2019 data for 2015-2018 for the purposes of Table 1 · Mileage was extrapolated using approximate unit counts of historical detailed inspection & Pole Test & Treat data & relative circuit mileage in High Fire Threat District (HFTD) and Non HFTD

## Table 2
Utility | Pacific Gas & Electric Company | Notes:
Table No. | 2 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
Date Modified | 2021-08-02
Note: These columns are placeholders for future QR submissions.
Table 2: Recent performance on outcome metrics | [7 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Outcome metric name | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
1. Risk events | 1.a. | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | 36643 | 37078 | 50711 | 34129 | 45989 | 1: 9455; 2: 9060; 3: 11358; 4: 9465; Note: These columns are placeholders for future QR submissions. 1: 15429; Note: These columns are placeholders for future QR submissions. 2: 10519 | Number per year
| 1.b. | Number of wires down (total) | 3280 | 3646 | 6475 | 2994 | 5577 | 1: 1174; 2: 677; 3: 804; 4: 639; Note: These columns are placeholders for future QR submissions. 1: 1952; Note: These columns are placeholders for future QR submissions. 2: 628 | Number of wires down per year
| 1.c. | Number of outage events not caused by contact with vegetation (total) | 32826 | 32596 | 42293 | 30741 | 37715 | 1: 7769; 2: 8236; 3: 10495; 4: 8788; Note: These columns are placeholders for future QR submissions. 1: 12764; Note: These columns are placeholders for future QR submissions. 2: 9838 | Number of outage events per year
| 1.d. | Number of outage events caused by contact with vegetation (total) | 3817 | 4482 | 8418 | 3388 | 8274 | 1: 1686; 2: 824; 3: 863; 4: 677; Note: These columns are placeholders for future QR submissions. 1: 2665; Note: These columns are placeholders for future QR submissions. 2: 681 | Number of outage events per year
2. Utility inspection findings - Distribution | 2.a. | Number of Level 1 findings (distribution - total) | 68 | 70 | 1608 | 6263 | 1152 | 1: 251; 2: 356; 3: 2474; 4: 253; Note: These columns are placeholders for future QR submissions. 1: 331; Note: These columns are placeholders for future QR submissions. 2: 914 | # findings
| 2.b. | Number of Level 2 findings (distribution - total) | 1890 | 2109 | 1930 | 2113 | 12687 | 1: 717; 2: 2490; 3: 4072; 4: 1288; Note: These columns are placeholders for future QR submissions. 1: 8100; Note: These columns are placeholders for future QR submissions. 2: 69627 | # findings
| 2.c. | Number of Level 3 findings (distribution - total) | 56966 | 66689 | 56166 | 40233 | 262331 | 1: 3953; 2: 53423; 3: 80864; 4: 20073; Note: These columns are placeholders for future QR submissions. 1: 1659; Note: These columns are placeholders for future QR submissions. 2: 15129 | # findings
| 2.d. | Number of distribution circuit miles inspected | 86040 | 87873 | 87590 | 111591 | 139400 | 1: 20367; 2: 36074; 3: 39402; 4: 25675; Note: These columns are placeholders for future QR submissions. 1: 15398; Note: These columns are placeholders for future QR submissions. 2: 40511 | # circuit miles
2. Utility inspection findings - Transmission | 2.a.ii | Number of Level 1 findings (transmission - total) | 1237 | 370 | 796 | 458 | 703 | 1: 145; 2: 184; 3: 685; 4: 265; Note: These columns are placeholders for future QR submissions. 1: 234; Note: These columns are placeholders for future QR submissions. 2: 146 | # findings
| 2.b.ii | Number of Level 2 findings (transmission - total) | 12861 | 11125 | 13296 | 23252 | 118543 | 1: 1525; 2: 12344; 3: 18901; 4: 8455; Note: These columns are placeholders for future QR submissions. 1: 2601; Note: These columns are placeholders for future QR submissions. 2: 8165 | # findings
| 2.c.ii | Number of Level 3 findings (transmission - total) | 1613 | 1619 | 3222 | 2324 | 14253 | 1: 297; 2: 7829; 3: 13269; 4: 4321; Note: These columns are placeholders for future QR submissions. 1: 899; Note: These columns are placeholders for future QR submissions. 2: 3827 | # findings
| 2.d.ii | Number of transmission circuit miles inspected | 22722 | 22723 | 22723 | 22722 | 22722 | 1: 3728; 2: 8388; 3: 9067; 4: 6400; Note: These columns are placeholders for future QR submissions. 1: 2294; Note: These columns are placeholders for future QR submissions. 2: 31722 | # circuit miles
3. Utility ignited wildfire fatalities | 3.a. | Fatalities due to utility-ignited wildfire (total) | 2 | 0 | 22 | 85 | 0 | 1: 0; 2: 0; 3: 4; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 0 | Number of fatalities per year
| 3.b. | Injuries due to utility-ignited wildfire (total) | - | - | - | - | - | 1: 0; 2: 0; 3: 1; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 0 | Number of injuries per year
4. Value of assets destroyed by utility-ignited wildfire, listed by asset type | 4.a. | Value of assets destroyed by utility-ignited wildfire (total) | $895.5M | $880k | $25.5B | $36k | $39k | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 0 | Dollars of damage or destruction per year
5. Structures damaged or destroyed by utility-ignited wildfire | 5.a. | Number of structures destroyed by utility-ignited wildfire (total) | 965 | 0 | 2299 | 18805 | 377 | 1: 0; 2: 0; 3: 209; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 0 | Number of structures destroyed per year | Three structures have been added to the 2020 total since the last submittal
| 5.b. | Critical infrastructure damaged/destroyed by utility-ignited wildfire (total) | 2 | 0 | 20 | 33 | 3 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 0 | Number of critical infrastructure damaged/destroyed per year
6. Acreage burned by utility-ignited wildfire | 6.a. | Acreage burned by utility-ignited wildfire (total) | 73328 | 2042 | 172205 | 167602 | 83643 | 1: 70; 2: 2209; 3: 58548; 4: 290; Note: These columns are placeholders for future QR submissions. 1: 742; Note: These columns are placeholders for future QR submissions. 2: 110 | Acres burned per year | Adjusted acreage of FREEDOM BLVD (Index 58) from 40 acres to 37 acres per Cal Fire Final Report
7. Number of utility wildfire ignitions | 7.a. | Number of ignitions (total) according to existing ignition data reporting requirement | 20 | 15 | 52 | 25 | 25 | 1: 0; 2: 15; 3: 13; 4: 1; Note: These columns are placeholders for future QR submissions. 1: 3; Note: These columns are placeholders for future QR submissions. 2: 3 | Number per year | The total number of historical ignitions has risen since the initial submission due to ongoing audits of systems of records including FAS, the EIR database, and CAP. It is likely the number of historical ignitions will continue to increase as other systems of record are audited for potential missed ignitions. | 7/19/21 - 3 Q2 incidents - SLOPE (Index 697), BUCK (index 733), & SILICON (Index 803)
| 7.b. | Number of ignitions in HFTD (subtotal) | 9 | 8 | 21 | 10 | 5 | 1: 0; 2: 4; 3: 6; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 2; Note: These columns are placeholders for future QR submissions. 2: 2 | Number in HFTD per year
| 7.c. | Number of ignitions in HFTD Zone 1 | 0 | 0 | 0 | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 0 | Number in HFTD Zone 1 per year
| 7.c.ii. | Number of ignitions in HFTD Tier 2 | 7 | 6 | 15 | 8 | 4 | 1: 0; 2: 4; 3: 6; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 1; Note: These columns are placeholders for future QR submissions. 2: 2 | Number in HFTD Tier 2 per year
| 7.c.iii. | Number of ignitions in HFTD Tier 3 | 2 | 2 | 6 | 2 | 1 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 1; Note: These columns are placeholders for future QR submissions. 2: 1 | Number in HFTD Tier 3 per year
| 7.d. | Number of ignitions in non-HFTD (subtotal) | 11 | 7 | 31 | 15 | 20 | 1: 0; 2: 11; 3: 7; 4: 1; Note: These columns are placeholders for future QR submissions. 1: 1; Note: These columns are placeholders for future QR submissions. 2: 1 | Number in non-HFTD per year
8. Fatalities resulting from utility wildfire mitigation initiatives | 8.a. | Fatalities due to utility wildfire mitigation activities (total) - "activities" defined as all activities accounted for in the 2020 WMP proposed WMP spend | - | - | - | 0 | 1 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 1; Note: These columns are placeholders for future QR submissions. 2: 2 | Number of fatalities per year
9. OSHA-reportable injuries from utility wildfire mitigation initiatives | 9.a. | OSHA-reportable injuries due to utility wildfire mitigation activities (total) - "activities" defined as all activities accounted for in the 2020 WMP proposed WMP spend | - | - | - | 0 | 53 | 1: 14; 2: 12; 3: 25; 4: 19; Note: These columns are placeholders for future QR submissions. 1: 1; Note: These columns are placeholders for future QR submissions. 2: 2 | Number of OSHA-reportable injuries per year
Updated comments for Table 1 (8/2/2021): Inspections and findings data correspond with the uptick of inspections that are being done in Q2. Please refer to the commitment list in the 2021 WMP for more information. Updated comments for Table 2: 5/3/2021 1) PG&E’s Electric Incident Investigation (EII) team is conducting a system of record audit for ignition events. The updated counts in Table 7.1 represent the events known to PG&E at the time of filing but are subject to change as the audit progresses. Changes are reflected in Purple font. 2) 2020 includes data related to the Zogg Fire, which is reported in compliance with D.19-05-037. PG&E's investigation into the cause of the Zogg Fire is ongoing. PG&E has included information related to the Zogg Fire in this table because CAL FIRE has announced its determination that PG&E's facilities caused the fire. Comments for Table 2: The data in Table 2 is derived from ignitions that are linked to a wildfire, which is defined as a fire greater than 10 acres in size. · Items 3.a (Fatalities due to utility-ignited wildfire [total]) and 3.b (Injuries due to utility-ignited wildfire (total)): PG&E provides in the attached data table 2015 through 2019 for wildfires that the California Department of Forestry and Fire protection (CAL FIRE) concluded were caused by PG&E equipment. · Item 4a (Value of assets destroyed by utility-ignited wildfire [total]): PG&E provides in the attached data table all 2015-2020 wildfires that involve disputes regarding destroyed assets that have settled. These settlements are lump sum settlements that do not break out the settlement dollars by damage category. In addition, the settlements reached related to the 2017 North Bay Fires and the 2018 Camp Fire (other than the settlement with the cities and counties) do not break out the settlement dollars by fire. Any attempt to break out the dollars by fire and/or damage category would be speculative. The settlements are totaled based on the year of the fire. The one exception is the 2018 Camp Fire which is reported with the 2017 North Bay Fires for the reasons described above. The chart does not include 2015-2020 wildfires that have not settled, which remain under investigation and/or civil discovery on causation issues, damages issues, or both. · Item 5b (Critical infrastructure damaged/destroyed by utility-ignited wildfire [total]): ‘Critical infrastructure’ is defined in accordance with the definition adopted in Decision (D.) 19-05-042 and modified in D.20-05-051. The number of critical infrastructure damaged/destroyed reflects the count of unique Service Point ID’s (meters) for red-tagged structures defined as critical infrastructure at the time of the wildfire. · Item 7a-d (Number of utility wildfire ignitions): The 2015 through 2018 ignition data is primarily based on fire incident reports filed with the California Public Utilities Commission (CPUC or Commission) annually in accordance with D.14-02-015. These reports include fire incidents that may be associated with PG&E facilities and meet the following conditions: (1) a self-propagating fire of material other than electrical and/or communication facilities (2) the resulting fire traveled greater than one linear meter from the ignition point, and (3) PG&E has knowledge that the fire occurred. Where not already included as part of the CPUC fire incidents report data, PG&E also included data for 2015 through 2018 wildfires that CAL FIRE concluded were caused by PG&E equipment. As of the time of the 2021 WMP submission, 2020 ignition data is being reviewed by PG&E in preparation for our 2020 fire incident that will be submitted by April 1, 2021.

## Table 3
Utility | Pacific Gas & Electric Company
Table No. | 3
Date Modified | 2021-02-05
Note: These columns are placeholders for future QR submissions.
Table 3: List and description of additional metrics | [9 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric | Definition | Purpose | Assumptions made to connect metric to purpose | Third-party validation (if any) | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
PG&E provided several metrics in the 2020 WMP for this section. With the update of the WMP template, all of these metrics were incorporated and included in other parts of the 2021 WMP. PG&E has no new or additional metrics to include to evaluate wildfire mitigation that are not already captured in other sections of the 2021 WMP. However, PG&E may analyze and look to reuse these metrics in ways not documented in the WMP as we continue to mature our data sets and modeling.

## Table 4
Utility | Pacific Gas & Electric Company
Table No. | 4
Date Modified | 2021-08-02
Note: These columns are placeholders for future QR submissions.
Table 4: Fatalities due to utility wildfire mitigation initiatives | [7 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Outcome metric name | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
1. Fatalities - Full-time Employee | 1.a. | Fatalities due to utility inspection - Full-time employee | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 0 | # fatalities
| 1.b. | Fatalities due to vegetation management - Full-time employee | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 0 | # fatalities
| 1.c. | Fatalities due to utility fuel management - Full-time employee | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 0 | # fatalities
| 1.d. | Fatalities due to grid hardening - Full-time employee | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 0 | # fatalities
| 1.e. | Fatalities due to other - Full-time employee | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 0 | # fatalities
2. Fatalities - Contractor | 2.a. | Fatalities due to utility inspection - Contractor | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 1 | # fatalities
| 2.b. | Fatalities due to vegetation management - Contractor | - | - | - | 0 | 0 | 1: 1; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 1; Note: These columns are placeholders for future QR submissions. 2: 0 | # fatalities
| 2.c. | Fatalities due to utility fuel management - Contractor | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 0 | # fatalities
| 2.d. | Fatalities due to grid hardening - Contractor | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 0 | # fatalities
| 2.e. | Fatalities due to other - Contractor | - | - | - | 0 | 1 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 1 | # fatalities
3. Fatalities - Member of public | 3.a. | Fatalities due to utility inspection - Public | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 0 | # fatalities
| 3.b. | Fatalities due to vegetation management - Public | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 0 | # fatalities
| 3.c. | Fatalities due to utility fuel management - Public | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 0 | # fatalities
| 3.d. | Fatalities due to grid hardening - Public | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 0 | # fatalities
| 3.e. | Fatalities due to other - Public | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 0 | # fatalities
Comments for Table 4: 1. Data for “Member of public” was derived from review of PG&E’s “Riskmaster” database, which tracks third party claims. 2. PG&E’s Community Wildfire Safety Program (CWSP), under which PG&E tracks our wildfire mitigation activities, was developed in 2018, with the above activities implemented in late 2018. Therefore, the “Year 2018” data above represents data from late 2018.

## Table 5
Utility | Pacific Gas & Electric Company
Table No. | 5
Date Modified | 2021-08-02
Note: These columns are placeholders for future QR submissions.
Table 5: OSHA-reportable injuries due to utility wildfire mitigation initiatives | [7 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Outcome metric name | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
1. OSHA injuries - Full-time Employee | 1.a. | OSHA injuries due to utility inspection - Full-time employee | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 0 | # OSHA-reportable injuries
| 1.b. | OSHA injuries due to vegetation management - Full-time employee | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 0 | # OSHA-reportable injuries
| 1.c. | OSHA injuries due to utility fuel management - Full-time employee | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 0 | # OSHA-reportable injuries
| 1.d. | OSHA injuries due to grid hardening - Full-time employee | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 0 | # OSHA-reportable injuries
| 1.e. | OSHA injuries due to other - Full-time employee | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 0 | # OSHA-reportable injuries
2. OSHA injuries - Contractor | 2.a. | OSHA injuries due to utility inspection - Contractor | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 0 | # OSHA-reportable injuries
| 2.b. | OSHA injuries due to vegetation management - Contractor | - | - | - | 1 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 2 | # OSHA-reportable injuries
| 2.c. | OSHA injuries due to utility fuel management - Contractor | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 0 | # OSHA-reportable injuries
| 2.d. | OSHA injuries due to grid hardening - Contractor | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 0 | # OSHA-reportable injuries
| 2.e. | OSHA injuries due to other - Contractor | - | - | - | 0 | 1 | 1: 0; 2: 0; 3: 1; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 0 | # OSHA-reportable injuries
3. OSHA injuries - Member of public | 3.a. | OSHA injuries due to utility inspection - Public | - | - | - | 0 | 0 | 1: 0; 2: 1; 3: 0; 4: 1; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 0 | # OSHA-reportable injuries
| 3.b. | OSHA injuries due to vegetation management - Public | - | - | - | 1 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 0 | # OSHA-reportable injuries
| 3.c. | OSHA injuries due to utility fuel management - Public | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 0 | # OSHA-reportable injuries
| 3.d. | OSHA injuries due to grid hardening - Public | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 0 | # OSHA-reportable injuries
| 3.e. | OSHA injuries due to other - Public | - | - | - | 0 | 0 | 1: 0; 2: 0; 3: 0; 4: 0; Note: These columns are placeholders for future QR submissions. 1: 0; Note: These columns are placeholders for future QR submissions. 2: 0 | # OSHA-reportable injuries
Comments for Table 5: 1. PG&E has limited information regarding injuries to contractors and members of the public, and any related medical treatment, during wildfire mitigation initiatives because PG&E is not responsible for reporting those injuries to OSHA. Thus, the figures in Table 5 relating to OSHA-reportable injuries to contractors and members of the public due to wildfire mitigation initiatives are based on PG&E's best available data for injuries that, given their severity, would have likely been reported to OSHA by PG&E had the injuries occurred to a PG&E employee. 2. PG&E’s CWSP, under which PG&E tracks our wildfire mitigation activities, was developed in 2018, with the above activities implemented in late 2018. Therefore, the “Year 2018” data above represents data from late 2018. 3. PG&E previously submitted data for OSHA-recordable injuries to employees, contractors, and members of the public due to wildfire mitigation initiatives as part of Table 6 of our 2020 Wildfire Mitigation Plan (WMP) and Table 5 of our 2021 WMP. In order to align with the WSD and the other utilities, we re-reviewed our records regarding injuries to employees, contractors, and members of the public to determine which injuries may be more specifically classified as OSHA-reportable injuries due to wildfire mitigation initiatives from 2018-2020 and amended Table 5 accordingly. The amendment was made on April 12, 2021 in response to California Public Advocates WMP Data Request 41. This Quarterly update to Table 5 is based on the amended version of Table 5 served on April 12, 2021. 4. OSHA-reportable injuries resulting in fatalities due to wildfire mitigation activities are captured in Table 4 rather than Table 5 to avoid double-counting.

## Table 6
Utility | Pacific Gas & Electric Company
Table No. | 6
Date Modified | 2021-08-02
Note: These columns are placeholders for future QR submissions.
Table 6: Weather patterns | [7 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Outcome metric name | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
1. Red Flag Warning Circuit Mile Days | 1.a. | Red Flag Warning overhead Circuit Mile days - entire utility territory | 148629.78 | 171642.81 | 594877.94 | 632033.39 | 577409.39 | 1: 0; 2: 104375.13; 3: 285515.17; 4: 365180.7; Note: These columns are placeholders for future QR submissions. 1: 6403.91; Note: These columns are placeholders for future QR submissions. 2: 141547.28 | Sum of circuit miles of utility grid subject to Red Flag Warning each day within a given time period, calculated as the number of circuit miles that were under an RFW multiplied by the number of days those miles were under said RFW. For example, if 100 circuit miles were under an RFW for 1 day, and 10 of those miles were under RFW for an additional day, then the total RFW circuit mile days would be 110.
| 1.b. | Red Flag Warning overhead Circuit Mile days - HFTD Zone 1 | 87.81 | 8.42 | 65.48 | 347.77 | 164.27 | 1: 0; 2: 0; 3: 154.46; 4: 163.51; Note: These columns are placeholders for future QR submissions. 1: -; Note: These columns are placeholders for future QR submissions. 2: 1.36 | Red Flag Warning OH Circuit Mile days, see above for definition
| 1.c. | Red Flag Warning overhead Circuit Mile days - HFTD Tier 2 | 30101.21 | 48603.57 | 169935.61 | 166968.54 | 132579.98 | 1: 0; 2: 14708.29; 3: 85128.14; 4: 105136.89; Note: These columns are placeholders for future QR submissions. 1: 2673.32; Note: These columns are placeholders for future QR submissions. 2: 43213.47 | Red Flag Warning OH Circuit Mile days, see above for definition
| 1.d. | Red Flag Warning overhead Circuit Mile days - HFTD Tier 3 | 12210.71 | 21835.32 | 89698.22 | 70654.04 | 56819.47 | 1: 0; 2: 3346.08; 3: 29214.41; 4: 56324.3; Note: These columns are placeholders for future QR submissions. 1: 516.29; Note: These columns are placeholders for future QR submissions. 2: 14284.15 | Red Flag Warning OH Circuit Mile days, see above for definition
| 1.e. | Red Flag Warning overhead Circuit Mile days - Non-HFTD | 106230.05 | 101195.51 | 335178.62 | 394063.04 | 387845.67 | 1: 0; 2: 86320.76; 3: 171018.16; 4: 203556; Note: These columns are placeholders for future QR submissions. 1: 3214.31; Note: These columns are placeholders for future QR submissions. 2: 84048.29 | Red Flag Warning OH Circuit Mile days, see above for definition
2. Wind conditions | 2.a. | High wind warnings | 2393.63 | 28023 | 140758.36 | 3996.58 | 83181.8 | 1: 3142.43; 2: 581.79; 3: 0; 4: 1137.73; Note: These columns are placeholders for future QR submissions. 1: 8415.73; Note: These columns are placeholders for future QR submissions. 2: 779.31 | Sum of circuit miles of utility grid subject to High Wind Warnings (HWW, as defined by the National Weather Service) each day within a given time period, calculated as the number of circuit miles that were under an HWW multiplied by the number of days those miles were under said HWW. For example, if 100 circuit miles were under an HWW for 1 day, and 10 of those miles were under HWW for an additional day, then the total HWW circuit mile days would be 110.
3. Other | 3.a. | Other relevant weather pattern metrics tracked (add additional rows as needed)
Comments for Table 6: Table 6 shows the trends of National Weather Service (NWS) issued Red Flag Warnings (RFWs) and High Wind Warnings (HWWs) over the last 5 years impacting PG&E circuits across the territory through the metrics RFW Circuit Mile Days and HWW Circuit Mile Days. NWS RFWs are a proxy for high fire danger conditions, while HWWs are issued for solely high wind threats, regardless of humidity values and fire danger. These values have changed from previous reports, which calculated RFW Day Circuit miles based on Fire Index Areas. For these metrics, circuit miles are now calculated by the NWS RFW and HWW polygons to give a more accurate and precise values for RFW Circuit Mile Days and HWW Circuit Mile Days.

## Table 7.1
| Utility | Pacific Gas & Electric Company | Notes:
| Table No. | 7.1 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
| Date Modified | 2021-08-02 | Data from 2015 - 2020 Q2 should be actual numbers. 2020 Q3 - 2023 should be projected. In future submissions update projected numbers with actuals
[6 empty] | Number of risk events | [10 empty] | Projected risk events
| Table 7.1: Key recent and projected drivers of risk events | [9 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
| Risk Event category | Cause category | # | Sub-cause category | Are risk events tracked for ignition driver? (yes / no) | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
x | Wire down event - Distribution | 1. Contact from object - Distribution | 1.a. | Veg. contact- Distribution | Yes | 1387 | 1618 | 3566 | 1052 | 3267 | 665 | 238 | 270 | 176 | 1096 | 167 | 268.0328 | 174.7176 | 654.9114 | 234.3893 | 265.9039 | 173.3299 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 1.b. | Animal contact- Distribution | Yes | 99 | 96 | 93 | 107 | 100 | 35 | 28 | 24 | 31 | 22 | 26 | 23.9092 | 30.8827 | 34.7124 | 27.7699 | 23.8028 | 30.7453 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 1.c. | Balloon contact- Distribution | Yes | 38 | 36 | 32 | 53 | 35 | 6 | 20 | 14 | 7 | 7 | 17 | 14 | 7 | 6 | 20 | 14 | 7 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 1.d. | Vehicle contact- Distribution | Yes | 551 | 629 | 600 | 602 | 561 | 126 | 153 | 187 | 157 | 133 | 167 | 187 | 157 | 126 | 153 | 187 | 157 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition. Q4 2020 includes minor updates based on post outage reviews.
|  |  | 1.e. | Other contact from object - Distribution | Yes | 104 | 123 | 108 | 102 | 106 | 26 | 17 | 20 | 18 | 31 | 27 | 20 | 18 | 26 | 17 | 20 | 18 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 2. Equipment / facility failure - Distribution | 2.a. | Connector damage or failure- Distribution | Yes | 518 | 518 | 943 | 500 | 767 | 144 | 109 | 113 | 116 | 367 | 105 | 112.3745 | 115.3579 | 142.2412 | 107.6687 | 111.6198 | 114.5832 | # risk events (excluding ignitions) | Assumed this was meant to indicate conductor damage and not connector damage since these would be covered as splices. This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 2.b. | Splice damage or failure — Distribution | Yes | 231 | 262 | 320 | 225 | 245 | 64 | 47 | 48 | 54 | 86 | 54 | 47.7343 | 53.7011 | 63.2183 | 46.426 | 47.4137 | 53.3405 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 2.c. | Crossarm damage or failure - Distribution | Yes | 36 | 50 | 86 | 46 | 69 | 13 | 10 | 6 | 19 | 27 | 7 | 5.9668 | 18.8948 | 12.8412 | 9.8779 | 5.9267 | 18.7679 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 2.d. | Insulator damage or failure- Distribution | Yes | 20 | 20 | 37 | 34 | 26 | 11 | 7 | 4 | 6 | 4 | 2 | 3.9779 | 5.9668 | 10.8656 | 6.9145 | 3.9511 | 5.9267 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 2.e. | Lightning arrestor damage or failure- Distribution | Yes | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 2.f. | Tap damage or failure - Distribution | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Unclear what is requested and assumed this data detail is not readily available.
|  |  | 2.g. | Tie wire damage or failure - Distribution | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | This data detail is not readily available and jumper wire failures are included with the splice failure data.
|  |  | 2.h. | Other - Distribution | Yes | 118 | 151 | 319 | 141 | 208 | 38 | 16 | 23 | 35 | 97 | 30 | 22.8727 | 34.8063 | 37.5359 | 15.8046 | 22.7191 | 34.5725 | # risk events (excluding ignitions) | Includes ignition events since this detail is not readily available to be excluded.
|  | 3. Wire-to-wire contact - Distribution | 3.a. | Wire-to-wire contact / contamination- Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Generally not applicable to wire down events.
|  | 4. Contamination - Distribution | 4.a. | Contamination - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Not applicable. PG&E uses contamination more as a condition of the equipment and not normally as a basic cause.
|  | 5. Utility work / Operation | 5.a. | Utility work / Operation | No | 8 | 22 | 9 | 12 | 15 | 3 | 2 | 6 | 3 | 5 | 8 | 5.8675 | 2.9337 | 2.9329 | 1.9553 | 5.8658 | 2.9329 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 6. Vandalism / Theft - Distribution | 6.a. | Vandalism / Theft - Distribution | Yes | 4 | 2 | 2 | 6 | 4 | 0 | 0 | 1 | 2 | 0 | 0 | 0.992 | 1.984 | 0 | 0 | 0.98433 | 1.9687 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 7. Other- Distribution | 7.a. | All Other- Distribution | Yes | 100 | 72 | 264 | 69 | 97 | 22 | 23 | 78 | 8 | 35 | 11 | 77.6538 | 7.9645 | 21.788 | 22.7783 | 77.2482 | 7.9229 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 8. Unknown- Distribution | 8.a. | Unknown - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | Generally not applicable to wire down events.
x | Wire down event - Transmission | 9. Contact from object - Transmission | 9.a. | Veg. contact- Transmission | Yes | 20 | 10 | 35 | 5 | 18 | 5 | 0 | 0 | 1 | 11 | 0 | 0 | 1 | 5 | 0 | 0 | 1 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 9.b. | Animal contact- Transmission | Yes | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 9.c. | Balloon contact- Transmission | Yes | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 9.d. | Vehicle contact- Transmission | Yes | 8 | 5 | 8 | 10 | 9 | 4 | 1 | 0 | 2 | 3 | 3 | 0 | 2 | 4 | 1 | 0 | 2 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 9.e. | Other contact from object - Transmission | Yes | 5 | 4 | 4 | 4 | 1 | 0 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3 | 0 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 10. Equipment / facility failure - Transmission | 10.a. | Connector damage or failure- Transmission | Yes | 7 | 14 | 8 | 7 | 28 | 6 | 1 | 1 | 3 | 23 | 1 | 1 | 3 | 6 | 1 | 1 | 3 | # risk events (excluding ignitions) | Assume CPUC meant "Conductor"; does not exclude events that led to CPUC reportable ignition
|  |  | 10.b. | Splice damage or failure — Transmission | Yes | 5 | 3 | 7 | 2 | 1 | 0 | 1 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 2 | 0 | # risk events (excluding ignitions) | Includes "Connector" failures; does not exclude events that led to CPUC reportable ignition
|  |  | 10.c. | Crossarm damage or failure - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 10.d. | Insulator damage or failure- Transmission | Yes | 3 | 0 | 2 | 2 | 1 | 1 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 2 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 10.e. | Lightning arrestor damage or failure- Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 10.f. | Tap damage or failure - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 10.g. | Tie wire damage or failure - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 10.h. | Other - Transmission | Yes | 5 | 2 | 15 | 2 | 3 | 2 | 0 | 1 | 0 | 4 | 1 | 1 | 0 | 2 | 0 | 1 | 0 | # risk events (excluding ignitions) | Pole & Line Switch failures; does not exclude events that led to CPUC reportable ignition
|  | 11. Wire-to-wire contact - Transmission | 11.a. | Wire-to-wire contact / contamination- Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 12. Contamination - Transmission | 12.a. | Contamination - Transmission | Yes | 2 | 0 | 1 | 1 | 2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 13. Utility work / Operation | 13.a. | Utility work / Operation | No | 1 | 0 | 1 | 1 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 14. Vandalism / Theft - Transmission | 14.a. | Vandalism / Theft - Transmission | Yes | 1 | 3 | 4 | 2 | 4 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 15. Other- Transmission | 15.a. | All Other- Transmission | Yes | 7 | 4 | 11 | 7 | 6 | 1 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 1 | 0 | 3 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 16. Unknown- Transmission | 16.a. | Unknown - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
x | Outage - Distribution | 17. Contact from object - Distribution | 17.a. | Veg. contact- Distribution | Yes | 3760 | 4432 | 8277 | 3361 | 8198 | 1665 | 823 | 863 | 674 | 2629 | 681 | 856.7121 | 669.0892 | 1639.7405 | 810.5144 | 849.9075 | 663.7748 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition. Q4 2020 includes minor updates based on post outage reviews.
|  |  | 17.b. | Animal contact- Distribution | Yes | 2354 | 2242 | 2197 | 2448 | 2071 | 402 | 648 | 632 | 757 | 495 | 783 | 629.6087 | 754.1357 | 398.6968 | 642.6754 | 626.8069 | 750.7797 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 17.c. | Balloon contact- Distribution | Yes | 476 | 526 | 526 | 647 | 465 | 105 | 214 | 158 | 129 | 152 | 303 | 158 | 129 | 105 | 214 | 158 | 129 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition. Q4 2020 includes minor updates based on post outage reviews.
|  |  | 17.d. | Vehicle contact- Distribution | Yes | 1819 | 2041 | 1917 | 1917 | 1837 | 418 | 592 | 567 | 544 | 463 | 575 | 567 | 544 | 418 | 592 | 567 | 544 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition. Q4 2020 includes minor updates based on post outage reviews.
|  |  | 17.e. | Other contact from object - Distribution | Yes | 729 | 645 | 629 | 693 | 735 | 158 | 184 | 181 | 185 | 185 | 222 | 181 | 185 | 158 | 184 | 181 | 185 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 18. Equipment / facility failure - Distribution | 18.a. | Capacitor bank damage or failure- Distribution | Yes | 57 | 65 | 83 | 55 | 70 | 7 | 22 | 17 | 21 | 20 | 20 | 16.9059 | 20.8838 | 6.9145 | 21.7313 | 16.7924 | 20.7435 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.b. | Conductor damage or failure — Distribution | Yes | 1281 | 1359 | 2063 | 1238 | 1926 | 384 | 281 | 297 | 322 | 807 | 346 | 295.356 | 320.2177 | 379.3099 | 277.5679 | 293.3725 | 318.0672 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition. Q4 2020 includes minor updates based on post outage reviews.
|  |  | 18.c. | Fuse damage or failure - Distribution | Yes | 373 | 352 | 479 | 305 | 341 | 48 | 84 | 190 | 125 | 171 | 154 | 188.9483 | 124.3081 | 47.4137 | 82.974 | 187.6794 | 123.4733 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.d. | Lightning arrestor damage or failure- Distribution | Yes | 144 | 145 | 139 | 135 | 131 | 26 | 42 | 31 | 46 | 36 | 28 | 30.8284 | 45.7454 | 25.6824 | 41.487 | 30.6214 | 45.4382 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.e. | Switch damage or failure- Distribution | Yes | 141 | 156 | 178 | 188 | 188 | 30 | 50 | 44 | 35 | 53 | 56 | 43.7565 | 34.8063 | 29.6336 | 49.3893 | 43.4626 | 34.5725 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.f. | Pole damage or failure - Distribution | Yes | 502 | 628 | 1111 | 665 | 1149 | 193 | 210 | 173 | 247 | 403 | 231 | 172.0424 | 245.6328 | 190.6427 | 207.4351 | 170.887 | 243.9832 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.g. | Insulator and brushing damage or failure - Distribution | Yes | 253 | 295 | 384 | 272 | 375 | 74 | 86 | 66 | 84 | 132 | 84 | 65.6347 | 83.535 | 73.0962 | 84.9496 | 65.1939 | 82.974 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.h. | Crossarm damage or failure - Distribution | Yes | 573 | 717 | 777 | 771 | 995 | 207 | 190 | 179 | 253 | 296 | 253 | 178.0092 | 251.5996 | 204.4717 | 187.6794 | 176.8137 | 249.9099 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.i. | Voltage regulator / booster damage or failure - Distribution | Yes | 59 | 62 | 59 | 52 | 59 | 13 | 22 | 17 | 16 | 12 | 25 | 16.9059 | 15.9114 | 12.8412 | 21.7313 | 16.7924 | 15.8046 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.j. | Recloser damage or failure - Distribution | Yes | 61 | 60 | 102 | 90 | 112 | 12 | 10 | 19 | 15 | 36 | 20 | 18.8948 | 14.917 | 11.8534 | 9.8779 | 18.7679 | 14.8168 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.k. | Anchor / guy damage or failure - Distribution | Yes | 36 | 41 | 47 | 47 | 57 | 14 | 9 | 19 | 14 | 23 | 10 | 18.8948 | 13.9225 | 13.829 | 8.8901 | 18.7679 | 13.829 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.l. | Sectionalizer damage or failure - Distribution | Yes | 4 | 3 | 2 | 4 | 3 | 0 | 0 | 2 | 0 | 3 | 2 | 1.9889 | 0 | 0 | 0 | 1.9756 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.m. | Connection device damage or failure - Distribution | Yes | 1210 | 1250 | 1687 | 1095 | 1386 | 322 | 264 | 264 | 325 | 558 | 362 | 262.5387 | 323.2011 | 318.0672 | 260.7756 | 260.7756 | 321.0305 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition. Q4 2020 includes minor updates based on post outage reviews.
|  |  | 18.n. | Transformer damage or failure - Distribution | Yes | 4224 | 3947 | 4977 | 3136 | 3969 | 728 | 1104 | 1856 | 1088 | 1206 | 1296 | 1845.7266 | 1081.9777 | 719.1084 | 1090.516 | 1833.3312 | 1074.7114 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 18.o. | Other - Distribution | Yes | 2241 | 2426 | 2612 | 2094 | 2242 | 376 | 529 | 640 | 448 | 650 | 656 | 636.4575 | 445.5202 | 371.4076 | 522.5389 | 632.1832 | 442.5282 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition. Q4 2020 includes minor updates based on post outage reviews.
|  | 19. Wire-to-wire contact - Distribution | 19.a. | Wire-to-wire contact / contamination- Distribution | Yes | 4900 | 5239 | 6731 | 5276 | 6732 | 1700 | 1178 | 1087 | 1383 | 2408 | 1257 | 1087 | 1383 | 1700 | 1178 | 1087 | 1383 | # risk events (excluding ignitions) | PG&E uses contamination more as a condition of the equipment and not normally as a basic cause. Assumed this cause refers to a Basic Cause of "Unknown" and a Fault Type of "Line to Line". This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition. Q4 2020 includes minor updates based on post outage reviews.
|  | 20. Contamination - Distribution | 20.a. | Contamination - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | PG&E typically uses contamination as a condition of the equipment and not normally as a basic cause.
|  | 21. Utility work / Operation | 21.a. | Utility work / Operation | No | 431 | 650 | 793 | 680 | 886 | 185 | 240 | 240 | 204 | 293 | 245 | 234.6987 | 199.4939 | 180.8624 | 234.6323 | 234.6323 | 199.4375 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 22. Vandalism / Theft - Distribution | 22.a. | Vandalism / Theft - Distribution | Yes | 45 | 26 | 26 | 58 | 44 | 10 | 13 | 17 | 16 | 13 | 12 | 16.8639 | 15.872 | 9.8433 | 12.7963 | 16.7337 | 15.7493 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 23. Other- Distribution | 23.a. | All Other- Distribution | Yes | 1818 | 752 | 1488 | 1232 | 978 | 111 | 255 | 1402 | 95 | 181 | 184 | 1395.7777 | 94.5784 | 109.9302 | 252.5423 | 1388.4873 | 94.0844 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition. Q4 2020 includes minor updates based on post outage reviews.
|  | 24. Unknown- Distribution | 24.a. | Unknown - Distribution | Yes | 7974 | 8185 | 12158 | 6726 | 9503 | 1978 | 1715 | 1971 | 2137 | 3809 | 2431 | 1962.2524 | 2127.5156 | 1958.9357 | 1698.4705 | 1952.0032 | 2116.4032 | # risk events (excluding ignitions) | Omits the outages reported with an unknown cause that are shown in the row above for wire-to-wire contacts. This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition. Q4 2020 includes minor updates based on post outage reviews.
x | Outage - Transmission | 25. Contact from object - Transmission | 25.a. | Veg. contact- Transmission | Yes | 57 | 50 | 141 | 27 | 76 | 21 | 1 | 0 | 3 | 36 | 0 | 0 | 3 | 21 | 1 | 0 | 3 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 25.b. | Animal contact- Transmission | Yes | 56 | 58 | 65 | 58 | 44 | 15 | 8 | 11 | 13 | 0 | 14 | 11 | 13 | 15 | 8 | 11 | 13 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 25.c. | Balloon contact- Transmission | Yes | 13 | 8 | 14 | 20 | 12 | 4 | 5 | 6 | 1 | 2 | 6 | 6 | 1 | 4 | 5 | 6 | 1 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 25.d. | Vehicle contact- Transmission | Yes | 61 | 66 | 69 | 79 | 49 | 18 | 14 | 17 | 24 | 23 | 23 | 17 | 24 | 18 | 14 | 17 | 24 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 25.e. | Other contact from object - Transmission | Yes | 34 | 22 | 20 | 14 | 26 | 2 | 5 | 19 | 2 | 9 | 3 | 19 | 2 | 2 | 5 | 19 | 2 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 26. Equipment / facility failure - Transmission | 26.a. | Capacitor bank damage or failure- Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.b. | Conductor damage or failure — Transmission | Yes | 14 | 29 | 23 | 24 | 53 | 16 | 3 | 5 | 15 | 26 | 4 | 5 | 15 | 16 | 3 | 5 | 15 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.c. | Fuse damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.d. | Lightning arrestor damage or failure- Transmission | Yes | 0 | 2 | 1 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 1 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.e. | Switch damage or failure- Transmission | Yes | 67 | 24 | 25 | 17 | 34 | 8 | 6 | 5 | 3 | 4 | 7 | 5 | 3 | 8 | 6 | 5 | 3 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.f. | Pole damage or failure - Transmission | Yes | 27 | 15 | 53 | 42 | 68 | 7 | 7 | 8 | 5 | 19 | 4 | 8 | 5 | 7 | 7 | 8 | 5 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.g. | Insulator and brushing damage or failure - Transmission | Yes | 51 | 75 | 78 | 86 | 65 | 19 | 40 | 26 | 33 | 11 | 16 | 26 | 33 | 19 | 40 | 26 | 33 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.h. | Crossarm damage or failure - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.i. | Voltage regulator / booster damage or failure - Transmission | Yes | 5 | 7 | 8 | 1 | 6 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.j. | Recloser damage or failure - Transmission | Yes | 36 | 30 | 44 | 29 | 29 | 10 | 4 | 12 | 9 | 5 | 8 | 12 | 9 | 10 | 4 | 12 | 9 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.k. | Anchor / guy damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 2 | 1 | 0 | 0 | 2 | 1 | 1 | 2 | 2 | 1 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.l. | Sectionalizer damage or failure - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.m. | Connection device damage or failure - Transmission | Yes | 19 | 37 | 32 | 18 | 51 | 3 | 16 | 24 | 8 | 3 | 2 | 24 | 8 | 3 | 16 | 24 | 8 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.n. | Transformer damage or failure - Transmission | Yes | 1 | 6 | 0 | 2 | 9 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  |  | 26.o. | Other - Transmission | Yes | 63 | 45 | 56 | 40 | 49 | 12 | 19 | 7 | 9 | 13 | 4 | 7 | 9 | 12 | 19 | 7 | 9 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 27. Wire-to-wire contact - Transmission | 27.a. | Wire-to-wire contact / contamination- Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 28. Contamination - Transmission | 28.a. | Contamination - Transmission | Yes | 22 | 18 | 25 | 51 | 17 | 6 | 13 | 9 | 6 | 4 | 16 | 9 | 6 | 6 | 13 | 9 | 6 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 29. Utility work / Operation | 29.a. | Utility work / Operation | No | 51 | 36 | 50 | 76 | 451 | 25 | 56 | 70 | 109 | 77 | 122 | 70 | 109 | 25 | 56 | 70 | 109 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 30. Vandalism / Theft - Transmission | 30.a. | Vandalism / Theft - Transmission | Yes | 7 | 10 | 9 | 5 | 21 | 2 | 2 | 4 | 1 | 1 | 1 | 4 | 1 | 2 | 2 | 4 | 1 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 31. Other- Transmission | 31.a. | All Other- Transmission | Yes | 436 | 138 | 388 | 168 | 314 | 93 | 57 | 163 | 25 | 115 | 26 | 163 | 25 | 93 | 57 | 163 | 25 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
|  | 32. Unknown- Transmission | 32.a. | Unknown - Transmission | Yes | 158 | 158 | 168 | 187 | 162 | 26 | 34 | 36 | 34 | 45 | 25 | 36 | 34 | 26 | 34 | 36 | 34 | # risk events (excluding ignitions) | This data includes those risk events that may have contributed to ignition events; PG&E’s datasets do not provide the level of detail needed to precisely exclude the outages or wire down events that led to an ignition.
x | Ignition - Distribution | 33. Contact from object - Distribution | 33.a. | Veg. contact- Distribution | Yes | 106 | 108 | 177 | 124 | 136 | 10 | 38 | 54 | 25 | 32 | 45 | 53.4274 | 24.7349 | 9.7789 | 37.1598 | 52.8061 | 24.4473 | # ignitions
|  |  | 33.b. | Animal contact- Distribution | Yes | 54 | 41 | 62 | 54 | 67 | 3 | 15 | 21 | 6 | 5 | 16 | 20.9131 | 5.9752 | 2.9731 | 14.8655 | 20.8117 | 5.9462 | # ignitions
|  |  | 33.c. | Balloon contact- Distribution | Yes | 23 | 13 | 11 | 13 | 15 | 0 | 5 | 5 | 4 | 1 | 10 | 4.9854 | 3.9884 | 0 | 4.9685 | 4.9685 | 3.9748 | # ignitions
|  |  | 33.d. | Vehicle contact- Distribution | Yes | 47 | 36 | 55 | 28 | 36 | 4 | 18 | 24 | 9 | 3 | 14 | 23.9043 | 8.9641 | 3.9654 | 17.8445 | 23.7927 | 8.9223 | # ignitions
|  |  | 33.e. | Other contact from object - Distribution | Yes | 1 | 1 | 2 | 50 | 20 | 2 | 16 | 6 | 1 | 2 | 16 | 5.9722 | 0.99536 | 1.9799 | 15.8392 | 5.9397 | 0.98995 | # ignitions
|  | 34. Equipment / facility failure - Distribution | 34.a. | Capacitor bank damage or failure- Distribution | Yes | 14 | 12 | 13 | 8 | 7 | 0 | 5 | 2 | 0 | 0 | 2 | 1.9991 | 0 | 0 | 4.995 | 1.998 | 0 | # ignitions
|  |  | 34.b. | Conductor damage or failure — Distribution | Yes | 47 | 59 | 73 | 40 | 82 | 4 | 28 | 20 | 19 | 13 | 27 | 19.9298 | 18.9333 | 3.9696 | 27.7872 | 19.848 | 18.8556 | # ignitions
|  |  | 34.c. | Fuse damage or failure - Distribution | Yes | 8 | 7 | 10 | 2 | 5 | 1 | 2 | 7 | 1 | 0 | 2 | 6.9571 | 0.99388 | 0.98702 | 1.974 | 6.9091 | 0.98702 | # ignitions
|  |  | 34.d. | Lightning arrestor damage or failure- Distribution | Yes | 7 | 3 | 6 | 1 | 3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.60821 | 0 | 0 | # ignitions
|  |  | 34.e. | Switch damage or failure- Distribution | Yes | 3 | 3 | 4 | 1 | 2 | 0 | 1 | 2 | 0 | 0 | 3 | 2 | 0 | 0 | 1 | 2 | 0 | # ignitions
|  |  | 34.f. | Pole damage or failure - Distribution | Yes | 6 | 7 | 13 | 11 | 6 | 0 | 5 | 3 | 4 | 2 | 4 | 2.9934 | 3.9911 | 0 | 4.976 | 2.9856 | 3.9808 | # ignitions
|  |  | 34.g. | Insulator and brushing damage or failure - Distribution | Yes | 7 | 4 | 9 | 5 | 4 | 0 | 1 | 2 | 3 | 1 | 0 | 1.9956 | 2.9934 | 0 | 0.99523 | 1.9905 | 2.9857 | # ignitions
|  |  | 34.h. | Crossarm damage or failure - Distribution | Yes | 5 | 8 | 13 | 2 | 2 | 0 | 1 | 1 | 0 | 0 | 5 | 0.99494 | 0 | 0 | 0.98904 | 0.98904 | 0 | # ignitions
|  |  | 34.i. | Voltage regulator / booster damage or failure - Distribution | Yes | 5 | 1 | 4 | 0 | 2 | 0 | 2 | 2 | 0 | 0 | 1 | 1.9944 | 0 | 0 | 1.9878 | 1.9878 | 0 | # ignitions
|  |  | 34.j. | Recloser damage or failure - Distribution | Yes | 0 | 3 | 3 | 0 | 3 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | # ignitions
|  |  | 34.k. | Anchor / guy damage or failure - Distribution | Yes | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.98574 | 0 | 0 | 0 | # ignitions
|  |  | 34.l. | Sectionalizer damage or failure - Distribution | Yes | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 34.m. | Connection device damage or failure - Distribution | Yes | 44 | 24 | 39 | 3 | 1 | 0 | 13 | 15 | 9 | 2 | 22 | 14.9482 | 8.9689 | 0 | 12.9029 | 14.8879 | 8.9327 | # ignitions
|  |  | 34.n. | Transformer damage or failure - Distribution | Yes | 18 | 13 | 23 | 18 | 20 | 1 | 6 | 14 | 0 | 2 | 2 | 13.9522 | 0 | 0.99261 | 5.9556 | 13.8965 | 0 | # ignitions
|  |  | 34.o. | Other - Distribution | Yes | 38 | 26 | 29 | 42 | 27 | 1 | 8 | 7 | 8 | 3 | 11 | 6.981 | 7.9783 | 0.99412 | 7.953 | 6.9589 | 7.953 | # ignitions
|  | 35. Wire-to-wire contact - Distribution | 35.a. | Wire-to-wire contact / contamination- Distribution | Yes | 4 | 2 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 36. Contamination - Distribution | 36.a. | Contamination - Distribution | Yes | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 4 | 0 | 0 | 0 | 4 | 0 | 1 | 0 | 4 | # ignitions
|  | 37. Utility work / Operation | 37.a. | Utility work / Operation | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 38. Vandalism / Theft - Distribution | 38.a. | Vandalism / Theft - Distribution | Yes | 6 | 2 | 4 | 0 | 1 | 0 | 0 | 2 | 1 | 1 | 2 | 2 | 1 | 0 | 0 | 2 | 1 | # ignitions
|  | 39. Other- Distribution | 39.a. | All Other- Distribution | Yes | 1 | 6 | 1 | 8 | 6 | 0 | 1 | 3 | 4 | 0 | 0 | 2.9893 | 3.9857 | 0 | 0.99225 | 2.9768 | 3.969 | # ignitions
|  | 40. Unknown- Distribution | 40.a. | Unknown - Distribution | Yes | 1 | 1 | 4 | 25 | 14 | 0 | 1 | 0 | 0 | 2 | 9 | 0 | 0 | 0 | 0.98997 | 0 | 0 | # ignitions
x | Ignition - Transmission | 41. Contact from object - Transmission | 41.a. | Veg. contact- Transmission | Yes | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | # ignitions
|  |  | 41.b. | Animal contact- Transmission | Yes | 7 | 9 | 11 | 12 | 8 | 0 | 0 | 7 | 1 | 0 | 0 | 7 | 1 | 0 | 0 | 7 | 1 | # ignitions
|  |  | 41.c. | Balloon contact- Transmission | Yes | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | # ignitions
|  |  | 41.d. | Vehicle contact- Transmission | Yes | 0 | 1 | 1 | 3 | 4 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | # ignitions
|  |  | 41.e. | Other contact from object - Transmission | Yes | 0 | 0 | 0 | 3 | 2 | 0 | 2 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 1 | 0 | # ignitions
|  | 42. Equipment / facility failure - Transmission | 42.a. | Capacitor bank damage or failure- Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 42.b. | Conductor damage or failure — Transmission | Yes | 1 | 3 | 3 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 2 | 1 | 1 | 0 | 0 | 1 | 1 | # ignitions
|  |  | 42.c. | Fuse damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 42.d. | Lightning arrestor damage or failure- Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 42.e. | Switch damage or failure- Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 42.f. | Pole damage or failure - Transmission | Yes | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 42.g. | Insulator and brushing damage or failure - Transmission | Yes | 1 | 0 | 2 | 1 | 2 | 0 | 0 | 2 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 2 | 0 | # ignitions
|  |  | 42.h. | Crossarm damage or failure - Transmission | Yes | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 42.i. | Voltage regulator / booster damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | # ignitions
|  |  | 42.j. | Recloser damage or failure - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 42.k. | Anchor / guy damage or failure - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 42.l. | Sectionalizer damage or failure - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 42.m. | Connection device damage or failure - Transmission | Yes | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 42.n. | Transformer damage or failure - Transmission | Yes | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 42.o. | Other - Transmission | Yes | 3 | 1 | 3 | 3 | 3 | 0 | 0 | 1 | 3 | 0 | 4 | 1 | 3 | 0 | 0 | 1 | 3 | # ignitions
|  | 43. Wire-to-wire contact - Transmission | 43.a. | Wire-to-wire contact / contamination- Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 44. Contamination - Transmission | 44.a. | Contamination - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | # ignitions
|  | 45. Utility work / Operation | 45.a. | Utility work / Operation | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 46. Vandalism / Theft - Transmission | 46.a. | Vandalism / Theft - Transmission | Yes | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 47. Other- Transmission | 47.a. | All Other- Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | # ignitions
|  | 48. Unknown- Transmission | 48.a. | Unknown - Transmission | Yes | 0 | 0 | 0 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
Updated comments for Table 7.1 (5/3/2021): 1) PG&E’s Electric Incident Investigation (EII) team is conducting a system of record audit for ignition events. The updated counts in Table 7.1 represent the events known to PG&E at the time of filing but are subject to change as the audit progresses. Changes are reflected in Purple font. 2) 7.1 Q1 2021 values are based on actuals. Projections from Q2 2021 - Q4 2022 are based on the respective 2020 values. Updated comments for Table 7.1 (3/17/2021): PG&E’s Electric Incident Investigation (EII) team is conducting a system of record audit for ignition events. The updated counts in Table 7.1 represent the events known to PG&E at the time of filing but are subject to change as the audit progresses. Changes are reflected in Red font. Original Comments for Table 7.1: The fire ignition data provided in this table is based on fire incident reports filed with the CPUC annually in accordance with D.14-02-015. The ignition data provided in these tables was pulled from PG&E’s systems in mid-January 2021 and reflects preliminary data for two reasons: first, PG&E’s final 2020 fire ignition report is due on April 1, 2021 and 2020 data will be further reviewed in advance of that filing. Second, in late 2020 PG&E self-identified a data omission regarding prior year’s fire ignition data in the annual reports submitted and notified the CPUC of this issue on December 23, 2020. We anticipate completing an investigation into this issue to determine any fire ignition data that were omitted from our 2014-2019 reports by the end of the first quarter of 2021. Based on the results of our investigation, we plan to submit amendments to our annual reports and provide a supplemental filing updating the ignition data in Tables 7.1 and 7.2. More detail is provided in WMP Section 6.7 discussion.
Comments for Table 7.1: Key Recent and Projected Drivers of Ignition Probability, Last 5 Years (Distribution System): To the extent available, PG&E’s Integrated Logging Information System – Operations Data Base (ILIS-ODB) was used to provide the level of detail contained in Table 7.1 (Distribution) that includes both sustained and momentary outages experienced on our distribution system. When reviewing this data, the following should be noted: · Based on PG&E’s standard definition, a distribution wire down event results in a reportable outage event and occurs when a normally energized electric primary distribution conductor is broken, or stays intact, and falls from its intended position to rest on the ground or a foreign object. PG&E used this standard definition in this year’s report and thus it does not include any secondary related wire down events. However, it should also be noted that any primary or secondary wire down condition that resulted in an outage event is also reported in the distribution outage results. · In our 2020 WMP, PG&E utilized a different data extraction method attempting to identify a larger number of distribution wire down event conditions. However, it was subsequently determined this method resulted in an erroneously higher number of distribution wire down events due to various data issues such as momentary outages resulting from the same wire down event/condition that was also reported as a sustained outage. · For sub-cause category 2.a.”Connector damage or failure – Distribution,” it was assumed that the word “Connector” was meant to indicate “Conductor” since connector damage would typically be reported as splice damage. · For sub-cause category 8.a. “Unknown – Distribution,” this generally does not apply to distribution wire down events. · PG&E was unsure what was intended by the use of the term “Fuse damage or failure” because when a fuse isolates a fault condition, it will become permanently damaged and by design will no longer conduct electricity. For this subcategory, PG&E has interpreted it as only those outage events when a fuse was reported as the actual failed equipment. · PG&E does not have an outage cause classification that specifically matches the terms, “Tap damage or failure – Distribution” and “Tie wire damage or failure – Distribution” and thus did not use these categories in this report. · For “Wire-to-wire contact/Contamination,” PG&E typically does not use this term for distribution wire down events. In addition, PG&E typically uses contamination more as a condition of the equipment and not normally as a basic cause. For this category under the Distribution outages, PG&E assumed this cause refers to a Basic Cause of “Unknown” and a Fault Type of “Line to Line.” · For “Contamination – Distribution,” PG&E uses contamination more as a condition of the equipment and not as a basic cause. As such, PG&E does not have an outage classification that matches this term. · For “Unknown – Distribution” outages, this category omits outages reported with a Basic Cause of “Unknown” and a Fault Type of “Line to Line” covered as “Wire-to-wire contact/Contamination” outages noted in the above bullet item. · Due to their relatively small contribution, the Commission does not require transformer-only outages be reported in the annual electric system reliability metrics. However, transformer-only outages are reported within PG&E’s Field Automation System (FAS) and most were also reported in PG&E’s ILIS-ODB outage data base. PG&E is including these transformer-only outages in the WMP reporting to reflect the full picture of outage incidents which could have represented ignition potential. PG&E also further enhanced our reporting process/controls in September 2020 to ensure future transformer-only outages are fully reported in our ILIS-ODB outage data base and is working to improve outage cause reporting. · In Table 7.1 (Distribution), columns under the category ‘Projected risk events’ depict the projections in the respective years. Projections are based on forecasts submitted in the 2020 RAMP Report.
Comments for Table 7.1: Key Recent and Projected Drivers of Ignition Probability, Last 5 Years (Transmission System): PG&E’s Transmission Operations Tracking & Logging (TOTL) application was used as the primary data source for Table 7.1 (Transmission) which includes unplanned outages experienced on the transmission (i.e., >50 kV) system. Unplanned outages include those due to an “automatic” operation (i.e., the transmission line relayed automatically by a protective device (typically a circuit breaker) and either automatically tested OK, tested no good, or was set up not to test (e.g., automatics disabled or cut out for wildfire risk mitigation)). Unplanned outages also include those where the line was manually removed from service by Operations on an “emergency” basis, usually to repair or replace an imminent failure of an asset. Such emergency forced outages (EFOs) are taken without securing approval from the California Independent System Operator (CAISO). Planned or “scheduled” outages are not included. Scheduled outages differ from EFOs in that PG&E garnered CAISO approval prior to the line being removed from service. Based on PG&E’s standard definition, a transmission wire down event (similar to distribution) results in a reportable outage event (note: customers may or may not have been de-energized) and occurs when a normally energized electric transmission conductor fails in service and falls from its intended position to rest on the ground or a foreign object. • Sub-cause category 10.a. “Connector damage or failure – Transmission,” PG&E assumed that the word “Connector” was meant to indicate “Conductor” since connector damage would be reported separately in 10.b. • Sub-cause category 10.f. “Tap damage or failure – Transmission,” PG&E does not have an outage cause classification that specifically matches such. • Sub-cause category 10.g. “Tie wire damage or failure – Transmission” does not exist in PG&E outage reporting. • Sub-cause category 11.a. and 27.a. “Wire-to-wire contact/Contamination-Transmission” does not exist in PG&E transmission outage reporting and therefore has no data entries. • Unlike distribution outage reporting, cause category “Contamination – Transmission” is tracked and reported accordingly. • Every effort is made to minimize the number of outages assigned a cause category “Unknown – Transmission” for automatic type outages. At least one and sometimes more patrols are conducted after the outage to determine cause and certainly to find and correct any damaged equipment, usually with the help of fault location data provided by System Protection to help focus on the failure point. It’s also important to note that any outage due to animal contact is one where the patrol found a carcass to support the cause of animal, otherwise the choice “Unknown” is used. • Sub-cause category 26.c. “Fuse damage or failure” has no meaning for unplanned transmission outages. • Sub-cause category 26.h. “Crossarm damage or failure – Transmission” is not separately reported but included as part of reporting in the Sub-cause category “Pole damage or failure – Transmission,” if applicable. • Sub-cause category 26.j. “Recloser damage or failure – Transmission” represents outages where a circuit breaker failed in service and led to an outage. • Sub-cause category 26.l. “Sectionalizer damage or failure – Transmission” has no entries; rather, transmission lines are sectionalized using line switches, hence such failures are captured in cause Category 26.e. “Switch damage or failure- Transmission.” • In Table 7.1 (Transmission), columns under the category ‘Projected risk events’ depict the projections in the respective years. Projections are based on forecasts submitted in the 2020 RAMP Report.

## Table 7.2
| Utility | Pacific Gas & Electric Company | Notes:
| Table No. | 7.2 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV. |  | l
| Date Modified | 2021-08-02 | Data from 2015 - 2019 should be actual numbers. 2020 - 2023 should be projected. In future submissions update projected numbers with actuals
[6 empty] | Number of ignitions by HFTD tier | [23 empty] | 2021 numbers are Q1-Q2 actuals |  |  |  | Projected yearly ignitions by HFTD tier
| Table 7.2: Key recent and projected drivers of ignitions by HFTD region |  |  |  |  | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3
|  | Metric type | # | Ignition driver | Are ignitions tracked for ignition driver? (yes / no) | 2015 | 2015 | 2015 | 2015 | 2016 | 2016 | 2016 | 2016 | 2017 | 2017 | 2017 | 2017 | 2018 | 2018 | 2018 | 2018 | 2019 | 2019 | 2019 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
x | Ignition - Distribution | 1. Contact from object - Distribution | 1.a. | Veg. contact- Distribution | Yes | 44 | 1 | 38 | 23 | 45 | 0 | 40 | 23 | 76 | 0 | 61 | 40 | 56 | 0 | 32 | 36 | 74 | 0 | 48 | 16 | 63 | 0 | 37 | 27 | 37 | 1 | 18 | 21 | 63 | 0 | 35.4454 | 25.8656 | # ignitions
|  |  | 1.b. | Animal contact- Distribution | Yes | 48 | 0 | 11 | 2 | 38 | 0 | 10 | 2 | 56 | 0 | 14 | 3 | 42 | 0 | 16 | 8 | 63 | 0 | 11 | 1 | 36 | 0 | 9 | 0 | 17 | 0 | 4 | 0 | 36 | 0 | 8.6152 | 0 | # ignitions
|  |  | 1.c. | Balloon contact- Distribution | Yes | 19 | 0 | 4 | 0 | 12 | 0 | 2 | 0 | 11 | 0 | 0 | 1 | 10 | 0 | 3 | 0 | 16 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 10 | 0 | 1 | 0 | 14 | 0 | 0 | 0 | # ignitions
|  |  | 1.d. | Vehicle contact- Distribution | Yes | 37 | 0 | 9 | 1 | 24 | 0 | 13 | 0 | 41 | 0 | 11 | 4 | 21 | 0 | 8 | 2 | 35 | 0 | 5 | 0 | 42 | 0 | 10 | 3 | 14 | 0 | 3 | 0 | 42 | 0 | 9.6982 | 2.9095 | # ignitions
|  |  | 1.e. | Other contact from object - Distribution | Yes | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 34 | 0 | 11 | 8 | 16 | 0 | 5 | 1 | 19 | 0 | 6 | 0 | 14 | 0 | 4 | 0 | 19 | 0 | 5.844 | 0 | # ignitions
|  | 2. Equipment / facility failure - Distribution | 2.a. | Capacitor bank damage or failure- Distribution | Yes | 12 | 0 | 2 | 0 | 10 | 0 | 1 | 1 | 11 | 0 | 1 | 1 | 5 | 0 | 1 | 2 | 7 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | # ignitions
|  |  | 2.b. | Conductor damage or failure — Distribution | Yes | 35 | 0 | 10 | 3 | 46 | 0 | 10 | 6 | 57 | 0 | 16 | 3 | 27 | 0 | 11 | 2 | 68 | 0 | 11 | 4 | 63 | 0 | 8 | 0 | 32 | 0 | 7 | 1 | 63 | 0 | 7.7444 | 0 | # ignitions
|  |  | 2.c. | Fuse damage or failure - Distribution | Yes | 5 | 0 | 2 | 1 | 7 | 0 | 0 | 0 | 8 | 0 | 2 | 0 | 2 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 7 | 0 | 2 | 2 | 2 | 0 | 0 | 0 | 6.9775 | 0 | 1.9085 | 1.9085 | # ignitions
|  |  | 2.d. | Lightning arrestor damage or failure- Distribution | Yes | 6 | 0 | 1 | 0 | 3 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.61462 | 0 | 0 | 0 | # ignitions
|  |  | 2.e. | Switch damage or failure- Distribution | Yes | 3 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | # ignitions
|  |  | 2.f. | Pole damage or failure - Distribution | Yes | 4 | 0 | 1 | 1 | 5 | 0 | 2 | 0 | 12 | 0 | 2 | 0 | 7 | 0 | 4 | 0 | 6 | 0 | 0 | 1 | 8 | 0 | 4 | 0 | 5 | 0 | 1 | 0 | 8 | 0 | 3.8604 | 0 | # ignitions
|  |  | 2.g. | Insulator and brushing damage or failure - Distribution | Yes | 7 | 0 | 1 | 0 | 4 | 0 | 0 | 0 | 9 | 0 | 2 | 0 | 5 | 0 | 0 | 1 | 3 | 0 | 2 | 1 | 4 | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 4 | 0 | 1.9151 | 0 | # ignitions
|  |  | 2.h. | Crossarm damage or failure - Distribution | Yes | 5 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 5 | 0 | 5 | 3 | 2 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 4 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | # ignitions
|  |  | 2.i. | Voltage regulator / booster damage or failure - Distribution | Yes | 2 | 0 | 3 | 0 | 0 | 0 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 3 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 3 | 0 | 0.97756 | 0 | # ignitions
|  |  | 2.j. | Recloser damage or failure - Distribution | Yes | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | # ignitions
|  |  | 2.k. | Anchor / guy damage or failure - Distribution | Yes | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | # ignitions
|  |  | 2.l. | Sectionalizer damage or failure - Distribution | Yes | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 2.m. | Connection device damage or failure - Distribution | Yes | 39 | 1 | 2 | 2 | 20 | 0 | 3 | 1 | 29 | 0 | 9 | 2 | 2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 29 | 0 | 8 | 0 | 20 | 0 | 4 | 0 | 29 | 0 | 7.6548 | 0 | # ignitions
|  |  | 2.n. | Transformer damage or failure - Distribution | Yes | 15 | 0 | 4 | 0 | 11 | 0 | 2 | 0 | 18 | 1 | 3 | 1 | 11 | 0 | 2 | 5 | 19 | 0 | 1 | 0 | 15 | 0 | 6 | 0 | 4 | 0 | 0 | 0 | 15 | 0 | 5.7271 | 0 | # ignitions
|  |  | 2.o. | Other - Distribution | Yes | 32 | 0 | 4 | 5 | 21 | 0 | 3 | 3 | 23 | 0 | 5 | 4 | 26 | 0 | 12 | 7 | 25 | 0 | 4 | 1 | 21 | 0 | 3 | 0 | 9 | 0 | 4 | 1 | 21 | 0 | 2.9168 | 0 | # ignitions
|  | 3. Wire-to-wire contact - Distribution | 3.a. | Wire-to-wire contact / contamination- Distribution | Yes | 2 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 4. Contamination - Distribution | 4.a. | Contamination - Distribution | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 2 | 0 | # ignitions
|  | 5. Utility work / Operation | 5.a. | Utility work / Operation | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 6. Vandalism / Theft - Distribution | 6.a. | Vandalism / Theft - Distribution | Yes | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 2 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 3 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | # ignitions
|  | 7. Other- Distribution | 7.a. | All Other- Distribution | Yes | 1 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5 | 0 | 3 | 0 | 4 | 0 | 1 | 1 | 4 | 0 | 2 | 2 | 0 | 0 | 0 | 0 | 4 | 0 | 1.9262 | 1.9262 | # ignitions
|  | 8. Unknown- Distribution | 8.a. | Unknown - Distribution | Yes | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 19 | 0 | 7 | 1 | 13 | 0 | 3 | 0 | 1 | 0 | 0 | 0 | 7 | 0 | 4 | 0 | 1 | 0 | 0 | 0 | # ignitions
x | Ignition - Transmission | 9. Contact from object - Transmission | 9.a. | Veg. contact- Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | # ignitions
|  |  | 9.b. | Animal contact- Transmission | Yes | 3 | 0 | 4 | 0 | 5 | 0 | 4 | 0 | 5 | 0 | 4 | 2 | 5 | 0 | 4 | 3 | 7 | 0 | 1 | 0 | 3 | 0 | 3 | 2 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 2 | # ignitions
|  |  | 9.c. | Balloon contact- Transmission | Yes | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | # ignitions
|  |  | 9.d. | Vehicle contact- Transmission | Yes | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | # ignitions
|  |  | 9.e. | Other contact from object - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | # ignitions
|  | 10. Equipment / facility failure - Transmission | 10.a. | Capacitor bank damage or failure- Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 10.b. | Conductor damage or failure — Transmission | Yes | 0 | 0 | 1 | 0 | 1 | 0 | 2 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | # ignitions
|  |  | 10.c. | Fuse damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 10.d. | Lightning arrestor damage or failure- Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 10.e. | Switch damage or failure- Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 10.f. | Pole damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 10.g. | Insulator and brushing damage or failure - Transmission | Yes | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | # ignitions
|  |  | 10.h. | Crossarm damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 10.i. | Voltage regulator / booster damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | # ignitions
|  |  | 10.j. | Recloser damage or failure - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 10.k. | Anchor / guy damage or failure - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 10.l. | Sectionalizer damage or failure - Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 10.m. | Connection device damage or failure - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 10.n. | Transformer damage or failure - Transmission | Yes | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  |  | 10.o. | Other - Transmission | Yes | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 3 | 0 | 2 | 0 | 1 | 0 | 1 | 0 | 2 | 1 | 2 | 0 | 1 | 1 | 1 | 0 | 2 | 1 | # ignitions
|  | 11. Wire-to-wire contact - Transmission | 11.a. | Wire-to-wire contact / contamination- Transmission | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 12. Contamination - Transmission | 12.a. | Contamination - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | # ignitions
|  | 13. Utility work / Operation | 13.a. | Utility work / Operation | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 14. Vandalism / Theft - Transmission | 14.a. | Vandalism / Theft - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
|  | 15. Other- Transmission | 15.a. | All Other- Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | # ignitions
|  | 16. Unknown- Transmission | 16.a. | Unknown - Transmission | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | # ignitions
Updated comments for Table 7.2 (5/3/2021): 1) PG&E’s Electric Incident Investigation (EII) team is conducting a system of record audit for ignition events. The updated counts in Table 7.2 represent the events known to PG&E at the time of filing but are subject to change as the audit progresses. Changes are reflected in Purple font. 2021 values are based on actuals for Q1. 2022 values are projections for the entire year based on 2020 as baseline. 2) Changes are reflected in Purple font. 2021 values are based on actuals for Q1. 2022 values are projections for the entire year based on 2020 as baseline. Updated comments for Table 7.2 (3/17/2021): PG&E’s Electric Incident Investigation (EII) team is conducting a system of record audit for ignition events. The updated counts in Table 7.2 represent the events known to PG&E at the time of filing but are subject to change as the audit progresses. Changes are reflected in Red font. Original Comments for Table 7.2: The fire ignition data provided in this table is based on fire incident reports filed with the CPUC annually in accordance with D.14-02-015. The ignition data provided in these tables was pulled from PG&E’s systems in mid-January 2021 and reflects preliminary data for two reasons: first, PG&E’s final 2020 fire ignition report is due on April 1, 2021 and 2020 data will be further reviewed in advance of that filing. Second, in late 2020 PG&E self-identified a data omission regarding prior year’s fire ignition data in the annual reports submitted and notified the CPUC of this issue on December 23, 2020. We anticipate completing an investigation into this issue to determine any fire ignition data that were omitted from our 2014-2019 reports by the end of the first quarter of 2021. Based on the results of our investigation, we plan to submit amendments to our annual reports and provide a supplemental filing updating the ignition data in Tables 7.1 and 7.2. More detail is provided in WMP Section 6.7 discussion.

## Table 8
| Utility | Pacific Gas & Electric Company
| Table No. | 8
| Date Modified | 2021-08-02
Note: These columns are placeholders for future QR submissions.
| Table 8: State of service territory and utility equipment |  |  | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3
| Metric type | # | Outcome metric name | 2015 | 2015 | 2015 | 2015 | 2016 | 2016 | 2016 | 2016 | 2017 | 2017 | 2017 | 2017 | 2018 | 2018 | 2018 | 2018 | 2019 | 2019 | 2019 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comments
x | 1. State of service territory and equipment in urban areas | 1.a. | Circuit miles (including WUI and non-WUI) | [16 empty] | 15604 | 9 | 996 | 395 | 16296 | 1 | 1064 | 383 | 15565.0208 | 0.17539 | 996.5036 | 377.8579 |  |  |  |  | Circuit miles | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.b. | Circuit miles in WUI | [16 empty] | 4195 | 8 | 721 | 340 | 4791 | 0 | 754 | 319 | 4631.5248 | 0 | 726.406 | 323.3133 |  |  |  |  | Circuit miles in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.c. | Number of critical facilities (including WUI and non-WUI) | [16 empty] | 17009 | 7 | 442 | 204 | 51008 |  | 1356 | 477 | 52153 |  | 1369 | 484 |  |  |  |  | Number of critical facilities | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.d. | Number of critical facilities in WUI | [16 empty] | 4213 | 5 | 402 | 172 | 13782 |  | 1051 | 421 | 13925 |  | 1058 | 427 |  |  |  |  | Number of critical facilities in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.e. | Number of customers (including WUI and non-WUI) | [16 empty] | 3966386 | 2172 | 76068 | 29274 | 4088697 | 9 | 79518 | 29936 | 4106748 | 9 | 80092 | 30045 |  |  |  |  | Number of customers | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.f. | Number of customers in WUI | [16 empty] | 1165448 | 1943 | 66452 | 27165 | 1195814 | 7 | 68926 | 27751 | 1199487 | 7 | 69505 | 27849 |  |  |  |  | Number of customers in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.g. | Number of customers belonging to access and functional needs populations (including WUI and non-WUI) | [16 empty] | 120605 | 45 | 2084 | 727 | 158034 |  | 3384 | 1198 | 166520 |  | 3631 | 1298 |  |  |  |  | Number of customers belonging to access and functional needs populations | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.h. | Number of customers belonging to access and functional needs populations in WUI | [16 empty] | 38384 | 39 | 1895 | 688 | 51034 |  | 3070 | 1121 | 53827 |  | 3283 | 1212 |  |  |  |  | Number of customers belonging to access and functional needs populations in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.i. | Circuit miles of overhead transmission lines (including WUI and non-WUI) | [16 empty] | 2178.8 | 0 | 226.8 | 62.3 | 2177.9 |  | 226.7 | 61.6 | 2031.5998 |  | 209.102 | 51.5246 |  |  |  |  | Circuit miles of overhead transmission lines | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.j. | Circuit miles of overhead transmission lines in WUI | [16 empty] | 516.9 | 0 | 87.6 | 37.5 | 517 |  | 88.5 | 36.8 | 502.9743 |  | 84.2786 | 34.5686 |  |  |  |  | Circuit miles of overhead transmission lines in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.k. | Circuit miles of overhead distribution lines (including WUI and non-WUI) | [16 empty] | 14141 | 0.5 | 840.6 | 326.9 | 14118 | 0.5 | 836.9 | 321.3 | 13533.421 | 0.17539 | 787.4016 | 326.3333 |  |  |  |  | Circuit miles of overhead distribution lines | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.l. | Circuit miles of overhead distribution lines in WUI | [16 empty] | 4278.7 | 0.4 | 664.1 | 288.2 | 4274.2 | 0.3 | 665.1 | 282.3 | 4128.5506 | 0 | 642.1275 | 288.7447 |  |  |  |  | Circuit miles of overhead distribution lines in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.m. | Number of substations (including WUI and non-WUI) | [16 empty] | 314 | 0 | 18 | 0 | 323 | - | 19 | - | 298 |  | 17 | [5 empty] | Number of substations | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.n | Number of substations in WUI | [16 empty] | 94 | 0 | 14 | 0 | 93 | - | 13 | - | 35 |  | 11 | [5 empty] | Number of substations in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.o. | Number of weather stations (including WUI and non-WUI) | [16 empty] | 1 | 0 | 7 | 3 | 17 | 0 | 17 | 8 | 19 |  | 17 | 8 |  |  |  |  | Number of weather stations | See section 6.5 for a note on why 2015-2018 data is not available
|  | 1.p. | Number of weather stations in WUI | [16 empty] | 0 | 0 | 4 | 3 | 12 | 0 | 10 | 6 | 13 |  | 10 | 6 |  |  |  |  | Number of weather stations in WUI | See section 6.5 for a note on why 2015-2018 data is not available
x | 2. State of service territory and equipment in rural areas | 2.a. | Circuit miles (including WUI and non-WUI) | [16 empty] | 45119 | 87 | 17020 | 7229 | 44489 | 8 | 17321 | 7262 | 45130.8224 | 8.658 | 16886.7296 | 7086.9501 |  |  |  |  | Circuit miles | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.b. | Circuit miles in WUI | [16 empty] | 7962 | 57 | 9479 | 4671 | 7932 | 4 | 10846 | 4698 | 8004.1555 | 4.2102 | 9472.0481 | 4624.7714 |  |  |  |  | Circuit miles in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.c. | Number of critical facilities (including WUI and non-WUI) | [16 empty] | 10134 | 42 | 1857 | 1009 | 19815 | 4 | 5223 | 2683 | 20338 | 4 | 5262 | 2689 |  |  |  |  | Number of critical facilities | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.d. | Number of critical facilities in WUI | [16 empty] | 2532 | 29 | 1153 | 690 | 7228 | 3 | 3471 | 1945 | 7302 | 3 | 3508 | 1954 |  |  |  |  | Number of critical facilities in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.e. | Number of customers (including WUI and non-WUI) | [16 empty] | 1051321 | 3877 | 249888 | 130048 | 974331 | 401 | 250571 | 131232 | 980921 | 404 | 251101 | 131433 |  |  |  |  | Number of customers | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.f. | Number of customers in WUI | [16 empty] | 483462 | 3493 | 116821 | 210802 | 467317 | 368 | 211175 | 117920 | 469036 | 371 | 211912 | 118293 |  |  |  |  | Number of customers in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.g. | Number of customers belonging to access and functional needs populations (including WUI and non-WUI) | [16 empty] | 37116 | 158 | 11161 | 5530 | 43594 | 4 | 14670 | 7127 | 45602 | 4 | 15225 | 7473 |  |  |  |  | Number of customers belonging to access and functional needs populations | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.h. | Number of customers belonging to access and functional needs populations in WUI | [16 empty] | 18815 | 149 | 10055 | 5217 | 23914 | 4 | 13219 | 6729 | 25032 | 5 | 13740 | 7063 |  |  |  |  | Number of customers belonging to access and functional needs populations in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.i. | Circuit miles of overhead transmission lines (including WUI and non-WUI) | [16 empty] | 8747.9 | 3 | 2962.8 | 1095.7 | 8748.4 | 3 | 2962.2 | 1095.5 | 8862.1719 | 3.0302 | 2874.8612 | 1070.1237 |  |  |  |  | Circuit miles of overhead transmission lines | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.j. | Circuit miles of overhead transmission lines in WUI | [16 empty] | 917.8 | 1.3 | 830 | 291 | 917.8 | 1.3 | 829.2 | 290.7 | 913.0444 | 1.3172 | 814.0966 | 284.0796 |  |  |  |  | Circuit miles of overhead transmission lines in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.k. | Circuit miles of overhead distribution lines (including WUI and non-WUI) | [16 empty] | 35771.5 | 5.4 | 14469.7 | 6281.4 | 35740.8 | 5.3 | 14358.9 | 6166.4 | 36268.6505 | 5.6278 | 14011.8684 | 6016.8264 |  |  |  |  | Circuit miles of overhead distribution lines | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.l. | Circuit miles of overhead distribution lines in WUI | [16 empty] | 7008.8 | 2.7 | 8724.8 | 4446.9 | 7013.6 | 2.7 | 8712.9 | 4407.6 | 7091.1111 | 2.893 | 8657.9515 | 4340.6918 |  |  |  |  | Circuit miles of overhead distribution lines in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.m. | Number of substations (including WUI and non-WUI) | [16 empty] | 289 | 0 | 35 | 7 | 351 | 1 | 68 | 26 | 378 | 1 | 102 | 51 |  |  |  |  | Number of substations | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.n | Number of substations in WUI | [16 empty] | 67 | 0 | 27 | 18 | 66 |  | 29 | 19 | 69 |  | 35 | 18 |  |  |  |  | Number of substations in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.o. | Number of weather stations (including WUI and non-WUI) | [16 empty] | 59 | 0 | 250 | 157 | 135 | 0 | 399 | 205 | 164 |  | 470 | 232 |  |  |  |  | Number of weather stations | See section 6.5 for a note on why 2015-2018 data is not available
|  | 2.p. | Number of weather stations in WUI | [16 empty] | 18 | 0 | 85 | 73 | 41 | 0 | 125 | 92 | 46 |  | 153 | 102 |  |  |  |  | Number of weather stations in WUI | See section 6.5 for a note on why 2015-2018 data is not available
x | 3. State of service territory and equipment in highly rural areas | 3.a. | Circuit miles (including WUI and non-WUI) | [16 empty] | 7302 | 39 | 4539 | 825 | 7216 | 12 | 4024 | 675 | 7293.8856 | 12.0612 | 4469.6536 | 820.2407 |  |  |  |  | Circuit miles | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.b. | Circuit miles in WUI | [16 empty] | 563 | 9 | 1035 | 331 | 498 | 1 | 942 | 274 | 574.983 | 1.1956 | 1038.8232 | 326.6308 |  |  |  |  | Circuit miles in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.c. | Number of critical facilities (including WUI and non-WUI) | [16 empty] | 649 | 8 | 326 | 104 | 1087 | 2 | 797 | 297 | 1135 | 2 | 808 | 296 |  |  |  |  | Number of critical facilities | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.d. | Number of critical facilities in WUI | [16 empty] | 108 | 4 | 144 | 60 | 250 | 1 | 385 | 185 | 256 | 1 | 387 | 185 |  |  |  |  | Number of critical facilities in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.e. | Number of customers (including WUI and non-WUI) | [16 empty] | 39611 | 1303 | 33739 | 9840 | 37193 | 93 | 30689 | 8545 | 37289 | 93 | 30636 | 8577 |  |  |  |  | Number of customers | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.f. | Number of customers in WUI | [16 empty] | 14576 | 1068 | 22200 | 7919 | 13629 | 45 | 20733 | 7059 | 13632 | 45 | 20825 | 7103 |  |  |  |  | Number of customers in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.g. | Number of customers belonging to access and functional needs populations (including WUI and non-WUI) | [16 empty] | 878 | 7 | 1098 | 231 | 981 |  | 1287 | 263 | 1018 |  | 1289 | 276 |  |  |  |  | Number of customers belonging to access and functional needs populations | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.h. | Number of customers belonging to access and functional needs populations in WUI | [16 empty] | 475 | 4 | 813 | 188 | 456 |  | 961 | 215 | 467 |  | 959 | 226 |  |  |  |  | Number of customers belonging to access and functional needs populations in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.i. | Circuit miles of overhead transmission lines (including WUI and non-WUI) | [16 empty] | 1691.7 | 3.1 | 1039.3 | 135.5 | 1691.8 | 3.1 | 1039.2 | 135.4 | 1723.9569 | 3.1029 | 1144.0926 | 175.5219 |  |  |  |  | Circuit miles of overhead transmission lines | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.j. | Circuit miles of overhead transmission lines in WUI | [16 empty] | 40.8 | 0 | 83.9 | 24.3 | 40.8 | 0 | 83.9 | 24.2 | 49.9226 | 0 | 102.0172 | 31.2659 |  |  |  |  | Circuit miles of overhead transmission lines in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.k. | Circuit miles of overhead distribution lines (including WUI and non-WUI) | [16 empty] | 5579.8 | 9 | 3032.4 | 546.9 | 5524.2 | 9 | 2984.8 | 540.1 | 5569.9287 | 8.9583 | 3325.561 | 644.7188 |  |  |  |  | Circuit miles of overhead distribution lines | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.l. | Circuit miles of overhead distribution lines in WUI | [16 empty] | 458.8 | 1.2 | 855.3 | 254.4 | 457.4 | 1.2 | 858.5 | 249.7 | 525.0604 | 1.1956 | 936.806 | 295.3649 |  |  |  |  | Circuit miles of overhead distribution lines in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.m. | Number of substations (including WUI and non-WUI) | [16 empty] | 51 | 0 | 22 | 6 | 57 |  | 19 | 5 | 69 |  | 65 | 16 |  |  |  |  | Number of substations | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.n | Number of substations in WUI | [16 empty] | 3 | 0 | 7 | 3 | 4 |  | 7 | 2 | 4 |  | 17 | 4 |  |  |  |  | Number of substations in WUI | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.o. | Number of weather stations (including WUI and non-WUI) | [16 empty] | 13 | 0 | 113 | 24 | 32 | 0 | 166 | 26 | 45 |  | 187 | 28 |  |  |  |  | Number of weather stations | See section 6.5 for a note on why 2015-2018 data is not available
|  | 3.p. | Number of weather stations in WUI | [16 empty] | 3 | 0 | 18 | 8 | 5 | 0 | 29 | 8 | 6 |  | 31 | 9 |  |  |  |  | Number of weather stations in WUI | See section 6.5 for a note on why 2015-2018 data is not available
Updated comments for Table 8 (8/2/2021): Customers belonging to AFN (Access and Functional Needs) population dataset is based on Medical Baseline Customers only and does not reflect the revision of AFN definition in the 2021 WMP. This is due to the system limitation of the data within the various systems that are not currently connected to the enterprise GIS database. Please note, a weather station, although installed by 6/30, should not be counted towards the 2021 WMP commitment (i.e., PGE-1859) as it was installed to support a different weather station program. Thus, the total count of stations is 1170 with 1169 counted towards the WMP commitment. Updated comments for Table 8 (6/3/2021): PG&E has updated the number of weather stations installed in 2019 & 2020, please refer to Weather Station Self-Identification Notice, dated June 1, 2021 for further information. Comments for Table 8: Table 8 seeks information regarding the current baseline state of HFTD and non-HFTD service territory, as located in urban versus rural versus highly rural areas, including a subset with the Wildland-Urban Interface (WUI). The WUI is defined as areas where homes are built near or among lands prone to wildland fires. PG&E identifies WUI areas within PG&E’s service territory based upon data provided by the University of Wisconsin-Madison SILVIS Lab, available here: http://silvis.forest.wisc.edu/data/wui-change/, shows the WUI areas within California as of 2010. Note that in Table 8 data for 2015-2018 has not been provided for two reasons: (1) PG&E planned and executed a multi-year project starting in 2013 that included converting legacy sources of electric facility information into a single enterprise GIS database. The conversion started in 2014 and was completed in 2018. This conversion was executed, reviewed, and accepted in phases for the entire PG&E service territory during these project years. There is no historical database of the electric facilities during the requested years from 2015 to 2018 that would contain a complete and accurate inventory of all the electric facilities metrics requested in Table 8. (2) PG&E’s GIS system is a dynamic ‘real-time’ system that reflects the current assets in PG&E’s service territory, when old assets are removed or replaced they are removed from the GIS system. Therefore, snapshots of asset information at prior points in history, before the WMP process began in 2019, are not available. Substation count includes facility type: Distribution Switching station, Junction, Power House, Power Plant, Substation & Transmission Switching Station.

## Table 9
| Utility | Pacific Gas & Electric Company | Notes:
| Table No. | 9 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV. Report net additions using positive numbers and net removals and undergrounding using negative numbers for circuit miles and numbers of substations. Only report changes expected within the target year.
| Date Modified | 2021-06-03 | For example, if 20 net overhead circuit miles are planned for addition by 2023, with 15 being added by 2022 and 5 more added by 2023, then report “15” for 2022 and “5” for 2023. Do not report cumulative change across years. In this case, do not report “20” for 2023, but instead the number planned to be added for just that year, which is “5”.
|  |  |  | Actual |  |  |  | Projected
| Table 9: Location of actual and planned utility equipment additions or removal year over year |  |  | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3
| Metric type | # | Outcome metric name | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s)
x | 1. Planned utility equipment net addition (or removal) year over year - in urban areas | 1.a. | Circuit miles of overhead transmission lines | -0.9 | 0 | -0.1 | -0.7 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles
|  | 1.b. | Circuit miles of overhead distribution lines | -23 | 0 | -3.7 | -5.6 | 0 | 0 | 0 | 0 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles
|  | 1.c. | Circuit miles of overhead transmission lines in WUI | 0.1 | 0 | 0.9 | -0.7 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles in WUI
|  | 1.d. | Circuit miles of overhead distribution lines in WUI | -4.5 | -0.1 | 1 | -5.9 | 0 | 0 | 0 | 0 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles in WUI
|  | 1.e. | Number of substations | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of substations
|  | 1.f. | Number of substations in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of substations in WUI
|  | 1.g. | Number of weather stations | 16 | 0 | 10 | 5 | 10 | 0 | 21 | 2 | Note 2 | Note 2 | Note 2 | Note 2 | Number of weather stations
|  | 1.h. | Number of weather stations in WUI | 12 | 0 | 6 | 3 | 1 | 0 | 1 | 0 | Note 2 | Note 2 | Note 2 | Note 2 | Number of weather stations in WUI
x | 2. Planned utility equipment net addition (or removal) year over year - in rural areas | 2.a. | Circuit miles of overhead transmission lines | 0.5 | 0 | -0.6 | -0.2 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles
|  | 2.b. | Circuit miles of overhead distribution lines | -30.7 | -0.1 | -110.8 | -115 | 0 | 0 | -2.4 | -0.5 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles
|  | 2.c. | Circuit miles of overhead transmission lines in WUI | 0 | 0 | -0.8 | -0.3 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles in WUI
|  | 2.d. | Circuit miles of overhead distribution lines in WUI | 4.8 | 0 | -11.9 | -39.3 | 0 | 0 | -0.6 | -0.1 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles in WUI
|  | 2.e. | Number of substations | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | -1 | -1 | Number of substations
|  | 2.f. | Number of substations in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | Number of substations in WUI
|  | 2.g. | Number of weather stations | 76 | 0 | 149 | 48 | 24 | 1 | 30 | 15 | Note 2 | Note 2 | Note 2 | Note 2 | Number of weather stations
|  | 2.h. | Number of weather stations in WUI | 23 | 0 | 40 | 19 | 8 | 0 | 8 | 5 | Note 2 | Note 2 | Note 2 | Note 2 | Number of weather stations in WUI
x | 3. Planned utility equipment net addition (or removal) year over year - in highly rural areas | 3.a. | Circuit miles of overhead transmission lines | 0.1 | 0 | -0.1 | -0.1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles
|  | 3.b. | Circuit miles of overhead distribution lines | -55.6 | 0 | -47.6 | -6.8 | -0.8 | 0 | -3.3 | -0.8 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles
|  | 3.c. | Circuit miles of overhead transmission lines in WUI | 0 | 0 | 0 | -0.1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles in WUI
|  | 3.d. | Circuit miles of overhead distribution lines in WUI | -1.4 | 0 | 3.2 | -4.7 | 0 | 0 | -2.12 | -0.2 | Note 1 | Note 1 | Note 1 | Note 1 | Circuit miles in WUI
|  | 3.e. | Number of substations | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of substations
|  | 3.f. | Number of substations in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of substations in WUI
|  | 3.g. | Number of weather stations | 19 | 0 | 53 | 2 | 7 | 0 | 0 | 1 | Note 2 | Note 2 | Note 2 | Note 2 | Number of weather stations
|  | 3.h. | Number of weather stations in WUI | 2 | 0 | 11 | 0 | 3 | 0 | 0 | 0 | Note 2 | Note 2 | Note 2 | Note 2 | Number of weather stations in WUI
Updated comments for Table 9 (6/3/2021):
PG&E has updated the number of weather stations installed in 2019 & 2020, please refer to Weather Station Self-Identification Notice, dated June 1, 2021 for further information.
Notes for Table 9:
The data presented in this table are based on the best knowledge that PG&E has as of January 2021. As better data becomes available, this will be updated in the quarterly updates.
Note 1: For transmission line additions and removals for 2021 and 2022, project prioritization and timing have not been fully determined or mapped.
Note 2: PG&E's weather station goal is to install 1,300 by the end of 2021 and then assess the need for further locations. Therefore, weather station additions for 2022 are undetermined at this time.
Other comments:
1) The data presented for 2021 Distribution removals/additions represents the work for removal of idle facilities. There are many other reasons that conductor may be added or removed.
2) The 2020 Actual data was derived by subtracting the 2019 data from the 2020 data in Table 8, and reflects the total net change in the system year-over-year.
3) The same layers used in Table 8 have been used to determine Population Density, HFTD, and WUI.

## Table 10
| Utility | Pacific Gas & Electric Company | Notes:
| Table No. | 10 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
| Date Modified | 2021-02-05 | In future submissions update planned upgrade numbers with actuals
|  |  | In the comments column on the far-right, enter the relevant program target(s) associated | Actual |  |  |  | Projected
| Table 10: Location of actual and planned utility infrastructure upgrades year over year |  |  | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | HFTD Zone 1 | HFTD Tier 2 | HFTD Tier 3
| Metric type | # | Outcome metric name | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Comment
x | 1. Planned utility infrastructure upgrades year over year - in urban areas | 1.a. | Circuit miles of overhead transmission lines planned for upgrades (including WUI and non-WUI) | Note 1 | Note 1 | Note 1 | Note 1 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Circuit miles | See Note 1 & Note 4
|  | 1.b. | Circuit miles of overhead distribution lines planned for upgrades (including WUI and non-WUI) | 0.3 | 0 | 1.4 | 4.1 | 6.6 | 0 | 0 | 4.6 | Note 3 | Note 3 | Note 3 | Note 3 | Circuit miles | See Note 3 & Note 5
|  | 1.c. | Circuit miles of overhead transmission lines planned for upgrades in WUI | Note 1 | Note 1 | Note 1 | Note 1 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Circuit miles in WUI | See Note 1 & Note 4
|  | 1.d. | Circuit miles of overhead distribution lines planned for upgrades in WUI | 0.3 | 0 | 1.4 | 4.1 | 6.6 | 0 | 0 | 4.6 | Note 3 | Note 3 | Note 3 | Note 3 | Circuit miles in WUI | See Note 3 & Note 5
|  | 1.e. | Number of substations planned for upgrades (including WUI and non-WUI) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Number of substations | PG&E is interpreting substation enhancements to be significant enhancement to substation buses.
|  | 1.f. | Number of substations planned for upgrades in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Number of substations in WUI | PG&E is interpreting substation enhancements to be significant enhancement to substation buses.
|  | 1.g. | Number of weather stations planned for upgrades (including WUI and non-WUI) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of weather stations | See Note 2
x |  | 1.h. | Number of weather stations planned for upgrades in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of weather stations in WUI | See Note 2
| 2. Planned utility infrastructure upgrades year over year - in rural areas | 2.a. | Circuit miles of overhead transmission lines planned for upgrades (including WUI and non-WUI) | Note 1 | Note 1 | Note 1 | Note 1 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Circuit miles | See Note 1 & Note 4
|  | 2.b. | Circuit miles of overhead distribution lines planned for upgrades (including WUI and non-WUI) | 1 | 0 | 5.1 | 114.3 | 3.3 | 0 | 5.8 | 26.8 | Note 3 | Note 3 | Note 3 | Note 3 | Circuit miles | See Note 3 & Note 5
|  | 2.c. | Circuit miles of overhead transmission lines planned for upgrades in WUI | Note 1 | Note 1 | Note 1 | Note 1 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Circuit miles in WUI | See Note 1 & Note 4
|  | 2.d. | Circuit miles of overhead distribution lines planned for upgrades in WUI | 0.7 | 0 | 1.8 | 104.5 | 3.3 | 0 | 2.4 | 20 | Note 3 | Note 3 | Note 3 | Note 3 | Circuit miles in WUI | See Note 3 & Note 5
|  | 2.e. | Number of substations planned for upgrades (including WUI and non-WUI) | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of substations | PG&E is interpreting substation enhancements to be significant enhancement to substation buses.
|  | 2.f. | Number of substations planned for upgrades in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of substations in WUI | PG&E is interpreting substation enhancements to be significant enhancement to substation buses.
x |  | 2.g. | Number of weather stations planned for upgrades (including WUI and non-WUI) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of weather stations | See Note 2
|  | 2.h. | Number of weather stations planned for upgrades in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of weather stations in WUI | See Note 2
| 3. Planned utility infrastructure upgrades year over year - in highly rural areas | 3.a. | Circuit miles of overhead transmission lines planned for upgrades (including WUI and non-WUI) | Note 1 | Note 1 | Note 1 | Note 1 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Circuit miles | See Note 1 & Note 4
|  | 3.b. | Circuit miles of overhead distribution lines planned for upgrades (including WUI and non-WUI) | 0 | 0 | 1.8 | 1.1 | 0 | 0 | 4.2 | 0.9 | Note 3 | Note 3 | Note 3 | Note 3 | Circuit miles | See Note 3 & Note 5
|  | 3.c. | Circuit miles of overhead transmission lines planned for upgrades in WUI | Note 1 | Note 1 | Note 1 | Note 1 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Note 4 | Circuit miles in WUI | See Note 1 & Note 4
|  | 3.d. | Circuit miles of overhead distribution lines planned for upgrades in WUI | 0 | 0 | 0.5 | 1.1 | 0 | 0 | 0.3 | 0.1 | Note 3 | Note 3 | Note 3 | Note 3 | Circuit miles in WUI | See Note 3 & Note 5
|  | 3.e. | Number of substations planned for upgrades (including WUI and non-WUI) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of substations | PG&E is interpreting substation enhancements to be significant enhancement to substation buses.
|  | 3.f. | Number of substations planned for upgrades in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of substations in WUI | PG&E is interpreting substation enhancements to be significant enhancement to substation buses.
|  | 3.g. | Number of weather stations planned for upgrades (including WUI and non-WUI) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of weather stations | See Note 2
|  | 3.h. | Number of weather stations planned for upgrades in WUI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Number of weather stations in WUI | See Note 2
Comments for Table 10: The data presented in Table 10 are based on the best knowledge that PG&E has as of January 2021. As better data becomes available, this will be updated in the quarterly updates. Note 1: PG&E reconductored approximately 103 HFTD and 127 Non-HFTD miles of transmission conductor across its service territory in 2020, but all jobs have not been mapped into the GIS system in order to break the data down as required by this table. Note 2: PG&E has no plans to upgrade or modify existing weather stations. Note 3: PG&E is in the process of replanning Distribution system hardening work for 2021 and 2022. 2021 data is shown as of the time of submission, but does not reflect all projects that will be completed in 2021 and will be revised in future submissions. Because of this replanning, 2022 planning is not yet complete. Note 4: PG&E does not have an equivalent "system hardening" program for transmission conductor, but PG&E is planning to reconductor 92 HFTD miles and 90 Non-HFTD miles in 2021. The preliminarily planned jobs have not been mapped in order to break the data down for this table. There will also be other upgrades during 2021 and 2022 to transmission lines in the normal course of PG&E’s business. Note 5: PG&E hardened 342 miles in 2020 but not all projects have been mapped as of January 2021 and therefore may not be included in this data. Other comments: 1) The same layers used in Table 8 have been used to determine Population Density, HFTD, and WUI.

## Table 11
Utility | Pacific Gas & Electric Company | Notes:
Table No. | 11 | "PSPS" = Public Safety Power Shutoff
Date Modified | 2021-08-02 | In future submissions update planned upgrade numbers with actuals
|  |  | Section 1: Historical Data (Event Actuals) | [10 empty] | Section 2: Forecasted Data (average of historical data) | [5 empty] | Section 3: Forecasted Data with 2021 Planned WMP Mitigations in Place | [5 empty] | Section 4: Forecasted data with 2021 Mitigations and 2020 PSPS Protocols Plus Tree Overstrike Potential and Priority Tags Criteria Added
Table 11: Recent use of PSPS and other PSPS metrics | [7 empty] | 1 | 2 | 3 | 4 | 1 | Q2 | 3 | 4 | 1 | 2 | 3 | 4 | 3 | 4 | 1 | 2 | 3 | 4 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Outcome metric name | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | Unit(s) | Baseline Forecast Comments
1. Recent use of PSPS | 1.a. | Frequency of PSPS events (total) | 0 | 0 | 0 | 1 | 9 | 0 | 0 | 2 | 4 | 1 | 0 | 0.45455 | 2 | 0.3 | 0.18182 | 0.45455 | 2 | 0.45455 | 2 | 0.3 | 0.18182 | 0.45455 | 2 | 0.79091 | 3.48 | 0.522 | 0.31636 | 0.79091 | 3.48 | Number of instances where utility operating protocol requires de-energization of a circuit or portion thereof to reduce ignition probability, per quarter or year. Only include events in which de-energization ultimately occurred | Base Forecast: 11-year average using backcast re-analysis
| 1.b. | Scope of PSPS events (total) | 0 | 0 | 0 | 41 | 13122 | 0 | 0 | 408 | 1924 | 18 | 0 | 14.6281 | 550.7273 | 5 | 3.2066 | 14.6281 | 550.7273 | 13.4579 | 506.6691 | 4.6 | 2.9501 | 13.4579 | 506.6691 | 21.8243 | 821.6551 | 7.4597 | 4.7841 | 21.8243 | 821.6551 | Circuit-events, measured as the number of circuits de-energized in part or in whole by each PSPS event, summed across each quarter or year. | Base Forecast: 11-year average using backcast re-analysis
| 1.c. | Duration of PSPS events (total), in customer-hours | 0 | 0 | 0 | 1517371 | 90740214 | 0 | 0 | 7540563.6175 | 14736124.6822 | 347470.136 | 0 | 947652.0561 | 22605223.0166 | 1168058 | 1140763.0455 | 947652.0561 | 22605223.0166 | 854403.0938 | 20380869.0717 | 1053121.0928 | 1028511.9618 | 854403.0938 | 20380869.0717 | 1350929.1989 | 32224966.5623 | 1665129.7784 | 1626219.3462 | 1350929.1989 | 32224966.5623 | Customer hours of de-energization due to PSPS per quarter or year | Base Forecast: 11-year average using backcast re-analysis
2. Customer hours of PSPS and other outages | 2.a. | Customer hours of planned outages including PSPS (total) | 1400185 | 1390308 | 1513383 | 4015315 | 101200587 | 508425 | 439423 | 8384809 | 15784931.2 | 919249 | 856249.5833 | 1496771.7561 | 23126780.0166 | 1560622 | 1648185.8455 | 1496771.7561 | 23126780.0166 | 1403522.7938 | 20902426.0717 | 1445684.9781 | 1535934.7618 | 1403522.7938 | 20902426.0717 | 1900048.8989 | 32746523.5623 | 2057693.597 | 2133642.1462 | 1900048.8989 | 32746523.5623 | Total customer hours of planned outages per quarter or year | Base Forecast: 10-year historical average plus 11-year average using backcast re-analysis
| 2.b. | Customer hours of unplanned outages, not including PSPS (total) | 11961864 | 9745978 | 32897043 | 24589665 | 28791354 | 7070484 | 3075467 | 6303666 | 3370778.6 | 15076957 | 3569115.4833 | 3353012.2 | 7033480.7 | 7156787 | 3252816.4 | 3353012.2 | 7033480.7 | 3353012.2 | 7033480.7 | 7156787 | 3252816.4 | 3353012.2 | 7033480.7 | 3353012.2 | 7033480.7 | 7156787 | 3252816.4 | 3353012.2 | 7033480.7 | Total customer hours of unplanned outages per quarter or year | Base Forecast: 10-year historical average
| 2.c. | System Average Interruption Duration Index (SAIDI) (including PSPS) | 147.2 | 121.9 | 374.3 | 309.3 | 1395.4 | 81.4 | 37.7 | 157.7 | 204.1 | 170.3 | 47.1 | 53.0647 | 329.8391 | 95.4 | 53.5768 | 53.0647 | 329.8391 | 52.0448 | 305.5108 | 94.1183 | 52.3491 | 52.0448 | 305.5108 | 57.4755 | 435.0528 | 100.812 | 58.8864 | 57.4755 | 435.0528 | SAIDI index value (hours) = sum of all interruptions in time period where each interruption is defined as sum(duration of interruption in hours * # of customer interruptions) / Total number of customers served | Base Forecast: 10-year historical average plus 11-year average using backcast re-analysis
| 2.d. | System Average Interruption Duration Index (SAIDI) (excluding PSPS) | 147.2 | 121.9 | 374.3 | 292.9 | 334.4 | 81.4 | 37.7 | 73.6 | 44.8 | 167.1 | 47.1 | 42.7 | 82.6 | 82.6 | 41.1 | 42.7 | 82.6 | 42.7 | 82.6 | 82.6 | 41.1 | 42.7 | 82.6 | 42.7 | 82.6 | 82.6 | 41.1 | 42.7 | 82.6 | SAIDI index value (hours) = sum of all interruptions in time period where each interruption is defined as sum(duration of interruption in hours * # of customer interruptions) / Total number of customers served | Base Forecast: 10-year historical average
| 2.e. | System Average Interruption Frequency Index (SAIFI) (including PSPS) | 1.053 | 1.102 | 1.549 | 1.175 | 1.996 | 0.344 | 0.309 | 0.493 | 0.415 | 0.458 | 0.35 | 0.34501 | 0.60141 | 0.4 | 0.324 | 0.34501 | 0.60141 | 0.34269 | 0.58266 | 0.376 | 0.32639 | 0.34269 | 0.58266 | 0.55574 | 0.94488 | 0.60975 | 0.5293 | 0.55574 | 0.94488 | SAIFI index value = sum of all interruptions in time period where each interruption is defined as (total # of customer interruptions) / (total # of customers served) | Base Forecast: 10-year historical average plus 11-year average using backcast re-analysis
| 2.f. | System Average Interruption Frequency Index (SAIFI) (excluding PSPS) | 1.053 | 1.102 | 1.549 | 1.165 | 1.596 | 0.344 | 0.309 | 0.449 | 0.337 | 0.457 | 0.35 | 0.316 | 0.367 | 0.4 | 0.324 | 0.316 | 0.367 | 0.316 | 0.367 | 0.4 | 0.324 | 0.316 | 0.367 | 0.316 | 0.367 | 0.4 | 0.324 | 0.316 | 0.367 | SAIFI index value = sum of all interruptions in time period where each interruption is defined as (total # of customer interruptions) / (total # of customers served) | Base Forecast: 10-year historical average
3. Critical infrastructure impacted by PSPS | 3.a. | Critical infrastructure outage customer-hours due to PSPS | 0 | 0 | 0 | 23257 | 810940.6833 | 0 | 0 | 139703.1325 | 282103.9075 | 2 | 0 | 18022.0757 | 225290.3007 | 9754 | 11006.3909 | 18022.0757 | 225290.3007 | 16248.7034 | 203121.7351 | 8794.2064 | 9923.362 | 16248.7034 | 203121.7351 | 25691.4425 | 321163.494 | 13904.8539 | 15690.2048 | 25691.4425 | 321163.494 | Number of critical infrastructure (in accordance with D.19-05-042) locations impacted per hour multiplied by hours offline per quarter or year | Base Forecast: 11-year average using backcast re-analysis
4. Community outreach of PSPS metrics | 4.a. | # of customers impacted by PSPS | 0 | 0 | 0 | 60806 | 2036019 | 0 | 0 | 232875 | 416810 | 5099 | 0 | 30103.1818 | 478502.2727 | 31453 | 25555 | 30103.1818 | 478502.2727 | 27694.9273 | 440222.0909 | 28936.76 | 23510.6 | 27694.9273 | 440222.0909 | 44912.3097 | 713899.3604 | 46926.165 | 38126.6698 | 44912.3097 | 713899.3604 | # of customers impacted by PSPS (if multiple PSPS events impact the same customer, count each event as a separate customer) | Base Forecast: 11-year average using backcast re-analysis
| 4.b. | # of medical baseline customers impacted by PSPS | 0 | 0 | 0 | 2529 | 83333 | 0 | 0 | 14741 | 27065 | 274 | 0 | 1998.5455 | 16996.0909 | 922 | 882.0909 | 1998.5455 | 16996.0909 | 1838.6618 | 15636.4036 | 848.24 | 811.5236 | 1838.6618 | 15636.4036 | 2981.7211 | 25357.243 | 1375.5738 | 1316.0317 | 2981.7211 | 25357.243 | # of customers impacted by PSPS (if multiple PSPS events impact the same customer, count each event as a separate customer) | Base Forecast: 11-year average using backcast re-analysis
| 4.c. | # of customers notified prior to initiation of PSPS event | 0 | 0 | 0 | 69229 | 2517105 | 0 | 0 | 293681 | 735708 | 22433 | 0 | 39751.4967 | 631866.1473 | 41535 | 33745.5856 | 39751.4967 | 631866.1473 | 36571.377 | 581316.8555 | 38212.2 | 31045.9387 | 36571.377 | 581316.8555 | 59307.0706 | 942709.9182 | 61967.9605 | 50346.5779 | 59307.0706 | 942709.9182 | # of customers notified of PSPS event prior to initiation quarter or year. (if multiple PSPS events impact the same customer, count each event in which customer was notified as a separate customer) | Base Forecast: 11-year historical average of impacted customers multiplied by the 2-year historical average for customer notifications.
| 4.d. | # of medical baseline customers notified prior to initiation of PSPS event | 0 | 0 | 0 | 3610 | 105606 | 0 | 0 | 22927 | 47914 | 1174 | 0 | 2817.9652 | 23964.6254 | 1301 | 1243.7553 | 2817.9652 | 23964.6254 | 2592.528 | 22047.4553 | 1196.92 | 1144.2549 | 2592.528 | 22047.4553 | 4204.2508 | 35753.9174 | 1941.0212 | 1855.6152 | 4204.2508 | 35753.9174 | # of customers notified of PSPS event prior to initiation per quarter or year. (if multiple PSPS events impact the same customer, count each event in which customer was notified as a separate customer) | Base Forecast: 2-year historical average
| 4.e. | % of customers notified prior to a PSPS event impacting them | 0 | 0 | 0 | 113.9% | 123.6% | 0 | 0 | 126.1% | 176.5% | 439.9% | 0 | 132.1% | 132.1% | 132.1% | 132.1% | 132.1% | 132.1% | 132.1% | 132.1% | 132% | 132.1% | 132.1% | 132.1% | 132.1% | 132.1% | 132% | 132.1% | 132.1% | 132.1% | =4.c. / 4.a. | Base Forecast: 2-year historical average
| 4.f. | % of medical baseline customers notified prior to a PSPS event impacting them | 0 | 0 | 0 | 142.7% | 126.7% | 0 | 0 | 155.5% | 177% | 428.5% | 0 | 141% | 141% | 141% | 141% | 141% | 141% | 141% | 141% | 141% | 141% | 141% | 141% | 141% | 141% | 141% | 141% | 141% | 141% | =4.d. / 4.b. | Base Forecast: 2-year historical average
5. Other PSPS metrics | 5.a. | Number of PSPS events triggered where no de-energization occurred | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | - | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1.74 | 0 | 0 | 0 | 1.74 | Number of instances where utility notified the public of a potential PSPS event but no de-energization followed per quarter or year. | Base Forecast: 2-year average
| 5.b. | Number of customers located on de-energized circuits | 0 | 0 | 0 | 60806 | 2831593 | 0 | 0 | 320057 | 929101 | 24021 | 0 | 45739.8095 | 727052.8055 | 47791 | 38829.1457 | 45739.8095 | 727052.8055 | 42080.6247 | 668888.5811 | 43967.72 | 35722.814 | 42080.6247 | 668888.5811 | 68241.3075 | 1084723.2341 | 71301.5722 | 57930.973 | 68241.3075 | 1084723.2341 | For the circuits de-energized for PSPS, the total customers served by the de-energized circuits. This is summed across all PSPS events per quarter or year. This customer count may be larger than the number of customers de-energized in each PSPS event, if only portions of circuits were de-energized due to sectionalization. | Base Forecast: 2-year historical average
| 5.c. | Customer hours of PSPS per RFW OH circuit mile day | 0 | 0 | 0 | 2.7985 | 195.9072 | 0 | 0 | 31.9665 | 40.353 | 6786.71 | 0 | 1.5843 | 16.3331 | 0 | 3.6031 | 1.5843 | 16.3331 | 5.7136 | 58.9036 | 0 | 12.9941 | 5.7136 | 58.9036 | 9.034 | 93.1348 | 0 | 20.5455 | 9.034 | 93.1348 | =1.c. / RFW OH circuit mile days in time period | Base Forecast: 2-year historical average
| 5.d. | Frequency of PSPS events (total) - High Wind Warning wind conditions | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | Events over time period that overlapped with a High Wind Warning as defined by the National Weather Service | Base Forecast: 2-year historical average
| 5.e. | Scope of PSPS events (total) - High Wind Warning wind conditions | 0 | 0 | 0 | 0 | 365568 | 0 | 0 | 0 | 0 | 4696 | 0 | 0 | 182784 | 0 | 0 | 0 | 182784 | 0 | 182784 | 0 | 0 | 0 | 182784 | 0 | 182784 | 0 | 0 | 0 | 182784 | Estimated customers impacted over time period that overlapped with a High Wind Warning as defined by the National Weather Service | Base Forecast: 2-year historical average
| 5.f. | Duration of PSPS events (total) - High Wind Warning wind conditions | 0 | 0 | 0 | 0 | 5749687 | 0 | 0 | 0 | 0 | 38.6 | 0 | 0 | 2874843.5 | 0 | 0 | 0 | 2874843.5 | 0 | 2874843.5 | 0 | 0 | 0 | 2874843.5 | 0 | 2874843.5 | 0 | 0 | 0 | 2874843.5 | Customer hours over time period that overlapped with a High Wind Warning as defined by the National Weather Service | Base Forecast: 2-year historical average
Updated comments for Table 11 (8/2/2021): 1. Replace Q2 projected with Q2 actuals data. Updated comments for Table 11 (6/3/2021): 1. PG&E submits this updated Table 11 in connection with our response to Critical Issue No. PGE-01 from the WSD. For further information on the data included in the revised Table 11, please reference our response to Critical Issue No. PGE-01 in our updated 2021 Wildfire Mitigation Plan provided on June 3, 2021. Updated comments for Table 11 (3/17/2020): 1. Removed whole number rounding for PSPS events which updated fields reliant on PSPS events per quarter. 2. Changed denominator of past PSPS lookback and event data from 11 to 10 to reflect the past 11 years of data (10 year lookback plus 2020 actuals) which updated fields reliant on duration, customer impact and scope. 3. Utilized actual event customer hours for 2020 which updated fields reliant on duration. 4. Changed denominator from 10-year average to 2-year average. 5. 2020 Q3 data for critical infrastructure updated. Original Comments for Table 11: PG&E has outlined the past and forecasted PSPS metrics in Table 11, which is utilizing historic recorded data for actuals and an analysis of the past ten years of weather data to provide the forecasted metrics. The forecasted numbers are largely weather dependent and do not include any event size or length reductions from the 2020 planned work. Further information historical lookback of the last ten years of weather data and its uses and limitations can be found in Section 8.1. PG&E projected PSPS metrics in 2021, and Table 11 keeps those values static for 2022. PG&E anticipates continued improvement from 2021 to 2022, but we do not yet have analysis on the value of those improvements. Thus, for the purposes of this table, no improvements have been assumed.

## Table 12
Utility | Pacific Gas & Electric Company | Notes:
Table No. | 12 | Risk-Spend-Efficiency (RSE) is defined as "An estimate of the cost-effectiveness of initiative, calculated by dividing the mitigation risk reduction benefit by the mitigation cost estimate based on the full set of risk reduction benefits estimated from the incurred costs."
Date Modified | 2021-06-10 | CAPEX = Capital expenditure; OPEX = Operating expenditure. In future submissions update planned spend, line miles treated, RSE, etc. with updated projections and actuals. Additional instructions can be found in QR information.
[18 empty] | Actual | Actual | Actual | Projected | Projected | Projected | Projected | Projected | Projected
Table 12: Mitigation initiative financials | [17 empty] | CAPEX ($ thousands) | OPEX ($ thousands) | Line miles to be treated | CAPEX ($ thousands) | OPEX ($ thousands) | Line miles to be treated | CAPEX ($ thousands) | OPEX ($ thousands) | Line miles to be treated | Line miles to be treated comments | Line miles to be treated comments | Line miles to be treated comments |  | Action PGE-4 (Class A): In its 2021 WMP update, PG&E shall submit a table describing its risk assessment techniques used for each initiative in the format used by Southern California Edison (SCE) [See SCE RCP at 9] | [5 empty] | Action PGE-6 (Class-A): In its 2021 WMP update, PG&E shall provide a timeline that shows when it expects each individual initiative in its WMP to be incorporated into its risk modeling. | Action PGE-8 subpart 1 (Class A): In its 2021 WMP update, PG&E shall: 1) update Tables 21-30 to reflect a quantitative value to accurately reflect risk reduction effectiveness instead of the current qualitative descriptions | Action PGE-8 subpart 2 (Class A): Provide a column describing the program under which each initiative falls
Metric type | WMP Table # / Category | WMP Initiative # | Initiative activity | Primary driver targeted | Secondary driver targeted | Year initiated | Estimated RSE in non-HFTD region | Estimated RSE in HFTD Zone 1 | Estimated RSE in HFTD Tier 2 | Estimated RSE in HFTD Tier 3 | If existing: most recent proceeding that has reviewed program | If new: memorandum account | Current compliance status - In / exceeding compliance with regulations | Associated rule(s) - if multiple, separate by semi-colon - ";" | If spend not disaggregated by category, note spend category or mark general operations | Comments | Comments on RSE | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2020 | 2021 | 2022 | Comments on Financials | Risk to be Mitigated | Risk Spend Efficiency (RSE) Calculated | Risk Informed Prioritization | Current Risk Models Used | Future Risk-Informed Decision Making Enhancements | Comments for Risk Informed Prioritization | Year initiative will be incorporated into risk modeling | Notes on Risk Effectiveness Quantification | Program
Other | Risk Assessment & Mapping | 7.3.1.1 | 7.3.1.1 A summarized risk map that shows the overall ignition probability and estimated wildfire consequence along the electric lines and equipment | All Drivers | All Drivers | 2018 | 0 | 573.8737 | 573.8737 | 573.8737 | 2020 GRC, Transmission Owner | N/A | N/A | N/A |  |  |  | 0 | 634.6424 | N/A | 0 | 676.1709 | N/A | 0 | 760.4664 | N/A | N/A - Risk Analysis activities generally performed by internal electric operations staff with costs not tracked separately | N/A - Risk Analysis activities generally performed by internal electric operations staff with costs not tracked separately | N/A - Risk Analysis activities generally performed by internal electric operations staff with costs not tracked separately |  | Ignition Risk - All Drivers | Yes | Yes | 2021 Wildfire Distribution Risk Model, Transmission Operability Assessment Model | Wildfire Distribution Risk Model, Wildfire Transmission Risk Model | Focused on HFTD; old: Distribution maps for our System Hardening and EVM programs that combine ignition probability and wildfire consequences; do not have this for transmission | 2021 | Drivers and RSEs can be seen in Table 12. This initiative reduces the likelihood of ignition risk mitigating all drivers, with an effectiveness as follows: All Drivers (Equipment Failure, Vegetation etc.) : 8.6% | Support
Other | Risk Assessment & Mapping | 7.3.1.2 | 7.3.1.2 Climate-driven risk map and modelling based on various relevant weather scenarios | N/A - Foundational | N/A - Foundational | <2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | N/A | N/A |  |  |  | 0 | 955.836 | N/A | 0 | 1623 | N/A | 0 | 1572 | N/A | N/A - Climate driven risk mapping is an aspect of weather and fire modeling, captured in Table 22, Initiative 4-1, Forecast of a fire risk index, fire potential index, or similar | N/A - Climate driven risk mapping is an aspect of weather and fire modeling, captured in Table 22, Initiative 4-1, Forecast of a fire risk index, fire potential index, or similar | N/A - Climate driven risk mapping is an aspect of weather and fire modeling, captured in Table 22, Initiative 4-1, Forecast of a fire risk index, fire potential index, or similar |  | Ignition Risk - All Drivers | No | Yes | Program Owner Prioritized (See Narrative) | Wildfire Distribution Risk Model, Enterprise Risk Model | All PG&E per narrative; Climate-driven risk analysis and modeling | 2021 | Risk reduction not quantified. Foundational Initiative, for which distinct financial and quantification data not currently available. | Support
Other | Risk Assessment & Mapping | 7.3.1.3 | 7.3.1.3 Ignition probability mapping showing the probability of ignition along the electric lines and equipment | All Drivers | All Drivers | 2018 | 0 | 573.8737 | 573.8737 | 573.8737 | 2020 GRC, Transmission Owner | N/A | N/A | N/A |  |  |  | 0 | 634.6424 | N/A | 0 | 676.1709 | N/A | 0 | 760.4664 | N/A | N/A - Circuit based ignition probabilities and risk analysis activities generally performed by internal electric operations staff with costs not tracked separately | N/A - Circuit based ignition probabilities and risk analysis activities generally performed by internal electric operations staff with costs not tracked separately | N/A - Circuit based ignition probabilities and risk analysis activities generally performed by internal electric operations staff with costs not tracked separately |  | Ignition Risk - All Drivers | Yes | No | N/A | Wildfire Probability of Ignition Model | All PG&E; Ignition probability mapping | 2021 | Drivers and RSEs can be seen in Table 12. This initiative reduces the likelihood of ignition risk mitigating all drivers, with an effectiveness as follows: All Drivers (Equipment Failure, Vegetation etc.) : 8.6% | Support
Other | Risk Assessment & Mapping | 7.3.1.4 | 7.3.1.4 Initiative mapping and estimation of wildfire and PSPS risk-reduction impact | N/A - Foundational | N/A - Foundational | 2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC, Transmission Owner | N/A | N/A | N/A |  |  |  | 0 | 15.5357 | N/A | 0 | 21.6389 | N/A | 0 | 22.2881 | N/A | N/A - Risk Analysis activities generally performed by internal electric operations staff with costs not tracked separately | N/A - Risk Analysis activities generally performed by internal electric operations staff with costs not tracked separately | N/A - Risk Analysis activities generally performed by internal electric operations staff with costs not tracked separately |  | Ignition Risk - All Drivers, Wildfire Consequence, PSPS Consequence | No | Yes | 2021 Wildfire Distribution Risk Model, Transmission Operability Assessment Model | Wildfire Distribution Risk Model, Wildfire Transmission Risk Model, Future State PSPS Consequence Model | ; For PSPS events, PG&E uses weather, fuel moisture, and Fire Potential Index models which inform the decision as to whether a PSPS is necessary. Composite Risk Model provides the capability to estimate the relative risk reduction for specific mitigation options. | 2022 | Risk reduction not quantified. Foundational Initiative, for which distinct financial and quantification data not currently available. | Support
Other | Risk Assessment & Mapping | 7.3.1.5 | 7.3.1.5 Match drop simulations showing the potential wildfire consequence of ignitions that occur along the electric lines and equipment | N/A - Foundational | N/A - Foundational | 2019 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC | N/A | N/A | N/A |  |  |  | 0 | 3584 | N/A | 0 | 3300 | N/A | 0 | 3396.36 | N/A | N/A - 5.3.1.5 is an aspect of weather and fire modeling, captured in Table 22, Initiative 4-1, Forecast of a fire risk index, fire potential index, or similar | N/A - 5.3.1.5 is an aspect of weather and fire modeling, captured in Table 22, Initiative 4-1, Forecast of a fire risk index, fire potential index, or similar | N/A - 5.3.1.5 is an aspect of weather and fire modeling, captured in Table 22, Initiative 4-1, Forecast of a fire risk index, fire potential index, or similar |  | Wildfire Consequence | No | Yes | Wildfire Consequence Model | Wildfire Consequence Model | "The Technosylva wildfire spread model results are available across all HFTD areas and the HFRA identified by PG&E. "; Wildfire spread risk modeling - Technosylva | 2021 | Risk reduction not quantified. Foundational Initiative, for which distinct financial and quantification data not currently available. | Situational Awareness
Other | Risk Assessment & Mapping | 7.3.1.6 | 7.3.1.6 Weather-Driven Risk Map and Modelling Based on Various Relevant Weather Scenarios | N/A - Foundational | N/A - Foundational | <2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC | N/A | N/A | N/A |  |  |  | 0 | 475.4166 | N/A | 0 | 543.7722 | N/A | 0 | 555.2307 | N/A | N/A - 7.3.1.6 Weather-Driven Risk Map and Modelling Based on Various Relevant Weather Scenarios not in Sept 9 2020 filing | N/A - 7.3.1.6 Weather-Driven Risk Map and Modelling Based on Various Relevant Weather Scenarios not in Sept 9 2020 filing | N/A - 7.3.1.6 Weather-Driven Risk Map and Modelling Based on Various Relevant Weather Scenarios not in Sept 9 2020 filing |  | Ignition Risk - All Drivers | No | No | N/A | Wildfire Distribution Risk Model, Wildfire Transmission Risk Model | All PG&E per narrative; Weather-driven risk map/modelling | 2021 | Risk reduction not quantified. Foundational Initiative, for which distinct financial and quantification data not currently available. | Situational Awareness
Other | Situational Awareness & Forecasting | 7.3.2.1.1 | 7.3.2.1.1 Advanced weather monitoring and weather stations, Numerical Weather Prediction | Consequence - PSPS | No other consequences reflected | <2018 | 0 | 1652.0439 | 1652.0439 | 1652.0439 | 2020 GRC | N/A | N/A | N/A |  |  |  | 0 | 488.1249 | N/A | 0 | 590.6583 | N/A | 0 | 607.846 | N/A | N/A - 7.3.2.1.1 Advanced weather monitoring and weather stations, Numerical Weather Prediction not in Sept 9 2020 filing | N/A - 7.3.2.1.1 Advanced weather monitoring and weather stations, Numerical Weather Prediction not in Sept 9 2020 filing | N/A - 7.3.2.1.1 Advanced weather monitoring and weather stations, Numerical Weather Prediction not in Sept 9 2020 filing |  | Ignition Risk - All Drivers, PSPS Consequence | Yes | No | N/A | POMMS | All PG&E per narrative; High resolution weather models are used by PG&E and other CA utilities to forecast the weather and critical components such as temperature, wind speed and relative humidity | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the consequence of PSPS, specifically mitigating the impact to customers from PSPS events, with an effectiveness as follows: PSPS Impact Reduction Effectiveness - 7.4% | Situational Awareness
Other | Situational Awareness & Forecasting | 7.3.2.1.2 | 7.3.2.1.2 Advanced weather monitoring and weather stations, Fuel Moisture Sampling and Modeling | Consequence - PSPS | No other consequences reflected | 2018 | 0 | 2867.2036 | 2867.2036 | 2867.2036 | 2020 GRC | N/A | N/A | N/A |  |  |  | 0 | 45.423 | N/A | 0 | 123.368 | N/A | 0 | 126.9703 | N/A | N/A - 7.3.2.1.2 Advanced weather monitoring and weather stations, Fuel Moisture Sampling and Modeling not in Sept 9 2020 filing | N/A - 7.3.2.1.2 Advanced weather monitoring and weather stations, Fuel Moisture Sampling and Modeling not in Sept 9 2020 filing | N/A - 7.3.2.1.2 Advanced weather monitoring and weather stations, Fuel Moisture Sampling and Modeling not in Sept 9 2020 filing |  | Ignition Risk - All Drivers, PSPS Consequence | Yes | No | N/A | Fuel Condition Models | All PG&E per narrative; Fuel Moisture Sampling and Modeling | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the consequence of PSPS, specifically mitigating the impact to customers from PSPS events, with an effectiveness as follows: PSPS Impact Reduction Effectiveness - 2% | Situational Awareness
Other | Situational Awareness & Forecasting | 7.3.2.1.3 | 7.3.2.1.3 Advanced weather monitoring and weather stations, Weather Stations | Consequence - PSPS | No other consequences reflected | 2018 | 0 | 127.3245 | 127.3245 | 127.3245 | 2020 GRC | N/A | N/A | N/A |  |  |  | 8314.9397 | 111.2093 | 9623.5908 | 6398.9101 | 1571.588 | 7146.2308 | 6396 | 1638.5046 | 0 | Assumption that 1,300 for the entire program will cover all of T2 and T3. Equation is # of weather stations/ 1,300 * total T1 Z1 T2 and T3 circuit miles. We do have tier 1 weather stations so including all line miles in territory in formula. | Assumption that 1,300 for the entire program will cover all of T2 and T3. Equation is # of weather stations/ 1,300 * total T1 Z1 T2 and T3 circuit miles. We do have tier 1 weather stations so including all line miles in territory in formula. | Assumption that 1,300 for the entire program will cover all of T2 and T3. Equation is # of weather stations/ 1,300 * total T1 Z1 T2 and T3 circuit miles. We do have tier 1 weather stations so including all line miles in territory in formula. |  | Ignition Risk - All Drivers, PSPS Consequence | Yes | Yes | Program Owner Prioritized (See Narrative) | POMMS | "station siting effort of each weather station"; Weather stations | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the consequence of PSPS, specifically mitigating the impact to customers from PSPS events, with an effectiveness as follows: PSPS Impact Reduction Effectiveness - 1% | Situational Awareness
Other | Situational Awareness & Forecasting | 7.3.2.1.4 | 7.3.2.1.4 Advanced weather monitoring and weather stations, Wildfire Cameras | All Drivers | All Drivers | 2018 | 0 | 89.4017 | 96.0517 | 98.527 | 2020 GRC | N/A | N/A | N/A |  |  |  | 0 | 6955.7637 | 11148.12 | 0 | 9385.2751 | 6967.575 | 0 | 11515.0758 | 6812.74 | Assumption is that 600 for the entire program will cover all HFTD. Equation is # of cameras/600 * total T+D HFTD circuit miles. | Assumption is that 600 for the entire program will cover all HFTD. Equation is # of cameras/600 * total T+D HFTD circuit miles. | Assumption is that 600 for the entire program will cover all HFTD. Equation is # of cameras/600 * total T+D HFTD circuit miles. |  | Wildfire Consequence | Yes | Yes | Program Owner Prioritized (See Narrative) | N/A | Tier 2/3 HFTDs; Wildfire cameras | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the likelihood of ignition risk, specifically mitigating all drivers for large, destructive, and catastrophic fire outcomes, with an effectiveness as follows: Likelihood of ignition due to all drivers - 4% | Situational Awareness
Other | Situational Awareness & Forecasting | 7.3.2.1.5 | 7.3.2.1.5 Advanced weather monitoring and weather stations, Fire Detection & Alerting | All Drivers | All Drivers | 2019 | 0.59812 | 334.4747 | 359.3538 | 368.6149 | 2020 GRC | N/A | N/A | N/A |  |  |  | 0 | 257 | 81004 | 0 | 340.6595 | 81004 | 0 | 350.5786 | 81004 | Program applies to all tiers in Distribution. Assumption is this program treats all miles. | Program applies to all tiers in Distribution. Assumption is this program treats all miles. | Program applies to all tiers in Distribution. Assumption is this program treats all miles. |  | Wildfire Consequence | Yes | No | N/A | N/A | All PG&E per narrative because these is satellite data *Note - Current Risk Model used is Enterprise Risk Model because that is the RSE model; Satellite fire detection and alerting system in | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the likelihood of ignition risk, specifically mitigating all drivers for large, destructive, and catastrophic fire outcomes, with an effectiveness as follows: Likelihood of ignition due to all drivers - 4% | Situational Awareness
Other | Situational Awareness & Forecasting | 7.3.2.1.6 | 7.3.2.1.6 Advanced weather monitoring and weather stations, Other Meteorology Tools and Upgrades | N/A - Foundational | N/A - Foundational | 2019 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC | N/A | N/A | N/A |  |  |  | 0 | 325.4166 | N/A | 0 | 393.7722 | N/A | 0 | 405.2307 | N/A | N/A - 7.3.2.1.6, Other Meteorology Tools and Upgrades not in Sept 9 2020 filing | N/A - 7.3.2.1.6, Other Meteorology Tools and Upgrades not in Sept 9 2020 filing | N/A - 7.3.2.1.6, Other Meteorology Tools and Upgrades not in Sept 9 2020 filing |  | Wildfire Consequence | No | No | N/A | N/A | All PG&E per narrative; Meteorology tools and upgrades: This would be the catch-all for the rest of the items so that we can put the entire meteorology budget into this one line item and then they can put the initiatives or tools as sub-items underneath this. | We are not planning to include this initiative. | Risk reduction not quantified. Foundational Initiative, for which distinct financial and quantification data not currently available. | Situational Awareness
Other | Situational Awareness & Forecasting | 7.3.2.2.1 | 7.3.2.2.1 Continuous monitoring sensors, Electric Transmission SEL T400L | N/A - Pilot | N/A - Pilot | 2019 | N/A - Pilot | N/A - Pilot | N/A - Pilot | N/A - Pilot | Transmission Owner | N/A | N/A | N/A |  |  |  | 633 | 0 | N/A | 0 | 0 | N/A | 0 | 0 | N/A | Line miles treated is not an appropriate metric to measure this initiative. | Line miles treated is not an appropriate metric to measure this initiative. | Line miles treated is not an appropriate metric to measure this initiative. |  | Ignition Risk -Equipment Failure | No | No | N/A | N/A | Line monitoring non-tripping travelling wave relays (SEL T400L) | We are not planning to include this initiative. | Risk reduction not quantified. As a pilot initiative, the necessary data to evaluate risk reduction is not currently available, but this technology has the potential to identify failures more quickly or before failures occur. Technology could also improve response time to system failures or potential ignitions with the possibility of reducing consequence of ignitions. | Operational Practices
Other | Situational Awareness & Forecasting | 7.3.2.2.2 | 7.3.2.2.2 Continuous monitoring sensors, SmartMeter™ Partial Voltage Detection (Formerly Known as Enhanced Wires Down Detection) | Equipment Failure | No other drivers addressed | 2019 | 3.9558 | 1602.038 | 1602.038 | 1602.038 | 2020 GRC | N/A | N/A | N/A |  |  |  | 1215.5724 | 3.6572 | 81004 | 331.0142 | 0 | 81004 | 515.1544 | 84.732 | 81004 | Program applies to all of T3 and T2 in Distribution, but based on language in 2021 WMP, this program can apply to all Smart Meters and therefore, the entire service territory. | Program applies to all of T3 and T2 in Distribution, but based on language in 2021 WMP, this program can apply to all Smart Meters and therefore, the entire service territory. | Program applies to all of T3 and T2 in Distribution, but based on language in 2021 WMP, this program can apply to all Smart Meters and therefore, the entire service territory. |  | Ignition Risk - Equipment Failure | Yes | No | N/A | N/A | SmartMeter™ partial voltage detection (sends real-time alarms to Distribution management system under partial voltage conditions) | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the likelihood of ignition risk, specifically mitigating the equipment failure driver for large, destructive, and catastrophic fire outcomes, with an effectiveness as follows: Likelihood of ignition due to equipment failure - 6.6% | Situational Awareness
Other | Situational Awareness & Forecasting | 7.3.2.2.3 | 7.3.2.2.3 Continuous monitoring sensors, Distribution Fault Anticipation Technology and Early Fault Detection | All Drivers, All Consequences | All Drivers, All Consequences | 2019 | 0 | 23.1046 | 23.1046 | 23.1046 | EPIC | FRMMA and WMPMA | N/A | N/A |  |  |  | 0 | 750.2567 | 719 | 5611.836 | 912.352 | TBD | 14219.66 | 2108.136 | TBD | Actuals were for the two circuits completed in 2020 for the pilot | The intent is to deploy EFD and DFA sensors on a total of 600-800 circuits in Tier 2 and Tier 3 HFTD areas, mitigating 28,000 total line miles (20,200 miles in Tier 2, 7,800 miles in Tier 3), across several General Rate Case (GRC) cycles. | The intent is to deploy EFD and DFA sensors on a total of 600-800 circuits in Tier 2 and Tier 3 HFTD areas, mitigating 28,000 total line miles (20,200 miles in Tier 2, 7,800 miles in Tier 3), across several General Rate Case (GRC) cycles. |  | Ignition Risk - Equipment Failure, Wildfire Consequences | Yes | Yes | Program Owner Prioritized (See Narrative) | N/A | Distribution Fault Anticipation (DFA) captures primary distribution disturbance current and voltage waveforms. This is an EPIC project. | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the likelihood of ignition risk and consequence of wildfire risk, specifically mitigating the equipment failure and vegetation drivers and financial, safety, and reliability consequences, with effectiveness as follows: Likelihood of ignition due to equipment failure or vegetation - 6%, and financial, safety, and reliability consequences of ignition - 6% | Operational Practices
Other | Situational Awareness & Forecasting | 7.3.2.2.4 | 7.3.2.2.4 Continuous monitoring sensors, Sensor IQ | N/A - Foundational | N/A - Foundational | 2020 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | WMCE | FRMMA / WMPMA | N/A | N/A |  |  |  | 0 | 1870.7814 | 25439 | 0 | 533 | 25439 | 0 | 0 | 25439 | Program applies to all of T3 and T2 in Distribution and complete in 2020. Beyond the HFTD was not contemplated at the time | Program applies to all of T3 and T2 in Distribution and complete in 2020. Beyond the HFTD was not contemplated at the time | Program applies to all of T3 and T2 in Distribution and complete in 2020. Beyond the HFTD was not contemplated at the time |  | Ignition Risk -Equipment Failure | No | Yes | Program Owner Prioritized (See Narrative) | N/A | Sensor IQ on ~500K SmartMeters™ (in HFTD areas) to identify service transformers failures and may include other use cases. | We are not planning to include this initiative. | Risk reduction not quantified. Foundational Initiative, for which distinct financial and quantification data not currently available. | Situational Awareness
Other | Situational Awareness & Forecasting | 7.3.2.2.5 | 7.3.2.2.5 Continuous monitoring sensors, Line Sensor Devices | All Drivers, All Consequences | All Drivers, All Consequences | 2019 | 0 | 126.7969 | 126.7969 | 126.7969 | N/A | FRMMA / WMPMA | N/A | N/A |  |  |  | 2590.165 | 0 | 4313 | 6420 | 0 | 2310.2 | 7620 | 0 | 2310.2 | 2020 WMP describes reaching 12,000 miles over the next 3 years, with a starting point of 3,000 miles to be completed by 2020. Equation for 2021 and beyond is (28,000-4,898)/10 years. All miles are described as HFTD miles. | 2020 WMP describes reaching 12,000 miles over the next 3 years, with a starting point of 3,000 miles to be completed by 2020. Equation for 2021 and beyond is (28,000-4,898)/10 years. | 2020 WMP describes reaching 12,000 miles over the next 3 years, with a starting point of 3,000 miles to be completed by 2020. Equation for 2021 and beyond is (28,000-4,898)/10 years. |  | Ignition Risk -Equipment Failure | Yes | Yes | Program Owner Prioritized (See Narrative) | N/A | Line sensor devices (continuously measure current in real-time and report events) | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the likelihood of ignition risk and consequence of wildfire risk, specifically mitigating the equipment failure and vegetation drivers and financial, safety, and reliability consequences, with effectiveness as follows: Likelihood of ignition due to equipment failure or vegetation - 1.81%, and financial, safety, and reliability consequences of ignition - 1.81% | Operational Practices
Other | Situational Awareness & Forecasting | 7.3.2.2.6 | 7.3.2.2.6 Continuous monitoring sensors, Distribution Arcing Fault Signature Library | N/A - Pilot | N/A - Pilot | 2020 | N/A - Pilot | N/A - Pilot | N/A - Pilot | N/A - Pilot | WMCE | FRMMA / WMPMA | N/A | N/A |  |  |  | 0 | 563.4847 | N/A | 0 | 30 | N/A | 0 | 0 | N/A | Since this is purely an R&D project, the initial scope of deployment will be on a single circuit that has a high occurrence of faults with a wide range of causes. The circuit includes sections that are within the Tier 2 and Tier 3 HFTD areas. | Since this is purely an R&D project, the initial scope of deployment will be on a single circuit that has a high occurrence of faults with a wide range of causes. The circuit includes sections that are within the Tier 2 and Tier 3 HFTD areas. | Since this is purely an R&D project, the initial scope of deployment will be on a single circuit that has a high occurrence of faults with a wide range of causes. The circuit includes sections that are within the Tier 2 and Tier 3 HFTD areas. |  | Ignition Risk -Equipment Failure | No | Yes | Program Owner Prioritized (See Narrative) | N/A | Partnership with 2 national labs to install high fidelity optical sensor technology on a distribution feeder to complete a Distribution Arcing Fault Signature Library | We are not planning to include this initiative. | Risk reduction not quantified. As a pilot initiative, the necessary data to evaluate risk reduction is not currently available, but this technology has the potential to identify failures more quickly or before failures occur. Technology could also improve response time to system failures or potential ignitions with the possibility of reducing consequence of ignitions. | Operational Practices
Other | Situational Awareness & Forecasting | 7.3.2.3 | 7.3.2.3 Fault indicators for detecting faults on electric lines and equipment | All Drivers, All Consequences | All Drivers, All Consequences | <2018 | N/A | N/A | N/A | N/A | 2020 GRC | N/A | N/A | N/A |  |  |  | 500 | 0 | N/A | 514 | 0 | N/A | 543.7154 | 0 | N/A | We have not yet determined a long-term plan for fault indicators and their detection of faults on electrical lines and equipment. Long-term plan milestones are still under development with Electric Operations and Asset Management as we evaluate our current protection and automation standards/initiatives. | We have not yet determined a long-term plan for fault indicators and their detection of faults on electrical lines and equipment. Long-term plan milestones are still under development with Electric Operations and Asset Management as we evaluate our current protection and automation standards/initiatives. | We have not yet determined a long-term plan for fault indicators and their detection of faults on electrical lines and equipment. Long-term plan milestones are still under development with Electric Operations and Asset Management as we evaluate our current protection and automation standards/initiatives. |  | Ignition Risk - All Drivers, Wildfire Consequence | No | No | N/A | N/A | Fault indicators | We are not planning to include this initiative. | Risk reduction not quantified. Initiative does not currently capture data found usable for risk reduction calculation. Attempt will be made to calculate the RSE for the 2022 WMP submission. | Operational Practices
Other | Situational Awareness & Forecasting | 7.3.2.4 | 7.3.2.4 Forecast of a fire risk index, fire potential index, or similar | Consequence - PSPS | No other consequences reflected | <2018 | 0 | 311.6314 | 311.6314 | 311.6314 | 2020 GRC | N/A | N/A | N/A |  |  |  | 0 | 2082.6273 | 25439 | 0 | 2545.9816 | 25439 | 0 | 2619.738 | 25439 | Program applies to HFTD | Program applies to HFTD | Program applies to HFTD |  | Ignition Risk - All Drivers, PSPS Consequence | Yes | Yes | Program Owner Prioritized (See Narrative) | Large Fire Probability Model | Fire Modeling: Fire Potential Index (FPI) Model, daily/hourly tool to drive operational decision to reduce fire risk. | 2021 | Drivers and RSEs can be seen in Table 12. This initiative reduces the consequence of PSPS, specifically mitigating the impact to customers from PSPS events, with an effectiveness as follows: PSPS Impact Reduction Effectiveness - 15% | Situational Awareness
Other | Situational Awareness & Forecasting | 7.3.2.5 | 7.3.2.5 Personnel monitoring areas of electric lines and equipment in elevated fire risk conditions | Consequence - Financial | No other consequences reflected | 2018 | 0 | 0.50237 | 0.53955 | 0.55339 | 2020 GRC | N/A | N/A | N/A |  |  |  | 250.785 | 3068.3805 | N/A | 30.3054 | 4187.8 | N/A | 238.074 | 4972.6 | N/A | Line miles treated is not an appropriate metric to measure this initiative. | Line miles treated is not an appropriate metric to measure this initiative. | Line miles treated is not an appropriate metric to measure this initiative. |  | Wildfire Consequence | Yes | Yes | Program Owner Prioritized (See Narrative) | N/A | Safety and Infrastructure Protection Team | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the consequence of wildfire risk, specifically mitigating the financial consequence, with an effectiveness as follows: Financial consequence of catastrophic and destructive ignitions - 0.15%, Financial consequence of small and large ignitions - 1.99% | Situational Awareness
Other | Situational Awareness & Forecasting | 7.3.2.6 | 7.3.2.6 Weather forecasting and estimating impacts on electric lines and equipment | Consequence - PSPS | No other consequences reflected | <2018 | 0 | 991.2263 | 991.2263 | 991.2263 | 2020 GRC | N/A | N/A | N/A |  |  |  | 0 | 488.1249 | 25439 | 1028 | 1105.6583 | 25439 | 1058 | 1137.846 | 25439 | Program applies to HFTD | Program applies to HFTD | Program applies to HFTD |  | Ignition Risk - All Drivers, PSPS Consequence | Yes | No | N/A | Storm Outage Prediction Program and Model | SOPP (Storm Outage Prediction Program), operated by Meteorology team, used to mitigate operational risk from adverse weather events that can cause unplanned outages. | 2021 | Drivers and RSEs can be seen in Table 12. This initiative reduces the consequence of PSPS, specifically mitigating the impact to customers from PSPS events, with an effectiveness as follows: PSPS Impact Reduction Effectiveness - 15% | Situational Awareness
Other | Situational Awareness & Forecasting | 7.3.2.7 | 7.3.2.7 Other, Wildfire Safety Operations Center (WSOC) | N/A - Foundational | N/A - Foundational | 2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC | N/A | N/A | N/A |  |  |  | -34.0887 | 4117.327 | 25439 | 1542.0027 | 6193 | 25439 | 105.7812 | 7170 | 25439 | Program applies to HFTD | Program applies to HFTD | Program applies to HFTD |  | Wildfire Consequence | No | No | N/A | N/A | Wildfire Safety Operations Center (WSOC) | We are not planning to include this initiative. | Risk reduction not quantified. Foundational Initiative, for which distinct financial and quantification data not currently available. | Situational Awareness
Other | Situational Awareness & Forecasting | 7.3.2.8 | 7.3.2.8 Other, Meteorology Analytics/Operations Center | N/A - Foundational | N/A - Foundational | 2020 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | WMCE | FRMMA / WMPMA | N/A | N/A |  |  |  | 920.104 | 0 | 25439 | 0 | 0 | 25439 | 0 | 0 | 25439 | Program applies to HFTD | Program applies to HFTD | Program applies to HFTD |  | Ignition Risk - All Drivers | No | No | N/A | N/A | Meteorology Operations Center | We are not planning to include this initiative. | Risk reduction not quantified. Foundational Initiative, for which distinct financial and quantification data not currently available. | Situational Awareness
Grid hardening | Grid Design & System Hardening | 7.3.3.1 | 7.3.3.1 Capacitor maintenance and replacement program | Equipment Failure | No other drivers addressed | <2018 | 0.42412 | 279.2509 | 280.4843 | 279.7268 | 2020 GRC | N/A | In Compliance | GO 95 |  |  |  | 8248.0023 | 313.71 | 24263 | 11358.4836 | 311.5665 | 24263 | 7561.823 | 311.5665 | 24263 | Assume that these remediations are tags/notifications resulting from inspections based on the new inspection cycle of 100% T3, 33% T2, 20% T1 going forward. For 2019 assumes 100% of Tiers 2&3 based on WSIP | Assume that these remediations are tags/notifications resulting from inspections based on the new inspection cycle of 100% T3, 33% T2, 20% T1 going forward. For 2019 assumes 100% of Tiers 2&3 based on WSIP | Assume that these remediations are tags/notifications resulting from inspections based on the new inspection cycle of 100% T3, 33% T2, 20% T1 going forward. For 2019 assumes 100% of Tiers 2&3 based on WSIP |  | Ignition Risk -Equipment Failure | Yes | Yes | Program Owner Prioritized (See Narrative) | Wildfire Distribution Risk Model | Capacitor maintenance and replacement (PG&E annually tests and inspects ~11,400 capacitors, ~10% of which require corrective action). | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the likelihood of ignition risk, specifically mitigating the equipment failure driver and capacitor bank subdriver, with an effectiveness as follows: Likelihood of ignition due to Equipment Failure of Capacitor - 90% | Maintenance
Grid hardening | Grid Design & System Hardening | 7.3.3.2-Baseline-D | 7.3.3.2-Baseline-D Circuit breaker maintenance and installation to de-energize lines upon detecting a fault, Baseline - Maintenance Substation Distribution | Equipment Failure | No other drivers addressed | <2018 | N/A | N/A | N/A | N/A | 2020 GRC | N/A | In Compliance | GO 174 |  |  |  | 16707.3584 | 2368.259 | N/A | 7041.5183 | 2364.1278 | N/A | 21.7908 | 2364.1278 | N/A | Line miles treated is not an appropriate metric for substation related investments | Line miles treated is not an appropriate metric for substation related investments | Line miles treated is not an appropriate metric for substation related investments |  | Ignition Risk -Equipment Failure | No | Yes | Program Owner Prioritized (See Narrative) | N/A | Maintenance of circuit breakers and reclosers used as substation circuit breakers | We are not planning to include this initiative. | Risk reduction not quantified. Initiative does not currently capture data found usable for risk reduction calculation. Attempt will be made to calculate the RSE for the 2022 WMP submission. | Maintenance
Grid hardening | Grid Design & System Hardening | 7.3.3.2-Baseline-T | 7.3.3.2-Baseline-T Circuit breaker maintenance and installation to de-energize lines upon detecting a fault, Baseline - Maintenance Substation Transmission | Equipment Failure | No other drivers addressed | <2018 | N/A | N/A | N/A | N/A | Transmission Owner | N/A | In Compliance | GO 174 |  |  |  | 28912.459 | 2172.6184 | N/A | 27029.0436 | 2011.5548 | N/A | 31695.034 | 1958 | N/A | Line miles treated is not an appropriate metric for substation related investments | Line miles treated is not an appropriate metric for substation related investments | Line miles treated is not an appropriate metric for substation related investments |  | Ignition Risk -Equipment Failure | No | Yes | Program Owner Prioritized (See Narrative) | N/A | Maintenance of circuit breakers and reclosers used as substation circuit breakers | We are not planning to include this initiative. | Risk reduction not quantified. Initiative does not currently capture data found usable for risk reduction calculation. Attempt will be made to calculate the RSE for the 2022 WMP submission. | Maintenance
Grid hardening | Grid Design & System Hardening | 7.3.3.2-Enhanced-D | 7.3.3.2-Enhanced-D Circuit breaker maintenance and installation to de-energize lines upon detecting a fault, Enhanced - Maintenance Substation Distribution | Equipment Failure | No other drivers addressed | 2019 | N/A | N/A | N/A | N/A | 2020 GRC | FRMMA / WMPMA | In Compliance | GO 174 |  |  |  | 3345.9811 | 484.8695 | N/A | 657.2115 | 295.4761 | N/A | 675.6134 | 120.8445 | N/A | Line miles treated is not an appropriate metric for substation related investments | Line miles treated is not an appropriate metric for substation related investments | Line miles treated is not an appropriate metric for substation related investments |  | Ignition Risk -Equipment Failure | No | Yes | Program Owner Prioritized (See Narrative) | N/A | Maintenance of circuit breakers and reclosers used as substation circuit breakers | We are not planning to include this initiative. | Risk reduction not quantified. Initiative does not currently capture data found usable for risk reduction calculation. Attempt will be made to calculate the RSE for the 2022 WMP submission. | Maintenance
Grid hardening | Grid Design & System Hardening | 7.3.3.2-Enhanced-T | 7.3.3.2-Enhanced-T Circuit breaker maintenance and installation to de-energize lines upon detecting a fault, Enhanced - Maintenance Substation Transmission | Equipment Failure | No other drivers addressed | 2019 | N/A | N/A | N/A | N/A | Transmission Owner | N/A | In Compliance | GO 174 |  |  |  | 2992.3352 | 747.4385 | N/A | 643.6299 | 1132.3118 | N/A | 659.3536 | 553.4312 | N/A | Line miles treated is not an appropriate metric for substation related investments | Line miles treated is not an appropriate metric for substation related investments | Line miles treated is not an appropriate metric for substation related investments |  | Ignition Risk -Equipment Failure | No | Yes | Program Owner Prioritized (See Narrative) | N/A | Maintenance of circuit breakers and reclosers used as substation circuit breakers | We are not planning to include this initiative. | Risk reduction not quantified. Initiative does not currently capture data found usable for risk reduction calculation. Attempt will be made to calculate the RSE for the 2022 WMP submission. | Maintenance
Grid hardening | Grid Design & System Hardening | 7.3.3.3 | 7.3.3.3 Covered conductor installation | Equipment Failure | No other drivers addressed | See Initiative 7.3.3.17.1 | N/A | lowUG: 4.40 to highUG: 4.50 | lowUG: 4.40 to highUG: 4.50 | lowUG: 4.40 to highUG: 4.50 | See Initiative 7.3.3.17.1 | N/A | Exceeds | GO 95 | 7.3.3.17.1 Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | Range represents values based on low to high UG miles ranging from 10% to 31% per year. | 448962 | 0 | 339.3 | lowUG: $254,100 to highUG: $188,312 | 0 | lowUG: 146 to highUG: 108.2 | lowUG: $659,660 to highUG: $495,659 | 0 | lowUG: 397 to highUG: 298.3 | Covered conductor in this initiative is in HFTDs | Covered conductor in this initiative is in HFTDs | Covered conductor in this initiative is in HFTDs |  | Ignition Risk - All Drivers | No | Yes | 2021 Wildfire Distribution Risk Model | Wildfire Distribution Risk Model | Covered conductor installation (narrative currently notes that PG&E does not have a standalone program to replace bare conductor with covered conductor; installation of covered conductor is part of System Hardening program). | 2021 | Risk reduction not quantified independently. Initiative complementary to 7.3.3.17.1. Please refer to 7.3.3.17.1. | System Hardening
Grid hardening | Grid Design & System Hardening | 7.3.3.4 | 7.3.3.4 Covered conductor maintenance | Equipment Failure | No other drivers addressed | 2018 | 1.7385 | 2491.7921 | 2119.7927 | 2119.3925 | 2020 GRC | FRMMA / WMPMA | In Compliance | GO 95 |  |  |  | 10670.643 | 8597.3799 | 24263 | 14419.982 | 9037.8945 | 24263 | 12496.0865 | 4058.1442 | 24263 | Assume that these remediations are tags/notifications resulting from inspections based on the new inspection cycle of 100% T3, 33% T2, 20% T1 going forward. For 2019 assumes 100% of Tiers 2&3 based on WSIP | Assume that these remediations are tags/notifications resulting from inspections based on the new inspection cycle of 100% T3, 33% T2, 20% T1 going forward. For 2019 assumes 100% of Tiers 2&3 based on WSIP | Assume that these remediations are tags/notifications resulting from inspections based on the new inspection cycle of 100% T3, 33% T2, 20% T1 going forward. For 2019 assumes 100% of Tiers 2&3 based on WSIP |  | Ignition Risk - All Drivers | Yes | Yes | Program Owner Prioritized (See Narrative) | Wildfire Distribution Risk Model | Covered conductor maintenance is a part of PG&E's routine overhead maintenance | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the likelihood of ignition risk, specifically mitigating the equipment failure driver and conductor subdriver, with an effectiveness as follows: Likelihood of ignition due to Equipment Failure of Conductor - 90% | Maintenance
Grid hardening | Grid Design & System Hardening | 7.3.3.5 | 7.3.3.5 Crossarm maintenance, repair, and replacement | Equipment Failure | No other drivers addressed | <2018 | 0.5585 | 535.1508 | 619.3008 | 619.2245 | 2020 GRC, Transmission Owners | FRMMA / WMPMA | Exceeds | GO95, GO165, FERC TPL Standards |  |  |  | 67301.3931 | 618.8625 | 54084 | 61025.0598 | 778.4836 | 54084 | 47523.6961 | 597.9065 | 54084 | Based on 2021 WMP write up, PG&E conducts annual patrols in urban areas and bi-annual patrols in rural areas, visually looking for damaged equipment and other defects on the distribution overhead system | Based on 2021 WMP write up, PG&E conducts annual patrols in urban areas and bi-annual patrols in rural areas, visually looking for damaged equipment and other defects on the distribution overhead system | Based on 2021 WMP write up, PG&E conducts annual patrols in urban areas and bi-annual patrols in rural areas, visually looking for damaged equipment and other defects on the distribution overhead system |  | Ignition Risk -Equipment Failure | Yes | Yes | Program Owner Prioritized (See Narrative) | N/A | Crossarm maintenance repair and replacement | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the likelihood of ignition risk, specifically mitigating the equipment failure driver and crossarm subdriver, with an effectiveness as follows: Likelihood of ignition due to Equipment Failure of Crossarm - 90% | Maintenance
Grid hardening | Grid Design & System Hardening | 7.3.3.6 | 7.3.3.6 Distribution pole replacement and reinforcement, including with composite poles | Equipment Failure | No other drivers addressed | <2018 | 0.20232 | 1610.3112 | 246.6917 | 377.9822 | 2020 GRC | FRMMA / WMPMA | Exceeds | GO 95 |  |  |  | 238786.0534 | 4783.4683 | 24263 | 301006.6627 | 3458.006 | 24263 | 356337.3161 | 3458.006 | 24263 | Assume that these remediations are tags/notifications resulting from inspections based on the new inspection cycle of 100% T3, 33% T2, 20% T1 going forward. For 2019 assumes 100% of Tiers 2&3 based on WSIP | Assume that these remediations are tags/notifications resulting from inspections based on the new inspection cycle of 100% T3, 33% T2, 20% T1 going forward. For 2019 assumes 100% of Tiers 2&3 based on WSIP | Assume that these remediations are tags/notifications resulting from inspections based on the new inspection cycle of 100% T3, 33% T2, 20% T1 going forward. For 2019 assumes 100% of Tiers 2&3 based on WSIP |  | Ignition Risk -Equipment Failure | Yes | Yes | Program Owner Prioritized (See Narrative) | Wildfire Distribution Risk Model | Distribution pole replacement and reinforcement which is part of PG&E's Pole Test & Treat program | 2022 | Drivers and RSEs can be seen in Table 12. This initiative reduces the likelihood of ignition risk, specifically mitigating the equipment failure driver and pole subdriver, with an effectiveness as follows: Likelihood of ignition due to Equipment Failure of Poles - 90% | Maintenance
Grid hardening | Grid Design & System Hardening | 7.3.3.7 | 7.3.3.7 Expulsion fuse replacement | Equipment Failure | No other drivers addressed | <2018 | 0 | 24.9046 | 25.1497 | 25.1503 | 2020 GRC | N/A | Exceeds | GO 95 |  |  |  | 7846.551 | 0 | 1219.1756 | 15124.923 | 0 | 2275.2889 | 15433.4726 | 0 | 2275.2889 | Based on recent re-count of non-exempt fuses (13,500) and the total HFTD mileage (25,597), mileage updated to match unit forecasts. | Based on recent re-count of non-exempt fuses (13,500) and the total HFTD mileage (25,597), mileage updated to match unit forecasts. | Based on recent re-count of non-exempt fuses (13,500) and the total HFTD mileage (25,597), mileage updated to match unit forecasts. |  | Ignition Risk -Equipment Failure | Yes | Yes | Program Owner Prioritized (See Narrative) | Wildfire Distribution Risk Model | Expulsion fuse replacement (eliminate non-exempt overhead line equipment in HFTD areas) | 2021 | Drivers and RSEs can be seen in Table 12. This initiative reduces the likelihood of ignition risk, specifically mitigating the equipment failure driver and fuse subdriver, with an effectiveness as follows: Likelihood of ignition due to Equipment Failure of Fuse/Cutout : 90% Fuse is only 42% of cutout/Fuse subdriver. Effectiveness at Cutout/Fuse subdriver is 90% * 42% = 37.6% | Operational Practices
Grid hardening | Grid Design & System Hardening | 7.3.3.8.1 | 7.3.3.8.1 Grid topology improvements to mitigate or reduce PSPS events, Distribution Line Sectionalizing | Consequence - PSPS | No other consequences reflected | 2019 | 0 | 39.4802 | 39.4802 | 39.4802 | 2020 GRC | N/A | Exceeds | GO 95 |  |  |  | 70044.7358 | 0 | N/A | 27627.6962 | 0 | N/A | 17623.0616 | 0 | N/A | Focus of switches is to reduce PSPS event scope, not related to "line miles treated" [Prior comment: Based on WMP write up 10 year program with 603 in 2020, 250 in 2021, and 100 in 2022, with at total of 1653 over the 10 years if 100 per year starting in 2022. Multiplied % by total HFTD miles.] | Focus of switches is to reduce PSPS event scope, not related to "line miles treated" [Prior comment: Based on WMP write up 10 year program with 603 in 2020, 250 in 2021, and 100 in 2022, with at total of 1653 over the 10 years if 100 per year starting in 2022. Multiplied % by total HFTD miles.] | Focus of switches is to reduce PSPS event scope, not related to "line miles treated" [Prior comment: Based on WMP write up 10 year program with 603 in 2020, 250 in 2021, and 100 in 2022, with at total of 1653 over the 10 years if 100 per year starting in 2022. Multiplied % by total HFTD miles.] |  | PSPS Consequence | Yes | Yes | Program Owner Prioritized (See Narrative) | Future State PSPS Consequence Model | Distribution segmentation strategies: (a) adding automated sectionalizing devices; (b) circuit reconfiguration / pre-PSPS Event switching; and (c) additional system hardening to support PSPS switching. | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the consequence of PSPS, specifically mitigating the impact to customers from PSPS events, with an effectiveness as follows: PSPS Impact Reduction Effectiveness - 1.7% | Operational Practices
Grid hardening | Grid Design & System Hardening | 7.3.3.8.2 | 7.3.3.8.2 Grid topology improvements to mitigate or reduce PSPS events, Transmission Line Sectionalizing | Consequence - PSPS | No other consequences reflected | 2020 | 0 | 255.1026 | 255.1026 | 255.1026 | Transmission Owner | N/A | N/A | N/A |  | Focus of switches is to reduce PSPS event scope, not related to "line miles treated" |  | 48850.3611 | 0 | N/A | 39185.1052 | 0 | N/A | 48155.642 | 0 | N/A | Focus of switches is to reduce PSPS event scope, not related to "line miles treated" [Prior comment: Based on WMP write up 10 year program with 603 in 2020, 250 in 2021, and 100 in 2022, with at total of 1653 over the 10 years if 100 per year starting in 2022. Multiplied % by total HFTD miles.] | Focus of switches is to reduce PSPS event scope, not related to "line miles treated" [Prior comment: Based on WMP write up 10 year program with 603 in 2020, 250 in 2021, and 100 in 2022, with at total of 1653 over the 10 years if 100 per year starting in 2022. Multiplied % by total HFTD miles.] | Focus of switches is to reduce PSPS event scope, not related to "line miles treated" [Prior comment: Based on WMP write up 10 year program with 603 in 2020, 250 in 2021, and 100 in 2022, with at total of 1653 over the 10 years if 100 per year starting in 2022. Multiplied % by total HFTD miles.] |  | PSPS Consequence | Yes | Yes | Program Owner Prioritized (See Narrative) | Future State PSPS Consequence Model | Installing SCADA switches on transmission lines to support faster restoration during outage events. | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the consequence of PSPS, specifically mitigating the impact to customers from PSPS events, with an effectiveness as follows: PSPS Impact Reduction Effectiveness - 12.5% | Operational Practices
Grid hardening | Grid Design & System Hardening | 7.3.3.8.3 | 7.3.3.8.3 Grid topology improvements to mitigate or reduce PSPS events, Distribution Line Motorized Switch Operator Pilot | N/A - Foundational | N/A - Foundational | 2020 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC | N/A | N/A | N/A |  |  |  | 119.2788 | 0 | N/A | 5262.4183 | 0 | N/A | 3356.7736 | 0 | N/A | Focus of switches is to reduce PSPS event scope, not related to "line miles treated" [Prior note: 54 SCADA switches were installed in T2 and T3 in 2019. However focus of the program was on reliability improvement. Focus switched for 2020 on mitigating PSPS impacts.] | Focus of switches is to reduce PSPS event scope, not related to "line miles treated" [Prior note: 54 SCADA switches were installed in T2 and T3 in 2019. However focus of the program was on reliability improvement. Focus switched for 2020 on mitigating PSPS impacts.] | Focus of switches is to reduce PSPS event scope, not related to "line miles treated" [Prior note: 54 SCADA switches were installed in T2 and T3 in 2019. However focus of the program was on reliability improvement. Focus switched for 2020 on mitigating PSPS impacts.] |  | PSPS Consequence | No | Yes | Program Owner Prioritized (See Narrative) | Future State PSPS Consequence Model |  | We are not planning to include this initiative. | Risk reduction not quantified. Foundational Initiative, for which distinct financial and quantification data not currently available. | Operational Practices
Grid hardening | Grid Design & System Hardening | 7.3.3.9.1 | 7.3.3.9.1 Installation of system automation equipment, Installation of System Automation Equipment | Equipment Failure, All Consequence | No other drivers addressed | <2018 | N/A | N/A | N/A | N/A | 2020 GRC | N/A | Exceeds | GO 95 |  |  |  | 17226.2273 | 10.1405 | N/A | 16996.1601 | 134.2274 | N/A | 15557.9593 | 138.1469 | N/A | Line miles treated is not an appropriate metric for substation related investments | Line miles treated is not an appropriate metric for substation related investments | Line miles treated is not an appropriate metric for substation related investments | The cells highlighted in orange in this row have been corrected to address a double-counting error in the financials. | Ignition Risk - Equipment Failure, Wildfire Consequences | No | No | N/A | N/A |  | We are not planning to include this initiative. | Risk reduction not quantified. Foundational Initiative, for which distinct financial and quantification data not currently available. | Operational Practices
Grid hardening | Grid Design & System Hardening | 7.3.3.9.2 | 7.3.3.9.2 Installation of system automation equipment, Single phase reclosers | Equipment Failure, All Consequence | No other drivers addressed | 2019 | N/A | N/A | N/A | N/A | 2020 GRC | N/A | Exceeds | GO 95 |  |  |  | 0 | 0 | N/A | 2304.747 | 0 | N/A | 2772.5253 | 0 | N/A | Line miles treated is not an appropriate metric for substation related investments | Line miles treated is not an appropriate metric for substation related investments | Line miles treated is not an appropriate metric for substation related investments |  | Ignition Risk - Equipment Failure, Wildfire Consequences | No | Yes | Program Owner Prioritized (See Narrative) | N/A |  | We are not planning to include this initiative. | Risk reduction not quantified. Foundational Initiative, for which distinct financial and quantification data not currently available. | Operational Practices
Grid hardening | Grid Design & System Hardening | 7.3.3.10 | 7.3.3.10 Maintenance, repair, and replacement of connectors, including hotline clamps | Equipment Failure | No other drivers addressed | <2018 | 1.3745 | 3913.7492 | 2632.1582 | 2697.7763 | 2020 GRC, Transmission Owners | FRMMA / WMPMA | Exceeds | GO95, GO165, PRC 4292, FERC TPL Standards |  |  |  | 1233.5027 | 7931.7331 | N/A | 199.4683 | 869.5081 | N/A | 172.8555 | 445.9096 | N/A | No particular line miles addressed, repairs are identified and managed through existing, other programs. [Prior note: Whole system, 100% for 2019 based on WSIP and 100% T3, 33% T2, 20% T1 based on new inspection cycle] | No particular line miles addressed, repairs are identified and managed through existing, other programs. [Prior note: Whole system, 100% for 2019 based on WSIP and 100% T3, 33% T2, 20% T1 based on new inspection cycle] | No particular line miles addressed, repairs are identified and managed through existing, other programs. [Prior note: Whole system, 100% for 2019 based on WSIP and 100% T3, 33% T2, 20% T1 based on new inspection cycle] |  | Ignition Risk -Equipment Failure | Yes | Yes | Program Owner Prioritized (See Narrative) | N/A |  | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the likelihood of ignition risk, specifically mitigating the equipment failure driver and Splice/Clamp/Connector subdriver, with an effectiveness as follows: Likelihood of ignition due to Equipment Failure of Splice/Clamp/Connector - 90% | Maintenance
Grid hardening | Grid Design & System Hardening | 7.3.3.11.1 | 7.3.3.11.1 Mitigation of impact on customers and other residents affected during PSPS event, Generation for PSPS Mitigation | Consequence - PSPS | No other consequences reflected | 2019 | 0 | 7.729 | 7.729 | 7.729 | 2020 GRC | Microgrid Memo Account FRMMA / WMPMA | N/A | N/A |  | Substation work is not related to circuit miles |  | 35952.7601 | 138451 | N/A | 47470.9987 | 103371.381 | N/A | 49257.893 | 131385.3859 | N/A | N/A 0 substation should not be calculated by circuit mile | N/A 0 substation should not be calculated by circuit mile | N/A 0 substation should not be calculated by circuit mile |  | PSPS Consequence | Yes | Yes | Program Owner Prioritized (See Narrative) | Future State PSPS Consequence Model |  | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the consequence of PSPS, specifically mitigating the impact to customers from PSPS events, with an effectiveness as follows: PSPS Impact Reduction Effectiveness - 1.2% | DGEM
Grid hardening | Grid Design & System Hardening | 7.3.3.11.2 | 7.3.3.11.2 Mitigation of impact on customers and other residents affected during PSPS event, Substation activities to enable reduction of PSPS impacts | N/A - Foundational | N/A - Foundational | 2020 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC, Transmission Owner | N/A | N/A | N/A |  | Substation work is not related to circuit miles |  | 11342.0273 | 0 | N/A | 2627.7738 | 0 | N/A | 0 | 0 | N/A | N/A 0 substation should not be calculated by circuit mile | N/A 0 substation should not be calculated by circuit mile | N/A 0 substation should not be calculated by circuit mile |  | PSPS Consequence | No | Yes | Program Owner Prioritized (See Narrative) | Future State PSPS Consequence Model |  | We are not planning to include this initiative. | Risk reduction not quantified. Foundational Initiative, for which distinct financial and quantification data not currently available. | Operational Practices
Grid hardening | Grid Design & System Hardening | 7.3.3.11.3 | 7.3.3.11.3 Mitigation of impact on customers and other residents affected during PSPS event, Emergency Back-up Generation – PG&E Service Centers & Materials Distribution Centers | N/A - Foundational | N/A - Foundational | 2021 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | WMCE | FRMMA / WMPMA | N/A | N/A |  | Facility specific work not related to line miles. |  | 38390.6442 | 544.5578 | N/A | 54764.521 | 1000 | N/A | 21272.963 | 1029.2 | N/A | CRESS Project - line miles not applicable | CRESS Project - line miles not applicable | CRESS Project - line miles not applicable |  | PSPS Consequence | No | Yes | Program Owner Prioritized (See Narrative) | Future State PSPS Consequence Model |  | We are not planning to include this initiative. | Risk reduction not quantified. Foundational Initiative, for which distinct financial and quantification data not currently available. | Operational Practices
Grid hardening | Grid Design & System Hardening | 7.3.3.12.1 | 7.3.3.12.1 Other corrective action, Distribution Substation | Animal | No other drivers addressed | <2018 | 0 | 0 | 0 | 0 | 2020 GRC | FRMMA / WMPMA | N/A | N/A |  |  |  | 4960.89 | 4117.7435 | N/A | 4533.1822 | 4664.3344 | N/A | 5419.3287 | 4796.8891 | N/A | N/A 0 substation should not be calculated by circuit mile | N/A 0 substation should not be calculated by circuit mile | N/A 0 substation should not be calculated by circuit mile |  | Ignition Risk - Animal | Yes | Yes | Program Owner Prioritized (See Narrative) | N/A |  | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the likelihood of ignition risk under category Distance Gap and sub driver Natural/Outside force with an effectiveness as follows: Likelihood of ignition - 15% | Operational Practices
Grid hardening | Grid Design & System Hardening | 7.3.3.12.2 | 7.3.3.12.2 Other corrective action, Transmission Substation | Animal | No other drivers addressed | <2018 | 0 | 0 | 0 | 0 | Transmission Owner | N/A | N/A | N/A |  |  |  | 958.5485 | 1717.5279 | N/A | 2881.7326 | 2572.4205 | N/A | 1827.8001 | 3258.9829 | N/A | N/A 0 substation should not be calculated by circuit mile | N/A 0 substation should not be calculated by circuit mile | N/A 0 substation should not be calculated by circuit mile |  | Ignition Risk - Animal | Yes | Yes | Program Owner Prioritized (See Narrative) | N/A |  | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the likelihood of ignition risk under category Distance Gap and sub driver Natural/Outside force with an effectiveness as follows: Likelihood of ignition - 15% | Operational Practices
Grid hardening | Grid Design & System Hardening | 7.3.3.12.3 | 7.3.3.12.3 Other corrective action, Maintenance, Transmission | Equipment Failure | No other drivers addressed | <2018 | 0.0020362 | 0 | 13.7573 | 13.7573 | Transmission Owner | N/A | In Compliance | GO95, GO165, FERC TPL Standards |  |  |  | 453389.7051 | 98704.3026 | 5234.6 | 442630.7354 | 100936.2257 | 5234.6 | 276800.7052 | 113644.082 | 5234.6 | Transmission 100% for 2019 based on WSIP and 100% T3, 33% T2, 20% T1 based on new inspection cycle | Transmission 100% for 2019 based on WSIP and 100% T3, 33% T2, 20% T1 based on new inspection cycle | Transmission 100% for 2019 based on WSIP and 100% T3, 33% T2, 20% T1 based on new inspection cycle |  | Ignition Risk -Equipment Failure | Yes | Yes | Program Owner Prioritized (See Narrative) | N/A |  | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the likelihood of ignition risk, specifically mitigating the equipment failure driver and Equipment-Other subdriver, with an effectiveness as follows: Likelihood of ignition due to Equipment Failure of Equipment-Other - 90% | Maintenance
Grid hardening | Grid Design & System Hardening | 7.3.3.12.4 | 7.3.3.12.4 Other corrective action, Maintenance, Distribution | Equipment Failure | No other drivers addressed | <2018 | 0.12435 | 212.457 | 212.457 | 212.457 | 2020 GRC | FRMMA / WMPMA | In Compliance | GO 95 |  |  |  | 249937.5369 | 98481.9083 | 24263 | 259826.5092 | 62218.4855 | 24263 | 257591.3088 | 39681.8232 | 24263 | 100% for 2019 based on WSIP and 100% T3, 33% T2, 20% T1 based on new inspection cycle | 100% for 2019 based on WSIP and 100% T3, 33% T2, 20% T1 based on new inspection cycle | 100% for 2019 based on WSIP and 100% T3, 33% T2, 20% T1 based on new inspection cycle |  | Ignition Risk -Equipment Failure | Yes | Yes | Program Owner Prioritized (See Narrative) | N/A |  | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the likelihood of ignition risk, specifically mitigating the Vegetation, Unk or Other, 3rd Party drivers and Other/Unknown, Unk or Other - Other, 3rd Party - Other sub-drivers, with an effectiveness as follows: Likelihood of ignition due to Vegetation, Unk or Other, 3rd Party of Other/Unknown, Unk or Other - Other, 3rd Party - Other - 90% | Maintenance
Grid hardening | Grid Design & System Hardening | 7.3.3.13 | 7.3.3.13 Pole loading infrastructure hardening and replacement program based on pole loading assessment program | Equipment Failure | No other drivers addressed | <2018 | 0.17899 | 64.8548 | 64.8133 | 65.0528 | 2020 GRC | FRMMA / WMPMA | Exceeds | GO 95 |  |  |  | 13772.3389 | 61.0714 | 6359.75 | 12440.4137 | 152 | 6359.75 | 8190 | 19 | 6359.75 | 4 year program for HFTD, T1 will occur after 2024. | 4 year program for HFTD, T1 will occur after 2024. | 4 year program for HFTD, T1 will occur after 2024. |  | Ignition Risk -Equipment Failure | Yes | Yes | Program Owner Prioritized (See Narrative) | N/A |  | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the likelihood of ignition risk, specifically mitigating the equipment failure driver and pole subdriver, with an effectiveness as follows: Likelihood of ignition due to Equipment Failure of Poles - 90% | Maintenance
Grid hardening | Grid Design & System Hardening | 7.3.3.14 | 7.3.3.14 Transformers maintenance and replacement | Equipment Failure | No other drivers addressed | <2018 | 0.1085 | 38.6403 | 38.6378 | 38.6539 | 2020 GRC | FRMMA / WMPMA | Exceeds | GO 95 |  |  |  | 89274.4055 | 60.5671 | 24263 | 124240.3371 | 43.6193 | 24263 | 94822.2253 | 19.5857 | 24263 | 100% for 2019 based on WSIP and 100% T3, 33% T2, 20% T1 based on new inspection cycle | 100% for 2019 based on WSIP and 100% T3, 33% T2, 20% T1 based on new inspection cycle | 100% for 2019 based on WSIP and 100% T3, 33% T2, 20% T1 based on new inspection cycle |  | Ignition Risk -Equipment Failure | Yes | Yes | Wildfire Consequence Model | Wildfire Distribution Risk Model, Wildfire Consequence Model |  | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the likelihood of ignition risk, specifically mitigating the equipment failure driver and transformer subdriver, with an effectiveness as follows: Likelihood of ignition due to Equipment Failure of Transformer - 90% | Maintenance
Grid hardening | Grid Design & System Hardening | 7.3.3.15 | 7.3.3.15 Transmission tower maintenance and replacement | Equipment Failure | No other drivers addressed | <2018 | N/A | N/A | N/A | N/A | Transmission Owner | N/A | Exceeds | GO95, GO165 |  |  |  | 41221.0384 | 50942.2682 | 5234.6 | 40400.6545 | 55276.7962 | 5234.6 | 41147 | 74000 | 5234.6 | Transmission 100% for 2019 based on WSIP and 100% T3, 33% T2, 20% T1 based on new inspection cycle | Transmission 100% for 2019 based on WSIP and 100% T3, 33% T2, 20% T1 based on new inspection cycle | Transmission 100% for 2019 based on WSIP and 100% T3, 33% T2, 20% T1 based on new inspection cycle |  | Ignition Risk -Equipment Failure | No | Yes | Transmission Operability Assessment Model | Wildfire Transmission Risk Model |  | We are not planning to include this initiative. | Risk reduction not quantified. Initiative does not currently capture data found usable for risk reduction calculation. Attempt will be made to calculate the RSE for the 2022 WMP submission. | Maintenance
Grid hardening | Grid Design & System Hardening | 7.3.3.16 | 7.3.3.16 Undergrounding of electric lines and/or equipment | N/A - Complementary | N/A - Complementary | <2018 | N/A | lowUG: 3.51 to highUG: 3.50 | lowUG: 3.51 to highUG: 3.50 | lowUG: 3.51 to highUG: 3.50 | N/A | N/A | Exceeds | GO 95 | 7.3.3.17.1 Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution |  | Range represents values based on low to high UG miles ranging from 10% to 31% per year. | 11180 | 0 | 2.7 | lowUG: $79,200 to highUG: $245,520 | 0 | lowUG: 18 to highUG: 55.8 | lowUG: $204,160 to highUG: $632,896 | 0 | lowUG: 47 to highUG: 145.7 |  |  |  |  | Ignition Risk -Equipment Failure | No | Yes | 2021 Wildfire Distribution Risk Model | Wildfire Distribution Risk Model |  | 2021 | Risk reduction not quantified independently. Initiative complementary to 7.3.3.17.1. Please refer to 7.3.3.17.1. | System Hardening
Grid hardening | Grid Design & System Hardening | 7.3.3.17.1 | 7.3.3.17.1 Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution | Equipment Failure, Vegetation, Animal, 3rd Party | No other drivers addressed | 2018 | 0 | lowUG: 4.6 to highUG: 4.3 | lowUG: 4.6 to highUG: 4.3 | lowUG: 4.6 to highUG: 4.3 | 2020 GRC | N/A | Exceeds | GO 95 |  |  |  | 460142.0956 | 0 | 342 | 338400 | 0 | 180 | 872320 | 0 | 470 | Metric is miles, based on narrative, 180 in 2021, 464 in 2022 (2021-2023 target is to complete 1127 miles) | Metric is miles, based on narrative, 180 in 2021, 464 in 2022 (2021-2023 target is to complete 1127 miles) | Metric is miles, based on narrative, 180 in 2021, 464 in 2022 (2021-2023 target is to complete 1127 miles) |  | Ignition Risk - Equipment Failure, Vegetation, Animal, 3rd Party | Yes | Yes | 2021 Wildfire Distribution Risk Model | Wildfire Distribution Risk Model |  | 2021 | Drivers and RSEs can be seen in Table 12. Referred to the RAMP_filing, M2-System hardening program and utilized the Mitigation Effectiveness % calculations. Please refer to 7.3.3.17.1 M2 ¦ Summary Analysis tab in the ERRATA_7.3.3_RSE Input Template_EO_WLDFR. | System Hardening
Grid hardening | Grid Design & System Hardening | 7.3.3.17.2 | 7.3.3.17.2 Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Transmission | Equipment Failure | No other drivers addressed | 2019 | N/A | N/A | N/A | N/A | Transmission Owner | N/A | Exceeds | GO95, GO165, FERC TPL Standards |  |  |  | 203036.2366 | 0 | N/A | 273713.0238 | 0 | 92 | 276057.4717 | 0 | TBD | Miles to be treated reference the 92 miles of Transmission Conductor to be replaced in HFTD areas in 2021. [Prior note: Only program in this section that miles could apply to is 71Z ROW clearing] | Miles to be treated reference the 92 miles of Transmission Conductor to be replaced in HFTD areas in 2021. [Prior note: Only program in this section that miles could apply to is 71Z ROW clearing] | Miles to be treated reference the 92 miles of Transmission Conductor to be replaced in HFTD areas in 2021. [Prior note: Only program in this section that miles could apply to is 71Z ROW clearing] | The cells highlighted in orange in this row have been corrected to address a double-counting error in the financials. | Ignition Risk -Equipment Failure | No | Yes | Transmission Operability Assessment Model | Wildfire Transmission Risk Model |  | 2021 | Risk reduction not quantified. Initiative does not currently capture data found usable for risk reduction calculation. Attempt will be made to calculate the RSE for the 2022 WMP submission. | System Hardening
Grid hardening | Grid Design & System Hardening | 7.3.3.17.3 | 7.3.3.17.3 Updates to grid topology to minimize risk of ignition in HFTDs, Surge Arrestor | Equipment Failure | No other drivers addressed | <2018 | 0.04882 | 2.6743 | 2.69 | 2.6921 | 2020 GRC | N/A | Exceeds | GO 95 |  |  |  | 63497.9185 | 0 | 12926.4383 | 88859.3889 | 0 | 19245.6504 | 16853.5704 | 0 | TBD | Utilized risk reduction % assumptions for each year and applied to line miles . Total units over program will be 90k, used 2020:14,362, 2021:21,383 and 2022:TBD units to calculate percentage (e.g. 14,362/90,000=15.95%) and applied to total distribution system miles (e.g. 15,95%*81,004 miles). | Utilized risk reduction % assumptions for each year and applied to line miles . Total units over program will be 90k, used 2020:14,362, 2021:21,383 and 2022:TBD units to calculate percentage (e.g. 14,362/90,000=15.95%) and applied to total distribution system miles (e.g. 15,95%*81,004 miles). | Utilized risk reduction % assumptions for each year and applied to line miles . Total units over program will be 90k, used 2020:14,362, 2021:21,383 and 2022:TBD units to calculate percentage (e.g. 14,362/90,000=15.95%) and applied to total distribution system miles (e.g. 15,95%*81,004 miles). |  | Ignition Risk -Equipment Failure | Yes | Yes | Program Owner Prioritized (See Narrative) | Wildfire Distribution Risk Model |  | 2021 | Drivers and RSEs can be seen in Table 12. Referred to PG&E's 2020 RAMP Report, M2-System hardening program and utilized the Mitigation Effectiveness % calculations, from the M2 ¦ Summary Analysis tab for Surge Arrestor - 90% | Operational Practices
Grid hardening | Grid Design & System Hardening | 7.3.3.17.4 | 7.3.3.17.4 Updates to grid topology to minimize risk of ignition in HFTDs, Rapid Earth Current Fault Limiter | Equipment Failure, Vegetation | No other drivers addressed | 2019 | 0 | 36.3528 | 36.3528 | 36.3528 | EPIC | FRMMA / WMPMA | N/A | N/A |  |  |  | 4798.22 | 6425.33 | N/A | 8224 | 0 | N/A | 16924.992 | 0 | N/A | A long-term plan will be developed after successful completion of the pilot and identifications of lessons learned in 2021 | A long-term plan will be developed after successful completion of the pilot and identifications of lessons learned in 2021 | A long-term plan will be developed after successful completion of the pilot and identifications of lessons learned in 2021 |  | Ignition Risk -Equipment Failure, Vegetation | Yes | Yes | Program Owner Prioritized (See Narrative) | Wildfire Distribution Risk Model |  | 2022 | Drivers and RSEs can be seen in Table 12. Mitigation effectiveness analysis was conducted by analyzing the Feb 2013 – April 2018 distribution ignition data with its fault type. The analysis process flow is as follows: Assigning quantitative effectiveness values to determine ignitions that potentially would be mitigated by installing REFCL: REFCL Subject Matter Expert reviewed the fault type of ignitions at 12kV, identifying whether it is Line to Ground fault, or Line to Line to Ground Fault. SMEs applied the following estimates of mitigation effectiveness for the REFCL to different types of fault type: 1. Line to Ground Faults: 92%. 2. Line to Line to Ground Faults: the current Ground Fault Neutralizer (GFN) design is likely to achieve significant (50-90%) mitigation of ignition risk from complex faults that present as two-phases-to-ground earth faults. Assumed 50% for this analysis. Total number of ignitions at 12 kV with Line to Ground Faults: 175 Total number of ignitions at 12 kV with Line to Line to Ground Faults: 16 Total number of ignitions at 12 kV with all Fault types: 292* Effectiveness = (175*92%+16*50%)/292 = 58% * Ignored 38 ignitions that were not able to identify fault types. | Operational Practices
Grid hardening | Grid Design & System Hardening | 7.3.3.17.5 | 7.3.3.17.5 Updates to grid topology to minimize risk of ignition in HFTDs, Remote Grid | N/A - Complementary | N/A - Complementary | 2020 | N/A | 36.5971 | 36.5971 | 36.5971 | N/A | FRMMA / WMPMA | Exceeds | GO 95 | Initiative 7.3.3.17.5 only shows PMO team costs. Construction financial costs are part of 7.3.3.17.1: Updates to grid topology to minimize risk of ignition in HFTDs, System Hardening, Distribution. |  | Range represents values based on low to high UG miles ranging from 10% to 31% per year. | 0 | 755.2311 | N/A | 5100 | 1382.4175 | 16 | 8500 | 1422.6459 | 26 | PG&E has not determined a long-term plan yet for this initiative. Pending the success of initial Remote Grid projects, we will be evaluating the reduction in wildfire ignition risk and costs, engineering and execution feasibility, and overall service quality in order to determine the long-term path and program scalability | PG&E has not determined a long-term plan yet for this initiative. Pending the success of initial Remote Grid projects, we will be evaluating the reduction in wildfire ignition risk and costs, engineering and execution feasibility, and overall service quality in order to determine the long-term path and program scalability | PG&E has not determined a long-term plan yet for this initiative. Pending the success of initial Remote Grid projects, we will be evaluating the reduction in wildfire ignition risk and costs, engineering and execution feasibility, and overall service quality in order to determine the long-term path and program scalability |  | Ignition Risk -Equipment Failure | No | Yes | Program Owner Prioritized (See Narrative) | Wildfire Distribution Risk Model |  | 2022 | Risk reduction not quantified independently. Initiative complementary to 7.3.3.17.1. Please refer to 7.3.3.17.1. | Operational Practices
Grid hardening | Grid Design & System Hardening | 7.3.3.17.6 | 7.3.3.17.6 Updates to grid topology to minimize risk of ignition in HFTDs, Butte County Rebuild | All Drivers | All Drivers | 2019 | 0.0096936 | 9.3422 | 9.3422 | 9.3422 | N/A | N/A | Exceeds | GO 95 |  |  |  | 29796.1122 | 0 | 30 | 53555.04 | 0 | 23 | 55429.4664 | 0 | 23 | The impacted area is primarily in T2 and T3 areas | The impacted area is primarily in T2 and T3 areas | The impacted area is primarily in T2 and T3 areas |  | Ignition Risk - All Drivers | Yes | Yes | Program Owner Prioritized (See Narrative) | Wildfire Distribution Risk Model |  | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. Undergrounding of electric assets eliminated the risk of ignition caused by all Drivers by 100%. To be conservative, program effectiveness of 95% is used. | System Hardening
Asset inspection | Asset Management & Inspections | 7.3.4.1 | 7.3.4.1 Detailed inspections of distribution electric lines and equipment | Equipment Failure | No other drivers addressed | <2018 | 0.12125 | 75.3757 | 37.2864 | 52.0254 | 2020 GRC | FRMMA / WMPMA | In Compliance | GO 165 |  |  |  | 0 | 132613.9446 | 24263 | 0 | 95924.4351 | 24263 | 0 | 65903.4965 | 24263 | 100% for 2019 based on WSIP and 100% T3, 33% T2, 20% T1 based on new inspection cycle | 100% for 2019 based on WSIP and 100% T3, 33% T2, 20% T1 based on new inspection cycle | 100% for 2019 based on WSIP and 100% T3, 33% T2, 20% T1 based on new inspection cycle |  | Ignition Risk -Equipment Failure | Yes | Yes | Program Owner Prioritized (See Narrative) | Wildfire Distribution Risk Model |  | 2021 | Drivers and RSEs can be seen in Table 12. This initiative reduces the likelihood of ignition risk, specifically mitigating the equipment failure driver, with an effectiveness as follows: Likelihood of ignition due to Equipment Failure - 52.65% | Inspections
Asset inspection | Asset Management & Inspections | 7.3.4.2 | 7.3.4.2 Detailed inspections of transmission electric lines and equipment | Equipment Failure | No other drivers addressed | <2018 | 0.0041799 | 113.3854 | 8.0878 | 120.2557 | Transmission Owner | N/A | In Compliance | GO 165 |  |  |  | 0 | 89857.2372 | 5234.6 | 0 | 105104.218 | 5234.6 | 0 | 109048.312 | 5234.6 | Transmission 100% for 2019 based on WSIP and 100% T3, 33% T2, 20% T1 based on new inspection cycle | Transmission 100% for 2019 based on WSIP and 100% T3, 33% T2, 20% T1 based on new inspection cycle | Transmission 100% for 2019 based on WSIP and 100% T3, 33% T2, 20% T1 based on new inspection cycle |  | Ignition Risk -Equipment Failure | Yes | Yes | Program Owner Prioritized (See Narrative) | Wildfire Transmission Risk Model |  | 2021 | Drivers and RSEs can be seen in Table 12. This initiative reduces the likelihood of ignition risk, specifically mitigating the equipment failure driver, with an effectiveness as follows: Likelihood of ignition due to Equipment Failure - 95.39% | Inspections
Asset inspection | Asset Management & Inspections | 7.3.4.3 | 7.3.4.3 Improvement of inspections | Equipment Failure | No other drivers addressed | <2018 | 314.261 | 89375.4303 | 89375.4303 | 89375.4303 | 2020 GRC | FRMMA / WMPMA | N/A | N/A |  |  |  | 0 | 223.8438 | N/A | 0 | 14.9078 | N/A | 0 | 31.6082 | N/A | Line miles treated is not an appropriate metric for a system/process improvement | Line miles treated is not an appropriate metric for a system/process improvement | Line miles treated is not an appropriate metric for a system/process improvement |  | Ignition Risk -Equipment Failure | Yes | Yes | Program Owner Prioritized (See Narrative) | N/A |  | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the likelihood of ignition risk, specifically mitigating the equipment failure driver with an effectiveness as follows: Administrative Barrier category, addressing Human Error Risk driver - 8.4% | Inspections
Asset inspection | Asset Management & Inspections | 7.3.4.4 | 7.3.4.4 Infrared inspections of distribution electric lines and equipment | Equipment Failure | No other drivers addressed | <2018 | 0.12509 | 35.69 | 35.69 | 35.69 | 2020 GRC | N/A | Exceeds | GO 165 |  |  |  | 0 | 1561.3355 | N/A | 0 | 2319.9993 | N/A | 0 | 2319.9993 | N/A | Line miles treated is not an appropriate metric for a system/process improvement | Line miles treated is not an appropriate metric for a system/process improvement | Line miles treated is not an appropriate metric for a system/process improvement |  | Ignition Risk -Equipment Failure | Yes | Yes | 2021 Wildfire Distribution Risk Model | Wildfire Distribution Risk Model |  | 2023 or later | Drivers and RSEs can be seen in Table 12. This initiative reduces the likelihood of ignition risk, specifically mitigating the equipment failure driver, with an effectiveness as follows: Likelihood of ignition due to Equipment Failure - 2.03% | Inspections
Asset inspection | Asset Management & Inspections | 7.3.4.5 | 7.3.4.5 Infrared inspections of transmission electric lines and equipment | Equipment Failure | No other drivers addressed | <2018 | 0.0013815 | 2.2657 | 2.2657 | 2.2771 | Transmission Owner | N/A | In Compliance | GO95, GO165 |  |  |  | 0 | 1443.6 | 5234.6 | 0 | 2219.646 | 5234.6 | 0 | 2219.646 | 5234.6 | Transmission 100% for 2019 based on WSIP and 100% T3, 33% T2, 20% T1 based on new inspection cycle | Transmission 100% for 2019 based on WSIP and 100% T3, 33% T2, 20% T1 based on new inspection cycle | Transmission 100% for 2019 based on WSIP and 100% T3, 33% T2, 20% T1 based on new inspection cycle |  | Ignition Risk -Equipment Failure | Yes | Yes | Program Owner Prioritized (See Narrative) | Wildfire Transmission Risk Model |  | 2023 or later | Drivers and RSEs can be seen in Table 12. This initiative reduces the likelihood of ignition risk, specifically mitigating the equipment failure driver, with an effectiveness as follows: Likelihood of ignition due to Equipment Failure - 0.75% | Inspections
Asset inspection | Asset Management & Inspections | 7.3.4.6 | 7.3.4.6 Intrusive pole inspections | Equipment Failure | No other drivers addressed | <2018 | 0.025047 | 0 | 4.573 | 4.8403 | 2020 GRC | N/A | Exceeds | GO 165 & GO 95 rule 44.3 |  |  |  | 0 | 17446.6652 | 8100.4 | 0 | 21227.0659 | 8100.4 | 0 | 21227.0659 | 8100.4 | Based on a ten year cycle | Based on a ten year cycle | Based on a ten year cycle |  | Ignition Risk -Equipment Failure | Yes | Yes | Program Owner Prioritized (See Narrative) | Wildfire Distribution Risk Model |  | 2023 or later | Drivers and RSEs can be seen in Table 12. This initiative reduces the likelihood of ignition risk, specifically mitigating the equipment failure driver, with an effectiveness as follows: Likelihood of ignition due to Equipment Failure - Pole: 92.41% | Inspections
Asset inspection | Asset Management & Inspections | 7.3.4.7 | 7.3.4.7 LiDAR Inspections of Distribution Electric Lines and Equipment | N/A - Pilot | N/A - Pilot | <2018 | N/A - Pilot | N/A - Pilot | N/A - Pilot | N/A - Pilot | 2020 GRC | N/A | Exceeds | GO 165 |  |  |  | 0 | 6100 | 3000 | 0 | 4500 | N/A | 0 | 6500 | N/A | Updated based on language in the 2021 WMP narrative. | In 2021, evaluation of how to effectively integrate the data into existing operational tools will be conducted. Based on the effectiveness of operationalizing the derivative LiDAR products, additional LiDAR collection may be planned and considered for non HFTD areas. | In 2021, evaluation of how to effectively integrate the data into existing operational tools will be conducted. Based on the effectiveness of operationalizing the derivative LiDAR products, additional LiDAR collection may be planned and considered for non HFTD areas. |  | Ignition Risk -Equipment Failure | No | No | N/A | N/A |  | We are not planning to include this initiative. | Risk reduction not quantified. As a pilot initiative, the necessary data to evaluate risk reduction has not been captured, but this technology has the potential to reduce risk of ignitions by determining the condition of the assets after they have been identified in the field. | Inspections
Asset inspection | Asset Management & Inspections | 7.3.4.8 | 7.3.4.8 LiDAR Inspections of Transmission Electric Lines and Equipment | Equipment Failure | No other drivers addressed | See Initiative 7.3.5.8 | N/A | N/A | N/A | N/A | See Initiative 7.3.5.8 | See Initiative 7.3.5.8 | See Initiative 7.3.5.8 | See Initiative 7.3.5.8 | 7.3.5.8 LiDAR inspections of vegetation around transmission electric lines and equipment |  |  | 0 | 0 | N/A | 0 | 0 | N/A | 0 | 0 | N/A | PG&E does not have a long-term plan established for LiDAR inspections of electric transmission assets. As noted above, PG&E is exploring the use of this technology which may, or may not, result in the development of a program to leverage this technology for asset inspections in the future. | PG&E does not have a long-term plan established for LiDAR inspections of electric transmission assets. As noted above, PG&E is exploring the use of this technology which may, or may not, result in the development of a program to leverage this technology for asset inspections in the future. | PG&E does not have a long-term plan established for LiDAR inspections of electric transmission assets. As noted above, PG&E is exploring the use of this technology which may, or may not, result in the development of a program to leverage this technology for asset inspections in the future. |  | Ignition Risk -Equipment Failure | No | No | N/A | N/A |  | We are not planning to include this initiative. | Risk reduction not quantified. Initiative does not currently capture data determined to be usable for RSE calculation. Attempt will be made to calculate the RSE for the 2022 WMP submission. | Inspections
Asset inspection | Asset Management & Inspections | 7.3.4.9 | 7.3.4.9 Other discretionary inspection of distribution electric lines and equipment, beyond inspections mandated by rules and regulations | N/A - Complementary | N/A - Complementary | See Initiatives 7.3.4.1 and 7.3.4.4 | See Initiatives 7.3.4.1 and 7.3.4.4 | See Initiatives 7.3.4.1 and 7.3.4.4 | See Initiatives 7.3.4.1 and 7.3.4.4 | See Initiatives 7.3.4.1 and 7.3.4.4 | See Initiatives 7.3.4.1 and 7.3.4.4 | See Initiatives 7.3.4.1 and 7.3.4.4 | See Initiatives 7.3.4.1 and 7.3.4.4 | See Initiatives 7.3.4.1 and 7.3.4.4 | 7.3.4.1 Detailed inspections of distribution electric lines and equipment, and 7.3.4.4 Infrared inspections of distribution electric lines and equipment |  |  | 0 | 0 | 24263 | 0 | 0 | 24263 | 0 | 0 | 24263 | 100% for 2019 based on WSIP and 100% T3, 33% T2, 20% T1 based on new inspection cycle | 100% for 2019 based on WSIP and 100% T3, 33% T2, 20% T1 based on new inspection cycle | 100% for 2019 based on WSIP and 100% T3, 33% T2, 20% T1 based on new inspection cycle |  | Ignition Risk -Equipment Failure | No | No | N/A | N/A |  | We are not planning to include this initiative. | Risk reduction not quantified independently. Initiative complementary to 7.3.4.1 & 7.3.4.4. Please refer to 7.3.4.1 & 7.3.4.4. | Inspections
Asset inspection | Asset Management & Inspections | 7.3.4.10 | 7.3.4.10 Other discretionary inspection of transmission electric lines and equipment, beyond inspections mandated by rules and regulations | N/A - Pilot | N/A - Pilot | <2018 | N/A - Pilot | N/A - Pilot | N/A - Pilot | N/A - Pilot | Transmission Owner | N/A | In Compliance | GO95, GO165 |  |  |  | 80 | 267.2554 | 5234.6 | 81.9544 | 274.558 | 5234.6 | 86.0134 | 289.6665 | 5234.6 | Transmission 100% for 2019 based on WSIP and 100% T3, 33% T2, 20% T1 based on new inspection cycle | Transmission 100% for 2019 based on WSIP and 100% T3, 33% T2, 20% T1 based on new inspection cycle | Transmission 100% for 2019 based on WSIP and 100% T3, 33% T2, 20% T1 based on new inspection cycle |  | Ignition Risk -Equipment Failure | No | Yes | Program Owner Prioritized (See Narrative) | Wildfire Transmission Risk Model |  | We are not planning to include this initiative. | Risk reduction not quantified. As a pilot initiative, the necessary data to evaluate risk reduction has not been captured, but this technology has the potential to reduce risk of ignitions due to equipment failures by identifying/detecting any potential failure modes may not be easily detectable, including those not visible through a visual inspection, before a failure occurs. | Inspections
Asset inspection | Asset Management & Inspections | 7.3.4.11 | 7.3.4.11 Patrol inspections of distribution electric lines and equipment | Equipment Failure | No other drivers addressed | <2018 | 0.20722 | 58.5608 | 58.5608 | 0 | 2020 GRC | N/A | In Compliance | GO 165 |  |  |  | 0 | 8710.2209 | 56541 | 0 | 9281.0109 | 56541 | 0 | 9281.0109 | 56541 | Based on 0% in T3, 66% T 2 and 80% Non-HFTD annually (all miles that are not inspected are patrolled) | Based on 0% in T3, 66% T 2 and 80% Non-HFTD annually (all miles that are not inspected are patrolled) | Based on 0% in T3, 66% T 2 and 80% Non-HFTD annually (all miles that are not inspected are patrolled) |  | Ignition Risk -Equipment Failure | Yes | Yes | Program Owner Prioritized (See Narrative) | N/A |  | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the likelihood of ignition risk, specifically mitigating the equipment failure driver, with an effectiveness as follows: Likelihood of ignition due to Equipment Failure - 3.58% | Inspections
Asset inspection | Asset Management & Inspections | 7.3.4.12 | 7.3.4.12 Patrol inspections of transmission electric lines and equipment | Equipment Failure | No other drivers addressed | <2018 | 4.5713 | 7136.0651 | 7136.0651 | 0 | Transmission Owner | N/A | In Compliance | GO95, GO167 |  |  |  | 0 | 47.9886 | 13400 | 0 | 86.3754 | 13400 | 0 | 83.6831 | 13400 | Based on 0% in T3, 66% T 2 and 80% Non-HFTD annually (all miles that are not inspected are patrolled) | Based on 0% in T3, 66% T 2 and 80% Non-HFTD annually (all miles that are not inspected are patrolled) | Based on 0% in T3, 66% T 2 and 80% Non-HFTD annually (all miles that are not inspected are patrolled) |  | Ignition Risk -Equipment Failure | Yes | Yes | Program Owner Prioritized (See Narrative) | N/A |  | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the likelihood of ignition risk, specifically mitigating the equipment failure driver, with an effectiveness as follows: Likelihood of ignition due to Equipment Failure - 28.65% | Inspections
Asset inspection | Asset Management & Inspections | 7.3.4.13 | 7.3.4.13 Pole loading assessment program to determine safety factor | Equipment Failure | No other drivers addressed | <2018 | 0 | 2.0754 | 3.9204 | 2.0537 | N/A | FRMMA / WMPMA | Exceeds | GO 165 |  |  |  | 0 | 18604.3079 | 6359.75 | 0 | 14540 | 6359.75 | 0 | 13094 | 6359.75 | Narrative states that goal is to complete all HFTD poles by 2024. Assumed 25% per year for 2020, 2021 and 2022. | Narrative states that goal is to complete all HFTD poles by 2024. Assumed 25% per year for 2020, 2021 and 2022. | Narrative states that goal is to complete all HFTD poles by 2024. Assumed 25% per year for 2020, 2021 and 2022. |  | Ignition Risk -Equipment Failure | Yes | Yes | Program Owner Prioritized (See Narrative) | N/A |  | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the likelihood of ignition risk, specifically mitigating the equipment failure driver with an effectiveness as follows: Detect/Notify/Respond category, addressing Functional Failure Risk driver - 6.9% | Inspections
Asset inspection | Asset Management & Inspections | 7.3.4.14 | 7.3.4.14 Quality assurance / quality control of inspections | Equipment Failure | No other drivers addressed | <2018 | 12.1473 | 3449.6335 | 3449.6335 | 3449.6335 | 2020 GRC | FRMMA / WMPMA | Exceeds | GO 165 |  |  |  | 0 | 1831.4492 | N/A | 0 | 121.973 | N/A | 0 | 258.6127 | N/A | Line miles is not an appropriate metric for these other initiatives | Line miles is not an appropriate metric for these other initiatives | Line miles is not an appropriate metric for these other initiatives |  | Ignition Risk -Equipment Failure | Yes | Yes | Program Owner Prioritized (See Narrative) | N/A |  | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the likelihood of ignition risk, specifically mitigating the equipment failure driver with an effectiveness as follows: Administrative Barrier category, addressing Human Error Risk driver - 11.4% | Inspections
Asset inspection | Asset Management & Inspections | 7.3.4.15-T | 7.3.4.15-T Substation inspections, Enhanced Transmission, Substation | All Drivers | All Drivers | 2018 | 0.00112 | 0 | 0 | 0 | Transmission Owner | N/A | Exceeds | GO 174, CAISO TCA (Transmission Control Agreement) |  |  |  | 0 | 11267.8134 | N/A | 0 | 5226.7995 | N/A | 0 | 3360.18 | N/A | Line Miles = N/A as substation assets are not associated with circuit miles | Line Miles = N/A as substation assets are not associated with circuit miles | Line Miles = N/A as substation assets are not associated with circuit miles |  | Ignition Risk -Equipment Failure | Yes | Yes | Program Owner Prioritized (See Narrative) | N/A |  | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the likelihood of ignition risk mitigating all drivers, with an effectiveness as follows: All Drivers (Equipment Failure, Vegetation etc.) - 99.89% | Inspections
Asset inspection | Asset Management & Inspections | 7.3.4.15-D | 7.3.4.15-D Substation inspections, Enhanced Distribution, Substation | All Drivers | All Drivers | 2018 | 0.0049911 | 0 | 0 | 0 | 2020 GRC | FRMMA / WMPMA | Exceeds | GO 174 |  |  |  | 0 | 9681.5266 | N/A | 0 | 5980.6235 | N/A | 0 | 7394.0962 | N/A | Line Miles = N/A as substation assets are not associated with circuit miles | Line Miles = N/A as substation assets are not associated with circuit miles | Line Miles = N/A as substation assets are not associated with circuit miles |  | Ignition Risk -Equipment Failure | Yes | Yes | Program Owner Prioritized (See Narrative) | N/A |  | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the likelihood of ignition risk mitigating all drivers, with an effectiveness as follows: All Drivers (Equipment Failure, Vegetation etc.) - 99.51% | Inspections
Vegetation management project | Vegetation Management & Inspections | 7.3.5.1 | 7.3.5.1 Additional efforts to manage community and environmental impacts | N/A - Foundational | N/A - Foundational | <2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC, Transmission Owner | CEMA | In Compliance | GO 95 Rule 35, and PRC 4293 |  |  |  | 0 | 22278.1394 | 99165 | 0 | 24075.6844 | 99165 | 0 | 24130.3911 | 99165 | In 2020 WMP Initiative captures community engagement and environmental support of all vegetation management in T2/T3 areas (distribution, transmission, routine and Enhanced). In 2021 WMP this program was described as being applicable to the entire T&D system. | In 2020 WMP Initiative captures community engagement and environmental support of all vegetation management in T2/T3 areas (distribution, transmission, routine and Enhanced). In 2021 WMP this program was described as being applicable to the entire T&D system. | In 2020 WMP Initiative captures community engagement and environmental support of all vegetation management in T2/T3 areas (distribution, transmission, routine and Enhanced). In 2021 WMP this program was described as being applicable to the entire T&D system. |  | Ignition Risk - Vegetation | No | No | N/A | N/A |  | We are not planning to include this initiative. | Risk reduction not quantified. Foundational initiative, for which distinct financial and quantification data is not currently available. | Vegetation Management
Vegetation management project | Vegetation Management & Inspections | 7.3.5.2 | 7.3.5.2 Detailed inspections of vegetation around distribution electric lines and equipment | Vegetation | No other drivers addressed | <2018 | 4.4737 | 5910.6732 | 5910.6732 | 5910.6732 | 2020 GRC | N/A | In Compliance | GO 95 Rule 35, and PRC 4293 |  |  |  | 0 | 1097664.9365 | 81004 | 0 | 1065058.6895 | 81004 | 0 | 1023428.6887 | 81004 | Full Distribution System treated annually | Full Distribution System treated annually | Full Distribution System treated annually |  | Ignition Risk - Vegetation | Yes | No | N/A | N/A |  | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the likelihood of ignition risk, specifically mitigating the vegetation driver, with an effectiveness as follows: Likelihood of ignition due to Vegetation - 99.4% | Vegetation Management
Vegetation management project | Vegetation Management & Inspections | 7.3.5.3 | 7.3.5.3 Detailed inspections of vegetation around transmission electric lines and equipment | N/A - Complementary | N/A - Complementary | <2018 | See Initiative 7.3.5.8 | See Initiative 7.3.5.8 | See Initiative 7.3.5.8 | See Initiative 7.3.5.8 | Transmission Owner | N/A | In Compliance | GO95, PRC 4293 |  |  |  | 45622.1908 | 85255.6855 | 18161 | 85910.4342 | 101242.853 | 18161 | 61701 | 104009.9099 | 18161 | Applies to all transmission system miles annually | Applies to all transmission system miles annually | Applies to all transmission system miles annually |  | Ignition Risk - Vegetation | No | Yes | Program Owner Prioritized (See Narrative) | N/A |  | We are not planning to include this initiative. | Risk reduction not quantified independently. Initiative complementary to 7.3.5.8. Please refer to 7.3.5.8. | Vegetation Management
Vegetation management project | Vegetation Management & Inspections | 7.3.5.4 | 7.3.5.4 Emergency response vegetation management due to red flag warning or other urgent conditions | Vegetation | No other drivers addressed | <2018 | N/A | N/A | N/A | N/A | 2020 GRC | N/A | In Compliance | GO 95 Rule 35, and PRC 4293 |  |  |  | 0 | 5970.4966 | 99165 | 0 | 5981.7034 | 99165 | 0 | 5734.45 | 99165 | Applies to all T&D system annually | Applies to all T&D system annually | Applies to all T&D system annually |  | Ignition Risk - Vegetation | No | Yes | Program Owner Prioritized (See Narrative) | Wildfire Distribution Risk Model, consistent with response, but this one is stated as 2023 or later |  | 2023 or later | Risk reduction not quantified. Initiative does not currently capture data determined to be usable for RSE calculation. Attempt will be made to calculate the RSE for the 2022 WMP submission. | Vegetation Management
Vegetation management project | Vegetation Management & Inspections | 7.3.5.5 | 7.3.5.5 Fuel management and reduction of “slash” from vegetation management activities | N/A - Pilot | N/A - Pilot | <2018 | N/A - Pilot | N/A - Pilot | N/A - Pilot | N/A - Pilot | 2020 GRC | N/A | Exceeds | GO 95 Rule 35, PRC 4293 and PRC 4292 |  |  |  | 0 | 23665.9934 | N/A | 0 | 27871.9547 | TBD | 0 | 28937.2648 | TBD | PG&E is still in the process of building a framework for fuel reduction work. In 2020, different strategies were discussed and benchmarking with other utility companies was completed. | PG&E is still in the process of building a framework for fuel reduction work. In 2020, different strategies were discussed and benchmarking with other utility companies was completed. | PG&E is still in the process of building a framework for fuel reduction work. In 2020, different strategies were discussed and benchmarking with other utility companies was completed. |  | Ignition Risk - Vegetation | No | Yes | Vegetation Risk Model | Wildfire Distribution Risk Model, consistent with response, but this one is stated as 2023 or later |  | 2022 | Risk reduction not quantified. As a pilot initiative, the necessary data to evaluate risk reduction has not been captured, but this technology has the potential to reduce risk of ignition that could spread into a wildfire. Initiative is currently being scoped. | Vegetation Management
Vegetation management project | Vegetation Management & Inspections | 7.3.5.6 | 7.3.5.6 Improvement of inspections | N/A - Complementary | N/A - Complementary | <2018 | See Initiative 7.3.5.2 and 7.3.5.8 | See Initiative 7.3.5.2 and 7.3.5.8 | See Initiative 7.3.5.2 and 7.3.5.8 | See Initiative 7.3.5.2 and 7.3.5.8 | 2020 GRC | N/A | In Compliance | GO 95 Rule 35, PRC 4293, and PRC 4295 |  |  |  | 0 | 1299.3908 | N/A | 0 | 1199.3898 | N/A | 0 | 1113.0646 | N/A | Determined the line miles are not applicable to this improvement initiative. Alternatively it could apply to all T&D system miles | Determined the line miles are not applicable to this improvement initiative. Alternatively it could apply to all T&D system miles | Determined the line miles are not applicable to this improvement initiative. Alternatively it could apply to all T&D system miles |  | Ignition Risk - Vegetation | No | Yes | Program Owner Prioritized (See Narrative) | N/A |  | We are not planning to include this initiative. | Risk reduction not quantified independently. Initiative complementary to 7.3.5.2 & 7.3.5.8. Please refer to 7.3.5.2 & 7.3.5.8. | Vegetation Management
Vegetation management project | Vegetation Management & Inspections | 7.3.5.7 | 7.3.5.7 LiDAR inspections of vegetation around distribution electric lines and equipment | N/A - Pilot | N/A - Pilot | <2018 | N/A - Pilot | N/A - Pilot | N/A - Pilot | N/A - Pilot | 2020 GRC | N/A | In Compliance | GO 95 Rule 35, PRC 4293, and PRC 4295 |  |  |  | 0 | 2590.275 | 0 | 0 | 3050.6232 | TBD | 0 | 3167.2228 | TBD | TBD, per the2021 WMP narrative | TBD, per the2021 WMP narrative | TBD, per the2021 WMP narrative |  | Ignition Risk - Vegetation | No | Yes | Program Owner Prioritized (See Narrative) | N/A |  | We are not planning to include this initiative. | Risk reduction not quantified. As a pilot initiative, the necessary data to evaluate risk reduction has not been captured, but this technology has the potential to reduce ignition risk. LiDAR is used to identify strike-potential trees to reduce the risk of vegetation contact with overhead powerlines. | Vegetation Management
Vegetation management project | Vegetation Management & Inspections | 7.3.5.8 | 7.3.5.8 LiDAR inspections of vegetation around transmission electric lines and equipment | Vegetation | No other drivers addressed | <2018 | 0 | 2118.7593 | 2118.7593 | 2118.7593 | Transmission Owner | N/A | In Compliance | GO95, PRC 4293 and FAC 003-4 |  |  |  | 0 | 25222.3537 | 18161 | 0 | 29952.0558 | 18161 | 0 | 30770.672 | 18161 | Applies to all transmission system miles annually | Applies to all transmission system miles annually | Applies to all transmission system miles annually |  | Ignition Risk - Vegetation | Yes | No | N/A | N/A |  | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12.This initiative reduces the likelihood of ignition risk, specifically mitigating the vegetation driver, with an effectiveness as follows: Likelihood of ignition due to Vegetation - 99.79% | Vegetation Management
Vegetation management project | Vegetation Management & Inspections | 7.3.5.9 | 7.3.5.9 Other discretionary inspections of vegetation around distribution electric lines and equipment | Vegetation | No other drivers addressed | <2018 | 0.01464 | 24695.4091 | 24695.4091 | 24695.4091 | 2020 GRC | N/A | Exceeds | GO 95 Rule 35, PRC 4292, PRC 4293, and PRC 4295 |  |  |  | 0 | 516.627 | 81004 | 0 | 397.4037 | 81004 | 0 | 404.6587 | 81004 | Applies to all distribution system miles annually | Applies to all distribution system miles annually | Applies to all distribution system miles annually |  | Ignition Risk - Vegetation | Yes | Yes | Program Owner Prioritized (See Narrative) | N/A |  | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the likelihood of ignition risk, specifically mitigating the vegetation driver, with an effectiveness as follows: Likelihood of ignition due to Vegetation - 99.92% | Vegetation Management
Vegetation management project | Vegetation Management & Inspections | 7.3.5.10 | 7.3.5.10 Other discretionary inspections of vegetation around transmission electric lines and equipment | N/A - Complementary | N/A - Complementary | See Initiative 7.3.5.3 | See Initiative 7.3.5.3 | See Initiative 7.3.5.3 | See Initiative 7.3.5.3 | See Initiative 7.3.5.3 | See Initiative 7.3.5.3 | See Initiative 7.3.5.3 | See Initiative 7.3.5.3 | See Initiative 7.3.5.3 | 7.3.5.3 Detailed inspections of vegetation around transmission electric lines and equipment |  |  | 0 | 0 | 18161 | 0 | 0 | 18161 | 0 | 0 | 18161 | Applies to all transmission system miles annually | Applies to all transmission system miles annually | Applies to all transmission system miles annually |  | Ignition Risk - Vegetation | No | No | N/A | N/A |  | We are not planning to include this initiative. | Risk reduction not quantified independently. Initiative complementary to 7.3.5.8. Please refer to 7.3.5.8. | Vegetation Management
Vegetation management project | Vegetation Management & Inspections | 7.3.5.11 | 7.3.5.11 Patrol inspections of vegetation around distribution electric lines and equipment | N/A - Complementary | N/A - Complementary | See Initiative 7.3.5.2 | See Initiative 7.3.5.2 | See Initiative 7.3.5.2 | See Initiative 7.3.5.2 | See Initiative 7.3.5.2 | See Initiative 7.3.5.2 | See Initiative 7.3.5.2 | See Initiative 7.3.5.2 | See Initiative 7.3.5.2 | 7.3.5.2 Detailed inspections of vegetation around distribution electric lines and equipment |  |  | 0 | 0 | 81004 | 0 | 0 | 81004 | 0 | 0 | 81004 | Applies to all distribution system miles annually | Applies to all distribution system miles annually | Applies to all distribution system miles annually |  | Ignition Risk - Vegetation | No | No | N/A | N/A |  | We are not planning to include this initiative. | Risk reduction not quantified independently. Initiative complementary to 7.3.5.2. Please refer to 7.3.5.2. | Vegetation Management
Vegetation management project | Vegetation Management & Inspections | 7.3.5.12 | 7.3.5.12 Patrol inspections of vegetation around transmission electric lines and equipment | N/A - Complementary | N/A - Complementary | See Initiative 7.3.5.3 | See Initiative 7.3.5.3 | See Initiative 7.3.5.3 | See Initiative 7.3.5.3 | See Initiative 7.3.5.3 | See Initiative 7.3.5.3 | See Initiative 7.3.5.3 | See Initiative 7.3.5.3 | See Initiative 7.3.5.3 | 7.3.5.3 Detailed inspections of vegetation around transmission electric lines and equipment |  |  | 0 | 0 | 20724 | 0 | 0 | 20724 | 0 | 0 | 20724 | Applies to whole transmission system and Distribution EVM Line Miles | Applies to whole transmission system and Distribution EVM Line Miles | Applies to whole transmission system and Distribution EVM Line Miles |  | Ignition Risk - Vegetation | No | No | N/A | N/A |  | We are not planning to include this initiative. | Risk reduction not quantified independently. Initiative complementary to 7.3.5.8. Please refer to 7.3.5.8. | Vegetation Management
Vegetation management project | Vegetation Management & Inspections | 7.3.5.13 | 7.3.5.13 Quality assurance / quality control of vegetation inspections | N/A - Foundational | N/A - Foundational | <2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2017 GRC, Transmission Owner | N/A | In Compliance | GO 95 Rule 35, and PRC 4293 |  |  |  | 0 | 11694.5175 | 99165 | 0 | 10794.5086 | 99165 | 0 | 10017.581 | 99165 | Line miles treated would apply to both T&D routine programs | Line miles treated would apply to both T&D routine programs | Line miles treated would apply to both T&D routine programs |  | Ignition Risk - Vegetation | No | Yes | Program Owner Prioritized (See Narrative) | N/A |  | We are not planning to include this initiative. | Risk reduction not quantified. Foundational initiative, for which distinct financial and quantification data not currently available. | Vegetation Management
Vegetation management project | Vegetation Management & Inspections | 7.3.5.14 | 7.3.5.14 Recruiting and training of vegetation management personnel | N/A - Foundational | N/A - Foundational | <2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | N/A | N/A |  |  |  | 0 | 14.3955 | N/A | 0 | 13.0577 | N/A | 0 | 11.9184 | N/A | Determined the line miles are not applicable to this improvement initiative. Alternatively it could apply to all T&D system miles | Determined the line miles are not applicable to this improvement initiative. Alternatively it could apply to all T&D system miles | Determined the line miles are not applicable to this improvement initiative. Alternatively it could apply to all T&D system miles |  | Ignition Risk - Vegetation | No | No | N/A | N/A |  | We are not planning to include this initiative. | Risk reduction not quantified. Foundational initiative, for which distinct financial and quantification data not currently available. | Vegetation Management
Vegetation management project | Vegetation Management & Inspections | 7.3.5.15 | 7.3.5.15 Remediation of at-risk species | Vegetation | No other drivers addressed | 2018 | 0 | 3.9515 | 3.9515 | 3.9515 | 2020 GRC | N/A | Exceeds | GO 95 Rule 35, and PRC 4293 |  |  |  | 0 | 115876.6134 | 1878 | 0 | 136470.406 | 1800 | 0 | 141686.5202 | 1800 | This programs is planned and tracked using miles as updated in the 2021 WMP | This programs is planned and tracked using miles as updated in the 2021 WMP | This programs is planned and tracked using miles as updated in the 2021 WMP |  | Ignition Risk - Vegetation | Yes | Yes | Vegetation Risk Model | N/A |  | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the likelihood of ignition risk, specifically mitigating the vegetation driver, with an effectiveness as follows: Likelihood of ignition due to Vegetation: Branch (Not Overhanging, 4-12ft), Fell into (slight defect), Grow Into - 50% Branch (Not Overhanging, within 4ft), Branch (Overhanging) - 90% Fell into (Moderate-Severe defect) - 95% | Vegetation Management
Vegetation management project | Vegetation Management & Inspections | 7.3.5.16 | 7.3.5.16 Removal and remediation of trees with strike potential to electric lines and equipment | N/A - Complementary | N/A - Complementary | See Initiatives 7.3.5.2, 7.3.5.3, and 7.3.5.15 | See Initiative 7.3.5.8 | See Initiative 7.3.5.8 | See Initiative 7.3.5.8 | See Initiative 7.3.5.8 | See Initiatives 7.3.5.2, 7.3.5.3, and 7.3.5.15 | See Initiatives 7.3.5.2, 7.3.5.3, and 7.3.5.15 | See Initiatives 7.3.5.2, 7.3.5.3, and 7.3.5.15 | See Initiatives 7.3.5.2, 7.3.5.3, and 7.3.5.15 | 7.3.5.2 Detailed inspections of vegetation around distribution electric lines and equipment, 7.3.5.3 Detailed inspections of vegetation around transmission electric lines and equipment, and 7.3.5.15 Remediation of at-risk species |  |  | 0 | 0 | N/A | 0 | 0 | N/A | 0 | 0 | N/A | PG&E does not perform a separate effort to identify, remove and remediate trees with strike potential. | PG&E does not perform a separate effort to identify, remove and remediate trees with strike potential. | PG&E does not perform a separate effort to identify, remove and remediate trees with strike potential. |  | Ignition Risk - Vegetation | No | No | N/A | N/A |  | We are not planning to include this initiative. | Risk reduction not quantified independently. Initiative complementary to 7.3.5.8. Please refer to 7.3.5.8. | Vegetation Management
Vegetation management project | Vegetation Management & Inspections | 7.3.5.17.1 | 7.3.5.17.1 Substation inspection , Distribution substation | Vegetation | No other drivers addressed | <2018 | N/A | N/A | N/A | N/A | 2020 GRC | N/A | Exceeds | GO 95 Rule 35 / PRC 4293 / NERC Standard FAC-003-4 |  |  |  | 0 | 293.552 | N/A | 0 | 308.2479 | N/A | 0 | 309.7018 | N/A | Line miles treated is not an appropriate metric for substation related investments | Line miles treated is not an appropriate metric for substation related investments | Line miles treated is not an appropriate metric for substation related investments |  | Ignition Risk - Vegetation | No | Yes | Program Owner Prioritized (See Narrative) | N/A |  | We are not planning to include this initiative. | Risk reduction not quantified. Initiative does not currently capture data found usable for risk reduction calculation. Attempt will be made to calculate the RSE for the 2022 WMP submission. | Vegetation Management
Vegetation management project | Vegetation Management & Inspections | 7.3.5.17.2 | 7.3.5.17.2 Substation inspection , Transmission substation | Vegetation | No other drivers addressed | <2018 | N/A | N/A | N/A | N/A | Transmission Owner | N/A | Exceeds | GO 95 Rule 35 / PRC 4293 / NERC Standard FAC-003-4 |  |  |  | 0 | 159.355 | N/A | 0 | 231.0334 | N/A | 0 | 244.9312 | N/A | Line miles treated is not an appropriate metric for substation related investments | Line miles treated is not an appropriate metric for substation related investments | Line miles treated is not an appropriate metric for substation related investments |  | Ignition Risk - Vegetation | No | Yes | Program Owner Prioritized (See Narrative) | N/A |  | We are not planning to include this initiative. | Risk reduction not quantified. Initiative does not currently capture data found usable for risk reduction calculation. Attempt will be made to calculate the RSE for the 2022 WMP submission. | Vegetation Management
Vegetation management project | Vegetation Management & Inspections | 7.3.5.18.1 | 7.3.5.18.1 Substation vegetation management, Maintenance substation distribution | Vegetation | No other drivers addressed | <2018 | N/A | N/A | N/A | N/A | 2020 GRC | FRMMA / WMPMA | Exceeds | GO 95 Rule 35 / PRC 4293 / NERC Standard FAC-003-4 |  |  |  | 0 | 3020.0514 | N/A | 0 | 2830.7953 | N/A | 0 | 2733.5915 | N/A | Line miles treated is not an appropriate metric for substation related investments | Line miles treated is not an appropriate metric for substation related investments | Line miles treated is not an appropriate metric for substation related investments |  | Ignition Risk - Vegetation | No | Yes | Program Owner Prioritized (See Narrative) | N/A |  | We are not planning to include this initiative. | Risk reduction not quantified. Initiative does not currently capture data found usable for risk reduction calculation. Attempt will be made to calculate the RSE for the 2022 WMP submission. | Vegetation Management
Vegetation management project | Vegetation Management & Inspections | 7.3.5.18.2 | 7.3.5.18.2 Substation vegetation management, Maintenance substation transmission | Vegetation | No other drivers addressed | <2018 | N/A | N/A | N/A | N/A | Transmission Owner | N/A | In Compliance | GO 95 Rule 35 / PRC 4293 / NERC Standard FAC-003-3 |  |  |  | 0 | 2774.3378 | N/A | 0 | 3939.902 | N/A | 0 | 3645.0859 | N/A | Line miles treated is not an appropriate metric for substation related investments | Line miles treated is not an appropriate metric for substation related investments | Line miles treated is not an appropriate metric for substation related investments |  | Ignition Risk - Vegetation | No | Yes | Program Owner Prioritized (See Narrative) | N/A |  | We are not planning to include this initiative. | Risk reduction not quantified. Initiative does not currently capture data found usable for risk reduction calculation. Attempt will be made to calculate the RSE for the 2022 WMP submission. | Vegetation Management
Vegetation management project | Vegetation Management & Inspections | 7.3.5.19 | 7.3.5.19 Vegetation inventory system | N/A - Foundational | N/A - Foundational | <2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC | N/A | N/A | N/A |  |  |  | 0 | 7392.0092 | 99165 | 0 | 8069.6249 | 99165 | 0 | 8110.5831 | 99165 | Line miles treated would apply to both T&D routine programs | Line miles treated would apply to both T&D routine programs | Line miles treated would apply to both T&D routine programs |  | Ignition Risk - Vegetation | No | Yes | Program Owner Prioritized (See Narrative) | N/A |  | We are not planning to include this initiative. | Risk reduction not quantified. Foundational initiative, for which distinct financial and quantification data not currently available. | Vegetation Management
Vegetation management project | Vegetation Management & Inspections | 7.3.5.20 | 7.3.5.20 Vegetation management to achieve clearances around electric lines and equipment | N/A - Complementary | N/A - Complementary | See Initiatives 7.3.5.2 and 7.3.5.3 | See Initiatives 7.3.5.2 and 7.3.5.8 | See Initiatives 7.3.5.2 and 7.3.5.8 | See Initiatives 7.3.5.2 and 7.3.5.8 | See Initiatives 7.3.5.2 and 7.3.5.8 | See Initiatives 7.3.5.2 and 7.3.5.3 | See Initiatives 7.3.5.2 and 7.3.5.3 | See Initiatives 7.3.5.2 and 7.3.5.3 | See Initiatives 7.3.5.2 and 7.3.5.3 | 7.3.5.2 Detailed inspections of vegetation around distribution electric lines and equipment, and 7.3.5.3 Detailed inspections of vegetation around transmission electric lines and equipment |  |  | 0 | 0 | 99165 | 0 | 0 | 99165 | 0 | 0 | 99165 | Line miles treated would apply to both T&D routine programs | Line miles treated would apply to both T&D routine programs | Line miles treated would apply to both T&D routine programs |  | Ignition Risk - Vegetation | No | No | N/A | N/A |  | We are not planning to include this initiative. | Risk reduction not quantified independently. Initiative complementary to 7.3.5.2 & 7.3.5.8. Please refer to 7.3.5.2 & 7.3.5.8. | Vegetation Management
Other | Grid Operations & Operating Protocols | 7.3.6.1 | 7.3.6.1 Automatic recloser operations | All Drivers | All Drivers | 2018 | N/A | N/A | N/A | N/A | 2020 GRC | N/A | N/A | N/A |  |  |  | 0 | 36 | N/A | 0 | 37.008 | N/A | 0 | 39.1475 | N/A | Line miles is not an applicable metric | Line miles is not an applicable metric | Line miles is not an applicable metric |  | Ignition Risk - All Drivers | No | Yes | Program Owner Prioritized (See Narrative) | N/A |  | We are not planning to include this initiative. | Risk reduction not quantified. Initiative does not currently capture data found usable for risk reduction calculation. Attempt will be made to calculate the RSE for the 2022 WMP submission. | Operational Practices
Other | Grid Operations & Operating Protocols | 7.3.6.2 | 7.3.6.2 Crew-accompanying ignition prevention and suppression resources and services | Consequence - Financial | No other consequences reflected | 2018 | 0 | 0.4242 | 0.4556 | 0.46729 | 2020 GRC | N/A | N/A | N/A |  |  |  | 752.3551 | 9205.1416 | N/A | 90.9163 | 12563.4 | N/A | 714.222 | 14917.8 | N/A | Line miles is not an applicable metric | Line miles is not an applicable metric | Line miles is not an applicable metric |  | Wildfire Consequence | Yes | Yes | Program Owner Prioritized (See Narrative) | N/A |  | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the consequence of wildfire risk, specifically mitigating the financial consequence, with an effectiveness as follows: Financial consequence of catastrophic and destructive ignitions - 0.38%, Financial consequence of small and large ignitions - 4.97% | Operational Practices
Other | Grid Operations & Operating Protocols | 7.3.6.3 | 7.3.6.3 Personnel work procedures and training in conditions of elevated fire risk | N/A - Foundational | N/A - Foundational | <2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC | FRMMA / WMPMA | N/A | N/A |  |  |  | 0 | 839.8231 | N/A | 0 | 1000 | N/A | 0 | 1029.2 | N/A | Line miles is not an applicable metric | Line miles is not an applicable metric | Line miles is not an applicable metric |  | Ignition Risk - All Drivers, Wildfire Consequence | No | Yes | Program Owner Prioritized (See Narrative) | N/A |  | We are not planning to include this initiative. | Risk reduction not quantified. Foundational Initiative, for which distinct financial and quantification data not currently available. | Support
Other | Grid Operations & Operating Protocols | 7.3.6.4-D | 7.3.6.4-D Protocols for PSPS re-energization, Distribution | Consequence - PSPS | No other consequences reflected | 2018 | 0 | 2.1531 | 2.1531 | 2.1531 | 2020 GRC | N/A | N/A | N/A |  |  |  | 1021 | 79791.7165 | N/A | 249 | 81080.0063 | N/A | 256 | 71900.2765 | N/A | Line miles is not an applicable metric | Line miles is not an applicable metric | Line miles is not an applicable metric |  | PSPS Consequence | Yes | Yes | Program Owner Prioritized (See Narrative) | Future State PSPS Consequence Model |  | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the consequence of PSPS, specifically mitigating the impact to customers from PSPS events, with an effectiveness as follows: PSPS Impact Reduction Effectiveness - 1.65% | Operational Practices
Other | Grid Operations & Operating Protocols | 7.3.6.4-T | 7.3.6.4-T Protocols for PSPS re-energization, Transmission | Consequence - PSPS | No other consequences reflected | 2018 | 0 | 28.6918 | 28.6918 | 28.6918 | Transmission Owner | N/A | N/A | N/A |  |  |  | 0 | 1329 | N/A | 0 | 1356 | N/A | 0 | 1395 | N/A | Line miles is not an applicable metric | Line miles is not an applicable metric | Line miles is not an applicable metric |  | PSPS Consequence | Yes | Yes | Program Owner Prioritized (See Narrative) | Future State PSPS Consequence Model |  | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the consequence of PSPS, specifically mitigating the impact to customers from PSPS events, with an effectiveness as follows: PSPS Impact Reduction Effectiveness - 1.65% | Operational Practices
Other | Grid Operations & Operating Protocols | 7.3.6.5-D | 7.3.6.5-D PSPS events and mitigation of PSPS impacts , Distribution | Equipment Failure, Vegetation | No other drivers addressed | 2018 | N/A | N/A | N/A | N/A | 2020 GRC | FRMMA / WMPMA | N/A | N/A |  |  |  | 0 | 80462 | 25439 | 0 | 68379 | 25439 | 0 | 70368 | 25439 | Units provided are number of events “forecasted”. Number of miles impacted will be dependent on scope of events. Line miles provided are for the entire Z1 T2 T3 Distribution system. | Units provided are number of events “forecasted”. Number of miles impacted will be dependent on scope of events. Line miles provided are for the entire Z1 T2 T3 Distribution system. | Units provided are number of events “forecasted”. Number of miles impacted will be dependent on scope of events. Line miles provided are for the entire Z1 T2 T3 Distribution system. |  | Ignition Risk - Equipment Failure, Vegetation | No | Yes | Program Owner Prioritized (See Narrative) | Large Fire Probability Model |  | We are not planning to include this initiative. | For this initiative, PG&E represents PSPS as a wildfire mitigation. PG&E represents risk reduction for PSPS mitigations in other initiatives. Risk reduction of PSPS in itself is expected to provide a large risk reduction. However, given WSD's feedback that "electrical corporations shall not rely on RSE calculations as a tool to justify the use of PSPS", PG&E will re-assess and bit is not presenting an RSE at this time. | Operational Practices
Other | Grid Operations & Operating Protocols | 7.3.6.5-T | 7.3.6.5-T PSPS events and mitigation of PSPS impacts , Transmission | Equipment Failure, Vegetation | No other drivers addressed | 2018 | N/A | N/A | N/A | N/A | Transmission Owner | N/A | N/A | N/A |  |  |  | 0 | 350 | 5528 | 0 | 302 | 5528 | 0 | 311 | 5528 | Units provided are number of events “forecasted”. Number of miles impacted will be dependent on scope of events. Line miles provided are for the entire Z1 T2 T3 Transmission system. | Units provided are number of events “forecasted”. Number of miles impacted will be dependent on scope of events. Line miles provided are for the entire Z1 T2 T3 Transmission system. | Units provided are number of events “forecasted”. Number of miles impacted will be dependent on scope of events. Line miles provided are for the entire Z1 T2 T3 Transmission system. |  | Ignition Risk - Equipment Failure, Vegetation | No | Yes | Program Owner Prioritized (See Narrative) | Large Fire Probability Model |  | We are not planning to include this initiative. | For this initiative, PG&E represents PSPS as a wildfire mitigation. PG&E represents risk reduction for PSPS mitigations in other initiatives. Risk reduction of PSPS in itself is expected to provide a large risk reduction. However, given WSD's feedback that "electrical corporations shall not rely on RSE calculations as a tool to justify the use of PSPS", PG&E will re-assess and refrain from presenting a Risk Spend Efficiency at this time. | Operational Practices
Other | Grid Operations & Operating Protocols | 7.3.6.6 | 7.3.6.6 Stationed and on-call ignition prevention and suppression resources and services | Consequence - Financial | No other consequences reflected | 2018 | 0 | 0.43753 | 0.46991 | 0.48197 | 2020 GRC | N/A | N/A | N/A |  |  |  | 250.785 | 3068.3805 | N/A | 30.3054 | 6060.7537 | N/A | 238.074 | 4972.6 | N/A | Line miles is not an applicable metric | Line miles is not an applicable metric | Line miles is not an applicable metric |  | Wildfire Consequence | Yes | Yes | Program Owner Prioritized (See Narrative) | N/A |  | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the consequence of wildfire risk, specifically mitigating the financial consequence, with an effectiveness as follows: Financial consequence of catastrophic and destructive ignitions - 0.15%, Financial consequence of small and large ignitions - 1.99% | Operational Practices
Other | Grid Operations & Operating Protocols | 7.3.6.7 | 7.3.6.7 Other, Aviation Support | Consequence - PSPS | No other consequences reflected | <2018 | 0 | 95.2409 | 95.2409 | 95.2409 | 2020 GRC, Transmission Owner | FRMMA / WMPMA | N/A | N/A |  |  |  | 480.5551 | 5397.5698 | N/A | 15000 | 5910.18 | N/A | 10000 | 4326.18 | N/A | Line miles is not an applicable metric | Line miles is not an applicable metric | Line miles is not an applicable metric |  | PSPS Consequence | Yes | Yes | Program Owner Prioritized (See Narrative) | Future State PSPS Consequence Model |  | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the consequence of PSPS, specifically mitigating the impact to customers from PSPS events, with an effectiveness as follows: PSPS Impact Reduction Effectiveness - 10.34% | Support
Other | Data Governance | 7.3.7.1 | 7.3.7.1 Centralized repository for data | N/A - Foundational | N/A - Foundational | <2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC and Transmission Owner | N/A | N/A | N/A |  |  |  | 0 | 841.612 | N/A | 0 | 1126.9596 | N/A | 0 | 1160.7684 | N/A | Line miles is not an applicable metric | Line miles is not an applicable metric | Line miles is not an applicable metric |  | Ignition Risk - All Drivers | No | No | N/A | N/A |  | We are not planning to include this initiative. | Risk reduction not quantified. Foundational Initiative, for which distinct financial and quantification data not currently available. | Support
Other | Data Governance | 7.3.7.2 | 7.3.7.2 Collaborative research on utility ignition and/or wildfire | N/A - Foundational | N/A - Foundational | 2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC, EPIC | N/A | N/A | N/A |  |  |  | 0 | 1457.7518 | N/A | 0 | 1915.2949 | N/A | 0 | 400 | N/A | Line miles is not an applicable metric | Line miles is not an applicable metric | Line miles is not an applicable metric |  | Ignition Risk - All Drivers | No | No | N/A | N/A |  | We are not planning to include this initiative. | Risk reduction not quantified. Foundational Initiative, for which distinct financial and quantification data not currently available. | Support
Other | Data Governance | 7.3.7.3 | 7.3.7.3 Documentation and disclosure of wildfire-related data and algorithms | N/A - Foundational | N/A - Foundational | <2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC and Transmission Owner | N/A | N/A | N/A |  |  |  | 0 | 420.806 | N/A | 0 | 563.4798 | N/A | 0 | 580.3842 | N/A | Line miles is not an applicable metric | Line miles is not an applicable metric | Line miles is not an applicable metric |  | Ignition Risk - All Drivers | No | Yes | Program Owner Prioritized (See Narrative) | N/A |  | We are not planning to include this initiative. | Risk reduction not quantified. Foundational Initiative, for which distinct financial and quantification data not currently available. | Support
Other | Data Governance | 7.3.7.4 | 7.3.7.4 Tracking and analysis of near miss data | N/A - Foundational | N/A - Foundational | <2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC and Transmission Owner | N/A | N/A | N/A |  |  |  | 0 | 723.3121 | N/A | 0 | 993.1548 | N/A | 0 | 1022.9494 | N/A | Line miles is not an applicable metric | Line miles is not an applicable metric | Line miles is not an applicable metric |  | Ignition Risk - All Drivers | No | No | N/A | N/A |  | We are not planning to include this initiative. | Risk reduction not quantified. Foundational Initiative, for which distinct financial and quantification data not currently available. | Support
Other | Data Governance | 7.3.7.5 | 7.3.7.5 Other, IT projects to support wildfire mitigation work | N/A - Foundational | N/A - Foundational | 2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC and Transmission Owner | FRMMA / WMPMA | N/A | N/A |  |  |  | 66711.555 | 46464.1706 | N/A | 86346.4478 | 56416.7512 | N/A | 88764.1483 | 58064.1204 | N/A | Line miles is not an applicable metric | Line miles is not an applicable metric | Line miles is not an applicable metric |  | Ignition Risk - All Drivers | No | No | N/A | N/A |  | We are not planning to include this initiative. | Risk reduction not quantified. Foundational Initiative, for which distinct financial and quantification data not currently available. | Support
Other | Resource allocation methodology | 7.3.8.1 | 7.3.8.1 Allocation methodology development and application | N/A - Foundational | N/A - Foundational | <2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC and Transmission Owner | N/A | N/A | N/A |  |  |  | 0 | 4117.9849 | N/A | 0 | 4167.3789 | N/A | 0 | 4074.0555 | N/A | Line miles is not an applicable metric | Line miles is not an applicable metric | Line miles is not an applicable metric |  | Ignition Risk - All Drivers Wildfire Consequence | No | Yes | Program Owner Prioritized (See Narrative) | N/A |  | We are not planning to include this initiative. | Risk reduction not quantified. Foundational Initiative, for which distinct financial and quantification data not currently available. | Support
Other | Resource allocation methodology | 7.3.8.2 | 7.3.8.2 Risk reduction scenario development and analysis | N/A - Foundational | N/A - Foundational | <2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC and Transmission Owner | N/A | N/A | N/A |  |  |  | 0 | 712.1583 | N/A | 0 | 735.2054 | N/A | 0 | 821.2719 | N/A | Line miles is not an applicable metric | Line miles is not an applicable metric | Line miles is not an applicable metric |  | Ignition Risk - All Drivers Wildfire Consequence | Yes | No | N/A | Wildfire Distribution Risk Model, Wildfire Transmission Risk Model |  | 2022 | Risk reduction not quantified. Foundational Initiative, for which distinct financial and quantification data not currently available. | Support
Other | Resource allocation methodology | 7.3.8.3 | 7.3.8.3 Risk spend efficiency analysis | N/A - Foundational | N/A - Foundational | <2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC and Transmission Owner | N/A | N/A | N/A |  |  |  | 0 | 1760.3915 | N/A | 0 | 2218.7012 | N/A | 0 | 2283.7422 | N/A | Line miles is not an applicable metric | Line miles is not an applicable metric | Line miles is not an applicable metric |  | Ignition Risk - All Drivers Wildfire Consequence | No | No | N/A | Wildfire Distribution Risk Model, Wildfire Transmission Risk Model |  | 2022 | Risk reduction not quantified. Foundational Initiative, for which distinct financial and quantification data not currently available. | Support
Other | Emergency planning and preparedness | 7.3.9.1 | 7.3.9.1 Adequate and trained workforce for service restoration | All Consequences | All Consequences | <2018 | 0 | 126.3692 | 126.3692 | 126.3692 | 2020 GRC | N/A | N/A | N/A |  |  |  | 126.3102 | 1842.9107 | N/A | 0 | 2124.1463 | N/A | 0 | 2192.1951 | N/A | Line miles is not an applicable metric | Line miles is not an applicable metric | Line miles is not an applicable metric |  | Wildfire Consequence, PSPS Consequence | Yes | No | N/A | N/A |  | We are not planning to include this initiative. | Drivers and RSEs can be seen in Table 12. This initiative reduces the consequence of wildfire risk, specifically mitigating the equipment failure driver, with an effectiveness as follows: Consequence of ignitions: Safety developing rapidly = 5.3% Consequence of Ignition: Electric Reliability developing gradually = 13.25% Consequence of ignitions: Financial developing rapidly = 5.3% | Support
Other | Emergency planning and preparedness | 7.3.9.2 | 7.3.9.2 Community outreach, public awareness, and communications efforts | All Consequences | All Consequences | <2018 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.1 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.2 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.3 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.4 | 2020 GRC and Transmission Owner | FRMMA / WMPMA | N/A | N/A |  |  |  | 0 | 6477.669 | N/A | 0 | 7530.9174 | N/A | 0 | 7702.9997 | N/A | Line miles is not an applicable metric | Line miles is not an applicable metric | Line miles is not an applicable metric |  | Wildfire Consequence, PSPS Consequence | Yes | Yes | Program Owner Prioritized (See Narrative) | N/A |  | We are not planning to include this initiative. | Independent risk reduction calculation does not apply - see 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.1 | Support
Other | Emergency planning and preparedness | 7.3.9.3 | 7.3.9.3 Customer support in emergencies | All Consequences | All Consequences | <2018 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.1 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.2 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.3 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.4 | Emergency Consumer Protections | ECPMA FRMMA / WMPMA | In Compliance | • Gas & Electric Rules 1, 6, 11, 19.1, 19.2, and 19.3 • Electric Rules 12, 13, 15, 16, 21 |  |  |  | 0 | 3712.1701 | N/A | 0 | 3100 | N/A | 0 | 3190.52 | N/A | Line miles is not an applicable metric | Line miles is not an applicable metric | Line miles is not an applicable metric |  | Wildfire Consequence, PSPS Consequence | Yes | No | N/A | N/A |  | We are not planning to include this initiative. | Independent risk reduction calculation does not apply - see 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.1 | Support
Other | Emergency planning and preparedness | 7.3.9.4 | 7.3.9.4 Disaster and emergency preparedness plan | All Consequences | All Consequences | <2018 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.1 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.2 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.3 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.4 | N/A | FRMMA / WMPMA | In Compliance | GO 166 Standards 1-13 |  |  |  | 696 | 3833 | N/A | 1542 | 5459 | N/A | 1856.5 | 5617.5 | N/A | Line miles is not an applicable metric | Line miles is not an applicable metric | Line miles is not an applicable metric |  | Wildfire Consequence, PSPS Consequence | Yes | No | N/A | N/A |  | We are not planning to include this initiative. | Independent risk reduction calculation does not apply - see 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.1 | Support
Other | Emergency planning and preparedness | 7.3.9.5 | 7.3.9.5 Preparedness and planning for service restoration | All Consequences | All Consequences | <2018 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.1 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.2 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.3 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.4 | 2020 GRC | N/A | N/A | N/A |  |  |  | 252.6205 | 3685.8215 | N/A | 0 | 4248.2927 | N/A | 0 | 4384.3902 | N/A | Line miles is not an applicable metric | Line miles is not an applicable metric | Line miles is not an applicable metric |  | Wildfire Consequence, PSPS Consequence | Yes | No | N/A | N/A |  | We are not planning to include this initiative. | Independent risk reduction calculation does not apply - see 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.1 | Support
Other | Emergency planning and preparedness | 7.3.9.6 | 7.3.9.6 Protocols in place to learn from wildfire events | All Consequences | All Consequences | <2018 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.1 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.2 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.3 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.4 | 2020 GRC | N/A | N/A | N/A |  |  |  | 138.9413 | 2027.2018 | N/A | 0 | 2336.561 | N/A | 0 | 2411.4146 | N/A | Line miles is not an applicable metric | Line miles is not an applicable metric | Line miles is not an applicable metric |  | Wildfire Consequence, PSPS Consequence | Yes | No | N/A | N/A |  | We are not planning to include this initiative. | Independent risk reduction calculation does not apply - see 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.1 | Support
Other | Emergency planning and preparedness | 7.3.9.7 | 7.3.9.7 Other, Mutual Assistance | All Consequences | All Consequences | <2018 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.1 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.2 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.3 | See 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.4 | N/A | N/A | N/A | N/A |  |  |  | 0 | 0 | N/A | 0 | 0 | N/A | 0 | 0 | N/A | Line miles is not an applicable metric | Line miles is not an applicable metric | Line miles is not an applicable metric |  | Wildfire Consequence, PSPS Consequence | Yes | No | N/A | N/A |  | We are not planning to include this initiative. | Independent risk reduction calculation does not apply - see 7.3.9.1. All EP&R costs and risk reduction have been combined as one RSE reflected in 7.3.9.1 | Support
Other | Stakeholder Cooperation & Community Engagement | 7.3.10.1 | 7.3.10.1 Community engagement | N/A - Foundational | N/A - Foundational | 2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC and Transmission Owner | N/A | N/A | N/A |  |  |  | 0 | 9513.653 | N/A | 0 | 10514.1085 | N/A | 0 | 10807.2986 | N/A | Line miles is not an applicable metric | Line miles is not an applicable metric | Line miles is not an applicable metric |  | PSPS Consequence | No | Yes | Program Owner Prioritized (See Narrative) | N/A |  | We are not planning to include this initiative. | Risk reduction not quantified. Foundational Initiative, for which distinct financial and quantification data not currently available. | Support
Other | Stakeholder Cooperation & Community Engagement | 7.3.10.2 | 7.3.10.2 Cooperation and best practice sharing with agencies outside CA | N/A - Foundational | N/A - Foundational | <2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC and Transmission Owner | N/A | N/A | N/A |  |  |  | 0 | 12.5 | N/A | 0 | 12.865 | N/A | 0 | 13.2407 | N/A | Line miles is not an applicable metric | Line miles is not an applicable metric | Line miles is not an applicable metric |  | Ignition Risk - All Drivers | No | No | N/A | N/A |  | We are not planning to include this initiative. | Risk reduction not quantified. Foundational Initiative, for which distinct financial and quantification data not currently available. | Support
Other | Stakeholder Cooperation & Community Engagement | 7.3.10.3 | 7.3.10.3 Cooperation with suppression agencies | N/A - Foundational | N/A - Foundational | <2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | FRMMA WMPMA | N/A | N/A |  |  |  | 696 | 3833 | N/A | 1542 | 5459 | N/A | 1856.5 | 5617.5 | N/A | Line miles is not an applicable metric | Line miles is not an applicable metric | Line miles is not an applicable metric |  | Wildfire Consequence - All Consequences - Safety, Reliability, Financial | No | No | N/A | N/A |  | We are not planning to include this initiative. | Risk reduction not quantified. Foundational Initiative, for which distinct financial and quantification data not currently available. | Support
Other | Stakeholder Cooperation & Community Engagement | 7.3.10.4 | 7.3.10.4 Forest service and fuel reduction cooperation and joint roadmap | N/A - Foundational | N/A - Foundational | <2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC, Transmission Owner | FRMMA / WMPMA | N/A | N/A |  |  |  | 0 | 2687.3067 | N/A | 0 | 2786.7812 | N/A | 0 | 2862.5952 | N/A | Line miles is not an applicable metric | Line miles is not an applicable metric | Line miles is not an applicable metric |  | Wildfire Consequence - All Consequences - Safety, Reliability, Financial | No | Yes | Program Owner Prioritized (See Narrative) | N/A |  | We are not planning to include this initiative. | Risk reduction not quantified. Foundational Initiative, for which distinct financial and quantification data not currently available. | Support
Other | Stakeholder Cooperation & Community Engagement | 7.3.10.5 | 7.3.10.5 Other, PMO and General Wildfire Support | N/A - Foundational | N/A - Foundational | 2018 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | 2020 GRC | FRMMA / WMPMA Microgrid Memo Account | N/A | N/A |  |  |  | 0 | 31628.1884 | N/A | 0 | 32933.4952 | N/A | 0 | 32362.2457 | N/A | Line miles is not an applicable metric | Line miles is not an applicable metric | Line miles is not an applicable metric |  | Ignition Risk - All Drivers | No | N/A | N/A | N/A |  | We are not planning to include this initiative. | Risk reduction not quantified. Foundational Initiative, for which distinct financial and quantification data not currently available. | Support
|  | Total | [14 empty] | Total* | 2353974.1508 | 2467294.7956 | 1520272.2247 | 2497119.547 | 2396404.6897 | 1515112.845 | 2750126.5708 | 2367363.7557 | 1488764.1289
Updated comments for Table 12 (June 10, 2021): *PG&E has included in row 134 the totals for the financials and line miles treated numbers in Columns T-AB. For the purposes of completing the RSE calculations per the requirements in Critical Issue No. 3, PG&E disaggregated the spend and line miles treated for 7.3.3.17.1 (spend and line miles treated numbers are now spread over 7.3.3.3, 7.3.3.16, 7.3.3.17.5). For the capital costs and line miles treated columns, the formula for the totals in row 134 excludes the amounts in 7.3.3.3, 7.3.3.16, and 7.3.3.17.5 and dollars counted for the total are only from 7.3.3.17.1. For operating expense costs, the formula for the totals in row 134 excludes the amounts in 7.3.3.3 and 7.3.3.16, and dollars counted for the total are from 7.3.3.17.1 and 7.3.3.17.5 (expense dollars for 7.3.3.17.5 are not bundled with 7.3.3.17.1, only capital costs are). Updated comments for Table 12 (June 3, 2021): As discussed in Attachment "2021WMP_Revision_PGE-05_Atch01", the orange cells in this table highlight the differences between the June 3, 2021 submission and May 3, 2021 submission. In the course of preparing the requested 2021 WMP HFTD/Territory-wide data per Revision Notice, Critical Issue #5, we also reviewed the data again and made some adjustments to the line miles treated and financial numbers. Details on these changes are reflected in the "line miles treated comments" columns (Columns AC-AE) and the "Comments on Financials" column (Column AF). We have provided the original "May 3, 2021 filing" line miles treated and financial numbers in "Attachment 2021WMP_Revision_Change log". Comments for Table 12: 1. Table 12 includes a column labeled “Current compliance status – In / exceeding with regulations.” For purposes of this column and the adjacent column regarding rules, PG&E has interpreted the term “regulations” to mean CPUC General Orders and federal or state laws. However, for PSPS related initiatives, because of the relative newness of the PSPS program and lack of current regulations, PG&E has included CPUC decisions and resolutions as “regulations.” 2. PG&E is providing the following explanation regarding the financial spend information provided: • Mitigation and control work has been included in this Wildfire Mitigation Plan (WMP) and these tables that spans multiple cost recovery mechanisms including the General Rate Case (GRC), Transmission Owner (TO) rate case at the Federal Energy Regulatory Commission (FERC), Catastrophic Event Memorandum Account (CEMA), Fire Risk Mitigation Memorandum Account (FRMMA), Wildfire Mitigation Plan Memorandum Account (WMPMA), and EPIC. Some of these costs have already been approved for inclusion in customer rates and some of these costs are still pending review or approval through open and transparent cost recovery proceedings; • Financial figures have been mapped to each initiative and/or category based upon the activity being described in Section 7.3 of this document; • While the primary work performed for wildfire risk mitigation is in the HFTD areas, some work and financial costs associated with Non-HFTD areas have been included in some of these the financial figures; • The costs reflected are PG&E’s best estimate of the costs for the proposed programs as of February 5, 2021. Further changes to 2021 budgets and work plans are possible and actual costs may vary substantially from these plans depending on actual work completion, conditions and requirements; and, • For the “2020 Actual” and “2020 Projected” columns in Table 12, the population of work included in these financial data sets is aligned to the 2021 WMP scope and list of initiatives. Please note that due to changes in scope for some initiatives from the 2020 WMP to 2021 WMP (for example, PG&E has added/removed sub-initiatives or as indicated above, we are now referencing some Non-HFTD work and financials), we aligned the 2020 financial information with the 2021 scope to ensure consistency across the years of the table. 3. The “Program” column has been added to the WSD-defined template for Table 12 in response to Action Item PG&E-8 (Class A), more information is provided in section 4.6.1 on PG&E’s response to Action PG&E-8 (Class A).