## Discovery Log
**This Discovery Log reflects Data Requests completed as of 05:00PM each Wednesday
SDG&E 2023 WMP Discovery Log
Question Count | Party Name | DR Set # | Data Request | Question No. | Question ID | Question | Response | Requestor | Date Rec'd | Final Due Date | Date Sent | Link | Number of Atchs | NDA Required | WMP Section | Category | Sub Category
1 | CalPA | 2023-01 | CalPA-2023-01 | 1 | CalPA-2023-01.1 | Please provide a copy of each WMP-related document, submission, or report you submit to the Office of Energy Infrastructure Safety (Energy Safety) in 2023 that is related to your WMP. Provide the copy to Cal Advocates within one business day of the document’s submittal to Energy Safety. (If you have submitted the document to Energy Safety in 2023 prior to this data request, please provide a copy as soon as possible and no later than 10 business days from the issuance of this data request.) This request is limited to materials or documents that (1) are related to work plans, initiative targets, risk models, risk spend efficiency (RSE) calculations, or WMP change orders; and (2) are provided to Energy Safety to provide additional details or context concerning information or statements in your WMP (and any subsequent revisions or change orders affecting your WMP). | SDG&E generally objects to the request on the grounds set forth in General Objections Nos. 1, 2, 3, 5, and 7. Subject to the foregoing objections, SDG&E will address the request in Question 1 as reports are submitted to Energy Safety. | Aaron Louie | 2023-02-07 | 2023-02-15 | 2023-02-15 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-01.pdf | 0 | Yes | WMP Pre-Submissions | Administrative | N/A | N/A
2 | CalPA | 2023-01 | CalPA-2023-01 | 2 | CalPA-2023-01.2 | Please provide a copy of your WMP pre-submission within two business days of its submission to Energy Safety. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 1, 5, and 6. SDG&E further objects to the request on the grounds that it is not consistent with the 2023-2025 WMP Process and Evaluation Guidelines (2023 Guidelines) issued by Energy Safety. Per the 2023 Guidelines, the WMP pre-submission is not a public document and does not commence the WMP Review Process (2023 Guidelines at 3). “The completeness check is not a substantive review of WMP content; a substantive review occurs during the WMP evaluation process.” (Id.) Through public dissemination of the WMP pre-submission beyond Energy Safety’s completeness check, Cal Advocates attempts to further extend the WMP review period established by Public Utilities Code Section 8386.3(a) by an additional six weeks. This is both inconsistent with Section 8386.3(a) but also the spirit of the 2023 Guidelines, which establish that the pre-submission process occurs “prior to commencing evaluation.” (2023 Guidelines at 3). SDG&E respectfully requests that, to preserve the three-month review period, Cal Advocates refrain from any public dissemination of the pre-submission. SDG&E further notes that, due to the nature of the pre-submission completeness check process, there may be potential changes to the WMP pre-submission that may occur between now and the actual WMP submission date on March 27, either as required by Energy Safety or as made by SDG&E. Subject to the foregoing objections, SDG&E responds as follows: SDG&E’s 2023-2025 WMP Pre-submission is attached. | Aaron Louie | 2023-02-07 | 2023-02-15 | 2023-02-15 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-01.pdf | 0 | No | WMP Pre-Submissions | Administrative | N/A | N/A
3 | CalPA | 2023-01 | CalPA-2023-01 | 3 | CalPA-2023-01.3 | Provide a copy of all documents or files that are referenced in your WMP Quarterly Data Reports and submitted to Energy Safety (including but not limited to all PDFs, spatial data files, non-spatial data files, and confidential attachments) on the same business day that the document is sent to Energy Safety. | SDG&E generally objects to the request on the grounds set forth in General Objections Nos. 1, 2, 3, 5, and 7. Subject to the foregoing objections, SDG&E will address the request as documents and files are made available. | Aaron Louie | 2023-02-07 | 2023-05-01 | 2023-02-15 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-01.pdf | 0 | No | WMP QDR | Administrative | N/A | N/A
4 | CalPA | 2023-01 | CalPA-2023-01 | 4 | CalPA-2023-01.4 | Provide a copy to Cal Advocates of all your confidential responses to WMP discovery requests, on the same business day that you send the documents to the issuer of the discovery request. This includes: a) Confidential responses to WMP discovery requests issued by Energy Safety. b) Confidential responses to WMP discovery requests issued by other entities. | SDG&E generally objects to the request on the grounds set forth in General Objections Nos. 1, 2, 3, 5, and 7. Subject to the foregoing objections, SDG&E will address the request as documents and files are made available. | Aaron Louie | 2023-02-07 | N/A | 2023-02-15 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-01.pdf | 0 | No | WMP DRs | Administrative | N/A | N/A
5 | CalPA | 2023-02 | CalPA-2023-02 | 1 | CalPA-2023-02.1 | Please identify and provide a copy of all quality assurance or quality control (QA/QC) reports conducted by internal entities that were completed since January 1, 2022 and that examined any programs, initiatives, or strategies described in your 2022 WMP Update. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 1, 2, 3, 5, and 7. Subject to the foregoing objections, SDG&E responds as follows: Emergency Management SDG&E did not activate our PSPS protocols in 2022 therefore there are no QA/QC reports for actual events. In 2022 Emergency Management did conduct After-Action Reviews (AAR) for the following PSPS exercises: • PSPS Functional Exercise Aug 2022 • PSPS Tabletop with External Partners Jun 2022 • PSPS Notification Functional Exercise May 2022 Where external partners participated in the exercises, they were also included in development of the AAR report. Opportunities for input varied between in-person AAR workshops and online surveys. Each AAR also includes an Improvement Plan (IP) to capture items where corrective actions have been identified and assigned. AAR’s are completed in accordance with FEMA Homeland Security Exercise and Evaluation Program (HSEEP) guidelines. Electric Distribution Operations Electric Distribution Operations records emergency outage data for the entire service territory. We perform an internal two-stage review of all emergency outage data to ensure customer impact and restoration steps are accurate, but there are no QA/QC reports generated by Electric Distribution Operations as part of our review. The outage data we gather is audited internally by the Electric Reliability department.Vegetation Management Vegetation Management Quality Assurance team has several documents attached. They are summaries of pole brush audits, pre-inspection audits and post tree trimming work audits. Vegetation management QA team audits Wood Pole Inspection (WPI) These audits are performed on a monthly basis of completed pole inspections. Construction The SDG&E Portfolio & Project Management (PPM) Quality Assurance & Quality Control (QA/QC) department, in collaboration with WMP program and project leaders, examines WMP projects to verify compliance of project designs and construction to applicable SDG&E standards, specifications, and industry codes. Throughout 2022, thousands of facilities’ design packages were reviewed and, after construction, field inspected, assessed, and/or audited. After performing pre- and post-construction reviews and inspections, observations are presented to the project leads for resolution. PPM QA/QC completed assessments for approximately 5,000 work packages (3,500 work packages comprise WMP efforts), which identified approximately 46,000 pre-construction observations (Figure 1) and 6,000 post-construction findings. The figure below shows the estimated composition of findings identified in 2022 for all projects, including WMP projects, which comprise a subset of these data. Figure 1 depicts the most common pre-construction review observations related to material selection and general design errors. These observations are provided to the responsible Designer or Engineer for consideration and resolution, prior to issuance to construction. The composition of observations identified during post-construction inspections are: (1) as-built condition conflicts with current SDG&E Standards, (2) field conditions do not match design, (3) missing or incorrect hardware or pole tag markings, and (4) communication (Communication Infrastructure Provider (CIP), i.e. third party communication providers) line is not transferred to new facility. Over 2022, the average findings per structure totaled 1.31. These efforts fulfill one of several components of quality assurance and quality control due diligence for WMP programs and projects. Safety Management System SDG&E submits the attached Audit Advisory Memorandum issued March 2, 2022 (“21-204 – SDG&E Safety Management System Program Assessment”). Sempra’s Audit Services performed an advisory review of SDG&E’s Safety Management System (SMS). The scope of this Audit Services advisory included a documentation review of SMS governance framework and processes with a primary objective to support a successful launch, including areas where investments maybe necessary to ensure enduring success of the program, such as additional resources and technology. Transmission and Substation Ops SDG&E submits its Transmission Construction and Maintenance Quality Control Verification Report. The attached report (“Transmission Construction and Maintenance Quality Control Verification Report 2022”) describes audits performed in 2022, including only structures in the HFTD Meteorology SDG&E network of weather stations • SDG&E operates a dense network of surface weather network, currently made of 222 weather stations, and it is foundational to SDG&E’s ability to understand and predict the potential of elevated fire weather events and their impacts on local communities in its service territory. It is imperative that this weather network remains operational at all costs as it allows us to have a real-time monitoring of weather conditions that could be crucial in accurately determining the precise timing and location of powerline de-energizations required during the Public Safety Power Shutoff (PSPS) events. During the course of the year in 2022, SDG&E performs maintenance work to its weather stations by calibrating its sensors and replacing its batteries that are not in their optical states. 221 weather stations were calibrated in 2022. SDG&E supercomputing clusters in support of performing high-resolution numerical weather prediction forecast simulations that are tailored to the SDG&E service territory • To stay informed on future weather conditions that could lead to increased wildfire risk and other hazardous conditions, SDG&E performs ensembles of the state-of-the-art numerical weather prediction model forecast simulations on its in-house supercomputers every day. This allows SDG&E to monitor and to predict the wildfire risk by calculating its Fire Potential Index (FPI), which is a planning and decision-supporting tool designed to reduce the wildfire risk by examining the susceptibility of the environment to fire and its daily calculations are shared broadly with the community. Therefore, ensuring that the inhouse supercomputing clusters remain in healthy mode is critical. Noting that the currently in-production computing infrastructures were reaching the end of expective lifetime, SDG&E have taken a proactive action and purchased new supercomputing clusters in 2022. Purchasing the new supercomputing clusters means setting up the latest version of the numerical weather prediction model and optimizing its configuration that will be running operationally, so SDG&E have performed the model validation simulations for a selection of high-impact weather conditions ranging from Santa Ana winds, winter storms/atmospheric rivers, and monsoonal thunderstorms Advancing the science of fire spread modeling • To increase the accuracy of predicting the rate of fire spread, SDG&E has collaborated with an academic partner (SJSU: San Jose State University) to further advance the science of fire spread modeling. The SJSU fire spread model is an improvement over the popularly used fire spread model by incorporating the effects of two-way coupling between the atmosphere and fire-induced heat fluxes into the model. SJSU has also been developing the new live fuel moisture model that can be used in their coupled weather-fire model. ML-based model of predicting vegetation-related outages • SDG&E have established an external collaborative partnership with San Diego Supercomputer Center (SDSC) to construct a ML-based model of predicting vegetationrelated outages by examining previous vegetation-related outages and weather conditions that were associated with them. The daily output from the model will be useful in safe and reliable operations of the grid system. Running a large ensemble of weather forecasts to improve the prediction of Santa Ana winds • Given intrinsic uncertainty associated with numerical weather prediction, it is imperative to measure and quantify the uncertainty in the forecasted weather conditions, especially if high-impact weather conditions, such as gusty Santa Ana winds, are expected over the service territory. For this reasons, SDG&E have partnered with UC San Diego CW3E (Center for Western Weather and Water Extreme) to perform a large ensemble (200 members) of the weather forecasts for uncertainty quantification and use the 200-member ensemble to derive an index (Santa Ana Index) that characterizes the potential impact of predicted gusty offshore winds. Customer Programs Within SDG&E, the Customer Programs department facilitates the operation of the Generator Assistance Program (GAP), which offers point-of-sale rebates (via instant rebate coupons) and downstream rebates (via post-purchase application) for portable generator and battery units to qualifying customers in HFTD Tiers 2 and 3. This program is managed by a third-party and the QA/QC processes includes the following. It should be noted that no formal QA/QC reports are generated, but the third-party utilizes this structure to notify SDG&E of any QA/QC updates that are needed: • Fraud QA: Run weekly reports to prevent ineligible or fraudulent reservations using bogus email accounts (example: fred@fakemail.xyz) • Coupon Participation limit QA: A weekly verification that checks coupon reservations against each program’s past participation rules and logic (e.g. 1 coupon limit per eligible customer per year). An automated workflow uses these rules and compares them against the coupons that have been reserved to make sure everything is working properly. The process checks against duplicate addresses, account numbers, IP addresses, customer names, phone numbers, email addresses, etc., to make sure that each customer is participating per the GAP program’s participation limit rules. • Coupon/Rebate Application QA: Run weekly reports to verify all coupons and rebate applications are correctly filled out (no missing data, all naming conventions, product URLs, amounts are correct, etc.), all program specific information is being populated and that statuses are correct. • Portal QA: Monthly review of the program portal to verify accurate data, system performance, and product availability Asset Management SDG&E submits the attached 20 files which document QA/QC audits performed by our districts that perform our electric distribution asset inspections. These audits are performed by SDG&E’s Electric Construction Supervisors on a quarterly basis. These files consist of a summary document that outlines the number of audits required for the overhead detailed inspections (1.5% of the inspections completed), a detailed listing of those audits requiring to be performed, and audits for our overhead repairs (typically 1%). Drone Inspection Program SDG&E performs quality assurance reviews on all inspections completed as part of its Drone Investigation Assessment and Repair (DIAR) Program. After the Inspector completes the inspection, a Supervisor reviews the assessment and images before approving the inspection results. If any discrepancies are identified, the Supervisor will provide feedback to the Inspector during regular team meetings and the inspection findings will be updated prior to finalization. The images and findings are then processed through the machine learning models in production. Similarly, if there are any variations between the results of the machine learning model findings and the Inspector’s findings, that information will be reviewed and validated by the Supervisor. Information will be sent back to the Supervisor and the missed issues will be included in the inspection findings prior to finalization. Access and Functional Needs PSPS 112221 After Action Review_PSPS Partners 120621 After a PSPS event, 211 prepares and submits a detailed summary of actions completed and services provided to SDG&E medical baseline and/or access and functional needs customers that call in during a PSPS event. Details summarized in the report includes: calls intake, referral services such as, hotel stays, transportation, and back-up power unit if needed. AudioEye Issue Report sdge.com-02_16_2023 Effective real-time communications with customer affected by PSPS and other power outages is critical for the health and safety of all customers. One of our most important customer communication channels is the SDGE.com website and the PSPS preparedness and event information within the site. The Audio Eye Issue Report is run every week and constant improvements and accessibility enhancements are being made to address issues identified within the report. Accessibility of the website, to the WCAG 2.1 AA success criteria, is a constant focus and high importance for SDG&E. AudioEye monitors SDGE.com and SDGEnews.com for accessibility issues and provides technical reports and remediation solutions with our Web Team. AE-STAR-sdge.com-2023-02-16 The AudioEye Sustainable Testing and Remediation (STAR) Plan provides SDG&E’s Web Team with a road map of corrective measures each week to enhance and comply with accessibility guidelines (WCAG 2.1 AA) | Aaron Louie | 2023-02-07 | 2023-02-22 | 2023-02-22 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-02.pdf https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-02%20Q1%20Attachment.zip | 1 | No | 2022 WMP | QA/QC | N/A | N/A
6 | CalPA | 2023-02 | CalPA-2023-02 | 2 | CalPA-2023-02.2 | Please identify and provide a copy of all quality assurance or quality control (QA/QC) reports conducted by external entities that were completed since January 1, 2022 and that examined any programs, initiatives, or strategies described in your 2022 WMP Update. External entities include, but are not limited to, consultants, contractors, auditors, court-appointed monitors, and Independent Evaluators. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 1, 2, 3, 5, and 7. Subject to the foregoing objections, SDG&E responds as follows: Transmission and Substation Operations In 2022, the CPUC ESRB conducted 4 audits as follows: • June 13-17 – Orange County District Substation Audit • December 5-9 – Northeast District Substation Audit • December 12-16 – Metro District Substation Audit • December 12-16 – Mountain/Inland/Coastal Transmission Audit Copies of the CPUC audit reports for the three substation audits are provided as part of this data request response. The audit for the December Mountain/Inlad/Coastl Transmission area has not yet been received from the CPUC. SDG&E references the “2022 California Independent System Operator Corporation (ISO) Maintenance Review – Final Report” attached hereto. The report published November 2022 documents the ISO 2022 annual maintenance review of SDG&E’s filed maintenance practices for transmission facilities placed under the ISO operational control. Electric Regional Operations In 2022, the CPUC ESRB conducted one audit associated with distribution operations and maintenance as follows: • August 1-5 – Beach Cities District Audit A copy of the CPUC audit report for Beach Cities District is provided as part of this data request response. Emergency Management Emergency Management activities are typically audited by external entities the year following the activities, for example, 2022 activities will be audited in 2023. Therefore, there are no QA/QC reports conducted by external entities in 2022 for 2022 WMP activities. | Aaron Louie | 2023-02-07 | 2023-02-22 | 2023-02-22 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-02.pdf https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-02%20Q2%20Attachment.zip | 1 | No | 2022 WMP | QA/QC | N/A | N/A
7 | CalPA | 2023-02 | CalPA-2023-02 | 3 | CalPA-2023-02.3 | Provide an Excel table of all defects in the year 2022 found by Energy Safety’s Compliance Branch (as rows) that includes the following information in separate columns. a) Associated circuit name b) Defect type c) Description of defect d) WMP initiative (from your 2022 WMP update) associated with defect e) Date that the defect was identified f) Date that the defect was corrected g) If the defect has not yet been corrected as of the issuance date of this data request, a brief explanation h) Priority level of corresponding corrective tag i) Geographic latitude of defect in decimal degrees, truncated to seven decimal places j) Geographic longitude of defect in decimal degrees, truncated to seven decimal places | SDG&E objects to the request on the grounds set forth in General Objections Nos. 5 and 8. Subject to the foregoing objections, SDG&E responds as follows: N/A | Aaron Louie | 2023-02-07 | 2023-02-22 | 2023-02-22 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-02.pdf | 0 | No | 2022 WMP | Defects | N/A | N/A
8 | CalPA | 2023-03 | CalPA-2023-03 | 1 | CalPA-2023-03.1 | Provide an Excel table of all distribution circuits existing as of January 1, 2023 (as rows) that includes the following information in separate columns. a) Circuit name b) Circuit ID number c) Total circuit miles d) Circuit miles in Non-HFTD Areas e) Circuit miles in Other HFTD f) Circuit miles in HFTD Tier 2 g) Circuit miles in HFTD Tier 3 h) Circuit voltage i) Circuit SAIDI (System Average Interruption Duration Index) for 2021 j) Circuit SAIDI (System Average Interruption Duration Index) for 2022 k) Circuit SAIFI (System Average Interruption Frequency Index) for 2021 l) Circuit SAIFI (System Average Interruption Frequency Index) for 2022 m) Circuit MAIFI (Momentary Average Interruption Frequency Index) for 2021 n) Circuit MAIFI (Momentary Average Interruption Frequency Index) for 2022 o) Total customer-minutes of de-energization on the circuit due to PSPS events in 2021 (sum of customer-minutes across all PSPS events). p) Total customer-minutes of de-energization on the circuit due to PSPS events in 2022 (sum of customer-minutes across all PSPS events). q) Total customer-minutes of de-energization on the circuit due to fast-trip settings in 2021. r) Total customer-minutes of de-energization on the circuit due to fast-trip settings in 2022. s) Number of trees that were worked on for EVM in Non-HFTD in 2021 t) Number of trees that were worked on for EVM in Non-HFTD in 2022 u) Number of trees that were worked on for EVM in Other HFTD in 2021 v) Number of trees that were worked on for EVM in Other HFTD in 2022 w) Number of trees that were worked on for EVM in HFTD Tier 2 in 2021 x) Number of trees that were worked on for EVM in HFTD Tier 2 in 2022 y) Number of trees that were worked on for EVM in HFTD Tier 3 in 2021 z) Number of trees that were worked on for EVM in HFTD Tier 3 in 2022 aa) Miles of covered conductor installed in Non-HFTD in 2021 bb) Miles of covered conductor installed in Non-HFTD in 2022 cc) Miles of covered conductor installed in Other HFTD in 2021 dd) Miles of covered conductor installed in Other HFTD in 2022 ee) Miles of covered conductor installed in HFTD Tier 2 in 2021 ff) Miles of covered conductor installed in HFTD Tier 2 in 2022 gg) Miles of covered conductor installed in HFTD Tier 3 in 2021 hh) Miles of covered conductor installed in HFTD Tier 3 in 2022 ii) Number of poles replaced in Non-HFTD in 2021 jj) Number of poles replaced in Non-HFTD in 2022 kk) Number of poles replaced in Other HFTD in 2021 ll) Number of poles replaced in Other HFTD in 2022 mm) Number of poles replaced in HFTD Tier 2 in 2021 nn) Number of poles replaced in HFTD Tier 2 in 2022 oo) Number of poles replaced in HFTD Tier 3 in 2021 pp) Number of poles replaced in HFTD Tier 3 in 2022 qq) Miles of underground conductor installation in Non-HFTD in 2021 rr) Miles of underground conductor installation in Non-HFTD in 2022 ss) Miles of underground conductor installation in Other HFTD in 2021 tt) Miles of underground conductor installation in Other HFTD in 2022 uu) Miles of underground conductor installation in HFTD Tier 2 in 2021 vv) Miles of underground conductor installation in HFTD Tier 2 in 2022 ww) Miles of underground conductor installation in HFTD Tier 3 in 2021 xx) Miles of underground conductor installation in HFTD Tier 3 in 2022 yy) Miles of LiDAR inspection in Non-HFTD in 2021 zz) Miles of LiDAR inspection in Non-HFTD in 2022 aaa) Miles of LiDAR inspection in Other HFTD in 2021 bbb) Miles of LiDAR inspection in Other HFTD in 2022 ccc) Miles of LiDAR inspection in HFTD Tier 2 in 2021 ddd) Miles of LiDAR inspection in HFTD Tier 2 in 2022 eee) Miles of LiDAR inspection in HFTD Tier 3 in 2021 fff) Miles of LiDAR inspection in HFTD Tier 3 in 2022 ggg) Number of detailed overhead inspections in Non-HFTD in 2021 hhh) Number of detailed overhead inspections in Non-HFTD in 2022 iii) Number of detailed overhead inspections in Other HFTD in 2021 jjj) Number of detailed overhead inspections in Other HFTD in 2022 kkk) Number of detailed overhead inspections in HFTD Tier 2 in 2021 lll) Number of detailed overhead inspections in HFTD Tier 2 in 2022 mmm) Number of detailed overhead inspections in HFTD Tier 3 in 2021 nnn) Number of detailed overhead inspections in HFTD Tier 3 in 2022 ooo) Number of sectionalization devices installed in Non-HFTD in 2021 ppp) Number of sectionalization devices installed in Non-HFTD in 2022 qqq) Number of sectionalization devices installed in Other HFTD in 2021 rrr) Number of sectionalization devices installed in Other HFTD in 2022 sss) Number of sectionalization devices installed in HFTD Tier 2 in 2021 ttt) Number of sectionalization devices installed in HFTD Tier 2 in 2022 uuu) Number of sectionalization devices installed in HFTD Tier 3 in 2021 vvv) Number of sectionalization devices installed in HFTD Tier 3 in 2022 | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, and 7. Subject to and without waiving the foregoing objections, SDG&E responds as follows: Please see response provided in “CalPA-SDGE-2023WMP-DR03.xlsx.” | Aaron Louie | 2023-02-07 | 2023-03-07 | 2023-03-07 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-03.pdf https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-03%20Attachment.xlsx | 1 | No | Other | Circuit Info | N/A | N/A
9 | CalPA | 2023-03 | CalPA-2023-03 | 2 | CalPA-2023-03.2 | Provide an Excel table of all transmission circuits existing as of January 1, 2023 (as rows) that includes the following information in separate columns. a) Circuit name b) Circuit ID number c) Total circuit miles d) Circuit miles in Non-HFTD Areas e) Circuit miles in Other HFTD f) Circuit miles in HFTD Tier 2 g) Circuit miles in HFTD Tier 3 h) Circuit voltage i) Total customer-minutes of de-energization on the circuit due to PSPS events in 2021 (sum of customer-minutes across all PSPS events). j) Total customer-minutes of de-energization on the circuit due to PSPS events in 2022 (sum of customer-minutes across all PSPS events). k) Total customer-minutes of de-energization on the circuit due to fast-trip settings in 2021. l) Total customer-minutes of de-energization on the circuit due to fast-trip settings in 2022. m) Number of support structures replaced in Non-HFTD in 2021 n) Number of support structures replaced in Non-HFTD in 2022 o) Number of support structures replaced in Other HFTD in 2021 p) Number of support structures replaced in Other HFTD in 2022 q) Number of support structures replaced in HFTD Tier 2 in 2021 r) Number of support structures replaced in HFTD Tier 2 in 2022 s) Number of support structures replaced in HFTD Tier 3 in 2021 t) Number of support structures replaced in HFTD Tier 3 in 2022 u) Miles of LiDAR inspection in Non-HFTD in 2021 v) Miles of LiDAR inspection in Non-HFTD in 2022 w) Miles of LiDAR inspection in Other HFTD in 2021 x) Miles of LiDAR inspection in Other HFTD in 2022 y) Miles of LiDAR inspection in HFTD Tier 2 in 2021 z) Miles of LiDAR inspection in HFTD Tier 2 in 2022 aa) Miles of LiDAR inspection in HFTD Tier 3 in 2021 bb) Miles of LiDAR inspection in HFTD Tier 3 in 2022 cc) Number of detailed aerial inspections in Non-HFTD in 2021 dd) Number of detailed aerial inspections in Non-HFTD in 2022 ee) Number of detailed aerial inspections in Other HFTD in 2021 ff) Number of detailed aerial inspections in Other HFTD in 2022 gg) Number of detailed aerial inspections in HFTD Tier 2 in 2021 hh) Number of detailed aerial inspections in HFTD Tier 2 in 2022 ii) Number of detailed aerial inspections in HFTD Tier 3 in 2021 jj) Number of detailed aerial inspections in HFTD Tier 3 in 2022 kk) Number of detailed climbing inspections in Non-HFTD in 2021 ll) Number of detailed climbing inspections in Non-HFTD in 2022 mm) Number of detailed climbing inspections in Other HFTD in 2021 nn) Number of detailed climbing inspections in Other HFTD in 2022 oo) Number of detailed climbing inspections in HFTD Tier 2 in 2021 pp) Number of detailed climbing inspections in HFTD Tier 2 in 2022 qq) Number of detailed climbing inspections in HFTD Tier 3 in 2021 rr) Number of detailed climbing inspections in HFTD Tier 3 in 2022 ss) Number of detailed ground inspections in Non-HFTD in 2021 tt) Number of detailed ground inspections in Non-HFTD in 2022 uu) Number of detailed ground inspections in Other HFTD in 2021 vv) Number of detailed ground inspections in Other HFTD in 2022 ww) Number of detailed ground inspections in HFTD Tier 2 in 2021 xx) Number of detailed ground inspections in HFTD Tier 2 in 2022 yy) Number of detailed ground inspections in HFTD Tier 3 in 2021 zz) Number of detailed ground inspections in HFTD Tier 3 in 2022 aaa) Number of sectionalization devices installed in Non-HFTD in 2021 bbb) Number of sectionalization devices installed in Non-HFTD in 2022 ccc) Number of sectionalization devices installed in Other HFTD in 2021 ddd) Number of sectionalization devices installed in Other HFTD in 2022 eee) Number of sectionalization devices installed in HFTD Tier 2 in 2021 fff) Number of sectionalization devices installed in HFTD Tier 2 in 2022 ggg) Number of sectionalization devices installed in HFTD Tier 3 in 2021 hhh) Number of sectionalization devices installed in HFTD Tier 3 in 2022 iii) Miles of transmission ROW expansion performed in Non-HFTD in 2021 jjj) Miles of transmission ROW expansion performed in Non-HFTD in 2022 kkk) Miles of transmission ROW expansion performed in Other HFTD in 2021 lll) Miles of transmission ROW expansion performed in Other HFTD in 2022 mmm) Miles of transmission ROW expansion performed in HFTD Tier 2 in 2021 nnn) Miles of transmission ROW expansion performed in HFTD Tier 2 in 2022 ooo) Miles of transmission ROW expansion performed in HFTD Tier 3 in 2021 ppp) Miles of transmission ROW expansion performed in HFTD Tier 3 in 2022 | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, and 7. Subject to and without waiving the foregoing objections, SDG&E responds as follows: Please see response provided in “CalPA-SDGE-2023WMP-DR03.xlsx.” | Aaron Louie | 2023-02-07 | 2023-03-07 | 2023-03-07 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-03.pdf https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-03%20Attachment.xlsx | 1 | No | Other | Circuit Info | N/A | N/A
10 | CalPA | 2023-03 | CalPA-2023-03 | 3 | CalPA-2023-03.3 | Provide an Excel table of all distribution circuits existing as of January 1, 2022 (as rows) that were removed or decommissioned in 2022, either partially or entirely. This includes permanent removal, removal of overhead lines that were moved underground, or overhead lines that were decommissioned but not physically removed. Include the following information in separate columns. a) Circuit name b) Circuit ID number c) Circuit miles removed or decommissioned in Non-HFTD Areas d) Circuit miles removed or decommissioned in Other HFTD e) Circuit miles removed or decommissioned in HFTD Tier 2 f) Circuit miles removed or decommissioned in HFTD Tier 3 g) Reason(s) for removal or decommissioning | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, and 7. Subject to and without waiving the foregoing objections, SDG&E responds as follows: Please see response provided in “CalPA-SDGE-2023WMP-DR03.xlsx.” | Aaron Louie | 2023-02-07 | 2023-03-07 | 2023-03-07 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-03.pdf https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-03%20Attachment.xlsx | 1 | No | Other | Circuit Info | N/A | N/A
11 | CalPA | 2023-03 | CalPA-2023-03 | 4 | CalPA-2023-03.4 | Provide an Excel table of all transmission circuits existing as of January 1, 2022 (as rows) that were removed or decommissioned in 2022, either partially or entirely. This includes permanent removal, removal of overhead lines that were moved underground, or overhead lines that were decommissioned but not physically removed. Include the following information in separate columns. a) Circuit name b) Circuit ID number c) Circuit miles removed or decommissioned in Non-HFTD Areas d) Circuit miles removed or decommissioned in Other HFTD e) Circuit miles removed or decommissioned in HFTD Tier 2 f) Circuit miles removed or decommissioned in HFTD Tier 3 g) Reason(s) for removal or decommissioning | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, and 7. Subject to and without waiving the foregoing objections, SDG&E responds as follows: Please see response provided in “CalPA-SDGE-2023WMP-DR03.xlsx.” | Aaron Louie | 2023-02-07 | 2023-03-07 | 2023-03-07 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-03.pdf https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-03%20Attachment.xlsx | 1 | No | Other | Circuit Info | N/A | N/A
12 | CalPA | 2023-03 | CalPA-2023-03 | 5 | CalPA-2023-03.5 | For each WMP initiative listed below, please state how the modeled Wildfire Risk Scores for each circuit or circuit-segment influenced where you performed work in 2022. a) EVM b) Covered conductor installation c) Undergrounding d) Distribution pole replacement e) Grid sectionalization f) Detailed inspections of distribution assets g) Detailed inspections of transmission assets h) Aerial inspections of distribution assets i) Aerial inspections of transmission assets j) LiDAR inspections of distribution assets k) LiDAR inspections of transmission assets | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, and 7. SDG&E further objects to the request on the grounds that it misstates facts or assumes facts that do not exist. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) SDG&E Vegetation Management (VM) does not utilize the modeled Wildfire Risk Scores to plan EVM (greater trim clearances) work within specific circuits or circuit segments. VM performs EVM as a component of its routine and off-cycle tree trim activities at the Vegetation Management Area (VMA) level throughout the HFTD. SDG&E follows a static, annual Master Schedule of VM activities for pre-inspection and tree trimming. Work may be prioritized as required if observed conditions warrant during the pre-inspection activity. While SDG&E’s EVM program does not scope work prioritizing circuit risk scores, it does focus on applying expanded post-trim clearances on targeted species identified as higher risk due to growth potential, failure characteristics, and relative outage frequency. The criteria for determining post‐trim clearances included multiple factors such as species, height, growth rate, health, location of defect, site conditions, pruning schedule, and proper pruning cuts. In 2022, SDG&E continued to perform required clearing activities on subject poles located within the SRA as required by Public Resources Code Section 4292. The SRA does not align completely with the HFTD boundary, so as an extra precautionary measure, SDG&E will consider additional poles located outside SRA where Public Resources Code Section 4292 does not apply, including on poles located within the Local Responsibility Areas. Additionally in 2022, SDG&E continued to perform vegetation fuels reduction activities surrounding poles located within the HFTD. For this activity, SDG&E does use the Circuit Risk Index and WiNGS modeling to determine areas to perform this work. b) Covered conductor installation The Wildfire Risk Scores are an output from the WiNGS-Planning Model and support with the prioritization of hardening. Currently, Risk Spend Efficiencies (RSEs) in the WiNGS-Planning are used to inform how to invest in mitigations that reduce risk. The WiNGS-Planning analyzes each circuit-segment to recommend strategic undergrounding (UG), covered conductor (CC) or no UG / CC. Although the risk reduction targets are often aimed at cost effectiveness, annual performance objectives, mileage targets, and other limitations and constraints are also considered to inform investment decisions. c) Undergrounding Please see response 5 (b). d) SDG&E did not complete any work for the Distribution Pole Replacement program in 2022. The future planned work for this program will have multiple risk categories and will be prioritized based on these categories. • Phase 1 (approximately 85 poles): Pole set in concrete and steel reinforced or pole set in concrete and not steel reinforced • Phase 2 (approximately 58 poles): Pole set in soil and steel reinforced • Phase 3 (approximately 1,379 poles): Pole set in soil and not steel reinforced e) SDG&E Grid Sectionalization program receives feedback from meteorology for PSPS opportunities based on new grid hardening projects such as Covered Conductor and Strategic Undergrounding in addition to stand-alone switch installations. SDG&E District Engineers also perform evaluations on the value of new switches by prioritizing customer impacts; they provide recommendations based on historical events and submit work order requests for new installations. f) Detailed inspections of distribution assets are mandated by GO 165, which determines the timeframe and cycle for performing inspections. Per GO 165, detailed inspections of overhead facilities are currently completed on a 5-year cycle for all overhead structures, including those in the HFTD. Although the modeled wildfire risk scores for each circuit are not explicitly used to determine where inspections are performed, non-routine ad hoc inspections may be conducted for operational or reliability purposes and consider various factors such as location and risk. Additionally, SDG&E prioritizes detailed inspections in the HFTD prior to fire season. Detailed inspections are also supplemented by risk-informed drone inspections. g) SDG&E does not currently model wildfire risk scores for transmission tielines; therefore, modeled wildfire risk scores did not influence where detailed inspections of transmission assets in 2022 were performed. h) The drone inspection program began in 2019, and its scope included all distribution structures in Tier 2 and Tier 3 of the HFTD and coastal canyon areas within the WUI. SDG&E successfully completed this program in 2022 inspecting every structure in the aforementioned regions. Circuit risk ranking in combination with a list of circuits that had previously been subject to a Public Safety Power Shutoff (PSPS) event was used to prioritize which circuits were inspected prior to others within that HFTD. For Tier 2 HFTD circuits, the circuit risk ranking was provided in response to CALPA DR5 Q9. i) SDG&E does not currently model wildfire risk scores for transmission tielines; therefore, modeled wildfire risk scores did not influence where aerial inspections of transmission assets in 2022 were performed. Aerial inspections were instead prioritized based on historical outage or fault data. j) In 2022, all distribution circuits within the HFTD had Light Detection and Ranging (LiDAR) data captured and processed. SDG&E did not utilize modeled wildfire risk scores to determine the scope of this program because all distribution circuits in the HFTD were included. k) SDG&E did not perform LiDAR inspections of transmission assets in 2022 except where there was distribution underbuilt on the structure. | Aaron Louie | 2023-02-07 | 2023-03-07 | 2023-03-07 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-03.pdf | 0 | No | 2022 WMP | Wildfire Risk Score | N/A | N/A
13 | CalPA | 2023-03 | CalPA-2023-03 | 6 | CalPA-2023-03.6 | For each WMP initiative listed below, please state how the modeled Wildfire Risk Scores for each circuit or circuit-segment influenced how work in 2022 was sequenced. a) EVM b) Covered conductor installation c) Undergrounding d) Distribution pole replacement e) Grid sectionalization f) Detailed inspections of distribution assets g) Detailed inspections of transmission assets h) Aerial inspections of distribution assets i) Aerial inspections of transmission assets j) LiDAR inspections of distribution assets k) LiDAR inspections of transmission assets | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, and 7. SDG&E further objects to the request to the extent it misstates facts and/or assumes facts that do not exist. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) SDG&E Vegetation Management (VM) does not utilize the modeled Wildfire Risk Scores to plan EVM (greater trim clearances) work within specific circuits or circuit segments. VM performs EVM as part of its routine and off-cycle tree trim activities at the Vegetation Management Area (VMA) level throughout the HFTD. SDG&E follows a static, annual Master Schedule of VM activities for pre-inspection and tree trimming. Work may be prioritized as required if observed conditions warrant during the pre-inspection activity. b) Covered conductor installation The Wildfire Risk Scores are an output from the WiNGS-Planning Model and support with the prioritization of hardening. Additional considerations such as efficiencies that can reduce the resource burden are considered. Limiting projects to geographically proximate locations can optimize survey time (reducing travel times for teams fielding the fire hardening scope), limit mobilization/demobilization for construction crews, and optimize use of existing laydown yards. Long-term planning is also considered to ensure that year-over-year mileage targets are met. After the circuit-segment mitigation projects have been selected and prioritized, a desktop scoping and feasibility study is performed which includes geography, prior hardening, loading, standards, land/environmental, operational improvements, easement constraints, reliability improvements, and construction cost savings all help to dictate the sequence of projects. c) Undergrounding Please see response 6 (b). d) For the Distribution Pole Replacement Program, Phase 1 poles would be addressed first, followed by Phase 2 then Phase 3. However, permitting, land rights, environmental mitigation, customer concerns, or a combination of these factors will drive the ultimate schedule on each pole's replacement. Where feasible, poles will be bundled together in a single work package to minimize the impact to the community and gain efficiency in the design, environmental, permitting, land rights, and construction process. In most cases a single work order package will bundle poles that are adjacent or within a few spans of each other and will require similar land rights, permitting, and/or land rights. e) SDG&E Grid Sectionalization program is sequenced based on input from multiple stakeholders who determine where the greatest customer impacts can be realized. When this evaluation is performed in association with work being performed associated with hardening initiatives such as Covered Conductor or Strategic Undergrounding, it is sequenced according to that program. f) Detailed inspections of distribution assets are mandated by GO 165, which determines the timeframe and cycle for performing inspections. GO 165 also prescribes the acceptable interval, a 4month period within the calendar year, which dictates the sequencing of inspections throughout the year. Although the modeled wildfire risk scores for each circuit are not explicitly used to determine the sequencing of inspections, SDG&E prioritizes detailed inspections in the HFTD prior to fire season and has shifted inspections into earlier intervals to address risk. Non-routine, ad hoc inspections may be conducted for operational or reliability purposes and consider various factors such as location and risk. Additionally, detailed inspections are also supplemented by risk-informed drone inspections. g) SDG&E does not currently model wildfire risk scores for transmission tielines; therefore, modeled wildfire risk scores did not influence how detailed inspections of transmission assets in 2022 were sequenced. h) The drone inspection program began in 2019, and its scope included all distribution structures in Tier 2 and Tier 3 of the HFTD and coastal canyon areas within the WUI. SDG&E successfully completed this program in 2022 inspecting every structure in aforementioned regions. Circuit risk ranking in combination with a list of circuits that had previously been subject to a Public Safety Power Shutoff (PSPS) event was used to prioritize which circuits were inspected prior to others within that HFTD. For Tier 2 HFTD circuits, the circuit risk ranking was provided CALPA DR5 Q9. i) SDG&E does not currently model wildfire risk scores for transmission tielines; therefore, modeled wildfire risk scores did not influence how aerial inspections of transmission assets in 2022 were sequenced. j) LiDAR inspections of distribution assets were captured for the entire HFTD. The sequencing of the work was not based on risk scores. The LiDAR data was captured by capturing all the circuits in a certain region to minimize the number of flights required to complete the data capture. k) SDG&E did not perform LiDAR inspections of transmission assets in 2022 except where there was distribution underbuilt on the structure. | Aaron Louie | 2023-02-07 | 2023-03-07 | 2023-03-07 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-03.pdf | 0 | No | 2022 WMP | Wildfire Risk Score | N/A | N/A
14 | CalPA | 2023-03 | CalPA-2023-03 | 7 | CalPA-2023-03.7 | For each WMP initiative listed below, please state how the modeled Wildfire Risk Scores for each circuit or circuit-segment influence where you plan to perform work in 2023. a) EVM b) Covered conductor installation c) Undergrounding d) Distribution pole replacement e) Grid sectionalization f) Detailed inspections of distribution assets g) Detailed inspections of transmission assets h) Aerial inspections of distribution assets i) Aerial inspections of transmission assets j) LiDAR inspections of distribution assets k) LiDAR inspections of transmission assets | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, and 7. SDG&E further objects to the request to the extent it misstates facts and/or assumes facts that do not exist. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) SDG&E Vegetation Management (VM) does not utilize the modeled Wildfire Risk Scores to plan EVM (greater trim clearances) work within specific circuits or circuit segments. VM performs EVM as part of its routine and off-cycle tree trim activities at the Vegetation Management Area (VMA) level throughout the HFTD. SDG&E follows a static, annual Master Schedule of VM activities for pre-inspection and tree trimming. Work may be prioritized as required if observed conditions warrant during the pre-inspection activity. While SDG&E’s EVM program does not scope work prioritizing circuit risk scores, it does focus on applying expanded post-trim clearances on targeted species identified as higher risk due to growth potential, failure characteristics, and relative outage frequency. The criteria for determining post‐trim clearances included multiple factors such as species, height, growth rate, health, location of defect, site conditions, pruning schedule, and proper pruning cuts. In 2023, SDG&E will continue to perform required clearing activities on subject poles located within the SRA as required by Public Resources Code Section 4292. The SRA does not align completely with the HFTD boundary, so as an extra precautionary measure, SDG&E will consider additional poles located outside SRA where Public Resources Code Section 4292 does not apply, including on poles located within the Local Responsibility Areas. Additionally in 2023, SDG&E will continue to perform vegetation fuels reduction activities surrounding poles located within the HFTD. For this activity, SDG&E does use the Circuit Risk Index and WiNGS modeling to determine areas to perform this work. b) Covered conductor installation Please see response 5 (b). c) Undergrounding Please see response 5 (b). d) SDG&E Distribution Pole Replacement does not utilize the modeled Wildfire Risk Scores to plan pole replacement work within specific circuits or circuit segments. The program will have multiple risk categories and will be prioritized based on these categories. • Phase 1 (approximately 85 poles): Pole set in concrete and steel reinforced or pole set in concrete and not steel reinforced • Phase 2 (approximately 58 poles): Pole set in soil and steel reinforced • Phase 3 (approximately 1,379 poles): Pole set in soil and not steel reinforced e) SDG&E Grid Sectionalization program receives feedback from meteorology for PSPS opportunities based on new grid hardening projects such as Covered Conductor and Strategic Undergrounding in addition to stand-alone switch installations. SDG&E District Engineers also perform evaluations on the value of new switches by prioritizing customer impacts; they provide recommendations based on historical events and submit work order requests for new installations. f) Detailed inspections of distribution assets are mandated by GO 165, which determines the timeframe and cycle for performing inspections. Per GO 165, detailed inspections of overhead facilities are currently completed on a 5-year cycle for all overhead structures, including those in the HFTD, and is not expected to change in 2023. Although the modeled wildfire risk scores for each circuit are not explicitly used to determine where inspections are performed, non-routine, ad hoc inspections may be conducted for operational or reliability purposes and consider various factors such as location and risk. Additionally, SDG&E prioritizes detailed inspections in the HFTD prior to fire season. Detailed inspections are also supplemented by risk-informed drone inspections. g) SDG&E does not currently model wildfire risk scores for transmission tielines; therefore, modeled wildfire risk scores will not influence where detailed inspections of transmission assets in 2023 are performed. h) The structures selected for SDG&E’s 2023 aerial drone inspections are identified by using a semiautomated Inspection Prioritization Model that combines PoF and consequence of failure (CoF) to determine structure risk and account for navigation efficiency. The program considers the riskiest 15 percent of overhead distribution structures within the HFTD and WUI. The model aligns with existing methods considering MAVF to identify and quantify risk and is easily modified to account for new attributes or changes in scope. i) SDG&E does not currently model wildfire risk scores for transmission tielines; therefore, modeled wildfire risk scores will not influence where aerial inspections of transmission assets in 2023 are performed. j) Because the entire HFTD was captured in 2022, a large-scale LiDAR collection initiative will not be implemented again for several years. However, LiDAR will continue to be captured to support pole loading calculations as needed for system hardening projects such as covered conductor and traditional overhead hardening, which are scoped in part utilizing modeled wildfire risk scores. LiDAR is needed to complete PLS-CADD during pre-construction and post-construction to verify compliance with GO95 and SDG&E standards and specifications. k) SDG&E will not perform LiDAR inspections of transmission assets in 2023. | Aaron Louie | 2023-02-07 | 2023-03-07 | 2023-03-07 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-03.pdf | 0 | No | 2023 WMP | Wildfire Risk Score | N/A | N/A
15 | CalPA | 2023-03 | CalPA-2023-03 | 8 | CalPA-2023-03.8 | For each WMP initiative listed below, please state how the modeled Wildfire Risk Scores for each circuit or circuit-segment influence how work in 2023 will be sequenced. a) EVM b) Covered conductor installation c) Undergrounding d) Distribution pole replacement e) Grid sectionalization f) Detailed inspections of distribution assets g) Detailed inspections of transmission assets h) Aerial inspections of distribution assets i) Aerial inspections of transmission assets j) LiDAR inspections of distribution assets k) LiDAR inspections of transmission assets | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, and 7. SDG&E further objects to the request to the extent it misstates facts and/or assumes facts that do not exist. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) SDG&E Vegetation Management (VM) does not utilize the modeled Wildfire Risk Scores to plan EVM (greater trim clearances) work within specific circuits or circuit segments. VM performs EVM as part of its routine and off-cycle tree trim activities at the Vegetation Management Area (VMA) level throughout the HFTD. SDG&E follows a static, annual Master Schedule of VM activities for pre-inspection and tree trimming. Work may be prioritized as required if observed conditions warrant during the pre-inspection activity. b) Covered conductor installation Please see response 6 (b). c) Undergrounding Please see response 6 (b). d) For the Distribution Pole Replacement Program, Phase 1 poles would be addressed first, followed by Phase 2 then Phase 3. However, permitting, land rights, environmental mitigation, customer concerns, or a combination of these factors will drive the ultimate schedule on each pole's replacement. Where feasible, poles will be bundled together in a single work package to minimize the impact to the community and gain efficiency in the design, environmental, permitting, land rights, and construction process. In most cases a single work order package will bundle poles that are adjacent or within a few spans of each other and will require similar land rights, permitting, and/or land rights. e) SDG&E Grid Sectionalization program is sequenced based on input from multiple stakeholders who determine where the greatest customer impacts can be realized. When this evaluation is performed in association with work being performed associated with hardening initiatives such as Covered Conductor or Strategic Undergrounding it is sequenced according to that program. f) Detailed inspections of distribution assets are mandated by GO 165, which determines the timeframe and cycle for performing inspections. GO 165 also prescribes the acceptable interval, a 4month period within the calendar year, which dictates the sequencing of inspections throughout the year and is not expected to change in 2023. Although the modeled wildfire risk scores for each circuit are not explicitly used to determine the sequencing of inspections, SDG&E prioritizes detailed inspections in the HFTD prior to fire season and has shifted inspections into earlier intervals to address risk. Non-routine, ad hoc inspections may be conducted for operational or reliability purposes and consider various factors such as location and risk. Additionally, detailed inspections are also supplemented by risk-informed drone inspections. g) SDG&E does not currently model wildfire risk scores for transmission tielines; therefore, modeled wildfire risk scores will not influence how detailed inspections of transmission assets in 2023 are sequenced. h) In 2023, the aerial drone inspection program considers the riskiest 15 percent of overhead distribution structures within the HFTD and WUI as described in Response 7h. The sequencing of these inspections is determined by navigation efficiencies and obtaining necessary landowner authorizations. For example, inspections within Department of Defense areas require waiver approval by the board and permission by the base depending on the area within the based that flights are requested. In addition, we have specific authorization to perform inspections on State Parks lands and need to provide advance notification with U.S. Forest Service, Bureau of Land Management, Tribal Governments and other entities, such as water districts. i) SDG&E does not currently model wildfire risk scores for transmission tielines; therefore, modeled wildfire risk scores will not influence how aerial inspections of transmission assets in 2023 are sequenced. j) Because the entire HFTD was captured in 2022, a large-scale LiDAR collection initiative will not be implemented again for several years. However, LiDAR will continue to be captured to support pole loading calculations as needed for system hardening projects such as covered conductor and traditional overhead hardening, which are scoped in part utilizing modeled wildfire risk scores. LiDAR is needed to complete PLS-CADD during pre-construction and post-construction to verify compliance with GO95 and SDG&E standards and specifications. k) SDG&E will not perform LiDAR inspections of transmission assets in 2023. | Aaron Louie | 2023-02-07 | 2023-03-07 | 2023-03-07 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-03.pdf | 0 | No | 2023 WMP | Wildfire Risk Score | N/A | N/A
16 | CalPA | 2023-03 | CalPA-2023-03 | 9 | CalPA-2023-03.9 | For each WMP initiative listed below, please state how the modeled Wildfire Risk Scores for each circuit or circuit-segment influence where you plan to perform work in 2024. l) EVM m) Covered conductor installation n) Undergrounding o) Distribution pole replacement p) Grid sectionalization q) Detailed inspections of distribution assets r) Detailed inspections of transmission assets s) Aerial inspections of distribution assets t) Aerial inspections of transmission assets u) LiDAR inspections of distribution assets v) LiDAR inspections of transmission assets | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, and 7. SDG&E further objects to the request to the extent it misstates facts and/or assumes facts that do not exist. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) SDG&E Vegetation Management (VM) does not utilize the modeled Wildfire Risk Scores to plan EVM (greater trim clearances) work within specific circuits or circuit segments. VM performs EVM as part of its routine and off-cycle tree trim activities at the Vegetation Management Area (VMA) level throughout the HFTD. SDG&E follows a static, annual Master Schedule of VM activities for pre-inspection and tree trimming. Work may be prioritized as required if observed conditions warrant during the pre-inspection activity. While SDG&E’s EVM program does not scope work prioritizing circuit risk scores, it does focus on applying expanded post-trim clearances on targeted species identified as higher risk due to growth potential, failure characteristics, and relative outage frequency. The criteria for determining post‐trim clearances included multiple factors such as species, height, growth rate, health, location of defect, site conditions, pruning schedule, and proper pruning cuts. In 2024, SDG&E will continue to perform required clearing activities on subject poles located within the SRA as required by Public Resources Code Section 4292. The SRA does not align completely with the HFTD boundary, so as an extra precautionary measure, SDG&E will consider additional poles located outside SRA where Public Resources Code Section 4292 does not apply, including on poles located within the Local Responsibility Areas. Additionally in 2024, SDG&E will continue to perform vegetation fuels reduction activities surrounding poles located within the HFTD. For this activity, SDG&E does use the Circuit Risk Index and WiNGS modeling to determine areas to perform this work. b) Covered conductor installation Please see response 5 (b). c) Undergrounding Please see response 5 (b). d) SDG&E Distribution Pole Replacement does not utilize the modeled Wildfire Risk Scores to plan pole replacement work within specific circuits or circuit segments. The program will have multiple risk categories and will be prioritized based on these categories. • Phase 1 (approximately 85 poles): Pole set in concrete and steel reinforced or pole set in concrete and not steel reinforced • Phase 2 (approximately 58 poles): Pole set in soil and steel reinforced • Phase 3 (approximately 1,379 poles): Pole set in soil and not steel reinforced e) SDG&E Grid Sectionalization program receives feedback from meteorology for PSPS opportunities based on new grid hardening projects such as Covered Conductor and Strategic Undergrounding in addition to stand-alone switch installations. SDG&E District Engineers also perform evaluations on the value of new switches by prioritizing customer impacts; they provide recommendations based on historical events and submit work order requests for new installations. f) Detailed inspections of distribution assets are mandated by GO 165, which determines the timeframe and cycle for performing inspections. Per GO 165, detailed inspections of overhead facilities are currently completed on a 5-year cycle for all overhead structures, including those in the HFTD, and is not expected to change in 2024. Although the modeled wildfire risk scores for each circuit are not explicitly used to determine where inspections are performed, non-routine, ad hoc inspections may be conducted for operational or reliability purposes and consider various factors such as location and risk. Additionally, SDG&E prioritizes detailed inspections in the HFTD prior to fire season. Detailed inspections are also supplemented by risk-informed drone inspections. g) SDG&E does not currently model wildfire risk scores for transmission tielines; therefore, modeled wildfire risk scores will not influence where detailed inspections of transmission assets in 2024 are performed. h) The structures selected for SDG&E’s 2024 aerial drone inspections will be identified using a semiautomated Inspection Prioritization Model that combines PoF and consequence of failure (CoF) to determine structure risk and account for navigation efficiency. The program considers the riskiest 15 percent of overhead distribution structures within the HFTD and WUI. The model aligns with existing methods considering MAVF to identify and quantify risk and is easily modified to account for new attributes or changes in scope. i) SDG&E does not currently model wildfire risk scores for transmission tielines; therefore, modeled wildfire risk scores will not influence where aerial inspections of transmission assets in 2024 are performed. j) Because the entire HFTD was captured in 2022, a large-scale LiDAR collection initiative will not be implemented again for several years. However, LiDAR will continue to be captured to support pole loading calculations as needed for system hardening projects such as covered conductor and traditional overhead hardening, which are scoped in part utilizing modeled wildfire risk scores. LiDAR is needed to complete PLS-CADD during pre-construction and post-construction to verify compliance with GO95 and SDG&E standards and specifications. k) SDG&E will not perform LiDAR inspections of transmission assets in 2024. | Aaron Louie | 2023-02-07 | 2023-03-07 | 2023-03-07 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-03.pdf | 0 | No | 2024 WMP | Wildfire Risk Score | N/A | N/A
17 | CalPA | 2023-03 | CalPA-2023-03 | 10 | CalPA-2023-03.10 | For each WMP initiative listed below, please state how the modeled Wildfire Risk Scores for each circuit or circuit-segment influence how work in 2024 will be sequenced. a) EVM b) Covered conductor installation c) Undergrounding d) Distribution pole replacement e) Grid sectionalization f) Detailed inspections of distribution assets g) Detailed inspections of transmission assets h) Aerial inspections of distribution assets i) Aerial inspections of transmission assets j) LiDAR inspections of distribution assets k) LiDAR inspections of transmission assets | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, and 7. SDG&E further objects to the request to the extent it misstates facts and/or assumes facts that do not exist. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) SDG&E Vegetation Management (VM) does not utilize the modeled Wildfire Risk Scores to plan EVM (greater trim clearances) work within specific circuits or circuit segments. VM performs EVM as part of its routine and off-cycle tree trim activities at the Vegetation Management Area (VMA) level throughout the HFTD. SDG&E follows a static, annual Master Schedule of VM activities for pre-inspection and tree trimming. Work may be prioritized as required if observed conditions warrant during the pre-inspection activity. b) Covered conductor installation Please see response 6 (b). c) Undergrounding Please see response 6 (b). d) For the Distribution Pole Replacement Program, Phase 1 poles would be addressed first, followed by Phase 2 then Phase 3. However, permitting, land rights, environmental mitigation, customer concerns, or a combination of these factors will drive the ultimate schedule on each pole's replacement. Where feasible, poles will be bundled together in a single work package to minimize the impact to the community and gain efficiency in the design, environmental, permitting, land rights, and construction process. In most cases a single work order package will bundle poles that are adjacent or within a few spans of each other and will require similar land rights, permitting, and/or land rights. e) SDG&E Grid Sectionalization program is sequenced based on input from multiple stakeholders who determine where the greatest customer impacts can be realized. When this evaluation is performed in association with work being performed associated with hardening initiatives such as Covered Conductor or Strategic Undergrounding it is sequenced according to that program. f) Detailed inspections of distribution assets are mandated by GO 165, which determines the timeframe and cycle for performing inspections. GO 165 also prescribes the acceptable interval, a 4month period within the calendar year, which dictates the sequencing of inspections throughout the year and is not expected to change in 2024. Although the modeled wildfire risk scores for each circuit are not explicitly used to determine the sequencing of inspections, SDG&E prioritizes detailed inspections in the HFTD prior to fire season and has shifted inspections into earlier intervals to address risk. Non-routine, ad hoc inspections may be conducted for operational or reliability purposes and consider various factors such as location and risk. Additionally, detailed inspections are also supplemented by risk-informed drone inspections. g) SDG&E does not currently model wildfire risk scores for transmission tielines; therefore, modeled wildfire risk scores will not influence how detailed inspections of transmission assets in 2024 are sequenced. h) In 2024, the aerial drone inspection program will consider the riskiest 15 percent of overhead distribution structures within the HFTD and WUI as described in Response 9h. The sequencing of the work will be performed as described in response in 8h, the sequencing of these inspections will be determined by navigation efficiencies and obtaining necessary landowner authorizations. i) SDG&E does not currently model wildfire risk scores for transmission tielines; therefore, modeled wildfire risk scores will not influence how aerial inspections of transmission assets in 2023 are sequenced. j) Because the entire HFTD was captured in 2022, a large-scale LiDAR collection initiative will not be implemented again for several years. However, LiDAR will continue to be captured to support pole loading calculations as needed for system hardening projects such as covered conductor and traditional overhead hardening, which are scoped in part utilizing modeled wildfire risk scores. LiDAR is needed to complete PLS-CADD during pre-construction and post-construction to verify compliance with GO95 and SDG&E standards and specifications. k) SDG&E will not perform LiDAR inspections of transmission assets in 2024. | Aaron Louie | 2023-02-07 | 2023-03-07 | 2023-03-07 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-03.pdf | 0 | No | 2024 WMP | Wildfire Risk Score | N/A | N/A
18 | CalPA | 2023-04 | CalPA-2023-04 | 1 | CalPA-2023-04.1 | For any WMP initiative for which you forecast capital expenditures in 2023 to be at least two times actual capital expenditures in 2022, please provide: a) The name of the initiative as it is identified in your 2023-2025 WMP b) The WMP Initiative number in Table 11 of your 2023-2025 WMP c) The name of the initiative as it is identified in your 2022 WMP Update d) The WMP Initiative number in Table 12 of your 2022 WMP Update e) An explanation for the projected increase. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, and 7. Subject to and without waiving the foregoing objections, SDG&E responds as follows: 1. a. Emergency preparedness plan b. WMP.1008 c. Community outreach, public awareness, and communications efforts d. 7.3.9.2 e. The projected increase is related to construction of the Wildfire and Climate Resilience Center (WCRC). The construction costs are a one-time expense that are expected to be mostly spent in 2023. Information on the WCRC will be reported in SDG&E’s 2023 WMP in section 8.4.3.4. 2. a. Transmission OH Hardening – Distribution Underbuild b. WMP.545 c. Overhead transmission fire hardening (Distribution Underbuilt) d. 7.3.3.17.2.3 e. The expected construction in 2022 experienced permitting delays resulted in lower construction costs. SDG&E only completed 0.6 miles of hardening for this initiative in 2022 which drove the lower than expected spend in 2022. 3. a. Microgrids b. WMP.462 c. Microgrids d. 7.3.3.8.2 e. SDG&E experienced delays acquiring appropriate and sufficient land rights for the microgrid projects and has been delayed in deploying the permanent renewable solutions. This has shifted spend from 2022 into 2023 and 2024. | Aaron Louie | 2023-02-07 | 2023-03-07 | 2023-03-07 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-04.pdf | 0 | No | 2023 WMP | Capital Expenditure | N/A | N/A
19 | CalPA | 2023-04 | CalPA-2023-04 | 2 | CalPA-2023-04.2 | For any WMP initiative for which you forecast capital expenditures in 2024 to be at least two times actual capital expenditures in 2022, please provide: a) The name of the initiative as it is identified in your 2023-2025 WMP b) The WMP Initiative number in Table 11 of your 2023-2025 WMP c) The name of the initiative as it is identified in your 2022 WMP Update d) The WMP Initiative number in Table 12 of your 2022 WMP Update e) An explanation for the projected increase. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, and 7. Subject to and without waiving the foregoing objections, SDG&E responds as follows: 1. a. Strategic Undergrounding b. WMP.473 c. Undergrounding of electric lines and/or equipment d. 7.3.3.16 e. The number of miles completed for strategic undergrounding is increasing from 65 miles completed in 2022 to 125 miles planned for 2024. 2. a. Transmission OH Hardening – Distribution Underbuild b. WMP.545 c. Overhead transmission fire hardening (Distribution Underbuilt) d. 7.3.3.17.2.3 e. The expected construction in 2022 experienced permitting delays and resulted in lower construction costs. SDG&E only completed 0.6 miles of hardening for this initiative in 2022 which drove the lower than expected spend in 2022. 3. a. Microgrids b. WMP.462 c. Microgrids d. 7.3.3.8.2 e. SDG&E experienced delays acquiring appropriate and sufficient land rights for the microgrid projects and has been delayed in deploying the permanent renewable solutions. This has shifted spend from 2022 into 2023 and 2024. 4. a. Environmental monitoring systems (Advanced weather monitoring) b. WMP.447 c. Advanced weather monitoring and weather stations d. 7.3.2.1 e. SDG&E plans to continue improvements to the weather station network such as upgrading batteries, charging regulators, and enhancing weather sensor dashboards. | Aaron Louie | 2023-02-07 | 2023-03-07 | 2023-03-07 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-04.pdf | 0 | No | 2024 WMP | Capital Expenditure | N/A | N/A
20 | CalPA | 2023-04 | CalPA-2023-04 | 3 | CalPA-2023-04.3 | For any WMP initiative for which you forecast operating expenditures in 2023 to be at least two times actual operating expenditures in 2022, please provide: a) The name of the initiative as it is identified in your 2023-2025 WMP b) The WMP Initiative number in Table 11 of your 2023-2025 WMP c) The name of the initiative as it is identified in your 2022 WMP Update d) The WMP Initiative number in Table 12 of your 2022 WMP Update e) An explanation for the projected increase. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, and 7. Subject to and without waiving the foregoing objections, SDG&E responds as follows: 1. a. Strategic Undergrounding b. WMP.473 c. Undergrounding of electric lines and/or equipment d. 7.3.3.16 e. SDG&E had lower than expected operating expenditures (0.14% of capital expenditure) for undergrounding completed in 2022. SDG&E expects operating expenditures to increase to 0.2% of capital expenditures in 2023. 2. a. Early Fault Detection b. WMP.1195 c. N/A (was included within Installation of system automation equipment) d. N/A (was included within 7.3.3.9) e. Early Fault Detection is a relatively new program and only incurred operating expenses of one thousand dollars in 2022. As the program grows and more sensors are installed, and more data is ingested, the operating expenses will increase. 3. a. A summarized risk map that shows the overall ignition probability and estimated wildfire consequence along the electric lines and equipment b. WMP.442 c. A summarized risk map that shows the overall ignition probability and estimated wildfire consequence along the electric lines and equipment d. 7.3.1.1 e. The increased costs associated with this initiative are driven by higher expected labor costs in 2023 associated with additional full time employees that started halfway through 2022 and four additional employees with a planned start date in the second quarter of 2023. Non-labor costs also increase for this initiative as there are additional expenses for contractors associated with developing and validating SDG&E’s risk modeling. | Aaron Louie | 2023-02-07 | 2023-03-07 | 2023-03-07 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-04.pdf | 0 | No | 2023 WMP | Capital Expenditure | N/A | N/A
21 | CalPA | 2023-04 | CalPA-2023-04 | 4 | CalPA-2023-04.4 | For any WMP initiative for which you forecast operating expenditures in 2024 to be at least two times actual operating expenditures in 2022, please provide: a) The name of the initiative as it is identified in your 2023-2025 WMP b) The WMP Initiative number in Table 11 of your 2023-2025 WMP c) The name of the initiative as it is identified in your 2022 WMP Update d) The WMP Initiative number in Table 12 of your 2022 WMP Update e) An explanation for the projected increase. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, and 7. Subject to and without waiving the foregoing objections, SDG&E responds as follows: 1. a. Avian Protection b. WMP.972 c. Avian Mitigation d. 7.3.3.18.3 e. SDG&E had lower than expected operating expenditures (0.86% of capital expenditure) for the avian protection work completed in 2022. SDG&E expects operating expenditures to increase to 4% of capital expenditures in 2024. 2. a. Generator Grant Program b. WMP.466 c. Generator Grant Program d. 7.3.3.11.1 e. SDG&E had lower than expected expenditures associated with the Generator Grant Program in 2022 because SDG&E did not experience any PSPS events. The lack of PSPS activations drove participation in SDG&E’s resiliency programs down in 2022. Expenditures in 2024 are expected to return to normal levels of participation assuming PSPS activations return to average levels. 3. a. Generator Assistance Program b. WMP.467 c. Generator Assistance Program d. 7.3.3.11.3 e. SDG&E had lower than expected expenditures associated with the Generator Assistance Program in 2022 because SDG&E did not experience any PSPS events. The lack of PSPS activations drove participation in SDG&E’s resiliency programs down in 2022. Expenditures in 2024 are expected to return to normal levels of participation assuming PSPS activations return to average levels. 4. a. Strategic Undergrounding b. WMP.473 c. Undergrounding of electric lines and/or equipment d. 7.3.3.16 e. SDG&E had lower than expected operating expenditures (0.14% of capital expenditure) for undergrounding completed in 2022. SDG&E expects operating expenditures to increase to approximately 1% of capital expenditures in 2024. 5. a. Early Fault Detection b. WMP.1195 c. N/A (was included within Installation of system automation equipment) d. N/A (was included within 7.3.3.9) e. Early Fault Detection is a relatively new program and only incurred operating expenses of one thousand dollars in 2022. As the program grows and more sensors are installed, and more data is ingested, the operating expenses will increase. 6. a. Allocation methodology development and application b. WMP.523 c. Allocation methodology development and application d. 7.3.8.1 e. SDG&E had lower than expected operating expenditures for this initiative in 2022 due to lower than planned labor costs. SDG&E expects to hire additional FTEs in 2024 to assist with additional workload including wildfire mitigation personnel, risk management, and PSPS. | Aaron Louie | 2023-02-07 | 2023-03-07 | 2023-03-07 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-04.pdf | 0 | No | 2024 WMP | Capital Expenditure | N/A | N/A
22 | CalPA | 2023-05 | CalPA-2023-05 | 1 | CalPA-2023-05.1 | a) Have you identified transportation corridors within your service territory where falling or failing lines or poles could currently limit egress and/or ingress during an emergency? b) If the answer to part (a) is yes, please describe how you identify such transportation corridors. c) If available, please provide a geospatial data file that contains all current identified transportation corridors with ingress and egress hazards. | SDG&E objects to the request on the grounds set forth in General Objections, 2, 5, and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) Corridors in SDG&E’s service territory where asset failure could limit egress/ingress during an emergency have not been identified. SDG&E is prepared to support the needs of first responders through participation in the County Evacuation Committee, the staffing of 24/7 response staff to respond to incidents, and regular training with first responder agencies. During real world incidents requiring evacuation, SDG&E serves as a cooperator at the incident command post and follows the ICS command structure to ensure life safety is the highest priority. b) N/A c) N/A | Aaron Louie | 2023-02-10 | 2023-03-10 | 2023-03-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-05.pdf | 0 | No | Other | Egress | N/A | N/A
23 | CalPA | 2023-05 | CalPA-2023-05 | 2 | CalPA-2023-05.2 | In response to Data Request CalAdvocates-SDG&E-2022WMP-13 on March 30, 2022, SDG&E provided information regarding its Wildfire Risk Reduction Model (WRRM-Ops) and stated “Currently the Technosylva Wildfire Analyst Enterprise software does not incorporate suppression effectiveness into simulations. However, development of a suppression effectiveness model is currently underway and being tested for implementation during the California 2022 fire season.” a) What is the current status of the effort to develop a suppression effectiveness model described in the quote above? b) Has SDG&E updated its WRRM-Ops model since its response referenced above, to incorporate fire suppression effectiveness? c) If the answer it part (b) is yes, when did SDG&E start to incorporate the additional factor of fire suppression effectiveness into its wildfire risk simulations? | SDG&E objects to the request on the grounds set forth in General Objections, 2, 5, and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) Due to the number of variables that would go into accurate suppression modeling and that these variables would be significantly impacted by human and other factors it has been determined that incorporating suppression into operational models can create issues when applying model outputs to real world outcomes. WFA does model what is named their Initial Attack Index and is referenced in the CalAdvocates-SDG&E-2022WMP-13, from available inputs which may enable a SME to estimate the effectiveness of suppression. Factors that are considered by a SME include but are not limited to staffing levels, location relative to responding resources, other active incidents, and the accessibility of the incident. By excluding suppression, model outputs can more effectively be compared to each other because of consistent assumptions. It is also important to remember that the operational picture may change minute to minute and tactical actions taken in the field are typically based on real world observation. b) No, see answer a. c) NA | Aaron Louie | 2023-02-10 | 2023-03-10 | 2023-03-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-05.pdf | 0 | No | Other | CalAdvocates-SDG&E-2022WMP-13 | N/A | N/A
24 | CalPA | 2023-05 | CalPA-2023-05 | 3 | CalPA-2023-05.3 | Provide an Excel table of all distribution circuit-segments that traverse HFTD areas (i.e., the segment has greater than 0 circuit-miles in HFTD) existing as of January 1, 2023. The Excel table should list each such circuit-segment as a row and include the following information in separate columns. For items (n) and (r), please include all relevant risk scores. For example, include vegetation risk score, conductor risk score, and any other driver-specific risk scores you have developed. Please insert additional columns as needed to accommodate this: a) Circuit name for the circuit that each segment is part of b) Circuit ID for the circuit that each segment is part of c) Name or ID number of each circuit segment d) Nominal voltage e) Total circuit-miles on the circuit-segment f) Overhead circuit-miles on the circuit-segment in Non-HFTD Areas g) Overhead circuit-miles on the circuit-segment in HFTD Tier 2 h) Overhead circuit-miles on the circuit-segment in HFTD Tier 3 i) Underground circuit-miles on the circuit-segment in Non-HFTD Areas j) Underground circuit-miles on the circuit-segment in HFTD Tier 2 k) Underground circuit-miles on the circuit-segment in HFTD Tier 3 l) Probability of ignition score for the circuit-segment, according to the risk model you used for your 2022 WMP filing m) Consequence of ignition score for the circuit-segment, according to the risk model you used for your 2022 WMP filing n) Total wildfire risk score(s) for the circuit-segment, according to the risk model you used for your 2022 WMP filing. Insert additional columns if needed o) Power Safety Power Shutoff (PSPS) risk score for the circuit-segment, according to the risk model you used for your 2022 WMP filing p) Probability of ignition score for the circuit-segment, according to the risk model you are using for your 2023-2025 WMP filing q) Consequence of ignition score for the circuit-segment, according to the risk model you are using for your 2023-2025 WMP filing r) Total wildfire risk score(s) for the circuit-segment, according to the risk model you are using for your 2023-2025 WMP filing. Insert additional columns if needed s) Power Safety Power Shutoff (PSPS) risk score for the circuit-segment, according to the risk model you are using for your 2023-2025 WMP filing. | SDG&E objects to the request on the grounds set forth in General Objections, 2, 5, and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: Please see attachment named “dr_ca_5_q3_nb_output_RDF_2023_03_03.xlsx” Circuit/segment IDs are reflective of the current state of the system, segment configuration and mileage. Risk scores from the 2023-2025 WMP used WiNGS 3.0 model version and risk scores from the 2022 WMP correlate to WiNGS 1.0 model version. Each risk score field is suffixed with its corresponding model version for clarity. A column header with the requested attributes is provided above the SDG&E report’s column headers to help correlate the results to the original request. While the risk scores for both model versions have been provided, direct comparison of these risk scores cannot be done effectively due to changing risk in the territory, system configuration changes, and updates between versions. Each model version contains several enhancements to improve risk quantification which adjust the risk scores. The models should be viewed as independent of each other with separate temporal and logical constraints. | Aaron Louie | 2023-02-10 | 2023-03-10 | 2023-03-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-05.pdf https://www.sdge.com/sites/default/files/regulatory/dr_ca_5_q3_nb_output_RDF_2023_03_03_Q3.xlsx | 1 | No | Other | Circuits | N/A | N/A
25 | CalPA | 2023-05 | CalPA-2023-05 | 4 | CalPA-2023-05.4 | Provide a geodatabase file containing the outputs from your current wildfire risk model (i.e., the model you are using for your 2023-2025 WMP filing), at the circuit-segment level. (This data should be equivalent to the previous question, but in GIS format.) Please provide, as line features, the most recent spatial data for all circuit segments for which your current risk model calculates circuit segment-level expected risk (i.e., probability of ignition multiplied by the consequence of ignition). Include the following attributes for each circuit segment: a) Items (a) through (c) of the previous question b) Items (p) through (s) of the previous question. | SDG&E objects to the request on the grounds set forth in General Objections, 2, 5, and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: Please see “WMP_DR_CA_05_Q4.gdb.7z.” The attached zipped gdb file is encrypted according to SDG&E’s GIS electric data policy. The cypher for this gdb is WmPwMpWMPwmp1! This gdb contains records from question 3 joined to the segments in the wings_circuit_segment feature class. A single record in the table from question 3 will typically join to two records in the feature class because the feature class contains two records per segment, one for overhead and one for underground. | Aaron Louie | 2023-02-10 | 2023-03-10 | 2023-03-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-05.pdf https://www.sdge.com/sites/default/files/regulatory/WMP_DR_CA_05_Q4.gdb_.7z | 1 | No | 2023 WMP | Wilfire Risk Model | N/A | N/A
26 | CalPA | 2023-05 | CalPA-2023-05 | 5 | CalPA-2023-05.5 | Please fill out the attached spreadsheet, CalAdvocates-SDGE-2023WMP-05_Attachment, Tab 1, requesting information regarding your asset inspections in 2022. | Please see “CalAdvocates-SDGE-2023WMP-05_Q5.xlsx” | Aaron Louie | 2023-02-10 | 2023-03-10 | 2023-03-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-05.pdf https://www.sdge.com/sites/default/files/regulatory/CalAdvocates-SDGE-2023WMP-05_Q5.xlsx | 1 | No | Other | CalAdvocates-SDGE-2023WMP-05 | N/A | N/A
27 | CalPA | 2023-05 | CalPA-2023-05 | 6 | CalPA-2023-05.6 | Please augment Table 13 of the non-spatial data tables in your WMP Quarterly Data Report for Q4 of 2022, which reports asset-related corrective notifications on electric circuits that were open at the end of the quarter. Add the following information in separate columns: a) Name of the associated circuit b) ID number of the associated circuit c) Geographic latitude in decimal degrees, truncated to seven decimal places d) Geographic longitude in decimal degrees, truncated to seven decimal places e) Object/damage code or other internal SDG&E description of defect. | SDG&E objects to the request on the grounds set forth in General Objections, 2, 5, and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: Additional columns were added in the file “ Copy of Table 13 Q4 2022 QDR Submission_Q6.xlsx” and can be found in the orange columns “M-Q.” It should be noted that circuit information on structures that are not associated to a primary distribution circuit are shown as “N/A”. Where circuit name is “Stub Pole” the corresponding structure does not have an associated circuit. Additionally, the locations (latitude and longitude) of assets that are 230 kV or above are not included due to confidentiality. | Aaron Louie | 2023-02-10 | 2023-03-10 | 2023-03-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-05.pdf https://www.sdge.com/sites/default/files/regulatory/Copy%20of%20Table%2013%20Q4%202022%20QDR%20Submission_Q6.xlsx | 1 | No | Other | QDR | N/A | N/A
28 | CalPA | 2023-05 | CalPA-2023-05 | 7 | CalPA-2023-05.7 | Regarding Table 13 of the non-spatial data tables in your WMP Quarterly Data Report for Q4 of 2022: a) In column “f. Due date of the original work order,” there are four rows with a due date of “#”. Please explain what this means or correct those entries. b) In column “f. Due date of the original work order,” the majority of the rows list the due date as “N/A.” Please explain why these work orders have no due date. c) In column “g. GO 95 rule 18 priority level of the original work order,” the majority of the rows list the priority level as “N/A.” Please explain why these work orders have no priority level. d) Does SDG&E have an internal system of priority levels for corrective notifications that differs from the system of priority levels specified in GO 95 Rule 18? e) If the answer to part (d) is yes, please explain SDG&E’s internal priority system. f) Does SDG&E ever re-inspect corrective notifications before they are resolved? g) If the answer to part (f) is yes, under what circumstances does SDG&E conduct re-inspections? | SDG&E objects to the request on the grounds set forth in General Objections, 2, 5, and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) Three of the four entries were inadvertently included in Table 13. Work order numbers 101797, 126966, and 90774 are work orders assigned to third party communications infrastructure providers to perform corrective work and are not work orders for which SDG&E is responsible. The fourth work order, 129910, was also inadvertently included at the time of reporting due to timing of the business process. The order was in the process of being evaluated to assign a due date, and thus should not have been included in Table 13. Table 13 will be amended to exclude these four work orders and will be submitted to Energy Safety per revision guidelines. b) The 8,581 work orders with “N/A” as the due date of the original work order are work orders that resulted from drone inspections. Because drone inspections are supplemental inspections to routine detailed and patrol inspections mandated under GO 165 and part of our auditable corrective maintenance program, there is no mandatory due date associated. However, SDG&E evaluates drone inspection findings, generates corrective work orders, and prioritizes the work with the remaining backlog of corrective work. c) The 8,581 work orders with N/A as the GO 95 rule 18 priority level are work orders that resulted from drone inspections. Because drone inspections are supplemental inspections to routine detailed and patrol inspections mandated under GO 165 and part of our auditable corrective maintenance program, there is no associated GO 95 rule 18 priority level. However, SDG&E evaluates drone inspection findings, generates corrective work orders, and prioritizes the work with the remaining backlog of corrective work. d) Yes, SDG&E utilizes internal severity levels for distribution drone inspections. Work orders resulting from distribution drone inspections are prioritized based on severity using the following designations at the time of inspection: Emergency, Priority, and NonCritical. Emergency work orders are completed immediately (typically within 1-3 days) and Priority work orders are prioritized over Non-Critical work orders during both engineering/design and construction phases. e) Yes. f) Work orders resulting from routine inspections are subject to a deferral approval process with management personnel if warranted under reasonable circumstances. Each deferral request is reviewed, and various factors are considered prior to approval, such as the reason for the delay and any potential safety concerns including anticipated weather conditions and current condition of the underlying issue. As part of that review, the issue may be re-assessed for safety to ensure the priority level of the corrective work remains appropriately assigned since the issue was first identified. In addition, SDG&E performs pre-event patrols and may review the condition of facilities associated with open work orders prior to and after certain weather events. Again, this is dependent on the type of work order and whether that work order is associated with a condition (e.g. crossarm damage versus missing signage) that could pose a safety risk. | Aaron Louie | 2023-02-10 | 2023-03-10 | 2023-03-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-05.pdf | 0 | No | Other | QDR | N/A | N/A
29 | CalPA | 2023-06 | CalPA-2023-06 | 1 | CalPA-2023-06.1 | Provide your workplan that describes where you will undertake EVM projects in 2023. This workplan should be in an Excel format, with circuit-segments as rows. Please include the following information in separate columns in the Excel spreadsheet at a minimum: a) Circuit name b) Circuit ID number c) Circuit-segment name d) Circuit-segment ID number e) EVM miles to be completed in 2023 f) Risk ranking of the circuit-segment. | SDG&E does not annually forecast where specific EVM projects will occur. The pre-inspection and tree trim activities follow an annual master schedule based on the Vegetation Management Area (VMA). The exact locations where EVM tree trim clearances will be performed are unknown until after the pre-inspection activity occurs and the trimming is completed. The tree trimmer determines which trees will require greater clearances based on multiple criteria including species, growth rate, tree health, and proper pruning practices. | Aaron Louie | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-06.pdf | 0 | No | Other | EVM | N/A | N/A
30 | CalPA | 2023-06 | CalPA-2023-06 | 2 | CalPA-2023-06.2 | Provide your workplan that describes where you will undertake EVM projects in 2024. This workplan should be in an Excel format, with circuit-segments as rows. Please include the following information in separate columns in the Excel spreadsheet at a minimum:. a) Circuit name b) Circuit ID number c) Circuit-segment name d) Circuit-segment ID number e) EVM miles to be completed in 2024 f) Risk ranking of the circuit-segment. | Please see response to Question 1. | Aaron Louie | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-06.pdf | 0 | No | Other | EVM | N/A | N/A
31 | CalPA | 2023-06 | CalPA-2023-06 | 3 | CalPA-2023-06.3 | Please provide a list of any incidents in 2022 where the actions of a VM contractor posed a safety risk to workers and/or the public. “Safety risk” here is defined as any occurrence on a worksite where the contractor’s actions created a safety hazard for either workers or the general public. For each instance, please provide: a) The date you were informed of the safety issue b) The date that the original work that created the safety issue was performed c) Whether the safety issue concerned a transmission or distribution circuit d) The vegetation management initiative involved in the original work e) A brief description of the safety issue involved. | Please see attachment titled, “SDGEResponse_CalAdvocates_DR-06.xlsx” at the tab for response 3. | Aaron Louie | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-06.pdf https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-06%20Attachment%20Q3.xlsx | 1 | No | Other | Vegetation Management | N/A | N/A
32 | CalPA | 2023-06 | CalPA-2023-06 | 4 | CalPA-2023-06.4 | Provide your workplan that describes where and when you will perform system hardening on distribution circuits in 2023. For projects that you expect to partially complete in 2023 (i.e., projects that started before 2023 and are expected to continue in 2023, or projects that are expected to be completed after 2023), please include the project and report the work what you forecast will actually be performed in calendar year 2023. For each project, include the following information in separate columns, at a minimum: a) Order number b) Program c) Circuit ID number d) Circuit-segment name or ID number (if the project affects more than one circuit-segment, please identify each one) e) Relevant wildfire risk score(s) from the wildfire risk model that you are using to estimate distribution risk in your 2023-2025 WMP filing f) The expected or actual start date of the project g) The expected completion date of the project h) Length (in circuit miles) of covered conductor to be installed in 2023 i) Length (in circuit miles) of underground conductor to be installed in 2023 j) Length (in circuit miles) of overhead conductor to be permanently removed in 2023 and replaced by underground conductor (note that this may differ slightly from the previous item due to differing overhead and underground routes) k) Length (in circuit miles) of overhead conductor to be permanently removed in 2023 and not replaced with covered conductor or undergrounded) l) Length (in circuit miles) of any bare-wire overhead system hardening project to be installed in 2023 (if this is greater than zero, please describe the type of system hardening project) m) Length (in circuit miles) of any other type of system hardening project to be installed in 2023 (if this is greater than zero, please describe the type of system hardening project). | Please see attachment titled, “SDGEResponse_CalAdvocates_DR-06.xlsx” at the tab for response 4. 8 | Aaron Louie | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-06.pdf | 0 | No | Other | System hardening | N/A | N/A
33 | CalPA | 2023-06 | CalPA-2023-06 | 5 | CalPA-2023-06.5 | Provide your workplan that describes where and when you will perform system hardening on distribution circuits in 2024. For projects that you expect to partially complete in 2024 (i.e., projects that are expected to start before 2024 and are expected to continue in 2024, or projects that are expected to be completed after 2024), please include the project and report the work that you forecast will actually be performed in calendar year 2024. For each project, include the following information in separate columns, at a minimum: a) Order number b) Program c) Circuit ID number d) Circuit-segment name or ID number (if the project affects more than one circuit-segment, please identify each one) e) Relevant wildfire risk score(s) from the wildfire risk model that you are using to estimate distribution risk in your 2023-2025 WMP filing f) The expected or actual start date of the project g) The expected completion date of the project. h) Length (in circuit miles) of covered conductor to be installed in 2024 i) Length (in circuit miles) of underground conductor to be installed in 2024 j) Length (in circuit miles) of overhead conductor to be permanently removed in 2024 and replaced by underground conductor (note that this may differ slightly from the previous item due to differing overhead and underground routes) k) Length (in circuit miles) of overhead conductor to be permanently removed in 2024 and not replaced with covered conductor or undergrounded) l) Length (in circuit miles) of any bare-wire overhead system hardening project to be installed in 2024 (if this is greater than zero, please describe the type of system hardening project) m) Length (in circuit miles) of any other type of system hardening project to be installed in 2024 (if this is greater than zero, please describe the type of system hardening project). | Please see attachment titled, “SDGEResponse_CalAdvocates_DR-06.xlsx” at the tab for response 5. | Aaron Louie | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-06.pdf | 0 | No | Other | System hardening | N/A | N/A
34 | CalPA | 2023-06 | CalPA-2023-06 | 6 | CalPA-2023-06.6 | For each of your 2023-2025 WMP system hardening initiatives, please provide disaggregated information related to expenditures and circuit miles treated in the attached table, CalAdvocates- SDGE-2023WMP-06_Attachment, Tab 1. Add columns as needed. | Relocation of Overhead to Underground (refer to cost break-out for WMP.473 of Table 11 submitted to OEIS and Table 8-3 of 2023 WMP Filing ) – The combined expenditures for both Capital and Operating expense for the 2022-2024 timeframe are as follows: $126.9M for 2022 ($126.7M capital, $0.2M Opex), $196.6M for 2023 ($196.2M Capital, $0.4M Opex), and $295M for 2024 ($292M Capital, $3M Opex). These expenditures will support the completion of 65 miles in 2022, 84 miles in 2023, and 125 miles in 2024. Covered Conductor (refer to cost break-out for WMP.455 of Table 11 submitted to OEIS and Table 8-3 of 2023 WMP Filing) – The combined expenditures for both Capital and Operating expense for the 2022-2024 timeframe are as follows: $93M for 2022 ($90M capital, $3M Opex), $79M for 2023 ($76.8M Capital, $2.2M Opex), and $59.8M for 2024 ($59.2M Capital, $0.6M Opex). These expenditures will support the completion of 63 miles for the 2022 and 60 miles each for the 2023-2024 timeframe. Traditional Hardening (refer to cost break-out for WMP.475 of Table 11 submitted to OEIS and Table 8-3 of 2023 WMP Filing) – The combined expenditures for both Capital and Operating expense for the 2022-2024 timeframe are as follows: $26.5M for 2022 ($23.3M capital, $3.2M Opex), $3.8M for 2023 ($2M Capital, $1.8M Opex), and $0.9M for 2024 ($0.8M Capital, $0.1M Opex). These expenditures will support the completion of 27 miles in 2022, and 2 miles in 2023. Distribution Underbuild (refer to cost break-out for WMP.545 of Table 11 submitted to OEIS and Table 8-3 of 2023 WMP Filing) – This initiative is capital only. The total expenditures for the 2022-2024 timeframe are as follows: $3.2M for 2022, $11.4M for 2023, and $14.8M for 2024. These expenditures will support the completion of 0.6 miles in 2022, 7 miles in 2023, and 1 mile in 2024. | Aaron Louie | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-06.pdf | 0 | No | 2023 WMP | System hardening initiatives | N/A | N/A
35 | CalPA | 2023-06 | CalPA-2023-06 | 7 | CalPA-2023-06.7 | Please provide a spreadsheet listing (as rows) each undergrounding project completed during the period of January 1, 2022, through December 31, 2022. For each project, please provide the following information (as columns): a) Project ID number or other identifier b) Circuit ID c) ID of each circuit segment that was entirely undergrounded in the project d) ID of each circuit segment that was partially undergrounded in the project e) County or counties where undergrounding took place f) Project start date g) Project completion date h) Total circuit-miles undergrounded i) Total miles of trenching required j) Total life-cycle electric costs5 of the project (i.e., costs attributed to your electric facilities), including costs for planning, design, permitting, and construction k) Total life-cycle costs of the project, including costs attributed to non-electric utilities, including costs for planning, design, permitting, and construction l) Whether this was a Rule 20 project (yes/no) m) Whether this was a WMP project (yes/no) n) Whether this was a post-wildfire rebuild project (yes/no) o) Whether you shared trenches for this project with any telecommunications utilities (yes/no) p) Whether you shared trenches for this project with gas facilities (yes/no). | Please see attachment titled, “SDGEResponse_CalAdvocates_DR-06.xlsx” at the tab for response 7. | Aaron Louie | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-06.pdf https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-06%20Attachment%20Q7.zip | 1 | No | Other | Undergrounding | N/A | N/A
36 | CalPA | 2023-06 | CalPA-2023-06 | 8 | CalPA-2023-06.8 | Please provide a geodatabase file with a polyline feature for each undergrounding project completed during the period of January 1, 2022 through December 31, 2022. In addition to the spatial location, please provide the following attributes for each project: a) Project ID number or other identifier, matching part (a) of the previous question b) Circuit ID c) Project completion date. | Please see “CalPA_DR06_Question7.zip.” | Aaron Louie | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-06.pdf | 0 | No | Other | Geodatabase-Undergrounding | N/A | N/A
37 | CalPA | 2023-06 | CalPA-2023-06 | 9 | CalPA-2023-06.9 | Identify any ignitions in 2022 associated with assets where you had an existing corrective notification at the time of the ignition. Please provide a spreadsheet listing each such ignition (as rows) with the following information in separate columns: a) Unique ignition ID b) Date of ignition c) Cause of ignition d) Type of asset associated with the ignition e) Acres burned f) Number of structures burned, if any g) Number of injuries associated with ignition, if any h) Asset ID of asset associated with ignition i) Circuit ID number of circuit associated with ignition j) Notification number(s) for the existing maintenance tag on the asset in question. | SDG&E did not experience any ignitions in 2022 associated with assets with an existing corrective notification at the time of ignition. | Aaron Louie | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-06.pdf | 0 | No | Other | Ignitions | N/A | N/A
38 | CalPA | 2023-06 | CalPA-2023-06 | 10 | CalPA-2023-06.10 | Regarding your PSPS circuit modeling capabilities: a) Please describe your present circuit modeling capabilities with regard to PSPS decisionmaking (“PSPS circuit modeling capabilities”), including with what level of granularity they are able to determine how circuit hardening efforts or other changes to a line segment will affect PSPS thresholds. b) Please describe any improvements to the present PSPS circuit modeling capabilities that you expect to implement in 2023. c) Please describe any improvements to the present PSPS circuit modeling capabilities that you expect to implement in 2024. d) Please describe the expected state of your PSPS circuit modeling capabilities at the conclusion of the 2023-2025 WMP cycle. | a) For the WiNGS-Planning Model, the PSPS risk is calculated at the segment level and is influenced by the maximum upstream segment PSPS probability. Mitigations that occur upstream of segments will also influence the risk of PSPS on downstream segments. Thus, the PSPS impact on a segment cannot be viewed in isolation and must be considered in the context of the electric network (other segments on the same circuit with their respective mitigations). When a segment is fully undergrounded back to the substation, the model would consider the risk of PSPS to be removed. When a segment is mitigated with covered conductor, we consider the PSPS threshold to be reduced based on associated wind alert speed updates. For WiNGS-Ops, models are developed at the segment level and take as inputs the circuit characteristics at the time that the model is run, which can be as granular as daily. Therefore, circuit hardening or other changes to a line segment, once recorded in SDG&E’s analytical data warehouses, are immediately reflected in WiNGS-Ops model outputs, which influences the decision to de-energize. Segments that have been hardened will show a lower quantified risk score, thereby lowering PSPS thresholds. b) The following updates are expected in 2023 for WiNGS-Planning: The current PSPS likelihood assessment is relatively new and is expected to be revamped in the current WMP cycle. Future enhancements already identified will include how weather conditions and ignition risk affect the annual likelihood of implementing PSPS. Although in the WiNGS-Planning Model the PSPS consequence assessment considers type of customers, it can be improved with further development of social vulnerability or availability of redundant back-up power systems that could reduce the impacts of a PSPS. The following updates are expected in 2023 for WiNGS-Ops : • Create PSPS scenarios with different event durations. • Revisit Subject Matter Expert AFN customer scaling factors in the Safety component. • Revisit Safety assumption of fatalities per customer minutes de-energized. • Review and update existing Financial assumptions. • Review and update existing Reliability assumptions. c) The following updates are expected in 2024 for WiNGS-Planning: • SDG&E will develop a model to estimate PSPS duration for all customer segments. • SDGE& will develop an egress model to capture PSPS hazard and exposure potential • SDG&E will incorporate community vulnerability into its models • SDGE& will incorporate an economic impact measurement into its model to capture PSPS hazard and exposure potential The following updates are expected in 2024 for WiNGS-Ops: • Revisit Subject Matter Expert AFN customer scaling factors in the Safety component. • Revisit Safety assumption of fatalities per customer minutes de-energized. • Review and update existing Financial assumptions. • Review and update existing Reliability assumptions. If ICE 2.0 model results are available and considered appropriate, update PSPS model assumptions with ICE 2.0 model estimates d) SDG&E plans to explore and evaluate the addition of missing model factors based on the assessment of data and resource availability as well as incremental value added. In the 2023 to 2025 WMP cycle, factors will be integrated where data is available and resources will be engaged to incorporate those factors into the models. Factors to be evaluated include PSPS likelihood and wildfire and PSPS consequence. Factors such as social vulnerability and the potential impact of long-term-duration fires will be evaluated to see if PSPS likelihood, and PSPS consequence can be improved. SDG&E also plans to identify opportunities for additional factors and initiate data gathering in the current WMP cycle to work towards integrating those factors in future WMP cycles. This will be a continuous process of evaluating what can be integrated meaningfully and what may need to be considered in future years to enhance quality and quantity of data over time. Where possible, proxies may be leveraged, and assumptions will be tracked and documented to fulfill the requirements. | Aaron Louie | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-06.pdf | 0 | No | Other | PSPS | N/A | N/A
39 | GreenPower | 2023-01 | GreenPower-2023-01 | 1 | GreenPower-2023-01.1 | Please provide San Diego Gas and Electric’s Pre-submission 2023-2025 WMP Base Plan filed on February 13, 2023, with the OEIS per the 2023 WMP Guidelines and Schedule document. Including all attachments and associated supporting documents required for the Pre-submission 2023-2025 WMP Base Plan filing. | See attached “SDGE 2023-2025 WMP Pre-Submittal.pdf” | Gregg Morris | 2023-03-01 | 2023-03-06 | 2023-03-02 | https://www.sdge.com/sites/default/files/regulatory/GreenPower-2023-01.pdf | 1 | No | WMP Pre-Submissions | Administrative | N/A | N/A
40 | GreenPower | 2023-02 | GreenPower-2023-02 | 1 | GreenPower-2023-02.1 | Please confirm and report on the accuracy of Table 15 “Ignition Likelihood” (Column J), “Ignition Risk” (Column H), and “Overall Utility Risk” (Column G) values, in the 2022 Quarter 4 Data Report (QDR) filed on February 1, 2023. GPI has identified a potential calculation error in the 2022 Quarter 4 Data Report (QDR) filed on February 1, 2023. The “Ignition Likelihood” field in Table 15, Column J does not equal the sum of the “Equipment Likelihood of Ignition” (Column K), “Contact from Vegetation Likelihood of Ignition” (Column L), and “Contact from Object Likelihood of Ignition” (Column M. An example is provided in Table 1. This is contrary to SCE’s Table 15 calculation method where: • Ignition Likelihood (Column J) = SUM (Equipment Likelihood of Ignition (Column K), Contact from Vegetation Likelihood of Ignition (Column L), Contact from Object Likelihood of Ignition (Column M)) An error in the “Ignition Likelihood” variable will also affect the accuracy of the “Ignition Risk” (Column H) and “Overall Utility Risk (Column G)” calculations (Table 1): • Ignition Risk (Column H) = Ignition Likelihood (Column J) x Wildfire Consequence (Column P) • Overall Utility Risk (Column G) = Ignition Risk (Column H) + PSPS Risk (Column I) An error in Column J “Ignition Likelihood” can also alter circuit/segment risk ranking, the top 5% risk segment list, and resulting risk mitigation work locations. In your response, please provide the following: (1) The equation used to calculate “Ignition Likelihood” in the original Quarter 4 QDR filing submission (Table 15, Column J); (2) Any necessary corrections to the “Ignition Likelihood” metric calculation including the equation used and output; (3) Any corrections to the “Ignition Risk” and “Overall Utility Risk” metrics, including equations used and output; (4) An explanation of whether corrections from 1-3 alter the ranking of the top 5 % risk-ranked circuits/segment spans or the circuits/segments that are included in Table 15; (5) An updated 2022 QDR Excel workbook that includes any corrections necessary for Table 15; | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, and 9. SDG&E further notes that, pursuant to the 2023 Wildfire Mitigation Plan Guidelines, the three business day data request turnaround does not go into effect for stakeholders until the submission of SDG&E’s Final Wildfire Mitigation Plan on March 27, 2023. SDG&E reserves the right to continue processing data request responses within the normal, 10-day turnaround, prior to March 27 and again subsequent to a decision on SDG&E’s 2023 WMP submission. Subject to and without waiving the foregoing objections, SDG&E responds as follows: In response to the data request for QDR Table 15 filed on February 1, 2023, SDG&E confirms the accuracy of the table as-is and, likewise, the methodology and formulas used to calculate “Ignition Likelihood” (Column J), “Ignition Risk” (Column H), and “Overall Utility Risk” (Column G). In summary, the approach used to calculate “Ignition Likelihood” will not equal the sum of the “Equipment Likelihood of Ignition” (Column K), “Contact from Vegetation Likelihood of Ignition” (Column L), and “Contact from Object Likelihood of Ignition” (Column M) due to the disparate approaches for calculating columns L and M. Columns A, E, F, G, H, and P, are derived from the WiNGS Planning model, which has an embedded ignition adjustment process separate from the values presented in columns K, L, M, N. More specifically, “Contact from Vegetation Likelihood of Ignition” (Column L) , “Contact from Object Likelihood of Ignition” (Column M) and “Equipment Likelihood of Ignition” are separate modules containing calculations not directly tied to “Ignition Likelihood”. Subsequently, “Ignition Risk”, the “Overall Utility Risk”, and the top 5% of risk segments will not be affected. (1) The equation used to calculate “Ignition Likelihood” in the original Quarter 4 QDR filing submission (Table 15, Column J); The equation used to calculate “Ignition Likelihood” (Table 15, Column J) is derived from the WiNGS Planning Ignition Rate Normalization Factor model that leverages the Likelihood of Risk Event by segment (this will be included in SDG&E’s forthcoming 2023 WMP 2023, in section 6.2.2.1). Ignition Likelihood is calculated using an annual ignition rate for the HFTD. The annual ignition rate is adjusted to account for local conditions including wind speed, historical tree strikes, vegetation density, asset hardening, and asset health. The normalization factor model used to leverage the ignition likelihood metric used in Table 15 is as follows: Adj. Ignition Rate = Initial Ignition Rate × Ignition Adj. Factori × Normalization Factor-i. Where, Initial Ignition Rate is the initial ignition rate prior to implementation of adjustment factor i, Ignition Adj. Factori is the adjustment factor metric tied to the adjustment factor i, Normalization Factori is the normalization factor tied to adjustment factor i, Adj. Ignition Rate is the adjusted ignition rate after implementation of adjustment factor i and i is the specific adjustment factor (e.g., wind speed, tree strikes, etc.). The normalization part of the process implementation is performed to maintain the same global annual ignition rate after each adjustment step. Thereby, the ignition rate is adjusted relatively among each circuit-segment according to each individual risk factor, while the global ignition rate across the full scope of circuit-segments remains constant. (2) Any necessary corrections to the “Ignition Likelihood” metric calculation including the equation used and output; Due to the unassociated approaches for calculating “Ignition Risk” vs. “Contact from Vegetation Likelihood of Ignition” and “Contact from Object Likelihood of Ignition”, SDG&E does not report any corrections to the Ignition Likelihood metric, including the equation used and final output. (3) Any corrections to the “Ignition Risk” and “Overall Utility Risk” metrics, including equations used and output; SDG&E does not report any corrections necessary for the Ignition Risk and Overall Utility Risk metrics, including the equations used and final outputs. (4) An explanation of whether corrections from 1-3 alter the ranking of the top 5 % risk-ranked circuits/segment spans or the circuits/segments that are included in Table 15; (5) An updated 2022 QDR Excel workbook that includes any corrections necessary for Table 15; SDG&E does not report a change in the top 5% of risk-ranked circuit segments and will not currently submit an updated 2022 QDR Excel workbook for Table 15. | Gregg Morris | 2023-03-07 | 2023-03-10 | 2023-03-10 | https://www.sdge.com/sites/default/files/regulatory/GreenPower-2023-01.pdf | 0 | No | Other | Validation of Ignition Likelihood | N/A | N/A
41 | MGRA | 2023-021 | MGRA-2023-021 | 1 | MGRA-2023-021.1 | Please provide for Asset Point data for Camera, Fuse, Support Structure, and Weather Station. | SDG&E has provided a compiled database inclusive of all 2022 data provided to Energy Safety. Please see “SDGE_MGRA_OEIS_2022.gdb.zip” | Joseph Mitchell | 2023-03-29 | 2023-04-03 | 2023-04-03 | https://www.sdge.com/sites/default/files/regulatory/MGRA-2023-01.pdf | 0 | No | Other | Asset Data | N/A | N/A
42 | MGRA | 2023-021 | MGRA-2023-021 | 2 | MGRA-2023-021.2 | Provide Asset Line data for Transmission Line (as permitted as non-confidential), Primary Distribution Line, and Secondary Distribution Line. | Please see “SDGE_MGRA_OEIS_2022.gdb.zip” | Joseph Mitchell | 2023-03-29 | 2023-04-03 | 2023-04-03 | https://www.sdge.com/sites/default/files/regulatory/MGRA-2023-01.pdf | 0 | No | Other | Asset Data | N/A | N/A
43 | MGRA | 2023-021 | MGRA-2023-021 | 3 | MGRA-2023-021.3 | Provide PSPS Event data. Include Event Log, Event Line, Event Polygon data. Please exclude customer meter data. Provide all PSPS Event Asset Damage data including photos. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 1, 2, 5, 8 and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: SDG&E did not have any PSPS events in 2022. | Joseph Mitchell | 2023-03-29 | 2023-04-03 | 2023-04-03 | https://www.sdge.com/sites/default/files/regulatory/MGRA-2023-01.pdf | 0 | No | Other | PSPS | N/A | N/A
44 | MGRA | 2023-021 | MGRA-2023-021 | 4 | MGRA-2023-021.4 | Provide Risk Event Point data, including Wire Down, Ignition, Transmission unplanned outage (as classified non-confidential), Distribution Unplanned Outage data, Distribution Vegetation Caused Unplanned Outage, Risk Event Asset Log. | Please see “SDGE_MGRA_OEIS_2022.gdb.zip” | Joseph Mitchell | 2023-03-29 | 2023-04-03 | 2023-04-03 | https://www.sdge.com/sites/default/files/regulatory/MGRA-2023-01.pdf | 0 | No | Other | Risk Event Data | N/A | N/A
45 | MGRA | 2023-021 | MGRA-2023-021 | 5 | MGRA-2023-021.5 | Provide photo data for Risk Events. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 1, 2, 5, 8 and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: SDG&E does not currently have or provide photo data for risk events to Energy Safety. | Joseph Mitchell | 2023-03-29 | 2023-04-03 | 2023-04-03 | https://www.sdge.com/sites/default/files/regulatory/MGRA-2023-01.pdf | 0 | No | Other | Photo Data | N/A | N/A
46 | MGRA | 2023-021 | MGRA-2023-021 | 6 | MGRA-2023-021.6 | Under Initiatives, please provide Grid Hardening data, including Hardening Log, Hardening Point, and Hardening Line data. Inspection data is not requested at this time. | Please see “SDGE_MGRA_OEIS_2022.gdb.zip” | Joseph Mitchell | 2023-03-29 | 2023-04-03 | 2023-04-03 | https://www.sdge.com/sites/default/files/regulatory/MGRA-2023-01.pdf | 0 | No | Other | Grid Hardening data | N/A | N/A
47 | MGRA | 2023-021 | MGRA-2023-021 | 7 | MGRA-2023-021.7 | Under Initiatives, please provide Other Initiative data for point, line, polygon features and the Other Initiative Log. | Please see “SDGE_MGRA_OEIS_2022.gdb.zip” | Joseph Mitchell | 2023-03-29 | 2023-04-03 | 2023-04-03 | https://www.sdge.com/sites/default/files/regulatory/MGRA-2023-01.pdf | 0 | No | Other | Other Initiative data | N/A | N/A
48 | MGRA | 2023-021 | MGRA-2023-021 | 8 | MGRA-2023-021.8 | Under Other Required Data, please provide Red Flag Warning Day polygon data. | Please see “SDGE_MGRA_OEIS_2022.gdb.zip” | Joseph Mitchell | 2023-03-29 | 2023-04-03 | 2023-04-03 | https://www.sdge.com/sites/default/files/regulatory/MGRA-2023-01.pdf | 0 | No | Other | Red Flag Warning Day polygon data | N/A | N/A
49 | MGRA | 2023-021 | MGRA-2023-021 | 9 | MGRA-2023-021.9 | Please provide a layer indicating calculated circuit-level risk using the methodology presented in the WMP. a. If independent probability and consequence layers exist, please provide these independently as well. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, 8 and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: SDG&E does not currently have or provide circuit-level risk information in a geodatabase format to Energy Safety as it has not yet fully developed this capability for its quarterly submissions. SDG&E currently plans to include this data with the next QDR submission to Energy Safety. | Joseph Mitchell | 2023-03-29 | 2023-04-03 | 2023-04-03 | https://www.sdge.com/sites/default/files/regulatory/MGRA-2023-01.pdf | 0 | No | Other | Layers | N/A | N/A
50 | CalPA | 2023-07 | CalPA-2023-07 | 1 | CalPA-2023-07.1 | SDG&E’s 2022 WMP stated that a planned enhancement for Initiative 7.3.5.2 (“Detailed inspections and management practices for vegetation clearances around distribution electrical lines and equipment”) was to “Explore the use of the WiNGS-Planning risk model to evaluate the effectiveness of vegetation management operations risk models to support future prioritization and implementation of tree trimming.”4 There is no mention of this sort in SDG&E’s 2023 WMP submission. a) Did SDG&E conduct the above-mentioned exploration in 2022? b) If the answer to subpart (a) is “yes,” please provide SDG&E’s conclusions regarding the use of the WiNGs-Planning risk model for the abovementioned purpose. c) If the answer to subpart (a) is “no,” please explain why not. d) If the answer to subpart (a) is “no,” does SDG&E plan to conduct the abovementioned exploration? e) If the answer to subpart (d) is “yes,” please state when SDG&E intends to do so. | SDG&E objects to the request on the grounds set forth in General Objections 3 and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) Yes, SDGE evaluated the application of WiNGS-Planning risk model for the user case of prioritizing vegetation operational activities. b) The conclusion is that WiNGS Planning model alone is not the best approach for identifying the trees or vegetation management areas that need to be prioritized for routine or non-routine inspections or tree trims, nor is it the best approach for informing relative risk for trees at the asset or circuit section. The purpose of the WiNGS Planning model is to identify the best deployment of underground and covered conductor for long term risk strategy. The WiNGS-Planning model includes limited height, which is one of variables to the system during extreme weather conditions. To predict where tree risks and hazard conditions are more likely to occur, annual tree inspection and tree trimming records are the key data inputs to train the machine learning model. Vegetation management mitigates all observed hazardous conditions impacting the electrical system, and trees identified with an urgent condition are prioritized for the tree trimming or removal activities. Therefore, SDGE’s conclusion is that the independent model developed by Logic20/20 that incorporates attributes collected from operational activities is a superior approach to determine the prioritization and implementation of tree trimming. See response in Question 3 for additional details regarding this model. The first iteration of such an independent model was completed in 2022. c) N/A d) N/A e) N/A | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-07.pdf | 0 | No | 2022 WMP | Initiative 7.3.5.2 | N/A | N/A
51 | CalPA | 2023-07 | CalPA-2023-07 | 2 | CalPA-2023-07.2 | SDG&E’s 2022 WMP stated regarding initiative 7.3.5.16 (“Removal and remediation of trees with strike potential to electric lines and equipment”) (hereinafter “this initiative”), SDG&E plans to further evolve this program over the next 10 years by leveraging enhanced VRI and WiNGS-Planning modeling data to develop a more strategic approach to identify areas of high risk and prioritization of mitigation efforts. SDG&E will also utilize LiDAR to improve its assessment of hazard trees.5 a) Does the above statement still represent SDG&E’s plans for this initiative? b) If the answer to subpart (a) is “no,” please describe how SDG&E’s plans for this initiative have changed since February 2022. c) If the answer to subpart (a) is “yes,” please provide SDG&E’s progress to date on implementing the plans described in the quote above. | a) Yes. However, as mentioned in 1 b), SDG&E anticipates that the independent model that is designed to incorporate all tree related attributes and additional environmental attributes is a superior approach to assess trees with strike potential. Once such a model is established, vegetation management does not rule out use of the application of WiNGS Planning model when it needs to prioritize segments within the risk areas indicated by the independent model. The overall risk or a particular risk score from the WiNGS Planning model might be considered during this risk-based decision-making process. SDG&E is still assessing the overall modeling and prioritization strategy of its vegetation management operations. b) N/A c) SDG&E provides progress for the development of independent vegetation contact risk model below. • Vegetation Tree Contact Risk Model with the San Diego Supercomputing Center. This model development leverages tree attributes collected from operational vegetation management activities and meteorology data such as wind gust and soil moisture in an effort to predict future vegetation contact given predicted weather conditions. The developers are currently integrating overhead conductors into the model and analyzing the model performance. SDG&E anticipates a first iteration of this model sometime near the end of 2023. LiDAR data implementation to enhance operational and vegetation contact risk modeling. SDG&E processed LiDAR data for 10 HFTD circuits in 2022 as proof of concept. In 2023, SDG&E is evaluating the methods and efforts to process the remaining circuits in the HFTD so that LiDAR data can be integrated into risk modeling. The timeline is not determined yet. | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-07.pdf | 0 | No | 2022 WMP | Initiative 7.3.5.16 | N/A | N/A
52 | CalPA | 2023-07 | CalPA-2023-07 | 3 | CalPA-2023-07.3 | SDG&E states on p. 6 of its 2023 WMP, “The Company [SDG&E] engaged a third-party to review the off-cycle schedule to determine whether there were advantages to modify the schedule based on a risk comparison of the Vegetation Management Areas (VMAs).” a) Please describe the scope, schedule, and methodology of the abovementioned third-party review. b) Please identify who conducted the abovementioned third-party review. c) When was the abovementioned third-party review completed? d) Please provide the results of the abovementioned third-party review. e) Please provide any documents generated from the abovementioned third-party review (e.g. reports, workpapers, etc.). f) Has SDG&E incorporated any findings or recommendations from the abovementioned third-party review into the methodology of its off-cycle patrol scheduling? g) If the answer to subpart (f) is “yes,” please describe how SDG&E has done so. h) If the answer to subpart (f) is “no,” please explain why not. | a) Scope: The scope was to utilize historical vegetation management data (inspection and trimming inspection records) and produce a risk-based approach to better inform the timing of non-routine HFTD vegetation inspections. The analysis used historical vegetation activity data (inspections and trims) to generate influential variables that capture a tree’s characteristics, growth patterns, and past activity. The scores produced from the model were then used to aggregate the level of influential variables up to the VMAs or segments to generate a risk-based approach to scheduling. Schedule: Below is the timeline and schedule that was used to deliver the work: b) Logic 20/20 is a business and technology consulting firm headquartered in Seattle, Washington. c) The review was completed at the end of 2022. d) Please see attachment titled, “SDGE_WMP-07 Q.3”. e) Please see attachment titled, “SDGE_WMP-07 Q.3”. f) Yes. g) This was the first iteration of a predictive model to prioritize inspection schedules. SDG&E intends to incorporate some of the recommendations from this study beginning in 2023. SDG&E plans to conduct the off-cycle patrol activities in the higher risk-ranked VMAs closer to the start of peak fire season (September 1), and to schedule the remaining HFTD VMA patrols in the preceding months to create parity in the schedule and without conflicting with other Vegetation Management activities in those same months. h) N/A | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-07.pdf https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-07%20Attachment%20Q3.pdf | 1 | No | 1 | 1 EXECUTIVE SUMMARY Page 1 | 1.1.1.4 | 1.1.1.4 Vegetation Management and Inspections Page6
53 | CalPA | 2023-07 | CalPA-2023-07 | 4 | CalPA-2023-07.4 | SDG&E states on p. 252 of its 2023 WMP, “The fuels management activity6 is currently not included in this application [Epoch] at this time.” a) Why is the fuels management activity not included in the Epoch application? b) Could inclusion of fuels management activity in the Epoch application improve the activity’s efficacy? c) Does SDG&E intend to include fuels management activity in the Epoch application at a later date? d) If the answer to subpart (c) is “yes,” please specify when SDG&E intends to include fuels management activity in Epoch. e) If the answer to subpart (c) is “no,” please explain why not. | SDG&E objects to the request on the grounds set forth in General Objections 3 and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) The development of the PowerWorks work management system and Epoch preceded the inception of the fuels management program by several years and, therefore, was not originally designed to accommodate this activity. Doing so would require a substantial software upgrade to the work management system including the creation of new electronic work order types for this activity, the development of new electronic activity forms, development of new invoicing integrations, and additional system user credentialing of contractors not currently working in Epoch. b) The inclusion of the fuels management activity in the Epoch application alone would not necessarily improve the efficacy of this activity. It may help create efficiencies in this activity over time as the program grows, more pole structures are added to the population of work sites, and if/where repeated, annual work creates a maintenance cycle. c) SDG&E may explore the feasibility and potential benefits for future integration of this activity within Epoch, but has not yet decided if this is a necessary enhancement given the effort and potential cost. d) SDG&E does not have a date at this time when this activity may be included in Epoch. e) See c) and d) above. | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-07.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.1 | 8.2.1 Overview Page 254
54 | CalPA | 2023-07 | CalPA-2023-07 | 5 | CalPA-2023-07.5 | SDG&E states on p. 252 of its 2023 WMP, “In general, a 15 percent sample [of vegetation management activities] is selected to be performed after activities are completed.” a) Please state the basis for choosing a sampling rate of 15 percent for vegetation management activities, as opposed to a higher sampling rate. b) Provide any supporting documentation for the choice of a 15% sampling rate, in the context referenced above. | a) SDG&E uses a 15% random rate as the baseline for auditing its vegetation management activities because it considers this an acceptable and representative sample of the population of completed work to reflect contractor performance. Vegetation management audit results do not yield a high percentage of fail rates that may otherwise inform of the need for a higher sample percentage rate, therefore, a 15% sample was selected. Increasing audit sample size for all activities would also require an increase in the number of audit resources at additional rate-payer expense. b) Please see SDG&E’s 2023-2025 Wildfire Mitigation Plan (https://www.sdge.com/2023-wildfire-mitigation-plan) , Table 8-18 on page 312 for audit result findings. | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-07.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.1 | 8.2.1 Overview Page 254
55 | CalPA | 2023-07 | CalPA-2023-07 | 6 | CalPA-2023-07.6 | SDG&E states on p. 252 of its 2023 WMP, “Vegetation Management performs a QA/QC audit (WMP.505) on a percentage of all activities. In general, a 15 percent sample is selected to be performed after activities are completed.” a) Please describe the procedure for the QA/QC audit that is performed on a 15 percent sample of vegetation management activities, referenced above. b) Please explain how SDG&E determines whether a particular VM worksite/project passes or fails the QA/QC audit referenced above. c) Please describe what happens if a particular VM worksite/project fails the audit referenced above. d) Does SDG&E analyze the results of these QA/QC audits by contractor to evaluate or compare the performance of VM contractors? | a) SDG&E utilizes Scheduling Work Orders (SWO) generated in in the SDG&E work management tool called CityWorks server. The SWO is unique to the Vegetation Management Area (VMA), and all assets (trees or poles) within the work order. City Works uses a randomizer to generate the audit sample population. The SWO is assigned to the contractor for issuance to the field auditor(s). The field auditor receives the assigned work via a dispatch work order (DWO) on their Mobil Data terminal (MDT). Each asset to be audited has a work point that links to the electronic record. Each audit asset is evaluated in the field and updated in the system as a pass or fail. b) Within Epoch, each audit asset has tabs and drop-down selections to identify pass or fail, and with additional codes such as insufficient clearance, debris left on site, no trim performed, and or poor trimming to document reason for failure to meet SDG&E scope of work, state and regulatory compliance, and arboricultural and industry standards. c) Failed assets within the SWO are recorded and returned to the contractor for review and correction. Audit failures not disputed by the contractor are re-worked at no additional cost to SDG&E. d) Yes, SDG&E reviews the completed audit results internally and meets regularly with contractors to further review the audit result. The meetings cover trends, recognize positive performance, and discuss actionable items on identified areas for improvement. | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-07.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.1 | 8.2.1 Overview Page 254
56 | CalPA | 2023-07 | CalPA-2023-07 | 7 | CalPA-2023-07.7 | SDG&E states on p. 261 of its 2023 WMP that detailed vegetation inspections “are scheduled and performed using a system of geographic VMA. The service territory is comprised of 133 VMAs.” How does SDG&E decide the boundaries for its vegetation management areas? | The VMA boundaries are static and were delineated variably using city boundaries, SDG&E Districts, roads, and a relative parity in the dispersal of inventory tree units located within. The service territory is further delineated by jurisdictional and fire designation areas including the SRA, LRA, and HFTD. These areas determine which rules and regulations apply. Each VMA has a unique three-digit number. The first digit identifies the SDG&E District. The second digit identifies whether a VMA is located within the State Responsibility Area (SRA). If the second digit is 5 or higher, it is within the SRA. The third digit is the sequential numeric assignment of the VMAs when first created. | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-07.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.2.1 | 8.2.2.1 Detailed Vegetation Inspections Page 264
57 | CalPA | 2023-07 | CalPA-2023-07 | 8 | CalPA-2023-07.8 | SDG&E states on p. 264 of its 2023 WMP, “During the post-trim QA/QC audit activity, an audit contractor performs a cursory vegetation inspection of all overhead lines within each VMA.” a) Please explain how a cursory inspection is performed on “all overhead lines within each VMA” as referenced above, while only a 15% sample of work is audited. b) Please describe the procedure that audit contractors use to perform a “cursory vegetation inspection of all overhead lines” as referenced above. | a) The cursory inspection during the post-trim audit activity consists of a visual assessment of trees in proximity to the overhead lines to verify vegetation clearance will hold compliance for the remainder of the VMA annual cycle. Data is not collected for trees not being audited unless it is determined the tree requires work due to vegetation clearance or presents a hazardous condition to the overhead line. Trees that require work will first be evaluated to see if the work was assigned during the trim activity. If so, the tree is failed for the audit and returned to the tree contractor for corrective action. If the tree was not part of the original work assigned, the auditor would enter the information and submit a follow-on work order to prune the tree. The cursory inspection is performed simultaneously with the VMA 15% sample of work being audited. b) Please response to a). | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-07.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.2.1.2 | 8.2.2.1.2 Frequency or Triggers Page 267
58 | CalPA | 2023-07 | CalPA-2023-07 | 9 | CalPA-2023-07.9 | SDG&E states on p. 264 of its 2023 WMP that since its 2022 WMP submission it “Engaged with a third party to study the correlation between enhanced tree trim clearances and reduction of vegetation-caused outages.” a) Please describe the scope, goals, analytical methods, and duration of the abovementioned third party study. b) Please identify who conducted the abovementioned third-party study. c) Has the abovementioned third-party study been completed? d) If the answer to subpart (c) is “yes,” please provide the results of the study. e) If the answer to subpart (c) is “yes,” please provide any documents generated by the study (e.g. reports, workpapers, etc.) f) If the answer to subpart (c) is “no,” please state when SDG&E expects the study to be complete | a) Please see SDG&E’s 2023-2025 Wildfire Mitigation Plan "Areas for Continued Improvement and Required Progress of the IOUs’ 2022 WMP Update Progression of Effectiveness of Enhanced Clearances Joint Study”, beginning on page 930. The same is also addressed in Appendix D: Areas for Continued Improvement SDGE-22-20 “Progression of Effectiveness of Enhanced Clearances Joint Study”, on page 534. b) Third-party vendor, EPRI, was hired in 2022 to conduct the study. c) This multi-year study is not yet completed. d) N/A e) N/A f) This study is scheduled to be completed by the end of 2025. | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-07.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.2.1.3 | 8.2.2.1.3 Accomplishments, Roadblocks, and Updates Page 267
59 | CalPA | 2023-07 | CalPA-2023-07 | 10 | CalPA-2023-07.10 | SDG&E states on p. 264 of its 2023 WMP that since its 2022 WMP submission it “Continued engagement with the San Diego Supercomputing Center (SDSC) to study the relationship between expanded clearances and reduction in tree-related outages.” a) Is the abovementioned study the same study referred to in Question 9? b) If the answer to subpart is (a) is “no,” please explain how it differs from the study referred to in Question 9. c) If the answer to part (a) is “no,” please respond to parts (a) and (c) - (f) of the previous question (Question 9), but with respect to the SDSC study instead of the third-party study. | a) Yes. The reference cited above should have been the ongoing study being performed by EPRI with the joint IOU’s. b) N/A c) N/A | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-07.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.2.2.3 | 8.2.2.2.3 Accomplishments, Roadblocks, and Updates Page 270
60 | CalPA | 2023-07 | CalPA-2023-07 | 11 | CalPA-2023-07.11 | SDG&E states on p. 265 of its 2023 WMP that a change it may implement to its detailed vegetation inspections is to “Further integrate and operationalize land-based (vehicle and personnel) LiDAR, satellite imagery technology, and risk analyses into detailed inspection activities and decision-making.” a) How does SDG&E plan to integrate LiDAR into detailed inspection activities and decision-making? b) How does SDG&E plan to integrate satellite imagery technology into detailed inspection activities and decision-making? c) How does SDG&E plan to integrate risk analyses into detailed inspection activities and decision-making? d) How does SDG&E expect the above-mentioned integrations will improve its detailed inspections activities and decision-making? | SDG&E objects to the request on the grounds set forth in General Objections 3 and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) SDG&E processed LiDAR data for 10 HFTD circuits in 2022 as proof of concept. In 2023, SDG&E is evaluating the methods and efforts to process the remaining circuits in the HFTD so that LiDAR data can be integrated into risk modeling. This data will provide additional situational awareness to capture the holistic picture of the vegetation conditions to inform the detailed inspections in HFTD. b) SDG&E is exploring the use of satellite imagery to assess the power of satellite data to inform near-real time risk, planning, monitoring, and operations across the entire service territory with preliminary use cases in vegetation encroachment, tree-strike, and change detection (e.g., per-pole and per-span risk). This proof of concept will explore the potential for a one-stop-shop for multiple Enterprise use cases with state-of-the-art, cost-effective, feasible, and scalable satellite data and workflows. c) LiDAR and satellite imagery may improve SDG&E’s risk modeling capabilities with the inclusion of additional data related to clearance history, strike tree population, environmental conditions, topography, soil moisture, species diversity, etc. Information from these technologies may also assist in analyses and planning. For field inspection activities, SDG&E is exploring how information from these technologies may improve decision making. This may include the addition of risk-ranking information for the inspector within the electronic record that indicates relative risk at the specific tree asset level, and/or where the tree is located. Such information may be helpful in deciding whether a tree requires work, the scope of work, and the prioritization. d) See c) above. | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-07.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.2.1.3 | 8.2.2.1.3 Accomplishments, Roadblocks, and Updates Page 267
61 | CalPA | 2023-07 | CalPA-2023-07 | 12 | CalPA-2023-07.12 | SDG&E states on p. 265 of its 2023 WMP that a change it may implement to its detailed vegetation inspections is to “Further integrate VRI into inspection activities for the HFTD.” a) How does SDG&E intend to further integrate VRI into inspection activities for the HFTD? b) How does SDG&E anticipate further integrating VRI into inspection activities for the HFTD will improve its inspection activities going forward? | SDG&E objects to the request on the grounds set forth in General Objections 3 and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) As mentioned in Question 1, Logic20/20’s independent model is designed to support inspection activities. The Vegetation Risk Index (VRI) is a situational awareness tool, not a risk model, that categorizes circuits and transmission lines based on tree species, tree height, tree count, and historical vegetation-related outages. With the VRI now available within the mobile application (Epoch), Vegetation Management field users will continue to use VRI as an additional tool in conjunction with the data outputs from Logic20/20’s model to inform where risk levels are relatively higher, and where additional VM work may be prudent. b) SDG&E is working with San Diego Super Computing Center to develop the predictive that incorporates wind conditions to better refine the risk score that can inform vegetation field inspections in HFTD. | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-07.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.2.1.3 | 8.2.2.1.3 Accomplishments, Roadblocks, and Updates Page 267
62 | CalPA | 2023-07 | CalPA-2023-07 | 13 | CalPA-2023-07.13 | SDG&E states on p. 265 of its 2023 WMP that a change it may implement to its detailed vegetation inspections is to “Further engage third party study on risk modeling at the tree asset and span level” (sic). a) Please describe the scope, goals, analytical methods, and duration of the abovementioned study. b) What are the anticipated outputs of the abovementioned study? c) How does SDG&E anticipate utilizing the outputs of the abovementioned study in its vegetation risk modeling or VM work prioritization? | SDG&E objects to the request on the grounds set forth in General Objections 3 and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) Scope: One potential application of the model outlined in Question 3 is to support the detailed inspection activities by displaying the key features trained in the model in Epoch. Goals: Such data variables would serve as a situational awareness tool to help inspectors to make informed decisions on the follow-up work. Analytical method: The model is trained using logistical regression methods. Features that are informational to inspection activities are identified by vegetation management. They will be aggregated at VMA or segment level. The final method is currently under evaluation. The duration of this implementation is planned to be by the end of the 2023-2025 WMP cycle. b) Anticipated outputs of this model application include the display of frequency of hazard trees, memos, and outages, as well as wind gusts and other environmental data points in Epoch. c) As mentioned in a), these data points generated from the predictive model could potentially be used to inform the prioritization of the hazard and memo trees during routine inspections. | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-07.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.2.1.3 | 8.2.2.1.3 Accomplishments, Roadblocks, and Updates Page 267
63 | CalPA | 2023-07 | CalPA-2023-07 | 14 | CalPA-2023-07.14 | SDG&E states on p. 266 of its 2023 WMP regarding its off-cycle inspection activities, The VMA ranking provides input for generating the off-cycle HFTD schedule, which evenly distributes labor across the first 8 months of the year, provides time between the detailed and off-cycle inspections, and places the riskiest areas to be inspected closest to fire season. a) How does VMA ranking generate or influence SDG&E’s off-cycle HFTD inspection schedule? b) What inputs other than VMA ranking, to the off-cycle HFTD inspection schedule exist? | SDG&E objects to the request on the grounds set forth in General Objections 3 and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) Using historic, aggregated tree asset level data to rank HFTD VMAs may assist with informed-decision making when scheduling the order of off-cycle inspections activities in advance of peak fire season. For example, tree conflict avoidance may best be achieved by performing the off-cycle inspection activity of the highest-ranked VMAs in the fall-summer timeframe so these circuits can be trimmed in advance of September, generally considered the beginning of peak Santa Ana and wildfire risk season in SDG&E’s service territory. b) Additional inputs to the off-cycle HFTD inspection schedule include the relative time period between the routine schedule of the other vegetation management activities, contractor resource allocation, and the ability to combine off-cycle patrols with other concurrent VM activities. | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-07.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.2.2.2 | 8.2.2.2.2 Frequency or Triggers Page 269
64 | CalPA | 2023-08 | CalPA-2023-08 | 1 | CalPA-2023-08.1 | SDG&E states on p. 268 of its 2023 WMP that a change to its off-cycle inspection activity within the next five years is to “Continue to research and modify off-cycle HFTD schedule were necessary to optimize risk reduction” (sic). a) What are SDG&E’s research needs in regards to the above? b) How does SDG&E intend to conduct the abovementioned research? c) What data sources or experiments does SDG&E intend to use to support the abovementioned research? d) What modifications does SDG&E anticipate making to the off-cycle HFTD schedule? Please describe any such changes. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 3, 5 and 9. Further, the request calls for speculation. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) The original off-cycle inspection schedule was based on the annual, pre-inspection schedule activity to allow a period of time to elapse between the activities. This off-cycle inspection was scheduled as a mid-cycle activity. The mid-cycle activity was a second annual inspection that occurred 6-months after the routine scheduled activity. To explore the use of a risk-informed approach to prioritize the VMAs within the HFTD, SDG&E partnered with Logic20/20 to develop a predictive model and explore potential model applicaitons. The first iteration of the model was completed by the end of 2022. This first iteration only includes data variables collected during vegetation management operational activities, such as tree trimming frequency and clearance. SDG&E will continue to explore the benefit of adding additional variables to the model to improve the performance and provide applicable data points. b) SDG&E partners with a third-party company, Logic20/20, who has been developing a machine learning approach to model and predict risk over time, while also assisting in model enhancement research and documentation development.c) SDG&E intends to leverage and test both internal and external data sources to (1) enhance the prediction capabilities of the model and (2) assist with operational decision making in the field. Internal data sources to be tested include vegetation activity records. External data sources to be assessed include the Weather and Research Forecasting (WRF) model. In addition to new weather variables, SDG&E is also exploring satellite imagery and other publicly available data sources to identify vegetation and terrain features. This includes assessing digital elevation models (DEMs) derived from the Shuttle Radar Topography Mission (SRTM) to produce topographic variables such as elevation, slope degree, and slope aspect. d) SDG&E has begun adopting the new eight-month off-cycle activity schedule resulting from the initial model developed by Logic 20/20 and will continue to refine where modifications may be warranted. | Aaron Louie | 2023-04-05 | 2023-04-13 | 2023-04-13 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-08.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.2.2.3 | 8.2.2.2.3 Accomplishments, Roadblocks, and Updates Page 270
65 | CalPA | 2023-08 | CalPA-2023-08 | 2 | CalPA-2023-08.2 | SDG&E states on p. 268 of its 2023 WMP that a change to its off-cycle inspection activity within the next five years is to “Identify proper resource need and allocation to perform the off-cycle HFTD inspection timely and efficiently.” a) Why has SDG&E not already accomplished the abovementioned identification of proper resource need and allocation, given that the off-cycle HFTD inspection program is already in place? b) Please identify SDG&Es current progress to date on identifying the proper resource need and allocation to perform the off-cycle HFTD inspection timely and efficiently. c) Please identify what SDG&E needs to do in order to identify the abovementioned resource need and allocation. d) Please provide the number of SDG&E’s off-cycle HFTD inspections that were completed on time in 2022 and the total number of off-cycle HFTD inspections. e) Were SDG&E’s off-cycle HFTD inspections completed timely in 2022? | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 3, 5 and 9. Further, the request mischaracterizes SDG&E’s statements in its WMP. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) The statement in Question 2a inaccurately characterizes DSG&E’s off-cycle inspection activity program. SDG&E was able to accomplish the resource needs based on the original mid-cycle pre-inspection VMA schedule. However, a compressed timeframe to complete the patrols in the entire HFTD before September 1 poses challenges. The new off-cycle patrol is an 8-month schedule based on the findings from the Logic2/020 model and will require resource allocation adjustments. b) The SDG&E WMP Lead Forester is responsible for creating the off-cycle VMA schedule and assigning the VMAs to the respective contractors and internal SDG&E Patrollers. The Lead Forester also works with the contractors to determine the required number of resources needed to complete the off-cycle patrols for each VMA each month. c) See b) above. d) All 105 (VMA) off-cycle HFTD inspection activities were completed on time in 2022. e) Yes. See Response to subpart d above. | Aaron Louie | 2023-04-05 | 2023-04-13 | 2023-04-13 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-08.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.2.2.3 | 8.2.2.2.3 Accomplishments, Roadblocks, and Updates Page 270
66 | CalPA | 2023-08 | CalPA-2023-08 | 3 | CalPA-2023-08.3 | SDG&E states on p. 268 of its 2023 WMP that a change to its off-cycle inspection activity within the next five years is to “Identify additional and proactive HFTD inspection activity opportunities such as pre-PSPS and adverse weather condition and event patrols.” a) Please describe how SDG&E intends to identify the abovementioned opportunities. b) What does a pre-PSPS inspection, referenced above, entail? c) What do “adverse weather condition and event patrols” referenced above entail? d) How will SDG&E assess the effectiveness of “additional and proactive HFTD inspection activity opportunities” referenced above? e) At what threshold of effectiveness would SDG&E propose the abovementioned opportunities as permanent programs or WMP initiatives? | a) In addition to off-cycle inspection activities, these opportunities will be identified as conditions occur via scheduled PSPS events, declared Red Flag Warnings from the National Weather Service, and Meteorology weather forecasts for advancing storms. b) A pre-PSPS inspection could entail a targeted field patrol of circuit segments scheduled to be de-energized in advance of the event to identify any hazardous tree conditions. c) Adverse weather conditions may include storms, Santa Ana Wind event, declared Red Flag Warning, and event patrols could entail a field assessment in targeted areas of the HFTD in advance of the event in order to prevent a tree/power line conflict. d) While the effectiveness may not be specifically quantifiable, it is presumed that these activities would mitigate observable risks. e) SDG&E anticipates that these additional activities will remain ad-hoc as conditions occur. | Aaron Louie | 2023-04-05 | 2023-04-13 | 2023-04-13 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-08.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.2.2.3 | 8.2.2.2.3 Accomplishments, Roadblocks, and Updates Page 270
67 | CalPA | 2023-08 | CalPA-2023-08 | 4 | CalPA-2023-08.4 | SDG&E states on p. 268 of its 2023 WMP that a change to its off-cycle inspection activity within the next five years is to “Further integrate and operationalize risk and condition-based data such as meteorology and environmental conditions into ground-level decision-making.”a) Please describe how SDG&E intends to accomplish the abovementioned integration and operationalization. b) How will the process described in your answer to subpart (a) improve ground-level decision-making regarding off-cycle inspections? | a) The partnership with Logic20/20 allows SDG&E to evaluate and operationalize the application of the predictive model. The model is trained using logistical regression methods. Features that are informational to inspection activities are identified by vegetation management. They will be aggregated at VMA or segment level. One of the applications identified in 2023 is to support the detailed inspection activities by displaying the key features trained in the model in Epoch. Such data variables would serve as a situational awareness tool to help inspectors to make informed decisions on the follow-up work. b) SDG&E plans to further test this first model and display selected variables for filed users in Epoch. These data variables include frequency of hazard trees, memos, and outages, as well as wind gusts and other environmental data points. These data points generated from the predictive model could be used to inform the prioritization of the hazard and memo trees during routine inspections where applicable. | Aaron Louie | 2023-04-05 | 2023-04-13 | 2023-04-13 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-08.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.2.2.3 | 8.2.2.2.3 Accomplishments, Roadblocks, and Updates Page 270
68 | CalPA | 2023-08 | CalPA-2023-08 | 5 | CalPA-2023-08.5 | SDG&E states on p. 269 of its 2023 WMP that “SDG&E sponsored a third-party study of its Fuels Treatment activities in 2022 to review the efficacy of the program and potential risk reduction.” a) What were the findings of the abovementioned study? b) Please identify who performed the abovementioned study. c) How has SDG&E integrated the findings of the abovementioned study into its planned fuels treatment activities for 2023-2025? d) Please provide any documents that were generated from the abovementioned study (e.g. reports, workpapers, etc.). | a) Please see report provided in SDG&E’s 2023-2025 Wildfire Mitigate Plan titled “WMS Work Summary” beginning on page 942. b) The study was conducted by Insight Global. c) This was the first study for SDG&E to assess the methodology and efficacy of the fuels management program of using 50 feet vegetation thinning radius as the basis of the activity. SDG&E has a small number of ignitions per year. Additionally, the accuracy of the ignition location prior to the initial WMP cycle does not support spatial analysis, resulting in limited data sample. Although this study does provide a statistical methodology for further analysis, as of now, SDG&E does not find any results that can be operationalized to its fuels treatment activities. d) Please see a) above. | Aaron Louie | 2023-04-05 | 2023-04-13 | 2023-04-13 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-08.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.3 | 8.2.3 Vegetation and Fuels Management Page 271
69 | CalPA | 2023-08 | CalPA-2023-08 | 6 | CalPA-2023-08.6 | SDG&E states on p. 269 of its 2023 WMP that an enhancement to its fuels treatment activity in 2023 will be to “Continue to assess cost/benefit and research alternatives such as fire retardants.” a) How does SDG&E intend to accomplish the abovementioned assessment and research? b) Please describe SDG&E’s progress to date regarding assessing cost/benefit of its fuels treatment program. c) Please describe SDG&E’s progress to date on the abovementioned research of alternatives | a) SDG&E has a current plan to perform an assessment of the unit cost of mechanical thinning compared with alternate options such as fire retardant and goat grazing. It further plans to include a comparison of the unit cost per in the preliminary planning phase to collaborate/fund a fire retardant project with San Diego County Fire in 2023. SDG&E is also planning to explore additional use of goat grazing as supplemental activity for fuels management. b) SDG&E plans to assess the alternate option of goat grazing by end of the second quarter of 2023, and the alternate option of fire retardant by end of quarter 3. Once data points are available, a cost/benefit assessment will be conducted. c) This research will be considered in the future. | Aaron Louie | 2023-04-05 | 2023-04-13 | 2023-04-13 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-08.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.3 | 8.2.3 Vegetation and Fuels Management Page 271
70 | CalPA | 2023-08 | CalPA-2023-08 | 7 | CalPA-2023-08.7 | SDG&E states on p. 269 of its 2023 WMP that an enhancement to its fuels treatment activity in 2023 will be to “Engage third party to study the methodology and effectiveness of the fuels treatment activity.” a) Will the abovementioned third party study be a continuation of the third party study referred to in Question 5, or a new study? b) If your answer to subpart (a) is “a new study,” please identify how the scope of work of the new study will be different from the previous study referenced in Question 5, and how it will add to the findings from the previous study. c) If your answer to subpart (a) is “a continuation of the third party study referred to in Question 5,” please identify how SDG&E’s continuation of that study will add to its findings and improve SDG&E’s fuels treatment program. | a) The initial study on the effectiveness is referred to in Question 5. SDG&E is looking into new approaches to further conduct the study in 2023. b) N/A c) This new approach may consider leveraging satellite imagery data for effectiveness research purpose, as well as efficiency in identifying the target poles for fuel treatment. | Aaron Louie | 2023-04-05 | 2023-04-13 | 2023-04-13 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-08.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.3 | 8.2.3 Vegetation and Fuels Management Page 271
71 | CalPA | 2023-08 | CalPA-2023-08 | 8 | CalPA-2023-08.8 | SDG&E states on p. 280 of its 2023 WMP that a change to its Vegetation Management Enterprise System since its last WMP is to add “New mapping capabilities to electronically track and document inspection progression” a) Please list and describe the abovementioned new mapping capabilities. b) How are the abovementioned new mapping capabilities currently improving SDG&E’s inspection programs? c) Does SDG&E intend to add mapping capabilities beyond what it has already? d) If your answer to subpart (c) is “yes,” please list and describe the planned future enhancements. | a) SDG&E developed and implemented a new work order progression tool in both the server side and field application of the PowerWorkz work management system. b) This new tool allows the desktop and field user the capability to visualize the progression of the inspection activity via map interface. This will increase efficiency and work production. c) Yes. d) SDG&E anticipates adding this same work progression tool as needed for other vegetation management activities. | Aaron Louie | 2023-04-05 | 2023-04-13 | 2023-04-13 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-08.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.4.6 | 8.2.4.6 Changes Since the Last WMP Submission Page 282
72 | CalPA | 2023-08 | CalPA-2023-08 | 9 | CalPA-2023-08.9 | SDG&E states on p. 280 of its 2023 WMP that a change to its Vegetation Management Enterprise System since its last WMP is to add “New data fields to electronically record customer refusals and other deferred work which negates the need for hard copy forms” and the “creation of a refusal/deferred work dashboard to track and manage time-sensitive tree work.” a) Please list and describe the abovementioned new data fields. b) How are the abovementioned new data fields improving SDG&E’s ability to respond to customer refusals and complete deferred work? | a) The new electronic data fields include category, reason for refusal/exception, type of contact, contractor, and comments. These new data fields are in addition to all the other information captured within the tree record, and provide a synopsis of the deferred work including why a customer is refusing trimming, why a tree cannot be trimmed on the routine cycle, the method of communication with the customer, date of the communication, and the ability to free-hand additional comments related to the location. b) This new electronic data capture helps streamline the deferred work process by eliminating the need for hard-copy documentation and filing, provides standardization and consistency of information, and facilitates reporting and follow-up efforts. | Aaron Louie | 2023-04-05 | 2023-04-13 | 2023-04-13 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-08.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.4.6 | 8.2.4.6 Changes Since the Last WMP Submission Page 282
73 | CalPA | 2023-08 | CalPA-2023-08 | 10 | CalPA-2023-08.10 | SDG&E states on p. 281 of its 2023 WMP regarding its QA/QC, “A higher sampling percentage is used for some enhanced vegetation management activities in the HFTD, including a 100 percent post-trim audit of all completed trim and removal work generated from the off-cycle HFTD inspection activities.” a) Is the abovementioned 100% post-trim audit conducted for all trim and removal activities in the HFTD, or just those that result from an off-cycle inspection? b) If the answer to subpart (a) is the latter, please explain why SDG&E does not audit 100% of all trim and removal work in the HFTD. | a) The 100% post-trim audit is limited to all trim and removal activities that result from the off-cycle (mid-cycle) HFTD inspection activities. b) The number of trees generated from the off-cycle HFTD inspection activity is relatively low. Therefore, a 100% audit of all trees is feasible and manageable without impacting audit resources or the activity schedule. Auditing all trim and removal activities in the HFTD would include tens of thousands of trees, necessitating significant additional workload and associated costs. SDG&E uses a 15% random rate as the baseline for auditing all other vegetation management activities because it believes this is an acceptable and representative sample of the population of completed work to reflect contractor performance. Vegetation management audit results do not yield a high percentage of fail rates that may otherwise inform of the need for a higher sample percentage rate, therefore, a 15% sample is used. Increasing audit sample size for all activities could require an increase in the number of audit resources at additional rate-payer expense and with limited incremental value and justification. | Aaron Louie | 2023-04-05 | 2023-04-13 | 2023-04-13 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-08.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.5.2 | 8.2.5.2 Sample Size Page 283
74 | CalPA | 2023-08 | CalPA-2023-08 | 11 | CalPA-2023-08.11 | SDG&E states on p. 282 of its 2023 WMP: A 100-percent audit of all completed tree trimming and removal work generated during the off-cycle, HFTD patrol activity was performed where feasible. SDG&E is considering the development of compliance-based audits as a measure of system status and reliability. Such audits may be performed across multiple VMAs and create benchmarking for the performance of vegetation management operations. a) Please identify where the abovementioned 100 percent audit has not been feasible. b) How has SDG&E overcome, or how does SDG&E plan to overcome (as applicable), roadblocks to attaining the 100 percent audit of all completed tree trimming and removal work generated during the off-cycle HFTD patrol activity? c) Please describe the scope, goals, methodology, and benchmarks of the abovementioned compliance-based audits. d) What statute(s) or General Order(s) would SDG&E’s compliance-based audits referenced above be complying with? e) How will SDG&E determine which VMAs to conduct the abovementioned compliance-based audits in? f) Please describe the benchmarking SDG&E intends to develop and perform for vegetation management operations performance. | a) Audits are performed by Vegetation Management Area (VMA). Instances where a 100% audit has not been feasible in an individual VMA include where there is an inability to physically reach a tree due to an access constraint, or an ongoing customer refusal. b) Instances of a less than 100% audit are infrequent and do not result in a significant impact to the overall results of an audit. SDG&E does have a process to track and follow-up with audit trees that are customer refusals. c) As stated in the quoted language above, SD&GE is considering this approach and has not yet begun the development of a compliance-based audit and the specific methodology. d) General Order 95, Rule 35, Public Resources Code 4292, and Public Resources Code 4293 e) SD&GE has not yet begun the development of a compliance-based audit and the specific methodology. One option may be a randomized sample of VMAs located within a specific SDG&E Operations & Maintenance District. f) See c) above. | Aaron Louie | 2023-04-05 | 2023-04-13 | 2023-04-13 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-08.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.5.6 | 8.2.5.6 Process Changes Since the Last WMP Submission Page 284
75 | CalPA | 2023-08 | CalPA-2023-08 | 12 | CalPA-2023-08.12 | SDG&E states on p. 252 of its 2023 WMP, “Contractors are required to provide the necessary training to their workforce on the technical capabilities to perform the work.” a) Please identify what necessary training is required for contractors to perform SDG&E’s vegetation management work. b) Does SDG&E inform VM contractors what training is necessary to perform SDG&E’s VM work? c) Does SDG&E review the training or certifications that its contractors provide to their workforces? d) Does SDG&E verify that contractors’ workforces are properly trained to perform SDG&E’s vegetation management work? e) Please describe SDG&E’s process, if any, that is currently in place to review contractor workforce qualifications and/or ability to perform SDG&E’s VM work? | a) For tree trimming, the necessary training includes electrical and safety awareness, proper use of equipment, and proper pruning practices. For pre-inspection the necessary training includes electrical and safety awareness, species identification and growth characteristics, and hazard tree assessment. b) In addition to the abovementioned training, SDG&E requires the contractors to perform customer service, environmental, and fire preparedness training. c) Yes. d) Yes. e) Vegetation Management contractors are required to attain certain certifications for specific positions. SDG&E periodically reviews contractor adherence to these requirements on a periodic basis. VM contractors also provide annually the content and sign-in logs for each of the training modules SDG&E requires. | Aaron Louie | 2023-04-05 | 2023-04-13 | 2023-04-13 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-08.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.1 | 8.2.1 Overview Page 254
76 | CalPA | 2023-08 | CalPA-2023-08 | 13 | CalPA-2023-08.13 | SDG&E states on p. 266 of its 2023 WMP, “Any priority tree work identified during the off-cycle HFTD patrol is expedited as needed via the “Memo” process to mitigate the risk.” a) Please state how many “Memo” processes were initiated related to priority tree work identified in HFTD 2 areas during 2022. b) Please state how many “Memo” processes were initiated related to priority tree work identified in HFTD 3 areas during 2022. | a) 27 units were initiated in HFTD 2 during 2022 off-cycle inspections b) 60 units were initiated in HFTD 3 during 2022 off-cycle inspections | Aaron Louie | 2023-04-05 | 2023-04-13 | 2023-04-13 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-08.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.2.2.2 | 8.2.2.2.2 Frequency or Triggers Page 269
77 | CalPA | 2023-08 | CalPA-2023-08 | 14 | CalPA-2023-08.14 | SDG&E states on p. 266 of its 2023 WMP: In early 2022, a third-party vendor was engaged to conduct an efficacy study of the off-cycle HFTD patrol schedule to determine the optimum schedule based on historical tree risk within each HFTD VMA… The study also considered increasing the 3-month off-cycle HFTD schedule to an 8-month schedule (January to August) and prioritizing the patrol activity for the riskiest VMAs closer to the month of September. This risk-based approach generates a machine learning model that scores trees based on descriptive features, historical growth patterns, and historical priority “Memo” trims. a) Please identify who conducted the abovementioned third-party study? Please provide name of individual or business and address if available. b) Has the above-mentioned study been completed, as of the 2023 WMP submission date? c) If the answer to subpart (b) is “yes,” please provide the results of the study. d) If the answer to subpart (b) is “yes,” please any documents generated by the study (e.g. reports, workpapers, etc.). e) If the answer to subpart (b) is “no,” please state when SDG&E expects the study to be complete. f) After the abovementioned third-party study is complete, does SDG&E plan on using the abovementioned risk-based approach and “machine learning model that scores trees” as an enhancement to its WiNGS-Planning model? g) Does SDG&E have additional plans to refine the abovementioned risk-based approach to improve SDG&E’s off-cycle inspections process? h) For this 2023-2025 WMP cycle, does SDG&E plan on continuing with an 8-month off-cycle inspection schedule? | a) The study was performed by Logic 20/20. b) The first iteration of this data model was completed in late 2022. c) See attachment “SDGE-WMP2023-08_Q.14.pdf” d) See attachment “SDGE-WMP2023-08_Q.14.pdf” e) N/A f) No g) Yes. h) Yes. | Aaron Louie | 2023-04-05 | 2023-04-13 | 2023-04-13 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-08.pdf https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-08%20Attachment%20Q14.pdf | 1 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | 8.2.2.2.2 | 8.2.2.2.2 Frequency or Triggers Page 269
78 | CalPA | 2023-09 | CalPA-2023-09 | 1 | CalPA-2023-09.1 | Regarding Appendix F, OEIS Table 9-2 (Frequently De-energized Circuits) on WMP Appendix F p. 12-17: a) Please clarify if Entry 9 is missing or if Table 9-2 entries were misnumbered. b) If there was an error in OEIS Table 9-2, please provide a corrected version. c) Please explain why covered conductor is not considered as a mitigation for these Frequently De-energized Circuits. | a) Table 9-2 was misnumbered. b) See attached updated Appendix F, which includes an updated Table 9-2. This update will also be included in SDG&E’s non-substantive errata of the 2023-2025 Wildfire Mitigation Plan to be submitted on April 26, 2023. c) The Covered Conductor Program has the potential to raise the threshold for PSPS events to higher wind speeds compared to bare conductor hardening; however, as of the end of 2022 no circuits have been fully hardened with covered conductor and therefore the threshold for PSPS events has not been raised on any circuits with covered conductor installed. Based on benchmarking with other IOUs and SDG&E’s testing of covered conductors, the PSPS wind speed threshold for fully covered circuit segments is expected to be set to between 55 and 60 mph. As discussed in the response to Areas for Continued Improvement SDGE-22-11 in Appendix D of the 2023-2025 Wildfire Mitigation Plan, SDG&E expects to complete covered conductor testing and finalize this threshold by December 2023. | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-09.pdf https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-09%20Attachment%20Q1.pdf | 1 | No | Appendix F | OEIS Table 9-2 | N/A | N/A
79 | CalPA | 2023-09 | CalPA-2023-09 | 2 | CalPA-2023-09.2 | SDG&E states on p. 418 of its 2023 WMP that, “In advance of an approaching Santa Ana Wind event, the WiNGS-Ops model is utilized as an additional data point to determine if there are areas in the service territory where the wildfire risk could outweigh the risk of PSPS.” Please list all additional “data points” that SDG&E uses, besides the WiNGS-Ops model, to determine if the wildfire risk could outweigh the risk of PSPS during an approaching Santa Ana Wind event. | Multiple factors inform the decision to de-energize. These factors are quantified into infrastructure and environmental risk factors. Infrastructure risk includes information in the field based on unresolved damage found during inspections, active temporary construction/configuration of the electrical system that may cause equipment to have de-rated mechanical strength, and a CRI that identifies locations in the electrical system with a potential of having higher failure rates. Field environment issues may also include real-time observations from QEWs, local fire authority response and fire suppression ability at the time of an event, and wind conditions. These factors are compiled and summarized by circuit section to assist with decisions to de-energize parts of the electrical system (see PSPS Decision-Making Framework). Baseline alert wind speeds are used to quantify infrastructure risk into actionable criteria. They are determined separately for each device tied to a weather station and are based on a variety of factors such as wind speeds, the VRI, and the CRI. Alert wind speed thresholds are lowered if the VRI or the CRI rating is high (see PSPS Decision-Making Framework). Other factors such as maintenance issues, existing construction, other real time observations, ongoing fires and/or ignitions, suppression capabilities, and/or system protection could lower the thresholds for specific events. | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-09.pdf | 0 | No | 9.2 | 9.2 Protocols on PSPS Page 416 | 9.2.2 | 9.2.2 Method that Evaluates Relative Consequences of PSPS and Wildfires Page 419
80 | CalPA | 2023-09 | CalPA-2023-09 | 3 | CalPA-2023-09.3 | Regarding PSPS and its relationship to Sensitive Relay Profile (SRP) settings: a) Please describe in detail the decision-making process for a scenario in which SDG&E anticipates PSPS conditions but decides to use SRP settings instead. b) Please list all dates in 2021 and 2022 when SDG&E anticipated PSPS conditions but utilized SRP settings instead, if this occurred. c) Please provide a narrative of the decision-making process for any instances listed in part (b) above. d) Please describe how SDG&E utilizes SRP during a PSPS event period. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2 and 3. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) SDG&E does not use SRP instead of PSPS as these two mitigations are not treated the same or used as substitutes for one another. SDG&E will utilize SRP if PSPS de-energizations are predicted or if the FPI is Extreme. These settings are implemented only during the at-risk period, not seasonally, and only in regions impacted by extreme weather. The following bullet points summarize the conditions which would warrant SRP enablement: • If the FPI is Extreme in Mountain Empire and/or Ramona, Tier 3 should have Sensitive Relay Settings enabled. • If the FPI is Extreme in Eastern and/or Northeast, the entire HFTD (Tier 2 and Tier 3) should have Sensitive Relay Settings enabled. • If the FPI is Extreme in Orange County, then the HFTD in Orange County should have Sensitive Relay Settings enabled. • If the FPI is Extreme in any of the San Diego County coastal districts (North Coast, Beach Cities, Metro) all the Coastal Circuits with Fire Risk should have Sensitive Relay Settings enabled. • If any circuits are identified for potential PSPS in Mountain Empire and/or Ramona in the Tier 3 HFTD, all circuits in the Tier 3 HFTD should have Sensitive Relay Settings enabled for the predicted PSPS district(s). • If any circuits are identified for potential PSPS in Eastern and/or Northeast or Tier 2 in Mountain Empire and Ramona, the HFTD (Tier 2 and Tier 3) should have Sensitive Relay Settings enabled for the predicted PSPS district(s). • If any circuits are identified for potential PSPS in Orange County, then the HFTD in Orange County should have Sensitive Relay Settings enabled. • If any circuits are identified for potential PSPS that are on the Coastal Circuits with Fire Risk list, then all the Coastal Circuits with Fire Risk should have Sensitive Relay Settings enabled for the predicted district(s). b) As stated above, SDG&E does not use SRP instead of PSPS as these two mitigations are not treated the same or used as substitutes for one another. c) As stated in parts a and b, SDG&E does not use SRP instead of PSPS as these two mitigations are not treated the same or used as substitutes for one another. d) SRP settings are enabled when the FPI is Extreme or PSPS de-energizations are predicted. These settings are implemented only during the at-risk period, not seasonally, and only in regions impacted by extreme weather. When SRP is enabled, SDG&E has dedicated crews staffed for restoration and readiness response. Line SCADA crews are staffed 24/7, ready to respond to collect relay event records. Once collected, the records are sent to System Protection Engineering for review, who are also on 24/7 standby whenever SRP is enabled. These records help determine proper operation and aid in determining fault location. Feedback is then provided to the operations teams for better situational awareness. Protocols for testing/reclosing/restoration are no different between SRP and non-SRP conditions when under Extreme FPI or PSPS conditions. Automatic testing is not performed, and reclosing is disabled. A complete patrol is required, and step restore is performed for all outages. | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-09.pdf | 0 | No | Other | PSPS | N/A | N/A
81 | CalPA | 2023-09 | CalPA-2023-09 | 4 | CalPA-2023-09.4 | Regarding OneVoice communication to customers for SRP: a) In what circumstances does SDG&E plan to use OneVoice communication while SRP is enabled. b) Please list each type of situation for which SDG&E plans to use OneVoice to communicate with a customer regarding SRP. c) Please provide an example of the message SDG&E will send to a customer for each situation in which SDG&E uses OneVoice to communicate with a customer regarding SRP. d) When did SDG&E start using OneVoice to inform customers regarding SRP? e) At what point (i.e., or number of hours) prior to enabling SRP does SDG&E use OneVoice to notify customers? f) At what point (i.e., number of hours) after an SRP caused outage does SDG&E use OneVoice to notify customers? g) At what point (i.e., number of hours) after the line is restored does SDG&E use OneVoice to notify customers? | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2 and 3. Subject to and without waiving the foregoing objections, SDG&E responds as follows: SDG&E does not alter communications to customers when SRP is enabled. Outage response is no different for SRP outages versus non-SRP outages during an event. Outages are mapped on SDG&E’s public outage website with an estimated restoration time and information on outage cause. SDG&E staffs 24/7 System Protection support to review all SRP outages in real time to provide situational awareness to our operations teams in support of faster restorations. | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-09.pdf | 0 | No | Other | OneVoice | N/A | N/A
82 | CalPA | 2023-09 | CalPA-2023-09 | 5 | CalPA-2023-09.5 | WMP p. 375, OEIS Table 8-50 (Key Gaps and Limitations in Public Emergency Communication Strategy), states in part that “SDG&E has not been able to test notifications and messaging that were updated for the 2022 season. This messaging will be reviewed for any improvements in 2023…” Regarding SDG&E’s notifications and messaging for emergencies: a) Please provide a list of the improvements or enhancements that SDG&E made for the 2022 season. b) Please provide a list of the improvements or enhancements that SDG&E has made for the 2023 season (since the 2022 season). c) Does SDG&E conduct tests on its emergency communication processes to ensure customers are being appropriately notified? d) If the answer to part c) above is yes, when did SDG&E most recently conduct such testing? e) If the answer to part c) above is yes, please provide the results of SDG&E’s testing on its emergency communication processes. | a) A number of enhancements were made in 2022 to Enterprise Notification System (ENS) to improve data consistency across reporting and dashboards specific to PSPS events. The enhanced ENS data capabilities will support improved accuracy and consistency of data reporting in the post-event reports. Enhancements include: • Direct sync between the PSPS Dashboard and the ENS Dashboard to ensure customer counts and device lists match; • ENS data directly syncs with mobile platforms such as the Public Safety Partner Portal and mobile app to indicate customers who are de-energized and re-energized; • Enhanced notification reporting section of the ENS dashboard that allows for pre-incident, end of day, post-incident, and ad hoc reporting data to be readily available. Access opened to other key EOC positions to encourage more self-service and wider ability to cross reference and QA/QC data for post-event and post-season reporting. b) Enhancements for 2023 include Notification System Testing (NST) and streamlining data processes. Several solutions use the same data through different processes. Efforts will be made to streamline the data feeds which will lead to the eventual creation of “Enterprise Services”, a service to provide a single source of truth for data relating to PSPS de-energizations. c) SDG&E is creating a Notification System Testing (NST) program to test the notification system on a bi-annual basis. Pending internal approval, SDG&E anticipates testing will begin in Q2 2023. d) N/A - Testing has not yet been implemented. e) N/A - Testing has not yet been implemented. | Aaron Louie | 2023-04-05 | 2023-04-10 | 2023-04-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-09.pdf | 0 | No | 8.4 | 8.4 Emergency Preparedness Page 334 | 8.4.4.3 | 8.4.4.3 Current Gaps and Limitations Page 379
83 | OEIS | 2023-01 | OEIS-2023-01 | 1 | OEIS-2023-01.1 | Regarding Appendix B Items That Are Currently Optional Or “By Request” Only Provide the following, which are outlined in the 2023-2025 Wildfire Mitigation Plan Technical Guidelines, Appendix B. If the data is tabular (formulas, tables, graphs, charts) provide it in MS Excel. If the data is text-heavy, provide the information in MS Word. a. Detailed Model Documentation for each model and sub-model discussed in SDG&E’s response to Section 6.1.2 Summary of Risk Models (Technical documentation should be presented according to ASTM E 1472 – Standard Guide for Documenting Computer Software for Fire Models). i. Include a list of assumptions and known model limitations according to ASTM E 1895 – Standard Guide for Determining Uses and Limitations of Deterministic Fire Models. ii. Present verification and validation documentation according to the SFPE’s Guidelines for Substantiating a Fire Model for a Given Application or ASTM E 1355 – Standard Guide for Evaluating the Predicting Capability of Deterministic Fire Models. At a minimum, the documentation must include:1 (1) Purpose of the model/problem identification (2) Model version (3) Theoretical foundation (4) Mathematical foundation (5) External dependencies (6) Model substantiation (7) Sensitivity b. Model Substantiation:2 i. For each model, provide documentation of the following model substantiation studies: (1) Validation data (2) Model verification (3) Model validation (4) Model calibration c. Additional Models Supporting Risk Calculation:3 i. For each additional model that supports the risk calculations, provide weather analysis and fuel conditions. d. Calculation of Risk and Risk Components: Likelihood:4 i. More detailed information on: (1) Ignition Likelihood (2) Equipment Likelihood of Ignition (3) Contact from Vegetation Likelihood of Ignition (4) Contact from Object Likelihood of Ignition (5) Burn Probability (6) PSPS Likelihood e. Calculation of Risk and Risk Components: Consequence5 i. More detailed information on: (1) Wildfire Consequence (2) Wildfire Hazard Intensity (3) Wildfire Exposure Potential (4) Wildfire Vulnerability f. Calculation of Risk and Risk Components: PSPS Consequence6 i. More detailed information on: (1) PSPS Exposure Potential (2) Community Vulnerability to PSPS g. Calculation of Risk and Risk Components: Risk7 i. More detailed information on: (1) Ignition Risk (2) PSPS Risk (3) Overall Utility Risk | Link to the 2023 WMP: https://www.sdge.com/2023-wildfire-mitigation-plan WMP technical documentation: Attached as ”Model Documentation_Wings Planning V1.pdf,” and “Model Documentation_WiNGS-Ops V1.pdf.” WiNGS Planning: i. Reference section 6.2.3 of WMP 2023, page 73. ii. Reference section 2.6 of technical document for WiNGS Planning. At a minimum, the documentation must include:8 (1) Purpose of the model/problem identification – reference section 1.1 - Technical document for Wings Planning (2) Model version = reference section 1.2 - Technical document for Wings Planning (3) Theoretical foundation – reference section 2.3 - Technical document for Wings Planning (4) Mathematical foundation – reference section 2.4 - Technical document for Wings Planning (5) External dependencies –reference section 2.5.1 - Technical document for Wings Planning (6) Model substantiation - reference section 2.6 - Technical document for Wings Planning (7) Sensitivity – reference section 2.6.2 - Technical document for Wings Planning b. Model Substantiation:9 i. For each model, provide documentation of the following model substantiation studies: (1) Validation data reference section 2.6.2 - Technical document for Wings Planning (2) Model verification - reference section 2.6.1 - Technical document for Wings Planning (3) Model validation - reference section 2.6.2 - Technical document for Wings Planning (4) Model calibration - reference section 2.6.3 - Technical document for Wings Planning c. Additional Models Supporting Risk Calculation:10 i. For each additional model that supports the risk calculations, provide weather analysis and fuel conditions. Reference section 2.5 - Technical document for Wings Planning d. Calculation of Risk and Risk Components: Likelihood:11 i. More detailed information on: reference section 6.2.2.1, page 68 - Technical document for Wings Planning (1) Ignition Likelihood (2) Equipment Likelihood of Ignition (3) Contact from Vegetation Likelihood of Ignition (4) Contact from Object Likelihood of Ignition (5) Burn Probability (6) PSPS Likelihood e. Calculation of Risk and Risk Components: Consequence12 i. More detailed information on: - reference WMP 2023 section 6.2.2.2 page 70 (1) Wildfire Consequence (2) Wildfire Hazard Intensity (3) Wildfire Exposure Potential (4) Wildfire Vulnerability f. Calculation of Risk and Risk Components: PSPS Consequence13 i. More detailed information on: reference WMP 2023 section 6.2.2.2 page 70 (1) PSPS Exposure Potential (2) Community Vulnerability to PSPS g. Calculation of Risk and Risk Components: Risk14 i. More detailed information on: reference section 6.2.1 and 6.2.2 of WMP 2023, page 59 and 64 (1) Ignition Risk (2) PSPS Risk (3) Overall Utility Risk WiNGS Ops: i. Reference section 6.2.3 of WMP 2023, page 73 ii. Reference section 2.6 of technical document for WiNGS Ops (1) Purpose of the model/problem identification – Section 1.1 - Technical documentation for WiNGS Ops (2) Model version - (3) Theoretical foundation – Section 2.2.1 – Technical documentation for WiNGS Ops (4) Mathematical foundation Section 2.2.1 - Technical documentation for WiNGS Ops (5) External dependencies – (6) Model substantiation - Section 2.6 - Technical documentation for WiNGS Ops (7) Sensitivity – Section 2.6.2 - Technical documentation for WiNGS Ops b. Model Substantiation:15 Section 2.6 - Technical documentation for WiNGS Ops i. For each model, provide documentation of the following model substantiation studies: (1) Validation data (2) Model verification – Section 2.6.1 - Technical documentation for WiNGS Ops (3) Model validation – Section 2.6.2 - Technical documentation for WiNGS Ops (4) Model calibration – Section 2.2.3 - Technical documentation for WiNGS Ops | Sara Moore | 2023-04-07 | 2023-04-12 | 2023-04-12 | https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-01.pdf https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-01%20Attachment%20Q1%20%26%20Q2.zip | 1 | No | 6 | 6 RISK METHODOLOGY AND ASSESSMENT PAGE 52 | 6.1.2 | 6.1.2 Summary of Risk Models Page 54
84 | OEIS | 2023-01 | OEIS-2023-01 | 2 | OEIS-2023-01.2 | Regarding Comprehensive System Diagram for All Risk Models Used Provide comprehensive system diagrams in MS Visio or PPT for all risk models, including: 1. A comprehensive diagram for operational models 2. A comprehensive diagram for planning models Section 6.1.2, Summary of Risk Models, asks for a summary of risk models in table form with specific fields. Section 6.2.1, Risk and Risk Component Identification, asks for a chart that demonstrates the components of overall utility risk. This request is comprehensive of all models that work together in the Decision-Making Framework (DMF). The requested diagram should show: a. Interaction between the models presented graphically (e.g., inputs and outputs coming to and going from models to other models) b. Organization with the use of swimlanes where applicable c. Starting and ending points d. Decisions and process flows e. Use of a legend and colors to classify inputs/output types and model-to-model interactions f. The full cycle of models working together and creating feedback for model adjustments and fine-tuning | a.WiNGS Planning (Figure 6-7 – WMP 2023) WiNGS Ops Risk Calculation Process Flow Diagram (Figure 6-5 – WMP 2023) WiNGS-Ops (Figure 6-8 – WMP 2023) b. Please see response/figures in part a. c. Please see response/figures in part a. d. WiNGS Planning – Mitigation initiative prioritization (Figure 7-4 – WMP 2023) WiNGS Ops – PSPS Decision Making Framework e. Please see response/figures in part a. f. Please see “Model Documentation_Wings Planning V1.pdf,” section 2.6.2 Validation and 2.6.3 Calibration. Additionally see the “Model Documentation_WiNGS-Ops V1.pdf” section 2.6.2 Validation and 2.6.3 Calibration. | Sara Moore | 2023-04-07 | 2023-04-12 | 2023-04-12 | https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-01.pdf https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-01%20Attachment%20Q1%20%26%20Q2.zip | 1 | No | 6 | 6 RISK METHODOLOGY AND ASSESSMENT PAGE 52 | 6.1.2 | 6.1.2 Summary of Risk Models Page 54
85 | OEIS | 2023-01 | OEIS-2023-01 | 3 | OEIS-2023-01.3 | Regarding Portfolio Level Risk Analysis and Risk Spend Efficiency a. Provide an example of how risks are aggregated to a portfolio, and if and how interdependencies between the risks are explicitly captured in the portfolio. Response should be provided in Excel. Also include the level of organization for the portfolio (e.g., asset, geographical or business unit). b. Are tail-risks calculated on a portfolio of risks? If so, provide an example. c. Are probability distributions and interdependencies used as inputs to outputs for the bowties used in SDG&E’s WMP submission (see examples present in Appendix B)? If so, provide an example using the bowtie charts presented in SDG&E’s Appendix B submission. As appropriate, the response should be provided in Excel. d. Provide an example of how risk spend efficiency (RSE) deals with interdependent risks, and mutually exclusive risks. As appropriate, the response should be provided in Excel. e. Is RSE calculated for both average and tail? If so, provide an example. The response should be provided in Excel. | a. Per the WiNGS-Planning model risk inputs, inputs are assessed and treated as independent risk drivers and metrics that support the calculation of the risk scores, per the weighted sum framework of the model. The WiNGS-Planning model granularity is at the circuit-segment level. For the portfolio level reporting of the risk scores from the model, the risk scores are subsequently sum aggregated from the circuit-segment level to the portfolio level granularity. See attached .csv file “Question 3a - WF and PSPS risk scores - 2023 wmp output.csv” for the output of circuit-segment risk scores prior to sum aggregation to the portfolio level granularity, indicating how risk scores are aggregated. b. The top 5%, top 20%, and bottom 80% are calculated on the WiNGS Planning output. Please see SDG&E WMP 2023 - table 6.5 for a reference of the top 5% wildfire risk circuit segments. c. Assuming the bowties referred to are the flow diagrams (Figures 1 & 2) present in 2023 WMP Appendix B, two probability distributions are used as inputs to the model: FIRE SIMULATIONS (WRRM metrics) (percentiles) (Figure 2) and WEATHER DATA (percentiles) (Figure 2). No interdependencies are used as inputs. d. Per the WiNGS-Planning model risk inputs, inputs are assessed and treated as independent risk drivers and metrics that support the calculation of the risk scores. As such, RSE does not need to deal with interdependent or mutually exclusive risks as they are not present as inputs to the model. e. Within WiNGS-Planning, an RSE value is calculated for each circuit-segment mitigation combination. The RSE value is neither an average nor a tail value, but a single RSE value calculated from the risk reduction and cost assessed associated to the selected circuit-segment mitigation combination. | Sara Moore | 2023-04-07 | 2023-04-12 | 2023-04-12 | https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-01.pdf https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-01%20Attachment%20Q3.zip | 1 | No | Other | Portfolio Level Risk Analysis and Risk Spend Efficiency | N/A | N/A
86 | OEIS | 2023-01 | OEIS-2023-01 | 4 | OEIS-2023-01.4 | Regarding Cost-Benefit Within and Overall Decision-Making Framework a. If projects are justified based on a multi-attribute value functions/cost basis, what threshold or hurdle is used? b. How is the chance that a project exceeds the threshold computed? c. If projects are justified based on a multi-attribute value functions/cost basis, what threshold or hurdle is used? | a. A financial analysis was conducted analyzing different portfolios ultimately identified the risk mitigation and hardening strategy that reflected the inflection point between risk and cost. The RSE threshold is set to meet targeted risk reduction percentages over time, while also meeting construction mileage targets. To achieve the desired risk reduction, the RSE threshold based on the model that forms the basis of SDG&E’s 2023 Wildfire Mitigation Plan was 29. The WiNGS model employs a decision tree to select mitigations. The decision tree does not compare covered conductor RSE to underground RSE. The first branch on the decision tree is to measure the validity of undergrounding per segment. Each segment is qualified as whether it meets the RSE for undergrounding. If the segment meets or exceeds the undergrounding RSE, the model recommends undergrounding as the proposed mitigation. Segments that do not meet the undergrounding RSE, are then evaluated for covered conductor mitigations. If the RSE for covered conductor is met or exceeded, the proposed mitigation is covered conductor. When neither condition is met, no mitigation is recommended. b. For every mitigation project informed by the WiNGS-Planning model, the project is required to have met the threshold framework described above and have had an optimal recommended mitigation assigned to it. Therefore, every project will have met the threshold prior to implementation. c. Please see response a. | Sara Moore | 2023-04-07 | 2023-04-12 | 2023-04-12 | https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-01.pdf | 0 | No | Other | Cost-Benefit Within and Overall Decision-Making Framework | N/A | N/A
87 | CalPA | 2023-10 | CalPA-2023-10 | 1 | CalPA-2023-10.1 | SDG&E states on p. 2 of its 2023 WMP regarding its Drone Investigation, Assessment and Repair (DIAR) Program, The program was successful in identifying additional risks that were not visible utilizing ground-based inspections… To continue to capture the enhanced risk reduction realized through the DIAR Program on a more permanent basis, risk modeling will be incorporated to identify the top 15 percent of HFTD structures by risk and drone inspections will be performed on those assets each year. a) Please describe the additional risks SDG&E identified through the DIAR program that were not identifiable from ground-based inspections. b) Are there risks commonly identified through ground-based inspections that are not generally visible utilizing drone-based inspections? Please describe. c) When does SDG&E plan on permanently implementing risk modeling within the DIAR program over the 2023-2025 WMP cycle? | a) In general, the drone inspections and imagery collected allowed inspectors to identify the following issues: 1) Issues visible only from above such as hollowed out pole tops, tracking on crossarms, transformer corrosion (visible only on the lids), and loose hardware that was blocked from view if looking up. 2) Smaller issues harder to see with the naked eye or with binoculars, such as frayed wire or small chips in insulators, that are more easily visible with high resolution imagery than can be enhanced on the computer screen. 3) Issues on poles that are more difficult to access because of terrain or topography. b) Some issues that are more commonly identified by ground-based inspections versus drone inspections include: damaged or loose guy wire, damaged or unsecured conduit, clearance or loose wires associated with communications infrastructure, and buried anchor. With that said, the drone inspection program includes both a ground-based inspection and an aerial inspection. Inspection teams consist of a qualified inspector and a drone pilot in an effort to capture issues identified better with a drone and those issues that are best observed from the ground. c) SDG&E began permanently implementing risk modeling with the DIAR program in 2023 with inspections starting in February 2023 and continuing throughout the 2023-2025 WMP cycle. | Aaron Louie | 2023-04-10 | 2023-04-14 | 2023-04-14 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-10.pdf | 0 | No | 1 | 1 EXECUTIVE SUMMARY Page 1 | 1.1 | 1.1 Summary of 2020–2022 WMP Cycle Page 1
88 | CalPA | 2023-10 | CalPA-2023-10 | 2 | CalPA-2023-10.2 | SDG&E states on p. 5 of its 2023 WMP, “The long-term outlook of the WiNGS-Planning portfolio shows the deployment of strategic undergrounding and covered conductor not only reduces current wildfire risk but also combats the increasing wildfire risk due to climate change.” a) How many miles of strategic undergrounding from 2019 through 2022 have been implemented based upon the recommendations provided by the WiNGs-Planning portfolio? b) How many miles of covered conductor installation from 2019 through 2022 have been implemented based upon the recommendations provided by the WiNGs-Planning portfolio? | SDG&E objects to the request on the grounds set forth in General Objections Nos. 5. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) WiNGS scoped segment mitigations beginning in 2022. SDG&E performed 65 miles of strategic undergrounding in 2022. b) WiNGS scoped segment mitigations beginning in 2022. SDG&E performed 61.2 miles of covered conductor in 2022. | Aaron Louie | 2023-04-10 | 2023-04-19 | 2023-04-19 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-10.pdf | 0 | No | 1.1.1 | 1.1.1 Major Lessons Learned Page 4 | 1.1.1.2 | 1.1.1.2 Wildfire Mitigation StrategyPage 5
89 | CalPA | 2023-10 | CalPA-2023-10 | 3 | CalPA-2023-10.3 | SDG&E states on p. 5 of its 2023 WMP, “Collaboration and testing have continued to improve SDG&E’s understanding of covered conductor’s ability to raise PSPS wind speed thresholds, which (although not finalized) are expected to increase to 55 to 60 miles per hour.” a) When does SDG&E plan on implementing the expected increase in PSPS wind speed thresholds for circuits with covered conductor? b) How would the above-mentioned expected increase in PSPS wind speed thresholds affect the most frequently de-energized circuits’ risk scores? c) Would the above-mentioned expected increase in wind speed threshold be applicable on all circuits across SDG&E’s entire service territory? | SDG&E objects to the request on the grounds set forth in General Objections Nos. 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) SDG&E expects to complete the first full segment of covered conductor in 2023. The ongoing lab testing and joint IOU collaboration will work to finalize the new wind speed threshold associated with fully covered segments when making PSPS decisions. As discussed in the response to Areas for Continued Improvement SDGE-22-11 in Appendix D of the 2023-2025 Wildfire Mitigation Plan, SDG&E expects to complete covered conductor testing and finalize this threshold by December 2023. b) Within the WiNGS-Planning model, the effect of wind speed threshold increases in the risk modeling has a decreased effect on the Covered Conductor PSPS probabilities assessed for each weather station. Each circuit-segment has an associated weather station assigned to it. The PSPS probabilities are positively correlated with the PSPS LoRE and PSPS risk score. c) Wind speed thresholds will only be increased on circuit segments that have been fully hardened with covered conductor. The wind speed threshold will apply across all fully covered conductor segments. | Aaron Louie | 2023-04-10 | 2023-04-14 | 2023-04-14 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-10.pdf | 0 | No | 1.1.1 | 1.1.1 Major Lessons Learned Page 4 | 1.1.1.3 | 1.1.1.3 Grid Design, Operations, and Maintenance Page 5
90 | CalPA | 2023-10 | CalPA-2023-10 | 4 | CalPA-2023-10.4 | SDG&E states on p. 10 of its 2023 WMP, “SDG&E will further advance implementation of new technologies such as Advanced Radio Frequency Sensors (ARFS) which officially kicked-off in mid-2022 after completing a 2-year demonstration.” a) Please describe the scope, goals, and analytical methods for the demonstration project noted above. b) Please provide the results of SDG&E’s findings after the 2-year demonstration referenced above. c) Please provide any documents generated from the above-mentioned 2-year demonstration (e.g. reports, workpapers, etc.). d) In 2022, how many Advanced Radio Frequency Sensors did SDG&E install in HFTD tier 2 areas? e) In 2022, how many Advanced Radio Frequency Sensors did SDG&E install in HFTD tier 3 areas? | a) SCOPE: Electrical equipment failures can cause significant damage, customer and employee safety impacts, high costs of repair, and extended outages to customers. Equipment failures, specifically located in the HFTD, can cause significant loss of life and property and should be avoided at all costs. Through years of research and development, SDG&E has developed, alongside its strategic vendor partnerships, ways to successfully detect what are known as incipient faults on the system with enough time to locate and potentially fix or replace equipment prior to it permanently failing. These incipient faults occur on failing pieces of equipment long before they fail violently and cause damage to the surrounding area. Recent advances in power quality, relaying, radio frequency, and other technologies have made it possible for utilities to identify and predict failures long before they occur. GOAL: The goal of the EFD Program (WMP.1195) is to utilize these technologies to detect and prevent significant equipment failures in the HFTD to address fire risk while also gaining the benefits of reducing customer forced outages. ANALYTICAL METHOD: Manual review of each paths detection energy plots to find signals indicating significant energy signals. This is followed by fielding of the location by a qualified electrical worker to identify damage to components that are generating the signals. b) See attached file “Results” for damage description and photos of damage found. i. Broken ceramic insulator found and replaced on C448 that was not identified during routine patrols. ii. Burned insulator found and replaced at Warners Substation on stepdown to circuit 211. iii. Multiple wire splices with internal partial discharge on C211 found and replaced. iv. Damaged insulator leaking to crossarm on C211 found and replaced. v. Bird nest on buck pole C211 found and removed. vi. Bird-caged jumper on C211 found and replaced. vii. Damaged conductor on C211, loose (not broken) strand, deemed no structural damage by QEW. viii. Bird-caged conductor found on C211 that was not identified during routine patrols; deemed no structural damage by QEW. ix. Animal damage to dead-end insulator on C211 found and replaced. x. Multiple instances of cosmetic wire slap damage to conductor; deemed no structural damage by electric troubleshooter. c) The final report for the 2-year demonstration is still in development. See attach file “Early Fault Detection Deployment Status.” d) In 2022, SDG&E installed 38 sensors in Tier 2. e) In 2022, SDG&E installed 26 sensors in Tier 3. | Aaron Louie | 2023-04-10 | 2023-04-14 | 2023-04-14 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-10.pdf https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-10%20Attachment%20Q4.zip | 1 | No | 4.2 | 4.2 Plan Objectives Page 16 | 4.2.1.3 | 4.2.1.3 Grid Design, Operations, and Maintenance Page 16
91 | CalPA | 2023-10 | CalPA-2023-10 | 5 | CalPA-2023-10.5 | SDG&E states on p. 16 of its 2023 WMP regarding its WiNGS-Planning model, The Wildfire Next Generation System Planning (WiNGS)-Planning model has incorporated additional inputs and refinements leading to a portfolio of approximately 1,500 miles of strategic undergrounding and 370 miles of covered conductor to be installed between 2022 and 2032. This portfolio will reduce the risk of wildfire by 83 percent… a) Please identify the “additional inputs and refinements” referenced above that SDG&E incorporated into the WiNGS-Planning model. b) Please describe how these above-mentioned “additional inputs and refinements” resulted in a portfolio of 1,500 miles of strategic undergrounding and 370 miles of covered conductor. c) Please provide a year-by-year breakdown of the estimated reduction of wildfire risk from 2022 until 2032 due to the input and refinements referenced above. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 3 and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) Refinements and updates include updated circuit segment and segment attribute data. Updated MAVF weights per current attributes and updates to ignition rate reduction variable accuracies. The model was improved with a hardening granularity that increased from 2 to 4 states, and improved accuracy of data collected (pole-miles hardened, pole-miles unhardened vs. RFS miles-hardened, CC-miles-hardened, TH-miles-hardened, miles-unhardened). Inclusion of lifecycle savings assessment from vegetation management, asset inspections and PSPS activations. b) The updates and refinements described optimize the model for more accurate risk-benefit assessment. The model is then run with the latest refreshed model features and data, resulting in an update to the output of the model for mitigation recommendation. This resulted in the updated mitigation mileage portfolio to most cost-effectively achieve the targeted risk reduction goals. | Aaron Louie | 2023-04-10 | 2023-04-19 | 2023-04-19 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-10.pdf | 0 | No | 4.2 | 4.2 Plan Objectives Page 16 | 4.2.1.2 | 4.2.1.2 Wildfire Mitigation Strategy Page 16
92 | CalPA | 2023-10 | CalPA-2023-10 | 6 | CalPA-2023-10.6 | Regarding SDG&E’s Figure 6-7 WiNGS-Planning Calculation Schematic on p. 66 of its 2023 WMP: a) Please describe in detail the review process that SDG&E SMEs undertake once the WiNGS-Planning has provided the mitigation recommendation for a specific circuit segment. b) Has SDG&E encountered a situation where an SDG&E SME recommends a different mitigation measure for a circuit segment than what was recommended by the WiNGS-Planning portfolio? c) If the answer to part (b) above is yes, please provide a narrative of how SDG&E determines what mitigation measure to move forward with in a scenario where SME and WiNGS-Planning recommendations conflict. | a) Review the WiNGS-Planning mitigation recommendations by the SDG&E SMEs considers the following aspects and limitations of the model to ensure cost-effective and pragmatic mitigation plans are released to design and construction. Wildfire Risk Rank The WiNGS Planning model ranks the fire risk contribution of each segment relative to that of all other segments. This ranking reflects the fire risk contribution of the segment before the recommended mitigation has been implemented. Typically, those circuits and segments with the greatest wildfire risk will be fire hardened first. Re-Hardening Prior to the development of the WiNGS model and before the establishment of the Strategic Undergrounding Program (SUG), SDG&E established and administered traditional fire hardening programs. Typically, these programs replaced wood poles with steel and new conductors. To limit both community disruptions and replacement of recently installed facilities, SDG&E has established re-hardening moratoriums. These re-hardening moratoriums influence the prioritization and schedule (i.e., the planned scope year) for implementing underground or covered conductor fire hardening mitigations for circuits or segments that were hardened through traditional programs. Segments subject to these moratoriums typically would not be worked until the moratorium has expired unless an exemption from leadership is received. Public Safety Power Shutoff To ensure that the selected fire risk mitigation does not miss an opportunity to mitigate PSPS risk, SDG&E SMEs look at both the likelihood and consequence of a PSPS event on the segment being hardened. The likelihood of a PSPS event for a given customer depends on the wind speeds and wind speed thresholds for the infrastructure (e.g., bare vs. covered conductor) both at and upstream of the segment that serves that customer.  The consequence of a PSPS event is dependent on the expected event duration and the number of customers that would be impacted during a PSPS event. ESH and Meteorology review the recommended mitigations as well as wind speed data and infrastructure both at the segment in question and upstream to understand the PSPS risk after the mitigation has been implemented. Efficiencies There are efficiencies in the scoping process that can reduce the burden on downstream resources and reduce costs. For example, limiting scope to geographically proximate segments can reduce:  Travel time for survey teams who are responsible for fielding the fire hardening scope.  Mobilization/demobilization for construction crews and make better use of existing laydown yards.  Cutover coordination Constructability Difficult terrain or environmental constraints may impede the completion of undergrounding projects. In those cases, pivots to CC OH are evaluated. This pivot from the WiNGS-Planning model may limit the risk reduction achieved for a particular segment. In these cases, SDG&E will determine if other mitigations (on this segment or elsewhere in the system) are necessary to achieve risk reduction targets. Covered conductor projects typically follow existing OH routes and easements, thereby limiting constructability issues. Construction Standards SDG&E reviews recommended mitigations to ensure alignment with existing construction standards. For example, installation of covered conductor within an Extra Heavy (Ice) Loading District requires a deviation request in accordance with Overhead Construction Standards. The necessary design changes may significantly increase the cost of the project. Where an underground route is available, SDG&E will consider a pivot to undergrounding in place of covered conducted in these extra heavy loading districts. b) SDG&E has encountered limited situations in which the SDG&E SME recommends a different mitigation measure. These situations are isolated to constructability concerns or instances where the recommended mitigation would deviate from construction standards. c) In instances where constructability concerns were not captured by the model, updated cost information that reflects these concerns is fed back into the model to determine if the mitigation recommended by WiNGS-Planning would change. If the recommended mitigation does not change (i.e., the risk-spend efficiency thresholds are still met), then the mitigation proceeds as originally recommended by the model. If the risk-spend efficiency thresholds are no longer met, then the updated mitigation is incorporated into the wildfire mitigation scoping plans. In those instances where deviations from construction standards are identified, construction standards take precedent. If construction standards limit the risk reduction achieved for a particular segment, SDG&E will determine if other mitigations (on this segment or elsewhere in the system) are necessary to achieve risk reduction targets. | Aaron Louie | 2023-04-10 | 2023-04-19 | 2023-04-19 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-10.pdf | 0 | No | 6.2.2 | 6.2.2 Risk and Risk Components Calculation Page 64 | Figure 6-7 | Figure 6-7: WiNGS-Planning Calculation Schematic
93 | CalPA | 2023-10 | CalPA-2023-10 | 7 | CalPA-2023-10.7 | SDG&E states on p. 111 of its 2023 WMP regarding Identification of Mitigation Initiatives, In the early phases of SDG&E’s wildfire mitigation efforts and prior to the use of WiNGS-Planning, SDG&E’s overhead bare conductor hardening programs focused on targeted only the spans identified as containing certain high-risk assets (e.g., bare conductor, aged wood poles). These programs were aimed at reducing the highest level of risk, focused specifically on the replacement of the identified high-risk assets, and did not address entire segments. Therefore, most circuit segments were left only partially hardened in the top risk areas. a) What is the total number of circuit miles that SDG&E has identified as being only partially hardened and where SDG&E needs to complete re-hardening work? b) Please disaggregate your response to part (a) by HFTD tier. c) Please provide a list of all the Circuit IDs that fall in the category described in part (a) above. d) Please describe how SDG&E intends to maintain operational flexibility while hardening the circuit miles referenced in your answer to part (c). e) When does SDG&E plan on starting to replace the above-mentioned circuit miles identified as needing re-hardening work? f) Of the projected 84 miles of strategic undergrounding for 2023, how many miles fall under the category of SDG&E’s re-hardening strategy referenced in the quote above? g) Please provide SDG&E’s costs projections for replacing existing hardened circuits during the 2023-2025 WMP cycle. h) What is SDG&E’s current estimate of the cost per circuit-mile for the projects identified in your response to part (f) of this question? i) Please provide any workpapers that SDG&E used to develop the cost estimates addressed in parts (g) and (h) of this question. j) Does SDG&E plan on completing system hardening work on entire circuit segments, as part of its re-hardening strategy referenced in the quote above? | SDG&E objects to the request on the grounds set forth in General Objections Nos. 3 and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) The total miles of partially hardened circuit segments within the current WMP cycle is: 651.5365666 b) Tier 2 partially hardened miles: 232.6886847. Tier 3 partially hardened miles: 418.8478819 c) The list of circuits that will experience re-hardening within the current WMP cycle is: 1030-989R, 220-288R, 220-294R, 220-298R, 222-1370R, 222-1401R, 222-1433R, 222-1441R, 222-1503, 222-2013R, 358-682F, 445-19R, 445-24R, 445-894R, 73-643R, 79-785, 972-8, CB 222, CB 73, CB OK1, 1021-25R, 1215-12R, 1215-28R, 157-204R, 176-197F, 176-200F, 176-41R, 211-279R, 212-638R, 212-739R, 215-38R, 217-837R, 221-782R, 230-133AE, 233-123R, 350-2192R, 350-2196R, 350-2201R, 441-23R, 441-27R, 441-30R, 444-43R, 520-1045R, 520-10R, 520-1489R, 520-35R, 520-45, 521-14R, 78-782R, 971-1973R, 974-23R, 974-35R, CB 971, 1233-252R, 237-2R d) SDG&E will continue to operate the distribution system consistent with any limitations attributable to existing field conditions. As re-hardening work proceeds, the limitations may be lessened or totally removed, thereby allowing SDG&E greater operational flexibility. e) In general, SDG&E will only re-harden these circuit miles after 5-years (at the earliest) after the energization date for traditionally hardened segments. In instances where covered conductor will be removed and conductor moved underground, this work will not occur until at least 7-years after energization of the covered conductor spans. Exceptions to these re-hardening moratoriums are possible, but are limited. An exception is approved only if the efficiencies and risk benefits of the project outweigh costs associated with re-hardening. f) For the 2023 strategic undergrounding projects, SDG&E made significant efforts to avoid re-hardening any traditional hardening segments. This minimized the total number of re-hardening miles in 2023. Re-hardening was only permitted if the benefits of such a project, including efficiencies gained from working in geographically proximate locations and PSPS risk reduction, outweighed the drawbacks of re-hardening (i.e., cost, community disturbance, etc.). 24.71SUG miles will be re-hardened in 2023. g) SDG&E’s costs projections for replacing existing hardened circuits during the 2023-2025 WMP cycle are 122,752,500 in total. Undergrounding comprises 109,642,500 of the total cost and covered conductor comprises 13,110,000 of the total cost. h) Strategic Undergrounding cost: 2,475,000 per mile, Covered Conductor: 1,000,000 per mile i) Please see attachment “DR_Cal Advocates_10_Q7.xlsx.” j) SDG&E plans to harden entire circuit segments consistent with the output of the WiNGS Planning Model, which makes mitigation recommendations for all segments within an entire circuit. | Aaron Louie | 2023-04-10 | 2023-04-19 | 2023-04-19 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-10.pdf https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-10%20Attachment%20Q7.xlsx | 1 | No | 7.1.4.2 | 7.1.4.2 Mitigation Initiative Prioritization Page 108 | 7.1.4.2.2 | 7.1.4.2.2 Identification of Mitigation Initiatives Page 109
94 | CalPA | 2023-10 | CalPA-2023-10 | 8 | CalPA-2023-10.8 | SDG&E states on p. 116 of its 2023 WMP regarding its WiNGS-Planning model, The WiNGS-Planning Model makes one of three recommendations to mitigate risk for each circuit segment with overhead exposure in the HFTD: 1) strategic undergrounding of electric lines, 2) installation of covered conductor, 3) no strategic undergrounding or covered conductor mitigation. a) Does SDG&E have a review process in place when the WiNGS-Planning model makes the recommendation of “no strategic undergrounding or covered conductor mitigation? b) If the answer to part (a) above is yes, please describe in detail what the review process entails and the steps that SDG&E takes to verify that no mitigation is required for the circuit segment. c) Does SDG&E perform other alternative mitigation measures on circuit segments when the WiNGS-Planning model recommends “no strategic undergrounding or covered conductor mitigation” as referenced above? d) If the answer to part (c) above is yes, please describe what mitigation measures SDG&E considers in such instances. | a) In instances where the mitigation for a circuit segment is inconsistent with other segments on the circuit (i.e., the WiNGS Planning Model recommends covered conductor or no mitigation within a circuit where other segments will be moved underground), SDG&E reviews the model inputs to determine the factor that drove the mitigation recommendation. After re-validating these inputs and seeking input from SMEs, pivots to the recommended mitigation are evaluated. b) See answer to Question 6 regarding the SME review. c) Yes SDG&E performs alternative mitigation measures on circuit segments for which WiNGS planning recommends no strategic undergrounding or covered conductor mitigation. These programs aim to reduce ignition risks for these remaining Overhead Distribution facilities. See answer to part d. d) The following mitigation measures are deployed on circuit segments where no mitigation is recommended by the WiNGS-Planning Model. 1. Advanced Protection Program – This program aims to prevent and mitigate the risks of fire incidents, create higher visibility and situational awareness in fire-prone areas, and allow for the implementation of new relay standards in locations where protection coordination is difficult due to lower fault currents attributed to high impedance faults. SDG&E’s advanced protection program is designed to reduce the risk of transmission or distribution risk events leading to an ignition. 2. Expulsion Fuse Replacement. The fuse replacement program replaces existing expulsion fuses that operate as described above with new more fire safe expulsion fuses that are approved by CAL FIRE and reduce the discharge expelled into the atmosphere, reducing the chance of a fuse operation leading to an ignition 3. Lightning Arrestor: SDG&E plans to replace existing arrestors in strategic locations within the HFTD with CAL FIRE approved lightning arrestors.. The CAL FIRE approved device comes with an external device that operates prior to the arrestor overloading, dramatically reducing the potential of becoming an ignition source 4. Hot Line Clamps. SDG&E has identified high risk connectors known as “hotline clamps” which are a potential weak connection that can fail during a fault on the system, resulting in a wire down event. This wire down event can lead to an energized wire on the ground or coming into contact with a foreign object, thus becoming an ignition source. DG&E is focusing this initiative on the HFTD portion of its service territory. 5. Drone inspections. See Section 8.1.3.7 of 2023WMP. 6. Vegetation Management. See Section 8.2 of 2023 WMP | Aaron Louie | 2023-04-10 | 2023-04-19 | 2023-04-19 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-10.pdf | 0 | No | 7.1.4.2 | 7.1.4.2 Mitigation Initiative Prioritization Page 108 | 7.1.4.2.4 | 7.1.4.2.4 Mitigation Initiative Prioritization to Reduce both Wildfire and PSPS Risk Page 113
95 | CalPA | 2023-10 | CalPA-2023-10 | 9 | CalPA-2023-10.9 | SDG&E states on p. 122 of its 2023 WMP regarding its WiNGS-Planning model, Based on these overall Wildfire and PSPS risk estimates derived from the WiNGS-Planning 3.0 model and targeted mileage scope per year, SDG&E estimates a reduction of approximately 80 percent of wildfire risk from the start of 2022 through the end of 2032. This is not including PSPS risk, probability of a PSPS occurring on a segment, and the estimation for climate change impacts to risk reduction. a) How did SDG&E calculate the above-mentioned “estimated reduction of approximately 80 percent of wildfire risk from the start of 2022 through the end of 2032”? b) Does SDG&E currently have an estimate of how many circuit miles will need to be hardened to achieve the planned reduction of 80 percent of wildfire risk referenced above? c) Has SDG&E calculated the minimum number of targeted circuit mileage that needs to be hardened to achieve the reduction of approximately 80 percent of wildfire risk referenced above? d) If the answer to part (c) above is yes, what is the minimum number of circuit miles of hardening needed to achieve the reduction of 80 percent of wildfire risk? e) Has SDG&E analyzed what percentage of risk reduction would be sufficient for its system to be deemed safe? f) If the answer to part (e) above is yes, please describe the findings of your analysis. g) As a long-term goal, what is the minimum percentage of risk reduction (from the level at the beginning of 2023) that SDG&E considers necessary? | SDG&E objects to the request on the grounds set forth in General Objections Nos. 1, 2, 3, 5, 7, and and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) SDG&E prepared its analysis of various wildfire mitigation scenarios while developing its first three-year Wildfire Mitigation Plan in response to the catastrophic wildfires of 2017-2018 and the passage of SB 901 and AB 1054. Based upon the data available at the time and its analysis, SDG&E ultimately opted for a risk mitigation and hardening strategy that reflected the inflection point between maximizing potential risk reduction while avoiding estimated exponential cost increases. SDG&E’s wildfire mitigation efforts are continually reassessed based upon revisions to regulatory requirements, realized cost efficiencies and new technologies, and stakeholder input through the wildfire mitigation plan process. Based on available information, SDG&E continues to pursue an overall approximate 80% reduction of wildfire risk through infrastructure hardening to promote community safety, increase reliability, and mitigate against PSPS impacts. b) The estimated mileage to reach 80% wildfire risk mitigation is 1,500 miles of undergrounding and 370 miles of covered conductor. c) Please reference response B d) Please reference response B. WiNGS-Planning optimizes the mitigation selection for wildfire risk reduction based on risk spend efficiency methodology summarized in WMP. e) SDG&E strives to have zero catastrophic wildfires associated with electric utility infrastructure. As previously noted and described in its WMP submission, SDG&E has focused on an 80% risk reduction through its grid hardening efforts to reasonably balance risk mitigation and cost. This risk mitigation may be supplemented by other risk mitigations, including but not limited to resiliency programs, vegetation management, grid operations protocols, and asset inspections as described in SDG&E’s WMP submission. f) N/A g) Please reference response e. | Aaron Louie | 2023-04-10 | 2023-04-19 | 2023-04-19 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-10.pdf | 0 | No | 7.2.2 | 7.2.2 Anticipated Risk Reduction Page 120 | 7.2.2.1 | 7.2.2.1 Projected Overall Risk Reduction Page 120
96 | CalPA | 2023-10 | CalPA-2023-10 | 10 | CalPA-2023-10.10 | SDG&E states on p. 155 of its 2023 WMP regarding the Strategic Undergrounding Program, Installations in the HFTD remain challenging due to difficult terrain, environmental constraints, permitting timelines, and acquisition of easements and land rights. Facilitating productive engagement with stakeholders in the telecommunication field will help streamline resources and obtain more support for undergrounding efforts. a) Please explain why SDG&E is not considering covered conductors for the areas identified in the quote above. b) Do covered conductor installations face the same challenges as those identified above? c) In 2021-2022, have there been instances where SDG&E planned a strategic undergrounding project, but found undergrounding to be infeasible due to the challenges described in the quote above, and therefore switched to installing covered conductor? Please explain your response, including the decision-making process to switch to installing covered conductor or not. d) Please identify an example of such a project in part (c) and provide a narrative of the decision-making process. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2 and 3. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) If WiNGS Planning recommends undergrounding, the segments are scoped with that mitigation effort. However, if a viable route is not identified or other limitations outside of SDG&E’s control are found, installing covered conductor is considered. b) Yes, installation of covered conductor can face the same challenges. c) Yes, all of the challenges stated continue to persist. There have been instances where SDG&E switched plans from undergrounding to installing covered conductor due to community opposition where residents refused to give SDG&E easements unless the telecommunication, in this case AT&T, committed to undergrounding its overhead facilities with SDG&E’s Strategic Undergrounding project. SDG&E had reached out to AT&T multiple times with their management and leadership of the community to address the issue as well as met with the community planning group and community leaders that SDG&E cannot force another utility to underground but has done what it can. AT&T does not have the same urgency to underground in relation to wildfire safety and informed SDG&E that they do not have a financial mechanism to support the undergrounding efforts in the back country at this time. d) The community of Sherilton Valley on C79 is an example of an undergrounding project where SDG&E switched to installing covered conductor due to the reason explained in part c above. C79 is one of the most frequently deenergized circuits due to PSPS. SDG&E evaluated feasibility of covered conductor as an alternative hardening mitigation and determined that it is feasible and will require 3-4 easements to support hardening the line to advance wildfire safety and reduce the PSPS impacts during adverse weather conditions. | Aaron Louie | 2023-04-10 | 2023-04-14 | 2023-04-14 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-10.pdf | 0 | No | 8.1.2.2 | 8.1.2.2 Undergrounding of Electric Lines and/or Equipment Page 152 | 8.1.2.2.5 | 8.1.2.2.5 Updates to the Activity Page 153
97 | CalPA | 2023-10 | CalPA-2023-10 | 11 | CalPA-2023-10.11 | SDG&E states on p. 405 of its 2023 WMP regarding undergrounding of its frequently de-energized circuits, To date, SDG&E has completed 68.16 miles of undergrounding and plans to underground 178.02 miles by 2025 and 393.1 miles by 2032. Two of the fifteen frequently de-energized circuits will be completely undergrounded within 10 years. a) Please identify by circuit ID (according to Table 9-2: Frequently De-energized circuits in Appendix F) which two of the fifteen frequently de-energized circuits will be completely undergrounded within 10 years as referenced above? b) Please explain SDG&E’s decision-making process, in choosing the above-mentioned two circuits that will be completely undergrounded first within 10 years. c) Does SDG&E have a ranking or schedule of when its frequently de-energized circuits will be completely hardened? d) If the answer to part (c) above is no, how will SDG&E determine which frequently de-energized circuits to complete next? e) For the above-mentioned two frequently de-energized circuits that will be completed within 10 years, what is the total circuit mile length that will be undergrounded? f) How many customers receive service on the two circuits identified above? g) Does SDG&E have an estimate for the annual number of customer minutes of service interruption that will be avoided as a result of undergrounding the two circuits discussed above? h) How does SDG&E plan to mitigate PSPS impacts on the above-mentioned remaining 13 frequently de-energized circuits? i) Does SDG&E plan to completely underground or otherwise harden the above-mentioned remaining 13 frequently de-energized circuits? If so, what is SDG&E’s planned timeline for this work? | a) As mentioned in the column “Measure taken, or planned to be taken, to reduce the need for an impact of future PSPS of circuit” of Table 9-2: Frequently De-energized Circuits in Appendix F of the 2023-2025 Wildfire Mitigation Plan, circuits 358 and 909 are in scope to be completely undergrounded by 2032 and 2026, respectively. b) The decision-making process for prioritizing and implementing mitigation initiatives for these circuits and all other circuits is described in Section 7.1.4.2.4 of the 2023-2025 WMP. c) SDG&E has developed preliminary work schedules that are reflected in the column “Measure taken, or planned to be taken, to reduce the need for an impact of future PSPS of circuit” of Table 9-2: Frequently De-energized Circuits in Appendix F of the 2023-2025 Wildfire Mitigation Plan. Construction schedules beyond 2025 will be developed based on the risk ranking of the segment, and in consideration of permitting, customer, and other challenges detailed elsewhere in the WMP. d) The decision-making process for prioritizing and implementing mitigation initiatives for these circuits and all other circuits is described in Section 7.1.4.2.4 of the 2023-2025 WMP. This includes outputs from the WiNGS-Planning model. e) As mentioned in the column “Measure taken, or planned to be taken, to reduce the need for an impact of future PSPS of circuit” of Table 9-2: Frequently De-energized Circuits in Appendix F of the 2023-2025 Wildfire Mitigation Plan, the total circuit mile length that will be undergrounded is 21.9 miles for circuit 358 and 35 miles for circuit 909. Once all undergrounding work is completed, the total circuit mile length is estimated to be 36.5 miles for circuit 358 and 37 miles for circuit 909. f) As mentioned in the column “Number of Customers Served by Circuit” of Table 9-2: Frequently De-energized Circuits in Appendix F of the 2023-2025 Wildfire Mitigation Plan, circuit 358 currently serves 1,153 customers and circuit 909 currently serves 423 customers. g) No, SDG&E does not have an estimate for the annual number of customer minutes of service interruption that will be avoided at a circuit level. However, SDG&E anticipates that the PSPS risk will be eliminated once all undergrounding work is completed and that the annual number of customer minutes of service interruption due to PSPS will be zero for circuits 358 and 909. h) In addition to the hardening and impact mitigation efforts listed in the column “Measure taken, or planned to be taken, to reduce the need for an impact of future PSPS of circuit” of Table 9-2: Frequently De-energized Circuits in Appendix F of the 2023-2025 Wildfire Mitigation Plan, SDG&E will continue to target customers on the frequently de-energized circuits for our backup resiliency programs (Standby Power Program, Generator Grant Program, and Generator Assistance Program). The Emergency Backup Generator Program is a reserve of backup batteries established specifically for expedited delivery during active PSPS events, which come pre-charged and can be delivered within 1-4 hours of eligible requests. Also available to the public during a PSPS event are SDG&E’s Community Resource Centers (CRCs), where customers impacted by active PSPS events can receive additional resiliency items and services (device charging, water/ice, snacks, AFN Go Kits, real-time event updates and information, wi-fi access, restrooms, etc). Additionally, mobile battery solutions are, and will continue to be, deployed to create temporary microgrid solutions to support communities as well as CRCs. Specifically for the AFN community impacted by PSPS de-energizations, SDG&E partners with the San Diego Food Bank, Feeding America, Meals on Wheels and other local food partners to provide food resources, Facilitating Access to Coordinated Transportation (FACT) to provide accessible transportation, The Salvation Army to provide no-cost hotel stays, and other service programs to perform in-home wellness checks. SDG&E also partners with 211 San Diego and 211 Orange County to connect individuals with services directly provided by partners contracted with SDG&E, as well as more than 1,000 regional Community Business Organizations (CBOs) who provide services. These services are available to all customers experiencing a PSPS de-energization and are not specific to the remaining 13 frequently de-energized circuits. For more detailed information on services provided to mitigate PSPS impacts, please see the AFN Plan in Appendix G of SDG&E’s 2023-2025 Wildfire Mitigation Plan. i) SDG&E will underground, install covered conductor, or retain traditionally hardened infrastructure on these frequently de-energized circuits in accordance with the recommendations in WiNGS-Planning and consistent with SME review. The hardening plans are described in in the column “Measure taken, or planned to be taken, to reduce the need for an impact of future PSPS of circuit” of Table 9-2: Frequently De-energized Circuits in Appendix F of the 2023-2025 Wildfire Mitigation Plan | Aaron Louie | 2023-04-10 | 2023-04-19 | 2023-04-19 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-10.pdf | 0 | No | 9 | 9 PUBLIC SAFETY POWER SHUTOFF Page 407 | 9.1.2 | 9.1.2 Identification of Frequently De-energized Circuits Page 408
98 | CalPA | 2023-10 | CalPA-2023-10 | 12 | CalPA-2023-10.12 | Referring to the column titled “Measure taken, or planned to be taken, to reduce the need for and impact of future PSPS of circuit,” within OEIS Table 9-2: Frequently De-energized circuits and the values SDG&E presents as “miles in scope to be completed by 2025 and 2032”: a) Are the reported values the total length of the circuit segment or the minimum length needed to be undergrounded for SDG&E to reduce the need of a future PSPS event along the circuit segment? b) How did SDG&E determine the miles in scope for each circuit? | a) The reported values are the total underground mileage planned for the circuit. Through these undergrounding efforts, the need for future PSPS is reduced by eliminating overhead exposure where wind speeds are often high. b) The miles are recommended by the WiNGS-Planning Model, using a cost-benefit approach to select circuit-segments for mitigations prioritization. | Aaron Louie | 2023-04-10 | 2023-04-14 | 2023-04-14 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-10.pdf |  | No | 9.1.2 | 9.1.2 Identification of Frequently De-energized Circuits Page 408 | Table 9-2 | Table 9-2: Frequently De-energized Circuits* 409
99 | MGRA | 2023-02 | MGRA-2023-02 | 1 | MGRA-2023-02.1 | Regarding the Advance Radio Frequency Sensors (ARFS) that “officially kicked off in 2022 after completing a 2 year demonstration” (p. 9): a. Provide technical documentation on the ARFS. b. Provide results of internal testing that led to the conclusion that the demonstration was successful and merits further development. c. Please provide best estimates as to the risk reduction that this technology provides for an instrumented circuit. d. Please provide 3 and 10 year estimations for deployment of this technology, including: a) Percent of HFRA covered by the technology, b) Percent of non-UG HFRA covered by the technology, c) Estimates of total fraction of risk mitigated in the HFRA. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2 and 8. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a. ARFS use radio frequency monitoring of partial discharge from primary conductors to find, replace, and/or repair damaged components before they ultimately fail. Sensors are installed for each phase at 4-km intervals along a circuit extending from just outside the substation to the end of its furthest branches. Data is collected every second and backhauled on commercial cell communication networks to web servers. Software analysis eliminates spurious signals and isolates signals which are generated by the electrical facilities. Comparing the timing of the arrival of the signals at two adjacent installations (nodes) allows the location of the equipment generating the signal to be determined within 10 meters on the path between the nodes. The developer analyzes the data and provides monthly reports showing low-medium-high risk ratings for each structure on the path, allowing targeted inspections of the facilities to find the damaged equipment generating the signal. ARFS are a proprietary solution procured from IND.t, technical documentation for these sensors may be referenced on https://ind-technology.com/ b. The following items are examples of damage found as a result of Early Fault Detection (EFD) technology: i. Broken ceramic insulator found and replaced that was not identified during routine patrols. ii. Burned insulator found and replaced. iii. Multiple wire splices with internal partial discharge found and replaced. iv. Damaged insulator leaking to crossarm found and replaced. v. Bird nest on buck pole found and removed. vi. Bird-caged jumper found and replaced. vii. Damaged conductor, loose (not broken) strand, deemed no structural damage by QEW. viii. Bird-caged conductor found that was not identified during routine patrols; deemed no structural damage by QEW. ix. Animal damage to dead-end insulator found and replaced. x. Multiple instances of cosmetic wire slap damage to conductor; deemed no structural damage by electric troubleshooter. c. Below is the risk reduction estimation for Early Fault Detection as presented in SDG&E’s 2023-2025 WMP in Section 8.1.2.8.2 Early Fault Detection. d. 3- and 10-year estimations for deployment of this technology are as follows: a) For years 2023-2025, it is estimated that 17% of the HFTD will be enabled with EFD technology, and 36% enabled over the next ten years. b) The EFD program primarily focuses on overhead conductors. If the circuit contains a mix of OH and UG conductors a small percentage of UG conductors may be enabled. For years 2023-2025 it is estimated 16% of EFD deployments will cover non-UG HFTD circuits. The ten-year estimated total percentage is approximately 34%. c) Refer to table in response C above for estimate of the total fraction of risk mitigated in the HFTD. | Joseph Mitchell | 2023-04-17 | 2023-04-20 | 2023-04-20 | https://www.sdge.com/sites/default/files/regulatory/MGRA-2023-02.pdf | 0 | No | 1.2.3 | 1.2.3 Plan Objectives Page 9 | N/A | N/A
100 | MGRA | 2023-02 | MGRA-2023-02 | 2 | MGRA-2023-02.2 | In OEIS Table 601: Summary of Risk Models, what are: a. Maximum buildings destroyed, b. Maximum acres affected per segment, c. Max wind gust (specifically over which period(s)), d. Wildfire adjustment factor, including algorithm/code to compute it. | a. For WiNGS Planning, max ignition simulation 100th percentile buildings destroyed tied to a segment. This comes as an input from the Technosyla WRRM model b. For WiNGS Planning, max ignition simulation 100th percentile acres burned tied to a segment. This comes as an input from the Technosyla WRRM model c. For WiNGS Planning, maximum wind gust recorded gust at weather station associated to segment. Period is over entire weather history for the given segment’s associated weather station. d. Ignition adjustment factor that converts the circuit-segment ignition rate to wildfire rate. Where Wildfire Frequency is the frequency in years of expected wildfires occurring. | Joseph Mitchell | 2023-04-17 | 2023-04-20 | 2023-04-20 | https://www.sdge.com/sites/default/files/regulatory/MGRA-2023-02.pdf | 0 | No | 6.1.2 | 6.1.2 Summary of Risk Models Page 54 | N/A | N/A
101 | MGRA | 2023-02 | MGRA-2023-02 | 3 | MGRA-2023-02.3 | Regarding the Wind Gust Annual ignition rate (p. 68), a. Over what period of time is the wind gust annual rate recorded? b. Are wind gusts in this model restricted to those occurring during fire weather events (Santa Ana), or year round? c. What facts, analysis, data, or references does SDG&E use to assume a baseline of “one catastrophic event every 15 years”? (p. 80) | a. Period is over entire weather history for the given segment’s associated weather station b. Year round. c. The analysis behind the assumption are detailed and can be referenced in SDGE’s 2019 Risk Assessment Mitigation Phase (Chapter SDG&E-1), Wildfires Involving SDG&E Equipment, Section IV ‘Risk Quantification’, Sub-section B ‘Source of Input’. | Joseph Mitchell | 2023-04-17 | 2023-04-20 | 2023-04-20 | https://www.sdge.com/sites/default/files/regulatory/MGRA-2023-02.pdf | 0 | No | 6.2.2 | 6.2.2 Risk and Risk Components Calculation Page 64 | 6.2.2.1 | 6.2.2.1 Likelihood Page 68
102 | MGRA | 2023-02 | MGRA-2023-02 | 4 | MGRA-2023-02.4 | For SDG&E’s calculation of Number of Serious Injuries and Fatalities (SIFs) perstructure destroyed (p. 73), what data set does SDG&E use to arrive at this number, and does it include territories outside of SDG&E’s service area? | SDG&E estimates the Number of Serious Injuries and Fatalities (SIFs) per structure destroyed based on CALFIRE dataset (2010-2020) for all of California including fires outside of SDG&E’s service territory. Reference: https://www.fire.ca.gov/incidents/ | Joseph Mitchell | 2023-04-17 | 2023-04-20 | 2023-04-20 | https://www.sdge.com/sites/default/files/regulatory/MGRA-2023-02.pdf | 0 | No | 6.2.3 | 6.2.3 Key Assumptions and Limitations Page 73 | N/A | N/A
103 | MGRA | 2023-02 | MGRA-2023-02 | 5 | MGRA-2023-02.5 | In its climate change modeling, SDG&E uses a “Wildfire frequency adjustment to ignition rate based on the effect that climate change has on wildfire frequency,” and that this is: “Based on Monte Carlo analysis, not standard climate change scenarios.” Please provide a description, the documentation and workpapers leading to SDG&E’s Monte-Carlo based climate change scenarios. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 3, and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: As part of the calibration process for the ignition rate, the WiNGS-Planning model is adjusted to account for future climate change scenarios. SDG&E's "Top-down" Enterprise Risk model incorporates Climate Change impacts by simulating numerous scenarios of the potential effect of extreme weather conditions. SDG&E currently assumes a triangular distribution to increase the likelihood of ignitions in its service territory, where distribution parameters are Subject Matter Estimates based on the references listed below. SDG&E is currently working with industry experts, academia, government agencies, and other stakeholders to better understand and quantify the impact of Climate Change in its Wildfire and PSPS risk models. SDG&E will update its modeling assumptions based on the knowledge gained and feedback received during these collaborations. References: - https://www.energy.ca.gov/sites/default/files/2019-11/Statewide_Reports-SUM-CCCA4-2018-013_Statewide_Summary_Report_ADA.pdf - https://www.energy.ca.gov/sites/default/files/2019-11/Projections_CCCA4-CEC-2018-014_ADA.pdf - https://iopscience.iop.org/article/10.1088/1748-9326/ab83a7#erlab83a7s3 - https://amir.eng.uci.edu/publications/20_ERL_SoCal_Fire.pdf | Joseph Mitchell | 2023-04-17 | 2023-04-20 | 2023-04-20 | https://www.sdge.com/sites/default/files/regulatory/MGRA-2023-02.pdf | 0 | No | 6.2.3 | 6.2.3 Key Assumptions and Limitations Page 73 | N/A | N/A
104 | MGRA | 2023-02 | MGRA-2023-02 | 6 | MGRA-2023-02.6 | Please provide the GIS data set used showing categorized circuit risk in Figure 6- 12, p. 83. If this has already been provided in another form by SDG&E please direct us to the correct source. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: The GIS data displayed in Figure 6-12 is in flux and from an application that is in development using non-production GIS data. A production application is expected within the year with solidified data pipelines. Geospatial data of the WiNGS Planning risk scores is available upon request. | Joseph Mitchell | 2023-04-17 | 2023-04-20 | 2023-04-20 | https://www.sdge.com/sites/default/files/regulatory/MGRA-2023-02.pdf | 0 | No | 6.4.1 | 6.4.1 Top Risk Areas within the HFRA Page 81 | 6.4.1.1 | 6.4.1.1 Geospatial Maps of Top-Risk Areas within the HFRA Page 83
105 | MGRA | 2023-02 | MGRA-2023-02 | 7 | MGRA-2023-02.7 | For the table OEIS Table 6-5, the summary of Top-Risk Circuits, Segments, or Spans, please provide a full table containing all circuits in the HFRA in Excel spreadsheet format and showing risk ranking, segment ID, Overall Wildfire and PSPS Risk Score, Wildfire Risk Score, and PSPS Risk Score. | See attachment named “table_6_5_full_table_Question 7” | Joseph Mitchell | 2023-04-17 | 2023-04-20 | 2023-04-20 | https://www.sdge.com/sites/default/files/regulatory/MGRA-2023-02.pdf https://www.sdge.com/sites/default/files/regulatory/MGRA-2023-02%20Attachment%20Q7.xlsx | 1 | No | 6.2.2 | 6.2.2 Risk and Risk Components Calculation Page 64 | 6.2.2.1 | 6.2.2.1 Likelihood Page 68
106 | CalPA | 2023-11 | CalPA-2023-11 | 1 | CalPA-2023-11.1 | Regarding SDG&E’s SCADA Underground (UG) Switches: a) Please explain SDG&E’s operating procedure for operating a SCADA UG switch to energize and de-energize a circuit or circuit segment. b) Please provide SDG&E’s written procedures or other documentation related to your response to part (a). c) Please explain in detail SDG&E’s operating procedure, from start to finish, for the following operation: after opening a normally closed switch, the switch is returned to its normally closed position during switching. d) Please explain in detail SDG&E’s operating procedure, from start to finish, for the following operation: after closing a normally open switch, the switch is returned to its normally open position during switching. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, 8, and 10. Subject to and without waiving the foregoing objections, SDG&E responds as follows: A Distribution System Operator (DSO) in the control center sends a SCADA Command to the SCADA UG switch to either Close or Open the device, energizing or de-energizing the downstream segment. | Aaron Louie | 2023-04-18 | 2023-04-21 | 2023-04-26 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-11.pdf | 0 | No | Other | SCADA Underground (UG) Switches | N/A | N/A
107 | CalPA | 2023-11 | CalPA-2023-11 | 2 | CalPA-2023-11.2 | Regarding SDG&E’s Load Break Elbows: a) Please explain SDG&E’s operating procedure for operating a load break elbow in a vault to energize or de-energize a circuit or circuit segment. b) Please provide SDG&E’s written procedures or other documentation related to your response to part (a). c) Please explain in detail SDG&E’s operating procedure, from start to finish, for the following: after opening a circuit segment via a load break elbow that is normally in a closed position, the circuit segment is returned to its normally closed position during switching. d) Please explain in detail SDG&E’s operating procedure from start to finish of the following operation: after closing a circuit segment via a load break elbow that is normally in an open position, then the circuit segment is returned to its normally open position during switching. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, 8, and 10. Subject to and without waiving the foregoing objections, SDG&E responds as follows: Qualified Electrical Workers are given the proper authorization to perform switching by opening or closing the load break elbow with an insulated Live Line Tool. This will energize or deenergize the circuit or circuit segment. | Aaron Louie | 2023-04-18 | 2023-04-21 | 2023-04-26 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-11.pdf | 0 | No | Other | Load Break Elbows | N/A | N/A
108 | CalPA | 2023-11 | CalPA-2023-11 | 3 | CalPA-2023-11.3 | Regarding SDG&E’s Junction Boxes: a) Please explain in detail SDG&E’s operating procedure for operating a junction box in a vault to energize or de-energize a circuit or circuit segment. b) Please provide SDG&E’s written procedures or other documentation related to your response to part (a). c) Please explain in detail SDG&E’s operating procedure, from start to finish, for the following operation: after closing a circuit segment via a junction box that is normally in an open position, the circuit segment is returned to its normally open position during switching. d) Please explain in detail SDG&E’s operating procedure, from start to finish, for the following operation: after closing a circuit segment via a junction box that is normally in a closed position, the circuit segment is returned to its normally closed position during switching. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, 8, and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: Not applicable. Junction boxes are not a type of sectionalizing equipment used in energizing and de-energizing circuits or circuit segments. | Aaron Louie | 2023-04-18 | 2023-04-21 | 2023-04-21 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-11.pdf | 0 | No | Other | Junction Boxes | N/A | N/A
109 | CalPA | 2023-11 | CalPA-2023-11 | 4 | CalPA-2023-11.4 | Please explain SDG&E’s selection criteria for installing the following equipment on underground circuits: a) SCADA UG switches b) Junction boxes c) Load break elbows | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, 8, and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) SCADA UG switches replace existing overhead switches that are being removed. They are also added, as needed, to limit the number of customers within one sectionalizing device. b) Junction boxes are placed based off a combination of pulling calculations, cable reel lengths, and strategic location where the cabling needs to split in multiple directions. c) Load break elbows are used on new construction. | Aaron Louie | 2023-04-18 | 2023-04-21 | 2023-04-21 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-11.pdf | 0 | No | Other | Underground Circuits | N/A | N/A
110 | CalPA | 2023-11 | CalPA-2023-11 | 5 | CalPA-2023-11.5 | Please explain SDG&E’s selection criteria for installing the following equipment on underground circuits a) Pad-mounted transformers b) Subsurface transformers | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, 8, and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) Pad-mounted transformers are the preferred installation method for transformers b) Subsurface transformers are generally avoided, and Pad-mounted transformers are preferred. | Aaron Louie | 2023-04-18 | 2023-04-21 | 2023-04-21 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-11.pdf | 0 | No | Other | Underground Circuits | N/A | N/A
111 | CalPA | 2023-11 | CalPA-2023-11 | 6 | CalPA-2023-11.6 | For each of the undergrounding projects that SDG&E has planned for 2023, please answer the following questions on each project: a) How many SCADA underground switches will be installed? b) How many overhead switches will be removed? c) How many tie switches to adjacent circuits currently exist? d) How many OH tie switches to adjacent circuits will be removed? e) How many tie switches (OH or UG) will exist when the project is complete? f) How many SCADA overhead switches will be removed? g) How many SCADA underground switches will be installed as tie points to adjacent circuits? h) How many SCADA underground switches will be installed for sectionalizing? i) How many subsurface transformers will be installed? j) How many pad-mounted transformers will be installed? k) How many vaults will be installed? l) How many junction boxes will be installed? m) How many junction boxes will be installed for sectionalizing? n) How many junction boxes will be installed as tie points to adjacent circuits? o) How many load break elbows will be installed? p) How many load break elbows will be installed for sectionalizing? q) How many load break elbows will be installed as tie points to adjacent circuits? r) How many handholes will be installed? s) How many risers will be installed? | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) 2 b) 5 c) 1 d) 1 e) 1 f) 0 g) 1 h) 0 i) 0 j) 341 k) 0 l) 40 m) 40 n) 0 o) 1671 p) 1671 q) 0 r) 948 s) 46 | Aaron Louie | 2023-04-18 | 2023-04-21 | 2023-04-26 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-11.pdf | 0 | No | Other | Undergrounding Projects | N/A | N/A
112 | CalPA | 2023-11 | CalPA-2023-11 | 7 | CalPA-2023-11.7 | For each of the undergrounding projects that SDG&E has planned for 2024, please answer the following questions on each project: a) How many SCADA underground switches will be installed in each circuit. b) How many overhead switches will be removed? c) How many tie switches to adjacent circuits currently exist? d) How many OH tie switches to adjacent circuits will be removed? e) How many tie switches (OH or UG) will exist when the project is complete? f) How many SCADA overhead switches will be removed? g) How many SCADA underground switches will be installed as tie points to adjacent circuits? h) How many SCADA underground switches will be installed for sectionalizing? i) How many subsurface transformers will be installed? j) How many pad-mounted transformers will be installed? k) How many vaults will be installed? l) How many junction boxes will be installed? m) How many junction boxes will be installed for sectionalizing? n) How many junction boxes will be installed as tie points to adjacent circuits? o) How many load break elbows will be installed? p) How many load break elbows will be installed for sectionalizing? q) How many load break elbows will be installed as tie points to adjacent circuits? r) How many handholes will be installed? s) How many risers will be installed? | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, 8 and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) 14 b) 1 c) 4 d) 2 e) 6 f) 7 g) 1 h) 12 i) 0 j) 360 k) 0 l) 78 m) 78 n) 0 o) 1326 p) 1326 q) 0 r) 976 s) 68 | Aaron Louie | 2023-04-18 | 2023-04-21 | 2023-04-26 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-11.pdf | 0 | No | Other | Undergrounding Projects | N/A | N/A
113 | CalPA | 2023-11 | CalPA-2023-11 | 8 | CalPA-2023-11.8 | On page 155 of its WMP, SDGE discusses its WMP initiative related to Distribution Pole Replacements and Reinforcements.Please provide the average, median, minimum and maximum age of poles that SDG&E: a) Replaced in 2020 b) Repaired in 2020 c) Replaced in 2021 d) Repaired in 2021 e) Replaced in 2022 f) Repaired in 2022 | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, 8, and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) Replaced in 2020 average age = 40.7 years Replaced in 2020 median age = 40.8 years Replaced in 2020 minimum age = 0.2 years Replaced in 2020 maximum age = 90.9 years b) Repaired in 2020 average age = 50 years Repaired in 2020 median age = 71 years Repaired in 2020 minimum age = 15 years Repaired in 2020 maximum age = 85 years c) Replaced in 2021 average age = 42.9 years Replaced in 2021 median age = 45 years Replaced in 2021 minimum age = 0.25 years Replaced in 2021 maximum age = 101.5 years d) Repaired in 2021 average age = 50.5 years Repaired in 2021 median age = 49 years Repaired in 2021 minimum age = 13 years Repaired in 2021 maximum age = 101 years e) Replaced in 2022 average age = 44 years Replaced in 2022 median age = 47.2 years Replaced in 2022 minimum age = 1.4 years Replaced in 2022 maximum age = 84.4 years f) Repaired in 2022 average age = 50 years Repaired in 2022 median age = 47 years Repaired in 2022 minimum age = 40 years Repaired in 2022 maximum age = 71 years | Aaron Louie | 2023-04-18 | 2023-04-21 | 2023-04-21 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-11.pdf | 0 | No | 8.1.2.3 | 8.1.2.3 Distribution Pole Replacements and Reinforcements Page 154 | 8.1.2.3.2 | 8.1.2.3.2 Overview of the Activity Page 154
114 | CalPA | 2023-11 | CalPA-2023-11 | 9 | CalPA-2023-11.9 | On page 155 of its WMP, SDGE discusses its WMP initiative related to Distribution Pole Replacements and Reinforcements. Please provide the average, median, minimum and maximum age of poles that are scheduled to be: a) Replaced in 2023 b) Repaired in 2023 c) Replaced in 2024 d) Repaired in 2024 | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, 8, and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) SDG&E cannot provide data for work currently in process for 2023 as the final engineering and design will determine whether the pole will be replaced or repaired. However, below are the statistics for poles replaced year-to-date in 2023: Average age = 39.2 years Median age = 37.8 years Minimum age = 12.9 years Maximum age = 76.3 years b) SDG&E no longer reinforces damaged poles in the HFTD. Instead, SDG&E replaces the pole. c) SDG&E cannot forecast work in 2024, as this work results from 2023 maintenance and inspections that have not yet been completed. d) SDG&E no longer reinforces damaged poles in the HFTD. Instead, SDG&E replaces the pole. | Aaron Louie | 2023-04-18 | 2023-04-21 | 2023-04-26 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-11.pdf | 0 | No | 8.1.2.3 | 8.1.2.3 Distribution Pole Replacements and Reinforcements Page 154 | 8.1.2.3.2 | 8.1.2.3.2 Overview of the Activity Page 154
115 | CalPA | 2023-11 | CalPA-2023-11 | 10 | CalPA-2023-11.10 | Regarding pp. 165-166 of your 2023 WMP where SDG&E discusses initiatives related to the Installation of System Automation Equipment, a) What are the differences amongst Early Fault Detection (EFD), Wires Down Detection (WDD) and Falling Conduction Protection (FCP)? b) Please discuss the scope and status for EFD and its effectiveness with supporting data. c) Please discuss the scope and status for WDD and its effectiveness with supporting data. d) Please discuss the scope and status of FCP and its effectiveness with supporting data. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, 8, and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) EFD aims to utilize technologies such as Advanced Radio Frequency Sensors (ARFS) and Power Quality (PQ) Meters to detect and prevent significant equipment failures in order to address fire risk while also gaining the benefits of reducing customer forced outages. Wire Down Detection (WDD) leverages our existing Advanced Metering Infrastructure (AMI) network, providing “near time” analysis of circuit events. Falling Conductor Protection (FCP) is designed to trip distribution and transmission overhead circuits before broken conductors can reach the ground energized. b) The EFD Program (WMP.1195) scope aims to utilize Advanced Radio Frequency Sensors (ARFS) and Power Quality (PQ) Meter technologies to detect and prevent significant equipment failures in order to address fire risk while also gaining the benefits of reducing customer forced outages. During the demonstration phase of the program the following items were damage found as a result of Early Fault Detection (EFD) technology: (1) Broken ceramic insulator found and replaced that was not identified during routine patrols. (2) Burned insulator found and replaced. (3) Multiple wire splices with internal partial discharge found and replaced. (4) Damaged insulator leaking to crossarm found and replaced. (5) Bird nest found and removed. (6) Bird-caged jumper found and replaced. (7) Damaged conductor, loose (not broken) strand, deemed no structural damage by QEW. (8) Bird-caged conductor found that was not identified during routine patrols; deemed no structural damage by QEW. (9) Animal damage to dead-end insulator found and replaced. (10) Multiple instances of cosmetic wire slap damage to conductor; deemed no structural damage by electric troubleshooter. SDG&E considers the damage discovered as supportive of the efficacy of the system as designed and capable of detecting electrical components that pose a potential for risk. c) The scope of the Wire Down Detection (WDD) demonstration project was to use our existing AMI data to detect wire down in distribution networks. Preliminary analysis of WDD data showed promising results and the advanced analytics developed as part of this project demonstrated energized downed conductors and single-phase faults can be identified in near real time. d) FCP scope is a specific technology deployed as part of the overarching Advanced Protection Program (APP) as detailed in section 8.1.2.8.1 of our 2023-2025 WMP. The scope of Falling Conductor Protection (FCP) is to deploy sectionalizing devices such as reclosers, line monitoring sensors, and supporting network communication devices. FCP is designed to trip distribution and transmission overhead circuits before broken energized conductors can reach the ground. SDG&E successfully detected a broken conductor which occurred on a recently enabled FCP circuit in October of 2022. On October 29, 2022, SDG&E responded to reports of a wiredown. Upon arrival, it was confirmed there was a wire down and repairs were needed to restore the circuit to normal configuration. Upon investigation of FCP event records, it was discovered that the SDG&E FCP scheme on the circuit successfully detected the broken conductor. The scheme was still in test mode at the time and did not act to trip the circuit segment, as SDG&E has not yet enabled full tripping mode. However, this event which demonstrates the efficacy of the system in a real world scenario. SDG&E is continuing its strategic deployment of FCP throughout the HFTD and will continue to validate real-world scenarios which improve the efficacy of the technology. | Aaron Louie | 2023-04-18 | 2023-04-21 | 2023-04-21 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-11.pdf | 0 | No | 8.1.2.8 | 8.1.2.8 Installation of System Automation Equipment Page 162 | N/A | N/A
116 | CalPA | 2023-11 | CalPA-2023-11 | 11 | CalPA-2023-11.11 | Please provide an Excel sheet listing each circuit (in its own row) that had circuit outages that occurred from 2020 to 2022 in any HFTD area. A circuit outage is when the Substation circuit breaker trips and de-energizes the entire circuit due to a fault. For each circuit with an outage, the Excel sheet should list each Circuit Outage as a row. Please provide the following additional information (in columns): a) b) ID number of the circuit affected c) The date of the outage d) Cause of outage. e) For all equipment failure outages, please state the specific type of failure (i.e.: OH transformer failure, overload, cross arms, UG transformer failure, cable failure, splice failure etc.) f) The outage duration in minutes g) The total number of customers impacted. h) If all or part of the circuit is currently undergrounded, provide the date that OH to UG conversion was completed i) If all or part of the circuit is in scope of a planned undergrounding project, the forecast completion date of the OH to UG conversion project. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 1, 2, 5, 8, and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: See attachment “CalPA-SDGE-2023WMP-11_Q11.xlsx.” | Aaron Louie | 2023-04-18 | 2023-04-21 | 2023-04-21 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-11.pdf https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-11%20Attachment%20Q11.xlsx | 1 | No | Other | HFTD circuit outages | N/A | N/A
117 | CalPA | 2023-11 | CalPA-2023-11 | 12 | CalPA-2023-11.12 | Regarding SDG&E’s Average Peak Load for UG Projects. For the purposes of this question, if any portion of a circuit was or will be undergrounded as part of an OH to UG conversion project, the circuit should be included: a) Provide the average peak load to circuit ampacity in percent for 2017 through 2019 for the circuits with OH to UG conversion completed in 2020. b) Provide the average peak load to circuit ampacity in percent for 2018 through 2020 for the circuits with OH to UG conversion completed in 2021. c) Provide the average peak load to circuit ampacity in percent for 2019 through 2021 for the circuits with OH to UG conversion completed in 2022. d) Provide the average peak load to circuit ampacity in percent for 2020 through 2022 for the circuits that will be undergrounded in 2023. e) Provide average peak load to circuit ampacity in percent for 2020 through 2022 for the circuits that will be undergrounded in 2024. f) Provide the average peak load to circuit ampacity in percent for 2020 through 2022 for all adjacent circuits to the circuits that have OH to UG conversion projects in 2023. g) Provide the average peak load to circuit ampacity in percent for 2020 through 2022 for all adjacent circuits to the circuits that have OH to UG conversion projects in 2024. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, 8, 9 and 10. Subject to and without waiving the foregoing objections, SDG&E responds as follows: Please see “CONFIDENTIAL Question 12.zip.” | Aaron Louie | 2023-04-18 | 2023-04-21 | 2023-04-26 | Confidential | 1 | Yes | Other | Average Peak Load for UG Projects | N/A | N/A
118 | CalPA | 2023-12 | CalPA-2023-12 | 1 | CalPA-2023-12.1 | SDG&E’s response to question 2(c) of data request CalAdvocates-SDGE-2023WMP-07 discusses a “Vegetation Tree Contact Risk Model with the San Diego Supercomputing Center.” SDG&E’s response to question 3 of data request CalAdvocates-SDGE-2023WMP-07 discusses “a predictive model to prioritize inspection schedules” that was developed by Logic 20/20. a) Are the two models discussed above the same model? b) If the answer to part (a) is “no”, please describe the differences between the two models. | a) No. The two models discussed above are different. b) Vegetation Tree Contact Risk Model with the San Diego Supercomputing Center: The goal of this model is to predict the likelihood of tree-contact caused primary outages by leveraging tree variables collected during vegetation operational activities. This approach is meant to inform vegetation outage risk based on forecasted weather conditions. Thus, the positive observations used to train the predictive model are outage events caused by trees. The model is trained and tested to predict the likelihood of an inventory tree that might cause an outage given the tree related independent variables including location and weather conditions. The vegetation priority condition model with Logic 20/20: The goal of this model is to predict the likelihood a tree might be identified as a memo (priority) or reliability (hazard) tree by leveraging similar variables collected during vegetation operational activities including location and weather conditions. This approach is to provide data points that can assist operational activities, such as inspections and tree trim. Thus, the positive observations used to train the model are the inventory trees that had such conditions in the past. The model is trained and tested to predict the likelihood an inventory tree might have such conditions in the next cycle. Both teams are currently exploring new variables and methods that can improve the performance of the first iteration of the model. | Aaron Louie | 2023-04-24 | 2023-04-27 | 2023-04-27 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-12.pdf | 0 | No | Other | CalAdvocates-SDGE-2023WMP-07 | N/A | N/A
119 | CalPA | 2023-12 | CalPA-2023-12 | 2 | CalPA-2023-12.2 | SDG&E states in response to Question 11(a) of data request CalAdvocates-SDGE-2023WMP-07, “In 2023, SDG&E is evaluating the methods and efforts to process the remaining circuits in the HFTD so that LiDAR data can be integrated into risk modeling.” a) When does SDG&E expect to complete the abovementioned evaluation of methods and efforts? b) When does SDG&E expect to complete the abovementioned processing of remaining circuits in the HFTD? c) When does SDG&E expect to integrate LiDAR data into risk modeling per the above? | SDG&E objects to the request on the grounds set forth in General Objection Nos. 2, 3, and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) SDG&E’s partner, Sharper Shape, has completed the LiDAR flights in 2022. To identify the trees with strike potential, the imagery data points in HFTD were processed and completed in 2022, and SDG&E is working with another vendor, Logic20/20, to evaluate and validate codes of this output. Field validation is expected to occur in Q2, 2023. One other user case of the LiDAR imagery data points identified in 2022 was to calculate the tree density data variable. This use case was conducted as a proof of concept, and the cloud data points from 10 HFTD circuits were processed in 2022. SDG&E is also working with Logic20/20 to evaluate the efforts and use cases for processing the rest of the HFTD circuits for generating the tree density data variable. This is expected to be completed by Q4, 2023. b) This timeframe is yet to be determined. c) Based on the first iteration of the tree-condition predictive model, after integrating the data variable of tree-strike potential, the preliminary results show that this data variable does not have a significant improvement on the performance of the model. More iterations are needed. However, this data variable is critical for situational awareness. Other use cases of this data output are under evaluation, and the final time frame is yet to be determined. | Aaron Louie | 2023-04-24 | 2023-04-27 | 2023-04-27 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-12.pdf | 0 | No | Other | CalAdvocates-SDGE-2023WMP-07 | N/A | N/A
120 | CalPA | 2023-12 | CalPA-2023-12 | 3 | CalPA-2023-12.3 | SDG&E states in response to Question 11(b) of data request CalAdvocates-SDGE-2023WMP-07: SDG&E is exploring the use of satellite imagery to assess the power of satellite data to inform near-real time risk, planning, monitoring, and operations across the entire service territory with preliminary use cases in vegetation encroachment, tree-strike, and change detection (e.g., per-pole and per-span risk). This proof of concept will explore the potential for a one-stop-shop for multiple Enterprise use cases with state-of-the-art, cost-effective, feasible, and scalable satellite data and workflows. a) When would SDG&E anticipate developing the abovementioned “one-stop-shop”? b) Please list and describe the “multiple Enterprise use cases” mentioned above. c) Please describe the “satellite data and workflows” mentioned above. | SDG&E objects to the request on the grounds set forth in General Objection Nos. 2, 3, and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) SDG&E is currently conducting a proof of concept for the use cases of satellite imagery and features. The prototype is anticipated to be completed in Q2, 2022 and will ingest, store, visualize and analyze the satellite data. Compared to LiDAR data, current satellite data has some value limitations, such as radial clearance. The accuracy of the satellite data output, such as predicted tree height, is yet to be evaluated. Field validation is expected to occur in Q2, 2023. Thus, final implementation of these data points is yet to be determined. Decisions on investment & scaling into production will be determined post-prototype. b) • Vegetation Encroachment – ~35,000 high priority poles as per PRC 4292 that require 10ft radial clearance down to bare soil which can be identified with Satellite imagery & data. • Fuels Modification Program – 50ft+ from base of pole will be captured and analyzed to identify how much vegetation is growing in the surrounding areas. This will help the team and program understand regional vegetation and can further inform the Fuels Modification Program on prioritization & customer safety. • Tree-Strike Potential/Identification – Although Satellite can’t measure radial clearance within 4ft (as per PRC 4293), it can still be utilized to infer tree height through models, estimate Tree-Strikes, and provide a count of those trees to further inform and update data in the tree-strike inventory. • Change Detection (NDVI) – Change detection will be run on the 3 use cases listed above. • Pre & Post Wildfire Season near time captures for first 3 use cases. This can be utilized by the EOC during activations. • Customer Electrification Attributes – Satellite can be leveraged to gain a better understanding of customer electrification (EVs, solar panels, etc.) c) Satellite imagery/data is tasked (from Planet /AWS) and sent to Sempra’s Cloud environment. In the AWS Cloud environment images/data are stored, machine learning models and insights are created (in SageMaker) and visualized through a User Interface. The data, both in raw form and data products, is then made available in the DataMesh to be consumed by other groups throughout the organization. This data can feed risk models, field applications, etc., and can be consumed to be utilized for further machine learning models and insights. | Aaron Louie | 2023-04-24 | 2023-04-27 | 2023-04-27 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-12.pdf | 0 | No | Other | CalAdvocates-SDGE-2023WMP-07 | N/A | N/A
121 | CalPA | 2023-12 | CalPA-2023-12 | 4 | CalPA-2023-12.4 | SDG&E states in response to question 2(a) of data request CalAdvocates-SDGE-2023WMP-08 that “a compressed timeframe to complete the patrols in the entire HFTD before September 1 poses challenges. The new off-cycle patrol is an 8-month schedule based on the findings from the Logic 20/20 model and will require resource allocation adjustments.” a) What types of resources, referenced in the quote above, need adjusting (e.g., dollars, labor, etc.)? b) Please describe the nature of the abovementioned adjustments. c) When does SDG&E expect to complete the abovementioned adjustments? d) Will the abovementioned “resource allocation adjustments” lead SDG&E to shift resources away from other initiatives or activities? e) If the answer to the previous part is “yes,” please identify the initiatives/activities from which SDG&E will move resources and identify the resources involved. | SDG&E objects to the request on the grounds set forth in General Objection Nos. 2, 3 and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) Resources here refers to contractor labor; the number of inspectors needed to complete the off-cycle HFTD patrols on schedule. b) The adjustments include assigning contracted pre-inspectors from a routine-scheduled VMA activity to an off-cycle VMA patrol. c) The adjustments are made monthly when the off-cycle VMA patrols are scheduled. d) No, pre-inspection resources are sufficient to allow flexibility for these reassignments and do not negatively impact the ability to complete other initiatives and activities. e) N/A | Aaron Louie | 2023-04-24 | 2023-04-27 | 2023-04-27 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-12.pdf | 0 | No | Other | CalAdvocates-SDGE-2023WMP-08 | N/A | N/A
122 | CalPA | 2023-12 | CalPA-2023-12 | 5 | CalPA-2023-12.5 | SDG&E states in response to question 3(e) of data request CalAdvocates-SDGE-2023WMP-08 that “SDG&E anticipates that these additional activities [pre-PSPS and adverse weather condition and event patrols] will remain ad hoc as conditions occur”. a) To clarify, does the above quote mean that there is no point at which inspection activities will become a formal program or initiative (e.g. with set criteria, a budget, targets, etc.)? b) If the answer to part (a) is “yes,” please explain why. c) If the answer to part (a) is “no,” please explain if or when any of the abovementioned “additional activities” are likely to become a formal program or initiative. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2 and 3. Subject to the foregoing objections, SDG&E responds as follows: a) These activities are addressed in SDG&E’s WMP initiative 8.2.3.8; WMP.496, wherein the overview includes, “Vegetation Management’s static, annual Master Schedule provides a consistent method for planning and managing activities. The system also enables the flexibility for emergency response to unplanned or unscheduled work before, during, and after events such as PSPS, RFW, adverse weather, or a wildfire”. Such inspections are in addition to detailed inspections and off-cycle patrols and would generally be performed by SDG&E internal Patrollers in Vegetation Management. These additional activities are contingent on situational conditions (i.e., storm, RFW, etc.) that could warrant a pre or post event patrol. Frequency of such events are unpredictable, and therefore not subject to specific plan or schedule. However, SDG&E would anticipate always having the resources to perform these ad-hoc events. b) N/A c) See a) above | Aaron Louie | 2023-04-24 | 2023-04-27 | 2023-04-27 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-12.pdf | 0 | No | Other | CalAdvocates-SDGE-2023WMP-08 | N/A | N/A
123 | CalPA | 2023-12 | CalPA-2023-12 | 6 | CalPA-2023-12.6 | Please provide the following information regarding actual and projected costs for each WMP initiative under Chapter 8.2 (Vegetation Management and Inspections). Each initiative should be a row in the table below: | SDG&E objects to the request on the grounds set forth in General Objection Nos. 5, 6 and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: Please see SDG&E’s 2023-2025 Wildfire Mitigation Plan, Table 11, WMP Non-Spatial QDR. SDG&E provides forecast and actual costs for the four (4) initiatives above. With regard to WMP.494 (Detailed Inspection) this initiative includes the activities of detailed inspections, off-cycle patrol, quality assurance, and tree trimming. The 2023 & 2024 Operating Expense reflect the current forecasting capability of isolation costs specific to the initiatives in the WMP. | Aaron Louie | 2023-04-24 | 2023-04-27 | 2023-04-27 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-12.pdf | 0 | No | 8.2 | 8.2 Vegetation Management and Inspection Page 254 | N/A | N/A
124 | CalPA | 2023-13 | CalPA-2023-13 | 1 | CalPA-2023-13.1 | SDG&E reports, on page 148 of its WMP, that work orders are projected to decrease in future years after a large current influx of inspection findings caused primarily by SDG&E’s drone inspection program. a) Why has SDG&E’s drone inspection program led to an unusually large number of new work orders, as referenced above? b) What lessons has SDG&E learned about its non-drone inspection practices in comparison to drone programs, considering that the drone program has identified many maintenance needs that had not been previously identified, including 216 emergency items? | SDG&E objects to the request on the grounds set forth in General Objections Nos. 3 and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) As discussed in SDG&E’s 2023-2025 WMP Section 8.1.1.3.1, the Drone Investigation, Assessment and Repair (DIAR) Program performed inspections on every HFTD overhead distribution structure between 2019 and 2022. As a result, SDG&E saw an increased rate of DIAR Program findings of about 25 percent compared to approximately 6 percent for ground-based inspections. In general, the drone inspections and imagery collected allowed inspectors to identify the following issues: 1. Issues visible only from above, such as hollowed out pole tops, tracking on crossarms, transformer corrosion (visible only on the lids), and loose hardware that was blocked from view if looking up. 2. Smaller issues harder to see with the naked eye or with binoculars, such as frayed wire or small chips in insulators, that are more easily visible with high resolution imagery than can be enhanced on the computer screen. 3. Issues on poles that are more difficult to access because of terrain or topography. b) Non-drone inspections mandated under GO 165 can be supplemented with risk-informed drone inspections. Drone inspections include both a ground-based inspection and an aerial inspection. Inspection teams consist of a qualified inspector and a drone pilot in an effort to capture issues identified better with a drone and those issues that are best observed from the ground. Additionally, unplanned drone inspections can be utilized for operational and/or reliability needs. | Aaron Louie | 2023-04-25 | 2023-04-28 | 2023-04-28 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-13.pdf | 0 | No | 8.1.1.3 | 8.1.1.3 Performance Metrics Page 145 | N/A | N/A
125 | CalPA | 2023-13 | CalPA-2023-13 | 2 | CalPA-2023-13.2 | SDG&E states that 216 emergency items found by the drone inspection program have been repaired and closed.4 For each of these 216 emergency repair tags, please state: a) Circuit ID number b) Circuit voltage c) The date the issue was identified d) The date it was resolved e) A description of the damage f) How the issue was addressed, if applicable | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2 and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: (a) - (e) See “DIAR Emergency Issues 2019-2022.xlsx” that provide a list of all emergency issues identified through the drone inspection program from 2019-2022. The list includes responses to question 2(a) through (e). (f) Please note that for question 2(f), the issues were addressed through a repair or mitigation of the issue described on the data resolved. No further details are readily available without pulling as-built submittals for each issue. | Aaron Louie | 2023-04-25 | 2023-04-28 | 2023-04-28 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-13.pdf https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-13%20Attachment%20Q2.zip | 1 | No | 8.1.1.3.1 | 8.1.1.3.1 Distribution Inspection Findings and Open Work Orders Page 147 | N/A | N/A
126 | CalPA | 2023-13 | CalPA-2023-13 | 3 | CalPA-2023-13.3 | On page 199 of its WMP, SDG&E states that its damage detection models are 86% accurate at detecting damaged infrastructure photographed in drone inspections. a) How do human inspectors review SDG&E’s damage detection model’s damage findings for accuracy? b) Is all footage from SDG&E’s drone inspection program reviewed by human inspectors to verify that the damage detection model did not miss any instances of infrastructure damage? c) Please detail SDG&E’s protocols for addressing a situation where human inspectors identify errors in the damage detection model’s findings. d) If the answer to part (b) is yes, how does SDG&E use instances of damage missed by the damage detection models (i.e., false negatives) or flagged as damage when they are not (i.e., false positives) to better train damage detection models? | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2 and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) SDG&E performs quality assurance reviews on all inspections completed as part of its Drone Investigation Assessment and Repair (DIAR) Program. After the Inspector completes the inspection and the results are reviewed by the supervisor, the images and findings are processed through the machine learning models in production. When a model makes a prediction, it is surfaced for review to the supervisor with the predicted damage highlighted on the image. The supervisor can then verify or reject the predicted damage. If the damage is verified, it is added to the inspection report before it is finalized. b) Yes, all images are reviewed by human inspectors. In addition, human inspectors are in the field performing ground inspections with the drone pilots taking photos of the facility. c) See response in part (a) above. If a model finding is rejected by the supervisor, it is used to improve the model for future use. If the supervisor identifies an issue through their inspection of drone imagery that the model later misses, this is also used to improve the model for future use. d) Images and inspection findings are used to build, train, and enhance damage detection models that allow Intelligent Image Processing (IIP) technology to process imagery data and improve the quality of machine learning model capabilities. | Aaron Louie | 2023-04-25 | 2023-04-28 | 2023-04-28 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-13.pdf | 0 | No | 8.1.3.7 | 8.1.3.7 Drone Assessments (WMP.552) Page 202 | N/A | N/A
127 | CalPA | 2023-13 | CalPA-2023-13 | 4 | CalPA-2023-13.4 | On page 199 of its WMP, SDG&E states that its damage detection models are 86% accurate at detecting damaged infrastructure photographed in drone inspections. a) Please state the basis of the 86% accuracy figure noted above. b) For the 14% of results that are not accurate, mentioned above, i. what percentage of these inaccurate results are false negatives? ii. what percentage of these inaccurate results are false positives? c) For purposes of estimating the accuracy of the damage detection model, how does SDG&E identify instances where the model produces a false negative result? | a) Below are the definitions used for the accuracy metric: • True Positive (TP): Poles with damage detection found by inspector (or verified by supervisor) and model • True Negatives (TN): Poles with no issue detected by model or inspector; Poles with damage written up by inspector that is not in scope of damage detection models • False Positives (FP): Poles with damage detection found by model that is rejected by supervisor • False Negatives (FN): Poles with a damage identified by inspector that is in scope of damage detection models and not found by model The below metrics were taken from DIAR Tier 2 (7/7/2021 – 12/12/2022): Total Poles = 42,804 True Positive Poles = 10,268 True Negative Poles = 26,360 False Positive Poles = 3,334 False Negative Poles = 2,842 Accuracy = (TP+TN)/(TP+TN+FP+FN) = (10268 + 26360)/(10268 + 26360 + 3334 + 2842) = 0.86 b) For the 14% of results that are not accurate, see above for definitions and total results. i. % False Negative Poles = (FN)/(TP+TN+FP+FN) = (2,842)/(10268 + 26360 + 3334 +2842) = 0.07 ii. % False Positive Poles = (FP)/(TP+TN+FP+FN) = (3,334)/(10268 + 26360 + 3334 + 2842) = 0.08 c) The damage detection models are used in a Quality Assurance capacity for the drone inspection programs. In this human + machine partnership, a Qualified Inspector first reviews the drone imagery for potential damages and then the damage detection models automatically assess the same set of images to identify damages. When a potential damage is identified by the model, it validated against the inspector’s findings and if it is an “additional” damage not identified by the inspector, it is surfaced for review by the supervisor and added to the report before it is finalized if approved by the supervisor. If a damage is written up by the inspector and is not identified by the model, this is considered a false negative result to be used for improving the model for future use. | Aaron Louie | 2023-04-25 | 2023-04-28 | 2023-04-28 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-13.pdf | 0 | No | 8.1.3.7 | 8.1.3.7 Drone Assessments (WMP.552) Page 202 | N/A | N/A
128 | CalPA | 2023-13 | CalPA-2023-13 | 5 | CalPA-2023-13.5 | Please refer to SDG&E’s reports, on page 148 of its WMP, that open work orders are expected to stabilize as the DIAR Program revisits poles that have been previously inspected by drone. a) How did SDG&E incorporate the DIAR program’s infrastructure inspection and assessment results from its beginnings in 2019 through 2022 to improve SDG&E’s model related to probability of failure (PoF) in 2023? b) State the basis of how SDG&E arrives at 2250 forecasted distribution inspection findings each year in 2023, 2024, and 2025,5 in light of the most recent data on distribution inspection findings numbering 7,367.6 c) Please provide all available analyses, workpapers, studies or reports that support your response to the previous part. d) State the basis of how SDG&E arrives at a forecast of distribution open work orders numbering 5000 in 2023, 2000 in 2024, and 2000 in 2025,7 in light of the most recent data on distribution open work orders numbering 8,865.8 e) Please provide all available analyses, workpapers, studies or reports that support your response to the previous part. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 7 and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) SDG&E DIAR program’s infrastructure inspection and assessment results are incorporated into the probability of failure (PoF) model as the statistical or machine learning models are created based on asset attributes, historical outages, and historical weather conditions. b) SDG&E forecasts 2,250 distribution drone inspection findings based on 15% of ~15,000 drone inspections performed each year between 2023-2025. This is an estimate in between the 25% currently observed through the drone inspections from 2021-2022 and the ground inspection find rate of 6%. Since SDG&E has now completed drone inspections of its entire Tier 2 and Tier 3 overhead distribution facilities from 2019-2022, it is anticipated that the find rate will decrease from 25% and trend closer to the previous find rate of 6%. With the creation of its risk-informed drone inspection approach, SDG&E anticipates a steadier find rate in the future. c) Current program efforts are being used to validate this estimate as we do not yet have sufficient statistically significant data to prepare a study or report to substantiate this 15% value. We predict that it will take 2-3 years of implementation of our risk-informed drone inspections following the completion of the entire HFTD drone inspections to validate that 15% estimate. d) The estimates of distribution open work orders was specific to drone inspection open work orders as we anticipate the closure of the majority of open work orders found by drone inspections completed in 2019-2022 by 2024 and then closure of open work orders found annually within either 6 or 12 months after the inspections have been completed. So, on average we anticipate that of the 2,250 issues estimated to be found annually, some will be completed in the same calendar year and others will carry over into the following year; hence, a steady state of approximately 2,000 open work orders associated with distribution drone inspections cycling in a 12-month period. e) As per the discussion in 5(c), this currently being studied and analyzed as we do not have statistically significant data to prepare a study or report following our completion of drone inspections across the entire HFTD in an approximate 3.5-year period (9/2019-12/2022). | Aaron Louie | 2023-04-25 | 2023-04-28 | 2023-04-28 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-13.pdf | 0 | No | 8.1.1.3.1 | 8.1.1.3.1 Distribution Inspection Findings and Open Work Orders Page 147 | N/A | N/A
129 | CalPA | 2023-13 | CalPA-2023-13 | 6 | CalPA-2023-13.6 | SDG&E reports, on page 231 of its WMP, that it has a small percentage of open work orders in HFTDs that are overdue. a) Why does SDG&E forecast having overdue open work orders in 2023? b) Why does SDG&E forecast having overdue open work orders in 2024? c) Why does SDG&E forecast having overdue open work orders in 2025? | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 3 and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a - c) SDG&E defers open work under reasonable circumstances as authorized under GO 95 Rule 18. Because these deferrals inherently remain open past their initial due date for completion, they are considered overdue. A small percentage of work is forecasted to be deferred, and thus overdue, based on historical deferrals. | Aaron Louie | 2023-04-25 | 2023-04-28 | 2023-04-28 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-13.pdf | 0 | No | 8.1.7.6 | 8.1.7.6 Aging report for work orders past due Page 233 | N/A | N/A
130 | CalPA | 2023-13 | CalPA-2023-13 | 7 | CalPA-2023-13.7 | SDG&E reports, on page 226-227 of its WMP, that its Quality Assurance and Quality Control (QA/QC) of distribution detailed inspections are 100% accurate with zero audit findings in 2022. Please state the comparable figures (number of audit findings and the accuracy rate) for detailed distribution inspections in: a) 2019 b) 2020 c) 2021 | a-c) For 2019-2021, QA/QC of detailed distribution inspections are 100% accurate with zero audit findings. Because there is a gap in time between the inspection and audit of the inspection, SDG&E does not define any variances in findings as a failure since it is not possible to determine whether the condition was present at the time of inspection. As more imagery is collected with inspections, it may be possible to provide failure information in the future. | Aaron Louie | 2023-04-25 | 2023-04-28 | 2023-04-28 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-13.pdf | 0 | No | 8.1.6 | 8.1.6 Quality Assurance and Quality Control Page 226 | 8.1.6.2 | 8.1.6.2 QA/QC of Distribution Detailed Inspections (WMP.491) Page 227
131 | CalPA | 2023-13 | CalPA-2023-13 | 8 | CalPA-2023-13.8 | Please refer to SDG&E’s reports, on page 226-227 of its WMP, that its Quality Assurance and Quality Control (QA/QC) of distribution detailed inspections are 100% accurate with no audit findings in 2022. a) Please describe the QA/QC audit process for detailed distribution inspections. b) Please provide SDG&E’s internal protocols, procedures, or checklists regarding the QA/QC audit process for detailed distribution inspections. c) SDG&E describes how construction supervisors perform a field audit of an inspector’s work to validate the results of an inspection performed. What percentage of inspections do construction supervisors validate while in the field with inspectors? d) SDG&E states that between 0.5 percent and 1.5 percent of completed inspections per inspector are randomly selected and audited. Who performs the 0.5% to 1.5% audits of inspection results? e) Why does SDG&E select 0.5% to 1.5% of inspection results to audit? Please explain the reasoning for this proportion. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 7 and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a) As stated in SDG&E’s 2023-2025 WMP Section 8.1.6.2, QA/QC of distribution detailed inspections is managed by Operations and Engineering managers. Construction supervisors perform the field audit to validate the results of an inspection performed. Annually, between 0.5 percent and 1.5 percent of completed inspections per inspector are randomly selected and audited. Discrepancies identified during an audit are documented in the system of record and training opportunities are addressed real time with inspectors. Should there be a trend in discrepancies found for any given inspector, additional training may be required. b) See “ESP 612_Quarterly Audit Standard Practice_04122017 rev.pdf.” c) Inspections are not validated by construction supervisors while in the field with inspectors. Supervisors perform QA/QC during the next quarter after the inspectors have completed their field inspection. d) Construction supervisors perform the field audit to validate the results of an inspection performed. e) 0.5-1.5% represents a reasonable sample size that provides the construction supervisor with an indication of the inspector’s performance and quality of work and provides a reasonable number of quality control inspections that can be performed by the construction supervisors within a quarter. | Aaron Louie | 2023-04-25 | 2023-04-28 | 2023-04-28 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-13.pdf https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-13%20Attachment%20Q8.zip | 1 | No | 8.1.6 | 8.1.6 Quality Assurance and Quality Control Page 226 | 8.1.6.2 | 8.1.6.2 QA/QC of Distribution Detailed Inspections (WMP.491) Page 227
132 | CalPA | 2023-13 | CalPA-2023-13 | 9 | CalPA-2023-13.9 | Please describe the QA/QC audit results in 2022 for each type of asset inspections that SDG&E performs (e.g., detailed transmission inspections, routine distribution inspections, etc.). | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 3, and 7. Subject to and without waiving the foregoing objections, SDG&E responds as follows: As stated in SDG&E’s 2023-2025 WMP, 2022 audit results for each inspection program audited are as follows: Transmission: SDG&E does not currently define or track audit results for transmission inspections. A construction supervisor will validate whether conditions identified during inspections are valid or if no further maintenance is required. Discrepancies and lessons learned as a result of transmission audits are addressed and resolved in real time during staff meetings. Distribution Detailed: Discrepancies identified during an audit are documented in the system of record and training opportunities are addressed real time with inspectors. Should there be a trend in discrepancies found for any given inspector, additional training may be required. There were no audit findings in 2022. Distribution Drone Assessments: If any discrepancies are identified, the construction supervisor will provide feedback to the inspector during regular team meetings and the inspection findings will be updated prior to finalization. Similarly, if there are any variations between the results of the machine learning model findings and the Inspector’s findings, that information will be reviewed and validated by the construction supervisor. Information will be sent back to the construction supervisor and the missed issues will be included in the inspection findings prior to finalization. Lessons learned, as well as updates to inspection requirements are also incorporated into initial and refresher training materials. Wood Pole Intrusive: A third party is contracted to perform a field audit of the 10 percent of completed inspections for both distribution and transmission structures. The audit field verifies the initial inspection results monthly. Audit findings are recorded in the wood pole inspection management system and shared with program administrators. Results are reviewed and shared at routine monthly meetings with the intrusive inspectors and their leadership. Work is reissued to intrusive inspectors when discrepancies are identified, and corrections are performed within 2 weeks of the finding. Substation Patrols: The audit program for substation patrol inspections was implemented in the later half of 2022. A construction supervisor documents completion of the audit and notes any deficiencies in the substation maintenance system of record. There were no audit findings in 2022. | Aaron Louie | 2023-04-25 | 2023-04-28 | 2023-04-28 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-13.pdf | 0 | No | 8.1.6 | 8.1.6 Quality Assurance and Quality Control Page 226 | N/A | N/A
133 | MGRA | 2023-03 | MGRA-2023-03 | 1 | MGRA-2023-03.1 | SDG&E provided as an appendix a report authored by the San Diego Computing Center, which it used as its basis for Area for Continued Improvement SDGE-22-09. a. Please provide the definition of “wind gust” used in the SDSC analysis. b. Please provide the definition of “wind speed max” used in the SDSC analysis, differentiating it from “wind gust”. c. Please provide the definition of “wind speed mean” used in the SDSC analysis. d. When SDG&E refers to “deltas between wind speed and wind gust” is it referring to delta between “wind speed max” and “wind gust” or “wind speed mean” and “wind gust”. e. Please provide a tabular or spreadsheet form of figure “Outage v/s Non-Outage wind speed max %ile - 24h buckets all time”. f. Please provide a tabular or spreadsheet form of the figure “Outage v/s Non- Outage wind gust max %ile - 24h buckets all time”. g. Please provide a tabular or spreadsheet form of the figure “Outage v/s Non- Outage wind gust mean %ile - 24h buckets all time”. h. Please provide a tabular or spreadsheet form of the figure “Outage v/s Non- Outage wind gust delta max %ile - 24h buckets all time”. i. Please provide a tabular or spreadsheet form of the figure “Outage v/s Non- Outage wind gust delta mean %ile - 24h buckets all time”. | a. Wind gust is calculated through the wind speed and the UST variable from the forecast: wind_gust = wind_speed + 7.71*UST , where the value 7.71 was Methodology section. For each hour of the day, we can calculate the “wind gust”, which is simply another variable. c. “Wind speed mean” is the average value of the wind speed in a 24h bucket. It is calculated the same way we calculated “wind speed max”, but we used the “mean” aggregation for the “wind speed mean”. Please see the complete description of the process for calculating wind speed aggregated values in the Methodology section of the attached “Wind Analysis Report for SDG&E – DISTRIBUTED – April 2023.pdf” d. Delta(wind speed, wind gust) refers to the delta between the max and mean aggregations (for each 24h bucket) of wind speed and wind gust. In other words, delta max refers to the delta between wind speed max and wind gust max, and delta mean refers to the delta between wind speed mean and wind gust mean. Please see the detailed description in the Delta (wind speed, wind gust) Analysis section of the attached “Wind Analysis Report for SDG&E – DISTRIBUTED – April 2023.pdf.” For responses e-i, please see “Wind Analysis Report – Supplemental Materials.zip.” e. See figure 3 Figure 3 - Outage wind speed max %ile - 24h buckets all time.csv & Figure 3- NonOutage wind speed max %ile - 24h buckets all time.csv f. Please see Figure 17 - Outage wind gust max %ile - 24h buckets all time.csv & Figure 17 - NonOutage wind gust max %ile - 24h buckets all time.csv g. Please see Figure 19 - Outage wind gust mean %ile - 24h buckets all time.csv & Figure19 - NonOutage wind gust mean %ile - 24h buckets all time.csv h. Please see Figure 14 - Outage wind gust delta max %ile - 24h buckets all time.csv & Figure 14 - NonOutage wind gust delta max %ile - 24h buckets all time.csv i. Please see Figure 15 - Outage wind gust delta mean %ile - 24h buckets all time.csv & Figure 15 - NonOutage wind gust delta mean %ile - 24h buckets all time.csv. Additionally, please see Please see Figure 5 - Outage wind speed mean %ile - 24h buckets all time.csv & Figure 5 - NonOutage wind speed mean %ile - 24h buckets all time.csv for outage vs non-outage wind speed mean. previously discussed with SDGE. Note that the UST variable in the WRF data is updated every hour. b. “Wind speed max” is the maximum value of the wind speed in a 24h bucket. For an hourly updated model, there are 24 values corresponding to each hour of the day. “wind speed max” corresponds to the maximum of these 24 values. Please see the complete description of the process for calculating wind speed aggregated values in the | Joseph Mitchell | 2023-04-25 | 2023-04-28 | 2023-04-28 | https://www.sdge.com/sites/default/files/regulatory/MAGRA-2023-03.pdf https://www.sdge.com/sites/default/files/regulatory/MAGRA-2023-03%20Attachment%20Q1.zip | 1 | No | 10.2.2 | 10.2.2 Feedback from Energy Safety or Other Authoritative Bodies Page 425 | N/A | N/A
134 | MGRA | 2023-03 | MGRA-2023-03 | 2 | MGRA-2023-03.2 | What would the overall system PSPS risk reduction be reduced to if the minimum threshold for de-energization was raised to: a. 60 mph b. 65 mph c. 70 mph | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 3, and 9. Further, the request calls for speculation. Subject to and without waiving the foregoing objections, SDG&E responds as follows: The PSPS probabilities are currently derived by subject matter experts using their knowledge of local terrain and weather conditions. As a result, bracketing the PSPS threshold cannot be done in an automated and timely manner at this time. Sensitivity analyses are in the WiNGS Planning roadmap available in the 2023 WMP. A programmatic method of determining the PSPS thresholds, which would allow for sensitivity analysis of the PSPS threshold effect on PSPS risk reduction, will be evaluated in conjunction with the sensitivity analyses specified in the roadmap. | Joseph Mitchell | 2023-04-25 | 2023-04-28 | 2023-04-28 | https://www.sdge.com/sites/default/files/regulatory/MAGRA-2023-03.pdf | 0 | No | 10.2.2 | 10.2.2 Feedback from Energy Safety or Other Authoritative Bodies Page 425 | N/A | N/A
135 | MGRA | 2023-03 | MGRA-2023-03 | 3 | MGRA-2023-03.3 | On page D-29, SDG&E states that it “is awaiting the final Exponent report to be completed in April 2023 prior to re-evaluating the effectiveness of its Covered Conductor Program.” a. Is the Exponent report included in SDG&E’s WMP the “final” Exponent report? b. If not, please provide the final Exponent report upon availability. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 9 and 10. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a. The Exponent report for the study being performed by SDG&E was not included in SDG&E’s WMP. b. The report is currently expected to be delivered to SDG&E by the end of May. | Joseph Mitchell | 2023-04-25 | 2023-04-28 | 2023-04-28 | https://www.sdge.com/sites/default/files/regulatory/MAGRA-2023-03.pdf | 0 | No | N/A | N/A | N/A | N/A
136 | MGRA | 2023-03 | MGRA-2023-03 | 4 | MGRA-2023-03.4 | On page D-8, SDG&E states that “SDG&E has begun collaborating with RMS, a Moody’s Analytics Company, to model and quantify the impact of long-term duration fires. SDG&E will review RMS’s outputs and will evaluate the inclusion of these outputs in the WiNGS-Planning and WiNGS-Ops models in the 2023 to 2025 WMP cycle.” When are the results of this analysis expected to be available? | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 9 and 10. Further, the request calls for speculation. Subject to and without waiving the foregoing objections, SDG&E responds as follows: SDG&E plans to evaluate the inclusion of these outputs during our 2023 to 2025 WMP cycle and intends to share the progress of the evaluation in the WMP filing each year. | Joseph Mitchell | 2023-04-25 | 2023-04-28 | 2023-04-28 | https://www.sdge.com/sites/default/files/regulatory/MAGRA-2023-03.pdf | 0 | No | N/A | N/A | N/A | N/A
137 | MGRA | 2023-03 | MGRA-2023-03 | 5 | MGRA-2023-03.5 | For Ignition Rate Reduction tables (Table 8-29, MGRA-SDGE-2023WMP-02 Response), a. when “Ignition Rates” are given are these annual ignition rates or are these ignition rates per the entire measurement period (ex. 2017-2021)? b. when “Ignitions Reduced” is given are these annual ignitions or ignitions through the entire measurement period? | a. Ignition Rates are the average yearly ignitions for the time period between 2017-2021. b. Ignitions Reduced represents the number of ignitions that are reduced during the current WMP cycle 2023-2025. | Joseph Mitchell | 2023-04-25 | 2023-04-28 | 2023-04-28 | https://www.sdge.com/sites/default/files/regulatory/MAGRA-2023-03.pdf | 0 | No | Other | MGRA-SDGE-2023WMP-02 | N/A | N/A
138 | CalPA | 2023-14 | CalPA-2023-14 | 1 | CalPA-2023-14.1 | a) Describe SDG&E’s standard process for retiring an asset from service. b) Describe how SDG&E records the retirement of an asset from service. | SDG&E objects to the request on the grounds set forth in General Objections 2, 3, 5, and 6. SDG&E’s response is limited to its WMP and related activities. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a. SDG&E’s process for retirements differs depending on whether the asset being removed is accounted for on a unit basis or on a group basis. For assets accounted for on a unit basis, a separate record is maintained for each item placed into service, each item is individually depreciated over its expected remaining service life, and retirements are processed using information specific to the retired asset. For assets accounted for on a group basis, the cost of all assets in that class are combined and depreciated over the weighted average remaining service life of all assets in that group. When assets accounted for on a group basis are retired the average unit cost for the appropriate vintage of the asset class of the asset being retired is used as the cost basis for processing the retirement. b. As outlined in CPUC Standard Practice U-4, assets accounted for on the unit basis are retired by reducing (crediting) Plant In Service (FERC 101) by the value of the asset in that account and reducing (debiting) Accumulated Depreciation (FERC 108) by the depreciation taken on that asset recorded to that account. As outlined in CPUC Standard Practice U-4, assets accounted for on a group basis are retired by reducing (crediting) Plant In Service (FERC 101) by the average unit cost for the appropriate vintage of the asset class of the asset being retired, with a corresponding reduction (debit) to Accumulated Depreciation (FERC 108). | Aaron Louie | 2023-04-26 | 2023-05-05 | 2023-05-05 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-14.pdf | 0 | No | Other | Retiring an Asset from Service | N/A | N/A
139 | CalPA | 2023-14 | CalPA-2023-14 | 2 | CalPA-2023-14.2 | a) During the period from 2020-2022, did SDG&E replace any distribution conductor as part of its WMP activities for which SDG&E had not fully recovered the original cost of the conductor? This may involve undergrounding a previously hardened line, or replacing a bare overhead line with covered conductor. b) If the answer to part (a) is yes, what was SDG&E’s practice regarding cost recovery on the unrecovered portion of the value associated with the replaced conductor? c) If the answer to part (a) is yes, please provide the number of circuit miles of such conductor that SDG&E replaced. | SDG&E objects to the request on the grounds set forth in General Objections 2, 3, 5, 6, and 9. SDG&E’s response is limited to its WMP and related activities. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a. Yes. b. Distribution conductor is accounted for on a group basis. As outlined in CPUC Standard Practice U-4, for assets accounted for on a group basis any unrecovered portion of retired assets remains in Net Property, Plant, and Equipment, which is a component of rate base. Net Property, Plant, and Equipment is recovered through the depreciation component of a utility’s revenue requirement. c. It is unduly burdensome to provide the full number of assets and circuit miles not fully depreciated and such an analysis is not relevant to SDG&E’s WMP submission. SDG&E’s answer is limited to the circuit miles of conductor that previously underwent bare wire hardening to mitigate the risk of ignition, and now may be re-hardened due to being on a circuit segment targeted for underground and/or covered conductor installation. Currently 1.75 circuit miles of hardened assets were replaced with installation of covered conductor. SDG&E is still reviewing its Strategic Undergrounding historical information to determine if any miles of undergrounding in 2020-2022 included rehardening. | Aaron Louie | 2023-04-26 | 2023-05-05 | 2023-05-05 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-14.pdf | 0 | No | Other | Cost Recovery of Conductors | N/A | N/A
140 | CalPA | 2023-14 | CalPA-2023-14 | 3 | CalPA-2023-14.3 | a) In 2022, as part of its WMP system hardening activities, did SDG&E retire from service (i.e., replace, remove, destroy, or decommission) any assets that had not been fully depreciated at the time of retirement? b) Please describe how SDG&E recorded the retirement of assets during 2022 system hardening activities. | SDG&E objects to the request on the grounds set forth in General Objections 2, 3, 5, 6, and 9. SDG&E’s response is limited to its WMP and related activities. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a. Yes. b. As outlined in CPUC Standard Practice U-4, assets accounted for on a group basis are retired by reducing (crediting) Plant In Service (FERC 101) by the average unit cost for the appropriate vintage of the asset class of the asset being retired, with a corresponding reduction (debit) to Accumulated Depreciation (FERC 108). This methodology applies to WMP system hardening activities that were retired in 2022 as these assets are accounted for on a group basis. | Aaron Louie | 2023-04-26 | 2023-05-05 | 2023-05-05 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-14.pdf | 0 | No | Other | Asset Retirement | N/A | N/A
141 | CalPA | 2023-14 | CalPA-2023-14 | 4 | CalPA-2023-14.4 | a) In 2023, as part of its WMP system hardening activities, does SDG&E intend to retire from service (i.e., replace, remove, destroy, or decommission) any assets that are not fully depreciated at the time of retirement? b) Please describe how SDG&E will record the retirement of assets during 2023 system hardening activities. | SDG&E objects to the request on the grounds set forth in General Objections 2, 3, 5, 6, and 9. SDG&E’s response is limited to its WMP and related activities. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a. Yes b. As outlined in CPUC Standard Practice U-4, assets accounted for on a group basis will be retired by reducing (crediting) Plant In Service (FERC 101) by the average unit cost for the appropriate vintage of the asset class of the asset being retired, with a corresponding reduction (debit) to Accumulated Depreciation (FERC 108). This methodology applies to WMP system hardening activities that will be retired in 2023 as these assets are accounted for on a group basis. | Aaron Louie | 2023-04-26 | 2023-05-05 | 2023-05-05 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-14.pdf | 0 | No | Other | Planned Asset Retirement | N/A | N/A
142 | CalPA | 2023-14 | CalPA-2023-14 | 5 | CalPA-2023-14.5 | What is SDG&E’s standard practice for tracking assets that are retired from service before they are fully depreciated? | SDG&E objects to the request on the grounds set forth in General Objections 2, 3, 5, 6, and 9. SDG&E’s response is limited to its WMP and related activities. Subject to and without waiving the foregoing objections, SDG&E responds as follows: As outlined in CPUC Standard Practice U-4, assets accounted for on a group basis are depreciated as a group rather than individually. In accordance with this methodology, SDG&E does not specifically track assets that are retired from service before they are fully depreciated. | Aaron Louie | 2023-04-26 | 2023-05-05 | 2023-05-05 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-14.pdf | 0 | No | Other | Asset Tracking | N/A | N/A
143 | CalPA | 2023-14 | CalPA-2023-14 | 6 | CalPA-2023-14.6 | a) If SDG&E retires from service an asset that has not been fully depreciated, does it remove the remaining undepreciated value of the asset from its rate base? b) How does SDG&E determine the remaining undepreciated value of an asset at the time the asset is retired from service? c) Please describe any scenario in which SDG&E would retire from service an asset that has not been fully depreciated, but would keep the remaining undepreciated value of the asset in its rate base. | SDG&E objects to the request on the grounds set forth in General Objections 2, 3, 5, 6, and 9. SDG&E’s response is limited to its WMP and related activities. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a. No. As outlined in CPUC Standard Practice U-4, for assets accounted for on a group basis any unrecovered portion of retired assets remains in Net Property, Plant, and Equipment, which is a component of rate base. b. As outlined in CPUC Standard Practice U-4, assets accounted for on a group basis are depreciated as a group rather than individually. In accordance with this methodology, SDG&E does not determine the remaining undepreciated value of assets that are retired from service. c. As outlined in CPUC Standard Practice U-4, assets accounted for on a group basis are retired by reducing (crediting) Plant In Service (FERC 101) by the average unit cost for the appropriate vintage of the asset class of the asset being retired, with a corresponding reduction (debit) to Accumulated Depreciation (FERC 108). For assets accounted for on a group basis any undepreciated value of retired assets remains in Net Property, Plant, and Equipment, which is a component of rate base. | Aaron Louie | 2023-04-26 | 2023-05-05 | 2023-05-05 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-14.pdf | 0 | No | Other | Asset Depreication & Ratebase | N/A | N/A
144 | CalPA | 2023-14 | CalPA-2023-14 | 7 | CalPA-2023-14.7 | a) As of the date of this data request, does SDG&E’s rate base currently include any portion of the value of any assets that are no longer in service? b) If the answer to part (a) is yes, please explain why. c) If the answer to part (a) is no, list the controls in place that ensure SDG&E’s rate base does not currently include any portion of the value of assets that are no longer in service. | SDG&E objects to the request on the grounds set forth in General Objections 2, 3, 5, 6, and 9. SDG&E’s response is limited to its WMP and related activities. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a. Yes b. SDG&E’s practice for accounting for retired assets is consistent with CPUC Standard Practice U-4. . c. N/A | Aaron Louie | 2023-04-26 | 2023-05-05 | 2023-05-05 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-14.pdf | 0 | No | Other | Asset Depreication & Ratebase | N/A | N/A
145 | TURN | 2023-01 | TURN-2023-01 | 1 | TURN-2023-01.1 | For any project included in SDG&E’s Strategic Undergrounding program that was completed in 2020-2022, please identify the project by circuit or circuit segment name (the smallest applicable unit) and number of miles, and provide the RSE that SDG&E calculated for the project for: a. Undergrounding, b. Covered Conductor, and c. Any other alternative that SDG&E considered before opting for undergrounding. Please provide the input data and all calculations for the RSEs in Live Excel workbook(s). | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 3, 5, 9 and 10. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a. SDG&E did not calculate a circuit/segment-specific RSE for undergrounding on the circuits/circuit segments that were undergrounded in 2020 and 2021. Please see SDG&E’s respective WMP’s for 2020-2022 for the overall undergrounding RSE. SDG&E provides completed undergrounding projects for 2020 – 2022 in the file Strategic Undergrounding Projects Q1A and Q2A.xlsx and provides undergrounding RSEs for year 2022 in the file WMP_2023_TURN_DR_01_Q1_Q2.xlsx b. SDG&E did not calculate a circuit/segment-specific RSE for covered conductor on the circuits/circuit segments that were undergrounded in 2020 and 2021. Please see SDG&E’s respective WMP’s for 2020-2022 for the overall covered conductor RSE. SDG&E provides completed undergrounding projects for 2020 – 2022 in the file Strategic Undergrounding Projects Q1A and Q2A.xlsx and provides covered conductor RSEs for year 2022 in the file WMP_2023_TURN_DR_01_Q1_Q2.xlsx c. The overall circuit-level alternatives that SDG&E considers when assessing wildfire-mitigation grid hardening efforts are undergrounding, covered conductor, or no mitigation. If no mitigation is selected, SDG&E may still employ other wildfire mitigation strategies, including but not limited to vegetation management, avian mitigation, and advanced protection, as further detailed in SDG&E’s WMP initiatives. | Tom Long | 2023-05-01 | 2023-05-04 | 2023-05-04 | https://www.sdge.com/sites/default/files/regulatory/TURN-2023-01.pdf https://www.sdge.com/sites/default/files/regulatory/TURN-2023-01%20Attachment%20Q1%20%26%20Q2.xlsx https://www.sdge.com/sites/default/files/regulatory/TURN-2023-01%20Attachment%20Cont.%20Q1%20%26%20Q2.xlsx | 2 | No | Other | Completed Strategic Undergrounding Projects | N/A | N/A
146 | TURN | 2023-01 | TURN-2023-01 | 2 | TURN-2023-01.2 | For any project included in SDG&E’s planned Strategic Undergrounding program for completion in 2023-2025, please identify the project by circuit or circuit segment name (the smallest applicable unit) and number of miles, and provide the RSE that SDG&E calculated for the project for: a. Undergrounding, b. Covered Conductor, and c. Any other alternative that SDG&E considered before opting for undergrounding. Please provide the input data and all calculations for the RSEs in Live Excel workbook(s). | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 3, 9, and 10. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a. SDG&E provides planned undergrounding projects for 2023 – 2025 in the file Strategic Undergrounding Projects Q1A and Q2A.xlsx and provides undergrounding RSEs in the file WMP_2023_TURN_DR_01_Q1_Q2.xlsx b. SDG&E provides planned undergrounding projects for 2023 – 2025 in the file Strategic Undergrounding Projects Q1A and Q2A.xlsx and provides covered conductor RSEs in the file WMP_2023_TURN_DR_01_Q1_Q2.xlsx c. The overall circuit-level alternatives that SDG&E considers when assessing wildfire-mitigation grid hardening efforts are undergrounding, covered conductor, or no mitigation. If no mitigation is selected, SDG&E may still employ other wildfire mitigation strategies, including but not limited to vegetation management, avian mitigation, and advanced protection, as further detailed in SDG&E’s WMP initiatives. | Tom Long | 2023-05-01 | 2023-05-04 | 2023-05-04 | https://www.sdge.com/sites/default/files/regulatory/TURN-2023-01.pdf https://www.sdge.com/sites/default/files/regulatory/TURN-2023-01%20Attachment%20Q1%20%26%20Q2.xlsx https://www.sdge.com/sites/default/files/regulatory/TURN-2023-01%20Attachment%20Cont.%20Q1%20%26%20Q2.xlsx | 2 | No | Other | Planned Strategic Undergrounding Program | N/A | N/A
147 | TURN | 2023-01 | TURN-2023-01 | 3 | TURN-2023-01.3 | For the undergrounding work described in SDG&E’s 2023-2025 WMP, please describe SDG&E’s policy concerning undergrounding of service connections and the removal of poles on which service connections are attached. To the extent that this determination varies by project, please describe the criteria that SDG&E uses to decide whether SDG&E undergrounds service connections in a given location. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2 and 3. Subject to and without waiving the foregoing objections, SDG&E responds as follows: SDG&E’s Strategic Undergrounding Program includes service conversions where primary conductor is scoped and is informed by its WiNGS-Planning risk analysis to mitigate the risk of wildfire and PSPS customer impacts. Hence, poles on which service connections are attached will be removed as part of the underground conversion unless telecommunications equipment that SDG&E does not own or maintain is also attached to the pole. In that case, the pole is topped 12”-18” above telecommunications equipment and all SDG&E electrical facilities are removed. SDG&E then transfers ownership of the pole to the telecommunications provider. | Tom Long | 2023-05-01 | 2023-05-04 | 2023-05-04 | https://www.sdge.com/sites/default/files/regulatory/TURN-2023-01.pdf | 0 | No | Other | Planned Strategic Undergrounding Program | N/A | N/A
148 | TURN | 2023-01 | TURN-2023-01 | 4 | TURN-2023-01.4 | For the undergrounding work described in SDG&E’s 2023-2025 WMP, please describe SDG&E’s policy concerning undergrounding of secondary distribution lines (as opposed to primary lines) and the removal of poles on which secondary lines are attached. To the extent that this determination varies by project, please describe the criteria that SDG&E uses to decide whether SDG&E undergrounds secondary lines in a given location. | SDG&E’s Strategic Undergrounding Program includes the secondary distribution line conversions where primary conductor is scoped and is informed by its WiNGS-Planning risk analysis to mitigate the risk of wildfire and PSPS customer impacts. Hence, poles on which secondary is attached will be removed as part of the underground conversion unless telecommunications equipment that SDG&E does not own or maintain is also attached to the pole. In that case, the pole is topped 12”-18” above telecommunications equipment and all SDG&E electrical facilities are removed. SDG&E then transfers ownership of the pole to the telecommunications provider. | Tom Long | 2023-05-01 | 2023-05-04 | 2023-05-04 | https://www.sdge.com/sites/default/files/regulatory/TURN-2023-01.pdf | 0 | No | Other | Policy of undergrounding of secondary distribution lines | N/A | N/A
149 | TURN | 2023-01 | TURN-2023-01 | 5 | TURN-2023-01.5 | For the distribution circuits on which SDG&E has completed undergrounding as a wildfire mitigation in 2020-2022, please provide: a. The annual number of overhead miles of conductor removed, broken down by: primary conductor, secondary conductor, and services; b. The annual number of miles of underground line installed; c. SDG&E’s best estimate (which may be a rough approximation, if that is the best estimate) of the percentage of existing poles in the affected circuits (including poles supporting primary lines, secondary lines, and services) that were removed as a result of the undergrounding work in 2020-2022. Please explain how SDG&E made this calculation and provide all inputs and assumptions. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 3, 5, and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a. SDG&E does not track overhead miles of conductor removed by primary, secondary, and services and therefore does not have this data to distinguish in this category. The table below represents the total miles of overhead wires removed in 2020-2022. Year Total Miles Overhead Wires Removed 2020 1.32 2021 6.92 2022 23.85 b. The table below represents the total miles of underground installed and energized. Year Total Miles Underground Line Installed 2020 15.95 2021 26.24 2022 65.11 c. SDG&E does not track the question as asked. To provide an estimation, SDG&E used the total number of poles removed from the design package divided by the approximate total number of poles in the circuit before these poles were removed from service. Circuit Number 2020 2021 2022 C1030 0.50% 7.38% 17.06% C1458 10.28% C216 1.88% C221 0.18% 0.27% C358 5.30% C445 0.30% C448 0.45% C75 2.16% C79 0.05% C908 0.73% C972 9.98% CSL1 6.18% | Tom Long | 2023-05-01 | 2023-05-04 | 2023-05-04 | https://www.sdge.com/sites/default/files/regulatory/TURN-2023-01.pdf | 0 | No | Other | Completed Undergrounding Mitigation | N/A | N/A
150 | TURN | 2023-01 | TURN-2023-01 | 6 | TURN-2023-01.6 | For the distribution circuits on which SDG&E plans undergrounding as a wildfire mitigation in 2023-2025, please provide: a. The annual number of overhead miles of conductor planned to be removed, broken down by: primary conductor, secondary conductor, and services; b. The annual number of miles of underground line planned to be installed; c. SDG&E’s best estimate (which may be a rough approximation, if that is the best estimate) of the percentage of existing poles in the affected circuits (including poles supporting primary lines, secondary lines, and services) planned to be removed as a result of the planned undergrounding mileage in 2023-2025. Please explain how SDG&E made this calculation and provide all inputs and assumptions. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 3, 5 and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a. See response for 5a for tracking of primary, secondary and services. SUG projects are scoped by underground cable mileage to be installed, and not by overhead mileage to be removed. The overhead removal mileage will become available as design progresses. SDG&E does not currently have this information for projects scoped in 2024 and 2025. The table below represents removal miles for 2023 based solely on projects where design is complete. Year Total Miles Planned Overhead Wires Removed 2023 55.66 2024 NA 2025 NA b. Provided below is total miles of underground line planned to be installed and energized. Year Total Miles Planned Underground 2023 80 2024 125 2025 150 c. SUG projects are scoped by underground cable mileage to be installed, and not by overhead poles to be removed. The overhead removal of poles and not yet available and will become available as design progresses. SDG&E do not currently have this information for projects scoped in 2023-2025. | Tom Long | 2023-05-01 | 2023-05-04 | 2023-05-04 | https://www.sdge.com/sites/default/files/regulatory/TURN-2023-01.pdf | 0 | No | Other | Planned Undergrounding Mitigation | N/A | N/A
151 | TURN | 2023-01 | TURN-2023-01 | 7 | TURN-2023-01.7 | With respect to the targets for 2023-2025 in the row for Strategic Undergrounding in Table 8-3 of SDG&E’s 2023-2025 WMP: a. For each year, please provide SDG&E’s estimate of the overhead circuit miles that will be replaced and explain how this estimate was determined; and b. For the figures provided in response to subpart “a”, please provide an estimated breakdown of the overhead circuit miles planned to be replaced by: primary lines, secondary lines, and services. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 3, 5, 6 and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a. See response for question 6a. b. See response for question 5a and 6a. | Tom Long | 2023-05-01 | 2023-05-04 | 2023-05-04 | https://www.sdge.com/sites/default/files/regulatory/TURN-2023-01.pdf | 0 | No | Table 8-3 | Table 8-3: Grid Design, Operations, and Maintenance Targets by Year ............ 140 | N/A | N/A
152 | TURN | 2023-02 | TURN-2023-02 | 1 | TURN-2023-02.1 | Please provide data in SDG&E’s possession that indicates the following: a. The SAIDI (System Average Interruption Duration Index) for the years 2018- 2022 for underground distribution facilities; b. The MAIFI (Momentary Average Interruption Frequency Index) for the years 2018-2022 for underground distribution facilities; c. The SAIDI (System Average Interruption Duration Index) for the years 2018-2022 for overhead distribution facilities with covered conductor; d. The MAIFI (Momentary Average Interruption Frequency Index) for the years 2018-2022 for overhead distribution facilities with covered conductor; e. The SAIDI (System Average Interruption Duration Index) for the years 2018- 2022 for overhead distribution facilities without covered conductor; f. The MAIFI (Momentary Average Interruption Frequency Index) for the years 2018-2022 overhead distribution facilities without covered conductor. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 3, 5, and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: SAIDI is a systemwide measurement. SDG&E does not calculate SAIDI at a segment level and therefore cannot provide SAIDI or MAIFI for overhead distribution facilities with or without covered conductor separately (c-f). SDG&E has provided SAIDI and MAIFI for underground and overhead facilities in the responses to 1a and 1b below. | Tom Long | 2023-05-01 | 2023-05-05 | 2023-05-04 | https://www.sdge.com/sites/default/files/regulatory/TURN-2023-02.pdf | 0 | No | Other | SAIDI & MAIFI | N/A | N/A
153 | TURN | 2023-02 | TURN-2023-02 | 2 | TURN-2023-02.2 | Please describe any differences, as a general matter, in the reliability of SDG&E’s overhead distribution lines without covered conductor, overhead lines with covered conductor, and underground lines, including without limitation a comparison of the frequency of outages and the duration of outages. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 3, 5, and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: With respect to its WMP initiatives, SDG&E has not performed a reliability analysis of overhead distribution lines without covered conductor, overhead lines with covered conductor, and underground lines. SDG&E’s risk analysis to plan wildfire hardening efforts has been focused on risk events (outages that can lead to an ignition) to reduce the risk of wildfire and the impacts of PSPS. As a general matter, as explained in SDG&E’s WMP submission, undergrounding electrical infrastructure is the optimal means to reduce PSPS impacts on customers. | Tom Long | 2023-05-01 | 2023-05-05 | 2023-05-04 | https://www.sdge.com/sites/default/files/regulatory/TURN-2023-02.pdf | 0 | No | Other | Reliability | N/A | N/A
154 | TURN | 2023-02 | TURN-2023-02 | 3 | TURN-2023-02.3 | Please provide all reports or studies in SDG&E’s possession prepared from January 1, 2018 to the present that discuss the reliability of underground distribution facilities, overhead distribution facilities with covered conductor, or overhead distribution facilities without covered conductor, including but not limited to a discussion of frequency of outages, SAIDI data, duration of outages, and MAIFI data. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 3, 5 and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: With respect to its wildfire mitigation efforts, SDG&E has not performed any studies that discuss the reliability of underground distribution facilities, overhead distribution facilities with covered conductor, or overhead distribution facilities without covered conductor. As a general matter, please see SDG&E’s Electric System Reliability Annual Reports located at https://www.sdge.com/system-reliability for more information on system reliability. | Tom Long | 2023-05-01 | 2023-05-05 | 2023-05-04 | https://www.sdge.com/sites/default/files/regulatory/TURN-2023-02.pdf | 0 | No | Other | Reliability Reports | N/A | N/A
155 | CalPA | 2023-15 | CalPA-2023-15 | 1 | CalPA-2023-15.1 | Regarding SDG&E’s Underground (UG) Switches: a) List the types of UG switches that SDG&E uses in vaults. b) For each type of switch in the part (a), state whether it is manually operated or SCADA-capable. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 3, and 5. Subject to and without waiving the foregoing objections, SDG&E responds as follows: SDG&E has many types of subsurface structures in which switches may be installed, including handholes, manholes, and dry underground vaults. Of those switches, the electrical insulation types and their configurations for vault installations include: • Air o In-Out (Manual) • Oil o In-Out (Manual) o 4-Way (Manual & SCADA) o 5-Way (Manual & SCADA) • SF-6 Gas o 4-Way (Manual & SCADA) o 6-Way (Manual & SCADA) • Solid Di-Electric o In-Out (Manual) o 4-Way (Manual & SCADA) o 6-Way (SCADA) | Aaron Louie | 2023-05-03 | 2023-05-08 | 2023-05-08 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-15.pdf | 0 | No | Other | Underground (UG) Switches | N/A | N/A
156 | CalPA | 2023-15 | CalPA-2023-15 | 2 | CalPA-2023-15.2 | Regarding SDG&E’s Underground (UG) Switches: How far apart are the UG switches on a typical UG circuit segment in the HFTD? | Subject to and without waiving the foregoing objections, SDG&E responds as follows: Underground sectionalizing is not based on distance alone, but on multiple criteria. Below are some of the criteria that are outlined in SDG&E’s Electric Distribution Design Manual: 1. No more than one mile of overhead or underground feeder should exist between switches 2. An underground switch should be placed every 100A of actual 12kV peak load or 4000kVA of connected line transformer nameplate load, whichever comes first. 3. No more than 1000 metered customers shall be connected between switches 4. Dedicated switch positions for all 3000kVA transformer connections 5. All primary metered service connections to the feeder system shall be made through fuses, switches, or switch positions capable of fault interruption This list is not all-inclusive. | Aaron Louie | 2023-05-03 | 2023-05-08 | 2023-05-08 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-15.pdf | 0 | No | Other | Underground (UG) Switches | N/A | N/A
157 | CalPA | 2023-15 | CalPA-2023-15 | 3 | CalPA-2023-15.3 | Please explain the purpose of the riser installations in the WMP underground projects. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 3, and 5. Subject to and without waiving the foregoing objections, SDG&E responds as follows: Riser installations are used in WMP underground projects as transition points from overhead conductors to underground cables and vice versa. The “riser”, or conduit, will be attached to a pole which is then identified as a “riser pole”. | Aaron Louie | 2023-05-03 | 2023-05-08 | 2023-05-08 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-15.pdf | 0 | No | Other | Riser installations on WMP UG Projects | N/A | N/A
158 | CalPA | 2023-16 | CalPA-2023-16 | 1 | CalPA-2023-16.1 | In reference to the zip file named CONFIDENTIAL QUESTION 12.zip submitted by SDG&E in response to Question 12 of data request CalAdvocates-SDGE-2023WMP-11: a) Please provide a revised version of this spreadsheet that is clearly labeled. b) Please explain whether the “year” column refers to the year that the circuit was undergrounded or the year to which the peak loading calculation applies. c) Please explain what specific portion(s) of the Excel sheet in the zip file are responding to parts (f) and (g) of Question 12. | a) SDG&E provides clarification on the spreadsheet in parts (b) and (c) below. SDG&E did not edit the original spreadsheet. b) The “Year” column refers to the year the circuit is planned for undergrounding. The resulting average peak load is calculated for those years as defined in Question 12 parts (a) through (e). c) SDG&E has now included responses to parts (f) and (g) and are provided in cells columns e-j in “CONFIDENTIAL_CalPA-SDGE-2023WMP-16.” | Aaron Louie | 2023-05-03 | 2023-05-11 | 2023-05-11 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-16.pdf | 1 | Yes | Other | CalAdvocates-SDGE-2023WMP-11 | N/A | N/A
159 | MGRA | 2023-04 | MGRA-2023-04 | 1 | MGRA-2023-04.1 | For the Wind Adjustment Rate: a. What is the algorithm and formula used to apply the wind adjustment rate? b. What data was used to determine the wind adjustment rate? c. Show the analysis that determined the algorithm and formula from the available data. d. Show how the wind adjustment rate was validated to prove that it accurately represents the ignition rate. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2 and 3. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a. The generalized factor adjustment process implementation is depicted below: 𝐴𝐴𝐴𝐴𝐴𝐴.𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼 𝑅𝑅𝑅𝑅𝑅 𝑅𝑅= 𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼 𝐼𝐼 𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼 𝑅𝑅𝑅𝑅𝑅 𝑅𝑅×𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼 𝐴𝐴𝐴𝐴𝐴𝐴.𝐹𝐹𝐹 𝐹𝐹𝐹𝐹𝐹𝐹 𝐹𝐹𝑖𝑖×𝑁𝑁 𝑁𝑁 𝑁𝑁 𝐹𝐹𝐹 𝐹𝐹 𝐹𝐹𝑖𝑖 Where, Initial Ignition Rate is the initial ignition rate prior to implementation of adjustment factor i, Ignition Adj. Factori is the adjustment factor metric tied to the adjustment factor i, Normalization Factori is the normalization factor tied to adjustment factor i, Adj. Ignition Rate is the adjusted ignition rate after implementation of adjustment factor i and i is the specific adjustment factor (e.g., wind speed, tree strikes, etc.). For the wind speed ignition adj. factor, the historical max wind speeds are categorized into four severity ranges and each given an assigned adjustment factor rate: 1. < 40 mph = 0.025 2. 40 – 50 mph = 0.075 3. 50 – 60 mph = 0.225 4. > 60 mph = 0.675 b. Historical max wind speeds from associated weather stations tied to each circuit-segment. c. The generalized factor adjustment formula is devised using principles of weighted-sum modeling and factor-adjustment parametrization. The severity range bucketing and associated adjustment factor variables tied to each were informed by subject matter expert guidance. Note: The overall methodology for the WiNGS Planning ignition rate is currently undergoing evaluation for improvement. The current WiNGS Planning ignition rate methodology is based on the original methodology that was chosen by the development team during conception of the model. This methodology was retained during the WiNGS platform cut-over from Excel to Python/AWS to make sure output was as consistent as possible between architectural changes. d. Unit test verification steps are performed within the model to ensure that the normalization for each ignition rate adjustment step is performed correctly. Ad-hoc analysis by modeling team has shown positive correlation between ignition rates and wind speeds, as intended. Furthermore, a thorough third-party review has been performed on the WiNGS-Planning model and completed in 2023, which reviewed and evaluated the validity of the modeling steps within the model, including the Ignition Rate Normalization Factor Sub-Model and found that the model is a robust model which meets user needs and performs the function for which it was designed. The third party review found no high-severity issues that could change the output of the model. The WiNGS model output is furthermore scrutinized for validity by scoping engineers via the Desktop Feasibility Study, which is implemented during the project scoping process. Note: Section 6.7 of SDG&E’s WMP details the roadmap for formalizing the WiNGS Planning model’s validation process. | Joseph Mitchell | 2023-05-08 | 2023-05-12 | 2023-05-12 | https://www.sdge.com/sites/default/files/regulatory/MGRA-2023-04.pdf | 0 | No | Other | Ignition Model | N/A | N/A
160 | MGRA | 2023-04 | MGRA-2023-04 | 2 | MGRA-2023-04.2 | For the Vegetation Adjustment Rate: a. What is the algorithm and formula used to apply the vegetation adjustment rate? b. What data was used to determine the vegetation adjustment rate? c. Show the analysis that determined the algorithm and formula from the available data. d. Show how the vegetation adjustment rate was validated to prove that it accurately represents the ignition rate. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2 and 3. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a. The generalized factor adjustment process implementation is depicted below: 𝐴𝐴𝐴𝐴𝐴𝐴.𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼 𝑅𝑅𝑅𝑅𝑅 𝑅𝑅= 𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼 𝐼𝐼 𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼 𝑅𝑅𝑅𝑅𝑅 𝑅𝑅×𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼 𝐴𝐴𝐴𝐴𝐴𝐴.𝐹𝐹𝐹 𝐹𝐹𝐹𝐹𝐹𝐹 𝐹𝐹𝑖𝑖×𝑁𝑁 𝑁𝑁 𝑁𝑁 𝐹𝐹𝐹 𝐹𝐹 𝐹𝐹𝑖𝑖 Where, Initial Ignition Rate is the initial ignition rate prior to implementation of adjustment factor i, Ignition Adj. Factori is the adjustment factor metric tied to the adjustment factor i, Normalization Factori is the normalization factor tied to adjustment factor i, Adj. Ignition Rate is the adjusted ignition rate after implementation of adjustment factor i and i is the specific adjustment factor (e.g., wind speed, tree strikes, etc.). The tree strike ignition adj. factor = 𝑠𝑠𝑠𝑠𝑠𝑠𝑠𝑠𝑠𝑠𝑠𝑠𝑠𝑠 𝑡 𝑡𝑡𝑡𝑡𝑡𝑡 𝑠𝑠𝑠𝑠 𝑠𝑠𝑠𝑠 𝑝𝑝𝑝𝑝 𝑝𝑝𝑝𝑝 𝑐𝑐𝑐 𝑐𝑐𝑐 𝑠𝑠𝑠𝑠𝑠𝑠𝑠𝑠𝑠𝑠𝑠𝑠𝑠𝑠 𝑂𝑂𝑂𝑂 where a potential tree strike is a tree that is within contact-range proximity of the OH line. b. The Veg Management tree inventory points as well as Circuit Segment line features were used to create the tree strike data. c. The generalized factor adjustment formula is devised using principles of weighted-sum modeling and factor-adjustment parametrization. The associated adjustment factor variables tied to each were informed by subject matter expert guidance. Note: The overall methodology for the WiNGS Planning ignition rate is currently undergoing evaluation for improvement. The current WiNGS Planning ignition rate methodology is based on the original methodology that was chosen by the development team during conception of the model. This methodology was retained during the WiNGS platform cut-over from Excel to Python/AWS to make sure output was as consistent as possible between architectural changes. d. Unit test verification steps are performed within the model to ensure that the normalization for each ignition rate adjustment step is performed correctly. Ad-hoc analysis by modeling team has shown positive correlation between ignition rates and potential tree strikes per OH miles, as intended. Furthermore, a thorough third-party review has been performed on the WiNGS-Planning model and completed in 2023, which reviewed and evaluated the validity of the modeling steps within the model, including the Ignition Rate Normalization Factor Sub-Model and found that the model is a robust model which meets user needs and performs the function for which it was designed. The third party found no high-severity issues that could change the output of the model. The WiNGS model output is furthermore scrutinized for validity by scoping engineers via the Desktop Feasibility Study, which is implemented during the project scoping process. Note: Section 6.7 of SDG&E’s WMP details the roadmap for formalizing the WiNGS Planning model’s validation process. | Joseph Mitchell | 2023-05-08 | 2023-05-12 | 2023-05-12 | https://www.sdge.com/sites/default/files/regulatory/MGRA-2023-04.pdf | 0 | No | Other | Ignition Model | N/A | N/A
161 | MGRA | 2023-04 | MGRA-2023-04 | 3 | MGRA-2023-04.3 | For the Asset Health Adjustment Rate: a. What is the algorithm and formula used to apply the asset health adjustment rate? b. What data was used to determine the asset health adjustment rate? c. Show the analysis that determined the algorithm and formula from the available data. d. Show how the asset health adjustment rate was validated to prove that it accurately represents the ignition rate. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2 and 3. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a. The generalized factor adjustment process implementation is depicted below: 𝐴𝐴𝑑 .𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼 𝑅𝑅𝑅𝑅𝑅 𝑅𝑅= 𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼 𝐼𝐼 𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼 𝑅𝑅𝑅𝑅𝑅 𝑅𝑅×𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼 𝐴𝐴𝐴𝐴𝐴𝐴.𝐹𝐹𝐹 𝐹𝐹𝐹𝐹𝐹𝐹 𝐹𝐹𝑖𝑖×𝑁𝑁 𝑁𝑁 𝑁𝑁 𝐹𝐹𝐹 𝐹𝐹 𝐹𝐹𝑖𝑖 Where, Initial Ignition Rate is the initial ignition rate prior to implementation of adjustment factor i, Ignition Adj. Factori is the adjustment factor metric tied to the adjustment factor i, Normalization Factori is the normalization factor tied to adjustment factor i, Adj. Ignition Rate is the adjusted ignition rate after implementation of adjustment factor i and i is the specific adjustment factor (e.g., wind speed, tree strikes, etc.). The Asset Health adj. factor = (2∗(𝑆𝑆𝑆𝑆𝑆𝑆𝑆𝑆𝑆𝑆𝑆𝑆𝑆𝑆 𝑎 𝑎𝑎𝑎 𝑐𝑐 𝑐𝑐𝑐𝑐𝑐𝑐 𝑎 )𝑎 𝑎𝑎𝑎 {𝑆𝑆 𝑎 𝑎𝑎𝑎 𝑐𝑐 𝑐𝑐𝑐𝑐𝑐𝑐 𝑎 1, 𝑆𝑆 𝑎 𝑎𝑎𝑎 𝑐𝑐 𝑐𝑐𝑐𝑐𝑐𝑐 𝑎 2,…,𝑆𝑆 𝑎 𝑎𝑎𝑎 𝑐𝑐 𝑐𝑐𝑐𝑐𝑐𝑐 𝑎 𝑛𝑛 })+(𝑆𝑆 𝑐𝑐ℎ𝑖𝑖{𝑆𝑆 𝑐𝑐ℎ𝑖𝑖1, 𝑆𝑆 𝑐𝑐ℎ𝑖𝑖2,…,𝑆𝑆 𝑐𝑐ℎ𝑖𝑖𝑛𝑛 }) Where CHI is the Circuit Health Index and n is the count of segments in the model scope. b. Primary Overhead Conductor, Overhead Structure data from GIS Electric production database c. The generalized factor adjustment formula is devised using principles of weighted-sum modeling and factor-adjustment parametrization. The associated adjustment factor variables tied to each were informed by subject matter expert guidance. Note: The overall methodology for the WiNGS Planning ignition rate is currently undergoing evaluation for improvement. The current WiNGS Planning ignition rate methodology is based on the original methodology that was chosen by the development team during conception of the model. This methodology was retained during the WiNGS platform cut-over from Excel to Python/AWS to make sure output was as consistent as possible between architectural changes. d. Unit test verification steps are performed within the model to ensure that the normalization for each ignition rate adjustment step is performed correctly. Ad-hoc analysis by modeling team has shown positive correlation between ignition rates and the asset health attributes, as intended. Furthermore, a thorough third-party review has been performed on the WiNGS-Planning model and completed in 2023, which reviewed and evaluated the validity of the modeling steps within the model, including the Ignition Rate Normalization Factor Sub-Model and found that the model is a robust model which meets user needs and performs the function for which it was designed. The third party found no high-severity issues that could change the output of the model. The WiNGS model output is furthermore scrutinized for validity by scoping engineers via the Desktop Feasibility Study, which is implemented during the project scoping process. Note: Section 6.7 of SDG&E’s WMP details the roadmap for formalizing the WiNGS Planning model’s validation process. | Joseph Mitchell | 2023-05-08 | 2023-05-12 | 2023-05-12 | https://www.sdge.com/sites/default/files/regulatory/MGRA-2023-04.pdf | 0 | No | Other | Ignition Model | N/A | N/A
162 | MGRA | 2023-04 | MGRA-2023-04 | 4 | MGRA-2023-04.4 | For the Significant Wildfire Adjustment Rate: a. What is the algorithm and formula used to apply the significant wildfire adjustment rate? b. What data was used to determine the significant wildfire adjustment rate? c. Show the analysis that determined the algorithm and formula from the available data. d. Show how the significant wildfire adjustment rate was validated to prove that it accurately represents the ignition rate. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2 and 3. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a. The factor adjustment process implementation is depicted below: 𝑊𝑊𝑊𝑊𝑊𝑊𝑊𝑊 𝑊𝑊 𝑅𝑅𝑅𝑅𝑅 𝑅𝑅= 𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼 𝐼𝐼 𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼 𝑅𝑅𝑅𝑅𝑅 𝑅𝑅×𝑆𝑆 𝐴𝐴𝐴𝐴𝐴𝐴.𝐹𝐹𝐹 𝐹𝐹 𝐹𝐹 Where, Initial Ignition Rate is the initial ignition rate prior to implementation of the adjustment factor, SigWF Adj. Factor is the adjustment factor metric, Wildfire Rate is the adjusted wildfire rate after implementation of the adjustment factor. 𝑆𝑆𝑆𝑆𝑆𝑆𝑆𝑆𝑆𝑆 𝐴𝐴𝐴𝐴𝐴𝐴.𝐹𝐹𝐹 𝐹𝐹 𝐹𝐹 = 1(𝑊𝑊 𝑊𝑊 𝐹𝐹𝐹 𝐹𝐹 𝐹𝐹 × 𝐴𝐴 𝐻𝐻𝐻𝐻 𝐼𝐼 𝑅𝑅 ) Where wildfire frequency is represented in years, and Annual HFTD Ign Rate is the rate of ignition per year in the HFTD. b. See RAMP 2019, section IV, B. “Sources of Input” c. See RAMP 2019 ,section IV, B. “Sources of Input” d. See RAMP 2019 , section IV, B. “Sources of Input” | Joseph Mitchell | 2023-05-08 | 2023-05-12 | 2023-05-12 | https://www.sdge.com/sites/default/files/regulatory/MGRA-2023-04.pdf | 0 | No | Other | Ignition Model | N/A | N/A
163 | MGRA | 2023-04 | MGRA-2023-04 | 5 | MGRA-2023-04.5 | For the Hardening Adjustment Rate: a. What is the algorithm and formula used to apply the hardening adjustment rate? b. What data was used to determine the hardening adjustment rate? c. Show the analysis that determined the algorithm and formula from the available data. d. Show how the hardening adjustment rate was validated to prove that it accurately represents the ignition rate. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2 and 3. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a. The factor adjustment process implementation is depicted below: 𝐴𝐴𝐴𝐴𝐴𝐴.𝑊𝑊𝑊 𝑑𝑑𝑑𝑑𝑑𝑑𝑑𝑑𝑑𝑑 𝑅𝑅𝑅𝑅𝑅 𝑅𝑅= 𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼𝐼 𝐼𝐼 𝑊𝑊 𝑊𝑊 𝑅𝑅𝑅𝑅𝑅 𝑅𝑅×𝑃𝑃𝑃 𝐻𝐻 𝑖𝑖×(1−𝐼𝐼𝐼𝐼𝐼𝐼 𝐸𝐸 𝑅𝑅𝑅𝑅𝑅 𝑅𝑅𝑖𝑖) Where, Initial Wildfire Rate is the initial wildfire rate prior to implementation of the adjustment factor, 𝑃𝑃𝑃 𝐻𝐻𝐻𝐻𝐻𝐻𝐻𝐻𝐻𝐻𝐻𝐻𝐻𝐻 𝑛 𝑔 𝑖𝑖 is the percentage of segment hardening of hardening type i, 𝐼𝐼𝐼𝐼𝐼𝐼 𝐸𝐸 𝑅𝑅𝑅𝑅𝑅 𝑅𝑅𝑖𝑖 is the effectiveness rate of hardening type i, and i is the hardening state type. b. Primary Overhead Conductor, Overhead Structure data from GIS Electric production database c. The generalized factor adjustment formula is devised using principles of weighted-sum modeling and factor-adjustment parametrization. The associated effectiveness rates tied to each hardening type were informed by subject matter expert guidance and/or efficacy studies. Note: The overall methodology for the WiNGS Planning ignition rate is currently undergoing evaluation for improvement. The current WiNGS Planning ignition rate methodology is based on the original methodology that was chosen by the development team during conception of the model. This methodology was retained during the WiNGS platform cut-over from Excel to Python/AWS to make sure output was as consistent as possible between architectural changes. d. Efficacy studies and/or subject matter expert guidance has been utilized to assess the effectiveness rates that go into adjusting the ignition rate for the hardening state. Additionally, a thorough third-party review was performed on the WiNGS-Planning model and completed in 2023, which reviewed and evaluated the validity of the modeling steps within the model, including the Ignition Rate Normalization Factor Sub-Model and found that the model is a robust model which meets user needs and performs the function for which it was designed. The third party found no high-severity issues that could change the output of the model. The WiNGS model output is furthermore scrutinized for validity by scoping engineers via the Desktop Feasibility Study, which is implemented during the project scoping process. Note: Section 6.7 of SDG&E’s WMP details the roadmap for formalizing the WiNGS Planning model’s validation process. | Joseph Mitchell | 2023-05-08 | 2023-05-12 | 2023-05-12 | https://www.sdge.com/sites/default/files/regulatory/MGRA-2023-04.pdf | 0 | No | Other | Ignition Model | N/A | N/A
164 | GreenPower | 2023-03 | GreenPower-2023-03 | 1 | GreenPower-2023-03.1 | Please provide: - The number of trees removed in 2019, 2020, 2021, and 2022 and the program under which the removals occurred (e.g. Fall-in Mitigation Program) - The number of planned tree removals for 2023, 2024, and 2025, and the program under which the removals will occur (e.g. Fall-in Mitigation Program) - The number of remaining trees in SDG&Es tree inventory listed for removal | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2 and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: SDG&E’s fall-in mitigation is integrated within the detailed inspection and off-cycle HFTD patrol activities as provided in the 2023 WMP. SDG&E removes trees to prevent power line contact that may result from branch breakout or trunk failure (e.g., hazard tree), and/or to mitigate fast-growing trees or those that cannot be maintained by continued pruning. SDG&E does not plan in advance exactly how many trees will be removed in a calendar year. That determination is made at time of inspection taking into account current tree-specific and site-specific conditions. Please see attachment titled, “GPI_SDGE_2023WMP_03_Q1”. The worksheet includes all trees removed 2019-2022, and split out in a pivot table by hazard condition code (CDRRM; CGRRM), and those removed based on other criteria (CRM). The completed removal condition codes are: • CDRRM – Completed, dead, reliability removal • CGRRM – Completed, green, reliability removal • CRM – Completed removal | Zoe Harrold/Gregg Morris | 2023-05-11 | 2023-05-16 | 2023-05-16 | https://www.sdge.com/sites/default/files/regulatory/GPI-2023-03.pdf https://www.sdge.com/sites/default/files/regulatory/GPI-2023-03%20Attachment%20Q1.xlsx | 1 | No | Other | Fall-in Mitigation Program | N/A | N/A
165 | GreenPower | 2023-03 | GreenPower-2023-03 | 2 | GreenPower-2023-03.2 | Please provide the number of distribution line miles SDG&E will perform trimming on to achieve enhanced clearances (> 12’). | SDG&E objects to the request on the grounds set forth in General Objections Nos. 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: SDG&E does not plan or forecast in advance the number of miles it will perform enhanced clearance. This work is not planned in advance to occur on specific circuits or circuit segments within the HFTD. The determination of whether an individual tree will receive enhanced clearance is made at the time of trim based on the appropriate clearance needed for that tree considering variables such as species, growth rate, location of defect, proper pruning, and tree health. | Zoe Harrold/Gregg Morris | 2023-05-11 | 2023-05-16 | 2023-05-16 | https://www.sdge.com/sites/default/files/regulatory/GPI-2023-03.pdf | 0 | No | Other | Vegetation Management | N/A | N/A
166 | GreenPower | 2023-03 | GreenPower-2023-03 | 3 | GreenPower-2023-03.3 | Please provide any existing quantitative metrics (e.g. kg, truckloads, etc.) on the total amount of vegetation management “waste” (or residues) produced each year from 2020 – 2022, and the annual amounts that are disposed of at recycling facilities, landfills, biomass facilities, or other facilities. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 3, and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: The table below provides the annual amount (tonnage) of green waste disposal associated with vegetation management in years 2020-2022. Year Landfill Recycling Facility Total 2020 9704 4541 14245 2021 5753 5387 11140 2022 5449 5715 11164 Total 20906 15643 36549 | Zoe Harrold/Gregg Morris | 2023-05-11 | 2023-05-16 | 2023-05-16 | https://www.sdge.com/sites/default/files/regulatory/GPI-2023-03.pdf | 0 | No | Other | Vegetation Management | N/A | N/A
167 | GreenPower | 2023-03 | GreenPower-2023-03 | 4 | GreenPower-2023-03.4 | Please provide the number of customer requests to retain woody biomass resulting from vegetation management activities on private property, state property, and federal property. | As standard operating practice, SDG&E leaves large woody debris associated with tree pruning and removal activities on site, cut into manageable lengths. Large woody debris is considered material approximately greater than six (6) inches diameter. On public lands such as state and federal properties, wood debris is lopped and scattered or removed from site upon agency request. | Zoe Harrold/Gregg Morris | 2023-05-11 | 2023-05-16 | 2023-05-16 | https://www.sdge.com/sites/default/files/regulatory/GPI-2023-03.pdf | 0 | No | Other | Vegetation Management | N/A | N/A
168 | GreenPower | 2023-03 | GreenPower-2023-03 | 5 | GreenPower-2023-03.5 | Please describe current agreements and any recent (2021-Present) communications with state and federal agencies regarding fuels and slash management practices on state and federal lands, respectively. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2. Subject to and without waiving the foregoing objections, SDG&E responds as follows: SDG&E and the US Forester Service completed an updated Master Special Use Permit which describes utility protocols for activities occurring on the Cleveland National Forest. The permit includes protocols and requirements related to vegetation management activities such as tree trimming and fuels modification. As part of its Natural Communities Conservation Plan (NCCP), SDG&E performs pre-activity environmental reviews where activities are planned on public lands such as state parks, tribal lands, BLM, and US Forest Service. These environmental reviews identify protected species and define specific NCCP protocols and constraints for preventing negative impact to protected species. In conjunction with required notification protocols for these same agencies, SDG&E provides scoping details and schedules for annual vegetation management activities. | Zoe Harrold/Gregg Morris | 2023-05-11 | 2023-05-16 | 2023-05-16 | https://www.sdge.com/sites/default/files/regulatory/GPI-2023-03.pdf | 0 | No | Other | Vegetation Management | N/A | N/A
169 | GreenPower | 2023-03 | GreenPower-2023-03 | 6 | GreenPower-2023-03.6 | Please provide the number of tree rebates provided in the Community Tree Rebate Program (WMP.1326) for each year from 2019-2022 and the projected number of rebates for years 2023-2025. | The Community Tree Rebate Program was initiated in 2022. A total of 2,047 rebates were provided in 2022. SDG&E forecasts approximately 3,000 rebates annually for the next few years. The exact end date for this program has not been finalized. | Zoe Harrold/Gregg Morris | 2023-05-11 | 2023-05-16 | 2023-05-16 | https://www.sdge.com/sites/default/files/regulatory/GPI-2023-03.pdf | 0 | No | 8.2.3.6 | 8.2.3.6 High-Risk Species Page 279 |  | Community Tree Rebate Program (WMP.1326)
170 | MGRA | 2023-05 | MGRA-2023-05 | 1 | MGRA-2023-05.1 | 2022 Outages Please provide an Excel spreadsheet summarizing outage causes for 2022: a. The first column(s) should indicate the outage cause diagnosed by SCE. Following columns should contain: b. The fraction (in percentage) of all outages with the specific cause specified in the first column(s). c. The fraction (in percentage) of outages on completely bare wire overhead segments with the specific cause specified in the first column(s). d. The fraction (in percentage) of outages on completely covered conductor with the specific cause specified in the first column(s). Each of columns b, c, and d should total to 100%. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 3, and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a. Please see attached file, “MGRA-SDGE-2023WMP-05.xlsx.” The values in this column are the outage cause reported by SDG&E, and not SCE as stated in the question. b. Please see attached file, “MGRA-SDGE-2023WMP-05.xlsx.” The values in this column are the fraction of the outages with this cause code across all outages (both underground and overhead.) c. Please see attached file, “MGRA-SDGE-2023WMP-05.xlsx.” The values in this column are the fraction of overhead outages with this cause code across all overhead outages. For this request, SDG&E assumes all overhead outages are bare wire outages. SDG&E has approximately 98 miles of covered conductor installed on its system, all of which was installed since 2019. SDG&E has approximately 6,380 total miles of overhead distribution infrastructure which has been in place for decades. SDG&E does not currently separate overhead outages by bare wire and covered conductor due to the small sample size. d. Please see response to section c above. SDG&E does not currently separate overhead outages by bare wire and covered conductor due to the inadequate sample size. | Joseph Mitchell | 2023-05-15 | 2023-05-18 | 2023-05-18 | https://www.sdge.com/sites/default/files/regulatory/MGRA-2023-05.pdf https://www.sdge.com/sites/default/files/regulatory/MGRA-2023-05%20Attachment%20Q1.xlsx | 1 | No | Other | Otage causes for 2022 | N/A | N/A
171 | TURN | 2023-03 | TURN-2023-03 | 1 | TURN-2023-03.1 | Following up on the response to TURN data request 1-1 and 1-2 and particularly the file WMP_2023_TURN_DR_01_Q1_Q2. xlsx: a. Comparing the first and second tabs of that Excel file, the RSEs for covered conductor in the first tab show significantly higher values than the RSEs for covered conductor in the second tab. Please explain why this is so, including without limitation any changes in the RSE calculation between the WINGS v1 and v2 methodology that would explain this difference. b. Comparing the first and second tabs of that Excel file, the RSEs for covered conductor in the first tab generally significantly exceed the RSEs for undergrounding in the first tab. In contrast, in the second tab, the RSEs for covered conductor generally are fairly close to the RSEs for the undergrounding. Please explain why the relationship between RSEs for covered conductor and undergrounding is so different between the two tabs, including without limitation any changes in the RSE calculation between the WINGS v1 and v2 methodology that would explain this difference. | a. Accompanying notes provided in the third tab of the original Excel file ‘WMP_2023_TURN_DR_01_Q1_Q2.xlsx’ labeled ‘notes’ for TURN DR 1-1 and 1-2 state that “Comparison assessment between WiNGS 1.0 & 2.0 outputs cannot be performed across the board with every shared metric in the models, due to model updates and refinements made from 1.0 to 2.0. Metrics are best compared within the same model version, for most accurate comparison assessment”. The explanation for specific metric differences across models that are separated by a span of over two years of model refinement and development involve a myriad of individual data points that go into the WiNGS-Planning model framework, consisting of inputs, individual sub-models, model-families, risk component scores, and mitigation assessment functions. See below for a brief overview of the interconnections between the components of the model that include +200 fields that go into the calculation of the various model outputs, including the WF RSE values listed in the model output. See file ‘TURN-SDGE-2023_WMP-03_Question 1.xlsx’ for a complete list of all substantial model feature changes between the older model version and the latest WiNGS-Planning model. Though a myriad of factors influences the calculation of the mitigation specific WF RSE values of each circuit-segment, the following factors listed in ‘TURN-SDGE-2023_WMP-03_Question 1.xlsx’ play a key-role in the observed difference between the WF RSE values of going from old to the latest model: • Update to latest average annual HFTD ignition rate • Removal of legacy fixed project cost • Update of Ignition-to-Wildfire Rate (SigWF) factor • Implementation of building destroyed factor in WRRM Conditional Impact calculation for improved WF Consequence assessment See ‘‘TURN-SDGE-2023_WMP-03_Question 1.xlsx’ for more details on these and other model differences. b. Accompanying notes provided in the third tab of the original Excel file ‘WMP_2023_TURN_DR_01_Q1_Q2.xlsx’ labeled ‘notes’ for TURN DR 1-1 and 1-2 state that “Comparison assessment between WiNGS 1.0 & 2.0 outputs cannot be performed across the board with every shared metric in the models, due to model updates and refinements made from 1.0 to 2.0. Metrics are best compared within the same model version, for most accurate comparison assessment”. The explanation for specific metric differences across models that are separated by a span of over two years model refinement and development involve a myriad of individual data points that go into the WiNGS-Planning model framework, consisting of inputs, individual sub-models, modelfamilies, risk component scores, and mitigation assessment functions. See Figure 1 displayed in Response 1 for a brief overview of the interconnections between the components of the model that include +200 fields that go into the calculation of the various model outputs, including the WF RSE values listed in the model output. Though a myriad of factors influences the calculation of the mitigation specific WF RSE values of each circuit-segment, the following factors listed in ‘TURN-SDGE- 2023_WMP-03_Question 1.xlsx’ play a key-role in the observed differences between the WF RSE values of going from old to the latest model: • Cost-per-mile updates to Covered Conductor, Undergrounding, Traditional Hardening Conversion to Covered Conductor • Improved implementation of UG Contingency Factor • Implementation of Lifecycle Cost Savings in the Total Undergrounding Cost See ‘TURN-SDGE-2023_WMP-03_Question 1.xlsx’ for more details on these and other model differences. | Tom Long | 2023-05-16 | 2023-05-19 | 2023-05-19 | https://www.sdge.com/sites/default/files/regulatory/TURN-2023-03.pdf | 0 | No | Other | TURN-SDGE-2023WMP-01 | N/A | N/A
172 | TURN | 2023-03 | TURN-2023-03 | 2 | TURN-2023-03.2 | Comparing the wildfire mitigation work proposed in SDG&E’s WMP with the wildfire mitigation work proposed in SDG&E’s test year 2024 GRC (A.22-05-015 et al): a. Please describe any differences in wildfire mitigation programs proposed or volume of wildfire mitigation work proposed between the WMP and GRC for the years 2023-2025; and | a. SDG&E has performed this analysis across its vegetation management and certain grid hardening initiatives. This analysis is found in the respective spreadsheets, “TURN_SDGE_2023WMP_03_Grid Hardening Q2_Q3.xlsx.” and “TURN_SDGE_2023WMP_03_VM Q2_Q3.xlsx.” | Tom Long | 2023-05-16 | 2023-05-19 | 2023-05-19 | https://www.sdge.com/sites/default/files/regulatory/TURN-03%20Attachment%20Q2%20%26%20Q3%20Grid%20Hardening.xlsx https://www.sdge.com/sites/default/files/regulatory/TURN-03%20Attachment%20Q2%20%26%20Q3%20VM.xlsx | 2 | No | Other | GRC | N/A | N/A
173 | TURN | 2023-03 | TURN-2023-03 | 3 | TURN-2023-03.3 | For any differences (as described in subpart “a”), please provide a table that shows, on a program by program basis, the WMP proposal, the GRC proposal, and a description of the difference(s) between the two, including without limitation differences in volume or units of work. The table should include any wildfire mitigation programs that are proposed in one of the proceedings but not in the other. | a. SDG&E has performed this analysis across its vegetation management and certain grid hardening initiatives. This analysis is found in the respective spreadsheets, “TURN_SDGE_2023WMP_03_Grid Hardening Q2_Q3.xlsx.” and “TURN_SDGE_2023WMP_03_VM Q2_Q3.xlsx.” | Tom Long | 2023-05-16 | 2023-05-19 | 2023-05-19 | https://www.sdge.com/sites/default/files/regulatory/TURN-03%20Attachment%20Q2%20%26%20Q3%20Grid%20Hardening.xlsx https://www.sdge.com/sites/default/files/regulatory/TURN-03%20Attachment%20Q2%20%26%20Q3%20VM.xlsx | 2 | No | Other | GRC | N/A | N/A
174 | MGRA | 2023-06 | MGRA-2023-06 | 1 | MGRA-2023-06.1 | Follow up to DR 4: SDG&E stated that: “Furthermore, a thorough third-party review has been performed on the WiNGS-Planning model and completed in 2023, which reviewed and evaluated the validity of the modeling steps within the model, including the Ignition Rate Normalization Factor Sub-Model.” Please provide a non-confidential version of the third party review completed in 2023 which reviewed and evaluated the validity of the modeling steps within the model, including evaluation of all sub-models. | See attached file “WiNGS-Planning_Report_Final_2023_5_23.pdf.” | Joseph Mitchell | 2023-05-19 | 2023-05-24 | 2023-05-24 | https://www.sdge.com/sites/default/files/regulatory/MGRA-2023-06.pdf https://www.sdge.com/sites/default/files/regulatory/MGRA-2023-06%20Attachment%20Q1.pdf | 1 | No | Other | MGRA-SDGE-2023WMP-04 | N/A | N/A
175 | OEIS | 2023-02 | OEIS-2023-02 | 1 | OEIS-2023-02.1 | Regarding SDG&E’s Landscape Fuel Modeling Program Which vegetation, fire, and fuel characteristics landscape fuel modeling mapping program does SDG&E use (e.g., LANDFIRE) to perform its ignition and situational awareness modeling? Which version of this program does SDG&E use? Has SDG&E modified it or added any fuel models? | SDG&E uses Wildfire Analyst with annual updates from Technosylva Fuels program service. The SDG&E fuels models, unlike Landfire and other products, are based on an Object Based Image Analysis (OBIA) that utilizes current orthoimagery, satellite imagery, lidar, MS buildings, Landfire 2019/2020, historical fire perimeters, severity models, and other ancillary data in combination with machine learn techniques to characterize the landscape. The Scott & Burgan (200%) family of fuel models are utilized, along with custom fuel models in urban, road, agriculture, water and timber areas. Also, based on a ML model, Lidar based crown fuel variables were computed for the whole State, a significant advance from actual Landfire canopy variables. It is important to understand that when using this methodology, the fuel model assignments in the territory are not based on pixels, but are based on objects (polygons). The characterization of the fuel models is based on the full fuel models behavior inside the polygon: the individual type of vegetation in one pixel is not considered relevant and the fuel model assignment to each polygon reflects the distribution of the vegetation inside each polygon and the expected fire behavior of that fuel distribution. | Sara Moore | 2023-05-26 | 2023-06-01 | 2023-06-01 | https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-02.pdf | 0 | No | Other | Landscape Fuel Modeling Program | N/A | N/A
176 | OEIS | 2023-02 | OEIS-2023-02 | 2 | OEIS-2023-02.2 | Regarding SDG&E’s Weather Station Standards a. SDG&E states on page 302 (8.3.2.4.1) of the Base WMP “…the entire Weather Station Network is on a rotating calibration schedule…” and then goes to state on page 325 (8.3.5.5.4) “All weather stations are calibrated once per year.” i.Provide the installation and equipment standard that all SDG&E weather stations are installed to, including height from ground, direction of cross-arm, and which side of the pole/tower they are installed on. ii.Provide the total number of stations that were serviced annually over the past 3 years, and the maintenance preformed on each station. iii.Provide the total number of stations not serviced annually over the past 3 years. iv.Provide the estimated life span of each sensor and the replacement cycle for each. v.Provide the total number of repair requests initiated, per year, over the past 3 years. Include the time duration from initiation to completion of repair. | a.i. Please see attachments “Weather_Monitoring_System-Q02ai.pdf” and “Weather_Station_Calibration_Training-Q02ai.pdf.” a.ii 2020: 189 of 191 existing stations were calibrated. Two were removed from service due to undergrounding. A total of 31 new weather stations were installed and the calibration cycle for the new stations began in 2021. 2021: 220 weather stations calibrated (all except one newly-installed station). 2022: 221 weather stations calibrated (all except one station). a.iii Occasionally crews cannot reach a station to calibrate due to access issues (i.e. road washed out). Last year, one station was not calibrated due to such issues. a.iv. Estimated lifespan of five to ten years, which varies based on environmental conditions. Changes in communications technology or sunset of services can render devices obsolete.a.v. Attachment “WeeklyWX_PerformanceLog-Q02av.xlsx” provides basic overview of repair requests, however, more time would be needed to provide actual numbers. Average of one to three repair requests weekly, primarily either sensor or communications issues. Most are resolved within a week or so. Some issues may take months to resolve, such as communications issues due to the loss of a cell tower out of our control. | Sara Moore | 2023-05-26 | 2023-06-01 | 2023-06-01 | https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-02.pdf | 0 | No | 8.3.2 | 8.3.2 Environmental Monitoring Systems Page 301 | 8.3.2.4.1 | 8.3.2.4.1 Weather Stations and NDVI Cameras Page 306
177 | OEIS | 2023-02 | OEIS-2023-02 | 3 | OEIS-2023-02.3 | Regarding SDG&E’s Fuel Sampling Program a. SDG&E states on page 302 (8.3.2.4.2) of the Base WMP that it “…has begun implementing its own fuel moisture network of sensors to augment the existing Remote Automated Weather Stations (RAWS) DFM sensors throughout the county” and then on page 331 (8.3.6.3) states, “In 2023, continue to install DFM sensors on existing weather stations where fuel moisture data is sparse.” i.Provide a map of SDG&E’s Live Fuel Moisture (LFM) and Dead Fuel Moisture (DFM) sampling sites, including the U.S. Forest Service sampling sites utilized. ii.Provide a listing of the vegetation types SDG&E samples at each location and number of times per month SDG&E takes vegetation samples. iii.Provide the number of DFM sensors that SDG&E will add in 2023, along with their locations. iv.Does SDG&E use the National Fuel Moisture Database (or any other publicly accessible location) to store/share its results or derive further information from? | a.i. Please see attachment SDGE_Region_FM_Sites-Q03ai.PNG. a.ii. SDG&E currently only samples dead fuel moistures, therefore vegetation types are limited to dead and downed small sticks, twigs, leaves, and other vegetative debris. New observations are recorded every 10 minutes, resulting in 144 observations per day and more than 4,000 observations per month at five sites. a.iii. SDG&E will add three DFM sensors to the following weather station sites in 2023: Del Dios Highway (lat/lon = 33.03718/-117.16545) Elfin Forest (lat/lon = 33.07573/-117.19144) Barona Mesa (lat/lon = 32.97770/-116.78030) a.iv All SDG&E DFM data is available through MesoWest (https://mesowest.utah.edu/). SDG&E has leveraged the National Fuel Moisture Database to access historical and current LFM data. | Sara Moore | 2023-05-26 | 2023-06-01 | 2023-06-01 | https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-02.pdf | 0 | No | 8.3.2 | 8.3.2 Environmental Monitoring Systems Page 301 | 8.3.2.4.2 | 8.3.2.4.2 Fuel Moisture Page 306
178 | OEIS | 2023-02 | OEIS-2023-02 | 4 | OEIS-2023-02.4 | Regarding Sensitive Relay Profiles and Settings a. In response to SDGE-22-24, SDG&E states that 450 protective devices are capable of sensitive relay profiles (SRPs) across 225 circuits. Please provide: i. The associated percentage of circuits by mileage covered by these 450 protective devices. ii. The associated percentage of circuits within Tier 2 HFTD by mileage covered by these 450 protective devices. iii. The associated percentage of circuits within Tier 3 HFTD by mileage covered by these 450 protective devices. b. SDG&E states on page 233 of the Base WMP that “A study was completed to determine the impact of sensitive relay settings at reducing ignitions from risk events.” SDG&E also provides the results from this study in Table 8-29, “Ignition Rate with SRP Enabled” (p. 233). i. Provide the internal report or memo that describes the findings from this study. ii. If not included in the report or memo, provide separately the steps taken to determine the new settings and an explanation why these settings were found to be the most optimal ones for wildfire protection and customer reliability | a. In response to SDGE-22-24, SDG&E states that 450 protective devices are capable of sensitive relay profiles (SRPs) across 225 circuits. Please provide: i. The associated percentage of circuits by mileage covered by these 450 protective devices. ii. The associated percentage of circuits within Tier 2 HFTD by mileage covered by these 450 protective devices. iii. The associated percentage of circuits within Tier 3 HFTD by mileage covered by these 450 protective devices. b.i. Please see excel spreadsheet “4b.i_OEIS-P-WMP_2023-SDGE-002.xlsx” in folder. b.ii. The study provided in Item 4b (i) was not used for the purpose of determining optimal SRP settings but instead was used to quantify the impact that SRP settings have reducing ignition risks. SDG&E has a defined methodology for setting SRP that is used throughout our territory regardless of device location. SDG&E notes that it has employed the use of SRP as a wildfire mitigation tool for over a decade with minimal complaints from customers, and SRP-caused outages represent a small fraction of overall unplanned outages. | Sara Moore | 2023-05-26 | 2023-06-01 | 6/1/2023 & 6/7/2023 | https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-02.pdf | 0 | No | 8.1.8.1 | 8.1.8.1 Equipment Settings to Reduce Wildfire Risk Page 234 | 8.1.8.1.1 | 8.1.8.1.1 Protective Equipment and Device Settings Page 234
179 | OEIS | 2023-02 | OEIS-2023-02 | 5 | OEIS-2023-02.5 | Regarding Covered Conductor Maintenance Has SDG&E modified any of its inspection or maintenance practices to address covered conductor-related issues? If so, provide a description of these practices, including inspection checklists. | SDG&E has not modified any of its inspection or maintenance practices to address covered conductor-related issues at this time. | Sara Moore | 2023-05-26 | 2023-06-01 | 2023-06-01 | https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-02.pdf | 0 | No | Other | Covered Conductor Maintenance | N/A | N/A
180 | OEIS | 2023-02 | OEIS-2023-02 | 6 | OEIS-2023-02.6 | Regarding SDG&E’s Asset Inspection Program a. Provide the inspection checklists used for both SDG&E’s patrols and detailed inspections. b. Provide the QA/QC inspection checklists used for asset-related inspections. c. What items within the inspections checklist, if any, has SDG&E tailored to address wildfire risk-specific concerns? Which of these items differ from the items in the checklist associated with the standard GO 95 inspections? d. On average, how many detailed inspections are completed by inspectors per day? | a. Inspection checklists and requirements are found in the Corrective Maintenance Program Manual for electric distribution overhead patrols and detailed inspections. (2018 CMP Manual is provided in response folder for additional documentation). b. QA/QC inspections ended as of 2022 and were replaced with Risk-Informed Drone Inspections. Inspectors currently use the overhead detailed inspection checklists found in the 2018 Corrective Maintenance Program Manual. c. The overhead condition code template found on pages 46-48 of the Corrective Maintenance Program Manual identify codes under QC cycle (far right hand column). These QC codes were identified as having fire risk potential versus other condition codes associated with standard GO95 inspections. d. Depending on terrain and location, an average of 20 detailed inspections are completed per day per inspector. | Sara Moore | 2023-05-26 | 2023-06-01 | 2023-06-01 | https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-02.pdf | 0 | No | Other | Asset Inspection Program | N/A | N/A
182 | OEIS | 2023-03 | OEIS-2023-03 | 1 | OEIS-2023-03.1 | Regarding Table 8-38 “Emergency Preparedness Staffing and Qualifications” a. OEIS Table 8-38 “Emergency Preparedness Staffing and Qualifications” (ps. 345-354) lists a set of positions in the “Role” column. In some cases, it’s self-evident why a position is included (e.g., Access and Functional Needs Liaison) and in others it’s less self-evident (e.g., Gas Operations Commodity Liaison). By what criteria were positions selected to be included in that table? b. Which position in this table is the lead for PSPS emergency response concerns? c. Energy Safety notes that per the “Qualifications” column in that same table none of the positions included in this table are required to take the Incident Command System (ICS) 300 or ICS 400 courses. Is SDG&E intending to include these courses as requirements and if so for which positions? And/or does SDG&E have an equivalent training that it provides and if so for which positions? d. Are there any emergency preparedness trainings that are required of the positions in Table 8-38 that are not listed in the table under “Qualifications”? i. If so, please give the title of the training(s), the name of the provider, and which positions are required to take the training(s). e. Are any trainings required of the positions in this table specifically aimed at supporting collaborations with tribal communities? Are any trainings specifically aimed at supporting access and functional needs communities? i. If so, please give the title of the training(s), the name of the provider, and which positions are required to take the training(s). | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2 and 3. Subject to and without waiving the foregoing objections, SDG&E responds as follows: a. The positions were selected based on the direction from CAL OES California Standardized Training Institute (CSTI). All Command and General Staff positions will work towards a CAL OES EOC Utility Branch Credential. Command and General staff positions are section leads and above. b. There is no position that is considered a “lead” for PSPS emergency response concerns. SDG&E’s EOC is an all-hazards organization which does not change based on incident or event type. All positions with the EOC are trained on the appropriate protocols, processes, and procedures for PSPS respone c. SDG&E follows the CAL OES CSTI training plan for the EOC credential which does not require ICS 300 & 400.i. If so, please give the title of the training(s), the name of the provider, and which positions are required to take the training(s). N/A d. The only other trainings are internal which consist of EOC New Member Orientation, Summer Readiness, and Section Specific Mentoring. These trainings are provided by the internal Training & Exercise team and are required for all EOC responders. e. There are no required formal trainings for collaborations with tribal partners however our tribal liaisons work with our tribal partners on a consistent basis year-round. AFN Liaisons will be required to take a FEMA course ICS 368 which is in the process of being updated. There is a joint IOU team working with CSTI to customize the training to be more appropriate for utility AFN responders. | Sara Moore | 6/2/23023 | 2023-06-08 | 2023-06-08 | https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-03.pdf | 0 | No | OEIS Table 8-38 | Emergency Preparedness Staffing and Qualifications | N/A | N/A
183 | OEIS | 2023-03 | OEIS-2023-03 | 2 | OEIS-2023-03.2 | Regarding Projected Risk Reduction on Highest-Risk Circuits Scoped Outside of this WMP Cycle for Mitigation. Please provide a list of the top 5% of highest-risk circuit segments scoped outside of this WMP cycle for mitigation (e.g., not found in OEIS Table 7-4) with a description of each such segment, including: a. Any risk analysis findings, including risk score for the segment b. Total circuit miles in the segment and the asset description c. What mitigation initiatives have been undertaken thus far for the segment, including the completion date for each initiative d. The type of mitigation initiative planned for the segment (e.g., undergrounding or covered conductor) in future WMP cycles e. By what year the circuit segment will be fully mitigated f. What, if any, interim mitigation initiatives are planned to reduce risk on the circuit segment | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2 and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: See file “2023_WMP_OEIS_DR 3_Question_2_nb_output_KM_2023_06_06.xlsx.” Please see sheet titled ‘output’ for the data, and sheet titled ‘notes’ for additional clarifications and metadata on the output. | Sara Moore | 6/2/23023 | 2023-06-08 | 2023-06-08 | https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-03.pdf https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-03%20Attachment%20Q2.xlsx | 1 | No | Other | Projected Risk Reduction on Highest-Risk Circuits Scoped Outside of this WMP | N/A | N/A
184 | OEIS | 2023-03 | OEIS-2023-03 | 3 | OEIS-2023-03.3 | Regarding Risk Buy-down Estimates (Risk-Spend Efficiency) Information Required by the WMP Technical Guidelines The WMP Technical Guidelines require utilities to provide specific information on their use of risk buy-down estimates (e.g., risk-spend efficiency), resource optimization to maximize risk reduction, and prioritization of mitigation initiatives (Sections 7.1.4.1 and 7.1.4.2). The information provided by SDG&E does not allow an evaluator to reconcile content from Section 7 and it is also missing important information about risk buy-down estimates. In particular, evaluators need a detailed description of the risk buy-down estimation process to reconcile with the information provided in Tables 7-4 and 8-1 a. Please provide the following information in MS Word or MS Excel, as appropriate: i. Risk buy-down information in a table as follows, ranked in descending order of risk buy-down estimate (column G). Mitigation initiative (column “applicabl e initiatives” , Table 8- 1) Initiative Tracking ID WMP Categor y Circuit Segments Impacted Estimate d Risk Reductio n Estimated Cost Risk Buy-Down Estimate (Risk Reduction/Cost) - - - - - - - - - - - - - - - - - - - - - ii. Please submit an updated version of Table 7.4 that cross-references the table above. This cross-referencing can be done by assigning an index number to each mitigation initiative, where the index number is the risk buy-down estimate ranking from the table above. iii. Additionally, please submit a narrative explanation of how the information in the table above informed the prioritization of mitigation initiatives. Please include any instances where a mitigation initiative with a lower risk buy-down estimate received a higher priority over a mitigation initiative with a higher risk buy-down estimate. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2 and 9. Subject to and without waiving the foregoing objections, SDG&E responds as follows: i. See attached spreadsheet titled “Q3_i_Risk reduction and costs.xlsx.” ii. OEIS table 7-4 refers to the risk reduction at the circuit segment level for the Covered Conductor and Strategic Undergrounding programs as calculated by SDG&E’s WiNGS-Planning tool. The risk reduction values in this table are based on the segment-level information calculated within WiNGS-Planning. The risk reduction values presented in response to part ii reflect the risk reduction values of the programs at the tranche level for the respective HFTD tiers where installations occur for all mitigations. Due to the differences in the level of information and the calculations performed, these risk reduction values should not be directly compared against one another. For these reasons, the mitigations provided in response to part ii cannot be directly crossreferenced to Table 7-4. SDG&E’s mitigations (outside of covered conductor and undergrounding) are largely scoped and performed across the entire HFTD including the circuits referenced in Table 7-4, but risk reduction is not calculated at the circuit segment level. iii. SDG&E utilizes several components to make risk-informed decisions to prioritize mitigation initiatives. These components can be found in OEIS Table 4-2 of SDG&E’s 2023 WMP and are further described in Section 4.4.2. The risk reduction and RSE values represented at the tranche level are reviewed to ensure the programs will provide value and are one of many components that are taken into consideration when determining which mitigation is chosen. Subject matter expertise is utilized to understand the timeline for implementation, resource availability, and other factors to determine the capability to perform the work, and the appropriate level of investment. | Sara Moore | 6/2/23023 | 2023-06-08 | 2023-06-08 | https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-03.pdf https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-03%20Attachment%20Q3.xlsx | 1 | No | 7.1.4.1 & 7.1.4.2 | 7.1.4.1 Identifying and Evaluating Mitigation Initiatives Page 105 7.1.4.2 Mitigation Initiative Prioritization Page 108 | N/A | N/A
185 | OEIS | 2023-03 | OEIS-2023-03 | 4 | OEIS-2023-03.4 | Regarding Appendix B Items That Are Currently Optional Or “By Request” Only Please provide the following information, as described in the 2023-2025 Wildfire Mitigation Plan Technical Guidelines, Appendix B. If the information is tabular (e.g., formulas, tables, graphs, charts), please provide it in MS Excel format. If it is text-heavy, please provide it in MS Word format or (for very large files) PDF format. a. Please provide detailed model documentation for each model and sub-model discussed in SDG&E’s response to Section 6.1.2 “Summary of Risk Models” including all models outlined in Table 6-1. i. Technical documentation should be presented according to ASTM E 1472 – Standard Guide for Documenting Computer Software for Fire Models. ii. Include a list of assumptions and known model limitations according to ASTM E 1895 – Standard Guide for Determining Uses and Limitations of Deterministic Fire Models. iii. Present verification and validation documentation according to the SFPE’s Guidelines for Substantiating a Fire Model for a Given Application or ASTM E 1355 – Standard Guide for Evaluating the Predicting Capability of Deterministic Fire Models. 1. At a minimum, the documentation must include:1 a. Purpose of the model/problem identification, b. Model version, c. Theoretical foundation, d. Mathematical foundation, e. External dependencies, f. Model substantiation, g. Sensitivity i. Model Substantiation:2 for each model, provide documentation of the following model substantiation studies: 1. Validation data 2. Model verification 3. Model validation 4. Model calibration b. Additional models supporting SDG&E’s risk calculation3 i. For each additional model that supports the risk calculations, provide weather analysis and fuel conditions. c. Calculation of risk and risk components: likelihood.4 Please provide more information on: ii. Ignition likelihood iii. Equipment likelihood of ignition iv. Contact from vegetation likelihood of ignition v. Contact from object likelihood of ignition vi. Burn probability vii. PSPS likelihood d. Calculation of risk and risk components: consequence.5 Please provide more information on: i. Wildfire consequence ii. Wildfire hazard intensity iii. Wildfire exposure potential iv. Wildfire vulnerability e. Calculation of risk and risk components: PSPS consequence.6 Please provide more information on: i. PSPS exposure potential ii. Community vulnerability to PSPS f. Calculation of risk and risk components: risk.7 Please provide more information on: i. Ignition risk ii. PSPS risk iii. Overall utility risk | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2 and 6. Subject to and without waiving the foregoing objections, SDG&E responds as follows: NOTE: This question is identical to question 1 in OEIS-SDGE-2023WMP-01. Link to the 2023 WMP: https://www.sdge.com/2023-wildfire-mitigation-plan WiNGS Planning: i. WMP technical documentation: Attached as “Model Documentation_Wings Planning V1_FINAL SUBMITTED.pdf,” ii. Reference section 6.2.3 of WMP 2023 (page 73) and 2.4.3 – Technical document for WiNGS Planning. iii. Reference section 2.6 of technical document for WiNGS Planning. At a minimum, the documentation must include: (a) Purpose of the model/problem identification – reference sections 1.1 and 2.1.1 - Technical document for Wings Planning (b) Model version = reference section 1.2 - Technical document for Wings Planning (c) Theoretical foundation – reference section 2.3 - Technical document for Wings Planning (d) Mathematical foundation – reference section 2.4 - Technical document for Wings Planning (e) External dependencies – reference section 2.5.1 - Technical document for Wings Planning (f) Model substantiation - reference section 2.6 - Technical document for Wings Planning (g) Sensitivity – reference section 2.6.2 - Technical document for Wings Planning (i) Model Substantiation: for each model, provide documentation of the following model substantiation studies: 1. Validation data reference section 2.6.2 - Technical document for Wings Planning 2. Model verification - reference section 2.6.1 - Technical document for Wings Planning 3. Model validation - reference section 2.6.2 - Technical document for Wings Planning 4. Model calibration - reference section 2.6.3 - Technical document for Wings Planning b. Additional Models Supporting Risk Calculation: i. For each additional model that supports the risk calculations, provide weather analysis and fuel conditions. Reference section 2.5 - Technical document for Wings Planning c. Calculation of Risk and Risk Components: Likelihood - reference 6.2.2.1 of WMP 2023 (page 68) and section 2.4.1.3 - Technical document for Wings Planning i. Ignition Likelihood ii. Equipment Likelihood of Ignition iii. Contact from Vegetation Likelihood of Ignition iv. Contact from Object Likelihood of Ignition v. Burn Probability vi. PSPS Likelihood d. Calculation of Risk and Risk Components: Consequence - reference 6.2.2.2 of WMP 2023 (page 70) and section 2.4.1.4 - Technical document for Wings Planning i. Wildfire Consequence ii. Wildfire Hazard Intensity iii. Wildfire Exposure Potential iv. Wildfire Vulnerability e. Calculation of Risk and Risk Components: PSPS Consequence - reference 6.2.2.2 of WMP 2023 (page 70) i. PSPS Exposure Potential ii. Community Vulnerability to PSPS f. Calculation of Risk and Risk Components: Risk- reference section 6.2.1 and 6.2.2 of WMP 2023, page 59 and 64 i. Ignition Risk ii. PSPS Risk iii. Overall Utility Risk WiNGS Ops: a. i. WMP technical documentation: Attached as “Model Documentation_WiNGS-Ops V1_FINAL SUBMITTED.pdf.” ii. Reference section 6.2.3 of WMP 2023 (page 73) and 2.4.3 – Technical document for WiNGS Ops. iii. Reference section 2.6 of technical document for WiNGS Ops At a minimum, the documentation must include: (a) Purpose of the model/problem identification – reference sections 1.1 and 2.1.1 - Technical document for Wings Ops (b) Model version – (c) Theoretical foundation – Section 2.2.1 – Technical documentation for WiNGS Ops (d) Mathematical foundation Section 2.2.1 - Technical documentation for WiNGS Ops (e) External dependencies – reference section 2.5.1 - Technical document for Wings Ops (f) Model substantiation - Section 2.6 - Technical documentation for WiNGS Ops (g) Sensitivity – Section 2.6.2 - Technical documentation for WiNGS Ops (i) Model Substantiation: for each model, provide documentation of the following model substantiation studies: 1. Validation data 2. Model verification – Section 2.6.1 - Technical documentation for WiNGS Ops 3. Model validation – Section 2.6.2 - Technical documentation for WiNGS Ops 4. Model calibration – Section 2.6.3 - Technical documentation for WiNGS Ops | Sara Moore | 6/2/23023 | 2023-06-08 | 2023-06-08 | https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-03.pdf | 0 | No | 6.1.2 | 6.1.2 Summary of Risk Models Page 54 | Table 6-1 | N/A
186 | OEIS | 2023-04 | OEIS-2023-04 | 1 | OEIS-2023-04.1 | Regarding SDG&E’s Company Emergency and Disaster Preparedness Plan Please provide SDG&E’s Company Emergency and Disaster Preparedness Plan (CEADPP) either as a digital document or link to a website. | SDG&E’s latest Company Emergency and Disaster Preparedness Plan (CEADPP) is attached as “Q1.CEADPP-Rev 3-2023 updatePublic.pdf” | Sara Moore | 2023-06-09 | 2023-06-14 | 2023-06-14 | https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-04.pdf https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-04%20Attachment%20Q1.pdf | 1 | No | Other | Emergency and Disaster Preparedness Plan | N/A | N/A
187 | OEIS | 2023-04 | OEIS-2023-04 | 2 | OEIS-2023-04.2 | Regarding Emergency Preparedness After Action Reports Please provide all Emergency Preparedness After Action Reports related to wildfires and PSPS for 2021, 2022, and 2023 (if applicable), including any updates to Corrective Action Plan measures. | Attached are the following documents: • Q2.After Action Report_Improvement Plan_Border 32 Fire_FINAL.pdf • Q2.After Action Report_Improvement Plan_PSPS 11.22.2021_FINAL.pdf • Q2.Border 32 Corrective Actions.pdf • Q2.PSPS 11-22-21 Corrective Actions..pdf | Sara Moore | 2023-06-09 | 2023-06-14 | 2023-06-14 | https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-04.pdf https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-04%20Attachment%20Q2.zip | 1 | No | Other | Emergency Preparedness After Action Reports | N/A | N/A
188 | OEIS | 2023-04 | OEIS-2023-04 | 3 | OEIS-2023-04.3 | Regarding Emergency Preparedness Key Personnel, Qualifications, and Training On page 342 of its 2023-2025 WMP (Section 8.4.2.1.3 “Key Personnel, Qualifications, and Training”), SDG&E states, “a comprehensive training program has been implemented to support outage restoration, patrols, inspections, and maintenance...” Please provide the following details about this training program: a. A list of trainings included in this training program including the course provider and which Emergency Operations Center (EOC) positions are required to take each course. | SDG&E provides the following courses internally: Relief Electric Troubleshooter Task #14 STUEM300 CMP Line Patrol Inspections Task #15 Fire Calls (LINK) Task #046 Wildland Fire Prevention (LINK) Task #047 Public Safety Power Shutoff (LINK) SFUGN1O3 Wildland Fire Prevention & Safety Electric Troubleshooter STUEM300 CMP Line Patrol Inspections ESCPS205 PSPS Patroller (VR) ESCPS100 PSPS / Fire Training SFUGN1O3 Wildland Fire Prevention & Safety Relief Fault Finder ESCPS100 PSPS / Fire Training SFUGN1O3 Wildland Fire Prevention & Safety ESP 113.1 reviewed and discussed in class The following internal courses are required to obtain journeyman/linemen status, as applicable. Course Code Class Description STULA100 Line Assistant Orientation STUAP100 Apprentice Lineman Climbing STUAP115 Apprentice Lineman Beginning Secondary STUAP300 Apprentice Lineman U.G. Phase 1 STUAP120 Apprentice lineman Advanced Secondary STUAP125 Apprentice Lineman Transformer Connection Course Code Class Description STUAP126 Apprentice Lineman Hot Stick STUAP129 Apprentice Lineman 12kV Rubber Glove STUAP125 Apprentice Lineman 4kV Rubber Glove STUAP315 Apprentice Lineman UG Phase 3 STUEL320 U.G. CMP (initial) STUEL310 O.H. CMP (initial) STUEL115 Relief Fault Finder | Sara Moore | 2023-06-09 | 2023-06-14 | 2023-06-14 | https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-04.pdf | 0 | No | 8.4.2.1.3 | 8.4.2.1.3 Key Personnel, Qualifications, and Training Page 345 | N/A | N/A
189 | OEIS | 2023-04 | OEIS-2023-04 | 4 | OEIS-2023-04.4 | Regarding the Companywide Implementation of an Incident Command System On page 343 of its 2023-2025 WMP (Section 8.4.2.1.8 “Improvements/Updates since the Last WMP Submission”), SDG&E states, “Enhancements to CEADPP made in 2022: […] Updated the organization charts as we continue to implement companywide [Incident Command System]” (bold added). a. Please describe where SDG&E stands in its progress implementing a companywide Incident Command System (e.g., estimated percent of completion) and by what date (month and year) it expects to have completed implementing a companywide Incident Command System. b. Please clarify how these two statements relate to each other: a “comprehensive training program has been implemented” (p. 342); “we continue to implement companywide ICS” (p. 343). | a. Implementation of ICS is a continuous effort designed to capture a high attrition rate of emergency responders typically seen with career changes, retirements, and organizational changes. Currently, all onboarded EOC and field responders have been trained on the fundamentals of ICS and its application in a utility company, and ongoing training and mentorship is being provided to new and future team members. This continued effort is being led by the Training and Exercise Team in collaboration with the Operational Field and Emergency Readiness Team. b. SDG&E’s Emergency Management Training and Exercise Team, in collaboration with the Operational Field and Emergency Readiness Team, continue to support and facilitate robust ICS and responder training in compliance with external requirements and company needs. Training is a component of a functioning ICS structure but is not isolated as the sole element of success of ICS implementation. SDG&E will continue to support required and beneficial ICS training as part of ICS for the enterprise. | Sara Moore | 2023-06-09 | 2023-06-14 | 2023-06-14 | https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-04.pdf | 0 | No | 8.4.2.1.8 | 8.4.2.1.8 Improvements/Updates since the Last WMP Submission Page 346 | N/A | N/A
190 | OEIS | 2023-04 | OEIS-2023-04 | 5 | OEIS-2023-04.5 | Regarding the Verification Methods for 3- and 10-year Emergency Preparedness Objectives Please describe in a narrative format (2-3 sentences) the verification method for the following 3- and 10-year objectives from OEIS Table 8-33 “Emergency Preparedness Initiative Objectives (3-year plan)” and OEIS Table 8-34 “Emergency Preparedness Initiative Objectives (10-year plan).” Specify how the verification method will be used to verify that the objective is completed or implemented. a. From OEIS Table 8-33 “Emergency Preparedness Initiative Objectives (3-year plan)” (WMP p. 333) From OEIS Table 8-34 “Emergency Preparedness Initiative Objectives (10-year plan)” (WMP p. 335) | (a.i): Modernize and enhance workforce training in the areas of storm response, process, and documentation (collab with DOC-E and ERO After action reports are completed after each emergency event and reviewed to ensure emergency response training curriculums are adequate. Where there are areas for improvement, curriculums will be updated accordingly. SDG&E’s skills training center also proactively looks for opportunities to improve trainings utilizing technology, such as virtual reality. (a.ii): Expand Emergency Management Operations by increasing staff dedicated to enhancing various emergency programs. All IT related emergency management efforts are managed through IT in support of expanding Emergency Management Operations. Contract support has been obtained to manage and maintain all the computers in the EOC on an alternating (between primary and backup) monthly basis as we all and provide dedicated support for all EM staff to ensure the operational status of the assets. Daily tests are completed for all key dashboards used in making decisions in the EOC for events utilizing an automated test solution. (a.iii): Continue participation [in] and support of Mutual Assistance Programs Actively engaging in the continuation of agreements and collaborative efforts with other IOUs will ensure the continuation of participation in and support of mutual assistance programs. This engagement involves regularly reviewing and updating existing agreements (American Gas Association, California Utilities Emergency Association, Edison Electric Institute, Western Regional Mutual Assistance Group), fostering open communication channels with other IOUs statewide and regionally, and participating in mutual assistance deployments. (a.iv): Continue collaboration with 211 in San Diego and Orange County to support AFN customers To further facilitate collaboration between 211 San Diego and Orange County as well as other AFN support partners, SDG&E convenes a regional working group, which is a collaborative and informative session bringing together CBO, local government, and utility representatives to share lessons learned and refine SDG&E’s de-energization protocols. These de-energization protocols are put into practice alongside community partners with tabletop exercises which emphasize operational coordination, communication, public information and warning, and community resilience. The regional working group attendance is tracked, items discussed summarized and distributed to participants, and serves as a venue for relevant lessons learned from the exercise to be reviewed. (a.v): Enhance community outreach by incorporating effectiveness outreach survey feedback, expanding Tribal and AFN campaigns, enhancing partnerships with Indian Councils, Community Based Organizations (CBOs), and local school districts: Every year customer feedback is solicited about Wildfire Safety public education efforts using surveys. The feedback focuses on measuring recall and comprehension of communication tactics and messaging. The results of the feedback are then compared to the previous year’s customer research to measure public education performance and is then used to improve communications for the following year. For the second year, SDG&E conducted a focus group at the Annual Intertribal Long Term Recovery Foundation Resiliency Breakfast to get feedback on how SDG&E can continue to improve communication to connect support programs to tribal communities. Based on feedback received from the focus group discussions, SDG&E will provide presentations to the Tribal Fire Departments and incorporate cultural education on tribal knowledge and their relationship with fire at events and workshops. This year, SDG&E expanded their outreach by participating in the Southern Indian Health Council Healthy Family events. Additionally, Iipay Nation of Santa Ysabel is partnering with SDG&E to host a Wildfire Safety Fair in September. SDG&E continues to expand its reach to individuals with AFN by adding CBOs to its Energy Solutions Partner network that reach key demographics. These partnerships are leveraged to share Wildfire Safety and Preparedness public-education messaging through monthly social media toolkits, events, and presentations. Through these CBOs, SDG&E consistently seeks recommendations on ways to enhance our outreach and education efforts through 1x1 touchpoints with a dedicated Outreach Advisor. An annual survey is conducted of Critical Facility and Critical Infrastructure (CFCI) customers, including school districts, to measure their level of emergency preparedness and resiliency. The annual survey assesses and promotes public education regarding the importance of PSPS related emergency preparedness. School districts are given an opportunity to provide feedback regarding their PSPS emergency readiness and SDG&E’s methods of outreach. Additionally, CFCI educational webinars are held in advance of wildfire season to prepare school customers for potential PSPS events. Lastly, school districts have an assigned account executive that works closely with the districts to ensure their preparedness. (b.i): Increase stakeholder engagement and use of simulations to stress-test all-hazards response plans. Training and Exercise in collaboration with appropriate subject matter experts from the enterprise develop multiple HSEEP-guided exercises of both discussion and operations-based categories throughout the year to exercise current response plans and standard operating procedures. Leading up to these exercises, Training and Exercise invites all public safety partners to collaborate either as observers, planners, evaluators, or players in the exercises in compatible HSEEP planning processes and does additional outreach to targeted partners when requested via appropriate channels. Following the exercises, partners are invited to participate in feedback sessions and to give written feedback for lessons learned and suggestions for changes with stakeholders following best practices for AARs, Hotwashes, and written feedback solicitation. (b.ii): Develop Training Environments to better simulate all hazards and allow for more realistic exercises and training. This is an ongoing goal supported most recently by the development of a training environment for a PSPS dashboard. As the Training and Exercise program continues to develop in maturity, it will continue to support best practices for adhering to HSEEP compatible training and exercise experiences in venues most appropriate to the needs of responders for targeted all hazard preparedness. Like stated above, SDG&E will continue to work with partners and stakeholders in development of these training experiences and opportunities and will continue to gather feedback in HSEEP compatible AARs, Hotwashes, and written feedback solicitation. (b.iii): Establish more formalized review of operating procedures, benchmarking, and stakeholder engagement We currently have a formal review process guided by California Public Utilities Commission regulation, under General Order 166 and California State Assembly Bill 1650. This requirement is an annual review / presentation of our Company Emergency and Disaster Preparedness Plan. This regulatory review is led by company subject matter experts and presented to company stakeholders, community stakeholders including tribal and access and functional needs communities (AFN), as well as public safety partners consisting of first responders and government leaders. In addition, per our internal plans and maintenance policy, if a change in organization or regulatory requirement occurs, the plan is updated immediately irrespective of review schedules. (b.iv): Enhance customer communication and ability to reach vulnerable populations during emergencies. AFN Self-Identification campaign. The AFN Self-Identification effort is used to help identify Access and Functional Needs customers and their needs in order to target this segment when needed. Annual mailings are also sent to these customers about resources that are available during a wildfire, Public Safety Power shutoff or other emergency situations. (b.v): Enhance post event documentation and application of lessons learned to update plans and exercises. Agendas: These meetings provide opportunities to review plans, lessons learned, and survey results to share information across service territories and strengthen IOU alignment on AFN service delivery. Post-season PSPS survey results are shared, AFN notification plans are reviewed, and feedback from our partners in attendance is collected and applied. PSPS Pre-Season Report: PSPS Pre-Season Reports describe all the actions SDG&E has taken, or is taking, in preparation for potential PSPS events during the upcoming wildfire season. The reports specify lessons learned from past events, and how SDG&E is applying those lessons to their current preparations. Lessons Learned: SDG&E’s Emergency Management Training and Exercise Team, in collaboration with the Operational Field and Emergency Readiness Team, continue to support and facilitate the process of integrating lessons learned from identified corrective actions from HSEEP compatible post-event and post-exercise Hotwashes, AARs, and solicited feedback. After reviewing identified areas for improvement, Training and Exercise works with stakeholders and subject matter experts to incorporate the appropriate findings first into coverage in training curriculum and then into scenarios, expected actions, and events lists in exercises. Responses to expected actions are reviewed post-exercise and training to determine if additional training and support is needed to address areas needing improvements. | Sara Moore | 2023-06-09 | 2023-06-14 | 2023-06-14 | https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-04.pdf | 0 | No | 8.4.1.1 | 8.4.1.1 Objectives Page 336 | OEIS Table 8-33 | N/A
191 | OEIS | 2023-04 | OEIS-2023-04 | 6 | OEIS-2023-04.6 | Regarding the Progression of the Effectiveness of Enhanced Clearances Joint Study Please provide an update on the following items and the expected completion date for each: a. Standardization of the data collection process for the cross-utility database of tree-caused risk events. b. Determination of where and in what form the database will exist. c. Have the data in a common format and available for queries. | a. The Joint Investor-Owned Utility (IOU) Study on Enhanced Vegetation Clearances for Wildfire Mitigation technical work started in November 2022 and is scheduled to be completed by June 2024. The work is being led by The Electric Power Research Institute (EPRI) who was contracted to perform the third-party verification and analysis associated with the study. The study is divided into four phases: Database Evaluation; Database Development; Data Analysis; and Discussion of Options. Currently, we are completing the first phase, Database Evaluation, which is scheduled to conclude by the end of June 2023. During the Database Evaluation phase, the research team at EPRI requested and evaluated a sample set of data from each IOU. The team also facilitated a set of in-person and remote immersive discussions with each IOU’s respective subject matter experts in vegetation management to better understand what data is currently curated and to evaluate the level of quality and certainty of data contained in the individual IOUs’ database fields. The purpose of the immersive discussions was to understand the current database structures used by each utility, the method of recording data, the type of historical records available, the definitions of specific tree-pruning activities, the differences in the outage management systems, confidence in the time-series of the different database fields, and other information that may vary from utility to utility. Immersive discussions revealed significant differences between the databases from the three utilities. There were thousands of variables across the three different databases, only a subset of which were similar in terms of definition and methods of recording. The research team and IOU SMEs discussed the variables, and which might be the most instructive for understanding the effects of enhanced clearance on wildfire mitigation. Variables under discussion included definition of clearance levels/line clearances, timing of clearances, tree growth rates, event outages, trim codes, types of disturbances, weather at the time of the outage, distance to line of tree caused outage, definition of high fire risk area, date and time of tree caused outage, tree numbering system, tree species, ignition events, tree condition, and tree height, among other variables. The current plan is to streamline the joint IOU database to include just over 25 variables. The IOUs will be given this request for 25 variables and desired time series, to be uploaded to the joint IOU database. In addition to the common data variables, EPRI will also obtain and utilize the large set of the original data variables to more fully understand the data from each utility. There are plans to conduct individual analyses as well as the combined analysis. b. The database will sit on the EPRI Data Science Platform. It is a secure platform located on the EPRI server that will be accessible to the joint IOUs for querying. EPRI is in the process of deciding the best database type and architecture to warehouse the data to meet the needs of the project and to permit the IOUs with easy access. Decisions on this are anticipated in late summer 2023. c. The data will be accepted for ingestion into the joint IOU database in many forms (.csv, Excel files, spatial formats). The Database Development will be the phase where the architecture of the database will be determined and refined. Then, the data will be included into the joint database. The database will include a joint data component as well as individualized databases for each IOU so that the IOU SMEs will be able to conduct separate, individual, and confidential analysis if they would like to further explore their processed data. The Database Development will have an initial phase lasting through August 2023, followed by a Data Analysis phase lasting through March 2024. The research team anticipates that the data will be available for queries by the research team and IOU SMEs by late 2023. | Sara Moore | 2023-06-09 | 2023-06-14 | 2023-06-14 | https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-04.pdf | 0 | No | Other | Ennhanced Clearances Joint Study | N/A | N/A
192 | OEIS | 2023-04 | OEIS-2023-04 | 7 | OEIS-2023-04.7 | Regarding the SDG&E Framework for PSPS Risk The WMP Technical Guidelines for Section 7.1.4.1 “Identifying and Evaluating Mitigation Initiatives” (p.s. 63-64) and Section 7.1.4.2 “Mitigation Initiative Prioritization” (ps. 64-65) require a detailed discussion of likelihood, consequence, exposure potential and vulnerability for risk associated with Public Safety Power Shutoffs (PSPS). In order to help evaluators understand the calculations that produce a PSPS risk score, please provide the following information (in MS Excel format as applicable) on SDG&E’s PSPS-Likelihood (PSPS-L) and PSPS-Consequence (PSPS-C) models and also on how SDG&E calculates the impact of mitigation on PSPS risk: a. Provide details on the inputs to the PSPS-L model and calculation. i. Explain how PSPS protocols, FPI, and any data from other models and/or risk frameworks are combined to produce the likelihood of a PSPS event. This may be explained using a schematic supported by a narrative explanation. (1) In particular, explain how the historical backcast is used to predict future likelihood of a PSPS event. ii. On page 69 of SDG&E’s 2023-2025 WMP, SDG&E states that the PSPS likelihood probability “represents the likelihood that wind speeds measured at the weather station closest to a segment will exceed a set wind speed threshold (e.g., 50 mph) in a year.” Is wind speed therefore the only determinant of PSPS likelihood? iii. SDG&E adds in the same paragraph, “In order to determine the baseline PSPS risk, each segment utilizes the segment-specific probability and the maximum upstream probability.” Please provide a numerical example of how this works. (1) Provide SDG&E’s definition of “upstream” in a narrative format. b. Provide details on the inputs to the PSPS-C model and calculation. iv. Provide a schematic for the PSPS-C model, including process steps. (1) Describe the output of the PSPS lookback, if used. v. Does Customer Classification & Weighting affect the results? (1) If so, please explain how. c. On page 66, SDG&E’s Figure 6-7 “WiNGS-Planning Calculation Schematic” indicates that mitigation impacts are applied to total risk (i.e., the inherent [pre-mitigation] risk score minus the mitigation impact equals the residual [post-mitigation] risk score). Does SDG&E look at the impact of mitigation on the risk components (e.g., wildfire and PSPS) specifically for PSPS risk (i.e., a calculation where the inherent [pre-mitigation] PSPS risk score minus the PSPS mitigation impact equals the residual [post-mitigation] PSPS risk score)? vi. If yes, provide a table showing how the mitigation initiatives with the highest estimated risk reduction impact PSPS risk. | a. i. PSPS LoRE is the likelihood of a PSPS given a probabilistic set of environmental conditions. PSPS LoRE is informed by a PSPS Probability Model, which determines the probability and rate that a circuit segment will experience a PSPS de-energization within a year based on historical data. For more information, reference attached document Model Documentation WiNGS-Planning, section 2.4.2.2 Intermediate Risk Components, subsections PSPS LoRE and section 2.4.2.4 Individual Models, subsection PSPS Probability Model for additional information on PSPS-L. For reference, also see schematic Figure 2: WiNGS-Planning Model Process Flow Diagram in attached document Model Documentation WiNGS-Planning. ii. No, in addition to wind speed, High Fire Days and hardening status is also included. For more information, reference attached document Model Documentation WiNGS-Planning, section 2.4.2.2 Intermediate Risk Components, subsections PSPS LoRE and section 2.4.2.4 Individual Models, subsection PSPS Probability Model for additional information on PSPS-L. iii. PSPS LoRE utilizes data from Meteorology subject matter expertise and is based on the probability that a segment or its upstream segments will experience a PSPS de-energization during a High Fire Day based on their assessed Alert Speed thresholds as well the historical average number of High Fire Days observed. PSPS LoRE can be expressed as the following equation: PSPS LoRE = Incremental Upstream PSPS Probability X Annual Avg High Fire Days The Incremental Upstream PSPS Probability can be expressed as the following equation: Incremental Upstream PSPS Probability = Max(Select PSPS Probability – Maximum Upstream PSPS Probability, 0) Where the Select PSPS Probability is the probability of a select circuit-segment SCADA switch hitting its set alert speed threshold during a High Fire Day event and the Maximum Upstream PSPS Probability is the highest PSPS probability of a Circuit-Segment from a select Circuit-Segment up to its associated Circuit Breaker. Numerical Example: Given, Maximum Upstream PSPS Probability = 2% Annual Avg High Fire Days = 16 Incremental Upstream PSPS Probability = Max(3% - 2%, 0%) = 1% PSPS LoRE = 1% * 16 = 0.16 Upstream refers to the distribution network tracing of an asset (e.g. sectionalizing device) to its associated circuit breaker. b. iv. For detailed information on the calculation, reference section Model Documentation WiNGS-Planning, section 2.4.2.2 Intermediate Risk Components, subsection PSPS CoRE. For reference, also see schematic Figure 2: WiNGS-Planning Model Process Flow Diagram in attached document Model Documentation WiNGS-Planning. Regarding the mentioned ‘PSPS lookback’, this phrase is not immediately clear and would need further clarification to be answered. v. Yes, PSPS CoRE takes into account the customers downstream of where a de-energization may occur. As the impact of a PSPS de-energization is not the same for all customer types, a Customer Type Value Model within the PSPS CoRE element is utilized to account for more granularity in the PSPS consequence calculation. Based on subject matter expert assumptions, different weighting (or scaling factors) is applied to each customer type for the evaluation. For more information on this model and how the wind speed thresholds are incorporated in the PSPS Probability Model, please reference attached document Model Documentation WiNGS-Planning, section 2.4.2.4 Individual Models, subsections Customer Type Value Model. c. Yes vi. For the mitigated hardening states assessed in the model, namely Undergrounding, Covered Conductor, and Traditionally Hardened, the wind alert speed threshold associated with a specific weather station is assessed within the PSPS Probability Model to create an associated PSPS Probability for each of the mitigated hardening states. For more information on this model and how the wind speed thresholds are incorporated in the PSPS Probability Model, please reference attached document Model Documentation WiNGS-Planning, section 2.4.2.4 Individual Models, subsections PSPS Probability Model. | Sara Moore | 2023-06-09 | 2023-06-14 | 2023-06-14 | https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-04.pdf https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-04%20Attachment%20Q7.pdf | 1 | No | 7.1.4.1 | 7.1.4.1 Identifying and Evaluating Mitigation Initiatives Page 105 | N/A | N/A
193 | OEIS | 2023-05 | OEIS-2023-05 | 1 | OEIS-2023-05.1 | Regarding SDG&E’s Air Quality Management Program In Section 8.3.2.4.3 “Air Quality Management Program (WMP.970)” (SDG&E’s WMP page 302), SDG&E states, “The goal of the Air Quality Management Program (WMP.970) is to protect employees from PM2.5 exposure by quickly notifying employees when PM2.5 AQI thresholds are exceeded.” Will SDGE use this program to notify its customers that PM2.5 AQI thresholds are being exceeded as well? If yes, will SDGE place this critical information in a place where customers can get real time alerts? | The goal of SDG&E’s Air Quality Management Program is to protect employees from PM2.5 (particulate matter 2.5 microns or smaller in diameter) by quickly notifying employees when PM2.5 Air Quality Index thresholds are exceeded so they may take appropriate work precautions. Air quality conditions may be the result of wildfire smoke or other, non-wildfire related environmental conditions, however, given that smoke often impacts air quality for SDG&E emergency personnel and responders, this safety initiative was included in SDG&E’s 2023-2025 WMP. SDG&E does not currently plan to issue similar air quality warnings to the public, given the other available services that are more appropriate sources of public air quality warnings. The public can continue to obtain air quality information from the EPA AirNow or San Diego Air Pollution Control District. | Sara Moore | 2023-06-19 | 2023-06-22 | 2023-06-22 | https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-05.pdf | 0 | No | 8.3.2.4.3 | 8.3.2.4.3 Air Quality Management Program Page 306 | N/A | N/A
194 | OEIS | 2023-06 | OEIS-2023-06 | 1 | OEIS-2023-06.1 | Regarding SDG&E’s Early Fault Detection Device Installations SDG&E aims to implement 60 node installations of early fault detection (EFD) technology per year in 2023 through 2025. These installations will be prioritized in locations of older circuits that are not expected to be “significantly hardened” in the next few years. Please provide the risk ranking from the latest WiNGS-Planning tool of the circuits, segments, spans that have been prioritized for EFD device installation, as well as any other key metrics SDG&E is using to prioritize locations for EFD device installation. | SDG&E notes that the WiNGS Planning model is not used to scope the installation of Early Fault Detection (EFD). The WiNGS-Planning model was only used to scope covered conductor and undergrounding applications and did not inform the EFD program. For informational purposes only, attached is a spreadsheet that lists the circuits and their corresponding WiNGS-Planning Risk ranking that are planned to have Early Fault Detection (EFD) including both Advanced Radio Frequency Sensors (ARFS) and Power Quality (PQ) meters. The EFD program takes many considerations into account when selecting the optimal circuits to deploy ARFS or PQ meter EFD. Major criteria used to scope EFD for 2020-2022: 1. Circuits in HFTD Tier 3 or Tier 2 2. Circuits not scheduled to be rebuilt in the next 2-3 years through alternative grid hardening approaches. Other planned hardening was considered to address the need to use equipment for a reasonable life and promote cost efficiencies. This means some of the EFD circuits are usually not as high on the WiNGS model; those higher circuits are likely to be hardened with alternative methods. 3. Circuits with a history of outages related to potential ignition (i.e. undetermined cause, vegetation, animal or equipment failure) 4. Circuits with a high SAIDI/SAIFI. 5. Circuit length (for ARFS) to minimize excessive number of nodes which could extend the time to construct. 6. Circuits that are mainly overhead. Some underground segments may be considered, but every path has overhead facilities which still present a fire risk. 7. Circuits that have predicted cell reception based on provider maps. Actual cell reception was verified during initial fielding. 8. Circuits that may overlap with Falling Conductor Protection (FCP). The line monitors used for FCP are typically placed in similar locations to the EFD nodes. 9. Existing Power Quality monitors that needed to be added to the network. | Sara Moore | 2023-06-22 | 2023-06-27 | 2023-06-27 | https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-06.pdf https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-06%20Attachment%20Q1.xlsx | 1 | No | Other | Key metrics SDG&E is using to prioritize locations for EFD device installation. | N/A | N/A
195 | OEIS | 2023-07 | OEIS-2023-07 | 1 | OEIS-2023-07.1 | Regarding the Progression of the Effectiveness of Enhanced Clearances Joint Study a. Please indicate whether the database being developed by the third-party contractor includes both outages and ignitions caused by vegetation contact. b. Please describe how the third-party contractor and the three large IOUs plan to use the study’s data on vegetation-caused outages to assess the effectiveness of enhanced clearances. c. Please describe how the third-party contractor and the three large IOUs plan to use the study’s data on vegetation-caused ignitions to assess the effectiveness of enhanced clearances. d. Please list the attributes of vegetation-caused risk events that the third-party contractor selected for alignment and/or has already aligned in the database. | a. Yes, the database includes both outages and ignitions caused by vegetation contact. b. The IOUs plan to utilize the third-party contactor’s analysis to understand whether enhanced clearances (clearances greater than twelve-feet) affect the risk and frequency of outages caused by vegetation contact. The IOUs will review the analysis to draw conclusions including, but not limited to, which locations and what types of tree species should receive enhanced clearances. c. Similar to the response to part b, the research will additionally inform the IOUs about the effect of enhanced clearances on ignitions. The IOUs plan to utilize the results of the study to validate or explore enhancements to the current processes for determining which trees receive enhanced clearances. These enhancements could include certain portions of the service territory and certain tree species that should, or should not, receive enhanced clearances. d. There are thousands of variables across the different IOU databases, of which a subset are similar in terms of definition and methods of recording. The research team and IOU SMEs discussed the variables, and which might be the most instructive for understanding the effects of enhanced clearances on wildfire mitigation. Variables under discussion for the joint database include radial clearance, horizontal distance to line of tree causing outage, last vegetation maintenance date, latitude, longitude, high fire threat district, date and time of outage, tree species, ignition related to outage, tree inventory, tree growth rate, diameter at breast height of tree, outage cause codes, tree condition, tree height, forester comments, voltage of associated circuit, associated circuit, health/dead/dying tree, slope, wind direction, and terrain. The joint database is still under development, and the final variables to be used in the database will be determined over the next few months. | Sara Moore | 2023-08-07 | 2023-08-10 | 2023-08-10 | https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-07.pdf | 0 | No | Other | Enhanced Clearances Joint Study | N/A | N/A
196 | OEIS | 2023-08 | OEIS-2023-08 | 1 | OEIS-2023-08.1 | Regarding SDG&E’s Risk Score Calculations It is unclear from statements in its 2023-2025 WMP whether SDG&E uses expected or maximum value in its risk score calculations—likelihood (LoRE) multiplied by consequences (CoRE). SDG&E indicates on page 52 that “averages or expected values are used for LoRE and CoRE estimations,” while it indicates on page 67 (in the WINGS-Ops Calculation Schematic) that maximum values are being used to calculate risk in two places: “Max for each asset due to fire damage” and “Outages due to max fire at asset.” Please indicate whether the consequence component of SDG&E’s risk score calculations (CoRE) uses expected or maximum values. a. If SDG&E uses maximum values in the consequence component of its risk score calculations, please indicate which maximum values it uses and explain why maximum values are used instead of expected values. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 3. Subject to and without waiving the foregoing objections, SDG&E responds as follows: SDG&E quantifies risk consequence scores based on its Enterprise MAVF (page 52) outlined in the “RAMP – C Risk Quantification Framework and Risk Spend Efficiency” chapter.1 This methodology is followed to calculate Risk Spend Efficiencies (RSE) for the proposed mitigations. The WiNGS-Planning (page 66) and WiNGS-Ops (page 67) models are targeted for scenarios of weather conditions where the consequence of a potential ignition could be catastrophic. The models are designed to identify and recommend mitigations (grid hardening or PSPS, respectively between the models) to avoid a potential worst case scenario event. Consequently, the calculations incorporate maximum consequence values derived from the Technosylva modeling software, assuming unsuppressed 8-hour fire simulations during Santa Ana weather conditions. Technosylva estimates are included in: - For WiNGS-Ops, the maximum number of Acres and maximum number of Buildings Destroyed estimates are used in the “Max for each asset due to fire damage” calculation steps, while maximum Rate of Spread (ROS) estimates are included in the “Outages due to max fire at asset” calculation steps. For WiNGS-Planning, the maximum number of Acres and maximum number of Buildings Destroyed estimates are used in the “WRRM Conditional Impact Model.” 1 https://www.sdge.com/sites/default/files/regulatory/SCG_SDGE_RAMP-C_Risk_Quantification_Framework_and_Risk_Spend_Efficiency_5-17-21.pdf | Sara Moore | 2023-08-09 | 2023-08-14 | 2023-08-14 | https://www.sdge.com/sites/default/files/regulatory/OEIS-2023-08.pdf | 0 | No | 6 | 6 RISK METHODOLOGY AND ASSESSMENT PAGE 52 | 6.1.1 | 6.1.1 Overview Page 52
197 | CalPA | 2023-17 | CalPA-2023-17 | 1 | CalPA-2023-17.1 | (a) Please describe your general process or strategy for developing load forecasts. (b) Do you have a written process or procedure for developing load forecasts? (c) If the answer to (b) is "yes", provide a copy. (d) If the answer to (b) is "no", explain why not. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 3 and 5. Subject to and without waiving the foregoing objections, SDG&E responds as follows: (a) SDG&E responds to this question assuming the “load forecast” is asked in the context of its annual Distribution Planning Process (DPP). SDG&E provides a description of its load forecast process in its annually submitted Grid Needs Assessment (GNA) report.1 (b) Yes, this process is described in the GNA report. (c) A link to the GNA report is included in this response. (d) N/A | Aaron Louie | 2023-07-27 | 2023-08-10 | 2023-08-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-17.pdf | 0 | No | Other | Load Forecasts | N/A | N/A
198 | CalPA | 2023-17 | CalPA-2023-17 | 2 | CalPA-2023-17.2 | (a) Do you consider load growth projections when you determine which system hardening measures to deploy for wildfire mitigation purposes? (b) If the answer to (a) is "yes", explain how load growth projects influence your mitigation selection process. (c) If the answer to (a) is "no", explain why not. | Subject to and without waiving the foregoing objections, SDG&E responds as follows: (a) SDG&E’s WiNGS-Planning tool utilizes wildfire risk to prioritize and recommend system hardening mitigations. Load growth projections are not a factor within the WiNGS-Planning tool. (b) N/A (c) The primary objective of SDG&E’s wildfire mitigation system hardening initiatives is to reduce the risk of catastrophic wildfire by reducing the chance of infrastructure-related ignition. Load growth projections are not a factor in reducing this risk. As part of the planning for implementing these system hardening measures, however, load growth is reviewed and considered as described in responses three through six. Generally, within the HFTD areas as projects are designed for increased wind loading the conductor size will increase leading to additional capacity on these circuits. | Aaron Louie | 2023-07-27 | 2023-08-10 | 2023-08-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-17.pdf | 0 | No | Other | Load Forecasts | N/A | N/A
199 | CalPA | 2023-17 | CalPA-2023-17 | 3 | CalPA-2023-17.3 | (a) When you plan system hardening projects for wildfire mitigation purposes, do you design projects to accommodate forecasted load growth? (b) If yes, what degree of load growth do you design for? (c) Describe your process for incorporating forecasted load growth into the design of system hardening projects (for instance, which scenarios of possible load growth are considered). | SDG&E objects to the request on the grounds set forth in General Objections Nos. 3 and 5. Subject to and without waiving the foregoing objections, SDG&E responds as follows: (a) Yes. Distribution Planning is consulted during the planning stage of hardening projects to ensure current load and anticipated load growth are accounted for, in accordance with the response to Question 1. In addition, for undergrounding projects, distribution transformers are sized higher than current load requires in anticipation of future electrification demand. (b) SDG&E does not design its projects to meet a specific load growth amount. Rather, Distribution Planning is consulted to understand the current and future load requirements of the specific circuit being hardened. (c) Please see SDG&E’s GNA report referenced in question 1. | Aaron Louie | 2023-07-27 | 2023-08-10 | 2023-08-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-17.pdf | 0 | No | Other | Load Forecasts | N/A | N/A
200 | CalPA | 2023-17 | CalPA-2023-17 | 4 | CalPA-2023-17.4 | (a) In a typical bare conductor to covered conductor conversion project, is the intention to maintain, increase, or decrease the load capacity at peak operating temperatures? (b) Explain the reasoning for your response to part (a). | SDG&E objects to the request on the grounds set forth in General Objections Nos. 3 and 5. Subject to and without waiving the foregoing objections, SDG&E responds as follows: (a) In a typical bare conductor to covered conductor conversion project the intent is to increase load capacity. The covered conductor wire sizes utilized by SDG&E are typically larger than those being replaced. (b) Generally, when designing system hardening projects like covered conductor for increased wind loading, the conductor size will increase. This will correspondingly increase the load capacity on the circuit. As described in question three, Distribution Planning is consulted to ensure current and future load growth is considered. | Aaron Louie | 2023-07-27 | 2023-08-10 | 2023-08-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-17.pdf | 0 | No | Other | Covered Conductor Conversion Project | N/A | N/A
201 | CalPA | 2023-17 | CalPA-2023-17 | 5 | CalPA-2023-17.5 | (a) Are all new covered conductor installation projects designed to accommodate loads greater than current capacity for the same circuit? (b) If the answer to (a) is "yes", explain how. (c) If the answer to (a) is "no", explain why not. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 3 and 5. Subject to and without waiving the foregoing objections, SDG&E responds as follows: (a) Yes. See response to Question 3. Tie/Feeder lines are typically designed for 500 amps or more of capacity. (b) Distribution Planning is consulted during the planning stage of hardening projects to ensure current load and anticipated load growth are accounted for. The main feeder and ties to other circuits are designed utilizing conductor rated for 500 amps or more of capacity. | Aaron Louie | 2023-07-27 | 2023-08-10 | 2023-08-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-17.pdf | 0 | No | Other | Covered Conductors | N/A | N/A
202 | CalPA | 2023-17 | CalPA-2023-17 | 6 | CalPA-2023-17.6 | (a) Are all overhead to underground conductor conversion projects designed to accommodate loads greater than current capacity for the same circuit? (b) If the answer to (a) is "yes", explain how. (c) If the answer to (a) is "no", explain why not. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 3 and 5. Subject to and without waiving the foregoing objections, SDG&E responds as follows: (a) Yes. See response to Question 3. Tie/Feeder lines are typically designed utilizing conductor capable of 600 amps of capacity. (b) Distribution Planning is consulted during the planning stage of hardening projects to ensure current load and anticipated load growth are accounted for. The main feeder and ties to other circuits are designed utilizing conductor rated for 600 amps of capacity. | Aaron Louie | 2023-07-27 | 2023-08-10 | 2023-08-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-17.pdf | 0 | No | Other | Covered Conductors | N/A | N/A
203 | CalPA | 2023-17 | CalPA-2023-17 | 7 | CalPA-2023-17.7 | Describe the challenges or advantages entailed in increasing load capacity on a circuit that has previously been hardened with covered conductor. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 6. Subject to and without waiving the foregoing objections, SDG&E responds as follows: SDG&E responds to this question in the context of its annual Distribution Planning Process (DPP). SDG&E plans for load growth the same way regardless of if the circuit has been hardened with covered conductor or not. As previously discussed in prior responses, SDG&E’s installation of covered conductor typically involves increased load capacity as a result of the conductor size. | Aaron Louie | 2023-07-27 | 2023-08-10 | 2023-08-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-17.pdf | 0 | No | Other | Covered Conductors | N/A | N/A
204 | CalPA | 2023-17 | CalPA-2023-17 | 8 | CalPA-2023-17.8 | Describe the challenges or advantages entailed in increasing load capacity on a circuit that has previously been hardened with underground conductor. | SDG&E objects to the request on the grounds set forth in General Objections Nos. 3 and 5. Subject to and without waiving the foregoing objections, SDG&E responds as follows: SDG&E responds to this question in the context of its annual Distribution Planning Process (DPP). SDG&E plans for load growth the same way regardless of if the circuit has been hardened with underground conductor or not. | Aaron Louie | 2023-07-27 | 2023-08-10 | 2023-08-10 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-17.pdf | 0 | No | Other | Underground Conductor | N/A | N/A
205 | CalPA | 2023-17 | CalPA-2023-17 | 9 | CalPA-2023-17.9 | Provide a list of all circuits in your system. For each circuit, provide: (a) Circuit ID Number (b) Peak load in Amperes observed since January 1, 2014. (c) Circuit Capacity in Amperes | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, and 9. Specifically, the information requested in subsection (b) is beyond the scope of data that is available for dissemination. Subject to and without waiving the foregoing objections, SDG&E responds as follows: (a)(b) Please see attached confidential excel spreadsheet titled “CONFIDENTIAL_CalAdvocates-SDGE-2023WMP-DR_17_Q9_CircuitMaxAmps.xlsx” and associated confidentiality declaration. (a) (c) SDG&E has previously provided the requested Circuit ID Number and corresponding Circuit Capacity in its response to Data Request Cal Advocates - SDGE - 04 - R2106017 within the confidential spreadsheet (“Data Request Cal Advocates - SDGE - 04 - R2106017.xlsx”) on February 15, 2023. | Aaron Louie | 2023-07-27 | 2023-08-17 | 2023-08-17 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-17.pdf | 1 | Yes | Other | Circuits | N/A | N/A
206 | CalPA | 2023-17 | CalPA-2023-17 | 10 | CalPA-2023-17.10 | Provide updated GIS layers of primary distribution, secondary distribution, and transmission lines, with the following attributes: (a) Circuit ID Number (b) Peak load in Amperes observed since January 1, 2014. (c) Circuit Capacity in Amperes | SDG&E objects to the request on the grounds set forth in General Objections Nos. 2, 5, and 9. Specifically, the information requested in subsection (b) is beyond the scope of data that is available for dissemination. Subject to and without waiving the foregoing objections, SDG&E responds as follows: (b) SDG&E objects to this request on the grounds that it is overly broad and unduly burdensome, particularly when weighed against the questionable relevance of this information in assessing SDG&E’s Wildfire Mitigation Plan. SDG&E’s transmission system collects and stores information every 2 to 4 seconds. To pull, query, and sort this data since 2014 requires an unreasonable amount of resources to not only gather the data but to review the query results and remove anomalies that are inherent in data. Additionally, there are numerous facility ratings for our transmission system that could impact the results that have to be reviewed. SDG&E is unable to perform this work in a reasonable amount of time and believes the information already provided is sufficient to allow Cal Advocates insight into these issues. (a)(c) Please see attached confidential GIS layers titled “SDG&E_CalPA_SDG&E_2023WMP_17.gdb” and associated confidentiality declaration. | Aaron Louie | 2023-07-27 | 2023-08-17 | 2023-08-17 | https://www.sdge.com/sites/default/files/regulatory/CalPA-2023-17.pdf | 1 | Yes | Other | Circuits | N/A | N/A
No new data request responses since 8/24/2023
208 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
209 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
210 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
211 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
212 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
213 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
214 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
215 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
216 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
217 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
218 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
219 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
220 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
221 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
222 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
223 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
224 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
225 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
226 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
227 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
228 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
229 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
230 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
231 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
232 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
233 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
234 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
235 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
236 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
237 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
238 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
239 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
240 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
241 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
242 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
243 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
244 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
245 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
246 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
247 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
248 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
249 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
250 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
251 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
252 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
253 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
254 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
255 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
256 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
257 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
258 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
259 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
260 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
261 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
262 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
263 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
264 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
265 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
266 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
267 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
268 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
269 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
270 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
271 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
272 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
273 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
274 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
275 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
276 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
277 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
278 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
279 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
280 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
281 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
282 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
283 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
284 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
285 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
286 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
287 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
288 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
289 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
290 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
291 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
292 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
293 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
294 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
295 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
296 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
297 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
298 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
299 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A
300 |  |  | - |  | -. | [10 empty] | #N/A |  | #N/A

## WMP Sections (hidden)
1 | 1 EXECUTIVE SUMMARY Page 1 | 1
1.1 | 1.1 Summary of 2020–2022 WMP Cycle Page 1 | 1
1.1.1 | 1.1.1 Major Lessons Learned Page 4 | 4
1.1.1.1 | 1.1.1.1 Risk Methodology and Assessment Page 4 | 4
1.1.1.2 | 1.1.1.2 Wildfire Mitigation StrategyPage 5 | 5
1.1.1.3 | 1.1.1.3 Grid Design, Operations, and Maintenance Page 5 | 5
1.1.1.4 | 1.1.1.4 Vegetation Management and Inspections Page6 | 6
1.1.1.5 | 1.1.1.5 Situational Awareness and Forecasting Page 6 | 6
1.1.1.6 | 1.1.1.6 Emergency Preparedness Page 6 | 6
1.1.1.7 | 1.1.1.7 Community Outreach and Engagement Page 7 | 7
1.1.1.8 | 1.1.1.8 PSPS Page 7 | 7
1.2 | 1.2 Summary of 2023–2025 Base WMP Page7 | 7
1.2.1 | 1.2.1 Framework Page 8 | 8
1.2.2 | 1.2.2 Goal of the WMP Page 9 | 9
1.2.3 | 1.2.3 Plan Objectives Page 9 | 9
2 | 2 RESPONSIBLE PERSONS Page 11 | 11
3 | 3 STATUTORY REQUIREMENTS CHECKLIST Page 13 | 13
4 | 4 OVERVIEW OF WMP Page 16 | 16
4.1 | 4.1 Primary Goal Page 16 | 16
4.2 | 4.2 Plan Objectives Page 16 | 16
4.2.1.1 | 4.2.1.1 Risk Methodology and Assessment Page 16 | 16
4.2.1.2 | 4.2.1.2 Wildfire Mitigation Strategy Page 16 | 16
4.2.1.3 | 4.2.1.3 Grid Design, Operations, and Maintenance Page 16 | 16
4.2.1.4 | 4.2.1.4 Vegetation Management and Inspections Page 17 | 17
4.2.1.5 | 4.2.1.5 Situational Awareness and Forecasting Page 17 | 17
4.2.1.6 | 4.2.1.6 Emergency Preparedness Page 17 | 17
4.2.1.7 | 4.2.1.7 Community Outreach and Engagement Page 18 | 18
4.2.1.8 | 4.2.1.8 Public Safety Power Shutoff Page 18 | 18
4.3 | 4.3 Proposed Expenditures Page 18 | 18
4.4 | 4.4 Risk Informed Framework Page 19 | 19
4.4.1 | 4.4.1 Risk Assessment: Identification, Analysis, Evaluation, and Prioritization Page 21 | 21
4.4.2 | 4.4.2 Risk Strategy: Plan Development, Investment Decisions, Implementation, and Review Page 22 | 22
5 | 5 OVERVIEW OF THE SERVICE TERRITORY Page 25 | 25
5.1 | 5.1 Service Territory Page 25 | 25
5.2 | 5.2 Electrical Infrastructure Page 26 | 26
5.3 | 5.3 Environmental Settings Page 27 | 27
5.3.1 | 5.3.1 Fire Ecology Page 27 | 27
5.3.1.1 | 5.3.1.1 Ecological Regions Page 27 | 27
5.3.1.2 | 5.3.1.2 Climate and Weather Conditions Page 28 | 28
5.3.1.3 | 5.3.1.3 Fire Return Intervals Page 28 | 28
5.3.2 | 5.3.2 Catastrophic Wildfire History Page 29 | 29
5.3.3 | 5.3.3 High Fire Threat Districts Page 31 | 31
5.3.4 | 5.3.4 Climate Change Page 33 | 33
5.3.4.1 | 5.3.4.1 General Climate Conditions Page 33 | 33
5.3.4.2 | 5.3.4.2 Climate Change Phenomena and Trends Page35 | 35
5.3.5 | 5.3.5 Topography Page 39 | 39
5.4 | 5.4 Community Values at Risk Page 40 | 40
5.4.1 | 5.4.1 Urban, Rural, and Highly Rural Customers Page 40 | 40
5.4.2 | 5.4.2 Wildland-Urban Interfaces Page 41 | 41
5.4.3 | 5.4.3 Communities at Risk from Wildfire Page 41 | 41
5.4.3.1 | 5.4.3.1 Individuals at Risk from Wildfire Page 41 | 41
5.4.3.2 | 5.4.3.2 Social Vulnerability and Exposure to Electrical Corporation Wildfire Risk Page 42 | 42
5.4.3.3 | 5.4.3.3 Sub-Divisions with Limited Egress or No Secondary Egress Page 43 | 43
5.4.4 | 5.4.4 Critical Facilities and Infrastructure at Risk from Wildfire Page 44 | 44
5.4.5 | 5.4.5 Environmental Compliance and Permitting Page 46 | 46
5.4.5.1 | 5.4.5.1 Processes to Ensure Compliance Page 46 | 46
5.4.5.1.1 | 5.4.5.1.1 Environmental Services Page 46 | 46
5.4.5.1.2 | 5.4.5.1.2 Programmatic Endangered Species Act Permitting/Authorization Page 46 | 46
5.4.5.1.3 | 5.4.5.1.3 Cultural Resources Program Page 48 | 48
5.4.5.1.4 | 5.4.5.1.4 Municipal and State Agency Permits Page 49 | 49
5.4.5.2 | 5.4.5.2 Overcoming Roadblocks Page 50 | 50
5.4.5.3 | 5.4.5.3 Notable Changes to Environmental Compliance and/or Permitting Procedures Page 51 | 51
6 | 6 RISK METHODOLOGY AND ASSESSMENT PAGE 52 | 52
6.1 | 6.1 Methodology Page 52 | 52
6.1.1 | 6.1.1 Overview Page 52 | 52
6.1.2 | 6.1.2 Summary of Risk Models Page 54 | 54
6.2 | 6.2 Risk Analysis Framework Page 59 | 59
6.2.1 | 6.2.1 Risk and Risk Component Identification Page 59 | 59
6.2.2 | 6.2.2 Risk and Risk Components Calculation Page 64 | 64
6.2.2.1 | 6.2.2.1 Likelihood Page 68 | 68
6.2.2.2 | 6.2.2.2 Consequence Page 70 | 70
6.2.2.3 | 6.2.2.3 Risk Page 72 | 72
6.2.3 | 6.2.3 Key Assumptions and Limitations Page 73 | 73
6.3 | 6.3 Risk Scenarios Page 75 | 75
6.3.1 | 6.3.1 Design Basis Scenarios Page 76 | 76
6.3.2 | 6.3.2 Extreme-Event/High Uncertainty Scenarios Page 79 | 79
6.4 | 6.4 Risk Analysis Results and Presentation Page 80 | 80
6.4.1 | 6.4.1 Top Risk Areas within the HFRA Page 81 | 81
6.4.1.1 | 6.4.1.1 Geospatial Maps of Top-Risk Areas within the HFRA Page 83 | 83
6.4.1.2 | 6.4.1.2 Proposed Updates to HFTD Page 83 | 83
6.4.2 | 6.4.2 Top Risk-Contributing Circuits/Segments/Spans Page 84 | 84
6.4.3 | 6.4.3 Other Key Metrics Page 85 | 85
6.4.3.1 | 6.4.3.1 FPI Page 85 | 85
6.4.3.2 | 6.4.3.2 Red Flag Warning Page 85 | 85
6.4.3.3 | 6.4.3.3 High Wind Warnings Page 85 | 85
6.5 | 6.5 Enterprise System for Risk Assessment Page 86 | 86
6.6 | 6.6 Quality Assessment and Control Page 87 | 87
6.6.1 | 6.6.1 Independent Review Page 87 | 87
6.6.2 | 6.6.2 Model Controls, Design, and Review Page 89 | 89
6.6.2.1 | 6.6.2.1 Modularization Page 89 | 89
6.6.2.2 | 6.6.2.2 Reanalysis Page 89 | 89
6.6.2.3 | 6.6.2.3 Version Control Page 90 | 90
6.7 | 6.7 Risk Assessment Improvement Plan Page 90 | 90
6.7.1 | 6.7.1 RA-1-A Evaluate Additional Wildfire and PSPS Risk Assessment Factors Page 94 | 94
6.7.1.1 | 6.7.1.1 Problem Statement Page 94 | 94
6.7.1.2 | 6.7.1.2 Planned Improvement Page 94 | 94
6.7.1.3 | 6.7.1.3 Anticipated Benefit Page 95 | 95
6.7.1.4 | 6.7.1.4 Region Prioritization Page 95 | 95
6.7.2 | 6.7.2 RA-1-B Enhance Model Design and Architecture Page 95 | 95
6.7.2.1 | 6.7.2.1 Problem Statement Page 95 | 95
6.7.2.2 | 6.7.2.2 Planned Improvement Page 95 | 95
6.7.2.3 | 6.7.2.3 Anticipated Benefit Page 95 | 95
6.7.3 | 6.7.3 RA-2-A Evaluate Design and Extreme-Event Scenarios Page 96 | 96
6.7.3.1 | 6.7.3.1 Problem Statement Page 96 | 96
6.7.3.2 | 6.7.3.2 Planned Improvement Page 96 | 96
6.7.3.3 | 6.7.3.3 Anticipated Benefit Page 96 | 96
6.7.4 | 6.7.4 RA-3-A Establish Process to Continuously Evaluate HFTD Boundaries Page 96 | 96
6.7.4.1 | 6.7.4.1 Problem Statement Page 96 | 96
6.7.4.2 | 6.7.4.2 Planned Improvement Page 97 | 97
6.7.4.3 | 6.7.4.3 Anticipated Benefit Page 97 | 97
6.7.5 | 6.7.5 RA-3-B Enhance Model Documentation Page 97 | 97
6.7.5.1 | 6.7.5.1 Problem Statement Page 97 | 97
6.7.5.2 | 6.7.5.2 Planned Improvement Page 97 | 97
6.7.5.3 | 6.7.5.3 Anticipated Benefit Page 97 | 97
6.7.6 | 6.7.6 RA-4-A Improve Procedure for Independent Reviews of Data and Models Page 97 | 97
6.7.6.1 | 6.7.6.1 Problem Statement Page 97 | 97
6.7.6.2 | 6.7.6.2 Planned Improvement Page 98 | 98
6.7.6.3 | 6.7.6.3 Anticipated Benefit Page 98 | 98
6.7.7 | 6.7.7 RA-4-B Enhance Model Validation Process Page 98 | 98
6.7.7.1 | 6.7.7.1 Problem Statement Page 98 | 98
6.7.7.2 | 6.7.7.2 Planned Improvement Page 98 | 98
6.7.7.3 | 6.7.7.3 Anticipated Benefit Page 98 | 98
6.1.1 | 6.1.1 RA-5-A Deploy and Enhance WiNGS-Ops and WiNGS-Planning Visualization Platforms Page 99 | 99
6.7.7.4 | 6.7.7.4 Problem Statement Page 99 | 99
6.7.7.5 | 6.7.7.5 Planned Improvement Page 99 | 99
6.7.7.6 | 6.7.7.6 Anticipated Benefit Page 99 | 99
6.7.7.7 | 6.7.7.7 Region Prioritization Page 99 | 99
7 | 7 WILDFIRE MITIGATION STRATEGY DEVELOPMENT PAGE 100 | 100
7.1 | 7.1 Risk Evaluation Page 100 | 100
7.1.1 | 7.1.1 Approach Page 100 | 100
7.1.2 | 7.1.2 Key Stakeholders for Decision Making Page 100 | 100
7.1.3 | 7.1.3 Risk-Informed Prioritization Page 102 | 102
7.1.3.1 | 7.1.3.1 Selection of Areas for Mitigation Page 102 | 102
7.1.3.1.1 | 7.1.3.1.1 Geographic Scale used in Prioritization Page 102 | 102
7.1.3.1.2 | 7.1.3.1.2 Statistical Approach used to Select Candidates Page 102 | 102
7.1.3.1.3 | 7.1.3.1.3 Feasibility Constraints Page 103 | 103
7.1.3.2 | 7.1.3.2 Prioritized List of Risks Page 104 | 104
7.1.4 | 7.1.4 Mitigation Selection Process Page 104 | 104
7.1.4.1 | 7.1.4.1 Identifying and Evaluating Mitigation Initiatives Page 105 | 105
7.1.4.1.1 | 7.1.4.1.1 Procedures to Develop Mitigation Initiatives Page 105 | 105
7.1.4.1.2 | 7.1.4.1.2 Mitigation Initiatives that Address Local Wildfire Risk Drivers Page 105 | 105
7.1.4.1.3 | 7.1.4.1.3 Characterization of Uncertainties and Incorporation into the Decision-Making Process Page 106 | 106
7.1.4.1.4 | 7.1.4.1.4 Potential Mitigation Initiatives Page 106 | 106
7.1.4.1.5 | 7.1.4.1.5 MAVF and other Specific Risk Factors Page 108 | 108
7.1.4.2 | 7.1.4.2 Mitigation Initiative Prioritization Page 108 | 108
7.1.4.2.1 | 7.1.4.2.1 Evaluation of Potential Mitigation Initiatives Page 108 | 108
7.1.4.2.2 | 7.1.4.2.2 Identification of Mitigation Initiatives Page 109 | 109
7.1.4.2.3 | 7.1.4.2.3 Resource Optimization Page 111 | 111
7.1.4.2.4 | 7.1.4.2.4 Mitigation Initiative Prioritization to Reduce both Wildfire and PSPS Risk Page 113 | 113
7.1.4.3 | 7.1.4.3 Mitigation Initiative Scheduling Page 116 | 116
7.1.4.3.1 | 7.1.4.3.1 Mitigation Initiative Scheduling Page 116 | 116
7.1.4.3.2 | 7.1.4.3.2 Interim Mitigation Process Page 116 | 116
7.1.4.3.3 | 7.1.4.3.3 Monitoring Progress toward Targets with Known Limitations and Constraints Page 116 | 116
7.1.4.3.4 | 7.1.4.3.4 Measuring Effectiveness of Mitigation Initiatives Page 116 | 116
7.2 | 7.2 Wildfire Mitigation Strategy Page 117 | 117
7.2.1 | 7.2.1 Overview of Mitigation Initiatives and Activities Page 118 | 118
7.2.2 | 7.2.2 Anticipated Risk Reduction Page 120 | 120
7.2.2.1 | 7.2.2.1 Projected Overall Risk Reduction Page 120 | 120
7.2.2.2 | 7.2.2.2 Risk Impact of Mitigation Initiatives Page 123 | 123
7.2.2.3 | 7.2.2.3 Projected Risk Reduction on Highest-Risk Circuits Over the Three-Year WMP Cycle Page 125 | 125
7.2.3 | 7.2.3 Interim Mitigation Activities Page 127 | 127
8 | 8 WILDFIRE MITIGATIONS Page 129 | 129
8.1 | 8.1 Grid Design, Operations, and Maintenance Page 129 | 129
8.1.1 | 8.1.1 Overview Page 129 | 129
8.1.1.1 | 8.1.1.1 Objectives Page 131 | 131
8.1.1.2 | 8.1.1.2 Targets Page 140 | 140
8.1.1.3 | 8.1.1.3 Performance Metrics Page 145 | 145
8.1.1.3.1 | 8.1.1.3.1 Distribution Inspection Findings and Open Work Orders Page 147 | 147
8.1.1.3.2 | 8.1.1.3.2 Distribution Equipment related HFTD Ignitions and Outages Rate Page 148 | 148
8.1.1.3.3 | 8.1.1.3.3 Transmission Inspection Findings and Open Work Orders in HFTD Page 148 | 148
8.1.1.3.4 | 8.1.1.3.4 Transmission Equipment related HFTD Outages and Ignitions Page 149 | 149
8.1.2 | 8.1.2 Grid Design and System Hardening Page 150 | 150
8.1.2.1 | 8.1.2.1 Covered Conductor Installation Page 150 | 150
8.1.2.1.1 | 8.1.2.1.1 Utility Initiative Tracking ID Page 150 | 150
8.1.2.1.2 | 8.1.2.1.2 Overview of the Activity Page 150 | 150
8.1.2.1.3 | 8.1.2.1.3 Impact of the Activity on Wildfire Risk Page 151 | 151
8.1.2.1.4 | 8.1.2.1.4 Impact of the Activity on PSPS Risk Page 151 | 151
8.1.2.1.5 | 8.1.2.1.5 Updates to Initiative Page 152 | 152
8.1.2.2 | 8.1.2.2 Undergrounding of Electric Lines and/or Equipment Page 152 | 152
8.1.2.2.1 | 8.1.2.2.1 Utility Initiative Tracking ID Page 152 | 152
8.1.2.2.2 | 8.1.2.2.2 Overview of the Activity Page 152 | 152
8.1.2.2.3 | 8.1.2.2.3 Impact of the Activity on Wildfire Risk Page 153 | 153
8.1.2.2.4 | 8.1.2.2.4 Impact of the Activity on PSPS Risk Page 153 | 153
8.1.2.2.5 | 8.1.2.2.5 Updates to the Activity Page 153 | 153
8.1.2.3 | 8.1.2.3 Distribution Pole Replacements and Reinforcements Page 154 | 154
8.1.2.3.1 | 8.1.2.3.1 Utility Initiative Tracking ID Page 154 | 154
8.1.2.3.2 | 8.1.2.3.2 Overview of the Activity Page 154 | 154
8.1.2.3.3 | 8.1.2.3.3 Impact of the Activity on Wildfire Risk Page 155 | 155
8.1.2.3.4 | 8.1.2.3.4 Impact of the Activity on PSPS Risk Page 155 | 155
8.1.2.3.5 | 8.1.2.3.5 Updates to the Activity Page 155 | 155
8.1.2.4 | 8.1.2.4 Transmission Pole/Tower Replacements and Reinforcements Page 155 | 155
8.1.2.4.1 | 8.1.2.4.1 Utility Initiative Tracking ID Page 155 | 155
8.1.2.4.2 | 8.1.2.4.2 Overview of the Activity Page 155 | 155
8.1.2.4.3 | 8.1.2.4.3 Impact of the Activity on Wildfire Risk Page 155 | 155
8.1.2.4.4 | 8.1.2.4.4 Impact of the Activity on PSPS Risk Page 155 | 155
8.1.2.4.5 | 8.1.2.4.5 Updates to the Activity Page 156 | 156
8.1.2.5 | 8.1.2.5 Traditional Overhead Hardening Page 156 | 156
8.1.2.5.1 | 8.1.2.5.1 Distribution Overhead System Hardening (Traditional) Page 156 | 156
8.1.2.5.2 | 8.1.2.5.2 Transmission System Hardening Program Page 157 | 157
8.1.2.6 | 8.1.2.6 Emerging Grid Hardening Technology Installations and Pilots Page 160 | 160
8.1.2.7 | 8.1.2.7 Microgrids Page 160 | 160
8.1.2.7.1 | 8.1.2.7.1 Utility Initiative Tracking ID Page 160 | 160
8.1.2.7.2 | 8.1.2.7.2 Overview of the Activity Page 160 | 160
8.1.2.7.3 | 8.1.2.7.3 Impact of the Activity on Wildfire Risk Page 160 | 160
8.1.2.7.4 | 8.1.2.7.4 Impact of the Activity on PSPS Risk Page 161 | 161
8.1.2.7.5 | 8.1.2.7.5 Updates to the Activity Page 161 | 161
8.1.2.8 | 8.1.2.8 Installation of System Automation Equipment Page 162 | 162
8.1.2.8.1 | 8.1.2.8.1 Advanced Protection Page 162 | 162
8.1.2.8.2 | 8.1.2.8.2 Early Fault Detection Page 165 | 165
8.1.2.8.3 | 8.1.2.8.3 Distribution Communications Reliability Improvements Page 168 | 168
8.1.2.9 | 8.1.2.9 Line Removal (in HFTD) Page 169 | 169
8.1.2.9.1 | 8.1.2.9.1 Utility Initiative Tracking ID Page 169 | 169
8.1.2.9.2 | 8.1.2.9.2 Overview of the Activity Page 169 | 169
8.1.2.9.3 | 8.1.2.9.3 Impact of the Activity on Wildfire Risk Page 170 | 170
8.1.2.9.4 | 8.1.2.9.4 Impact of the Activity on PSPS Risk Page 170 | 170
8.1.2.9.5 | 8.1.2.9.5 Updates to the Activity Page 170 | 170
8.1.2.10 | 8.1.2.10 Other Grid Topology Improvements to Minimize Risk of Ignitions Page 170 | 170
8.1.2.10.1 | 8.1.2.10.1 SCADA Capacitors Maintenance and Replacement Program Page 170 | 170
8.1.2.10.2 | 8.1.2.10.2 Expulsion Fuse Replacement Program Page 172 | 172
8.1.2.10.2 | 8.1.2.10.3 Hotline Clamp Replacement Program Page 174 | 174
8.1.2.10.4 | 8.1.2.10.4 Lightning Arrestor Removal and Replacement Page 175 | 175
8.1.2.10.5 | 8.1.2.10.5 Avian Protection Program Page 177 | 177
8.1.2.10.6 | 8.1.2.10.6 Strategic Pole Replacement Program Page 178 | 178
8.1.2.10.7 | 8.1.2.10.7 Wireless Fault Indicators (WFIs) Page 180 | 180
8.1.2.11.11 | 8.1.2.11 Other Grid Topology Improvements to Mitigate or Reduce PSPS Events Page 181 | 181
8.1.2.11.1 | 8.1.2.11.1 PSPS Sectionalizing Enhancement Program Page 181
8.1.2.11.2 | 8.1.2.11.2 Standby Power Programs (Fixed Backup Power: Residential/Commercial) Page 182 | 182
8.1.2.11.3 | 8.1.2.11.3 Generator Grant Program Page 184 | 184
8.1.2.11.4 | 8.1.2.11.4 Generator Assistance Program Page 186 | 186
8.1.2.12 | 8.1.2.12 Other Technologies and Systems not Listed Above Page 187 | 187
8.1.2.12.1 | 8.1.2.12.1 Utility Initiative Tracking ID Page 187 | 187
8.1.2.12.2 | 8.1.2.12.2 Overview of the Activity Page 187 | 187
8.1.2.12.3 | 8.1.2.12.3 Impact of the Activity on Wildfire Risk Page 187 | 187
8.1.2.12.4 | 8.1.2.12.4 Impact of the Activity on PSPS Risk Page 187 | 187
8.1.2.12.5 | 8.1.2.12.5 Updates to the Activity Page 188 | 188
8.1.3 | 8.1.3 Asset Inspections Page 188 | 188
8.1.3.1 | 8.1.3.1 Distribution Overhead Detailed Inspections (WMP.478) Page 189 | 189
8.1.3.2 | 8.1.3.2 Transmission Overhead Detailed Inspections (WMP.479) Page 191 | 191
8.1.3.3 | 8.1.3.3 Distribution Infrared Inspections (WMP.481) Page 195 | 195
8.1.3.4 | 8.1.3.4 Transmission Infrared Inspections (WMP.482) Page 197 | 197
8.1.3.5 | 8.1.3.5 Distribution Wood Pole Intrusive Inspections (WMP.483) Page 199 | 199
8.1.3.6 | 8.1.3.6 Transmission Wood Pole Intrusive Inspections (WMP.1190) Page 202 | 202
8.1.3.7 | 8.1.3.7 Drone Assessments (WMP.552) Page 202 | 202
8.1.3.8 | 8.1.3.8 Distribution Overhead Patrol Inspections (WMP.488) Page 208 | 208
8.1.3.9 | 8.1.3.9 Transmission Overhead Patrol Inspections (WMP.489) Page 210 | 210
8.1.3.10 | 8.1.3.10 Transmission 69kV Tier 3 Visual Inspections (WMP.555) Page 213 | 213
8.1.3.11 | 8.1.3.11 Substation Patrol Inspections (WMP.492) Page 214 | 214
8.1.3.12 | 8.1.3.12 Discontinued Asset Inspection Programs Page 216 | 216
8.1.3.12 | 8.1.3.12.1 LiDAR Inspections of Transmission and Distribution Electric Lines and Equipment Page 216 | 216
8.1.3.12 | 8.1.3.12.2 HFTD Tier 3 Distribution Pole Inspections Page 217 | 217
8.1.4 | 8.1.4 Equipment Maintenance and Repair Page 217 | 217
8.1.4.1 | 8.1.4.1 Maintenance, Repair, and Replacement Strategies Page 217 | 217
8.1.4.2 | 8.1.4.2 Impact of Inspection Programs Page 219 | 219
8.1.5 | 8.1.5 Asset Management and Inspection Enterprise System(s) Page 220 | 220
8.1.5.1 | 8.1.5.1 Distribution Systems Page 220 | 220
8.1.5.2 | 8.1.5.2 Transmission Systems Page 220 | 220
8.1.5.3 | 8.1.5.3 Substation Systems Page 221 | 221
8.1.5.4 | 8.1.5.4 Integrated Asset Management Systems Page 222 | 222
8.1.5.4 | 8.1.5.4.1 WMP Data Platform Page 222 | 222
8.1.5.4 | 8.1.5.4.2 Asset 360 Page 223 | 223
8.1.5.4.3 | 8.1.5.4.3 Intelligent Image Processing Page 25 | 225
8.1.6 | 8.1.6 Quality Assurance and Quality Control Page 226 | 226
8.1.6.1 | 8.1.6.1 QA/QC of Transmission Inspections (WMP.1191) Page 227 | 227
8.1.6.2 | 8.1.6.2 QA/QC of Distribution Detailed Inspections (WMP.491) Page 227 | 227
8.1.6.3 | 8.1.6.3 QA/QC of Distribution Drone Assessments (WMP.1192) Page 228 | 228
8.1.6.4 | 8.1.6.4 QA/QC of Transmission & Distribution Wood Pole Intrusive Inspections (WMP.1193) Page 228 | 228
8.1.6.5 | 8.1.6.5 QA/QC of Substation Inspections (WMP.1194) Page 228 | 228
8.1.7 | 8.1.7 Open Work Orders Page 229 | 229
8.1.7.1 | 8.1.7.1 Procedures/Programs Documenting the Work Order Process Page 229 | 229
8.1.7.2 | 8.1.7.2 Prioritization of Work Orders Page 231 | 231
8.1.7.3 | 8.1.7.3 Plan for Eliminating a Backlog of Work Orders, if Applicable Page 231 | 231
8.1.7.4 | 8.1.7.4 Trends with Respect to Open Work Orders Page 231 | 231
8.1.7.5 | 8.1.7.5 Open work orders over time Page 231 | 231
8.1.7.6 | 8.1.7.6 Aging report for work orders past due Page 233 | 233
8.1.8 | 8.1.8 Grid Operations and Procedures Page 234 | 234
8.1.8.1 | 8.1.8.1 Equipment Settings to Reduce Wildfire Risk Page 234 | 234
8.1.8.1.1 | 8.1.8.1.1 Protective Equipment and Device Settings Page 234 | 234
8.1.8.1.2 | 8.1.8.1.2 Automatic recloser settings Page 234 | 234
8.1.8.1.3 | 8.1.8.1.3 Settings of other Emerging Technologies Page 236 | 236
8.1.8.2 | 8.1.8.2 Grid Response Procedures and Notifications Page 236 | 236
8.1.8.3 | 8.1.8.3 Personnel Work Procedures and Training in Conditions of Elevated Fire Risk Page 236 | 236
8.1.8.3.1 | 8.1.8.3.1 Procedures for Determining Operating Conditions Page 237 | 237
8.1.8.3.2 | 8.1.8.3.2 Procedures Regarding Deployment of Fire Mitigation Resources and Equipment Page 237 | 237
8.1.8.3.3 | 8.1.8.3.3 Aviation Firefighting Program Page 238 | 238
8.1.9 | 8.1.9 Workforce Planning Page 240 | 240
8.1.9.1 | 8.1.9.1 Asset Inspection Qualification Improvement Plans Page 252 | 252
8.1.9.1.1 | 8.1.9.1.1 Extended Reality Page 252 | 252
8.1.9.1.2 | 8.1.9.1.2 Line Checker Program Page 252 | 252
8.1.9.1.3 | 8.1.9.1.3 Safety Observations Page 252 | 252
8.1.9.1.4 | 8.1.9.1.4 Near Misses Reported 253 | 253
8.1.9.2 | 8.1.9.2 Grid Hardening Qualification Improvement Plans Page 254 | 254
8.1.9.3 | 8.1.9.3 Risk Event Inspection Improvement Plans 254 | 254
8.2 | 8.2 Vegetation Management and Inspection Page 254 | 254
8.2.1 | 8.2.1 Overview Page 254 | 254
8.2.1.1 | 8.2.1.1 Objectives Page 256 | 256
8.2.1.2 | 8.2.1.2 Targets Page 259 | 259
8.2.1.3 | 8.2.1.3 Performance Metrics Identified by the Electrical Corporation Page 261 | 261
8.2.1.3.1 | 8.2.1.3.1 Vegetation Inspections and Clearance in the HFTD Page 261 | 261
8.2.1.3.2 | 8.2.1.3.2 Vegetation Outages and Ignitions in the HFTD Page 262 | 262
8.2.2 | 8.2.2 Vegetation Inspections Page 263 | 263
8.2.2.1 | 8.2.2.1 Detailed Vegetation Inspections Page 264 | 264
8.2.2.1.1 | 8.2.2.1.1 Process Page 264 | 264
8.2.2.1.2 | 8.2.2.1.2 Frequency or Triggers Page 267 | 267
8.2.2.1.3 | 8.2.2.1.3 Accomplishments, Roadblocks, and Updates Page 267 | 267
8.2.2.2 | 8.2.2.2 Off-Cycle Patrol Inspections Page 268 | 268
8.2.2.2.1 | 8.2.2.2.1 Process Page 268 | 268
8.2.2.2.2 | 8.2.2.2.2 Frequency or Triggers Page 269 | 269
8.2.2.2.3 | 8.2.2.2.3 Accomplishments, Roadblocks, and Updates Page 270 | 270
8.2.3 | 8.2.3 Vegetation and Fuels Management Page 271 | 271
8.2.3.1 | 8.2.3.1 Pole Clearing Page 273 | 273
8.2.3.1.1 | 8.2.3.1.1 Utility Initiative Tracking ID Page 273 | 273
8.2.3.1.2 | 8.2.3.1.2 Overview of the Initiative Page 273 | 273
8.2.3.1.3 | 8.2.3.1.3 Governing Standards and Electrical Corporation Standard Operating Procedures Page 275 | 275
8.2.3.1.4 | 8.2.3.1.4 Updates to the Initiative Page 275 | 275
8.2.3.2 | 8.2.3.2 Wood and Slash Management Page 276 | 276
8.2.3.2.1 | 8.2.3.2.1 Utility Initiative Tracking ID Page 276 | 276
8.2.3.2.2 | 8.2.3.2.2 Overview of the Initiative Page 276 | 276
8.2.3.2.3 | 8.2.3.2.3 Governing Standards and Electrical Corporation Standard Operating Procedures 276 | 276
8.2.3.2.4 | 8.2.3.2.4 Updates to the Initiative Page 276 | 276
8.2.3.3 | 8.2.3.3 Clearance Page 276 | 276
8.2.3.3.1 | 8.2.3.3.1 Utility Initiative Tracking ID Page 277 | 277
8.2.3.3.2 | 8.2.3.3.2 Overview of the Initiative Page 277 | 277
8.2.3.3.3 | 8.2.3.3.3 Governing Standards and Electrical Corporation Standard Operating Procedures Page 278 | 278
8.2.3.3.4 | 8.2.3.3.4 Updates to the Initiative Page 279 | 279
8.2.3.4 | 8.2.3.4 Fall-in Mitigation Page 279 | 279
8.2.3.4.1 | 8.2.3.4.1 Utility Initiative Tracking ID Page 279 | 279
8.2.3.4.2 | 8.2.3.4.2 Overview of the Initiative Page 279 | 279
8.2.3.4.3 | 8.2.3.4.3 Governing Standards and Electrical Corporation Standard Operating Procedures Page 279 | 279
8.2.3.4.4 | 8.2.3.4.4 Updates to the Initiative Page 279 | 279
8.2.3.5 | 8.2.3.5 Substation Defensible Space Page 279 | 279
8.2.3.6 | 8.2.3.6 High-Risk Species Page 279 | 279
8.2.3.7 | 8.2.3.7 Fire-Resilient Right-of-Ways Page 280 | 280
8.2.3.8 | 8.2.3.8 Emergency Response Vegetation Management Page 280 | 280
8.2.3.8.1 | 8.2.3.8.1 Utility Initiative Tracking ID Page 280 | 280
8.2.3.8.2 | 8.2.3.8.2 Overview of the Initiative Page 280 | 280
8.2.3.8.3 | 8.2.3.8.3 Governing Standards and Electrical Corporation Standard Operating Procedures Page 281 | 281
8.2.3.8.4 | 8.2.3.8.4 Updates to the Initiative Page 281 | 281
8.2.4 | 8.2.4 Vegetation Management Enterprise System Page 281 | 281
8.2.4.1 | 8.2.4.1 Vegetation Inventory and Condition Database(s) Page 281 | 281
8.2.4.2 | 8.2.4.2 Internal Documentation of the Database(s) Page 281 | 281
8.2.4.3 | 8.2.4.3 Integration with Systems in Other Lines of Business Page 282 | 282
8.2.4.4 | 8.2.4.4 Integration with the Auditing System(s) Page 282 | 282
8.2.4.5 | 8.2.4.5 Internal Processes for Updating the System and Planned Updates Page 282 | 282
8.2.4.6 | 8.2.4.6 Changes Since the Last WMP Submission Page 282 | 282
8.2.5 | 8.2.5 Quality Assurance / Quality Control (QA/QC) Page 282 | 282
8.2.5.1 | 8.2.5.1 QA/QC Procedure/Program (WMP.505) Page 282 | 282
8.2.5.2 | 8.2.5.2 Sample Size Page 283 | 283
8.2.5.3 | 8.2.5.3 Who Performs QA/QC Page 284 | 284
8.2.5.4 | 8.2.5.4 Auditor Qualifications Page 284 | 284
8.2.5.5 | 8.2.5.5 QA/QC Findings and Incorporation of Lessons Learned Page 284 | 284
8.2.5.6 | 8.2.5.6 Process Changes Since the Last WMP Submission Page 284 | 284
8.2.6 | 8.2.6 Open Work Orders Page 284 | 284
8.2.6.1 | 8.2.6.1 Work Order Procedures Page 284 | 284
8.2.6.2 | 8.2.6.2 Work Order Prioritization Page 285 | 285
8.2.6.3 | 8.2.6.3 Work Order Backlogs Page Page 285 | 285
8.2.6.4 | 8.2.6.4 Work Order Trends Page 285 | 285
8.2.7 | 8.2.7 Workforce Planning Page 286 | 286
8.3 | 8.3 Situational Awareness and Forecasting Page 291 | 291
8.3.1 | 8.3.1 Overview Page 291 | 291
8.3.1.1 | 8.3.1.1 Objectives Page 292 | 292
8.3.1.2 | 8.3.1.2 Targets Page 298 | 298
8.3.1.3 | 8.3.1.3 Performance Metrics Page 298 | 298
8.3.2 | 8.3.2 Environmental Monitoring Systems Page 301 | 301
8.3.2.1 | 8.3.2.1 Existing Systems, Technologies, and Processes Page 301 | 301
8.3.2.1.1 | 8.3.2.1.1 Weather Stations and Normalized Difference Vegetation Index (NDVI) Cameras Page 301 | 301
8.3.2.1.2 | 8.3.2.1.2 Fuel Moisture Page 302 | 302
8.3.2.1.3 | 8.3.2.1.3 Air Quality Management Program (WMP.970) Page 302 | 302
8.3.2.2 | 8.3.2.2 Evaluation and Selection of New Systems Page 302 | 302
8.3.2.3 | 8.3.2.3 Planned Improvements Page Page 303 | 303
8.3.2.3.1 | 8.3.2.3.1 Weather Station Network and NDVI Cameras Page 303 | 303
8.3.2.3.2 | 8.3.2.3.2 Fuel Moisture Page Page 303 | 303
8.3.2.3.3 | 8.3.2.3.3 Air Quality Management Program Page 304 | 304
8.3.2.4 | 8.3.2.4 Evaluating Mitigation Initiatives Page 306 | 306
8.3.2.4.1 | 8.3.2.4.1 Weather Stations and NDVI Cameras Page 306 | 306
8.3.2.4.2 | 8.3.2.4.2 Fuel Moisture Page 306 | 306
8.3.2.4.3 | 8.3.2.4.3 Air Quality Management Program Page 306 | 306
8.3.3 | 8.3.3 Grid Monitoring Systems Page 307 | 307
8.3.3.1 | 8.3.3.1 Existing Systems, Technologies, and Procedures Page 307 | 307
8.3.3.2 | 8.3.3.2 Evaluation and Selection of New Systems Page 310 | 310
8.3.3.3 | 8.3.3.3 Planned Improvements Page 310 | 310
8.3.3.4 | 8.3.3.4 Evaluating Mitigation Initiatives Page 310 | 310
8.3.3.5 | 8.3.3.5 Enterprise System for Grid Monitoring Page 311 | 311
8.3.3.5.1 | 8.3.3.5.1 Database(s) Utilized for Storage Page 311 | 311
8.3.3.5.2 | 8.3.3.5.2 Internal Documentation of Database(s) Page 311 | 311
8.3.3.5.3 | 8.3.3.5.3 Integration with Systems in other Lines of Business Page 311 | 311
8.3.3.5.4 | 8.3.3.5.4 QA/QC or Auditing of the System Page 312 | 312
8.3.3.5.5 | 8.3.3.5.5 Updating the Enterprise System Including Database(s) Page 312 | 312
8.3.3.5.6 | 8.3.3.5.6 Changes to the Initiative since the Last WMP Submission Page 313 | 313
8.3.4 | 8.3.4 Ignition Detection Systems Page 313 | 313
8.3.4.1 | 8.3.4.1 Existing Ignition Detection Sensors and Systems Page 313 | 313
8.3.4.1.1 | 8.3.4.1.1 Satellite Based Remote Sensing Page 314 | 314
8.3.4.1.2 | 8.3.4.1.2 Cameras Page Page 315 | 315
8.3.4.1.3 | 8.3.4.1.3 WFA - Fire Growth Potential Software Page 316 | 316
8.3.4.1.4 | 8.3.4.1.4 AI Smoke Detection Algorithm . 316 | 316
8.3.4.2 | 8.3.4.2 Evaluation and Selection of New Detection Systems Page 317 | 317
8.3.4.2.1 | 8.3.4.2.1 Impact of new Detection Technologies Page 318 | 318
8.3.4.2.2 | 8.3.4.2.2 Efficacy of New Technologies Page 318 | 318
8.3.4.2.3 | 8.3.4.2.3 Budgeting Process Page 318 | 318
8.3.4.3 | 8.3.4.3 Planned Integration of New Detection Technologies Page 318 | 318
8.3.4.4 | 8.3.4.4 Evaluating Mitigation Initiatives Page 319 | 319
8.3.4.4.1 | 8.3.4.4.1 Satellite Based Remote Sensing Page 319 | 319
8.3.4.4.2 | 8.3.4.4.2 Cameras Page 319 | 319
8.3.4.4.3 | 8.3.4.4.3 Fire Grown Potential Software Page 319 | 319
8.3.4.4.4 | 8.3.4.4.4 AI Smoke Detection Page .. 319 | 319
8.3.4.5 | 8.3.4.5 Enterprise System for Ignition Detection Page 320 | 320
8.3.4.5.1 | 8.3.4.5.1 Database(s) Utilized for Storage Page 320 | 320
8.3.4.5.2 | 8.3.4.5.2 Internal Documentation of Database(s) Page 320 | 320
8.3.4.5.3 | 8.3.4.5.3 Integration with Systems in other Lines of Business Page 320 | 320
8.3.4.5.4 | 8.3.4.5.4 QA/QC or Auditing of the System Page 320 | 320
8.3.4.5.5 | 8.3.4.5.5 Internal Processes for Updating Enterprise System Including Database(s) Page 320 | 320
8.3.4.5.6 | 8.3.4.5.6 Changes to the Initiative since the Last WMP Submission Page 320 | 320
8.3.5 | 8.3.5 Weather Forecasting Page 320 | 320
8.3.5.1 | 8.3.5.1 Existing Modeling Approach Page 320 | 320
8.3.5.1.1 | 8.3.5.1.1 Weather Research and Forecasting (WRF) Page 321 | 321
8.3.5.1.2 | 8.3.5.1.2 SAWTI Page 322 | 322
8.3.5.2 | 8.3.5.2 Known Limitations of Existing Approach Page 322 | 322
8.3.5.3 | 8.3.5.3 Planned Improvements Page 323 | 323
8.3.5.4 | 8.3.5.4 Evaluating Mitigation Initiatives Page 324 | 324
8.3.5.5 | 8.3.5.5 Enterprise System for Weather Forecasting Page 327 | 327
8.3.5.5.1 | 8.3.5.5.1 Database(s) Utilized for Storage Page 327 | 327
8.3.5.5.2 | 8.3.5.5.2 Internal Documentation of Database(s) Page 328 | 328
8.3.5.5.3 | 8.3.5.5.3 Integration with Systems in other Lines of Business Page 328 | 328
8.3.5.5.4 | 8.3.5.5.4 QA/QC or Auditing of the System Page 328 | 328
8.3.5.5.5 | 8.3.5.5.5 Internal Processes for Updating Enterprise System Including Database(s) Page 329 | 329
8.3.5.5.6 | 8.3.5.5.6 Changes to the Initiative since the Last WMP Submission Page 329 | 329
8.3.6 | 8.3.6 Fire Potential Index Page 329 | 329
8.3.6.1 | 8.3.6.1 Existing Calculation Approach and Use Page 329 | 329
8.3.6.1.1 | 8.3.6.1.1 Efficacy Study: Determination of Average Distribution Ignition Percentages by Location and Operating Risk Condition Page 332 | 332
8.3.6.2 | 8.3.6.2 Known Limitations of Existing Approach Page 333 | 333
8.3.6.3 | 8.3.6.3 Planned Improvements Page 334 | 334
8.4 | 8.4 Emergency Preparedness Page 334 | 334
8.4.1 | 8.4.1 Overview Page 334 | 334
8.4.1.1 | 8.4.1.1 Objectives Page 336 | 336
8.4.1.2 | 8.4.1.2 Targets Page 339 | 339
8.4.1.3 | 8.4.1.3 Performance Metrics Identified by the Electrical Corporation Page 340 | 340
8.4.2 | 8.4.2 Emergency Preparedness Plan Page 341 | 341
8.4.2.1 | 8.4.2.1 Overview of Wildfire and PSPS Emergency Preparedness ..... 341 | 341
8.4.2.1.1 | 8.4.2.1.1 Purpose and Scope of the Plan Page 341 | 341
8.4.2.1.2 | 8.4.2.1.2 Overview of Wildfire and PSPS Protocols, Policies, and Procedures Page 342 | 342
8.4.2.1.3 | 8.4.2.1.3 Key Personnel, Qualifications, and Training Page 345 | 345
8.4.2.1.4 | 8.4.2.1.4 Resource Planning and Allocation Page 345 | 345
8.4.2.1.5 | 8.4.2.1.5 Drills, Simulations, and Tabletop Exercises Page 345 | 345
8.4.2.1.6 | 8.4.2.1.6 Coordination and Collaboration with Public Safety Partners Page 345 | 345
8.4.2.1.7 | 8.4.2.1.7 Notification of and Communication during and after a Wildfire or PSPS Event Page 345 | 345
8.4.2.1.8 | 8.4.2.1.8 Improvements/Updates since the Last WMP Submission Page 346 | 346
8.4.2.2 | 8.4.2.2 Key Personnel, Qualifications, and Training Page 346 | 346
8.4.2.2.1 | 8.4.2.2.1 Personnel Qualifications Page 346 | 346
8.4.2.2.2 | 8.4.2.2.2 Personnel and External Contractor Training Page 358 | 358
8.4.2.3 | 8.4.2.3 Drills, Simulations, and Tabletop Exercises Page 360 | 360
8.4.2.4 | 8.4.2.4 Schedule for Updating and Revising Plan Page 363 | 363
8.4.3 | 8.4.3 External Collaboration and Coordination Page 365 | 365
8.4.3.1 | 8.4.3.1 Emergency Planning Page 365 | 365
8.4.3.2 | 8.4.3.2 Communication Strategy with Public Safety Partners Page 368 | 368
8.4.3.3 | 8.4.3.3 Mutual Aid Agreements Page 372 | 372
8.4.3.4 | 8.4.3.4 Wildfire and Climate Resilience Center (WCRC) Page 374 | 374
8.4.4 | 8.4.4 Public Emergency Communication Strategy Page 375 | 375
8.4.4.1 | 8.4.4.1 Protocols for Emergency Communications Page 376 | 376
8.4.4.2 | 8.4.4.2 Messaging Page 378 | 378
8.4.4.3 | 8.4.4.3 Current Gaps and Limitations Page 379 | 379
8.4.5 | 8.4.5 Preparedness and Planning for Service Restoration Page 379 | 379
8.4.5.1 | 8.4.5.1 Overview of Service Restoration Plan Page 379 | 379
8.4.5.2 | 8.4.5.2 Planning and Allocation of Resources Page 381 | 381
8.4.5.3 | 8.4.5.3 Drills, Simulations, and Tabletop Exercises Page 382 | 382
8.4.6 | 8.4.6 Customer Support in Wildfire and PSPS Emergencies Page 385 | 385
8.4.6.1 | 8.4.6.1 Outage Reporting Page 385 | 385
8.4.6.2 | 8.4.6.2 Support for Low-Income Customers Page 385 | 385
8.4.6.3 | 8.4.6.3 Billing Adjustments Page 385 | 385
8.4.6.4 | 8.4.6.4 Deposit Waivers Page 386 | 386
8.4.6.5 | 8.4.6.5 Extended Payment Plans Page 386 | 386
8.4.6.6 | 8.4.6.6 Suspension of Disconnection and Nonpayment Fees Page 386 | 386
8.4.6.7 | 8.4.6.7 Repair Processing and Timing Page 386 | 386
8.4.6.8 | 8.4.6.8 Medical Baseline Support Services Page 386 | 386
8.4.6.9 | 8.4.6.9 Access to Electrical Corporation Representatives Page 387 | 387
8.5 | 8.5 Community Outreach and Engagement Page 388 | 388
8.5.1 | 8.5.1 Overview Page 388 | 388
8.5.1.1 | 8.5.1.1 Objectives Page 389 | 389
8.5.1.2 | 8.5.1.2 Targets Page 391 | 391
8.5.1.3 | 8.5.1.3 Performance Metrics Identified by the Electrical Corporation Page 391 | 391
8.5.2 | 8.5.2 Public Outreach and Education Awareness Program Page 392 | 392
8.5.2.1 | 8.5.2.1 Description of the program(s) Page 392 | 392
8.5.2.1.1 | 8.5.2.1.1 Wildfire and PSPS Safety Communications Prior to Events Page 392 | 392
8.5.2.1.2 | 8.5.2.1.2 Wildfire Safety Communications During PSPS Events Page 393 | 393
8.5.2.1.3 | 8.5.2.1.3 PSPS Notifications Page 393 | 393
8.5.2.1.4 | 8.5.2.1.4 Wildfire Safety Communications After an Event Page 394 | 394
8.5.2.2 | 8.5.2.2 Target Community Groups across the Service Territory Page 394 | 394
8.5.2.3 | 8.5.2.3 Community Partners Page 395 | 395
8.5.2.4 | 8.5.2.4 Outreach and Awareness Programs Page 397 | 397
8.5.3 | 8.5.3 Engagement with Access and Functional Needs Populations Page 401 | 401
8.5.3.1 | 8.5.3.1 Overview Page 401 | 401
8.5.3.2 | 8.5.3.2 Summary of Key AFN Demographics Page 401 | 401
8.5.3.3 | 8.5.3.3 Evaluation of Challenges and Needs during a Wildfire or PSPS Event Page 402 | 402
8.5.3.4 | 8.5.3.4 Plans to Address Needs of the AFN Customer Base Page 402 | 402
8.5.3.5 | 8.5.3.5 Ongoing Feedback Practices Page 402 | 402
8.5.4 | 8.5.4 Collaboration on Local Wildfire Mitigation Planning Page 403 | 403
8.5.5 | 8.5.5 Best Practice Sharing with Other Electrical Corporations Page 405 | 405
9 | 9 PUBLIC SAFETY POWER SHUTOFF Page 407 | 407
9.1 | 9.1 Overview Page 407 | 407
9.1.1 | 9.1.1 Key PSPS Statistics Page 407 | 407
9.1.2 | 9.1.2 Identification of Frequently De-energized Circuits Page 408 | 408
9.1.3 | 9.1.3 Objectives Page 412 | 412
9.1.4 | 9.1.4 Targets Page 414 | 414
9.1.5 | 9.1.5 Performance Metrics Page 415 | 415
9.2 | 9.2 Protocols on PSPS Page 416 | 416
9.2.1 | 9.2.1 Protocols that Determine the Need for PSPS Page 416 | 416
9.2.2 | 9.2.2 Method that Evaluates Relative Consequences of PSPS and Wildfires Page 419 | 419
9.2.3 | 9.2.3 Decision-Making Process for Initiating a PSPS Page 419 | 419
9.2.4 | 9.2.4 Protocols for Mitigating Public Safety Impacts of PSPS Page 421 | 421
9.3 | 9.3 Communication Strategy for PSPS Page 422 | 422
9.4 | 9.4 Key Personnel, Qualifications, and Training for PSPS Page 422 | 422
9.5 | 9.5 Planning and Allocation of Resources for Service Restoration due to PSPS Page 422 | 422
10 | 10 LESSONS LEARNED Page .... 423 | 423
10.1 | 10.1 Summary Page 423 | 423
10.2 | 10.2 Identification of Lessons Learned Page 423 | 423
10.2.1 | 10.2.1 Internal Monitoring and Evaluation Page 423 | 423
10.2.2 | 10.2.2 Feedback from Energy Safety or Other Authoritative Bodies Page 425 | 425
10.2.3 | 10.2.3 Collaborations with Other Electrical Corporations Page 426 | 426
10.2.4 | 10.2.4 Lessons Learned from Catastrophic Wildfires Page 427 | 427
10.3 | 10.3 Lessons Learned Page 429 | 429
11 | 11 CORRECTIVE ACTION PROGRAM Page 434 | 434
11.1 | 11.1 Prevent Recurrence of Risk Events Page 434 | 434
11.2 | 11.2 Address Findings from Internal and External Wildfire Investigations Page 435 | 435
11.3 | 11.3 Address Areas for Continued Improvement Identified by Energy Safety as Part of the WMP Evaluation Page 436 | 436
11.4 | 11.4 Process for Reviewing Improvement Area Page 436 | 436
11.4.1 | 11.4.1 Identify Insufficient Occurrence and Response Page 436 | 436
11.4.2 | 11.4.2 Identify Actions to Reduce Recurrence Page 436 | 436
11.4.3 | 11.4.3 Track Implementation Page 437 | 437
11.4.4 | 11.4.4 Improve External Communication Page 437 | 437
11.4.5 | 11.4.5 Integrate Lessons Learned Across Industry Page 438 | 438
11.4.6 | 11.4.6 Share Lessons Learned with Others Page 439 | 439
12 | 12 NOTICES OF VIOLATION AND DEFECT Page 440 | 440
List of Tables | List of Tables
Table 1-1 | Table 1-1: Successes and Lessons Learned for the 2020-2022 WMP Cycle........... 2 | . 2
Table 2-1 | Table 2-1: WMP Section Program Owners Page ... 11 | 11
Table 3-1 | Table 3-1: Statutory Requirements Checklist .. 13 | 13
Table 4-1 | Table 4-1: Summary of WMP Expenditures Page .. 18 | 18
Table 4-2 | Table 4-2: Risk-Informed Approach Components ......... 23 | 23
Table 5-1 | Table 5-1: Service Territory High-Level Statistics .......... 25 | 25
Table 5-2 | Table 5-2: Overview of Key Electrical Equipment ......... 27 | 27
Table 5-3 | Table 5-3: Existing Vegetation Types in the Service Territory ... 28 | 28
Table 5-4 | Table 5-4: Catastrophic Electrical Corporation Wildfires........... 30 | 30
Table 5-5 | Table 5-5: HFTD Statistics Page ... 33 | 33
Table 5-6 | Table 5-6: CFI Customers in Tier 2 of the HFTD ............ 44 | 44
Table 5-7 | Table 5-7: CFI Customers in Tier 3 of the HFTD ............ 45 | 45
Table 5-8 | Table 5-8: Relevant State and Federal Environmental Laws, Regulations, and Permitting Requirements for Implementing the WMP Page 49 | 49
Table 6-1 | Table 6-1: Enterprise CoRE MAVF Attributes Page 53 | 53
Table 6-2 | Table 6-2: Sub-Attributes of Health & Safety .. 53 | 53
Table 6-3 | Table 6-3: Sub-Attributes of Reliability Page ......... 53 | 53
Table 6-4 | Table 6-4: Summary of Risk Models Page . 54 | 54
Table 6-5 | Table 6-5: Risk Components for LoRE Page ........... 68 | 68
Table 6-6 | Table 6-6: Risk Components for Consequence 70 | 70
Table 6-7 | Table 6-7: Pre-Mitigation Analysis Risk Quantification Scores .. 72 | 72
Table 6-8 | Table 6-8: Risk Modeling Assumptions and Limitations ............ 73 | 73
Table 6-9 | Table 6-9: Summary of Design Basis Scenarios 76 | 76
Table 6-1 | Table 6-10: Summary of Design Parameters in WiNGS-Planning Visualization Application ......... 78 | 78
Table 6-1 | Table 6-11: Summary of Extreme-Event Scenarios ....... 80 | 80
Table 6-1 | Table 6-12: Summary of Top-Risk Segments Page 84 | 84
Table 6-1 | Table 6-13: Summary of Key Metrics by Statistical Frequency .. 86 | 86
Table 6-1 | Table 6-14: WiNGS-Planning and WiNGS-Ops Review Findings and Recommendations . 88 | 88
Table 6-1 | Table 6-15: Version Control Hierarchy for WiNGS-Planning 3.0 (in development) .......... 90 | 90
Table 6-1 | Table 6-16: Utility Risk Assessment Improvement Plan ............ 92 | 92
Table 7-1 | Table 7-1: Stakeholder Roles and Responsibilities in the Decision-Making Process ...... 101 | 101
Table 7-2 | Table 7-2: Risk Segment Scoped Mileage 2022-2027 . 103 | 103
Table 7-3 | Table 7-3: Prioritized Areas in the Service Territory Based on Overall Utility Risk ......... 104 | 104
Table 7-4 | Table 7-4: List and Description of Electrical Corporation-Specific WMP Mitigation Initiatives for 3-year and 10-year Outlooks Page ........ 118 | 118
Table 7-5 | Table 7-5: Wildfire Risk Reduction Projection ............ 124 | 124
Table 7-6 | Table 7-6: Summary of Risk Reduction for Top-Risk Segments ............ 126 | 126
Table 7-7 | Table 7-7: Interim Mitigations Initiatives Page .... 127 | 127
Table 8-1 | Table 8-1: Grid Design, Operations, and Maintenance Objectives (3-year plan) ........... 131 | 131
Table 8-2 | Table 8-2: Exemplar Grid Design, Operations, and Maintenance Objectives (10-year plan) ...... 136 | 136
Table 8-3 | Table 8-3: Grid Design, Operations, and Maintenance Targets by Year ............ 140 | 140
Table 8-4 | Table 8-4: Asset Inspections Targets by Year . 142 | 142
Table 8-5 | Table 8-5: Grid Design, Operations, and Maintenance Performance Metrics Results by Year ... 146 | 146
Table 8-6 | Table 8-6: Risk reduction estimation of the Covered Conductor Program........ 151 | 151
Table 8-7 | Table 8-7: Risk Reduction Estimation for the Strategic Undergrounding Program ........ 153 | 153
Table 8-8 | Table 8-8: Risk Reduction Estimation for Distribution Overhead Hardening .... 157 | 157
Table 8-9 | Table 8-9: Risk Reduction Estimation for Transmission Overhead Hardening .. 158 | 158
Table 8-10 | Table 8-10: Risk Reduction Estimation for Transmission-Distribution Underbuilt ......... 159 | 159
Table 8-11 | Table 8-11: Risk Reduction Estimation for Advance Protection ........... 163 | 163
Table 8-12 | Table 8-12: Risk Reduction Estimation for Advance Protection ........... 167 | 167
Table 8-13 | Table 8-13: Risk Reduction Estimation for SCADA Capacitors . 171 | 171
Table 8-14 | Table 8-14: Risk Reduction Estimation for the Expulsion Fuse Replacement Program .. 172 | 172
Table 8-15 | Table 8-15: CAL FIRE and Expulsion Fuse Operation 2015-2021 .......... 173 | 173
Table 8-16 | Table 8-16: CAL FIRE and Expulsion Fuse Operation 2015-2021 by HFTD Tier .. 174 | 174
Table 8-17 | Table 8-17: Risk Reduction Estimation for the HLC Program... 174 | 174
Table 8-18 | Table 8-18: Risk Reduction Estimation for Lightning Arrestor Program ............ 176 | 176
Table 8-19 | Table 8-19: Risk Reduction Estimation for Avian Covers ......... 177 | 177
Table 8-20 | Table 8-20: Risk Reduction Estimation for the Strategic Pole Replacement Program ... 179 | 179
Table 8-21 | Table 8-21: Risk Reduction for Wireless Fault Indicator Program ........ 181 | 181
Table 8-22 | Table 8-22: Asset Inspection Frequency, Method, and Criteria ........... 188 | 188
Table 8-23 | Table 8-23: GO 95, Rule 18 Inspection Finding Priority Levels 189 | 189
Table 8-24 | Table 8-24: Risk Reduction Estimation Methodology for the CMP ...... 191 | 191
Table 8-25 | Table 8-25: Risk Reduction Estimation Methodology for the Transmission Overhead Inspection Program Page ... 194 | 194
Table 8-26 | Table 8-26: Risk Reduction Methodology for Distribution Infrared Inspections Program .......... 196 | 196
Table 8-27 | Table 8-27: Risk Reduction Estimation for Transmission Infrared Inspections . 199 | 199
Table 8-28 | Table 8-28: Risk Reduction Methodology for Distribution Wood Pole Intrusive Inspections ..... 201 | 201
Table 8-29 | Table 8-29: Risk Reduction Methodology for the DIAR Program ......... 207 | 207
Table 8-30 | Table 8-30: Risk Reduction Estimation Methodology for Distribution Patrol Inspections .......... 210 | 210
Table 8-31 | Table 8-31: Risk Reduction Methodology for Transmission Overhead Patrol Inspections ......... 212 | 212
Table 8-32 | Table 8-32: Risk Reduction Estimation for Transmission Aerial 69KV Tier 3 Visual Inspections . 214 | 214
Table 8-33 | Table 8-33: Findings that Trigger Autogenerated Corrective Maintenance Order......... 216 | 216
Table 8-34 | Table 8-34: Maintenance and Replacement Strategies ........... 218 | 218
Table 8-35 | Table 8-35: Risk Event Rate with Pending Infractions 219 | 219
Table 8-36 | Table 8-36: Grid Design and Maintenance QA/QC Program ... 226 | 226
Table 8-37 | Table 8-37: Aging Report for Current Past Due Work Orders .. 233 | 233
Table 8-38 | Table 8-38: Ignition Rate with SRP Enabled Page 234 | 234
Table 8-39 | Table 8-39: Results of Reclosure Protocols in Ignition Avoidance ........ 235 | 235
Table 8-40 | Table 8-40: Effect of Special Work Procedures on Ignitions .... 237 | 237
Table 8-41 | Table 8-41: Effect of CFRs on Ignitions Page ....... 238 | 238
Table 8-42 | Table 8-42: Workforce Planning, Distribution Asset Inspections ......... 240 | 240
Table 8-43 | Table 8-43: Workforce Planning, Transmission Asset Inspections ....... 242 | 242
Table 8-44 | Table 8-44: Workforce Planning, Substation Asset Inspections ........... 244 | 244
Table 8-45 | Table 8-45: Workforce Planning, Distribution Grid Hardening 245 | 245
Table 8-46 | Table 8-46: Workforce Planning, Transmission Grid Hardening ........... 248 | 248
Table 8-47 | Table 8-47: Workforce Planning, Risk Event Inspection .......... 250 | 250
Table 8-48 | Table 8-48: Employee-Conducted Safety Observations .......... 252 | 252
Table 8-49 | Table 8-49: Employee-Submitted Near Misses ........... 253 | 253
Table 8-50 | Table 8-50: Vegetation Management Initiative Objectives (3-year plan) ......... 256 | 256
Table 8-51 | Table 8-51: Vegetation Management Initiative Objectives (10-year plan) ....... 257 | 257
Table 8-52 | Table 8-52: Vegetation Management Initiative Targets by Year .......... 259 | 259
Table 8-53 | Table 8-53: Vegetation Inspections Targets by Year... 260 | 260
Table 8-54 | Table 8-54: Vegetation Management and Inspection Performance Metrics Results by Year ..... 261 | 261
Table 8-55 | Table 8-55: Vegetation Management Inspection Frequency, Method, and Criteria ...... 263 | 263
Table 8-56 | Table 8-56: Vegetation Management QA/QC Program ........... 284 | 284
Table 8-57 | Table 8-57: Number of Past Due Vegetation Management Work Orders (Tree Units) Categorized by Age Page ... 286 | 286
Table 8-58 | Table 8-58: Vegetation Management Qualifications and Training ....... 288 | 288
Table 8-59 | Table 8-59: Situational Awareness Initiative Objectives (3-year plan) . 292 | 292
Table 8-60 | Table 8-60: Situational Awareness Initiative Objectives (10-year plan) ............ 296 | 296
Table 8-61 | Table 8-61: Situational Awareness Initiative Targets by Year .. 298 | 298
Table 8-62 | Table 8-62: Situational Awareness and Forecasting Performance Metrics Results by Year ....... 298 | 298
Table 8-63 | Table 8-63: Summary of Existing Systems, Technologies, and Procedures ....... 301 | 301
Table 8-64 | Table 8-64: Planned Improvements to Environmental Monitoring Systems .... 304 | 304
Table 8-65 | Table 8-65: Grid Operation Monitoring Systems ........ 308 | 308
Table 8-66 | Table 8-66: Planning Improvements to Grid Operation Monitoring Systems ... 310 | 310
Table 8-67 | Table 8-67: Ignition Detection Systems Currently Deployed ... 313 | 313
Table 8-68 | Table 8-68: Planning Improvements to New Fire Detection and Alarm Systems ........... 318 | 318
Table 8-69 | Table 8-69: Planned Improvements to Weather Forecasting Systems 323 | 323
Table 8-70 | Table 8-70: Fire Potential Features Page 331 | 331
Table 8-71 | Table 8-71: 5-Year Average Ignition Rate Page ... 332 | 332
Table 8-72 | Table 8-72: Emergency Preparedness Initiative Objectives (3-year plan) ......... 336 | 336
Table 8-73 | Table 8-73: Emergency Preparedness Initiative Objectives (10-year plan) ....... 338 | 338
Table 8-74 | Table 8-74: Emergency Preparedness Initiative Targets by Year .......... 339 | 339
Table 8-75 | Table 8-75: Emergency Preparedness Performance Metrics Results by Year ... 340 | 340
Table 8-76 | Table 8-76: Key Gaps and Limitations in Integrating Wildfire- and PSPS-Specific Strategies into Emergency Plan Page .... 346 | 346
Table 8-77 | Table 8-77: Emergency Preparedness Staffing and Qualifications ....... 348 | 348
Table 8-78 | Table 8-78: Electrical Corporation Personnel Training Program .......... 358 | 358
Table 8-79 | Table 8-79: Contractor Training Program Page ... 359 | 359
Table 8-80 | Table 8-80: Internal Drill, Simulation, and Tabletop Exercise Program 360 | 360
Table 8-81 | Table 8-81: External Drill, Simulation, and Tabletop Exercise Program ............ 360 | 360
Table 8-82 | Table 8-82: Wildfire-Specific Updates to the CEADPP 364 | 364
Table 8-83 | Table 8-83: State and Local Agency Collaboration(s) . 366 | 366
Table 8-84 | Table 8-84: Key Gaps and Limitations in Collaboration Activities with State and Local Agencies............ 367 | 367
Table 8-85 | Table 8-85: High-Level Communication Protocols, Procedures, and Systems with Public Safety Partners Page ... 369 | 369
Table 8-86 | Table 8-86: Key Gaps and Limitations in Communication Coordination with Public Safety Partners ...... 371 | 371
Table 8-87 | Table 8-87: High-Level Mutual Aid Agreement for Resources During a Wildfire or De-Energization Incident Page ... 373 | 373
Table 8-88 | Table 8-88: Protocols for Emergency Communication to Public Stakeholder Groups ... 377 | 377
Table 8-89 | Table 8-89: Key Gaps and Limitations in Public Emergency Communication Strategy .. 379 | 379
Table 8-90 | Table 8-90: Internal Drill, Simulation, and Tabletop Exercise Program for Service Restoration . 382 | 382
Table 8-91 | Table 8-91: External Drill, Simulation, and Tabletop Exercise Program for Service Restoration 383 | 383
Table 8-92 | Table 8-92: CRC Locations and Services Page ...... 386 | 386
Table 8-93 | Table 8-93: Community Outreach and Engagement Initiative Objectives (3-year plan) 389 | 389
Table 8-94 | Table 8-94: Community Outreach and Engagement Initiative Objectives (10-year plan) ........... 390 | 390
Table 8-95 | Table 8-95: Community Outreach and Engagement Initiative Targets by Year 391 | 391
Table 8-96 | Table 8-96: PSPS Outreach and Engagement Initiative Targets by Year............ 391 | 391
Table 8-97 | Table 8-97: Community Outreach and Engagement Performance Metrics Results by Year ....... 391 | 391
Table 8-98 | Table 8-98: List of Target Communities Page ...... 394 | 394
Table 8-99 | Table 8-99: List of Community Partners Page ..... 395 | 395
Table 8-100 | Table 8-100: Community Outreach and Education Programs . 398 | 398
Table 8-101 | Table 8-101: Collaboration in Local Wildfire Mitigation Planning* ...... 403 | 403
Table 8-102 | Table 8-102: Key Gaps and Limitations in Collaborating on Local Wildfire Mitigation Planning. 404 | 404
Table 8-103 | Table 8-103: Best Practice Sharing with Other Electrical Corporations ............ 406 | 406
Table 9-1 | Table 9-1: PSPS Event Statistics Page ..... 407 | 407
Table 9-2 | Table 9-2: Frequently De-energized Circuits* 409 | 409
Table 9-3 | Table 9-3: PSPS Objectives (3-year plan) Page .... 412 | 412
Table 9-4 | Table 9-4: PSPS Objectives (10-year plan) Page .. 413 | 413
Table 9-5 | Table 9-5: PSPS Targets by Year Page ..... 414 | 414
Table 9-6 | Table 9-6: PSPS Performance Metrics Results by Year 415 | 415
Table 10-1 | Table 10-1: Double Down Initiatives Page ........... 424 | 424
Table 10-2 | Table 10-2: Areas for Continued Improvement .......... 425 | 425
Table 10-3 | Table 10-3: Lessons Learned Page .......... 429 | 429
Table 12-1 | Table 12-1: List of Open Compliance Violations and Defects .. 440 | 440
List of Figures
Figure 1-1 | Figure 1-1: Enterprise Risk Management Framework for Development of the WMP ....... 9 | . 9
Figure 4-1 | Figure 4-1: Summary of WMP Expenditures Page . 19 | 19
Figure 4-2 | Figure 4-2: Enterprise Risk Management Framework .. 21 | 21
Figure 5-1 | Figure 5-1: Utility Service Territory of the Enterprise Risk Management Framework ..... 25 | 25
Figure 5-2 | Figure 5-2: Service Territory (polygons) and Distribution of Customers Served . 26 | 26
Figure 5-3 | Figure 5-3: Catastrophic Wildfire Map Page .......... 31 | 31
Figure 5-4 | Figure 5-4: Map of HFTD in the Service Territory ......... 32 | 32
Figure 5-5 | Figure 5-5: Annual Mean Climatology for the Service Territory 34 | 34
Figure 5-6 | Figure 5-6: Mean Annual Temperature for the Service Territory 1900s-2020s .. 36 | 36
Figure 5-7 | Figure 5-7: Mean Annual Precipitation for the Service Territory 1900s-2020s ... 36 | 36
Figure 5-8 | Figure 5-8: Projected Change in Minimum and Maximum Daily Temperatures . 37 | 37
Figure 5-9 | Figure 5-9: Extreme Fire Weather Days in the Service Territory ............ 39 | 39
Figure 5-10 | Figure 5-10: AFN Customers in the Service Territory ... 42 | 42
Figure 5-11 | Figure 5-11: Communities at Risk in the Service Territory ........ 43 | 43
Figure 6-1 | Figure 6-1: Enterprise CoRE MAVF Page ... 52 | 52
Figure 6-2 | Figure 6-2: Risk Identification Step of the Enterprise Risk Management Framework ...... 59 | 59
Figure 6-3 | Figure 6-3: Enterprise Utility Risk Overview Page . 60 | 60
Figure 6-4 | Figure 6-4: WiNGS-Planning Risk Calculation Process Flow Diagram ..... 61 | 61
Figure 6-5 | Figure 6-5: WiNGS-Ops Calculation Process Flow Diagram ....... 63 | 63
Figure 6-6 | Figure 6-6: Risk Analysis Step of the Enterprise Risk Management Framework . 65 | 65
Figure 6-7 | Figure 6-7: WiNGS-Planning Calculation Schematic ..... 66 | 66
Figure 6-8 | Figure 6-8: WiNGS-Ops Calculation Schematic 67 | 67
Figure 6-9 | Figure 6-9: WiNGS Visualization Interface Page .... 79 | 79
Figure 6-10 | Figure 6-10: Risk Evaluation & Prioritization Step of the Enterprise Risk Management Framework ......... 81 | 81
Figure 6-11 | Figure 6-11: Higher-Risk Urban Areas in Relation to HFTD ........ 82 | 82
Figure 6-12 | Figure 6-12: Map of Service Territory with Circuits Categorized in terms of Wildfire Risk ........... 83 | 83
Figure 7-1 | Figure 7-1: Risk Evaluation & Prioritization Step of the Enterprise Risk Management Framework ......... 100 | 100
Figure 7-2 | Figure 7-2: WiNGS-Planning: Wildfire Hardening Targets ....... 108 | 108
Figure 7-3 | Figure 7-3: Circuit 358-682F: Example of Prior Hardening ...... 111 | 111
Figure 7-4 | Figure 7-4: High-Level Mitigation Prioritization to Reduce Wildfire and PSPS Risk ........ 113 | 113
Figure 7-5 | Figure 7-5: Risk Mitigation Plan Development & Documentation Step of the Enterprise Risk Management Framework Page ........... 117 | 117
Figure 7-6 | Figure 7-6: Projected Overall Wildfire and PSPS Risk Reduction .......... 122 | 122
Figure 8-1 | Figure 8-1: Risk-Informed Investment decision & Risk Mitigation Implementation Step of the Enterprise Risk Management Framework Page ....... 129 | 129
Figure 8-2 | Figure 8-2: Distribution Inspection Findings and Open Work Orders ... 147 | 147
Figure 8-3 | Figure 8-3: Distribution Equipment related HFTD Ignitions and Outages Rate . 148 | 148
Figure 8-4 | Figure 8-4: Transmission Inspection Findings and Open Work Orders in HFTD 149 | 149
Figure 8-5 | Figure 8-5: Transmission Equipment related HFTD Outages and Ignitions ....... 150 | 150
Figure 8-6 | Figure 8-6: FPB Installation at Mobile Home Park Community ............ 183 | 183
Figure 8-7 | Figure 8-7: Distribution Detailed Overhead Inspections Process Flow . 190 | 190
Figure 8-8 | Figure 8-8: Transmission Detailed Overhead Inspections Process Flow ............ 193 | 193
Figure 8-9 | Figure 8-9: Distribution Infrared Inspections Process Flow ..... 195 | 195
Figure 8-10 | Figure 8-10: Transmission Infrared Inspections Process Flow . 198 | 198
Figure 8-11 | Figure 8-11: Wood Pole Intrusive Inspections Process Flow (Transmission and Distribution) ... 200 | 200
Figure 8-12 | Figure 8-12: Distribution Drone Inspections Process Flow ...... 204 | 204
Figure 8-13 | Figure 8-13: DIAR Inspection Prioritization Model ..... 206 | 206
Figure 8-14 | Figure 8-14: Distribution Patrol Inspections Process Flow ...... 209 | 209
Figure 8-15 | Figure 8-15: Transmission Patrol Overhead Inspections Process Flow 211 | 211
Figure 8-16 | Figure 8-16: Transmission Tier 3 69kV Inspections Process Flow ......... 213 | 213
Figure 8-17 | Figure 8-17: Substation Patrol Inspection Workflow .. 215 | 215
Figure 8-18 | Figure 8-18: Asset Criticality and Maintenance/Replacement Strategies ......... 218 | 218
Figure 8-19 | Figure 8-19: WMP Data Platform Page ... 223 | 223
Figure 8-20 | Figure 8-20: Asset 360 3-Year Roadmap Page ..... 225 | 225
Figure 8-21 | Figure 8-21: IIP 3-Year Roadmap Page ... 226 | 226
Figure 8-22 | Figure 8-22: Open Work Orders: Corrective Maintenance ...... 230 | 230
Figure 8-23 | Figure 8-23: Distribution Open Work Orders . 232 | 232
Figure 8-24 | Figure 8-24: Transmission Open Work Orders – Not Past Due 233 | 233
Figure 8-25 | Figure 8-25: Results of Reclosure Protocols in Fault Avoidance ........... 235 | 235
Figure 8-26 | Figure 8-26: Vegetation Inspections and Clearance in the HFTD ......... 262 | 262
Figure 8-27 | Figure 8-27: Vegetation Outages and Ignitions in the HFTD.... 263 | 263
Figure 8-28 | Figure 8-28: Detailed Vegetation Inspections Process Flow .... 266 | 266
Figure 8-29 | Figure 8-29: Fuels Modification Sites Using CRI and WRRM ... 272 | 272
Figure 8-30 | Figure 8-30: Pole Clearing (Brushing) Process Flow .... 274 | 274
Figure 8-31 | Figure 8-31: Enhanced Clearance Process Flow .......... 278 | 278
Figure 8-32 | Figure 8-32: Auditing Pre-Inspection, Tree Trim, and Pole Clearing Process Flow ......... 283 | 283
Figure 8-33 | Figure 8-33: Open Work Orders in the HFTD . 286 | 286
Figure 8-34 | Figure 8-34: Smoke Detection Image Identified by AI Smoke Detection Algorithm ...... 317 | 317
Figure 8-35 | Figure 8-35: SAWTI Across Time and Incidences of Major Wildfires .... 325 | 325
Figure 8-36 | Figure 8-36: Wind Gust Machine Learning Validation for West Alpine 326 | 326
Figure 8-37 | Figure 8-37: Example of ML Gust Forecast Model Output ...... 327 | 327
Figure 8-38 | Figure 8-38: Historical Major Wildfire Correlation to FPI ........ 333 | 333
Figure 8-39 | Figure 8-39: EOC Activation Levels Page 343 | 343
Figure 8-40 | Figure 8-40: SDG&E Response Phases Page ........ 344 | 344
Figure 8-41 | Figure 8-41: WCRC Floor Plan Page ........ 375 | 375
Figure 8-42 | Figure 8-42: Key Components of Service Restoration Procedures ....... 380 | 380
Figure 9-1 | Figure 9-1: Risk-Informed Investment Decision & Risk Mitigation Implementation Step of the Enterprise Risk Management Framework Page ....... 407 | 407
Figure 9-2 | Figure 9-2: Frequently De-Energized Circuits 411 | 411
Figure 9-3 | Figure 9-3: PSPS Customers Impact by RFW .. 416 | 416
Figure 9-4 | Figure 9-4: PSPS System Impact by RFW Page .... 416 | 416
Figure 9-5 | Figure 9-5: PSPS Decision-Making Framework ........... 420 | 420
Figure 10-1 | Figure 10-1: Monitoring & Review Step of the Enterprise Risk Management Framework ......... 423 | 423
Figure 11-1 | Figure 11-1: Monitoring & Review Step of the Enterprise Risk Management Framework ......... 434 | 434
Figure 12-1 | Figure 12-1: Monitoring & Review Step of the Enterprise Risk Management Framework ......... 440 | 440