## Cover Sheet Tables 1-12
| Yes | No | <-- for dropdowns
Energy Safety Data Guidelines Appendix D, Section 1.2
Wildifire Mitigation Data Tables Template: Tables 1 - 15
Update the below table to establish which reporting period this submission this represents.
Utility Name |  | SDG&E
First year of 3-year WMP cycle |  | 2023
Reporting Period year |  | 2023
Reporting Period quarter |  | Q4
Date Modified |  | 2024-02-01

## Table 1
UtilityID | SubmissionDate | InitiativeClassification | ProjectStartDate | ProjectEndDate | UtilityInitiativeName | InitiativeDescription | InitiativeObjecvtive | WMPInitiativeCategory | WMPInitiativeCategory# | WMPInitiativeActivity | ActivityNameifOther | WMPInitiativeActivity# | UtilityInitiativeTrackingID | WMPInitiativeCode | WMPPageNumber | RiskTargetReduction | MidYearTarget (Yes/No) | QuantTargetUnits | AnnualQuantTarget | ProjectedQuantProgressQ1 | ProjectedQuantProgressQ1-2 | ProjectedQuantProgressQ1-3 | ProjectedQuantProgressQ1-4 | QuantActualProgressQ1 | QuantActualProgressQ1-2 | QuantActualProgressQ1-3 | QuantActualProgressQ1-4 | AnnualQualTarget | QualActualProgressQ1 | QualActualProgressQ1-2 | QualActualProgressQ1-3 | QualActualProgressQ1-4 | Status | CorrectiveActionsIfDelayed | REFERENCE: Compliance Branch Requirements --> | Audit | Audit File Documentation Requested | FolderLink | PersonInChargeName | PersonInChargeEmail
SDG&E | 2024-02-01 | Project | 2023-01-01 | 2025-12-31 | Distribution OH Hardening - Covered Conductor | NA | Covered conductor utilizes conductors manufactured with an internal semiconducting layer and external insulating ultraviolet-resistant layer to provide incidental contact protection. The Covered Conductor program has the potential to raise the threshold for PSPS events to higher wind speeds compared to bare conductor. | Grid Design, Operations, and Maintenance | 8.1 | Covered Conductor Installation | NA | 8.1.2.1 | WMP.455 | SDGE_Grid Design, Operations, and Maintainence_Covered Conductor Installation _WMP.455_2023 | 151 | Contact from vegetation ignition likelihood Contact by object ignition likelihood | No | Miles | 60 | 18 | 33 | 45 | 60 | 3.78 | 16.8 | 52.92 | 78.76 | NA | NA | NA | NA | NA | Complete | [5 empty] | Shaun P. Gahagan | sgahagan@sdge.com
SDG&E | 2024-02-01 | Project | 2023-01-01 | 2025-12-31 | Strategic Undergrounding | NA | Strategic undergrounding converts overhead systems to underground, providing the dual benefits of nearly eliminating the risk of utility-caused wildfire and the need for PSPS events in these areas. | Grid Design, Operations, and Maintenance | 8.1 | Undergrounding of electric lines and/or equipment | NA | 8.1.2.2 | WMP.473 | SDGE_Grid Design, Operations, and Maintainence_Undergrounding of Electric Lines and/or Equipment _WMP.473_2023 | 153 | Equipment ignition likelihood Contact from vegetation ignition likelihood Contact by object ignition | No | Miles | 84.43 | 4.39 | 12.94 | 63.88 | 84.43 | 4.38 | 4.38 | 20.68 | 70.26 | NA | NA | NA | NA | NA | Delayed | Delay due to challenges in easement acquisitions and material shortage. Permitting also delayed due to external process changes including extended processing times. | . |  |  |  | Shaun P. Gahagan | sgahagan@sdge.com
SDG&E | 2024-02-01 | Project | 2023-01-01 | 2025-12-31 | Distribution OH System Hardening | NA | Bare Conductor Hardening includes the replacement of wood poles with steel, replacement of conductor with high-strength bare conductor, and in some cases permanent removal of overhead facilities. | Grid Design, Operations, and Maintenance | 8.1 | Traditional overhead hardening | NA | 8.1.2.5.1 | WMP.475 | SDGE_Grid Design, Operations, and Maintainence_Traditional Overhead Hardening (Distribution) _WMP.475_2023 | 157 | Equipment ignition likelihood | No | Miles | 1.9 | 1.8 | 1.8 | 1.8 | 1.9 | 1.31 | 1.78 | 2.13 | 2.33 | NA | NA | NA | NA | NA | Complete | [5 empty] | Shaun P. Gahagan | sgahagan@sdge.com
SDG&E | 2024-02-01 | Project | 2023-01-01 | 2025-12-31 | Transmission OH Hardening | NA | The Transmission System Hardening Program is a program that utilizes enhanced design criteria to replace wood poles with steel poles, replace aging conductors with high strength conductors, and increase conductor spacing in the HFTD to reduce the chance of risk events and ignitions. | Grid Design, Operations, and Maintenance | 8.1 | Traditional overhead hardening | NA | 8.1.2.5.2 | WMP.543 | SDGE_Grid Design, Operations, and Maintainence_Traditional Overhead Hardening (Transmission) _WMP.543_2023 | 159 | Equipment ignition likelihood | No | Miles | 14.1 | 4.8 | 7.8 | 8.8 | 14.1 | 3.36 | 3.36 | 3.65 | 15.76 | NA | NA | NA | NA | NA | Complete |  | . |  |  |  | Shaun P. Gahagan | sgahagan@sdge.com
SDG&E | 2024-02-01 | Project | 2023-01-01 | 2025-12-31 | Transmission OH Hardening - Distribution Underbuild | NA | The Transmission System Hardening Program is a program that utilizes enhanced design criteria to replace wood poles with steel poles, replace aging conductors with high strength conductors, and increase conductor spacing in the HFTD to reduce the chance of risk events and ignitions. | Grid Design, Operations, and Maintenance | 8.1 | Traditional overhead hardening | NA | 8.1.2.5.2 | WMP.545 | SDGE_Grid Design, Operations, and Maintainence_Traditional Overhead Hardening (Distribution Underbuilt)_WMP.545_2023 | 159 | Equipment ignition likelihood | No | Miles | 7.1 | 2.7 | 2.7 | 2.7 | 7.1 | 0.53 | 10.61 | 10.61 | 17.3 | NA | NA | NA | NA | NA | Complete | [5 empty] | Shaun P. Gahagan | sgahagan@sdge.com
SDG&E | 2024-02-01 | Project | 2023-01-01 | 2025-12-31 | Advanced Protection | NA | Advanced Protection creates higher visibility and situational awareness in fire-prone areas, and allow for the implementation of new relay and automation standards in locations where protection coordination is difficult due to lower fault currents attributed to high impedance faults. | Grid Design, Operations, and Maintenance | 8.1 | Installation of system automation equipment | NA | 8.1.2.8.1 | WMP.463 | SDGE_Grid Design, Operations, and Maintainence_Installation of System Automation Equipment (Advanced Protection)_WMP.463_2023 | 163 | Equipment ignition likelihood | No | Circuits | 5 | 2 | 3 | 4 | 5 | 1 | 2 | 2 | 4 | NA | NA | NA | NA | NA | Delayed | One planned Falling Conductor Protection (FCP) circuit was placed on construction hold due to planned undergrounding of a substantial portion of the circuit. | . |  |  |  | Shaun P. Gahagan | sgahagan@sdge.com
SDG&E | 2024-02-01 | Project | 2023-01-01 | 2025-12-31 | Early Fault Detection | NA | Early fault detection employs technologies such as Advance Radio Frequency Sensors (ARFS) and Power Quality (PQ) Meters to detect and prevent significant equipment failures before they occur. | Grid Design, Operations, and Maintenance | 8.1 | Installation of system automation equipment | NA | 8.1.2.8.2 | WMP.1195 | SDGE_Grid Design, Operations, and Maintainence_Installation of System Automation Equipment (EFD) _WMP.1195_2023 | 166 | Equipment ignition likelihood | No | Nodes | 60 | 0 | 20 | 40 | 60 | 0 | 4 | 16 | 32 | NA | NA | NA | NA | NA | Delayed | Proactively paused issuing construction packages of existing ready to construct projects due to design improvements found during QA/QC of previously constructed sites. | . |  |  |  | Shaun P. Gahagan | sgahagan@sdge.com
SDG&E | 2024-02-01 | Project | 2023-01-01 | 2025-12-31 | Distribution Communications Reliability Improvements | NA | The Distribution Communications Reliability Improvement (DCRI) program enables APP and EFD technologies as a reliable communication network is necessary for initiatives that require continuous communication. | Grid Design, Operations, and Maintenance | 8.1 | Installation of system automation equipment | NA | 8.1.2.8.3 | WMP.549 | SDGE_Grid Design, Operations, and Maintainence_Installation of System Automation Equipment (LTE)_WMP.549_2023 | 170 | Wildfire hazard PSPS exposure potential | No | Base Stations | 35 | 8 | 10 | 17 | 35 | 2 | 3 | 8 | 11 | NA | NA | NA | NA | NA | Delayed | Engineering design review delayed due to new Telecom team onboarding. | . |  |  |  | Shaun P. Gahagan | sgahagan@sdge.com
SDG&E | 2024-02-01 | Project | 2023-01-01 | 2025-12-31 | Capacitor Maintenance and replacement program (SCADA) | NA | The SCADA Capacitors Maintenance and Replacement Program will detect and isolate issues before a capacitor rupture occurs, reducing the failure mode most likely to lead to an ignition. | Grid Design, Operations, and Maintenance | 8.1 | Other grid topology improvements to minimize risk of ignitions | NA | 8.1.4.3 | WMP.453 | SDGE_Grid Design, Operations, and Maintainence_Other grid topology improvements to minimize risk of ignitions (SCADA) _WMP.453_2023 | 213 | Equipment ignition likelihood | No | Capacitors | 15 | 0 | 11 | 13 | 15 | 7 | 12 | 16 | 20 | NA | NA | NA | NA | NA | Complete | [5 empty] | Shaun P. Gahagan | sgahagan@sdge.com
SDG&E | 2024-02-01 | Project | 2023-01-01 | 2025-12-31 | Expulsion fuse replacement | NA | The Expulsion Fuse Replacement Program replaces existing expulsion fuses with new, more fire safe expulsion fuses that are approved by CAL FIRE. These new expulsion fuses reduce the discharge expelled into the atmosphere, reducing the chance of a fuse operation leading to an ignition. | Grid Design, Operations, and Maintenance | 8.1 | Other grid topology improvements to minimize risk of ignitions | NA | 8.1.4.4 | WMP.459 | SDGE_Grid Design, Operations, and Maintainence_Other grid topology improvements to minimize risk of ignitions (Expulsion Fuse Replacement) _WMP.459_2023 | 214 | Equipment ignition likelihood | No | Fuses | 40 | 10 | 20 | 30 | 40 | 2 | 8 | 18 | 36 | NA | NA | NA | NA | NA | Complete |  | . |  |  |  | Shaun P. Gahagan | sgahagan@sdge.com
SDG&E | 2024-02-01 | Project | 2023-01-01 | 2025-12-31 | Maintenance, repair, and replacement of connectors, including hotline clamps | NA | The Hotline Clamps (HLC) Replacement Program replaces HLC connections that are connected directly onto the overhead primary conductors with compression connections to eliminate the risk of the wire down failure and the associated wildfire risk. | Grid Design, Operations, and Maintenance | 8.1 | Other grid topology improvements to minimize risk of ignitions | NA | 8.1.4.5 | WMP.464 | SDGE_Grid Design, Operations, and Maintainence_Other grid topology improvements to minimize risk of ignitions (HLC)_WMP.464_2023 | 216 | Equipment ignition likelihood | No | HLCs | 250 | 63 | 126 | 188 | 250 | 77 | 400 | 775 | 962 | NA | NA | NA | NA | NA | Complete | [5 empty] | Shaun P. Gahagan | sgahagan@sdge.com
SDG&E | 2024-02-01 | Project | 2023-01-01 | 2025-12-31 | Lightning arrester removal and replacement | NA | Lightning Arrestors Replacement Program installs CAL FIRE-approved lightning arrestors to mitigate the impact of transient overvoltage on the electric system. CAL FIRE-approved lightning arrestors are equipped with an external device that operates prior to the arrestor overloading, dramatically reducing the potential of becoming an ignition source. | Grid Design, Operations, and Maintenance | 8.1 | Other grid topology improvements to minimize risk of ignitions | NA | 8.1.4.6 | WMP.550 | SDGE_Grid Design, Operations, and Maintainence_Other grid topology improvements to minimize risk of ignitions (Arrestors)_WMP.550_2023 | 218 | Equipment ignition likelihood | No | Arrestors | 1848 | 640 | 1531 | 1715 | 1848 | 578 | 1375 | 1896 | 2216 | NA | NA | NA | NA | NA | Complete | [5 empty] | Shaun P. Gahagan | sgahagan@sdge.com
SDG&E | 2024-02-01 | Project | 2023-01-01 | 2025-12-31 | Avian Protection | NA | Avian Protection is aimed at improving reliability and reducing the risk of faults and wire-down events associated with avian contact that can lead to ignitions. | Grid Design, Operations, and Maintenance | 8.1 | Other grid topology improvements to minimize risk of ignitions | NA | 8.1.2.10.1 | WMP.972 | SDGE_Grid Design, Operations, and Maintainence_Other grid topology improvements to minimize risk of ignitions (Avian)_WMP.972_2023 | 171 | Contact by object ignition | No | Poles | 200 | 50 | 100 | 150 | 200 | 81 | 263 | 517 | 657 | NA | NA | NA | NA | NA | Complete | [5 empty] | Shaun P. Gahagan | sgahagan@sdge.com
SDG&E | 2024-02-01 | Project | 2023-01-01 | 2025-12-31 | Strategic Pole Replacement Program | NA | Strategic Pole Replacement targets high-risk poles located throughout the service territory that are gas treated (also known as Cellon treatment) and are set in concrete and steel reinforced, steel reinforced and set in soil, or set in soil, and are not being address by other programs such as Covered Conductor Hardening or Strategic Undergrounding. | Grid Design, Operations, and Maintenance | 8.1 | Other grid topology improvements to minimize risk of ignitions | NA | 8.1.2.10.2 | WMP.1189 | SDGE_Grid Design, Operations, and Maintainence_Other grid topology improvements to minimize risk of ignitions (Pole Replacements)_WMP.1189_2023 | 173 | Equipment ignition likelihood | No | Poles | 60 | 0 | 0 | 27 | 60 | 0 | 0 | 0 | 1 | NA | NA | NA | NA | NA | Delayed | Remaining poles postponed to 2024 due to delayed design and limited construction resources. | . |  |  |  | Shaun P. Gahagan | sgahagan@sdge.com
SDG&E | 2024-02-01 | Project | 2023-01-01 | 2025-12-31 | PSPS Sectionalizing Enhancements | NA | PSPS Sectionalizing Enhancement Program installs switches in strategic locations, improving the ability to isolate high-risk areas for potential de energization. For example, switches are installed on circuits that have significant sections undergrounded, allowing customers with this lower-risk infrastructure to remain energized during weather events. | Grid Design, Operations, and Maintenance | 8.1 | Other grid topology improvements to mitigate or reduce PSPS events | NA | 8.1.2.11.1 | WMP.461 | SDGE_Grid Design, Operations, and Maintainence_Other grid topology improvements to mitigate or reduce PSPS events (PSPS Sectionalizing Enhancements)_WMP.461_2023 | 175 | PSPS exposure potential PSPS vulnerability | No | Switches | 10 | 6 | 9 | 10 | 10 | 0 | 1 | 8 | 10 | NA | NA | NA | NA | NA | Complete | [5 empty] | Shaun P. Gahagan | sgahagan@sdge.com
SDG&E | 2024-02-01 | Project | 2020-07-01 | 2025-12-31 | Fixed Power Backup | NA | This program assists backcountry residences, businesses, and local communities in the HFTD by providing a fixed installation backup generator, or a solar panel and battery backup system to keep customers energized during PSPS. | Grid Design, Operations, and Maintenance | 8.1 | Other grid topology improvements to mitigate or reduce PSPS events | NA | 8.1.2.11.2 | WMP.468 | SDGE_Grid Design, Operations, and Maintainence_Other grid topology improvements to mitigate or reduce PSPS events (Standby Power)_WMP.468_2023 | 175 | PSPS vulnerability | No | Generators | 300 | 50 | 100 | 250 | 300 | 38 | 128 | 302 | 362 | NA | NA | NA | NA | NA | Complete | [5 empty] | Shaun P. Gahagan | sgahagan@sdge.com
SDG&E | 2024-02-01 | Project | 2020-07-01 | 2025-12-31 | Generator Grant Program | NA | The Resiliency Grant Programs offer portable battery units with solar charging capacity to provide vulnerable customers with a means to keep small devices and appliances charged and powered during PSPS events. | Grid Design, Operations, and Maintenance | 8.1 | Other grid topology improvements to mitigate or reduce PSPS events | NA | 8.1.2.11.3 | WMP.466 | SDGE_Grid Design, Operations, and Maintainence_Other grid topology improvements to mitigate or reduce PSPS events (Generator Grant Program)_WMP.466_2023 | 177 | PSPS vulnerability | No | Generators | NA | NA | NA | NA | NA | NA | NA | NA | NA | Design and Implement the 2023 Generater Grant Program for mid-year launch to eligible Medical Baseline or Access and Functional Needs customers in the HFTD Tiers 2 and 3 with a history of PSPS. Develop eligible customer lists, outreach and customer communications, research and procure portable power stations, and manage participation process. | Scope of Work updates and budget negotiations completed. Amendment with Supply Management for finalization and execution. In process with Systems Support, to be complete by end of April. Will continue to perform periodic assessments of new and currently available portable battery products to inform program planning. Eligible customer list generated. List will be refreshed prior to program prelaunch and periodically throughout 2023, to capture and add newly eligable customers. | Qualified Product List finalized. All 2023 updated for customer communication, website, and outreach materials have been completed and in final review. Testing final edits to customer facing rebate portal, estimated to go live by end of July. | Outreach Materials - All eligible Medical Baseline and Life Support customers have sent program information materials via mail. The contractor, Richard Heath & Associates, is also performing outreach phone calls to eligible customers to notify them of qualification for the program and delivery appointment setting. Proactive phone outreach will continue into Q4. Wildfire Safety Fairs - Educated and collected information from customers interested in GGP during the Wildfire Safety Fairs, which had collectively over 3,000 customers in attendence this year. Partnerships - Outreach materials to Tribl Relations Manager to distribute to community leaders. GGP information included in newly created AFN outreach flyer. Continued strategy touchpoints with Tribal Nations and AFN to increase awareness of GGP. | Completed - Concluded performing outreach phone calls to eligible customers to notify them of qualification for the program and to schedule delivery appointments. ompleted end of year participation report including all deliveries that took place in 2023. A total of 805 backup batteries with solar charging panels were delivered to qualified customers in 2023. As the GGP program matures and the most at-risk qualifying customers are serviced, the remaining pool of eligible customers decreases resulting in a fewer number of brand new battery deliveries per year. Efforts will continue to be focused on delivering batteries to newly qualifying customers and outreach to past participants. Outreach to 2022 program participants began to gather information on satisfaction, provide re-education, answer questions, and provide warranty replacements if needed. Ongoing - Outreach efforts will continue into Q1 2024 and with both an email customer satisfaction survey and the expansion of follow-up calls (satisfaction, re-education, etc.) to 2023 participants. | Complete | [5 empty] | Shaun P. Gahagan | sgahagan@sdge.com
SDG&E | 2024-02-01 | Project | 2020-07-01 | 2025-12-31 | Generator Assistance Program | NA | The Resiliency Assistance Programs focus on enhancing resiliency for customers who reside in the HFTD and may be impacted by PSPS events. The program offers a rebate to customers providing a 70-to-90 percent discount on average portable generator models to mitigate the impacts of PSPS. | Grid Design, Operations, and Maintenance | 8.1 | Other grid topology improvements to mitigate or reduce PSPS events | NA | 8.1.2.11.4 | WMP.467 | SDGE_Grid Design, Operations, and Maintainence_Other grid topology improvements to mitigate or reduce PSPS events (Generator Assistance Program)_WMP.467_2023 | 179 | PSPS vulnerability | No | Generators | NA | NA | NA | NA | NA | NA | NA | NA | NA | Design and Implement the 2023 Generater Assistance Program for mid-year launch to eligible customers in the HFTD Tiers 2 and 3 with a history of PSPS. Develop eligible customer lists, outreach and customer communications, qualified rebate product lists, and implement changes for continuous improvement of the rebate application process and customer experience. | Scope of work updated completed. Budget negotiations close to completion, expected by 3rd week of April. In process with Systems Support, expected complete by end of April. Review od available backup battery in process, expected completion by mid-May. Eligible customer list generated. List will be refreshed prior to program prelaunch and periodically throughout 2023, to capture and add newly eligable customers. | All 2023 updated for customer communication, website, and outreach materials have been completed and in final review. All systems and processes updated and active for customer participation. Procedures in place for emergency deployment of backup batteries. | Marketing and Outreach - All eligible customers have sent program information materials via email or mail (if no email address on file). Marketing communication follow-up messaging will continue into Q4. Wildfire Safety Fairs - Distributed promotional materials and educated customers on GAP during the Wildfire Safety Fairs, which had collectively over 3,000 customers in attendence this year. | Completed - Program marketing to all eligible customers has concluded and all issued rebate coupons have expired as of 12/31/23. Coupons redeemed and post purchase rebate applications received towards the end of December are currently being processed. Final December participation details will be received mid-January. Customer satisfaction email survey developed and targeted to be distributed to 2023 participating customers second week of January 2024. In Process - End of program year participation reports are being finalized. Final December participation details will be received mid-January. A total of 197 rebates issued to qualifying customers in 2023 (as of 11/30). Final December participation details will be received mid-January. | Complete | [5 empty] | Shaun P. Gahagan | sgahagan@sdge.com
SDG&E | 2024-02-01 | Program | NA | NA | Distribution Overhead Detailed Inspections | NA | Perform OH detailed inspections, as scheduled, to reduce the risk of equipment failure. | Grid Design, Operations, and Maintenance | 8.1 | Asset Inspections | NA | 8.1.3.1 | WMP.478 | SDGE_Grid Design, Operations, and Maintainence_Asset Inspections (Detailed Inspections of Distribution Electric Lines and Equipment)_WMP.478_2023 | 182 | Equipment ignition likelihood | Yes | Structures | 11100 | 6350 | 8450 | 9650 | 11100 | 4326 | 8405 | 10601 | 11755 | NA | NA | NA | NA | NA | Complete | [5 empty] | Shaun P. Gahagan | sgahagan@sdge.com
SDG&E | 2024-02-01 | Program | NA | NA | Transmission Overhead Detailed Inspections | NA | Perform OH detailed inspections, as scheduled, to reduce the risk of equipment failure. | Grid Design, Operations, and Maintenance | 8.1 | Asset Inspections | NA | 8.1.3.2 | WMP.479 | SDGE_Grid Design, Operations, and Maintainence_Asset Inspections (Detailed Inspections of Transmission Electric Lines and Equipment) _WMP.479_2023 | 185 | Equipment ignition likelihood | Yes | Structures | 2387 | 531 | 850 | 1672 | 2387 | 130 | 723 | 1533 | 1928 | NA | NA | NA | NA | NA | Delayed | 13 tielines scheduled in Q1 2024 in compliance with CAISO-approved transmission maintenance practice. | . |  |  |  | Shaun P. Gahagan | sgahagan@sdge.com
SDG&E | 2024-02-01 | Program | NA | NA | Distribution Infrared Inspections | NA | Perform infrared inspections, as scheduled, to reduce the risk of equipment failure. | Grid Design, Operations, and Maintenance | 8.1 | Asset Inspections | NA | 8.1.3.3 | WMP.481 | SDGE_Grid Design, Operations, and Maintainence_Asset Inspections (Infrared Inspections of Distribution Electric Lines and Equipment)_WMP.481_2023 | 188 | Equipment ignition likelihood | Yes | Structures | 9578 | 3013 | 6343 | 8147 | 9578 | 2989 | 7279 | 10270 | 11900 | NA | NA | NA | NA | NA | Complete | [5 empty] | Shaun P. Gahagan | sgahagan@sdge.com
SDG&E | 2024-02-01 | Program | NA | NA | Transmission Infrared Inspections | NA | Perform infrared inspections, as scheduled, to reduce the risk of equipment failure. | Grid Design, Operations, and Maintenance | 8.1 | Asset Inspections | NA | 8.1.3.4 | WMP.482 | SDGE_Grid Design, Operations, and Maintainence_Asset Inspections (Infrared Inspections of Transmission Electric Lines and Equipment)_WMP.482_2023 | 189 | Equipment ignition likelihood | Yes | Structures | 6179 | 0 | 0 | 0 | 6179 | 0 | 0 | 6077 | 6077 | NA | NA | NA | NA | NA | Complete | [5 empty] | Shaun P. Gahagan | sgahagan@sdge.com
SDG&E | 2024-02-01 | Program | NA | NA | Distribution Wood Pole Intrusive Inspections | NA | Perform intrusive inspections, as scheduled, to reduce the risk of equipment failure | Grid Design, Operations, and Maintenance | 8.1 | Asset Inspections | NA | 8.1.3.5 | WMP.483 | SDGE_Grid Design, Operations, and Maintainence_Asset Inspections (Distribution Wood Pole Intrusive Pole Inspections)_WMP.483_2023 | 192 | Equipment ignition likelihood | Yes | Structures | 50 | 0 | 0 | 50 | 50 | 271 | 527 | 726 | 1038 | NA | NA | NA | NA | NA | Complete | [5 empty] | Shaun P. Gahagan | sgahagan@sdge.com
SDG&E | 2024-02-01 | Program | NA | NA | Transmission Wood Pole Intrusive Inspections | NA | Perform intrusive inspections, as scheduled, to reduce the risk of equipment failure | Grid Design, Operations, and Maintenance | 8.1 | Asset Inspections | NA | 8.1.3.6 | WMP.1190 | SDGE_Grid Design, Operations, and Maintainence_Asset Inspections (Wood Pole Trans)_WMP.1190_2023 | 194 | Equipment ignition likelihood | Yes | Structures | 73 | 0 | 0 | 0 | 73 | 1 | 38 | 38 | 90 | NA | NA | NA | NA | NA | Complete | [5 empty] | Shaun P. Gahagan | sgahagan@sdge.com
SDG&E | 2024-02-01 | Program | NA | NA | Drone Assessments | NA | Perform drone inspections on highest risk structures in the HFTD and WUI areas. | Grid Design, Operations, and Maintenance | 8.1 | Asset Inspections | NA | 8.1.3.7 | WMP.552 | SDGE_Grid Design, Operations, and Maintainence_Asset Inspections (Distribution Drone Assessments)_WMP.552_2023 | 194 | Equipment ignition likelihood | Yes | Structures | 13692 | 3426 | 6848 | 10270 | 13692 | 604 | 7599 | 15311 | 15311 | NA | NA | NA | NA | NA | Complete | [5 empty] | Shaun P. Gahagan | sgahagan@sdge.com
SDG&E | 2024-02-01 | Program | NA | NA | Distribution Overhead Patrol Inspections | NA | Perform OH patrol inspections, as scheduled, to reduce the risk of equipment failure | Grid Design, Operations, and Maintenance | 8.1 | Asset Inspections | NA | 8.1.3.8 | WMP.488 | SDGE_Grid Design, Operations, and Maintainence_Asset Inspections (Distribution OH Patrol Inspections)_WMP.488_2023 | 200 | Equipment ignition likelihood | Yes | Structures | 86880 | 35300 | 61800 | 86500 | 86880 | 24998 | 60986 | 83041 | 85857 | NA | NA | NA | NA | NA | Complete | [5 empty] | Shaun P. Gahagan | sgahagan@sdge.com
SDG&E | 2024-02-01 | Program | NA | NA | Transmission Overhead Patrol Inspections | NA | Perform OH patrol inspections, as scheduled, to reduce the risk of equipment failure | Grid Design, Operations, and Maintenance | 8.1 | Asset Inspections | NA | 8.1.3.9 | WMP.489 | SDGE_Grid Design, Operations, and Maintainence_Asset Inspections (Transmission Overhead Patrol)_WMP.489_2023 | 202 | Equipment ignition likelihood | Yes | Structures | 6337 | 0 | 6008 | 6008 | 6337 | 3120 | 5985 | 6200 | 6200 | NA | NA | NA | NA | NA | Complete | [5 empty] | Shaun P. Gahagan | sgahagan@sdge.com
SDG&E | 2024-02-01 | Program | NA | NA | Transmission 69kV Tier 3 Visual Inspections | NA | Perform supplemental inspections on all 69kV tielines in Tier 3 prior to wildfire season | Grid Design, Operations, and Maintenance | 8.1 | Asset Inspections | NA | 8.1.3.10 | WMP.555 | SDGE_Grid Design, Operations, and Maintainence_Asset Inspections (Transmission 69kV Tier 3)_WMP.555_2023 | 206 | Equipment ignition likelihood | Yes | Structures | 1632 | 0 | 0 | 1632 | 1632 | 0 | 0 | 1602 | 1602 | NA | NA | NA | NA | NA | Complete | [5 empty] | Shaun P. Gahagan | sgahagan@sdge.com
SDG&E | 2024-02-01 | Program | NA | NA | Substation Patrol inspections | NA | Perform substation patrols, as scheduled, to reduce the risk of equipment failure and to manage vegetation hazards within the substation. | Grid Design, Operations, and Maintenance | 8.1 | Asset Inspections | NA | 8.1.3.11 | WMP.492 | SDGE_Grid Design, Operations, and Maintainence_Asset Inspections (Substation Patrol)_WMP.492_2023 | 207 | Equipment ignition likelihood | No | Substations | 384 | 89 | 192 | 281 | 384 | 92 | 198 | 290 | 396 | NA | NA | NA | NA | NA | Complete | [5 empty] | Shaun P. Gahagan | sgahagan@sdge.com
SDG&E | 2024-02-01 | Program | NA | NA | QA/QC of Transmission Inspections | NA | Perform QA/QC of inspections to validate inspection results, either by field or desktop validation | Grid Design, Operations, and Maintenance | 8.1 | Quality assurance / quality control | NA | 8.1.6.1 | WMP.1191 | SDGE_Grid Design, Operations, and Maintainence_Quality assurance / quality control (Secondary Trans)_WMP.1191_2023 | 226 | Equipment ignition likelihood | Yes | Findings | 100% | 1 | 1 | 1 | 1 | 100% | 100% | 100% | 97% | NA | NA | NA | NA | NA | Complete | [5 empty] | Shaun P. Gahagan | sgahagan@sdge.com
SDG&E | 2024-02-01 | Program | NA | NA | QA/QC of Distribution Detailed Inspections | NA | Perform QA/QC of inspections to validate inspection results, either by field or desktop validation | Grid Design, Operations, and Maintenance | 8.1 | Quality assurance / quality control | NA | 8.1.6.2 | WMP.491 | SDGE_Grid Design, Operations, and Maintainence_Quality assurance / quality control (Distribution Detailed)_WMP.491_2023 | 226 | Equipment ignition likelihood | No | Structures | 160 | 0 | 0 | 0 | 160 | 8 | 68 | 111 | 150 | NA | NA | NA | NA | NA | Complete | [5 empty] | Shaun P. Gahagan | sgahagan@sdge.com
SDG&E | 2024-02-01 | Program | NA | NA | QA/QC of Distribution Drone Assessments | NA | Perform QA/QC of inspections to validate inspection results, either by field or desktop validation | Grid Design, Operations, and Maintenance | 8.1 | Quality assurance / quality control | NA | 8.1.6.3 | WMP.1192 | SDGE_Grid Design, Operations, and Maintainence_Quality assurance / quality control (Distribution Drone)_WMP.1192_2023 | 227 | Equipment ignition likelihood | No | Structures | 13692 | 3426 | 6753 | 10127 | 13500 | 604 | 7599 | 15311 | 15311 | NA | NA | NA | NA | NA | Complete | [5 empty] | Shaun P. Gahagan | sgahagan@sdge.com
SDG&E | 2024-02-01 | Program | NA | NA | QA/QC of Wood Pole Intrusive (Transmission & Distribution) | NA | Perform QA/QC of inspections to validate inspection results, either by field or desktop validation | Grid Design, Operations, and Maintenance | 8.1 | Quality assurance / quality control | NA | 8.1.6.4 | WMP.1193 | SDGE_Grid Design, Operations, and Maintainence_Quality assurance / quality control (Wood Pole Dist &Trans)_WMP.1193_2023 | 227 | Equipment ignition likelihood | No | Structures | 12 | 0 | 0 | 0 | 12 | 55 | 93 | 111 | 111 | NA | NA | NA | NA | NA | Complete | [5 empty] | Shaun P. Gahagan | sgahagan@sdge.com
SDG&E | 2024-02-01 | Program | NA | NA | QA/QC of Substation Inspections | NA | Perform QA/QC of inspections to validate inspection results, either by field or desktop validation | Grid Design, Operations, and Maintenance | 8.1 | Quality assurance / quality control | NA | 8.1.6.5 | WMP.1194 | SDGE_Grid Design, Operations, and Maintainence_Quality assurance / quality control (Periodic Review)_WMP.1194_2023 | 227 | Equipment ignition likelihood | No | Structures | 18 | 0 | 9 | 9 | 18 | 0 | 11 | 11 | 23 | NA | NA | NA | NA | NA | Complete | [5 empty] | Shaun P. Gahagan | sgahagan@sdge.com
SDG&E | 2024-02-01 | Project | 2022-01-01 | 2023-12-31 | Air Quality Index | NA | The AQI program will install particulate sensors and an automatic notification system to notify employees when the AQI for Particulate Matter 2.5 microns or smaller in diameter (PM2.5) exceeds 150 or exceeds 500 during wildfires. | Situational Awareness and Forecasting | 8.3 | Enviornmental monitoring System | NA | 8.3.2.1.3 | WMP.970 | SDGE_Situational Awareness and Forecasting_Environmental Monitoring System (Air Quality Index)_WMP.970_2023 | 298 | Wildfire hazard | No | Sensors | 6 | 3 | 6 | 6 | 6 | 2 | 5 | 5 | 5 | NA | NA | NA | NA | NA | Complete | [5 empty] | Sandeep Aujla | saujla@sdge.com
SDG&E | 2024-02-01 | Program | NA | NA | Detailed Inspections | NA | Vegetation management operations are driven by regulatory requirements and follow an annual, schedule that includes inspection, tree trimming, and auditing. During the annually scheduled routine inspection activity, all inventory trees are inspected to determine whether they require pruning to maintain mandated clearances from electrical lines. | Vegetation Management and Inspection | 8.2 | Vegetation Management Inspection Program | NA | 8.2.2.1 | WMP.494 | SDGE_Vegetation Management and Inspection_Vegetation Management Inspection Program (Detailed inspections of vegetation around distribution electric lines and equipment) _WMP.494_2023 | 260 | Contact from vegetation ignition likelihood | No | Inspections | 485400 | 123100 | 241800 | 374200 | 485400 | 116089 | 239800 | 364122 | 514626 | NA | NA | NA | NA | NA | Complete | [5 empty] | Oliva Reyes | oreyes@sdge.com
SDG&E | 2024-02-01 | Program | NA | NA | Off-Cycle Patrol | NA | Vegetation management operations are driven by regulatory requirements and follow an annual, schedule that includes inspection, tree trimming, and auditing. During the annually scheduled routine inspection activity, all inventory trees are inspected to determine whether they require pruning to maintain mandated clearances from electrical lines. | Vegetation Management and Inspection | 8.2 | Vegetation Management Inspection Program | NA | 8.2.2.2 | WMP.508 | SDGE_Vegetation Management and Inspection_Vegetation Management Inspection Program (Off-Cycle)_WMP.508_2023 | 265 | Contact from vegetation ignition likelihood | No | VMAs | 106 | 0 | 9 | 106 | 106 | 25 | 44 | 92 | 106 | NA | NA | NA | NA | NA | Complete | [5 empty] | Oliva Reyes | oreyes@sdge.com
SDG&E | 2024-02-01 | Program | NA | NA | Fuels management | NA | Wildland fuel reduction involves the thinning, pruning, and in some cases, removal of vegetation for the purpose of minimizing source material that could ignite and propagate a wildfire. | Vegetation Management and Inspection | 8.2 | Fuels management | NA | 8.2.3 | WMP.497 | SDGE_Vegetation Management and Inspection_Fuel Management (slash) _WMP.497_2023 | 273 | Wildfire hazard | No | Poles Cleared | 500 | 100 | 100 | 200 | 500 | 71 | 71 | 123 | 514 | NA | NA | NA | NA | NA | Complete |  | . |  |  |  | Oliva Reyes | oreyes@sdge.com
SDG&E | 2024-02-01 | Program | NA | NA | Pole Clearing (Brushing) | NA | Pole brushing is a fire prevention measure involving the removal of vegetation at the base of poles that carry specific types of electrical hardware that could cause sparking or molten material to fall to the ground. | Vegetation Management and Inspection | 8.2 | Pole Clearing | NA | 8.2.3.1 | WMP.512 | SDGE_Vegetation Management and Inspection_Pole Clearing (Brushing)_WMP.501_2023 | 270 | Wildfire hazard | No | Poles Brushed | 33010 | 12180 | 22630 | 24560 | 29101 | 13216 | 25591 | 31762 | 35258 | NA | NA | NA | NA | NA | Complete | [5 empty] | Oliva Reyes | oreyes@sdge.com
SDG&E | 2024-02-01 | Program | NA | NA | Clearance | NA | Vegetation Management defines enhanced clearances as greater than or equal to 12 feet at time of trim, which is the CPUC-recommended post-trim clearance for distribution voltages in the HFTD. SDG&E aims to achieve clearances up to 25 feet, where feasible, to achieve the optimal risk mitigation. | Vegetation Management and Inspection | 8.2 | Clearance | NA | 8.2.3.3 | WMP.501 | SDGE_Vegetation Management and Inspection_Clearance (Achieve clearances around electric lines and equipment) _WMP.512_2023 | 274 | Contact from vegetation ignition likelihood | No | Trees Trimmed or Removed | 11200 | 2750 | 5890 | 8780 | 11200 | 2423 | 5372 | 9551 | 13419 | NA | NA | NA | NA | NA | Complete | [5 empty] | Oliva Reyes | oreyes@sdge.com
SDG&E | 2024-02-01 | Program | NA | NA | QA/QC Vegetation Management | NA | SDG&E uses statistical sampling methodology in its audits of all Vegetation Management-related activities including pre-inspection, clearance (tree trimming), and pole clearing. Audit results are tracked, documented, and reported as a core component of contractor performance. | Vegetation Management and Inspection | 8.2 | Quality assurance / quality control | NA | 8.2.5 | WMP.505 | SDGE_Vegetation Management and Inspection_Quality assurance / quality control_WMP.505_2023 | 280 | Contact from vegetation ignition likelihood | No | Inspections | 15% | 15% | 15% | 15% | 15% | 23217 | 47, 533 | 66517 | 18% | NA | NA | NA | NA | NA | Complete | [5 empty] | Oliva Reyes | oreyes@sdge.com

## Table 2
| Utility | SDG&E | Notes:
| Table No. | 2 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
| Date Modified | 2024-02-01 | HWW = High wind warning
RFW = Red flag warning
[10 empty] | Actuals | [15 empty] | Note: These columns are placeholders for future QR submissions. | [7 empty] | Projected
| Table 2: Performance Metrics | [8 empty] | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
| Metric type | # | Metric name | Wind Warning Status | Program Name | HFTD Tier | Line Type | Inspection Type | Inspection Method | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | 2024 | 2024 | 2024 | 2024 | 2025 | 2025 | 2025 | 2025 | 2023 | 2024 | 2025 | Unit(s) | Comments | Blank Meaning
| 1. Risk Events | 1.a. | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | RFW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 | 0 | 17 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | 1 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 4 | 0 | 9 | 2 | 3 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW & RFW | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | None | N/A | HFTD Tier 2 | N/A | N/A | N/A | 58 | 62 | 49 | 44 | 68 | 48 | 88 | 71 | 57 | 50 | 56 | 51 | 72 | 51 | 54 | 50 | [11 empty] | Number of events
|  |  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | RFW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 | 0 | 10 | 5 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | 5 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 3 | 0 | 10 | 0 | 6 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW & RFW | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | None | N/A | HFTD Tier 3 | N/A | N/A | N/A | 27 | 50 | 57 | 39 | 52 | 42 | 70 | 57 | 36 | 34 | 38 | 32 | 52 | 22 | 44 | 29 | [11 empty] | Number of events
|  |  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | RFW only | N/A | Non- HFTD | N/A | N/A | N/A | 0 | 0 | 27 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW only | N/A | Non- HFTD | N/A | N/A | N/A | 2 | 0 | 0 | 0 | 35 | 0 | 0 | 1 | 0 | 0 | 5 | 2 | 39 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | HWW & RFW | N/A | Non- HFTD | N/A | N/A | N/A | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of all events with probability of ignition, including wires down, contacts with objects, line slap, events with evidence of heat generation, and other events that cause sparking or have the potential to cause ignition | None | N/A | Non- HFTD | N/A | N/A | N/A | 135 | 145 | 176 | 147 | 150 | 186 | 186 | 197 | 161 | 153 | 143 | 152 | 194 | 153 | 141 | 117 | [11 empty] | Number of events
| 1. Risk Events | 1.b. | Number of wires down | RFW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of wires down | HWW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of wires down | HWW & RFW | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of wires down | None | N/A | HFTD Tier 2 | N/A | N/A | N/A | 13 | 6 | 5 | 1 | 8 | 6 | 5 | 8 | 3 | 0 | 4 | 8 | 10 | 5 | 5 | 7 | [11 empty] | Number of events
|  |  | Number of wires down | RFW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of wires down | HWW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of wires down | HWW & RFW | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of wires down | None | N/A | HFTD Tier 3 | N/A | N/A | N/A | 2 | 2 | 3 | 3 | 7 | 4 | 2 | 6 | 4 | 3 | 1 | 3 | 7 | 0 | 4 | 2 | [11 empty] | Number of events
|  |  | Number of wires down | RFW only | N/A | Non- HFTD | N/A | N/A | N/A | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of wires down | HWW only | N/A | Non- HFTD | N/A | N/A | N/A | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of wires down | HWW & RFW | N/A | Non- HFTD | N/A | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of wires down | None | N/A | Non- HFTD | N/A | N/A | N/A | 14 | 11 | 9 | 20 | 13 | 17 | 9 | 20 | 19 | 11 | 11 | 18 | 35 | 17 | 14 | 8 | [11 empty] | Number of events
| 1. Risk Events | 1.c. | Number of outage events not caused by contact with vegetation | RFW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 | 0 | 17 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of outage events not caused by contact with vegetation | HWW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | 1 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 3 | 0 | 7 | 2 | 3 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of outage events not caused by contact with vegetation | HWW & RFW | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of outage events not caused by contact with vegetation | None | N/A | HFTD Tier 2 | N/A | N/A | N/A | 56 | 61 | 49 | 43 | 66 | 47 | 87 | 71 | 57 | 49 | 54 | 49 | 66 | 51 | 51 | 50 | [11 empty] | Number of events
|  |  | Number of outage events not caused by contact with vegetation | RFW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 | 0 | 9 | 5 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of outage events not caused by contact with vegetation | HWW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | 4 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 3 | 0 | 9 | 0 | 1 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of outage events not caused by contact with vegetation | HWW & RFW | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of outage events not caused by contact with vegetation | None | N/A | HFTD Tier 3 | N/A | N/A | N/A | 27 | 50 | 57 | 39 | 51 | 42 | 68 | 56 | 35 | 33 | 37 | 29 | 47 | 22 | 43 | 29 | [11 empty] | Number of events
|  |  | Number of outage events not caused by contact with vegetation | RFW only | N/A | Non- HFTD | N/A | N/A | N/A | 0 | 0 | 26 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of outage events not caused by contact with vegetation | HWW only | N/A | Non- HFTD | N/A | N/A | N/A | 2 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 4 | 2 | 29 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of outage events not caused by contact with vegetation | HWW & RFW | N/A | Non- HFTD | N/A | N/A | N/A | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of outage events not caused by contact with vegetation | None | N/A | Non- HFTD | N/A | N/A | N/A | 127 | 139 | 173 | 140 | 143 | 183 | 181 | 187 | 156 | 152 | 136 | 149 | 171 | 150 | 131 | 112 | [11 empty] | Number of events
| 1. Risk Events | 1.d. | Number of outage events caused by contact with vegetation | RFW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of outage events caused by contact with vegetation | HWW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of outage events caused by contact with vegetation | HWW & RFW | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of outage events caused by contact with vegetation | None | N/A | HFTD Tier 2 | N/A | N/A | N/A | 2 | 1 | 0 | 1 | 2 | 1 | 1 | 0 | 0 | 1 | 2 | 2 | 6 | 0 | 3 | 0 | [11 empty] | Number of events
|  |  | Number of outage events caused by contact with vegetation | RFW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of outage events caused by contact with vegetation | HWW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of outage events caused by contact with vegetation | HWW & RFW | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of outage events caused by contact with vegetation | None | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 1 | 1 | 1 | 1 | 3 | 5 | 0 | 1 | 0 | [11 empty] | Number of events
|  |  | Number of outage events caused by contact with vegetation | RFW only | N/A | Non- HFTD | N/A | N/A | N/A | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of outage events caused by contact with vegetation | HWW only | N/A | Non- HFTD | N/A | N/A | N/A | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of outage events caused by contact with vegetation | HWW & RFW | N/A | Non- HFTD | N/A | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | Number of events
|  |  | Number of outage events caused by contact with vegetation | None | N/A | Non- HFTD | N/A | N/A | N/A | 8 | 6 | 3 | 7 | 7 | 3 | 5 | 10 | 5 | 1 | 7 | 3 | 23 | 3 | 10 | 5 | [11 empty] | Number of events
| 1. Risk Events | 1.e. | Number of outage events on circuits with adjusted settings for protective devices enabled. | RFW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 | 0 | 13 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 4.6667 | 4.6667 | 4.6667 | Number of events
|  |  | Number of outage events on circuits with adjusted settings for protective devices enabled. | HWW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 1 | 1 | 1 | Number of events
|  |  | Number of outage events on circuits with adjusted settings for protective devices enabled. | HWW & RFW | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0.66667 | 0.66667 | 0.66667 | Number of events
|  |  | Number of outage events on circuits with adjusted settings for protective devices enabled. | All (regardless of RFW/HWW status) | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 | 0 | 13 | 2 | 3 | 0 | 0 | 2 | 0 | 0 | 5 | 2 | 0 | 0 | 0 | 0 | [8 empty] | 2.6667 | 2.6667 | 2.6667 | Number of events
|  |  | Number of outage events on circuits with adjusted settings for protective devices enabled. | RFW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 5 | 5 | 5 | Number of events
|  |  | Number of outage events on circuits with adjusted settings for protective devices enabled. | HWW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 2 | 2 | 2 | Number of events
|  |  | Number of outage events on circuits with adjusted settings for protective devices enabled. | HWW & RFW | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0.33333 | 0.33333 | 0.33333 | Number of events
|  |  | Number of outage events on circuits with adjusted settings for protective devices enabled. | All (regardless of RFW/HWW status) | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 | 0 | 15 | 1 | 6 | 0 | 0 | 1 | 0 | 0 | 2 | 3 | 0 | 0 | 0 | 4 | [8 empty] | 2 | 2 | 2 | Number of events
|  |  | Number of outage events on circuits with adjusted settings for protective devices enabled. | RFW only | N/A | Non- HFTD | N/A | N/A | N/A | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0.66667 | 0.66667 | 0.66667 | Number of events
|  |  | Number of outage events on circuits with adjusted settings for protective devices enabled. | HWW only | N/A | Non- HFTD | N/A | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | Number of events
|  |  | Number of outage events on circuits with adjusted settings for protective devices enabled. | HWW & RFW | N/A | Non- HFTD | N/A | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0.33333 | 0.33333 | 0.33333 | Number of events
|  |  | Number of outage events on circuits with adjusted settings for protective devices enabled. | All (regardless of RFW/HWW status) | N/A | Non- HFTD | N/A | N/A | N/A | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | [8 empty] | 0.66667 | 0.66667 | 0.66667 | Number of events
| 2. Time between vegetation inspection finding and resulting trimming activity | 2.d.2.a. | Median time | N/A |  | HFTD Tier 2 | Distribution | N/A | N/A | 120 | 92 | 96 | 106 | 76 | 56 | 75 | 98 | 81 | 60 | 76 | 79 | 78 | 71 | 90 | 75 | [11 empty] | hours
| 2. Time between vegetation inspection finding and resulting trimming activity | 2.d.2.b. | 95 percentile time | N/A |  | HFTD Tier 2 | Distribution | N/A | N/A | 162 | 128 | 137 | 141 | 114 | 102 | 114 | 141 | 117 | 93 | 127 | 108 | 109 | 119 | 131 | 135 | [11 empty] | hours
| 2. Time between vegetation inspection finding and resulting trimming activity | 2.d.3.a. | Median time | N/A |  | HFTD Tier 3 | Distribution | N/A | N/A | 118 | 98 | 92 | 112 | 83 | 73 | 85 | 85 | 101 | 69 | 67 | 73 | 78 | 58 | 77 | 91 | [11 empty] | hours
| 2. Time between vegetation inspection finding and resulting trimming activity | 2.d.3.b. | 95 percentile time | N/A |  | HFTD Tier 3 | Distribution | N/A | N/A | 160 | 134 | 171.45 | 144 | 124.1 | 112.45 | 126.35 | 151 | 124 | 100 | 120 | 103 | 112 | 96 | 132 | 102 | [11 empty] | hours
| 2. Time between vegetation inspection finding and resulting trimming activity | 2.d.4.a. | Median time | N/A |  | Non- HFTD | Distribution | N/A | N/A | 124 | 83 | 87 | 110 | 83 | 74 | 89 | 105 | 85 | 70 | 70 | 77 | 77 | 77 | 62 | 87 | [11 empty] | hours
| 2. Time between vegetation inspection finding and resulting trimming activity | 2.d.4.b. | 95 percentile time | N/A |  | Non- HFTD | Distribution | N/A | N/A | 161 | 115 | 147 | 154 | 129 | 106 | 131 | 142 | 136 | 100 | 112 | 116 | 115 | 118 | 109 | 116 | [11 empty] | hours
| 2. Time between vegetation inspection finding and resulting trimming activity | 2.t.2.a. | Median time | N/A |  | HFTD Tier 2 | Transmission | N/A | N/A | 111 | 85 | 92 | 92 | 105 | 74 | 75 | 103 | 71 | 69.5 | 70 | 85 | 85 | 67 | 70 | 95 | [11 empty] | hours
| 2. Time between vegetation inspection finding and resulting trimming activity | 2.t.2.b. | 95 percentile time | N/A |  | HFTD Tier 2 | Transmission | N/A | N/A | 172 | 317 | 263.4 | 127 | 118 | 97 | 138 | 141 | 112 | 88 | 275 | 116 | 107 | 347 | 103 | 135 | [11 empty] | hours
| 2. Time between vegetation inspection finding and resulting trimming activity | 2.t.3.a. | Median time | N/A |  | HFTD Tier 3 | Transmission | N/A | N/A | 96 | 122 | 91 | 102.5 | 86 | 77 | 81 | 63.5 | 102 | 43 | 68 | 83 | 81 | 50 | 84 | 101 | [11 empty] | hours
| 2. Time between vegetation inspection finding and resulting trimming activity | 2.t.3.b. | 95 percentile time | N/A |  | HFTD Tier 3 | Transmission | N/A | N/A | 113.25 | 123.3 | 363 | 103.85 | 86 | 100.2 | 139 | 163 | 102 | 82 | 114 | 90 | 118 | 80 | 218 | 120 | [11 empty] | hours
| 2. Time between vegetation inspection finding and resulting trimming activity | 2.t.4.a. | Median time | N/A |  | Non- HFTD | Transmission | N/A | N/A | 114 | 82 | 89 | 98 | 79 | 70 | 93 | 102 | 82 | 71 | 90 | 88 | 94 | 57 | 77 | 95 | [11 empty] | hours
| 2. Time between vegetation inspection finding and resulting trimming activity | 2.t.4.b. | 95 percentile time | N/A |  | Non- HFTD | Transmission | N/A | N/A | 176 | 123 | 121 | 154 | 113 | 118 | 135 | 136 | 150 | 99 | 112 | 126 | 127 | 96 | 119 | 125 | [11 empty] | hours
| 3. Time between level 1 asset inspection finding and resulting maintenance activity | 3.d.2.a. | Median time | N/A | N/A | HFTD Tier 2 | Distribution | N/A | N/A | 2 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 3 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | [11 empty] | hours | Source data contains incorrect date values,negative median is corrected using medians from other quarters.
| 3. Time between level 1 asset inspection finding and resulting maintenance activity | 3.d.2.b. | 95 percentile time | N/A | N/A | HFTD Tier 2 | Distribution | N/A | N/A | 2 | 2 | 0 | 0 | 2 | 1 | 1 | 65 | 22 | 28 | 138 | 156 | 0 | 3 | 1 | 0 | [11 empty] | hours
| 3. Time between level 1 asset inspection finding and resulting maintenance activity | 3.d.3.a. | Median time | N/A | N/A | HFTD Tier 3 | Distribution | N/A | N/A | 2 | 1 | 0 | 0 | 3 | 0 | 0 | 9 | 3 | 3 | 1 | 0 | 3 | 1 | 1 | 1 | [11 empty] | hours
| 3. Time between level 1 asset inspection finding and resulting maintenance activity | 3.d.3.b. | 95 percentile time | N/A | N/A | HFTD Tier 3 | Distribution | N/A | N/A | 3 | 1 | 0 | 0 | 3 | 2 | 0 | 12 | 3 | 3 | 1 | 0 | 3 | 3 | 3 | 1 | [11 empty] | hours
| 3. Time between level 1 asset inspection finding and resulting maintenance activity | 3.d.4.a. | Median time | N/A | N/A | Non- HFTD | Distribution | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 2 | 1 | [11 empty] | hours
| 3. Time between level 1 asset inspection finding and resulting maintenance activity | 3.d.4.b. | 95 percentile time | N/A | N/A | Non- HFTD | Distribution | N/A | N/A | 1 | 2 | 1 | 0 | 3 | 3 | 1 | 1 | 2 | 1 | 3 | 51 | 3 | 2 | 3 | 1 | [11 empty] | hours
| 3. Time between level 1 asset inspection finding and resulting maintenance activity | 3.t.2.a. | Median time | N/A | N/A | HFTD Tier 2 | Transmission | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | hours
| 3. Time between level 1 asset inspection finding and resulting maintenance activity | 3.t.2.b. | 95 percentile time | N/A | N/A | HFTD Tier 2 | Transmission | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | hours
| 3. Time between level 1 asset inspection finding and resulting maintenance activity | 3.t.3.a. | Median time | N/A | N/A | HFTD Tier 3 | Transmission | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | hours
| 3. Time between level 1 asset inspection finding and resulting maintenance activity | 3.t.3.b. | 95 percentile time | N/A | N/A | HFTD Tier 3 | Transmission | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | hours
| 3. Time between level 1 asset inspection finding and resulting maintenance activity | 3.t.4.a. | Median time | N/A | N/A | Non- HFTD | Transmission | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | hours
| 3. Time between level 1 asset inspection finding and resulting maintenance activity | 3.t.4.b. | 95 percentile time | N/A | N/A | Non- HFTD | Transmission | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | hours
| 4. Time between level 2 asset inspection finding and resulting maintenance activity | 4.d.2.a. | Median time | N/A | N/A | HFTD Tier 2 | Distribution | N/A | N/A | 271 | 116 | 176 | 240 | 243 | 44 | 47 | 47 | 192 | 223 | 240 | 243 | 306 | 314 | 206 | 180 | [11 empty] | hours
| 4. Time between level 2 asset inspection finding and resulting maintenance activity | 4.d.2.b. | 95 percentile time | N/A | N/A | HFTD Tier 2 | Distribution | N/A | N/A | 340 | 378 | 245 | 307 | 337 | 296 | 222 | 273 | 317 | 314 | 377 | 466 | 344 | 376 | 360 | 264 | [11 empty] | hours
| 4. Time between level 2 asset inspection finding and resulting maintenance activity | 4.d.3.a. | Median time | N/A | N/A | HFTD Tier 3 | Distribution | N/A | N/A | 32 | 109 | 121 | 144 | 26 | 92 | 157 | 184 | 50 | 119 | 168 | 238 | 33 | 27 | 76 | 141 | [11 empty] | hours
| 4. Time between level 2 asset inspection finding and resulting maintenance activity | 4.d.3.b. | 95 percentile time | N/A | N/A | HFTD Tier 3 | Distribution | N/A | N/A | 68 | 163 | 181 | 188 | 139 | 154 | 205 | 225 | 167 | 270 | 328 | 358 | 164 | 127 | 189 | 205 | [11 empty] | hours
| 4. Time between level 2 asset inspection finding and resulting maintenance activity | 4.d.4.a. | Median time | N/A | N/A | Non- HFTD | Distribution | N/A | N/A | 258 | 256 | 158 | 205 | 306 | 288 | 190 | 195 | 280 | 289 | 175 | 245 | 287 | 264 | 220 | 243 | [11 empty] | hours
| 4. Time between level 2 asset inspection finding and resulting maintenance activity | 4.d.4.b. | 95 percentile time | N/A | N/A | Non- HFTD | Distribution | N/A | N/A | 368 | 402 | 437 | 330 | 364 | 379 | 367 | 337 | 362 | 408 | 448 | 364 | 362 | 357 | 369 | 376 | [11 empty] | hours
| 4. Time between level 2 asset inspection finding and resulting maintenance activity | 4.t.2.a. | Median time | N/A | N/A | HFTD Tier 2 | Transmission | N/A | N/A | 142 | 266 | 237 | 198 | 213 | 138 | 257 | 163 | 133 | 0 | 5 | 0 | 353 | 238 | 147 | 163 | [11 empty] | hours
| 4. Time between level 2 asset inspection finding and resulting maintenance activity | 4.t.2.b. | 95 percentile time | N/A | N/A | HFTD Tier 2 | Transmission | N/A | N/A | 367.15 | 683.3 | 645 | 379 | 360 | 352 | 437 | 364.5 | 319 | 129.3 | 17.1 | 44.1 | 415 | 605 | 339 | 389.05 | [11 empty] | hours
| 4. Time between level 2 asset inspection finding and resulting maintenance activity | 4.t.3.a. | Median time | N/A | N/A | HFTD Tier 3 | Transmission | N/A | N/A | 0 | 102 | 130 | 357 | 179 | 32 | 0 | 0 | 51 | 8.5 | 0 | 0 | 160 | 344 | 345 | 347 | [11 empty] | hours
| 4. Time between level 2 asset inspection finding and resulting maintenance activity | 4.t.3.b. | 95 percentile time | N/A | N/A | HFTD Tier 3 | Transmission | N/A | N/A | 0 | 182.95 | 188 | 493 | 433 | 32 | 0 | 0 | 75 | 34 | 5.4 | 33.15 | 274 | 358 | 365 | 520.7 | [11 empty] | hours
| 4. Time between level 2 asset inspection finding and resulting maintenance activity | 4.t.4.a. | Median time | N/A | N/A | Non- HFTD | Transmission | N/A | N/A | 183 | 256 | 252 | 114 | 165 | 144 | 139 | 178 | 56 | 12 | 0 | 0 | 350 | 439 | 148 | 204 | [11 empty] | hours
| 4. Time between level 2 asset inspection finding and resulting maintenance activity | 4.t.4.b. | 95 percentile time | N/A | N/A | Non- HFTD | Transmission | N/A | N/A | 592.4 | 703 | 475 | 434 | 360 | 360 | 380.2 | 364 | 311.5 | 117.8 | 18.55 | 0 | 412 | 563 | 350.65 | 335.75 | [11 empty] | hours
| 5. Time between level 3 asset inspection finding and resulting maintenance activity | 5.d.2.a. | Median time | N/A | N/A | HFTD Tier 2 | Distribution | N/A | N/A | [27 empty] | hours |  | N/A
| 5. Time between level 3 asset inspection finding and resulting maintenance activity | 5.d.2.b. | 95 percentile time | N/A | N/A | HFTD Tier 2 | Distribution | N/A | N/A | [27 empty] | hours |  | N/A
| 5. Time between level 3 asset inspection finding and resulting maintenance activity | 5.d.3.a. | Median time | N/A | N/A | HFTD Tier 3 | Distribution | N/A | N/A | [27 empty] | hours |  | N/A
| 5. Time between level 3 asset inspection finding and resulting maintenance activity | 5.d.3.b. | 95 percentile time | N/A | N/A | HFTD Tier 3 | Distribution | N/A | N/A | [27 empty] | hours |  | N/A
| 5. Time between level 3 asset inspection finding and resulting maintenance activity | 5.d.4.a. | Median time | N/A | N/A | Non- HFTD | Distribution | N/A | N/A | [27 empty] | hours |  | N/A
| 5. Time between level 3 asset inspection finding and resulting maintenance activity | 5.d.4.b. | 95 percentile time | N/A | N/A | Non- HFTD | Distribution | N/A | N/A | [27 empty] | hours |  | N/A
| 5. Time between level 3 asset inspection finding and resulting maintenance activity | 5.t.2.a. | Median time | N/A | N/A | HFTD Tier 2 | Transmission | N/A | N/A | 273 | 127 | 26 | 248.5 | 110 | 231 | 8 | 37.5 | 267 | 25 | 0 | 0 | 221 | 0 | 73 | 84 | [11 empty] | hours
| 5. Time between level 3 asset inspection finding and resulting maintenance activity | 5.t.2.b. | 95 percentile time | N/A | N/A | HFTD Tier 2 | Transmission | N/A | N/A | 319 | 285.4 | 50.3 | 277.75 | 110 | 330.5 | 8 | 230 | 267 | 25 | 0 | 0 | 359 | 0 | 73 | 129 | [11 empty] | hours
| 5. Time between level 3 asset inspection finding and resulting maintenance activity | 5.t.3.a. | Median time | N/A | N/A | HFTD Tier 3 | Transmission | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | hours
| 5. Time between level 3 asset inspection finding and resulting maintenance activity | 5.t.3.b. | 95 percentile time | N/A | N/A | HFTD Tier 3 | Transmission | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | hours
| 5. Time between level 3 asset inspection finding and resulting maintenance activity | 5.t.4.a. | Median time | N/A | N/A | Non- HFTD | Transmission | N/A | N/A | 318 | 141 | 237 | 21 | 227 | 50 | 39 | 39 | 125 | 89 | 7.5 | 0 | 381 | 0 | 0 | 94 | [11 empty] | hours
| 5. Time between level 3 asset inspection finding and resulting maintenance activity | 5.t.4.b. | 95 percentile time | N/A | N/A | Non- HFTD | Transmission | N/A | N/A | 414 | 223.2 | 332.5 | 21 | 258.5 | 77 | 71 | 111.2 | 125 | 89.75 | 14.25 | 0 | 584 | 0 | 0 | 94 | [11 empty] | hours
| 6. Vegetation management work orders | 6.a. | Number of vegetation management open work orders (total) | N/A | N/A | N/A | N/A | N/A | N/A | 21231 | 17750 | 21796 | 21516 | 10843 | 13555 | 16745 | 13074 | 18103 | 19411 | 15446 | 14295 | 27211 | 26956 | 22498 | 23840 | [8 empty] | 16295 | 16295 | 16295 | Number of orders | Unit(s)= number of trees in HFTD. Open work orders by quarters are NOT accumulative. 2023Q2 was corrected during 2023Q3
| 6. Vegetation management work orders | 6.b. | Number of vegetation management past due work orders (total) | N/A | N/A | N/A | N/A | N/A | N/A | 57 | 1353 | 420 | 1616 | 53 | 49 | 109 | 573 | 1970 | 390 | 395 | 1359 | 1001 | 557 | 570 | 878 | [8 empty] | 1063.3333 | 1063.3333 | 1063.3333 | Number of orders | Unit(s)= number of trees in HFTD
| 7. Asset management work orders | 7.a. | Number of asset management open work orders (total) | N/A | N/A | N/A | N/A | N/A | N/A | 4665 | 5820 | 4671 | 3047 | 1655 | 1291 | 3666 | 6702 | 8741 | 9650 | 10007 | 8822 | 8034 | 6919 | 9399 | 7873 | [8 empty] | 5163 | 5163 | 5163 | Number of orders | Unit(s)= notifications. Open work orders by quarters are NOT accumulative. 2023Q2 was corrected during 2023Q3 submission based on the latest.
| 7. Asset management work orders | 7.b. | Number of asset management past due work orders (total) | N/A | N/A | N/A | N/A | N/A | N/A | 8 | 8 | 4 | 3 | 1 | 2 | 7 | 5 | 10 | 9 | 2 | 0 | 11 | 12 | 20 | 22 | [8 empty] | 6.6667 | 6.6667 | 6.6667 | Number of orders | Unit(s)= notifications. Past due work orders by quarters are NOT accumulative
| 8. Response Time | 8.a. | Response time to locked open circuit breaker | N/A | N/A | N/A | N/A | N/A | N/A | 2.14 | 1.23 | 0.55 | 1.22 | 0.98 | 0.83 | 1.91 | 1.19 | 0.79 | 0.81 | 0.63 | 0.71 | 1.34 | 2.58 | 1.0042 | 1.1589 | [11 empty] | Hours | Only outages with valid ETS response time are considered for this calculation. PSPS and de energized for safetey are excluded.
| 9. Fatalities and injuries due to utility-related ignitions | 9.a. | Fatalities due to utility-related ignitions (total) | N/A | N/A | N/A | N/A | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | Number of fatalities
|  | 9.b. | Injuries due to utility-related ignitions (total) | N/A | N/A | N/A | N/A | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | Number of injuries
| 10. Value of assets destroyed by utility-related ignitions, listed by asset type | 10.a. | Value of assets destroyed by utility-related ignitions (total) | N/A | N/A | N/A | N/A | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 1000
| 11. Structures damaged or destroyed by utility-related ignitions | 11.a. | Number of structures destroyed by utility-related ignitions (total) | N/A | N/A | N/A | N/A | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | Number of structures
|  | 11.b. | Critical infrastructure damaged/destroyed by utility-related ignitions (total) | N/A | N/A | N/A | N/A | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | Number of structures
| 12. Acreage burned by utility-ignited wildfires | 12.a. | Acreage burned by utility-ignited wildfires | N/A | N/A | N/A | N/A | N/A | N/A | 0.249 | 0.2591 | 7.6931 | 4.366 | 0.0121 | 0.3481 | 1.0087 | 0.6471 | 0.0095 | 0.8178 | 1.9931 | 1.0022 | 0 | 0.05 | 20.61 | 0.08608 | [11 empty] | Acres
| 13. Number of utility-related ignitions | 13.a. | Number of ignitions | RFW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0.33333 | 0.33333 | 0.33333 | Number of ignitions
| 13. Number of utility-related ignitions |  | Number of ignitions | HWW only | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0.33333 | 0.33333 | 0.33333 | Number of ignitions
| 13. Number of utility-related ignitions |  | Number of ignitions | HWW & RFW | N/A | HFTD Tier 2 | N/A | N/A | N/A | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0.33333 | 0.33333 | 0.33333 | Number of ignitions
| 13. Number of utility-related ignitions |  | Number of ignitions | None | N/A | HFTD Tier 2 | N/A | N/A | N/A | 1 | 2 | 4 | 2 | 1 | 2 | 3 | 2 | 1 | 2 | 2 | 1 | 0 | 2 | 2 | 0 | [8 empty] | 7.6667 | 7.6667 | 7.6667 | Number of ignitions
| 13. Number of utility-related ignitions |  | Number of ignitions | RFW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | Number of ignitions
| 13. Number of utility-related ignitions |  | Number of ignitions | HWW only | N/A | HFTD Tier 3 | N/A | N/A | N/A | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0.33333 | 0.33333 | 0.33333 | Number of ignitions
| 13. Number of utility-related ignitions |  | Number of ignitions | HWW & RFW | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | Number of ignitions
| 13. Number of utility-related ignitions |  | Number of ignitions | None | N/A | HFTD Tier 3 | N/A | N/A | N/A | 0 | 2 | 7 | 2 | 0 | 3 | 3 | 2 | 0 | 3 | 2 | 1 | 0 | 1 | 4 | 2 | [8 empty] | 8.3333 | 8.3333 | 8.3333 | Number of ignitions
| 13. Number of utility-related ignitions |  | Number of ignitions | RFW only | N/A | Non- HFTD | N/A | N/A | N/A | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0.33333 | 0.33333 | 0.33333 | Number of ignitions
| 13. Number of utility-related ignitions |  | Number of ignitions | HWW only | N/A | Non- HFTD | N/A | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | Number of ignitions
| 13. Number of utility-related ignitions |  | Number of ignitions | HWW & RFW | N/A | Non- HFTD | N/A | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | Number of ignitions
| 13. Number of utility-related ignitions |  | Number of ignitions | None | N/A | Non- HFTD | N/A | N/A | N/A | 1 | 1 | 3 | 0 | 1 | 4 | 3 | 0 | 1 | 2 | 5 | 0 | 0 | 2 | 1 | 2 | [8 empty] | 7 | 7 | 7 | Number of ignitions
x | 14. Grid condition findings from inspection | 14.d.2.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Aerial | 0 | 0 | 0 | 0 | 4135 | 919 | 2094 | 0 | 2413 | 0 | 0 | 0 | 1258 | 2495 | 1822 | 0 | [11 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.d.2.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | other | 3275 | 4479 | 926 | 275 | 11638 | 15055 | 12878 | 447 | 17452 | 14583 | 12291 | 325 | 10863 | 16275 | 11539 | 2446 | [11 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.d.2.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Aerial | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | other | 4770 | 2714 | 1155 | 472 | 7439 | 3926 | 1368 | 19 | 4214 | 4762 | 2438 | 443 | 2689 | 3068 | 1342 | 657 | [11 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.d.2.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Drone | 0 | 0 | 0 | 0 | 0 | 0 | 4573 | 8448 | 7283 | 3641 | 4878 | 284 | 90 | 4030 | 4262 | 0 | [11 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.d.2.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Aerial | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | other | 1 | 0 | 86 | 281 | 1964 | 1536 | 1104 | 488 | 1907 | 2300 | 808 | 353 | 894 | 3249 | 1406 | 995 | [11 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.d.2.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Aerial | 0 | 0 | 0 | 0 | 172.02 | 38.6 | 72 | 0 | 98.9 | 0 | 0 | 0 | 59 | 107.0636 | 69.64 | 0 | [11 empty] | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.d.2.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | other | 120 | 138.67 | 33.39 | 13.43 | 465.59 | 517.5 | 477.72 | 18.66 | 690.05 | 495.77 | 472.49 | 12.69 | 439 | 572.4789 | 428.77 | 90.94 | [11 empty] | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.d.2.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Aerial | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | other | 177.66 | 103.77 | 45.32 | 17.97 | 232.56 | 141.35 | 52.78 | 0.82 | 152.58 | 155.7 | 87.02 | 17.87 | 100 | 137.3852 | 60.28 | 30.89 | [11 empty] | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.d.2.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Drone | 0 | 0 | 0 | 0 | 0 | 0 | 279.11 | 520.81 | 423.51 | 204.45 | 299.83 | 116.38 | 4 | 186.2041 | 168.08 | 0 | [11 empty] | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.d.2.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Aerial | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | other | 0 | 0 | 0 | 6.03 | 55.85 | 40.94 | 30.58 | 11.5 | 79.6 | 91.68 | 23.22 | 8.63 | 3 | 146.7774 | 69.26 | 48.43 | [11 empty] | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.d.2.c.i | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.c.i | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.2.c.i | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.c.i | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | other | 10 | 3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.2.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | other | 4 | 6 | 3 | 0 | 2 | 1 | 1 | 0 | 2 | 3 | 1 | 0 | 0 | 4 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.2.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Drone | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 47 | 47 | 22 | 32 | 3 | 2 | 21 | 4 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.2.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | other | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.2.d.i | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.d.i | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.2.d.i | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.d.i | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | other | 17 | 10 | 3 | 2 | 38 | 82 | 37 | 3 | 26 | 48 | 26 | 0 | 78 | 136 | 13 | 2 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.2.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | other | 228 | 153 | 50 | 7 | 189 | 97 | 6 | 1 | 90 | 208 | 80 | 14 | 25 | 117 | 25 | 16 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.2.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Drone | 0 | 2 | 3 | 0 | 0 | 0 | 2778 | 3797 | 2730 | 1582 | 1854 | 245 | 22 | 1120 | 1270 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.2.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | other | 0 | 0 | 0 | 2 | 33 | 30 | 10 | 8 | 7 | 9 | 1 | 4 | 1 | 0 | 0 | 5 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.2.e.i | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.e.i | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.e.i | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.e.i | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | other | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | other | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.2.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | other | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Aerial | 0 | 0 | 0 | 0 | 607 | 814 | 420 | 0 | 555 | 54 | 33 | 0 | 689 | 801 | 1638 | 0 | [11 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.d.3.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | other | 1875 | 4082 | 979 | 20 | 13537 | 15352 | 8120 | 369 | 16643 | 11540 | 10442 | 35 | 12316 | 16289 | 7086 | 447 | [11 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.d.3.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Aerial | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | other | 15308 | 4269 | 1091 | 4 | 17460 | 3486 | 2229 | 1714 | 17765 | 1873 | 220 | 18 | 1680 | 1006 | 821 | 525 | [11 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.d.3.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Drone | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 328 | 48 | 16 | 0 | 471 | 562 | 2050 | 2840 | 0 | [11 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.d.3.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Aerial | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | other | 1 | 0 | 2800 | 3841 | 2991 | 741 | 52 | 113 | 2018 | 715 | 641 | 2249 | 2366 | 1289 | 1795 | 963 | [11 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.d.3.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Aerial | 0 | 0 | 0 | 0 | 27.71 | 39.75 | 14.75 | 0 | 30.6 | 3.1 | 1.86 | 0 | 33 | 38.5784 | 63.53 | 0 | [11 empty] | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.d.3.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | other | 64.92 | 179.62 | 38.16 | 1.3 | 548.08 | 630.78 | 322.38 | 11.2 | 662.24 | 486.32 | 415.99 | 1.83 | 507 | 665.6617 | 279.27 | 15.81 | [11 empty] | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.d.3.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Aerial | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | other | 607.4 | 178.86 | 42.28 | 0.13 | 619.97 | 145.71 | 86.29 | 61.33 | 653.69 | 78.55 | 8.34 | 0.85 | 68 | 42.5932 | 33.8 | 17.78 | [11 empty] | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.d.3.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Drone | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.23 | 3.46 | 0.74 | 0 | 23.04 | 23 | 93.6256 | 136.93 | 0 | [11 empty] | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.d.3.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Aerial | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | other | 0 | 0 | 98.42 | 101.2 | 107.55 | 26.25 | 0.68 | 3.89 | 103.6 | 29.13 | 28.69 | 94.09 | 125 | 56.3074 | 97.58 | 43.84 | [11 empty] | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.d.3.c.i | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.c.i | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.3.c.i | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.c.i | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | other | 0 | 0 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.3.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | other | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 5 | 0 | 0 | 4 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.3.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Drone | 27 | 32 | 11 | 2 | 0 | 0 | 1 | 10 | 0 | 0 | 1 | 1 | 3 | 8 | 3 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.3.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | other | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.3.d.i | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.d.i | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.3.d.i | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.d.i | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | other | 2 | 19 | 1 | 0 | 25 | 30 | 13 | 0 | 20 | 14 | 4 | 0 | 21 | 11 | 1 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.3.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | other | 324 | 96 | 17 | 0 | 273 | 72 | 12 | 23 | 123 | 25 | 11 | 1 | 16 | 9 | 2 | 29 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.3.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Drone | 3308 | 2201 | 803 | 152 | 0 | 2 | 4 | 133 | 16 | 11 | 3 | 93 | 134 | 533 | 885 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.3.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | other | 0 | 0 | 17 | 42 | 21 | 2 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 1 | 2 | 2 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.3.e.i | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.e.i | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.e.i | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.e.i | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | other | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | other | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.3.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | other | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.a.i | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.a.i | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Aerial | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 1 | 4 | 0 | 0 | [11 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.d.4.a.i | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.a.i | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | other | 28120 | 27542 | 24343 | 16661 | 43821 | 43511 | 40872 | 9114 | 43334 | 41600 | 46951 | 5104 | 36445 | 45150 | 49397 | 5362 | [11 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.d.4.a.ii | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.a.ii | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Aerial | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.a.ii | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.a.ii | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | other | 8079 | 10928 | 10231 | 3476 | 7184 | 7402 | 8264 | 2817 | 7209 | 6005 | 9553 | 1572 | 6747 | 11211 | 12358 | 3815 | [11 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.d.4.a.iii | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Drone | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 4 | 24 | 699 | 1536 | 3 | 897 | 612 | 0 | [11 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.d.4.a.iii | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Aerial | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.a.iii | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Other Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.a.iii | Number of assets inspected | N/A | N/A | Non-HFTD | Distribution | Other Inspection | other | 0 | 1 | 1233 | 1266 | 2483 | 5919 | 6165 | 7041 | 9375 | 10001 | 6259 | 3193 | 7670 | 4201 | 3481 | 3820 | [11 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.d.4.b.i | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.b.i | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014962 | 0 | 0 | [11 empty] | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.d.4.b.i | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.b.i | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | other | 539.91 | 541.62 | 525.01 | 297.48 | 879.96 | 938.6 | 838.37 | 164.66 | 854.11 | 907.3 | 950.04 | 112.57 | 749 | 948.0748 | 999.42 | 122.75 | [11 empty] | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.d.4.b.ii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.b.ii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Aerial | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.b.ii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.b.ii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | other | 131.34 | 187.9 | 164.89 | 74.54 | 111.01 | 119.19 | 144.1 | 47.53 | 168.43 | 118.84 | 203.22 | 28.78 | 127 | 209.2829 | 237.06 | 82.09 | [11 empty] | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.d.4.b.iii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Drone | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.9193 | 19.59 | 0 | [11 empty] | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.d.4.b.iii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Aerial | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.b.iii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Other Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.b.iii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Distribution | Other Inspection | other | 0 | 0 | 0.05 | 0.66 | 13.38 | 69.67 | 68.61 | 102.54 | 88.88 | 127.48 | 64.67 | 22.4 | 101 | 56.6163 | 30.65 | 55.06 | [11 empty] | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.d.4.c.i | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.c.i | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.4.c.i | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.c.i | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | other | 6 | 12 | 3 | 3 | 7 | 4 | 4 | 1 | 5 | 6 | 8 | 0 | 6 | 3 | 3 | 1 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.4.c.ii | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.c.ii | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.c.ii | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.c.ii | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | other | 14 | 12 | 14 | 2 | 13 | 10 | 4 | 1 | 5 | 4 | 11 | 2 | 2 | 16 | 5 | 7 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.4.c.iii | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Drone | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 25 | 0 | 4 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.4.c.iii | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.c.iii | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.c.iii | Level 1 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | other | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 5 | 1 | 3 | 1 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.4.d.i | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.d.i | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.4.d.i | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.d.i | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | other | 249 | 224 | 145 | 104 | 195 | 146 | 176 | 24 | 141 | 131 | 132 | 19 | 178 | 199 | 197 | 35 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.4.d.ii | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.d.ii | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.d.ii | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.d.ii | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | other | 383 | 383 | 279 | 80 | 380 | 404 | 270 | 54 | 295 | 215 | 270 | 41 | 320 | 364 | 398 | 162 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.4.d.iii | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Drone | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 174 | 409 | 0 | 256 | 186 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.4.d.iii | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.d.iii | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.d.iii | Level 2 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | other | 0 | 0 | 0 | 0 | 4 | 49 | 48 | 66 | 63 | 123 | 48 | 23 | 68 | 32 | 27 | 42 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.d.4.e.i | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.e.i | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.e.i | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.e.i | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | other | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.e.ii | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.e.ii | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.e.ii | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.e.ii | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | other | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.e.iii | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.e.iii | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Aerial | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.e.iii | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.d.4.e.iii | Level 3 findings | N/A | N/A | Non-HFTD | Distribution | Other Inspection | other | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Aerial | 3278 | 735 | 104 | 0 | 2366 | 1727 | 104 | 0 | 937 | 3297 | 104 | 0 | 1808 | 2346 | 102 | 0 | [11 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.2.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.2.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Aerial | 0 | 0 | 0 | 12 | 21 | 4 | 7 | 1 | 8 | 1 | 3 | 2 | 0 | 0 | 15 | 13 | [11 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.2.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | other | 159 | 471 | 171 | 384 | 387 | 530 | 464 | 175 | 185 | 228 | 484 | 507 | 138 | 482 | 145 | 178 | [11 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.2.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Drone | Actuals Q1: 73; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 607; Actuals Q1: 164; Actuals Q2: 19; Actuals Q3: 96; Actuals Q4: 14; Actuals Q1: 445; Actuals Q2: 61; Actuals Q3: 133; Actuals Q4: 124 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | No data for transmission drone inspection in 2023 as it's not performed | N/A
| 14. Grid condition findings from inspection | 14.t.2.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Aerial | 0 | 0 | 1983 | 2050 | 0 | 0 | 3663 | 518 | 0 | 0 | 3163 | 1106 | 0 | 0 | 4125 | 0 | [11 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.2.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | other | Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 1; Actuals Q2: 37; Actuals Q3: 0; Actuals 4: 43 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.2.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Aerial | 496.22 | 100.64 | 31.4 | 0 | 354.53 | 250.75 | 31.4 | 0 | 161.79 | 452 | 31.4 | 0 | 240 | 263.9823 | 24.06 | 0 | [11 empty] | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.t.2.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | other | Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals 4: 0 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.t.2.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Aerial | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | other | 28.59 | 109 | 20.6 | 91.22 | 53.91 | 76.82 | 143.23 | 28.31 | 47.8 | 67.87 | 57.16 | 68.58 | 0 | 5.4455 | 7.95 | 0 | [11 empty] | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.t.2.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Drone | Actuals Q1: 16.9356; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 70.8845; Actuals Q1: 46.5395; Actuals Q2: 5.6368; Actuals Q3: 6.3938; Actuals Q4: 1.7465; Actuals Q1: 47.8791; Actuals Q2: 8.1044; Actuals Q3: 16.9181; Actuals Q4: 15.6145 |  |  |  | # of circuit miles inspected by the utility | No data for transmission drone inspection in 2023 as it's not performed | N/A
| 14. Grid condition findings from inspection | 14.t.2.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Aerial | 0 | 0 | 265.95 | 348.38 | 0 | 0 | 567.01 | 62.48 | 0 | 0 | 476.36 | 159.85 | 0 | 0 | 461.13 | 0 | [11 empty] | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.t.2.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | other | Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals 4: 0 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.t.2.c.i | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.c.i | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.2.c.i | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.c.i | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.2.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.2.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 16 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.2.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Drone | Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 0; Actuals Q2: 4 |  |  |  | # of findings from these asset inspections | No data for transmission drone inspection in 2023 as it's not performed | N/A
| 14. Grid condition findings from inspection | 14.t.2.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.2.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | LiDAR | Actuals Q1: 0; Actuals Q2: 0 |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.2.d.i | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.d.i | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Aerial | 0 | 3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 1 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.2.d.i | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.d.i | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.2.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Aerial | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.2.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | other | 170 | 114 | 37 | 26 | 53 | 61 | 38 | 47 | 70 | 10 | 98 | 136 | 27 | 108 | 24 | 34 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.2.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Drone | Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 8; Actuals Q1: 1; Actuals Q2: 3; Actuals Q3: 42; Actuals Q4: 25; Actuals Q1: 2; Actuals Q2: 0; Actuals Q3: 2; Actuals Q4: 1; Actuals Q1: 0; Actuals Q2: 2 |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.2.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.2.e.i | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.e.i | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.2.e.i | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.e.i | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.2.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.2.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | other | 0 | 8 | 0 | 3 | 1 | 8 | 2 | 0 | 13 | 0 | 6 | 3 | 1 | 7 | 0 | 1 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.2.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Drone | Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0 |  |  |  | # of findings from these asset inspections | No data for transmission drone inspection in 2023 as it's not performed | N/A
| 14. Grid condition findings from inspection | 14.t.2.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.2.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.2.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Aerial | 1086 | 323 | 230 | 0 | 913 | 842 | 230 | 0 | 1023 | 745 | 230 | 0 | 1385 | 387 | 1828 | 0 | [11 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.3.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.a.i | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.3.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Aerial | 0 | 1 | 0 | 91 | 64 | 0 | 0 | 0 | 7 | 11 | 3 | 0 | 0 | 0 | 7 | 77 | [11 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.3.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.a.ii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | other | 0 | 229 | 562 | 167 | 193 | 161 | 0 | 37 | 197 | 204 | 81 | 35 | 0 | 110 | 643 | 126 | [11 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.3.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Drone | Actuals Q1: 0; Actuals Q2: 125; Actuals Q3: 53; Actuals Q4: 565; Actuals Q1: 24; Actuals Q2: 0; Actuals Q3: 1; Actuals Q4: 3; Actuals Q1: 2; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 5 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | No data for transmission drone inspection in 2023 as it's not performed | N/A
| 14. Grid condition findings from inspection | 14.t.3.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Aerial | 0 | 0 | 1108 | 675 | 0 | 0 | 1927 | 139 | 0 | 0 | 1957 | 44 | 0 | 0 | 1952 | 0 | [11 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.3.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.a.iii | Number of assets inspected | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | other | Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals 4: 0 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.3.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Aerial | 129.08 | 17.99 | 69.26 | 0 | 92.8 | 79.78 | 69.26 | 0 | 112 | 60.83 | 69.26 | 0 | 114 | 55.8647 | 54.89 | 0 | [11 empty] | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.t.3.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.b.i | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | other | Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals 4: 0 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.t.3.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Aerial | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.b.ii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | other | 0 | 20.53 | 55.05 | 73.33 | 54.52 | 30.47 | 0 | 6.46 | 28.87 | 78.29 | 5.11 | 6.04 | 0 | 9.1823 | 14.3 | 0 | [11 empty] | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.t.3.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Drone | Actuals Q1: 0; Actuals Q2: 15.321; Actuals Q3: 5.9054; Actuals Q4: 91.1276; Actuals Q1: 1.7387; Actuals Q2: 0; Actuals Q3: 0.17372; Actuals Q4: 0.21345; Actuals Q1: 0.075413; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0.30205 |  |  |  | # of circuit miles inspected by the utility | No data for transmission drone inspection in 2023 as it's not performed | N/A
| 14. Grid condition findings from inspection | 14.t.3.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Aerial | 0 | 0 | 171.66 | 58.44 | 0 | 0 | 237.35 | 4.54 | 0 | 0 | 229.92 | 12.18 | 0 | 0 | 221.44 | 0 | [11 empty] | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.t.3.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.b.iii | Number of circuit miles inspected | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | other | Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals 4: 0 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.t.3.c.i | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.c.i | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.c.i | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.c.i | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.c.ii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Drone | Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0 |  |  |  | # of findings from these asset inspections | No data for transmission drone inspection in 2023 as it's not performed | N/A
| 14. Grid condition findings from inspection | 14.t.3.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.c.iii | Level 1 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.d.i | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.d.i | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.d.i | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.d.i | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Aerial | 0 | 0 | 0 | 5 | 3 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 8 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.d.ii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | other | 0 | 12 | 8 | 13 | 14 | 0 | 0 | 0 | 33 | 25 | 4 | 10 | 0 | 6 | 72 | 20 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Drone | Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 9; Actuals Q1: 1; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0 |  |  |  | # of findings from these asset inspections | No data for transmission drone inspection in 2023 as it's not performed | N/A
| 14. Grid condition findings from inspection | 14.t.3.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.d.iii | Level 2 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.e.i | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.e.i | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.e.i | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.e.i | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.e.ii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Drone | Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0 |  |  |  | # of findings from these asset inspections | No data for transmission drone inspection in 2023 as it's not performed | N/A
| 14. Grid condition findings from inspection | 14.t.3.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.3.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.3.e.iii | Level 3 findings | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.a.i | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.a.i | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Aerial | 3984 | 2822 | 113 | 0 | 3294 | 3652 | 113 | 0 | 849 | 6195 | 113 | 0 | 1632 | 5372 | 110 | 0 | [11 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.4.a.i | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.a.i | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | other | 0 | 605 | 0 | 0 | 0 | 618 | 0 | 0 | 0 | 496 | 0 | 0 | 0 | 490 | 0 | 0 | [11 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.4.a.ii | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Drone | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.a.ii | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Aerial | 0 | 0 | 0 | 0 | 2 | 1 | 14 | 1 | 8 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.4.a.ii | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.a.ii | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | other | 704 | 780 | 727 | 386 | 1251 | 1102 | 392 | 331 | 579 | 762 | 360 | 286 | 426 | 853 | 693 | 503 | [11 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.4.a.iii | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Drone | Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 219; Actuals Q1: 3; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 71; Actuals Q4: 129 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility | No data for transmission drone inspection in 2023 as it's not performed | N/A
| 14. Grid condition findings from inspection | 14.t.4.a.iii | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Aerial | 0 | 0 | 4650 | 2163 | 0 | 0 | 6188 | 636 | 0 | 0 | 6286 | 479 | 0 | 0 | 6579 | 0 | [11 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.4.a.iii | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Other Inspection | LiDAR | [27 empty] | # of assets / structures (such as poles, transformers, etc.) inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.a.iii | Number of assets inspected | N/A | N/A | Non-HFTD | Transmission | Other Inspection | other | Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 11; Actuals Q2: 576; Actuals Q3: 187; Actuals 4: 70 |  |  |  | # of assets / structures (such as poles, transformers, etc.) inspected by the utility
| 14. Grid condition findings from inspection | 14.t.4.b.i | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.b.i | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Aerial | 448.19 | 282.1 | 31.88 | 0 | 439.14 | 297.82 | 31.88 | 0 | 180.77 | 568.66 | 31.88 | 0 | 153.22 | 483.9061 | 31.78 | 0 | [11 empty] | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.t.4.b.i | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.b.i | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | other | 0 | 37.47 | 0 | 0 | 0 | 38.15 | 0 | 0 | 0 | 31.26 | 0 | 0 | 0 | 30.3689 | 0 | 0 | [11 empty] | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.t.4.b.ii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Drone | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.b.ii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Aerial | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.b.ii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.b.ii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | other | 86.19 | 122.67 | 83.14 | 75.86 | 146.38 | 85.75 | 79.45 | 56.32 | 57.85 | 249.11 | 30.37 | 25.94 | 0 | 2.1505 | 12.49 | 22.56 | [11 empty] | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.t.4.b.iii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Drone | Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 24.0601; Actuals Q1: 0.7528; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 6.084; Actuals Q4: 11.9806 |  |  |  | # of circuit miles inspected by the utility | No data for transmission drone inspection in 2023 as it's not performed | N/A
| 14. Grid condition findings from inspection | 14.t.4.b.iii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Aerial | 0 | 0 | 470.08 | 262.34 | 0 | 0 | 639.4 | 100.39 | 0 | 0 | 706.11 | 37.38 | 0 | 0 | 605.2 | 0 | [11 empty] | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.t.4.b.iii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Other Inspection | LiDAR | [27 empty] | # of circuit miles inspected by the utility |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.b.iii | Number of circuit miles inspected | N/A | N/A | Non-HFTD | Transmission | Other Inspection | other | Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals 4: 0 |  |  |  | # of circuit miles inspected by the utility
| 14. Grid condition findings from inspection | 14.t.4.c.i | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.c.i | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.c.i | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.c.i | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.c.ii | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.c.ii | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.c.ii | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.c.ii | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.c.iii | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Drone | Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0 |  |  |  | # of findings from these asset inspections | No data for transmission drone inspection in 2023 as it's not performed | N/A
| 14. Grid condition findings from inspection | 14.t.4.c.iii | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.c.iii | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.c.iii | Level 1 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.d.i | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.d.i | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Aerial | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2 | 1 | 0 | 1 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.d.i | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.d.i | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.d.ii | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.d.ii | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.d.ii | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.d.ii | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | other | 233 | 130 | 71 | 53 | 115 | 194 | 105 | 106 | 73 | 32 | 34 | 78 | 57 | 161 | 164 | 116 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.d.iii | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Drone | Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 19; Actuals Q1: 1; Actuals Q2: 1; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 1; Actuals Q2: 2 |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.d.iii | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.d.iii | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.d.iii | Level 2 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | other | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.e.i | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.e.i | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.e.i | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.e.i | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.e.ii | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Drone | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.e.ii | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.e.ii | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.e.ii | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | other | 10 | 1 | 1 | 16 | 3 | 20 | 0 | 4 | 2 | 1 | 1 | 0 | 10 | 18 | 5 | 2 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.e.iii | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Drone | Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0 |  |  |  | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.e.iii | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
| 14. Grid condition findings from inspection | 14.t.4.e.iii | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | LiDAR | [27 empty] | # of findings from these asset inspections |  | N/A
| 14. Grid condition findings from inspection | 14.t.4.e.iii | Level 3 findings | N/A | N/A | Non-HFTD | Transmission | Other Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of findings from these asset inspections
x | 15. Grid condition fixes in response to inspection findings | 15.b.2.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.2.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | other | 10 | 3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.2.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | other | 4 | 6 | 3 | 0 | 2 | 1 | 1 | 0 | 2 | 3 | 1 | 0 | 0 | 4 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.2.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Drone | 0 | 0 | 0 | 0 | 0 | 8 | 24 | 47 | 35 | 38 | 21 | 3 | 4 | 19 | 4 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.2.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | other | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | other | 0 | 9 | 11 | 2 | 8 | 14 | 37 | 13 | 56 | 48 | 28 | 37 | 17 | 17 | 38 | 26 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | other | 95 | 113 | 101 | 98 | 149 | 110 | 32 | 49 | 100 | 30 | 42 | 74 | 61 | 125 | 69 | 10 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Drone | 0 | 0 | 0 | 1 | 18 | 61 | 87 | 662 | 669 | 642 | 1416 | 1085 | 843 | 1220 | 795 | 780 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | other | 0 | 0 | 0 | 0 | 27 | 20 | 4 | 4 | 12 | 4 | 5 | 10 | 4 | 2 | 0 | 1 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Patrol Inspection | other | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Detailed Inspection | other | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.2.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Distribution | Other Inspection | other | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | other | 0 | 0 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | other | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 5 | 0 | 0 | 4 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Drone | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 10 | 0 | 0 | 1 | 1 | 3 | 8 | 3 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | other | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | other | 1 | 6 | 9 | 1 | 2 | 20 | 30 | 10 | 8 | 26 | 12 | 3 | 1 | 11 | 7 | 5 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | other | 133 | 136 | 113 | 53 | 61 | 112 | 142 | 39 | 76 | 63 | 35 | 13 | 2 | 7 | 11 | 3 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Drone | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 68 | 40 | 21 | 13 | 15 | 71 | 348 | 368 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | other | 0 | 0 | 5 | 25 | 34 | 9 | 1 | 0 | 0 | 3 | 1 | 0 | 0 | 1 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Patrol Inspection | other | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Detailed Inspection | other | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.3.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Distribution | Other Inspection | other | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.i | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.i | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.i | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.i | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | other | 6 | 13 | 2 | 3 | 7 | 4 | 4 | 1 | 5 | 6 | 8 | 0 | 6 | 3 | 3 | 1 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.ii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.ii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.ii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.ii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | other | 14 | 12 | 14 | 2 | 13 | 10 | 4 | 1 | 5 | 3 | 12 | 2 | 2 | 16 | 5 | 7 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.iii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Drone | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 16 | 5 | 4 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.iii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.iii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.a.iii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | other | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 5 | 1 | 3 | 1 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.i | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.i | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.i | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.i | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | other | 26 | 78 | 79 | 135 | 195 | 215 | 145 | 126 | 167 | 114 | 106 | 82 | 98 | 102 | 58 | 66 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.ii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.ii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.ii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.ii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | other | 382 | 370 | 253 | 247 | 324 | 359 | 268 | 255 | 281 | 240 | 216 | 129 | 229 | 203 | 136 | 79 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.iii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Drone | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 11 | 116 | 95 | 92 | 110 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.iii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.iii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.b.iii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | other | 0 | 0 | 0 | 0 | 0 | 23 | 18 | 8 | 71 | 33 | 93 | 27 | 39 | 63 | 22 | 26 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.i | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.i | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.i | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.i | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Patrol Inspection | other | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.ii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.ii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.ii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.ii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Detailed Inspection | other | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.iii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.iii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | Aerial | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.iii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.b.4.c.iii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Distribution | Other Inspection | other | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Drone | Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0 |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Aerial | 0 | 1 | 0 | 0 | 2 | 0 | 1 | 1 | 1 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Aerial | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 2 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | other | 64 | 70 | 83 | 53 | 113 | 86 | 78 | 51 | 56 | 66 | 19 | 25 | 42 | 38 | 52 | 40 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Drone | Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 2; Actuals Q1: 2; Actuals Q2: 2; Actuals Q3: 12; Actuals Q4: 6; Actuals Q1: 7; Actuals Q2: 5; Actuals Q3: 18; Actuals Q4: 16; Actuals Q1: 3; Actuals Q2: 6 |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Aerial | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Patrol Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | Aerial | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Detailed Inspection | other | 8 | 4 | 4 | 9 | 5 | 2 | 3 | 4 | 4 | 5 | 1 | 1 | 2 | 0 | 1 | 3 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Drone | Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0 |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.2.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 2 | Transmission | Other Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.i | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.ii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Drone | Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0 |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.a.iii | Level 1 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.i | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Aerial | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 5 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.ii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | other | 13 | 5 | 1 | 29 | 6 | 9 | 3 | 11 | 8 | 28 | 5 | 3 | 6 | 11 | 8 | 3 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Drone | Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 3; Actuals Q1: 1; Actuals Q2: 1; Actuals Q3: 1; Actuals Q4: 2; Actuals Q1: 2; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0 |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.b.iii | Level 2 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.i | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Patrol Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.ii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Detailed Inspection | other | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Drone | Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0 |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.3.c.iii | Level 3 findings fixed | N/A | N/A | HFTD Tier 3 | Transmission | Other Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.i | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.i | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.i | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.i | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.ii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.ii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.ii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.ii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.iii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Drone | Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0 |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.iii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.iii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.a.iii | Level 1 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.i | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.i | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Aerial | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.i | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.i | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.ii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.ii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Aerial | 0 | 0 | 2 | 0 | 1 | 0 | 3 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.ii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.ii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | other | 146 | 143 | 78 | 97 | 91 | 159 | 91 | 147 | 140 | 87 | 50 | 24 | 120 | 39 | 16 | 22 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.iii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Drone | Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 5; Actuals Q2: 1; Actuals Q3: 6; Actuals Q4: 5; Actuals Q1: 3; Actuals Q2: 0; Actuals Q3: 1; Actuals Q4: 0 |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.iii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Aerial | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 3 | 0 | 1 | 0 | 0 | 0 | 2 | 1 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.iii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.b.iii | Level 2 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | other | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.i | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.i | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.i | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.i | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Patrol Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.ii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Drone | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.ii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | Aerial | 0 | 0 | 2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.ii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.ii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Detailed Inspection | other | 14 | 12 | 1 | 6 | 8 | 4 | 13 | 17 | 3 | 4 | 5 | 1 | 5 | 0 | 0 | 1 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.iii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Drone | Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0; Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 0; Actuals Q4: 0 |  |  |  | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.iii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.iii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | LiDAR | [27 empty] | # of asset inspection findings which have been fixed |  | N/A
| 15. Grid condition fixes in response to inspection findings | 15.t.4.c.iii | Level 3 findings fixed | N/A | N/A | Non-HFTD | Transmission | Other Inspection | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of asset inspection findings which have been fixed
x | 16. Vegetation clearance findings from inspection | 16.d.2.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Distribution | Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.2.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Distribution | Routine | Aerial | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.2.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Distribution | Routine | LiDAR | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.2.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Distribution | Routine | other | 41869 | 48585 | 22572 | 19722 | 31166 | 58689 | 25578 | 20843 | 36836 | 51265 | 26287 | 22845 | 33984 | 50979 | 26968 | 25737 | [11 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
| 16. Vegetation clearance findings from inspection | 16.d.2.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Distribution | Non-Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.2.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Distribution | Non-Routine | Aerial | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.2.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Distribution | Non-Routine | LiDAR | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDG&E recieved LiDAR inspection results for 10 HFTD circuits in year 2022 | N/A
| 16. Vegetation clearance findings from inspection | 16.d.2.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Distribution | Non-Routine | other | Actuals Q1: 28118; Actuals Q2: 12109; Actuals Q3: 58842; Actuals 4: 32534 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDGE records off-cycle work orders and VMAs, and all HFTD trees within the VMAs are counted as trees inspected. | N/A
| 16. Vegetation clearance findings from inspection | 16.d.2.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Distribution | Non-Routine | Drone | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | [11 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | This metric is based on vegetation related issues around structures from distribution asset drone inspection findings, total trees inspected is not tracked
| 16. Vegetation clearance findings from inspection | 16.d.2.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Distribution | Non-Routine | Aerial | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.2.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Distribution | Non-Routine | LiDAR | Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 3; Actuals Q4: 0 |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDG&E recieved LiDAR inspection results for 10 HFTD circuits in year 2022 | N/A for year 2023
| 16. Vegetation clearance findings from inspection | 16.d.2.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Distribution | Non-Routine | other | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDG&E is updating its database to separate off-cycle inspection from routine inspection. Findings of Non-Routine inspection are currently grouped in routine inspection findings | N/A
| 16. Vegetation clearance findings from inspection | 16.d.2.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Distribution | Routine | Drone | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.2.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Distribution | Routine | Aerial | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.2.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Distribution | Routine | LiDAR | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.2.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Distribution | Routine | other | 383 | 408 | 342 | 553 | 339 | 481 | 541 | 435 | 245 | 386 | 191 | 197 | 128 | 232 | 157 | 681 | [11 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
| 16. Vegetation clearance findings from inspection | 16.d.3.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Distribution | Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.3.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Distribution | Routine | Aerial | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.3.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Distribution | Routine | LiDAR | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.3.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Distribution | Routine | other | 25613 | 22926 | 47613 | 15046 | 18207 | 32021 | 49120 | 14428 | 23029 | 28321 | 38513 | 23190 | 19927 | 29307 | 33325 | 32012 | [11 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
| 16. Vegetation clearance findings from inspection | 16.d.3.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Distribution | Non-Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.3.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Distribution | Non-Routine | Aerial | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.3.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Distribution | Non-Routine | LiDAR | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDG&E recieved LiDAR inspection results for 10 HFTD circuits in year 2022 | N/A
| 16. Vegetation clearance findings from inspection | 16.d.3.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Distribution | Non-Routine | other | Actuals Q1: 17969; Actuals Q2: 26487; Actuals Q3: 47029; Actuals 4: 18968 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDGE is updating the database to capture this information | N/A
| 16. Vegetation clearance findings from inspection | 16.d.3.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Distribution | Non-Routine | Drone | 2 | 4 | 1 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | [11 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | This metric is based on vegetation related issues around structures from distribution asset drone inspection findings, total trees inspected is not tracked
| 16. Vegetation clearance findings from inspection | 16.d.3.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Distribution | Non-Routine | Aerial | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.3.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Distribution | Non-Routine | LiDAR | Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 1; Actuals Q4: 0 |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDG&E recieved LiDAR inspection results for 10 HFTD circuits in year 2022 | N/A for year 2023
| 16. Vegetation clearance findings from inspection | 16.d.3.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Distribution | Non-Routine | other | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDG&E is updating its database to separate off-cycle inspection from routine inspection. Findings of Non-Routine inspection are currently grouped in routine inspection findings | N/A
| 16. Vegetation clearance findings from inspection | 16.d.3.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Distribution | Routine | Drone | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.3.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Distribution | Routine | Aerial | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.3.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Distribution | Routine | LiDAR | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.3.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Distribution | Routine | other | 184 | 212 | 467 | 284 | 265 | 267 | 225 | 88 | 134 | 196 | 211 | 111 | 31 | 154 | 200 | 474 | [11 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
| 16. Vegetation clearance findings from inspection | 16.d.4.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Distribution | Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.4.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Distribution | Routine | Aerial | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.4.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Distribution | Routine | LiDAR | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.4.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Distribution | Routine | other | 56268 | 34555 | 48350 | 69008 | 53990 | 38400 | 58708 | 72084 | 65041 | 36958 | 55524 | 77669 | 59652 | 38658 | 52966 | 86909 | [11 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
| 16. Vegetation clearance findings from inspection | 16.d.4.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Distribution | Non-Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.4.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Distribution | Non-Routine | Aerial | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.4.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Distribution | Non-Routine | LiDAR | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDG&E recieved LiDAR inspection results for 10 HFTD circuits in year 2022 | N/A
| 16. Vegetation clearance findings from inspection | 16.d.4.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Distribution | Non-Routine | other | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDGE is updating the database to capture this information | N/A
| 16. Vegetation clearance findings from inspection | 16.d.4.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Distribution | Non-Routine | Drone | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 0 | 2 | 0 | [11 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | This metric is based on vegetation related issues around structures from distribution asset drone inspection findings, total trees inspected is not tracked
| 16. Vegetation clearance findings from inspection | 16.d.4.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Distribution | Non-Routine | Aerial | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.4.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Distribution | Non-Routine | LiDAR | Actuals Q1: 0; Actuals Q2: 0; Actuals Q3: 3; Actuals Q4: 0 |  |  |  | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDG&E recieved LiDAR inspection results for 10 HFTD circuits in year 2022 | N/A for year 2023
| 16. Vegetation clearance findings from inspection | 16.d.4.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Distribution | Non-Routine | other | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDG&E is updating its database to separate off-cycle inspection from routine inspection. Findings of Non-Routine inspection are currently grouped in routine inspection findings | N/A
| 16. Vegetation clearance findings from inspection | 16.d.4.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Distribution | Routine | Drone | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.4.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Distribution | Routine | Aerial | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.4.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Distribution | Routine | LiDAR | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.d.4.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Distribution | Routine | other | 439 | 408 | 1683 | 2108 | 373 | 505 | 2008 | 1886 | 503 | 484 | 503 | 1672 | 425 | 504 | 478 | 3492 | [11 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
| 16. Vegetation clearance findings from inspection | 16.t.2.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Transmission | Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.2.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Transmission | Routine | Aerial | 0 | 110 | 0 | 0 | 0 | 112 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 115 | 0 | 0 | [11 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
| 16. Vegetation clearance findings from inspection | 16.t.2.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Transmission | Routine | LiDAR | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.2.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Transmission | Routine | other | 874 | 1961 | 1353 | 1731 | 718 | 1907 | 1660 | 1677 | 939 | 1572 | 2064 | 1408 | 672 | 1662 | 1665 | 1560 | [11 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
| 16. Vegetation clearance findings from inspection | 16.t.2.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Transmission | Non-Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.2.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Transmission | Non-Routine | Aerial | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.2.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Transmission | Non-Routine | LiDAR | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.2.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 2 | Transmission | Non-Routine | other | Actuals Q1: 1427; Actuals Q2: 1212; Actuals Q3: 2766; Actuals 4: 147 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDGE is updating the database to capture this information | N/A
| 16. Vegetation clearance findings from inspection | 16.t.2.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Transmission | Non-Routine | Drone | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.2.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Transmission | Non-Routine | Aerial | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.2.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Transmission | Non-Routine | LiDAR | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.2.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Transmission | Non-Routine | other | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDG&E is updating its database to separate off-cycle inspection from routine inspection. Findings of Non-Routine inspection are currently grouped in routine inspection findings | N/A
| 16. Vegetation clearance findings from inspection | 16.t.2.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Transmission | Routine | Drone | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.2.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Transmission | Routine | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
| 16. Vegetation clearance findings from inspection | 16.t.2.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Transmission | Routine | LiDAR | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.2.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 2 | Transmission | Routine | other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
| 16. Vegetation clearance findings from inspection | 16.t.3.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Transmission | Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.3.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Transmission | Routine | Aerial | 0 | 3 | 0 | 3 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | [11 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
| 16. Vegetation clearance findings from inspection | 16.t.3.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Transmission | Routine | LiDAR | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.3.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Transmission | Routine | other | 373 | 261 | 939 | 79 | 237 | 98 | 965 | 189 | 172 | 56 | 1030 | 137 | 64 | 73 | 740 | 372 | [11 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
| 16. Vegetation clearance findings from inspection | 16.t.3.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Transmission | Non-Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.3.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Transmission | Non-Routine | Aerial | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.3.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Transmission | Non-Routine | LiDAR | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.3.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | HFTD Tier 3 | Transmission | Non-Routine | other | Actuals Q1: 603; Actuals Q2: 300; Actuals Q3: 384; Actuals 4: 18 |  |  |  | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDGE is updating the database to capture this information | N/A
| 16. Vegetation clearance findings from inspection | 16.t.3.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Transmission | Non-Routine | Drone | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.3.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Transmission | Non-Routine | Aerial | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.3.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Transmission | Non-Routine | LiDAR | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.3.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Transmission | Non-Routine | other | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDG&E is updating its database to separate off-cycle inspection from routine inspection. Findings of Non-Routine inspection are currently grouped in routine inspection findings | N/A
| 16. Vegetation clearance findings from inspection | 16.t.3.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Transmission | Routine | Drone | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.3.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Transmission | Routine | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
| 16. Vegetation clearance findings from inspection | 16.t.3.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Transmission | Routine | LiDAR | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.3.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | HFTD Tier 3 | Transmission | Routine | other | 1 | 1 | 1 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
| 16. Vegetation clearance findings from inspection | 16.t.4.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Transmission | Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.4.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Transmission | Routine | Aerial | 0 | 54 | 0 | 10 | 0 | 2 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 57 | 0 | 0 | [11 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
| 16. Vegetation clearance findings from inspection | 16.t.4.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Transmission | Routine | LiDAR | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.4.a.i | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Transmission | Routine | other | 1924 | 3227 | 7582 | 2091 | 1909 | 2810 | 7971 | 2090 | 2225 | 2972 | 6382 | 3493 | 1733 | 2781 | 5841 | 4275 | [11 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
| 16. Vegetation clearance findings from inspection | 16.t.4.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Transmission | Non-Routine | Drone | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.4.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Transmission | Non-Routine | Aerial | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.4.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Transmission | Non-Routine | LiDAR | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.4.a.ii | Number of trees inspected for vegetation compliance | N/A | N/A | Non-HFTD | Transmission | Non-Routine | other | [27 empty] | # of trees inspected for vegetation compliance based on GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDGE is updating the database to capture this information | N/A
| 16. Vegetation clearance findings from inspection | 16.t.4.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Transmission | Non-Routine | Drone | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.4.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Transmission | Non-Routine | Aerial | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.4.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Transmission | Non-Routine | LiDAR | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.4.b.i | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Transmission | Non-Routine | other | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of non-routine inspection. | SDG&E is updating its database to separate off-cycle inspection from routine inspection. Findings of Non-Routine inspection are currently grouped in routine inspection findings | N/A
| 16. Vegetation clearance findings from inspection | 16.t.4.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Transmission | Routine | Drone | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.4.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Transmission | Routine | Aerial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
| 16. Vegetation clearance findings from inspection | 16.t.4.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Transmission | Routine | LiDAR | [27 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection. |  | N/A
| 16. Vegetation clearance findings from inspection | 16.t.4.b.ii | Number of trees inspected where at least some vegetation was found in non-compliant condition | N/A | N/A | Non-HFTD | Transmission | Routine | other | 7 | 2 | 1 | 3 | 2 | 0 | 2 | 0 | 3 | 1 | 0 | 0 | 0 | 2 | 0 | 6 | [11 empty] | # of trees found to be non-compliant with GO 95, Rule 35, and PRC 4293 at the time of routine inspection.
x | 17. Community outreach metrics | 17.a. | % of customers notified of evacuation in evacuation zone of a utility-ignited wildfire | N/A | N/A | N/A | N/A | N/A | N/A | [27 empty] | Percentage of customers notified of evacuation | SDG&E does not track this data | N/A

## Table 3
Utility |  | SDG&E
Table No. |  | 3
Date Modified |  | 2024-02-01
[6 empty] | Actual | [7 empty] | Note: These columns are placeholders for future QR submissions. | [7 empty] | Projected
Table 3: List and description of additional metrics | [5 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric | # | Definition | Purpose | Assumptions made to connect metric to purpose | Third-party validation (if any) | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | 2024 | 2024 | 2024 | 2024 | 2025 | 2025 | 2025 | 2025 | 2023 | 2024 | 2025 | Unit(s) | Comments | Blank Meaning
1. Elevated FPI and Red Flag Warning Days | 1.a. | Number of High FPI days (elevated or extreme FPI) |  | Elevated or extreme FPI is associated with greater wildfire risk | No | Actual 1: 1; Actual 2: 30; Actual 3: 87; Actual 4: 33; Actual 1: 0; Actual 2: 7; Actual 3: 71; Actual 4: 25 |  |  |  | Days
| 1.b. | Number of RFW days |  | RFW is associated with greater wildfire risk. | No | Actual 1: 0; Actual 2: 0; Actual 3: 0; Actual 4: 1; Actual 1: 0; Actual 2: 0; Actual 3: 0; Actual 4: 0 |  |  |  | Days
2. Ignition Events | 2.a. | Vegetation caused ignitons in HFTD with elevated or higher FPI |  |  | No | Actual 1: 0; Actual 2: 0; Actual 3: 0; Actual 4: 1; Actual 1: 0; Actual 2: 0; Actual 3: 0; Actual 4: 0 |  |  |  | Ignitions
| 2.b. | Vegetation caused ignitons in HFTD with RFW |  |  | No | Actual 1: 0; Actual 2: 0; Actual 3: 0; Actual 4: 0; Actual 1: 0; Actual 2: 0; Actual 3: 0; Actual 4: 0 |  |  |  | Ignitions
| 2.c. | Equipment caused ignitions in HFTD with elevated or higher FPI |  |  | No | Actual 1: 0; Actual 2: 0; Actual 3: 0; Actual 4: 0; Actual 1: 0; Actual 2: 0; Actual 3: 0; Actual 4: 1 |  |  |  | Ignitions
| 2.d. | Equipment caused ignitions in HFTD with RFW |  |  | No | Actual 1: 0; Actual 2: 0; Actual 3: 0; Actual 4: 0; Actual 1: 0; Actual 2: 0; Actual 3: 0; Actual 4: 0 |  |  |  | Ignitions
| 2.e. | Balloons caused ignitions in HFTD with elevated or higher FPI |  |  | No | Actual 1: 0; Actual 2: 0; Actual 3: 2; Actual 4: 0; Actual 1: 0; Actual 2: 0; Actual 3: 0; Actual 4: 0 |  |  |  | Ignitions
| 2.f. | Balloons caused ignitions in HFTD with RFW |  |  | No | Actual 1: 0; Actual 2: 0; Actual 3: 0; Actual 4: 0; Actual 1: 0; Actual 2: 0; Actual 3: 0; Actual 4: 0 |  |  |  | Ignitions
| 2.g. | Vehicles caused ignitions in HFTD with elevated or higher FPI |  |  | No | Actual 1: 0; Actual 2: 0; Actual 3: 0; Actual 4: 0; Actual 1: 0; Actual 2: 0; Actual 3: 1; Actual 4: 0 |  |  |  | Ignitions
| 2.h. | Vehicles caused ignitions in HFTD with RFW |  |  | No | Actual 1: 0; Actual 2: 0; Actual 3: 0; Actual 4: 0; Actual 1: 0; Actual 2: 0; Actual 3: 0; Actual 4: 0 |  |  |  | Ignitions
| 2.i. | Equipment caused ignition rate in HFTD during high FPI |  |  | No | Actual 1: 0; Actual 2: 0; Actual 3: 0; Actual 4: 0; Actual 1: 0; Actual 2: 0; Actual 3: 0; Actual 4: 0.5 | 0.02 | 0.02 | 0.02 | Ignitions per high FPI day
| 2.j. | CPUC reportable secondary igntions |  |  | No | Actual 1: 0; Actual 2: 0; Actual 3: 1; Actual 4: 1; Actual 1: 0; Actual 2: 1; Actual 3: 1; Actual 4: 0 |  |  |  | Ignitions | CPUC reportable secondary ignitions is not an available driver in Table 6
3. Distribution Outages | 3.a. | Vegetation caused outages in HFTD with Elevated FPI |  |  | No | Actual 1: 1; Actual 2: 1; Actual 3: 5; Actual 4: 3; Actual 1: 0; Actual 2: 0; Actual 3: 1; Actual 4: 0 |  |  |  | Outages
| 3.b. | Vegetation caused outages in HFTD with RFW |  |  | No | Actual 1: 0; Actual 2: 0; Actual 3: 0; Actual 4: 0; Actual 1: 0; Actual 2: 0; Actual 3: 0; Actual 4: 0 |  |  |  | Outages
| 3.c. | Overhead faults on circuits in HFTD with Elevated or higher FPI |  |  | No | Actual 1: 2; Actual 2: 21; Actual 3: 82; Actual 4: 21; Actual 1: 0; Actual 2: 1; Actual 3: 43; Actual 4: 9 |  |  |  | Outages
| 3.d. | Overhead faults on circuits in HFTD with RFW |  |  | No | Actual 1: 0; Actual 2: 0; Actual 3: 0; Actual 4: 0; Actual 1: 0; Actual 2: 0; Actual 3: 0; Actual 4: 0 |  |  |  | Outages
| 3.e. | Energized wire down events in HFTD with Elevated or higher FPI |  |  | No | Actual 1: 1; Actual 2: 0; Actual 3: 6; Actual 4: 3; Actual 1: 0; Actual 2: 0; Actual 3: 3; Actual 4: 0 |  |  |  | Outages
| 3.f. | Energized wire down events in HFTD with RFW |  |  | No | Actual 1: 0; Actual 2: 0; Actual 3: 0; Actual 4: 0; Actual 1: 0; Actual 2: 0; Actual 3: 0; Actual 4: 0 |  |  |  | Outages
| 3.g. | Number of non-CALFIRE rated fuse operations in HFTD with Elevated or higher FPI |  |  | No | Actual 1: 0; Actual 2: 3; Actual 3: 8; Actual 4: 3; Actual 1: 0; Actual 2: 0; Actual 3: 5; Actual 4: 1 |  |  |  | Outages
| 3.h. | Number of non-CALFIRE rated fuse operations in HFTD with RFW |  |  | No | Actual 1: 0; Actual 2: 0; Actual 3: 0; Actual 4: 0; Actual 1: 0; Actual 2: 0; Actual 3: 0; Actual 4: 0 |  |  |  | Outages
| 3.i. | Overhead fault rate in HFTD during High FPI |  |  | No | Actual 1: 5; Actual 2: 0.83; Actual 3: 1.01; Actual 4: 0.55; Actual 1: 0; Actual 2: 0.57; Actual 3: 0.76; Actual 4: 0.64 |  |  |  | Overhead faults per high FPI day
4. Personnel Safety Leading Indicators | 4.a. | Near Miss Reporting |  |  | No | Actual 1: 66; Actual 2: 133; Actual 3: 99; Actual 4: 73; Actual 1: 123; Actual 2: 122; Actual 3: 103; Actual 4: 88 |  |  |  | Near miss events reported
| 4.b. | Safety Observations |  |  | No | Actual 1: 5651; Actual 2: 5569; Actual 3: 5318; Actual 4: 3817; Actual 1: 5115; Actual 2: 5264; Actual 3: 5428; Actual 4: 5052 |  |  |  | Observations performed
5. Other PSPS | 5.a. | Percent of customers being de-energized on PSPS circuits |  |  | No | Actual 1: 0; Actual 2: 0; Actual 3: 0; Actual 4: 0; Actual 1: 0; Actual 2: 0; Actual 3: 0; Actual 4: 0 | 42.231 | 42.231 | 42.231 | percent
| 5.b. | Number of circuits de-engergized |  |  | No | Actual 1: 0; Actual 2: 0; Actual 3: 0; Actual 4: 0; Actual 1: 0; Actual 2: 0; Actual 3: 0; Actual 4: 0 | 15.67 | 15.67 | 15.67 | circuits
6. Situational Awareness | 6.a. | Communication success rate of weather stations |  |  | Yes | Actual 1: 97.55; Actual 2: 98.56; Actual 3: 97.47; Actual 4: 96.69; Actual 1: 98.16; Actual 2: 95.92; Actual 3: 98.79; Actual 4: 99.1 | 97.51 | 97.51 | 97.51 | percent
| 6.b. | Post processing success rate - WRF simulations |  |  | Yes | Actual 1: 98.1; Actual 2: 96.8; Actual 3: 92.2; Actual 4: 99.1; Actual 1: 95.9; Actual 2: 100; Actual 3: 99.5; Actual 4: 99.9 | 97.45 | 97.45 | 97.45 | percent
| 6.c. | Post processing success rate - ML gust model |  |  | No | Actual 1: 95.6; Actual 2: 96.7; Actual 3: 89.1; Actual 4: 98.9; Actual 1: 97.2; Actual 2: 100; Actual 3: 99.5; Actual 4: 100 | 96.15 | 96.15 | 96.15 | percent
| 6.d. | Post processing success rate - SAWTI |  |  | No | Actual 1: 74.7; Actual 2: 55.1; Actual 3: 63.6; Actual 4: 94; Actual 1: 96.7; Actual 2: 91.2; Actual 3: 95.4; Actual 4: 97.1 | 93 | 93 | 93 | percent
| 6.e. | Post processing success rate - FPI |  |  | No | Actual 1: 96.1; Actual 2: 96.7; Actual 3: 89.7; Actual 4: 94; Actual 1: 96.7; Actual 2: 100; Actual 3: 98.9; Actual 4: 99.5 | 95.05 | 95.05 | 95.05 | percent
| 6.f. | Post processing success rate - OPI |  |  | No | Actual 1: 92.2; Actual 2: 96.2; Actual 3: 92.4; Actual 4: 98.4; Actual 1: 97.8; Actual 2: 100; Actual 3: 99.5; Actual 4: 100 | 94.3 | 94.3 | 94.3 | percent
7. Emergency Preparedness | 7.a | Percentage of community partners participating in local wildfire mitigation planning (in territory) |  |  | No | Actual 4: 100% | 90 | 90 | 90 | percent | No activities in 2023 Q4 | N/A
| 7.b | Percentage of Wildfire/PSPS events followed by an After-Action Review or feedback process |  |  | No | [16 empty] | 95 | 95 | 100 | percent | No activities in 2023 Q4 | N/A
8. Community Outreach and Engagement | 8.a | Percentage of individuals with AFN who were aware of what support and resources were available to them during a PSPS event. |  |  | No | [16 empty] | 80 | 80 | 80 | percent | No activities in 2023 Q4 | N/A
| 8.b | Percentage of individuals with AFN who were able to use necessary medical equipment to maintain necessary life functions for the duration of any PSPS event that affected them |  |  | No | [16 empty] | 80 | 80 | 80 | percent | No activities in 2023 Q4 | N/A
| 8.c | Percentage of individuals who utilized mitigation services and reported they were satisfied with the level of support |  |  | No | [16 empty] | 80 | 80 | 80 | percent | No activities in 2023 Q4 | N/A
| 8.d | Percentage of customers notified prior to a PSPS event impacting them |  |  | No | [16 empty] | 100 | 100 | 100 | percent | No activities in 2023 Q4 | N/A

## Table 4
Utility | SDG&E
Table No. | 4
Date Modified | 2024-02-01
Note: These columns are placeholders for future QR submissions.
Table 4: Weather patterns |  |  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Metric type | # | Metric name | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | 2024 | 2024 | 2024 | 2024 | 2025 | 2025 | 2025 | 2025 | Unit(s) | Comments | Blank Meaning
1. Red flag warning only overhead circuit mile days | 1.a. | Red Flag Warning Only overhead circuit mile days - HFTD tier 2 | 1: 0; 2: 0; 3: 0; 4: 148.1; 1: 0; 2: 0; 3: 0; 4: 0 | Sum of overhead circuit miles of utility grid subject to red flag warning each day within a given time period, calculated as the number of overhead circuit miles that were under an RFW multiplied by the number of days those circuit miles were under said RFW. For example, if 100 overhead circuit miles were under an RFW for 1 day, and 10 of those miles were under RFW for an additional day, then the total RFW OH circuit mile days would be 110.
| 1.b. | Red Flag Warning Only overhead circuit mile days - HFTD tier 3 | 1: 0; 2: 0; 3: 0; 4: 0; 1: 0; 2: 0; 3: 0; 4: 0 | Red flag warning overhead circuit mile days, see above for definition
| 1.c. | Red Flag Warning Only overhead circuit mile days - non-HFTD | 1: 0; 2: 0; 3: 0; 4: 163.57; 1: 0; 2: 0; 3: 0; 4: 0 | Red flag warning overhead circuit mile days, see above for definition
2. Wind condition overhead circuit mile days | 2.a. | High Wind Warning Only overhead circuit mile days - HFTD tier 2 | 1: 3365; 2: 519; 3: 1437; 4: 2477; 1: 3464; 2: 291; 3: 0; 4: 295 | Sum of overhead circuit miles of utility grid subject to high wind warnings (HWW, as defined by the National Weather Service) each day within a given time period, calculated as the number of overhead circuit miles that were under an HWW multiplied by the number of days those miles were under said HWW. For example, if 100 overhead circuit miles were under an HWW for 1 day, and 10 of those miles were under HWW for an additional day, then the total HWW OH circuit mile days would be 110.
| 2.b. | High Wind Warning Only overhead circuit mile days - HFTD tier 3 | 1: 3619; 2: 880; 3: 1535; 4: 2547; 1: 2832; 2: 468; 3: 0; 4: 0 | High wind warning overhead circuit mile days, see above for definition
| 2.c. | High Wind Warning Only overhead circuit mile days - non-HFTD | 1: 1761; 2: 0; 3: 1429; 4: 1139; 1: 5292; 2: 130; 3: 0; 4: 109 | High wind warning overhead circuit mile days, see above for definition
3. Wind condition and Red flag warning overhead circuit mile days | 3.a. | High Wind Warning and Red Flag Warning overhead circuit mile days - HFTD tier 2 | 1: 0; 2: 0; 3: 0; 4: 0; 1: 0; 2: 0; 3: 0; 4: 0 | Sum of overhead circuit miles of utility grid subject to concurrent red flag warning and a high wind warning each day within a given time period, calculated as the number of overhead circuit miles that were under an RFW and HWW multiplied by the number of days those circuit miles were under said RFW and HWW. For example, if 100 overhead circuit miles were under an RFW and HWW for 1 day, and 10 of those miles were under RFW and HWW for an additional day, then the total RFW and HWW OH circuit mile days would be 110.
| 3.b. | High Wind Warning and Red Flag Warning overhead circuit mile days - HFTD tier 3 | 1: 0; 2: 0; 3: 0; 4: 0; 1: 0; 2: 0; 3: 0; 4: 0 | High wind warning and red flag warning overhead circuit mile days, see above for definition
| 3.c. | High Wind Warning and Red Flag Warning overhead circuit mile days - non-HFTD | 1: 0; 2: 0; 3: 0; 4: 0; 1: 0; 2: 0; 3: 0; 4: 0 | High wind warning and red flag warning overhead circuit mile days, see above for definition
4. Fire potential index overhead circuit mile days | 4.a. | Fire potential index circuit mile days - HFTD tier 2 | 1: 2381; 2: 53889; 3: 176305; 4: 57262; 1: 0; 2: 9479.76; 3: 143227; 4: 39811.6 | Sum of overhead circuit miles of utility grid subject to high fire potential index (FPI, as defined by the utility in its WMP) each day within a given time period, calculated as the number of overhead circuit miles that were under a high FPI multiplied by the number of days those miles were under said FPI. For example, if 100 overhead circuit miles were under a high FPI for 1 day, and 10 of those miles were under a high FPI for an additional day, then the total FPI OH circuit mile days would be 110.
| 4.b. | Fire potential index circuit mile days - HFTD tier 3 | 1: 1906; 2: 52441; 3: 161387; 4: 57370; 1: 0; 2: 10911.58; 3: 127551; 4: 40925 | Fire potential index overhead circuit mile days, see above for definition
| 4.c. | Fire potential index circuit mile days - non-HFTD | 1: 2184; 2: 35293; 3: 144055; 4: 37740; 1: 0; 2: 6005.72; 3: 127388; 4: 26164 | Fire potential index overhead circuit mile days, see above for definition
5. Other | 5.a. | Other relevant weather pattern metrics tracked (add additional rows as needed)

## Table 5
Utility | SDG&E | Notes:
Table No. | 5 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
Date Modified | 2024-02-01 | Data from 2015 - 2021 should be actual numbers. 2022 and 2023 should be projected. In future submissions update projected numbers with actuals
[7 empty] | Actual number of risk events | [15 empty] | Projected risk events
Table 5: Risk event drivers | [6 empty] | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4
Risk event category | Metric type | # | Risk event driver | Line Type | HFTD Tier | Are risk events tracked for ignition driver? (yes / no) | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | 2024 | 2024 | 2024 | 2024 | 2025 | 2025 | 2025 | 2025 | 2023 | 2024 | 2025 | Unit(s) | Comments | Blank Meaning
Wire down event | 1. Fire | 1.a.d.0 | Fire | Distribution | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Wire down event | 1. Fire | 1.a.d.2 | Fire | Distribution | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Wire down event | 1. Fire | 1.a.d.3 | Fire | Distribution | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Wire down event | 1. Fire | 1.a.t.0 | Fire | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Wire down event | 1. Fire | 1.a.t.2 | Fire | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Wire down event | 1. Fire | 1.a.t.3 | Fire | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Wire down event | 2. Contact from object | 2.a.d.0 | Animal contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 1.4 | 1.4 | 1.4 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.a.d.2 | Animal contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.395 | 0.38 | 0.359 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.a.d.3 | Animal contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.38 | 0.36 | 0.332 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.a.t.0 | Animal contact | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 2. Contact from object | 2.a.t.2 | Animal contact | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 2. Contact from object | 2.a.t.3 | Animal contact | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 2. Contact from object | 2.b.d.0 | Balloon contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 1; Actual number of risk events Q3: 1; Actual number of risk events Q4: 1 | 4.2 | 4.2 | 4.2 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.b.d.2 | Balloon contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1 | 0.594 | 0.573 | 0.541 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.b.d.3 | Balloon contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.19 | 0.18 | 0.166 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.b.t.0 | Balloon contact | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 2. Contact from object | 2.b.t.2 | Balloon contact | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 2. Contact from object | 2.b.t.3 | Balloon contact | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 2. Contact from object | 2.c.d.0 | Land vehicle contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 8; Actual number of risk events Q2: 4; Actual number of risk events Q3: 6; Actual number of risk events Q4: 5; Actual number of risk events Q1: 4; Actual number of risk events Q2: 5; Actual number of risk events Q3: 5; Actual number of risk events Q4: 3 | 16 | 16 | 16 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.c.d.2 | Land vehicle contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 0; Actual number of risk events Q3: 3; Actual number of risk events Q4: 2; Actual number of risk events Q1: 4; Actual number of risk events Q2: 2; Actual number of risk events Q3: 1; Actual number of risk events Q4: 2 | 6.762 | 6.597 | 6.269 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.c.d.3 | Land vehicle contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 2; Actual number of risk events Q4: 1 | 1.933 | 1.848 | 1.724 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.c.t.0 | Land vehicle contact | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 2. Contact from object | 2.c.t.2 | Land vehicle contact | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 2. Contact from object | 2.c.t.3 | Land vehicle contact | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 2. Contact from object | 2.d.d.0 | Aircraft vehicle contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.d.d.2 | Aircraft vehicle contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.d.d.3 | Aircraft vehicle contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.193 | 0.185 | 0.172 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.d.t.0 | Aircraft vehicle contact | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 2. Contact from object | 2.d.t.2 | Aircraft vehicle contact | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 2. Contact from object | 2.d.t.3 | Aircraft vehicle contact | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 2. Contact from object | 2.e.d.3 | 3rd party contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.8 | 0.8 | 0.8 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.e.d.3 | 3rd party contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.e.d.3 | 3rd party contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.e.t.3 | 3rd party contact | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 2. Contact from object | 2.e.t.3 | 3rd party contact | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 2. Contact from object | 2.e.t.3 | 3rd party contact | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 2. Contact from object | 2.f.d.3 | Other contact from object | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 1; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1 | 5.6 | 5.6 | 5.6 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.f.d.3 | Other contact from object | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 1.779 | 1.728 | 1.622 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.f.d.3 | Other contact from object | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 2; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.761 | 0.72 | 0.663 | # risk events (excluding ignitions)
Wire down event | 2. Contact from object | 2.f.t.3 | Other contact from object | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 2. Contact from object | 2.f.t.3 | Other contact from object | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 2. Contact from object | 2.f.t.3 | Other contact from object | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 2. Contact from object | 2.g.d.3 | Unknown | Distribution | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E doesn't currently track this driver as contact from object. If no damage is found the risk event is categorized as "Unknown"
Wire down event | 2. Contact from object | 2.g.d.3 | Unknown | Distribution | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E doesn't currently track this driver as contact from object. If no damage is found the risk event is categorized as "Unknown"
Wire down event | 2. Contact from object | 2.g.d.3 | Unknown | Distribution | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E doesn't currently track this driver as contact from object. If no damage is found the risk event is categorized as "Unknown"
Wire down event | 2. Contact from object | 2.g.t.3 | Unknown | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E doesn't currently track this driver as contact from object. If no damage is found the risk event is categorized as "Unknown"
Wire down event | 2. Contact from object | 2.g.t.3 | Unknown | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E doesn't currently track this driver as contact from object. If no damage is found the risk event is categorized as "Unknown"
Wire down event | 2. Contact from object | 2.g.t.3 | Unknown | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E doesn't currently track this driver as contact from object. If no damage is found the risk event is categorized as "Unknown"
Wire down event | 3. Vegetation contact | 3.a.d.0 | Vegetation contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0; Actual number of risk events Q1: 10; Actual number of risk events Q2: 3; Actual number of risk events Q3: 2; Actual number of risk events Q4: 1 | 10.8 | 10.8 | 10.8 | # risk events (excluding ignitions)
Wire down event | 3. Vegetation contact | 3.a.d.2 | Vegetation contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 3; Actual number of risk events Q4: 0; Actual number of risk events Q1: 5; Actual number of risk events Q2: 0; Actual number of risk events Q3: 2; Actual number of risk events Q4: 0 | 2.852 | 2.505 | 2.157 | # risk events (excluding ignitions)
Wire down event | 3. Vegetation contact | 3.a.d.3 | Vegetation contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 3; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0 | 1.867 | 1.734 | 1.601 | # risk events (excluding ignitions)
Wire down event | 3. Vegetation contact | 3.a.t.0 | Vegetation contact | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 3. Vegetation contact | 3.a.t.2 | Vegetation contact | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 3. Vegetation contact | 3.a.t.3 | Vegetation contact | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.a.d.0 | Anchor/guy | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.a.d.2 | Anchor/guy | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.198 | 0.19 | 0.179 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.a.d.3 | Anchor/guy | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.a.t.0 | Anchor/guy | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.a.t.2 | Anchor/guy | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.a.t.3 | Anchor/guy | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.b.d.0 | Capacitor bank | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.b.d.2 | Capacitor bank | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.b.d.3 | Capacitor bank | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.b.t.0 | Capacitor bank | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.b.t.2 | Capacitor bank | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.b.t.3 | Capacitor bank | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.c.d.0 | Conductor | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 4; Actual number of risk events Q2: 3; Actual number of risk events Q3: 3; Actual number of risk events Q4: 4; Actual number of risk events Q1: 19; Actual number of risk events Q2: 2; Actual number of risk events Q3: 1; Actual number of risk events Q4: 1 | 17.4 | 17.4 | 17.4 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.c.d.2 | Conductor | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 2; Actual number of risk events Q3: 0; Actual number of risk events Q4: 2; Actual number of risk events Q1: 1; Actual number of risk events Q2: 1; Actual number of risk events Q3: 1; Actual number of risk events Q4: 4 | 6.544 | 6.345 | 6.014 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.c.d.3 | Conductor | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 3; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 1; Actual number of risk events Q1: 3; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1 | 6.655 | 6.333 | 5.876 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.c.t.0 | Conductor | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.2 | 0.2 | 0.2 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.c.t.2 | Conductor | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.392 | 0.377 | 0.377 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.c.t.3 | Conductor | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.d.d.0 | Connector device | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 2; Actual number of risk events Q1: 2; Actual number of risk events Q2: 1; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0 | 3.4 | 3.4 | 3.4 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.d.d.2 | Connector device | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0 | 2.37 | 2.279 | 2.152 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.d.d.3 | Connector device | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0 | 2.092 | 1.979 | 1.824 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.d.t.0 | Connector device | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.d.t.2 | Connector device | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.d.t.3 | Connector device | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.e.d.0 | Crossarm | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 2; Actual number of risk events Q1: 2; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 1 | 1 | 1 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.e.d.2 | Crossarm | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.198 | 0.19 | 0.179 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.e.d.3 | Crossarm | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.38 | 0.36 | 0.332 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.e.t.0 | Crossarm | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.e.t.2 | Crossarm | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.e.t.3 | Crossarm | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.f.d.0 | Fuse | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.f.d.2 | Fuse | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.f.d.3 | Fuse | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.f.t.0 | Fuse | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.f.t.2 | Fuse | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.f.t.3 | Fuse | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.g.d.0 | Cutout | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.4 | 0.4 | 0.4 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.g.d.2 | Cutout | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.g.d.3 | Cutout | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.2 | 0.2 | 0.2 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.g.t.0 | Cutout | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.g.t.2 | Cutout | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.g.t.3 | Cutout | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.h.d.0 | Insulator and bushing | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.2 | 0.2 | 0.2 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.h.d.2 | Insulator and bushing | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.h.d.3 | Insulator and bushing | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.h.t.0 | Insulator and bushing | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.h.t.2 | Insulator and bushing | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.h.t.3 | Insulator and bushing | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.i.d.0 | Lightning arrester | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0 | 0.2 | 0.2 | 0.2 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.i.d.2 | Lightning arrester | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.i.d.3 | Lightning arrester | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.i.t.0 | Lightning arrester | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.i.t.2 | Lightning arrester | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.i.t.3 | Lightning arrester | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.j.d.0 | Pole | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0 | 2 | 2 | 2 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.j.d.2 | Pole | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.79 | 0.76 | 0.717 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.j.d.3 | Pole | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 2; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.38 | 0.36 | 0.332 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.j.t.0 | Pole | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.j.t.2 | Pole | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.j.t.3 | Pole | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.k.d.0 | Recloser | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.k.d.2 | Recloser | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.k.d.3 | Recloser | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.k.t.0 | Recloser | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.k.t.2 | Recloser | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.k.t.3 | Recloser | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.l.d.0 | Relay | Distribution | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.l.d.2 | Relay | Distribution | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.l.d.3 | Relay | Distribution | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.l.t.0 | Relay | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.l.t.2 | Relay | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.l.t.3 | Relay | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.m.d.0 | Sectionalizer | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.m.d.2 | Sectionalizer | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.m.d.3 | Sectionalizer | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.m.t.0 | Sectionalizer | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.m.t.2 | Sectionalizer | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.m.t.3 | Sectionalizer | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.n.d.0 | Splice | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.n.d.2 | Splice | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.n.d.3 | Splice | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.n.t.0 | Splice | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.n.t.2 | Splice | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.n.t.3 | Splice | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.o.d.0 | Switch | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.4 | 0.4 | 0.4 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.o.d.2 | Switch | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.o.d.3 | Switch | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.o.t.0 | Switch | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.o.t.2 | Switch | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.o.t.3 | Switch | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.p.d.0 | Tap | Distribution | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for distribution wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.p.d.2 | Tap | Distribution | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for distribution wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.p.d.3 | Tap | Distribution | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for distribution wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.p.t.0 | Tap | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.p.t.2 | Tap | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.p.t.3 | Tap | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.q.d.0 | Tie wire | Distribution | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for distribution wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.q.d.2 | Tie wire | Distribution | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for distribution wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.q.d.3 | Tie wire | Distribution | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for distribution wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.q.t.0 | Tie wire | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.q.t.2 | Tie wire | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.q.t.3 | Tie wire | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.r.d.0 | Transformer | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.r.d.2 | Transformer | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.r.d.3 | Transformer | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.19 | 0.18 | 0.166 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.r.t.0 | Transformer | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.r.t.2 | Transformer | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.r.t.3 | Transformer | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.s.d.0 | Voltage regulator/booster | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.s.d.2 | Voltage regulator/booster | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.s.d.3 | Voltage regulator/booster | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.s.t.0 | Voltage regulator/booster | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.s.t.2 | Voltage regulator/booster | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.s.t.3 | Voltage regulator/booster | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 4. Equipment / facility failure or damage | 4.t.d.0 | Unknown | Distribution | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown wire-down events in the equipment failure category. If no damage is found the risk event is categorized as "Unknown"
Wire down event | 4. Equipment / facility failure or damage | 4.t.d.2 | Unknown | Distribution | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown wire-down events in the equipment failure category. If no damage is found the risk event is categorized as "Unknown"
Wire down event | 4. Equipment / facility failure or damage | 4.t.d.3 | Unknown | Distribution | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown wire-down events in the equipment failure category. If no damage is found the risk event is categorized as "Unknown"
Wire down event | 4. Equipment / facility failure or damage | 4.t.t.0 | Unknown | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown wire-down events in the equipment failure category. If no damage is found the risk event is categorized as "Unknown"
Wire down event | 4. Equipment / facility failure or damage | 4.t.t.2 | Unknown | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown wire-down events in the equipment failure category. If no damage is found the risk event is categorized as "Unknown"
Wire down event | 4. Equipment / facility failure or damage | 4.t.t.3 | Unknown | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown wire-down events in the equipment failure category. If no damage is found the risk event is categorized as "Unknown"
Wire down event | 4. Equipment / facility failure or damage | 4.u.d.0 | Other | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.4 | 0.4 | 0.4 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.u.d.2 | Other | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.126 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.u.d.3 | Other | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.u.t.0 | Other | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.u.t.2 | Other | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.2 | 0.2 | 0.2 | # risk events (excluding ignitions)
Wire down event | 4. Equipment / facility failure or damage | 4.u.t.3 | Other | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 5. Wire-to-wire contact | 5.a.d.0 | Wire-to-wire contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 5. Wire-to-wire contact | 5.a.d.2 | Wire-to-wire contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 5. Wire-to-wire contact | 5.a.d.3 | Wire-to-wire contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 5. Wire-to-wire contact | 5.a.t.0 | Wire-to-wire contact | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 5. Wire-to-wire contact | 5.a.t.2 | Wire-to-wire contact | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 5. Wire-to-wire contact | 5.a.t.3 | Wire-to-wire contact | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 6. Contamination | 6.a.d.0 | Contamination | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.2 | 0.2 | 0.2 | # risk events (excluding ignitions)
Wire down event | 6. Contamination | 6.a.d.2 | Contamination | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 6. Contamination | 6.a.d.3 | Contamination | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 6. Contamination | 6.a.t.0 | Contamination | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 6. Contamination | 6.a.t.2 | Contamination | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 6. Contamination | 6.a.t.3 | Contamination | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 7. Vandalism/theft | 7.a.d.0 | Vandalism/theft | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.6 | 0.6 | 0.6 | # risk events (excluding ignitions)
Wire down event | 7. Vandalism/theft | 7.a.d.2 | Vandalism/theft | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.199 | 0.194 | 0.184 | # risk events (excluding ignitions)
Wire down event | 7. Vandalism/theft | 7.a.d.3 | Vandalism/theft | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.58 | 0.554 | 0.517 | # risk events (excluding ignitions)
Wire down event | 7. Vandalism/theft | 7.a.t.0 | Vandalism/theft | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 7. Vandalism/theft | 7.a.t.2 | Vandalism/theft | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 7. Vandalism/theft | 7.a.t.3 | Vandalism/theft | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 8. Lightning | 8.a.d.0 | Lightning | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 1.2 | 1.2 | 1.2 | # risk events (excluding ignitions)
Wire down event | 8. Lightning | 8.a.d.2 | Lightning | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.994 | 0.97 | 0.922 | # risk events (excluding ignitions)
Wire down event | 8. Lightning | 8.a.d.3 | Lightning | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.193 | 0.185 | 0.172 | # risk events (excluding ignitions)
Wire down event | 8. Lightning | 8.a.t.0 | Lightning | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 8. Lightning | 8.a.t.2 | Lightning | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 8. Lightning | 8.a.t.3 | Lightning | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 9. Unknown | 9.a.d.0 | Unknown | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 9. Unknown | 9.a.d.2 | Unknown | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 9. Unknown | 9.a.d.3 | Unknown | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Wire down event | 9. Unknown | 9.a.t.0 | Unknown | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 9. Unknown | 9.a.t.2 | Unknown | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 9. Unknown | 9.a.t.3 | Unknown | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 10. Other | 10.a.d.0 | All Other | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 2; Actual number of risk events Q2: 2; Actual number of risk events Q3: 1; Actual number of risk events Q4: 1 | 0.8 | 0.8 | 0.8 | # risk events (excluding ignitions)
Wire down event | 10. Other | 10.a.d.2 | All Other | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.398 | 0.388 | 0.369 | # risk events (excluding ignitions)
Wire down event | 10. Other | 10.a.d.3 | All Other | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.58 | 0.554 | 0.517 | # risk events (excluding ignitions)
Wire down event | 10. Other | 10.a.t.0 | All Other | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 10. Other | 10.a.t.2 | All Other | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Wire down event | 10. Other | 10.a.t.3 | All Other | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track this driver for transmission wire-down events
Unplanned Outage | 11. Dig-in | 11.a.d.0 | Dig-in | Distribution | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Unplanned Outage | 11. Dig-in | 11.a.d.2 | Dig-in | Distribution | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Unplanned Outage | 11. Dig-in | 11.a.d.3 | Dig-in | Distribution | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Unplanned Outage | 11. Dig-in | 11.a.t.0 | Dig-in | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Unplanned Outage | 11. Dig-in | 11.a.t.2 | Dig-in | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Unplanned Outage | 11. Dig-in | 11.a.t.3 | Dig-in | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Unplanned Outage | 12. Fire | 12.a.d.0 | Fire | Distribution | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Unplanned Outage | 12. Fire | 12.a.d.2 | Fire | Distribution | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Unplanned Outage | 12. Fire | 12.a.d.3 | Fire | Distribution | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Unplanned Outage | 12. Fire | 12.a.t.0 | Fire | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Unplanned Outage | 12. Fire | 12.a.t.2 | Fire | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Unplanned Outage | 12. Fire | 12.a.t.3 | Fire | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Unplanned Outage | 13. Object contact | 13.a.d.0 | Animal contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 11; Actual number of risk events Q2: 6; Actual number of risk events Q3: 13; Actual number of risk events Q4: 10; Actual number of risk events Q1: 6; Actual number of risk events Q2: 11; Actual number of risk events Q3: 11; Actual number of risk events Q4: 7 | 34.8 | 34.8 | 34.8 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.a.d.2 | Animal contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 12; Actual number of risk events Q2: 11; Actual number of risk events Q3: 10; Actual number of risk events Q4: 4; Actual number of risk events Q1: 6; Actual number of risk events Q2: 6; Actual number of risk events Q3: 3; Actual number of risk events Q4: 2 | 25.874 | 24.877 | 23.493 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.a.d.3 | Animal contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 8; Actual number of risk events Q2: 5; Actual number of risk events Q3: 7; Actual number of risk events Q4: 3; Actual number of risk events Q1: 3; Actual number of risk events Q2: 5; Actual number of risk events Q3: 7; Actual number of risk events Q4: 3 | 22.057 | 20.873 | 19.24 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.a.t.0 | Animal contact | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 2; Actual number of risk events Q1: 0; Actual number of risk events Q2: 3; Actual number of risk events Q3: 0; Actual number of risk events Q4: 2 | 1.6 | 1.6 | 1.6 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.a.t.2 | Animal contact | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 3; Actual number of risk events Q3: 3; Actual number of risk events Q4: 0 | 1.978 | 1.936 | 1.936 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.a.t.3 | Animal contact | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.b.d.0 | Balloon contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 27; Actual number of risk events Q2: 36; Actual number of risk events Q3: 13; Actual number of risk events Q4: 10; Actual number of risk events Q1: 16; Actual number of risk events Q2: 28; Actual number of risk events Q3: 11; Actual number of risk events Q4: 16 | 100.4 | 100.4 | 100.4 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.b.d.2 | Balloon contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 4; Actual number of risk events Q4: 1; Actual number of risk events Q1: 1; Actual number of risk events Q2: 3; Actual number of risk events Q3: 1; Actual number of risk events Q4: 1 | 9.309 | 8.978 | 8.482 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.b.d.3 | Balloon contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 1; Actual number of risk events Q4: 1; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 4.183 | 3.959 | 3.649 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.b.t.0 | Balloon contact | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 7; Actual number of risk events Q3: 2; Actual number of risk events Q4: 2; Actual number of risk events Q1: 2; Actual number of risk events Q2: 3; Actual number of risk events Q3: 0; Actual number of risk events Q4: 2 | 14.2 | 14.2 | 14.2 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.b.t.2 | Balloon contact | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 3; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 3; Actual number of risk events Q2: 3; Actual number of risk events Q3: 3; Actual number of risk events Q4: 1 | 6.526 | 6.389 | 6.389 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.b.t.3 | Balloon contact | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.2 | 0.2 | 0.2 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.c.d.0 | Land vehicle contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 23; Actual number of risk events Q2: 14; Actual number of risk events Q3: 15; Actual number of risk events Q4: 20; Actual number of risk events Q1: 14; Actual number of risk events Q2: 17; Actual number of risk events Q3: 17; Actual number of risk events Q4: 14 | 62.8 | 62.8 | 62.8 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.c.d.2 | Land vehicle contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 7; Actual number of risk events Q2: 4; Actual number of risk events Q3: 7; Actual number of risk events Q4: 8; Actual number of risk events Q1: 8; Actual number of risk events Q2: 7; Actual number of risk events Q3: 8; Actual number of risk events Q4: 10 | 27.643 | 26.968 | 25.63 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.c.d.3 | Land vehicle contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 5; Actual number of risk events Q3: 0; Actual number of risk events Q4: 3; Actual number of risk events Q1: 4; Actual number of risk events Q2: 3; Actual number of risk events Q3: 6; Actual number of risk events Q4: 3 | 12.76 | 12.199 | 11.382 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.c.t.0 | Land vehicle contact | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 2; Actual number of risk events Q4: 2 | 1.4 | 1.4 | 1.4 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.c.t.2 | Land vehicle contact | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.4 | 0.4 | 0.4 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.c.t.3 | Land vehicle contact | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.2 | 0.2 | 0.2 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.d.d.0 | Aircraft vehicle contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.d.d.2 | Aircraft vehicle contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.d.d.3 | Aircraft vehicle contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.193 | 0.185 | 0.172 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.d.t.0 | Aircraft vehicle contact | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.d.t.2 | Aircraft vehicle contact | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.d.t.3 | Aircraft vehicle contact | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.e.d.0 | 3rd party contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 1; Actual number of risk events Q3: 1; Actual number of risk events Q4: 1; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 1 | 1.4 | 1.4 | 1.4 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.e.d.2 | 3rd party contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 1; Actual number of risk events Q3: 1; Actual number of risk events Q4: 1; Actual number of risk events Q1: 1; Actual number of risk events Q2: 1; Actual number of risk events Q3: 1; Actual number of risk events Q4: 1 | 1.2 | 1.2 | 1.2 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.e.d.3 | 3rd party contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 2.8 | 2.8 | 2.8 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.e.t.0 | 3rd party contact | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.e.t.2 | 3rd party contact | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.2 | 0.2 | 0.2 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.e.t.3 | 3rd party contact | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.f.d.0 | Other | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 2; Actual number of risk events Q3: 7; Actual number of risk events Q4: 3; Actual number of risk events Q1: 6; Actual number of risk events Q2: 4; Actual number of risk events Q3: 2; Actual number of risk events Q4: 4 | 23.8 | 23.8 | 23.8 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.f.d.2 | Other | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 1; Actual number of risk events Q3: 1; Actual number of risk events Q4: 2; Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 2 | 8.698 | 8.449 | 7.93 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.f.d.3 | Other | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 3; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 2 | 4.564 | 4.319 | 3.981 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.f.t.0 | Other | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 1 | 1 | 1 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.f.t.2 | Other | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.196 | 0.187 | 0.187 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.f.t.3 | Other | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.2 | 0.2 | 0.2 | # risk events (excluding ignitions)
Unplanned Outage | 13. Object contact | 13.g.d.0 | Unknown | Distribution | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown risk events in the contact from object category. If no damage is found the risk event is categorized as "Unknown"
Unplanned Outage | 13. Object contact | 13.g.d.2 | Unknown | Distribution | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown risk events in the contact from object category. If no damage is found the risk event is categorized as "Unknown"
Unplanned Outage | 13. Object contact | 13.g.d.3 | Unknown | Distribution | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown risk events in the contact from object category. If no damage is found the risk event is categorized as "Unknown"
Unplanned Outage | 13. Object contact | 13.g.t.0 | Unknown | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown risk events in the contact from object category. If no damage is found the risk event is categorized as "Unknown"
Unplanned Outage | 13. Object contact | 13.g.t.2 | Unknown | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown risk events in the contact from object category. If no damage is found the risk event is categorized as "Unknown"
Unplanned Outage | 13. Object contact | 13.g.t.3 | Unknown | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown risk events in the contact from object category. If no damage is found the risk event is categorized as "Unknown"
Unplanned Outage | 14. Vegetation contact | 14.a.d.0 | Vegetation contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 5; Actual number of risk events Q2: 1; Actual number of risk events Q3: 8; Actual number of risk events Q4: 3; Actual number of risk events Q1: 32; Actual number of risk events Q2: 3; Actual number of risk events Q3: 10; Actual number of risk events Q4: 5 | 29.6 | 29.6 | 29.6 | # risk events (excluding ignitions)
Unplanned Outage | 14. Vegetation contact | 14.a.d.2 | Vegetation contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 1; Actual number of risk events Q3: 4; Actual number of risk events Q4: 2; Actual number of risk events Q1: 6; Actual number of risk events Q2: 0; Actual number of risk events Q3: 3; Actual number of risk events Q4: 0 | 5.35 | 4.7 | 4.05 | # risk events (excluding ignitions)
Unplanned Outage | 14. Vegetation contact | 14.a.d.3 | Vegetation contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 1; Actual number of risk events Q3: 2; Actual number of risk events Q4: 3; Actual number of risk events Q1: 10; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0 | 4.11 | 3.82 | 3.52 | # risk events (excluding ignitions)
Unplanned Outage | 14. Vegetation contact | 14.a.t.0 | Vegetation contact | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.2 | 0.2 | 0.2 | # risk events (excluding ignitions)
Unplanned Outage | 14. Vegetation contact | 14.a.t.2 | Vegetation contact | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 14. Vegetation contact | 14.a.t.3 | Vegetation contact | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.a.d.0 | Anchor/guy | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.6 | 0.6 | 0.6 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.a.d.2 | Anchor/guy | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1 | 0.79 | 0.76 | 0.717 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.a.d.3 | Anchor/guy | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.a.t.0 | Anchor/guy | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.2 | 0.2 | 0.2 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.a.t.2 | Anchor/guy | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.a.t.3 | Anchor/guy | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.b.d.0 | Capacitor bank | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 3; Actual number of risk events Q2: 5; Actual number of risk events Q3: 1; Actual number of risk events Q4: 2; Actual number of risk events Q1: 4; Actual number of risk events Q2: 1; Actual number of risk events Q3: 3; Actual number of risk events Q4: 1 | 9 | 9 | 9 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.b.d.2 | Capacitor bank | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.87 | 0.475 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.b.d.3 | Capacitor bank | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.19 | 0.18 | 0.166 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.b.t.0 | Capacitor bank | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
Unplanned Outage | 15. Equipment / facility failure or damage | 15.b.t.2 | Capacitor bank | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
Unplanned Outage | 15. Equipment / facility failure or damage | 15.b.t.3 | Capacitor bank | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
Unplanned Outage | 15. Equipment / facility failure or damage | 15.c.d.0 | Conductor | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 5; Actual number of risk events Q2: 6; Actual number of risk events Q3: 4; Actual number of risk events Q4: 5; Actual number of risk events Q1: 23; Actual number of risk events Q2: 5; Actual number of risk events Q3: 3; Actual number of risk events Q4: 1 | 26.4 | 26.4 | 26.4 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.c.d.2 | Conductor | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 3; Actual number of risk events Q2: 6; Actual number of risk events Q3: 2; Actual number of risk events Q4: 3; Actual number of risk events Q1: 5; Actual number of risk events Q2: 3; Actual number of risk events Q3: 1; Actual number of risk events Q4: 5 | 10.27 | 9.875 | 9.326 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.c.d.3 | Conductor | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 5; Actual number of risk events Q2: 1; Actual number of risk events Q3: 4; Actual number of risk events Q4: 1; Actual number of risk events Q1: 3; Actual number of risk events Q2: 0; Actual number of risk events Q3: 2; Actual number of risk events Q4: 1 | 13.691 | 12.956 | 11.942 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.c.t.0 | Conductor | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 2; Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1 | 0.6 | 0.6 | 0.6 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.c.t.2 | Conductor | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 2; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.96 | 0.884 | 0.884 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.c.t.3 | Conductor | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.2 | 0.2 | 0.2 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.d.d.0 | Connection device | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 5; Actual number of risk events Q2: 11; Actual number of risk events Q3: 9; Actual number of risk events Q4: 13; Actual number of risk events Q1: 12; Actual number of risk events Q2: 12; Actual number of risk events Q3: 3; Actual number of risk events Q4: 3 | 36.4 | 36.4 | 36.4 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.d.d.2 | Connection device | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 3; Actual number of risk events Q2: 0; Actual number of risk events Q3: 3; Actual number of risk events Q4: 3; Actual number of risk events Q1: 3; Actual number of risk events Q2: 3; Actual number of risk events Q3: 3; Actual number of risk events Q4: 2 | 10.665 | 10.255 | 9.684 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.d.d.3 | Connection device | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 4; Actual number of risk events Q3: 2; Actual number of risk events Q4: 1; Actual number of risk events Q1: 5; Actual number of risk events Q2: 2; Actual number of risk events Q3: 1; Actual number of risk events Q4: 2 | 11.219 | 10.616 | 9.786 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.d.t.0 | Connection device | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.d.t.2 | Connection device | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.384 | 0.354 | 0.354 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.d.t.3 | Connection device | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.e.d.0 | Crossarm | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 10; Actual number of risk events Q2: 7; Actual number of risk events Q3: 6; Actual number of risk events Q4: 10; Actual number of risk events Q1: 9; Actual number of risk events Q2: 2; Actual number of risk events Q3: 5; Actual number of risk events Q4: 3 | 18.8 | 18.8 | 18.8 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.e.d.2 | Crossarm | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 4; Actual number of risk events Q2: 5; Actual number of risk events Q3: 5; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 3; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 5.333 | 5.127 | 4.842 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.e.d.3 | Crossarm | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 6; Actual number of risk events Q2: 1; Actual number of risk events Q3: 2; Actual number of risk events Q4: 1; Actual number of risk events Q1: 2; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 2 | 6.465 | 6.118 | 5.639 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.e.t.0 | Crossarm | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 2; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.e.t.2 | Crossarm | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.e.t.3 | Crossarm | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.f.d.0 | Fuse | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 4; Actual number of risk events Q2: 2; Actual number of risk events Q3: 4; Actual number of risk events Q4: 2; Actual number of risk events Q1: 11; Actual number of risk events Q2: 4; Actual number of risk events Q3: 4; Actual number of risk events Q4: 4 | 15.8 | 15.8 | 15.8 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.f.d.2 | Fuse | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0 | 4.543 | 4.368 | 4.125 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.f.d.3 | Fuse | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 1; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0 | 4.754 | 4.499 | 4.146 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.f.t.0 | Fuse | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
Unplanned Outage | 15. Equipment / facility failure or damage | 15.f.t.2 | Fuse | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
Unplanned Outage | 15. Equipment / facility failure or damage | 15.f.t.3 | Fuse | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
Unplanned Outage | 15. Equipment / facility failure or damage | 15.g.d.0 | Cutout | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 12; Actual number of risk events Q2: 8; Actual number of risk events Q3: 6; Actual number of risk events Q4: 6; Actual number of risk events Q1: 7; Actual number of risk events Q2: 5; Actual number of risk events Q3: 8; Actual number of risk events Q4: 5 | 29.4 | 29.4 | 29.4 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.g.d.2 | Cutout | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 5.4 | 5.4 | 5.4 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.g.d.3 | Cutout | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 3 | 3 | 3 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.g.t.0 | Cutout | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
Unplanned Outage | 15. Equipment / facility failure or damage | 15.g.t.2 | Cutout | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
Unplanned Outage | 15. Equipment / facility failure or damage | 15.g.t.3 | Cutout | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
Unplanned Outage | 15. Equipment / facility failure or damage | 15.h.d.0 | Insulator and bushing | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 1; Actual number of risk events Q1: 3; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 5.2 | 5.2 | 5.2 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.h.d.2 | Insulator and bushing | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 2; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 2.173 | 2.089 | 1.973 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.h.d.3 | Insulator and bushing | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 1; Actual number of risk events Q4: 1; Actual number of risk events Q1: 2; Actual number of risk events Q2: 1; Actual number of risk events Q3: 2; Actual number of risk events Q4: 0 | 0.57 | 0.54 | 0.498 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.h.t.0 | Insulator and bushing | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.2 | 0.2 | 0.2 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.h.t.2 | Insulator and bushing | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1 | 0.192 | 0.177 | 0.177 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.h.t.3 | Insulator and bushing | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.i.d.0 | Lightning arrestor | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 1; Actual number of risk events Q3: 2; Actual number of risk events Q4: 5; Actual number of risk events Q1: 2; Actual number of risk events Q2: 2; Actual number of risk events Q3: 7; Actual number of risk events Q4: 3 | 15 | 15 | 15 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.i.d.2 | Lightning arrestor | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 2; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 2 | 5.333 | 5.127 | 4.842 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.i.d.3 | Lightning arrestor | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 2; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 2; Actual number of risk events Q4: 1 | 3.803 | 3.599 | 3.317 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.i.t.0 | Lightning arrestor | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.i.t.2 | Lightning arrestor | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.i.t.3 | Lightning arrestor | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.4 | 0.4 | 0.4 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.j.d.0 | Pole | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 4; Actual number of risk events Q2: 7; Actual number of risk events Q3: 5; Actual number of risk events Q4: 5; Actual number of risk events Q1: 10; Actual number of risk events Q2: 8; Actual number of risk events Q3: 7; Actual number of risk events Q4: 6 | 18.8 | 18.8 | 18.8 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.j.d.2 | Pole | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 7; Actual number of risk events Q2: 6; Actual number of risk events Q3: 3; Actual number of risk events Q4: 3; Actual number of risk events Q1: 6; Actual number of risk events Q2: 3; Actual number of risk events Q3: 3; Actual number of risk events Q4: 0 | 12.443 | 11.964 | 11.298 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.j.d.3 | Pole | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 2; Actual number of risk events Q2: 2; Actual number of risk events Q3: 7; Actual number of risk events Q4: 2; Actual number of risk events Q1: 1; Actual number of risk events Q2: 2; Actual number of risk events Q3: 4; Actual number of risk events Q4: 1 | 13.5 | 12.776 | 11.776 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.j.t.0 | Pole | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 3; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 1.2 | 1.2 | 1.2 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.j.t.2 | Pole | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.192 | 0.177 | 0.177 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.j.t.3 | Pole | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.k.d.0 | Recloser | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1 | 0.6 | 0.6 | 0.6 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.k.d.2 | Recloser | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.79 | 0.76 | 0.717 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.k.d.3 | Recloser | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.391 | 0.375 | 0.354 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.k.t.0 | Recloser | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
Unplanned Outage | 15. Equipment / facility failure or damage | 15.k.t.2 | Recloser | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
Unplanned Outage | 15. Equipment / facility failure or damage | 15.k.t.3 | Recloser | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
Unplanned Outage | 15. Equipment / facility failure or damage | 15.l.d.0 | Relay | Distribution | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver - relays are located within other pieces of equipment (sectionalizers/reclosers/etc.)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.l.d.2 | Relay | Distribution | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver - relays are located within other pieces of equipment (sectionalizers/reclosers/etc.)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.l.d.3 | Relay | Distribution | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver - relays are located within other pieces of equipment (sectionalizers/reclosers/etc.)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.l.t.0 | Relay | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
Unplanned Outage | 15. Equipment / facility failure or damage | 15.l.t.2 | Relay | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
Unplanned Outage | 15. Equipment / facility failure or damage | 15.l.t.3 | Relay | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
Unplanned Outage | 15. Equipment / facility failure or damage | 15.m.d.0 | Sectionalizer | Distribution | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
Unplanned Outage | 15. Equipment / facility failure or damage | 15.m.d.2 | Sectionalizer | Distribution | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
Unplanned Outage | 15. Equipment / facility failure or damage | 15.m.d.3 | Sectionalizer | Distribution | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
Unplanned Outage | 15. Equipment / facility failure or damage | 15.m.t.0 | Sectionalizer | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
Unplanned Outage | 15. Equipment / facility failure or damage | 15.m.t.2 | Sectionalizer | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
Unplanned Outage | 15. Equipment / facility failure or damage | 15.m.t.3 | Sectionalizer | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
Unplanned Outage | 15. Equipment / facility failure or damage | 15.n.d.0 | Splice | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.n.d.2 | Splice | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.n.d.3 | Splice | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.n.t.0 | Splice | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
Unplanned Outage | 15. Equipment / facility failure or damage | 15.n.t.2 | Splice | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
Unplanned Outage | 15. Equipment / facility failure or damage | 15.n.t.3 | Splice | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
Unplanned Outage | 15. Equipment / facility failure or damage | 15.o.d.0 | Switch | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 2; Actual number of risk events Q3: 1; Actual number of risk events Q4: 6; Actual number of risk events Q1: 7; Actual number of risk events Q2: 2; Actual number of risk events Q3: 4; Actual number of risk events Q4: 3 | 12.4 | 12.4 | 12.4 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.o.d.2 | Switch | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 1.975 | 1.899 | 1.793 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.o.d.3 | Switch | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.19 | 0.18 | 0.166 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.o.t.0 | Switch | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1 | 0.2 | 0.2 | 0.2 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.o.t.2 | Switch | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.593 | 0.581 | 0.581 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.o.t.3 | Switch | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.p.d.0 | Tap | Distribution | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
Unplanned Outage | 15. Equipment / facility failure or damage | 15.p.d.2 | Tap | Distribution | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
Unplanned Outage | 15. Equipment / facility failure or damage | 15.p.d.3 | Tap | Distribution | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
Unplanned Outage | 15. Equipment / facility failure or damage | 15.p.t.0 | Tap | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
Unplanned Outage | 15. Equipment / facility failure or damage | 15.p.t.2 | Tap | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
Unplanned Outage | 15. Equipment / facility failure or damage | 15.p.t.3 | Tap | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
Unplanned Outage | 15. Equipment / facility failure or damage | 15.q.d.0 | Tie wire | Distribution | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
Unplanned Outage | 15. Equipment / facility failure or damage | 15.q.d.2 | Tie wire | Distribution | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
Unplanned Outage | 15. Equipment / facility failure or damage | 15.q.d.3 | Tie wire | Distribution | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
Unplanned Outage | 15. Equipment / facility failure or damage | 15.q.t.0 | Tie wire | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
Unplanned Outage | 15. Equipment / facility failure or damage | 15.q.t.2 | Tie wire | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
Unplanned Outage | 15. Equipment / facility failure or damage | 15.q.t.3 | Tie wire | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not currently track this driver
Unplanned Outage | 15. Equipment / facility failure or damage | 15.r.d.0 | Transformer | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 6; Actual number of risk events Q2: 6; Actual number of risk events Q3: 7; Actual number of risk events Q4: 5; Actual number of risk events Q1: 12; Actual number of risk events Q2: 4; Actual number of risk events Q3: 8; Actual number of risk events Q4: 0 | 19 | 19 | 19 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.r.d.2 | Transformer | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 5; Actual number of risk events Q2: 1; Actual number of risk events Q3: 3; Actual number of risk events Q4: 2; Actual number of risk events Q1: 4; Actual number of risk events Q2: 0; Actual number of risk events Q3: 3; Actual number of risk events Q4: 5 | 8.098 | 7.786 | 7.353 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.r.d.3 | Transformer | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 3; Actual number of risk events Q4: 4; Actual number of risk events Q1: 3; Actual number of risk events Q2: 0; Actual number of risk events Q3: 3; Actual number of risk events Q4: 0 | 7.606 | 7.198 | 6.634 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.r.t.0 | Transformer | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.r.t.2 | Transformer | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.r.t.3 | Transformer | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.s.d.0 | Voltage regulator/booster | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.2 | 0.2 | 0.2 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.s.d.2 | Voltage regulator/booster | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.988 | 0.95 | 0.897 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.s.d.3 | Voltage regulator/booster | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.s.t.0 | Voltage regulator/booster | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
Unplanned Outage | 15. Equipment / facility failure or damage | 15.s.t.2 | Voltage regulator/booster | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
Unplanned Outage | 15. Equipment / facility failure or damage | 15.s.t.3 | Voltage regulator/booster | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E's transmission lines do not contain this equipment
Unplanned Outage | 15. Equipment / facility failure or damage | 15.t.d.0 | Unknown | Distribution | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown risk events within equipment failure. If no damage is found the risk event is categorized as "Unknown"
Unplanned Outage | 15. Equipment / facility failure or damage | 15.t.d.2 | Unknown | Distribution | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown risk events within equipment failure. If no damage is found the risk event is categorized as "Unknown"
Unplanned Outage | 15. Equipment / facility failure or damage | 15.t.d.3 | Unknown | Distribution | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown risk events within equipment failure. If no damage is found the risk event is categorized as "Unknown"
Unplanned Outage | 15. Equipment / facility failure or damage | 15.t.t.0 | Unknown | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown risk events within equipment failure. If no damage is found the risk event is categorized as "Unknown"
Unplanned Outage | 15. Equipment / facility failure or damage | 15.t.t.2 | Unknown | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown risk events within equipment failure. If no damage is found the risk event is categorized as "Unknown"
Unplanned Outage | 15. Equipment / facility failure or damage | 15.t.t.3 | Unknown | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not track unkown risk events within equipment failure. If no damage is found the risk event is categorized as "Unknown"
Unplanned Outage | 15. Equipment / facility failure or damage | 15.u.d.0 | Other | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.4 | 0.4 | 0.4 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.u.d.2 | Other | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.063 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.u.d.3 | Other | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.307 | 0.091 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.u.t.0 | Other | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.u.t.2 | Other | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 1; Actual number of risk events Q1: 2; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.384 | 0.354 | 0.354 | # risk events (excluding ignitions)
Unplanned Outage | 15. Equipment / facility failure or damage | 15.u.t.3 | Other | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 16. Wire-to-wire contact | 16.a.d.0 | Wire-to-wire contact | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 3; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1; Actual number of risk events Q1: 3; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 1.4 | 1.4 | 1.4 | # risk events (excluding ignitions)
Unplanned Outage | 16. Wire-to-wire contact | 16.a.d.2 | Wire-to-wire contact | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 1.383 | 1.329 | 1.255 | # risk events (excluding ignitions)
Unplanned Outage | 16. Wire-to-wire contact | 16.a.d.3 | Wire-to-wire contact | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0; Actual number of risk events Q1: 2; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.38 | 0.36 | 0.332 | # risk events (excluding ignitions)
Unplanned Outage | 16. Wire-to-wire contact | 16.a.t.0 | Wire-to-wire contact | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 16. Wire-to-wire contact | 16.a.t.2 | Wire-to-wire contact | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 16. Wire-to-wire contact | 16.a.t.3 | Wire-to-wire contact | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 17. Contamination | 17.a.d.0 | Contamination | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 3; Actual number of risk events Q4: 1; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0 | 1.2 | 1.2 | 1.2 | # risk events (excluding ignitions)
Unplanned Outage | 17. Contamination | 17.a.d.2 | Contamination | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.198 | 0.191 | 0.18 | # risk events (excluding ignitions)
Unplanned Outage | 17. Contamination | 17.a.d.3 | Contamination | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 17. Contamination | 17.a.t.0 | Contamination | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 3; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.8 | 0.8 | 0.8 | # risk events (excluding ignitions)
Unplanned Outage | 17. Contamination | 17.a.t.2 | Contamination | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.194 | 0.183 | 0.183 | # risk events (excluding ignitions)
Unplanned Outage | 17. Contamination | 17.a.t.3 | Contamination | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 18. Vandalism/theft | 18.a.d.0 | Vandalism/theft | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 2; Actual number of risk events Q3: 1; Actual number of risk events Q4: 1 | 1.4 | 1.4 | 1.4 | # risk events (excluding ignitions)
Unplanned Outage | 18. Vandalism/theft | 18.a.d.2 | Vandalism/theft | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.994 | 0.97 | 0.922 | # risk events (excluding ignitions)
Unplanned Outage | 18. Vandalism/theft | 18.a.d.3 | Vandalism/theft | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 1.16 | 1.109 | 1.035 | # risk events (excluding ignitions)
Unplanned Outage | 18. Vandalism/theft | 18.a.t.0 | Vandalism/theft | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 18. Vandalism/theft | 18.a.t.2 | Vandalism/theft | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 18. Vandalism/theft | 18.a.t.3 | Vandalism/theft | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 19. Lightning | 19.a.d.0 | Lightning | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 7; Actual number of risk events Q2: 1; Actual number of risk events Q3: 1; Actual number of risk events Q4: 8; Actual number of risk events Q1: 2; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 6 | 23.8 | 23.8 | 23.8 | # risk events (excluding ignitions)
Unplanned Outage | 19. Lightning | 19.a.d.2 | Lightning | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 2; Actual number of risk events Q3: 1; Actual number of risk events Q4: 3; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 3 | 14.12 | 13.775 | 13.091 | # risk events (excluding ignitions)
Unplanned Outage | 19. Lightning | 19.a.d.3 | Lightning | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 1; Actual number of risk events Q3: 2; Actual number of risk events Q4: 2; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 5 | 16.047 | 15.341 | 14.313 | # risk events (excluding ignitions)
Unplanned Outage | 19. Lightning | 19.a.t.0 | Lightning | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 4 | 4 | 4 | # risk events (excluding ignitions)
Unplanned Outage | 19. Lightning | 19.a.t.2 | Lightning | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1 | 1 | 1 | 1 | # risk events (excluding ignitions)
Unplanned Outage | 19. Lightning | 19.a.t.3 | Lightning | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 2.6 | 2.6 | 2.6 | # risk events (excluding ignitions)
Unplanned Outage | 20. Government agency request | 20.a.d.0 | Government agency request | Distribution | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Unplanned Outage | 20. Government agency request | 20.a.d.2 | Government agency request | Distribution | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Unplanned Outage | 20. Government agency request | 20.a.d.3 | Government agency request | Distribution | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Unplanned Outage | 20. Government agency request | 20.a.t.0 | Government agency request | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Unplanned Outage | 20. Government agency request | 20.a.t.2 | Government agency request | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Unplanned Outage | 20. Government agency request | 20.a.t.3 | Government agency request | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Unplanned Outage | 21. Customer request | 21.a.d.0 | Customer request | Distribution | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Unplanned Outage | 21. Customer request | 21.a.d.2 | Customer request | Distribution | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Unplanned Outage | 21. Customer request | 21.a.d.3 | Customer request | Distribution | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Unplanned Outage | 21. Customer request | 21.a.t.0 | Customer request | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Unplanned Outage | 21. Customer request | 21.a.t.2 | Customer request | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Unplanned Outage | 21. Customer request | 21.a.t.3 | Customer request | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Unplanned Outage | 22. Emergency repairs | 22.a.d.0 | Emergency repairs | Distribution | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Unplanned Outage | 22. Emergency repairs | 22.a.d.2 | Emergency repairs | Distribution | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Unplanned Outage | 22. Emergency repairs | 22.a.d.3 | Emergency repairs | Distribution | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Unplanned Outage | 22. Emergency repairs | 22.a.t.0 | Emergency repairs | Transmission | Non-HFTD | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Unplanned Outage | 22. Emergency repairs | 22.a.t.2 | Emergency repairs | Transmission | HFTD Tier 2 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Unplanned Outage | 22. Emergency repairs | 22.a.t.3 | Emergency repairs | Transmission | HFTD Tier 3 | No | [19 empty] | # risk events (excluding ignitions) |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
Unplanned Outage | 23. Unknown | 23.a.d.0 | Unknown | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 25; Actual number of risk events Q2: 23; Actual number of risk events Q3: 35; Actual number of risk events Q4: 25; Actual number of risk events Q1: 43; Actual number of risk events Q2: 26; Actual number of risk events Q3: 26; Actual number of risk events Q4: 8 | 142.2 | 142.2 | 142.2 | # risk events (excluding ignitions)
Unplanned Outage | 23. Unknown | 23.a.d.2 | Unknown | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 10; Actual number of risk events Q2: 6; Actual number of risk events Q3: 11; Actual number of risk events Q4: 16; Actual number of risk events Q1: 20; Actual number of risk events Q2: 9; Actual number of risk events Q3: 16; Actual number of risk events Q4: 10 | 57.548 | 56.608 | 54.095 | # risk events (excluding ignitions)
Unplanned Outage | 23. Unknown | 23.a.d.3 | Unknown | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 11; Actual number of risk events Q2: 12; Actual number of risk events Q3: 16; Actual number of risk events Q4: 6; Actual number of risk events Q1: 17; Actual number of risk events Q2: 8; Actual number of risk events Q3: 12; Actual number of risk events Q4: 6 | 68.589 | 66.213 | 62.484 | # risk events (excluding ignitions)
Unplanned Outage | 23. Unknown | 23.a.t.0 | Unknown | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 1; Actual number of risk events Q3: 1; Actual number of risk events Q4: 0 | 3.2 | 3.2 | 3.2 | # risk events (excluding ignitions)
Unplanned Outage | 23. Unknown | 23.a.t.2 | Unknown | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 2; Actual number of risk events Q4: 1; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 1 | 3.646 | 3.359 | 3.359 | # risk events (excluding ignitions)
Unplanned Outage | 23. Unknown | 23.a.t.3 | Unknown | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0.4 | 0.4 | 0.4 | # risk events (excluding ignitions)
Unplanned Outage | 24. Other | 24.a.d.0 | All Other | Distribution | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 2; Actual number of risk events Q1: 2; Actual number of risk events Q2: 5; Actual number of risk events Q3: 5; Actual number of risk events Q4: 17 | 3.6 | 3.6 | 3.6 | # risk events (excluding ignitions)
Unplanned Outage | 24. Other | 24.a.d.2 | All Other | Distribution | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 2; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 1; Actual number of risk events Q4: 2 | 2.188 | 2.134 | 2.028 | # risk events (excluding ignitions)
Unplanned Outage | 24. Other | 24.a.d.3 | All Other | Distribution | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 2; Actual number of risk events Q4: 3 | 3.093 | 2.957 | 2.759 | # risk events (excluding ignitions)
Unplanned Outage | 24. Other | 24.a.t.0 | All Other | Transmission | Non-HFTD | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 1; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 1 | 1 | 1 | # risk events (excluding ignitions)
Unplanned Outage | 24. Other | 24.a.t.2 | All Other | Transmission | HFTD Tier 2 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 2; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)
Unplanned Outage | 24. Other | 24.a.t.3 | All Other | Transmission | HFTD Tier 3 | Yes | Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0; Actual number of risk events Q1: 0; Actual number of risk events Q2: 0; Actual number of risk events Q3: 0; Actual number of risk events Q4: 0 | 0 | 0 | 0 | # risk events (excluding ignitions)

## Table 6
Utility | SDG&E | Notes:
Table No. | 6 | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.
Date Modified | 2024-02-01 | Data from 2015 - 2021 should be actual numbers. 2022 and 2023 should be projected. In future submissions update projected numbers with actuals
[6 empty] | Actual number of ignitions | [15 empty] | Projected ignitions
Table 6: Ignition drivers | [5 empty] | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4
Metric type | # | Ignition driver | Line Type | HFTD Tier | Are ignitions tracked for ignition driver? (yes / no) | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | 2024 | 2024 | 2024 | 2024 | 2025 | 2025 | 2025 | 2025 | 2023 | 2024 | 2025 | Unit(s) | Comments | Blank Meaning
1. Dig-in | 1.a.d.0 | Dig-in | Distribution | Non-HFTD | No | [19 empty] | # ignitions |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
1. Dig-in | 1.a.d.2 | Dig-in | Distribution | HFTD Tier 2 | No | [19 empty] | # ignitions |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
1. Dig-in | 1.a.d.3 | Dig-in | Distribution | HFTD Tier 3 | No | [19 empty] | # ignitions |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
1. Dig-in | 1.a.t.0 | Dig-in | Transmission | Non-HFTD | No | [19 empty] | # ignitions |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
1. Dig-in | 1.a.t.2 | Dig-in | Transmission | HFTD Tier 2 | No | [19 empty] | # ignitions |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
1. Dig-in | 1.a.t.3 | Dig-in | Transmission | HFTD Tier 3 | No | [19 empty] | # ignitions |  | SDG&E does not consider this driver as a risk event - see comments in QDR cover letter
2. Contact from object | 2.a.d.0 | Animal contact | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.2 | 0.2 | 0.2 | # ignitions
2. Contact from object | 2.a.d.2 | Animal contact | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.4087 | 0.1556 | 0 | # ignitions
2. Contact from object | 2.a.d.3 | Animal contact | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 2; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 2; Actual number of ignitions Q4: 0 | 0.6871 | 0.4196 | 0.0491 | # ignitions
2. Contact from object | 2.a.t.0 | Animal contact | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
2. Contact from object | 2.a.t.2 | Animal contact | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.19922 | 0.19776 | 0.19776 | # ignitions
2. Contact from object | 2.a.t.3 | Animal contact | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.4 | 0.4 | 0.4 | # ignitions
2. Contact from object | 2.b.d.0 | Balloon contact | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 1.8 | 1.8 | 1.8 | # ignitions
2. Contact from object | 2.b.d.2 | Balloon contact | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.8095 | 0.5579 | 0.2603 | # ignitions
2. Contact from object | 2.b.d.3 | Balloon contact | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.6871 | 0.4196 | 0.0491 | # ignitions
2. Contact from object | 2.b.t.0 | Balloon contact | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 1 | 0.2 | 0.2 | 0.2 | # ignitions
2. Contact from object | 2.b.t.2 | Balloon contact | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 1; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.59922 | 0.59776 | 0.59776 | # ignitions
2. Contact from object | 2.b.t.3 | Balloon contact | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
2. Contact from object | 2.c.d.0 | Land vehicle contact | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.4 | 0.4 | 0.4 | # ignitions
2. Contact from object | 2.c.d.2 | Land vehicle contact | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 1.0576 | 0.9355 | 0.6934 | # ignitions
2. Contact from object | 2.c.d.3 | Land vehicle contact | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 0 | 0.3648 | 0.1386 | 0 | # ignitions
2. Contact from object | 2.c.t.0 | Land vehicle contact | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.4 | 0.4 | 0.4 | # ignitions
2. Contact from object | 2.c.t.2 | Land vehicle contact | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
2. Contact from object | 2.c.t.3 | Land vehicle contact | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.2 | 0.2 | 0.2 | # ignitions
2. Contact from object | 2.d.d.0 | Aircraft vehicle contact | Distribution | Non-HFTD | No | [19 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
2. Contact from object | 2.d.d.2 | Aircraft vehicle contact | Distribution | HFTD Tier 2 | No | [19 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
2. Contact from object | 2.d.d.3 | Aircraft vehicle contact | Distribution | HFTD Tier 3 | No | [19 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
2. Contact from object | 2.d.t.0 | Aircraft vehicle contact | Transmission | Non-HFTD | No | [19 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
2. Contact from object | 2.d.t.2 | Aircraft vehicle contact | Transmission | HFTD Tier 2 | No | [19 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
2. Contact from object | 2.d.t.3 | Aircraft vehicle contact | Transmission | HFTD Tier 3 | No | [19 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
2. Contact from object | 2.e.d.0 | 3rd party facility | Distribution | Non-HFTD | No | [19 empty] | # ignitions |  | SDGE includes this metric in #11 "Other"
2. Contact from object | 2.e.d.2 | 3rd party facility | Distribution | HFTD Tier 2 | No | [19 empty] | # ignitions |  | SDGE includes this metric in #11 "Other"
2. Contact from object | 2.e.d.3 | 3rd party facility | Distribution | HFTD Tier 3 | No | [19 empty] | # ignitions |  | SDGE includes this metric in #11 "Other"
2. Contact from object | 2.e.t.0 | 3rd party facility | Transmission | Non-HFTD | No | [19 empty] | # ignitions |  | SDGE includes this metric in #11 "Other"
2. Contact from object | 2.e.t.2 | 3rd party facility | Transmission | HFTD Tier 2 | No | [19 empty] | # ignitions |  | SDGE includes this metric in #11 "Other"
2. Contact from object | 2.e.t.3 | 3rd party facility | Transmission | HFTD Tier 3 | No | [19 empty] | # ignitions |  | SDGE includes this metric in #11 "Other"
2. Contact from object | 2.f.d.0 | Unknown | Distribution | Non-HFTD | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
2. Contact from object | 2.f.d.2 | Unknown | Distribution | HFTD Tier 2 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
2. Contact from object | 2.f.d.3 | Unknown | Distribution | HFTD Tier 3 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
2. Contact from object | 2.f.t.0 | Unknown | Transmission | Non-HFTD | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
2. Contact from object | 2.f.t.2 | Unknown | Transmission | HFTD Tier 2 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
2. Contact from object | 2.f.t.3 | Unknown | Transmission | HFTD Tier 3 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
2. Contact from object | 2.g.d.0 | Other | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 1 | 0.2 | 0.2 | 0.2 | # ignitions
2. Contact from object | 2.g.d.2 | Other | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.0095 | 0 | 0 | # ignitions
2. Contact from object | 2.g.d.3 | Other | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.2871 | 0.0196 | 0 | # ignitions
2. Contact from object | 2.g.t.0 | Other | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
2. Contact from object | 2.g.t.2 | Other | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 0 | 0.19922 | 0.19776 | 0.19776 | # ignitions
2. Contact from object | 2.g.t.3 | Other | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
3. Vegetation contact | 3.a.d.0 | Vegetation contact | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 1 | 1 | 1 | # ignitions
3. Vegetation contact | 3.a.d.2 | Vegetation contact | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
3. Vegetation contact | 3.a.d.3 | Vegetation contact | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.28251 | 0.010422 | 0 | # ignitions
3. Vegetation contact | 3.a.t.0 | Vegetation contact | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
3. Vegetation contact | 3.a.t.2 | Vegetation contact | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
3. Vegetation contact | 3.a.t.3 | Vegetation contact | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment/facility failure or damage | 4.a.d.0 | Anchor/guy | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.396 | 0.372 | 0.348 | # ignitions
4. Equipment / facility failure or damage | 4.a.d.2 | Anchor/guy | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.a.d.3 | Anchor/guy | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.a.t.0 | Anchor/guy | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.a.t.2 | Anchor/guy | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.a.t.3 | Anchor/guy | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.b.d.0 | Capacitor bank | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.2 | 0.2 | 0.2 | # ignitions
4. Equipment / facility failure or damage | 4.b.d.2 | Capacitor bank | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.b.d.3 | Capacitor bank | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.1959 | 0.1918 | 0.1918 | # ignitions
4. Equipment / facility failure or damage | 4.b.t.0 | Capacitor bank | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.b.t.2 | Capacitor bank | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.b.t.3 | Capacitor bank | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.c.d.0 | Conductor | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.196 | 0.172 | 0.148 | # ignitions
4. Equipment / facility failure or damage | 4.c.d.2 | Conductor | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.c.d.3 | Conductor | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.1296 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.c.t.0 | Conductor | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.c.t.2 | Conductor | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.c.t.3 | Conductor | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.d.d.0 | Connection device | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.38 | 0.34 | 0.3 | # ignitions
4. Equipment / facility failure or damage | 4.d.d.2 | Connection device | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 1; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.d.d.3 | Connection device | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 1 | 0.2525 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.d.t.0 | Connection device | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.d.t.2 | Connection device | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.d.t.3 | Connection device | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.e.d.0 | Crossarm | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.396 | 0.372 | 0.348 | # ignitions
4. Equipment / facility failure or damage | 4.e.d.2 | Crossarm | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.e.d.3 | Crossarm | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.e.t.0 | Crossarm | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.e.t.2 | Crossarm | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.e.t.3 | Crossarm | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.f.d.0 | Fuse | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.4 | 0.4 | 0.4 | # ignitions
4. Equipment / facility failure or damage | 4.f.d.2 | Fuse | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.f.d.3 | Fuse | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.2 | 0.2 | 0.2 | # ignitions
4. Equipment / facility failure or damage | 4.f.t.0 | Fuse | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.f.t.2 | Fuse | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.f.t.3 | Fuse | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.g.d.0 | Cutout | Distribution | Non-HFTD | No | [19 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
4. Equipment / facility failure or damage | 4.g.d.2 | Cutout | Distribution | HFTD Tier 2 | No | [19 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
4. Equipment / facility failure or damage | 4.g.d.3 | Cutout | Distribution | HFTD Tier 3 | No | [19 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
4. Equipment / facility failure or damage | 4.g.t.0 | Cutout | Transmission | Non-HFTD | No | [19 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
4. Equipment / facility failure or damage | 4.g.t.2 | Cutout | Transmission | HFTD Tier 2 | No | [19 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
4. Equipment / facility failure or damage | 4.g.t.3 | Cutout | Transmission | HFTD Tier 3 | No | [19 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
4. Equipment / facility failure or damage | 4.h.d.0 | Insulator and brushing | Distribution | Non-HFTD | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.h.d.2 | Insulator and brushing | Distribution | HFTD Tier 2 | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.h.d.3 | Insulator and brushing | Distribution | HFTD Tier 3 | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 1 | 1 | 1 | 1 | # ignitions
4. Equipment / facility failure or damage | 4.h.t.0 | Insulator and brushing | Transmission | Non-HFTD | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.h.t.2 | Insulator and brushing | Transmission | HFTD Tier 2 | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.h.t.3 | Insulator and brushing | Transmission | HFTD Tier 3 | No | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.i.d.0 | Lightning arrestor | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.i.d.2 | Lightning arrestor | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.3963 | 0.3926 | 0.3889 | # ignitions
4. Equipment / facility failure or damage | 4.i.d.3 | Lightning arrestor | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.7736 | 0.7472 | 0.7208 | # ignitions
4. Equipment / facility failure or damage | 4.i.t.0 | Lightning arrestor | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.i.t.2 | Lightning arrestor | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.i.t.3 | Lightning arrestor | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.j.d.0 | Pole | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.j.d.2 | Pole | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.j.d.3 | Pole | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.j.t.0 | Pole | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.j.t.2 | Pole | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.j.t.3 | Pole | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.k.d.0 | Recloser | Distribution | Non-HFTD | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.k.d.2 | Recloser | Distribution | HFTD Tier 2 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.k.d.3 | Recloser | Distribution | HFTD Tier 3 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.k.t.0 | Recloser | Transmission | Non-HFTD | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.k.t.2 | Recloser | Transmission | HFTD Tier 2 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.k.t.3 | Recloser | Transmission | HFTD Tier 3 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.l.d.0 | Relay | Distribution | Non-HFTD | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.l.d.2 | Relay | Distribution | HFTD Tier 2 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.l.d.3 | Relay | Distribution | HFTD Tier 3 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.l.t.0 | Relay | Transmission | Non-HFTD | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.l.t.2 | Relay | Transmission | HFTD Tier 2 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.l.t.3 | Relay | Transmission | HFTD Tier 3 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.m.d.0 | Sectionalizer | Distribution | Non-HFTD | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.m.d.2 | Sectionalizer | Distribution | HFTD Tier 2 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.m.d.3 | Sectionalizer | Distribution | HFTD Tier 3 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.m.t.0 | Sectionalizer | Transmission | Non-HFTD | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.m.t.2 | Sectionalizer | Transmission | HFTD Tier 2 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.m.t.3 | Sectionalizer | Transmission | HFTD Tier 3 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.n.d.0 | Splice | Distribution | Non-HFTD | No | [19 empty] | # ignitions |  | SDG&E tracks splice failure/damage under connection device
4. Equipment / facility failure or damage | 4.n.d.2 | Splice | Distribution | HFTD Tier 2 | No | [19 empty] | # ignitions |  | SDG&E tracks splice failure/damage under connection device
4. Equipment / facility failure or damage | 4.n.d.3 | Splice | Distribution | HFTD Tier 3 | No | [19 empty] | # ignitions |  | SDG&E tracks splice failure/damage under connection device
4. Equipment / facility failure or damage | 4.n.t.0 | Splice | Transmission | Non-HFTD | No | [19 empty] | # ignitions |  | SDG&E tracks splice failure/damage under connection device
4. Equipment / facility failure or damage | 4.n.t.2 | Splice | Transmission | HFTD Tier 2 | No | [19 empty] | # ignitions |  | SDG&E tracks splice failure/damage under connection device
4. Equipment / facility failure or damage | 4.n.t.3 | Splice | Transmission | HFTD Tier 3 | No | [19 empty] | # ignitions |  | SDG&E tracks splice failure/damage under connection device
4. Equipment / facility failure or damage | 4.o.d.0 | Switch | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 1; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.196 | 0.172 | 0.148 | # ignitions
4. Equipment / facility failure or damage | 4.o.d.2 | Switch | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.o.d.3 | Switch | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.o.t.0 | Switch | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.o.t.2 | Switch | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.o.t.3 | Switch | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.p.d.0 | Tap | Distribution | Non-HFTD | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.p.d.2 | Tap | Distribution | HFTD Tier 2 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.p.d.3 | Tap | Distribution | HFTD Tier 3 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.p.t.0 | Tap | Transmission | Non-HFTD | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.p.t.2 | Tap | Transmission | HFTD Tier 2 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.p.t.3 | Tap | Transmission | HFTD Tier 3 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.q.d.0 | Tie wire | Distribution | Non-HFTD | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.q.d.2 | Tie wire | Distribution | HFTD Tier 2 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.q.d.3 | Tie wire | Distribution | HFTD Tier 3 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.q.t.0 | Tie wire | Transmission | Non-HFTD | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.q.t.2 | Tie wire | Transmission | HFTD Tier 2 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.q.t.3 | Tie wire | Transmission | HFTD Tier 3 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.r.d.0 | Transformer | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.196 | 0.172 | 0.148 | # ignitions
4. Equipment / facility failure or damage | 4.r.d.2 | Transformer | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.r.d.3 | Transformer | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.r.t.0 | Transformer | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.r.t.2 | Transformer | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.r.t.3 | Transformer | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.s.d.0 | Voltage regulator/booster | Distribution | Non-HFTD | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.s.d.2 | Voltage regulator/booster | Distribution | HFTD Tier 2 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.s.d.3 | Voltage regulator/booster | Distribution | HFTD Tier 3 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.s.t.0 | Voltage regulator/booster | Transmission | Non-HFTD | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.s.t.2 | Voltage regulator/booster | Transmission | HFTD Tier 2 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.s.t.3 | Voltage regulator/booster | Transmission | HFTD Tier 3 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.t.d.0 | Unknown | Distribution | Non-HFTD | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.t.d.2 | Unknown | Distribution | HFTD Tier 2 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.t.d.3 | Unknown | Distribution | HFTD Tier 3 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.t.t.0 | Unknown | Transmission | Non-HFTD | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.t.t.2 | Unknown | Transmission | HFTD Tier 2 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.t.t.3 | Unknown | Transmission | HFTD Tier 3 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
4. Equipment / facility failure or damage | 4.u.d.0 | Other | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.58641 | 0.57282 | 0.55922 | # ignitions
4. Equipment / facility failure or damage | 4.u.d.2 | Other | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.6 | 0.6 | 0.6 | # ignitions
4. Equipment / facility failure or damage | 4.u.d.3 | Other | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.191 | 0.18199 | 0.17299 | # ignitions
4. Equipment / facility failure or damage | 4.u.t.0 | Other | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
4. Equipment / facility failure or damage | 4.u.t.2 | Other | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.2 | 0.2 | 0.2 | # ignitions
4. Equipment / facility failure or damage | 4.u.t.3 | Other | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
5. Wire-to-wire contact | 5.a.d.0 | Wire-to-wire contact | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.4 | 0.4 | 0.4 | # ignitions
5. Wire-to-wire contact | 5.a.d.2 | Wire-to-wire contact | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.0087 | 0 | 0 | # ignitions
5. Wire-to-wire contact | 5.a.d.3 | Wire-to-wire contact | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
5. Wire-to-wire contact | 5.a.t.0 | Wire-to-wire contact | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.2 | 0.2 | 0.2 | # ignitions
5. Wire-to-wire contact | 5.a.t.2 | Wire-to-wire contact | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
5. Wire-to-wire contact | 5.a.t.3 | Wire-to-wire contact | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
6. Contamination | 6.a.d.0 | Contamination | Distribution | Non-HFTD | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
6. Contamination | 6.a.d.2 | Contamination | Distribution | HFTD Tier 2 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
6. Contamination | 6.a.d.3 | Contamination | Distribution | HFTD Tier 3 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
6. Contamination | 6.a.t.0 | Contamination | Transmission | Non-HFTD | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
6. Contamination | 6.a.t.2 | Contamination | Transmission | HFTD Tier 2 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
6. Contamination | 6.a.t.3 | Contamination | Transmission | HFTD Tier 3 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
7. Protective device operation | 7.a.d.0 | Protective device operation | Distribution | Non-HFTD | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
7. Protective device operation | 7.a.d.2 | Protective device operation | Distribution | HFTD Tier 2 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
7. Protective device operation | 7.a.d.3 | Protective device operation | Distribution | HFTD Tier 3 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
7. Protective device operation | 7.a.t.0 | Protective device operation | Transmission | Non-HFTD | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
7. Protective device operation | 7.a.t.2 | Protective device operation | Transmission | HFTD Tier 2 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
7. Protective device operation | 7.a.t.3 | Protective device operation | Transmission | HFTD Tier 3 | No | [19 empty] | # ignitions |  | SDG&E does not currently track this driver
8. Vandalism/theft | 8.a.d.0 | Vandalism/theft | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.2 | 0.2 | 0.2 | # ignitions
8. Vandalism/theft | 8.a.d.2 | Vandalism/theft | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.0576 | 0 | 0 | # ignitions
8. Vandalism/theft | 8.a.d.3 | Vandalism/theft | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
8. Vandalism/theft | 8.a.t.0 | Vandalism/theft | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
8. Vandalism/theft | 8.a.t.2 | Vandalism/theft | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
8. Vandalism/theft | 8.a.t.3 | Vandalism/theft | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
9. Lightning | 9.a.d.0 | Lightning | Distribution | Non-HFTD | No | [19 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
9. Lightning | 9.a.d.2 | Lightning | Distribution | HFTD Tier 2 | No | [19 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
9. Lightning | 9.a.d.3 | Lightning | Distribution | HFTD Tier 3 | No | [19 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
9. Lightning | 9.a.t.0 | Lightning | Transmission | Non-HFTD | No | [19 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
9. Lightning | 9.a.t.2 | Lightning | Transmission | HFTD Tier 2 | No | [19 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
9. Lightning | 9.a.t.3 | Lightning | Transmission | HFTD Tier 3 | No | [19 empty] | # ignitions |  | SDG&E did not track this driver historically but can implement for future ignitions
10. Unknown | 10.a.d.0 | Unknown | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
10. Unknown | 10.a.d.2 | Unknown | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
10. Unknown | 10.a.d.3 | Unknown | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
10. Unknown | 10.a.t.0 | Unknown | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
10. Unknown | 10.a.t.2 | Unknown | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.39922 | 0.39776 | 0.39776 | # ignitions
10. Unknown | 10.a.t.3 | Unknown | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
11. Other | 11.a.d.0 | Other | Distribution | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
11. Other | 11.a.d.2 | Other | Distribution | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0.2576 | 0.1355 | 0 | # ignitions
11. Other | 11.a.d.3 | Other | Distribution | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
11. Other | 11.a.t.0 | Other | Transmission | Non-HFTD | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 1; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
11. Other | 11.a.t.2 | Other | Transmission | HFTD Tier 2 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions
11. Other | 11.a.t.3 | Other | Transmission | HFTD Tier 3 | Yes | Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0; Actual number of ignitions Q1: 0; Actual number of ignitions Q2: 0; Actual number of ignitions Q3: 0; Actual number of ignitions Q4: 0 | 0 | 0 | 0 | # ignitions

## Table 7
| Utility | SDG&E
| Table No. | 7
| Date Modified | 2024-02-01
[7 empty] | Actual | [15 empty] | Projected
| Table 7: State of service territory and utility equipment | [5 empty] | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4
| Metric type | # | Line Type | HFTD Tier | Area Type | WUI Status | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | 2024 | 2024 | 2024 | 2024 | 2025 | 2025 | 2025 | 2025 | 2023 | 2024 | 2025 | Unit(s) | Comments | Blank Meaning
| 1. Overhead circuit miles | 1.d.0.a.i | Distribution | Non-HFTD | Urban | WUI | Actual Q1: 402.386; Actual Q2: 401.8; Actual Q3: 400.4; Actual Q4: 396.95; Actual Q1: 394.971; Actual Q2: 394.78; Actual Q3: 394.46; Actual Q4: 394.24 | 396.95 | 396.83 | 396.83 | Circuit miles
|  | 1.d.0.a.ii | Distribution | Non-HFTD | Urban | Non-WUI | Actual Q1: 2084.8061; Actual Q2: 2083; Actual Q3: 2078.7; Actual Q4: 2072.42; Actual Q1: 2072.019; Actual Q2: 2071.65; Actual Q3: 2069.44; Actual Q4: 2066.75 | 2072.42 | 2072.08 | 2072.08 | Circuit miles
|  | 1.d.0.b.i | Distribution | Non-HFTD | Rural | WUI | Actual Q1: 181.1752; Actual Q2: 179.5; Actual Q3: 179.1; Actual Q4: 175.06; Actual Q1: 175.199; Actual Q2: 175.3; Actual Q3: 175.17; Actual Q4: 175.16 | 175.06 | 175.06 | 175.06 | Circuit miles
|  | 1.d.0.b.ii | Distribution | Non-HFTD | Rural | Non-WUI | Actual Q1: 181.6525; Actual Q2: 181; Actual Q3: 180.4; Actual Q4: 178.02; Actual Q1: 179.844; Actual Q2: 179.05; Actual Q3: 179.05; Actual Q4: 177.85 | 178.02 | 178.02 | 178.02 | Circuit miles
|  | 1.d.0.c.i | Distribution | Non-HFTD | Highly rural | WUI | Actual Q1: 34.6812; Actual Q2: 34.7; Actual Q3: 34.7; Actual Q4: 34.68; Actual Q1: 34.681; Actual Q2: 34.83; Actual Q3: 34.83; Actual Q4: 34.83 | 34.68 | 34.68 | 34.68 | Circuit miles
|  | 1.d.0.c.ii | Distribution | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 110.9032; Actual Q2: 109.4; Actual Q3: 109.3; Actual Q4: 109.39; Actual Q1: 109.496; Actual Q2: 109.61; Actual Q3: 109.61; Actual Q4: 109.61 | 109.39 | 109.39 | 109.39 | Circuit miles
|  | 1.d.2.a.i | Distribution | HFTD Tier 2 | Urban | WUI | Actual Q1: 95.397; Actual Q2: 95.4; Actual Q3: 95.4; Actual Q4: 91.06; Actual Q1: 91.218; Actual Q2: 91.25; Actual Q3: 91.43; Actual Q4: 91.38 | 91.06 | 90.91 | 90.91 | Circuit miles
|  | 1.d.2.a.ii | Distribution | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 85.4078; Actual Q2: 85.4; Actual Q3: 86; Actual Q4: 83.37; Actual Q1: 83.409; Actual Q2: 83.87; Actual Q3: 83.83; Actual Q4: 83.79 | 83.17 | 83.17 | 82.73 | Circuit miles
|  | 1.d.2.b.i | Distribution | HFTD Tier 2 | Rural | WUI | Actual Q1: 853.0178; Actual Q2: 854.1; Actual Q3: 853.2; Actual Q4: 849.24; Actual Q1: 849.288; Actual Q2: 850.1; Actual Q3: 850.61; Actual Q4: 850.22 | 836.96 | 836.87 | 781.46 | Circuit miles
|  | 1.d.2.b.ii | Distribution | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 604.804; Actual Q2: 604.3; Actual Q3: 603.2; Actual Q4: 598.65; Actual Q1: 597.224; Actual Q2: 595.64; Actual Q3: 595.68; Actual Q4: 591.97 | 571.01 | 567.79 | 548.09 | Circuit miles
|  | 1.d.2.c.i | Distribution | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 20.378; Actual Q2: 20.2; Actual Q3: 20.2; Actual Q4: 20.17; Actual Q1: 20.175; Actual Q2: 20.3; Actual Q3: 20.3; Actual Q4: 20.3 | 20.17 | 15.45 | 14.12 | Circuit miles
|  | 1.d.2.c.ii | Distribution | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 153.178; Actual Q2: 152.5; Actual Q3: 152.2; Actual Q4: 151.98; Actual Q1: 151.324; Actual Q2: 151.91; Actual Q3: 151.91; Actual Q4: 151.89 | 151.98 | 105.93 | 98.33 | Circuit miles
|  | 1.d.3.a.i | Distribution | HFTD Tier 3 | Urban | WUI | Actual Q1: 5.2602; Actual Q2: 5.3; Actual Q3: 5.3; Actual Q4: 4.77; Actual Q1: 4.776; Actual Q2: 4.9; Actual Q3: 4.9; Actual Q4: 4.9 | 4.77 | 4.77 | 4.77 | Circuit miles
|  | 1.d.3.a.ii | Distribution | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: 0.098864; Actual Q2: 0.1; Actual Q3: 0.1; Actual Q4: 0.04; Actual Q1: 0.04; Actual Q2: 0.04; Actual Q3: 0.04; Actual Q4: 0.04 | 0.04 | 0.04 | 0.04 | Circuit miles
|  | 1.d.3.b.i | Distribution | HFTD Tier 3 | Rural | WUI | Actual Q1: 660.5458; Actual Q2: 659.3; Actual Q3: 657.3; Actual Q4: 655.3; Actual Q1: 650.348; Actual Q2: 651.92; Actual Q3: 650.48; Actual Q4: 644.55 | 637.07 | 618.13 | 563.83 | Circuit miles
|  | 1.d.3.b.ii | Distribution | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 784.9341; Actual Q2: 784; Actual Q3: 783.3; Actual Q4: 778.42; Actual Q1: 773.666; Actual Q2: 774.78; Actual Q3: 774.96; Actual Q4: 770.99 | 740.68 | 679.01 | 604.35 | Circuit miles
|  | 1.d.3.c.i | Distribution | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 27.1703; Actual Q2: 27.3; Actual Q3: 27.3; Actual Q4: 25.92; Actual Q1: 25.921; Actual Q2: 26.02; Actual Q3: 25.53; Actual Q4: 25.51 | 24.16 | 23.36 | 19.2 | Circuit miles
|  | 1.d.3.c.ii | Distribution | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 163.6017; Actual Q2: 164.6; Actual Q3: 164.5; Actual Q4: 162.91; Actual Q1: 162.854; Actual Q2: 163.11; Actual Q3: 163.04; Actual Q4: 163.04 | 126.88 | 114.19 | 104.68 | Circuit miles
|  | 1.t.0.a.i | Transmission | Non-HFTD | Urban | WUI | Actual Q1: 143.5205; Actual Q2: 143.5; Actual Q3: 142.8; Actual Q4: 134.21; Actual Q1: 135.934; Actual Q2: 135.93; Actual Q3: 135.93; Actual Q4: 135.9 | 134.71 | 134.71 | 134.71 | Circuit miles
|  | 1.t.0.a.ii | Transmission | Non-HFTD | Urban | Non-WUI | Actual Q1: 293.5383; Actual Q2: 293.6; Actual Q3: 294.3; Actual Q4: 286.76; Actual Q1: 288.295; Actual Q2: 288.29; Actual Q3: 288.28; Actual Q4: 288.2 | 286.76 | 286.76 | 286.76 | Circuit miles
|  | 1.t.0.b.i | Transmission | Non-HFTD | Rural | WUI | Actual Q1: 61.4661; Actual Q2: 61.5; Actual Q3: 61.5; Actual Q4: 55.46; Actual Q1: 55.435; Actual Q2: 55.43; Actual Q3: 55.48; Actual Q4: 55.48 | 55.46 | 55.46 | 55.46 | Circuit miles
|  | 1.t.0.b.ii | Transmission | Non-HFTD | Rural | Non-WUI | Actual Q1: 114.889; Actual Q2: 114.9; Actual Q3: 114.9; Actual Q4: 113.58; Actual Q1: 113.37; Actual Q2: 113.37; Actual Q3: 113.37; Actual Q4: 113.37 | 113.58 | 112.68 | 112.68 | Circuit miles
|  | 1.t.0.c.i | Transmission | Non-HFTD | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.0.c.ii | Transmission | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 22.8057; Actual Q2: 22.8; Actual Q3: 22.8; Actual Q4: 22.81; Actual Q1: 22.806; Actual Q2: 22.81; Actual Q3: 22.81; Actual Q4: 22.81 | 22.81 | 22.81 | 22.81 | Circuit miles
|  | 1.t.2.a.i | Transmission | HFTD Tier 2 | Urban | WUI | Actual Q1: 42.1131; Actual Q2: 42.1; Actual Q3: 42.1; Actual Q4: 36.41; Actual Q1: 36.562; Actual Q2: 36.72; Actual Q3: 36.72; Actual Q4: 36.72 | 36.41 | 36.41 | 36.41 | Circuit miles
|  | 1.t.2.a.ii | Transmission | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 66.05; Actual Q2: 66.1; Actual Q3: 66.1; Actual Q4: 58.22; Actual Q1: 59.499; Actual Q2: 59.5; Actual Q3: 59.5; Actual Q4: 59.5 | 58.22 | 58.22 | 58.22 | Circuit miles
|  | 1.t.2.b.i | Transmission | HFTD Tier 2 | Rural | WUI | Actual Q1: 127.3992; Actual Q2: 127.4; Actual Q3: 127.4; Actual Q4: 118.09; Actual Q1: 118.123; Actual Q2: 118; Actual Q3: 115.49; Actual Q4: 115.48 | 118.09 | 118.09 | 118.09 | Circuit miles
|  | 1.t.2.b.ii | Transmission | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 446.0614; Actual Q2: 445.4; Actual Q3: 445.3; Actual Q4: 443.23; Actual Q1: 443.817; Actual Q2: 443.86; Actual Q3: 443.14; Actual Q4: 443.79 | 443.23 | 443.23 | 443.23 | Circuit miles
|  | 1.t.2.c.i | Transmission | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.2.c.ii | Transmission | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 23.425; Actual Q2: 23.4; Actual Q3: 23.4; Actual Q4: 23.42; Actual Q1: 23.425; Actual Q2: 23.42; Actual Q3: 23.42; Actual Q4: 23.42 | 23.42 | 23.42 | 23.42 | Circuit miles
|  | 1.t.3.a.i | Transmission | HFTD Tier 3 | Urban | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.3.a.ii | Transmission | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.3.b.i | Transmission | HFTD Tier 3 | Rural | WUI | Actual Q1: 21.7848; Actual Q2: 21.8; Actual Q3: 21.9; Actual Q4: 22.02; Actual Q1: 22.026; Actual Q2: 22.02; Actual Q3: 21.44; Actual Q4: 21.44 | 22.02 | 22.02 | 22.02 | Circuit miles
|  | 1.t.3.b.ii | Transmission | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 228.3155; Actual Q2: 228.3; Actual Q3: 228.2; Actual Q4: 229.49; Actual Q1: 229.495; Actual Q2: 229.49; Actual Q3: 226.23; Actual Q4: 226.24 | 229.49 | 229.49 | 229.49 | Circuit miles
|  | 1.t.3.c.i | Transmission | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 2.8612; Actual Q2: 2.9; Actual Q3: 2.9; Actual Q4: 2.82; Actual Q1: 2.817; Actual Q2: 2.82; Actual Q3: 2.82; Actual Q4: 2.82 | 2.82 | 2.82 | 2.82 | Circuit miles
|  | 1.t.3.c.ii | Transmission | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 15.7502; Actual Q2: 15.7; Actual Q3: 15.7; Actual Q4: 15.68; Actual Q1: 15.685; Actual Q2: 15.68; Actual Q3: 15.68; Actual Q4: 15.68 | 15.68 | 15.68 | 15.68 | Circuit miles
x | 2. Underground circuit miles | 2.d.0.a.i | Distribution | Non-HFTD | Urban | WUI | Actual Q1: 1917.2263; Actual Q2: 1918.5924; Actual Q3: 1921.9079; Actual Q4: 1913.63; Actual Q1: 1914.255; Actual Q2: 1916.08; Actual Q3: 1919.06; Actual Q4: 1921.96 | 1913.63 | 1913.63 | 1913.63 | Circuit miles
|  | 2.d.0.a.ii | Distribution | Non-HFTD | Urban | Non-WUI | Actual Q1: 4871.7412; Actual Q2: 4880.5676; Actual Q3: 4889.9997; Actual Q4: 4880.8; Actual Q1: 4884.161; Actual Q2: 4889.56; Actual Q3: 4897.9; Actual Q4: 4903.42 | 4880.8 | 4880.8 | 4880.8 | Circuit miles
|  | 2.d.0.b.i | Distribution | Non-HFTD | Rural | WUI | Actual Q1: 617.1331; Actual Q2: 617.3898; Actual Q3: 617.5733; Actual Q4: 595.16; Actual Q1: 595.531; Actual Q2: 595.87; Actual Q3: 597.12; Actual Q4: 597.66 | 595.16 | 595.16 | 595.16 | Circuit miles
|  | 2.d.0.b.ii | Distribution | Non-HFTD | Rural | Non-WUI | Actual Q1: 900.3336; Actual Q2: 902.6644; Actual Q3: 903.3794; Actual Q4: 875.6; Actual Q1: 875.968; Actual Q2: 878.61; Actual Q3: 879.8; Actual Q4: 881.38 | 875.6 | 875.6 | 875.6 | Circuit miles
|  | 2.d.0.c.i | Distribution | Non-HFTD | Highly rural | WUI | Actual Q1: 17.4837; Actual Q2: 17.4176; Actual Q3: 17.42; Actual Q4: 17.77; Actual Q1: 17.768; Actual Q2: 17.77; Actual Q3: 17.77; Actual Q4: 17.77 | 17.77 | 17.77 | 17.77 | Circuit miles
|  | 2.d.0.c.ii | Distribution | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 60.3223; Actual Q2: 59.7315; Actual Q3: 59.8382; Actual Q4: 57.13; Actual Q1: 57.612; Actual Q2: 57.61; Actual Q3: 57.8; Actual Q4: 58.11 | 57.13 | 57.13 | 57.13 | Circuit miles
|  | 2.d.2.a.i | Distribution | HFTD Tier 2 | Urban | WUI | Actual Q1: 782.7751; Actual Q2: 783.103; Actual Q3: 783.703; Actual Q4: 772.24; Actual Q1: 772.247; Actual Q2: 772.13; Actual Q3: 772.28; Actual Q4: 772.5 | 772.39 | 772.39 | 772.39 | Circuit miles
|  | 2.d.2.a.ii | Distribution | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 153.7559; Actual Q2: 154.003; Actual Q3: 154.91; Actual Q4: 153.16; Actual Q1: 153.198; Actual Q2: 153.52; Actual Q3: 155.5; Actual Q4: 156.77 | 153.16 | 153.21 | 153.46 | Circuit miles
|  | 2.d.2.b.i | Distribution | HFTD Tier 2 | Rural | WUI | Actual Q1: 1006.8711; Actual Q2: 1007.9572; Actual Q3: 1010.5566; Actual Q4: 997.38; Actual Q1: 997.748; Actual Q2: 1006.41; Actual Q3: 1008; Actual Q4: 1010.69 | 1017.58 | 1017.6 | 1082 | Circuit miles
|  | 2.d.2.b.ii | Distribution | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 332.7001; Actual Q2: 336.0513; Actual Q3: 340.8217; Actual Q4: 343.31; Actual Q1: 345.414; Actual Q2: 348.07; Actual Q3: 351.59; Actual Q4: 357.69 | 370.67 | 370.75 | 383.46 | Circuit miles
|  | 2.d.2.c.i | Distribution | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 1.5643; Actual Q2: 1.5745; Actual Q3: 1.5747; Actual Q4: 1.57; Actual Q1: 1.571; Actual Q2: 1.57; Actual Q3: 1.57; Actual Q4: 1.57 | 1.57 | 12.92 | 14.29 | Circuit miles
|  | 2.d.2.c.ii | Distribution | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 8.7884; Actual Q2: 8.8564; Actual Q3: 8.8576; Actual Q4: 9.03; Actual Q1: 9.033; Actual Q2: 9.03; Actual Q3: 9.03; Actual Q4: 9.03 | 9.03 | 61.23 | 69.46 | Circuit miles
|  | 2.d.3.a.i | Distribution | HFTD Tier 3 | Urban | WUI | Actual Q1: 2.7216; Actual Q2: 2.7553; Actual Q3: 2.7557; Actual Q4: 0.62; Actual Q1: 0.617; Actual Q2: 0.62; Actual Q3: 0.62; Actual Q4: 0.99 | 0.65 | 0.65 | 0.65 | Circuit miles
|  | 2.d.3.a.ii | Distribution | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: -9.8398e-07; Actual Q2: -8.7401e-16; Actual Q3: -8.7413e-16; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
|  | 2.d.3.b.i | Distribution | HFTD Tier 3 | Rural | WUI | Actual Q1: 292.2907; Actual Q2: 293.147; Actual Q3: 300.6672; Actual Q4: 315.57; Actual Q1: 316.734; Actual Q2: 316.97; Actual Q3: 324.16; Actual Q4: 333.45 | 359.6 | 402.91 | 482.44 | Circuit miles
|  | 2.d.3.b.ii | Distribution | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 139.7184; Actual Q2: 143.0801; Actual Q3: 146.4461; Actual Q4: 149.56; Actual Q1: 150.679; Actual Q2: 151.61; Actual Q3: 154.04; Actual Q4: 163.62 | 196.01 | 277.31 | 345.86 | Circuit miles
|  | 2.d.3.c.i | Distribution | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 6.5187; Actual Q2: 6.4947; Actual Q3: 7.2829; Actual Q4: 8.44; Actual Q1: 8.445; Actual Q2: 8.44; Actual Q3: 10.11; Actual Q4: 10.32 | 19.25 | 26.09 | 31.62 | Circuit miles
|  | 2.d.3.c.ii | Distribution | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 25.0296; Actual Q2: 25.0931; Actual Q3: 25.2934; Actual Q4: 25.61; Actual Q1: 25.236; Actual Q2: 25.21; Actual Q3: 26.41; Actual Q4: 26.85 | 66.87 | 88.22 | 96.26 | Circuit miles
|  | 2.t.0.a.i | Transmission | Non-HFTD | Urban | WUI | Actual Q1: 31.2127; Actual Q2: 31.1076; Actual Q3: 30.8921; Actual Q4: 25.86; Actual Q1: 25.855; Actual Q2: 25.86; Actual Q3: 28.5; Actual Q4: 28.71 | 25.86 | 25.86 | 25.86 | Circuit miles
|  | 2.t.0.a.ii | Transmission | Non-HFTD | Urban | Non-WUI | Actual Q1: 79.3126; Actual Q2: 79.1324; Actual Q3: 78.6003; Actual Q4: 65.12; Actual Q1: 65.121; Actual Q2: 65.04; Actual Q3: 68.02; Actual Q4: 68.02 | 65.12 | 65.12 | 65.12 | Circuit miles
|  | 2.t.0.b.i | Transmission | Non-HFTD | Rural | WUI | Actual Q1: 10.047; Actual Q2: 10.0102; Actual Q3: 9.9267; Actual Q4: 9.98; Actual Q1: 10.154; Actual Q2: 10.15; Actual Q3: 10.15; Actual Q4: 10.15 | 9.98 | 9.98 | 9.98 | Circuit miles
|  | 2.t.0.b.ii | Transmission | Non-HFTD | Rural | Non-WUI | Actual Q1: 14.6575; Actual Q2: 14.6356; Actual Q3: 14.5206; Actual Q4: 22.52; Actual Q1: 22.551; Actual Q2: 22.55; Actual Q3: 22.55; Actual Q4: 22.58 | 22.52 | 22.52 | 22.52 | Circuit miles
|  | 2.t.0.c.i | Transmission | Non-HFTD | Highly rural | WUI | Actual Q1: 0.28464; Actual Q2: 0.2824; Actual Q3: 0.28; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
|  | 2.t.0.c.ii | Transmission | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 0.98205; Actual Q2: 0.96847; Actual Q3: 0.96182; Actual Q4: 0.35; Actual Q1: 0.348; Actual Q2: 0.35; Actual Q3: 0.35; Actual Q4: 0.35 | 0.35 | 0.35 | 0.35 | Circuit miles
|  | 2.t.2.a.i | Transmission | HFTD Tier 2 | Urban | WUI | Actual Q1: 12.7437; Actual Q2: 12.697; Actual Q3: 12.597; Actual Q4: 13.29; Actual Q1: 13.289; Actual Q2: 13.29; Actual Q3: 13.29; Actual Q4: 13.29 | 13.29 | 13.29 | 13.29 | Circuit miles
|  | 2.t.2.a.ii | Transmission | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 2.5032; Actual Q2: 2.497; Actual Q3: 2.49; Actual Q4: 1.37; Actual Q1: 1.372; Actual Q2: 1.37; Actual Q3: 1.37; Actual Q4: 1.37 | 1.37 | 1.37 | 1.37 | Circuit miles
|  | 2.t.2.b.i | Transmission | HFTD Tier 2 | Rural | WUI | Actual Q1: 16.392; Actual Q2: 16.3428; Actual Q3: 16.2434; Actual Q4: 12.93; Actual Q1: 12.925; Actual Q2: 12.93; Actual Q3: 12.7; Actual Q4: 12.7 | 12.93 | 12.93 | 12.93 | Circuit miles
|  | 2.t.2.b.ii | Transmission | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 5.4164; Actual Q2: 5.4487; Actual Q3: 5.4783; Actual Q4: 8.53; Actual Q1: 8.525; Actual Q2: 8.53; Actual Q3: 8.58; Actual Q4: 8.58 | 8.53 | 8.53 | 8.53 | Circuit miles
|  | 2.t.2.c.i | Transmission | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 0.025467; Actual Q2: 0.025528; Actual Q3: 0.025311; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
|  | 2.t.2.c.ii | Transmission | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 0.14308; Actual Q2: 0.1436; Actual Q3: 0.14237; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
|  | 2.t.3.a.i | Transmission | HFTD Tier 3 | Urban | WUI | Actual Q1: 0.044308; Actual Q2: 0.044674; Actual Q3: 0.044294; Actual Q4: 0.94; Actual Q1: 0.935; Actual Q2: 0.94; Actual Q3: 0.94; Actual Q4: 0.94 | 0.94 | 0.94 | 0.94 | Circuit miles
|  | 2.t.3.a.ii | Transmission | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: -1.6019e-08; Actual Q2: -1.4171e-17; Actual Q3: -1.405e-17; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
|  | 2.t.3.b.i | Transmission | HFTD Tier 3 | Rural | WUI | Actual Q1: 4.7585; Actual Q2: 4.753; Actual Q3: 4.8328; Actual Q4: 4.46; Actual Q1: 4.458; Actual Q2: 4.46; Actual Q3: 4.46; Actual Q4: 4.46 | 4.46 | 4.46 | 4.46 | Circuit miles
|  | 2.t.3.b.ii | Transmission | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 2.2746; Actual Q2: 2.3199; Actual Q3: 2.3539; Actual Q4: 2.05; Actual Q1: 1.991; Actual Q2: 1.99; Actual Q3: 1.99; Actual Q4: 2.15 | 2.05 | 2.05 | 2.05 | Circuit miles
|  | 2.t.3.c.i | Transmission | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 0.10613; Actual Q2: 0.1053; Actual Q3: 0.11706; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
|  | 2.t.3.c.ii | Transmission | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 0.40749; Actual Q2: 0.40685; Actual Q3: 0.40656; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
| 3. Critical facilities | 3.0.a.i | N/A | Non-HFTD | Urban | WUI | Actual Q1: 2172; Actual Q2: 2205; Actual Q3: 3071; Actual Q4: 3080; Actual Q1: 3071; Actual Q2: 3059; Actual Q3: 3057; Actual Q4: 3045 | 3080 | 3080 | 3080 | Number of critical facilities
|  | 3.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | Actual Q1: 11246; Actual Q2: 11597; Actual Q3: 15603; Actual Q4: 15568; Actual Q1: 15520; Actual Q2: 15400; Actual Q3: 15330; Actual Q4: 15203 | 15568 | 15568 | 15568 | Number of critical facilities
|  | 3.0.b.i | N/A | Non-HFTD | Rural | WUI | Actual Q1: 509; Actual Q2: 518; Actual Q3: 722; Actual Q4: 721; Actual Q1: 719; Actual Q2: 713; Actual Q3: 713; Actual Q4: 710 | 721 | 721 | 721 | Number of critical facilities
|  | 3.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | Actual Q1: 2016; Actual Q2: 2033; Actual Q3: 2615; Actual Q4: 2597; Actual Q1: 2593; Actual Q2: 2551; Actual Q3: 2547; Actual Q4: 2537 | 2597 | 2597 | 2597 | Number of critical facilities
|  | 3.0.c.i | N/A | Non-HFTD | Highly rural | WUI | Actual Q1: 3; Actual Q2: 3; Actual Q3: 3; Actual Q4: 3; Actual Q1: 3; Actual Q2: 3; Actual Q3: 3; Actual Q4: 3 | 3 | 3 | 3 | Number of critical facilities
|  | 3.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 115; Actual Q2: 112; Actual Q3: 138; Actual Q4: 137; Actual Q1: 139; Actual Q2: 138; Actual Q3: 138; Actual Q4: 138 | 137 | 137 | 137 | Number of critical facilities
|  | 3.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | Actual Q1: 683; Actual Q2: 690; Actual Q3: 889; Actual Q4: 879; Actual Q1: 879; Actual Q2: 877; Actual Q3: 880; Actual Q4: 882 | 879 | 879 | 879 | Number of critical facilities
|  | 3.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 243; Actual Q2: 244; Actual Q3: 346; Actual Q4: 346; Actual Q1: 344; Actual Q2: 342; Actual Q3: 342; Actual Q4: 340 | 346 | 346 | 346 | Number of critical facilities
|  | 3.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | Actual Q1: 778; Actual Q2: 824; Actual Q3: 1067; Actual Q4: 1060; Actual Q1: 1056; Actual Q2: 1051; Actual Q3: 1048; Actual Q4: 1047 | 1060 | 1060 | 1060 | Number of critical facilities
|  | 3.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 588; Actual Q2: 595; Actual Q3: 958; Actual Q4: 945; Actual Q1: 952; Actual Q2: 934; Actual Q3: 935; Actual Q4: 934 | 945 | 945 | 945 | Number of critical facilities
|  | 3.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 18; Actual Q2: 18; Actual Q3: 20; Actual Q4: 20; Actual Q1: 20; Actual Q2: 20; Actual Q3: 20; Actual Q4: 20 | 20 | 20 | 20 | Number of critical facilities
|  | 3.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 58; Actual Q2: 59; Actual Q3: 83; Actual Q4: 83; Actual Q1: 83; Actual Q2: 82; Actual Q3: 81; Actual Q4: 81 | 83 | 83 | 83 | Number of critical facilities
|  | 3.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | Actual Q1: 5; Actual Q2: 5; Actual Q3: 5; Actual Q4: 5; Actual Q1: 5; Actual Q2: 4; Actual Q3: 4; Actual Q4: 4 | 5 | 5 | 5 | Number of critical facilities
|  | 3.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of critical facilities
|  | 3.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | Actual Q1: 396; Actual Q2: 402; Actual Q3: 518; Actual Q4: 517; Actual Q1: 519; Actual Q2: 519; Actual Q3: 519; Actual Q4: 515 | 517 | 517 | 517 | Number of critical facilities
|  | 3.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 611; Actual Q2: 628; Actual Q3: 795; Actual Q4: 793; Actual Q1: 785; Actual Q2: 783; Actual Q3: 784; Actual Q4: 781 | 793 | 793 | 793 | Number of critical facilities
|  | 3.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 26; Actual Q2: 31; Actual Q3: 44; Actual Q4: 44; Actual Q1: 45; Actual Q2: 45; Actual Q3: 45; Actual Q4: 45 | 44 | 44 | 44 | Number of critical facilities
|  | 3.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 56; Actual Q2: 58; Actual Q3: 75; Actual Q4: 75; Actual Q1: 76; Actual Q2: 76; Actual Q3: 76; Actual Q4: 76 | 75 | 75 | 75 | Number of critical facilities
| 4. Residential customers | 4.0.a.i | N/A | Non-HFTD | Urban | WUI | Actual Q4: 201832; Actual Q1: 202677; Actual Q2: 202851; Actual Q3: 202899; Actual Q4: 202909 | 201832 | 201832 | 201832 | Number of residential customers | GIS is an as-built system, historical customer counts are not available.
|  | 4.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | Actual Q4: 875662; Actual Q1: 880414; Actual Q2: 882243; Actual Q3: 884158; Actual Q4: 885546 | 875662 | 875662 | 875662 | Number of residential customers | GIS is an as-built system, historical customer counts are not available.
|  | 4.0.b.i | N/A | Non-HFTD | Rural | WUI | Actual Q4: 36776; Actual Q1: 36938; Actual Q2: 36985; Actual Q3: 37005; Actual Q4: 37050 | 36776 | 36776 | 36776 | Number of residential customers | GIS is an as-built system, historical customer counts are not available.
|  | 4.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | Actual Q4: 38010; Actual Q1: 38473; Actual Q2: 38632; Actual Q3: 38703; Actual Q4: 38803 | 38010 | 38010 | 38010 | Number of residential customers | GIS is an as-built system, historical customer counts are not available.
|  | 4.0.c.i | N/A | Non-HFTD | Highly rural | WUI | Actual Q4: 994; Actual Q1: 997; Actual Q2: 996; Actual Q3: 996; Actual Q4: 999 | 994 | 994 | 994 | Number of residential customers | GIS is an as-built system, historical customer counts are not available.
|  | 4.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | Actual Q4: 1665; Actual Q1: 1668; Actual Q2: 1678; Actual Q3: 1680; Actual Q4: 1678 | 1665 | 1665 | 1665 | Number of residential customers | GIS is an as-built system, historical customer counts are not available.
|  | 4.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | Actual Q4: 66347; Actual Q1: 66670; Actual Q2: 66798; Actual Q3: 66994; Actual Q4: 67135 | 66347 | 66347 | 66347 | Number of residential customers | GIS is an as-built system, historical customer counts are not available.
|  | 4.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | Actual Q4: 16620; Actual Q1: 16949; Actual Q2: 17030; Actual Q3: 17056; Actual Q4: 17096 | 16620 | 16620 | 16620 | Number of residential customers | GIS is an as-built system, historical customer counts are not available.
|  | 4.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | Actual Q4: 58039; Actual Q1: 58206; Actual Q2: 58249; Actual Q3: 58306; Actual Q4: 58507 | 58039 | 58039 | 58039 | Number of residential customers | GIS is an as-built system, historical customer counts are not available.
|  | 4.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | Actual Q4: 19964; Actual Q1: 20341; Actual Q2: 20346; Actual Q3: 20445; Actual Q4: 20583 | 19964 | 19964 | 19964 | Number of residential customers | GIS is an as-built system, historical customer counts are not available.
|  | 4.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | Actual Q4: 273; Actual Q1: 273; Actual Q2: 271; Actual Q3: 269; Actual Q4: 269 | 273 | 273 | 273 | Number of residential customers | GIS is an as-built system, historical customer counts are not available.
|  | 4.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q4: 468; Actual Q1: 472; Actual Q2: 474; Actual Q3: 475; Actual Q4: 477 | 468 | 468 | 468 | Number of residential customers | GIS is an as-built system, historical customer counts are not available.
|  | 4.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | Actual Q4: 100; Actual Q1: 100; Actual Q2: 100; Actual Q3: 101; Actual Q4: 101 | 100 | 100 | 100 | Number of residential customers | GIS is an as-built system, historical customer counts are not available.
|  | 4.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | Actual Q4: 3; Actual Q1: 3; Actual Q2: 3; Actual Q3: 3; Actual Q4: 3 | 3 | 3 | 3 | Number of residential customers | GIS is an as-built system, historical customer counts are not available.
|  | 4.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | Actual Q4: 18008; Actual Q1: 18094; Actual Q2: 18106; Actual Q3: 18128; Actual Q4: 18125 | 18008 | 18008 | 18008 | Number of residential customers | GIS is an as-built system, historical customer counts are not available.
|  | 4.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | Actual Q4: 6882; Actual Q1: 7015; Actual Q2: 7051; Actual Q3: 7053; Actual Q4: 7031 | 6882 | 6882 | 6882 | Number of residential customers | GIS is an as-built system, historical customer counts are not available.
|  | 4.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | Actual Q4: 911; Actual Q1: 912; Actual Q2: 913; Actual Q3: 912; Actual Q4: 911 | 911 | 911 | 911 | Number of residential customers | GIS is an as-built system, historical customer counts are not available.
|  | 4.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q4: 857; Actual Q1: 861; Actual Q2: 862; Actual Q3: 863; Actual Q4: 861 | 857 | 857 | 857 | Number of residential customers | GIS is an as-built system, historical customer counts are not available.
| 5. Commercial customers | 5.0.a.i | N/A | Non-HFTD | Urban | WUI | Actual Q4: 14613; Actual Q1: 14582; Actual Q2: 14595; Actual Q3: 14654; Actual Q4: 14655 | 14613 | 14613 | 14613 | Number of commercial customers | GIS is an as-built system, historical customer counts are not available.
|  | 5.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | Actual Q4: 92909; Actual Q1: 93333; Actual Q2: 93500; Actual Q3: 93604; Actual Q4: 93564 | 92909 | 92909 | 92909 | Number of commercial customers | GIS is an as-built system, historical customer counts are not available.
|  | 5.0.b.i | N/A | Non-HFTD | Rural | WUI | Actual Q4: 4569; Actual Q1: 4578; Actual Q2: 4569; Actual Q3: 4563; Actual Q4: 4569 | 4569 | 4569 | 4569 | Number of commercial customers | GIS is an as-built system, historical customer counts are not available.
|  | 5.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | Actual Q4: 24860; Actual Q1: 24825; Actual Q2: 24888; Actual Q3: 24882; Actual Q4: 24920 | 24860 | 24860 | 24860 | Number of commercial customers | GIS is an as-built system, historical customer counts are not available.
|  | 5.0.c.i | N/A | Non-HFTD | Highly rural | WUI | Actual Q4: 100; Actual Q1: 100; Actual Q2: 101; Actual Q3: 99; Actual Q4: 99 | 100 | 100 | 100 | Number of commercial customers | GIS is an as-built system, historical customer counts are not available.
|  | 5.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | Actual Q4: 548; Actual Q1: 547; Actual Q2: 533; Actual Q3: 529; Actual Q4: 528 | 548 | 548 | 548 | Number of commercial customers | GIS is an as-built system, historical customer counts are not available.
|  | 5.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | Actual Q4: 4247; Actual Q1: 4343; Actual Q2: 4347; Actual Q3: 4357; Actual Q4: 4375 | 4247 | 4247 | 4247 | Number of commercial customers | GIS is an as-built system, historical customer counts are not available.
|  | 5.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | Actual Q4: 2364; Actual Q1: 2395; Actual Q2: 2385; Actual Q3: 2404; Actual Q4: 2406 | 2364 | 2364 | 2364 | Number of commercial customers | GIS is an as-built system, historical customer counts are not available.
|  | 5.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | Actual Q4: 5018; Actual Q1: 5027; Actual Q2: 4994; Actual Q3: 4991; Actual Q4: 4978 | 5018 | 5018 | 5018 | Number of commercial customers | GIS is an as-built system, historical customer counts are not available.
|  | 5.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | Actual Q4: 4076; Actual Q1: 4106; Actual Q2: 4101; Actual Q3: 4105; Actual Q4: 4137 | 4076 | 4076 | 4076 | Number of commercial customers | GIS is an as-built system, historical customer counts are not available.
|  | 5.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | Actual Q4: 44; Actual Q1: 44; Actual Q2: 44; Actual Q3: 44; Actual Q4: 44 | 44 | 44 | 44 | Number of commercial customers | GIS is an as-built system, historical customer counts are not available.
|  | 5.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q4: 214; Actual Q1: 212; Actual Q2: 209; Actual Q3: 209; Actual Q4: 206 | 214 | 214 | 214 | Number of commercial customers | GIS is an as-built system, historical customer counts are not available.
|  | 5.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | Actual Q4: 18; Actual Q1: 18; Actual Q2: 17; Actual Q3: 16; Actual Q4: 16 | 18 | 18 | 18 | Number of commercial customers | GIS is an as-built system, historical customer counts are not available.
|  | 5.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of commercial customers | GIS is an as-built system, historical customer counts are not available.
|  | 5.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | Actual Q4: 2300; Actual Q1: 2320; Actual Q2: 2314; Actual Q3: 2305; Actual Q4: 2296 | 2300 | 2300 | 2300 | Number of commercial customers | GIS is an as-built system, historical customer counts are not available.
|  | 5.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | Actual Q4: 2506; Actual Q1: 2521; Actual Q2: 2485; Actual Q3: 2503; Actual Q4: 2498 | 2506 | 2506 | 2506 | Number of commercial customers | GIS is an as-built system, historical customer counts are not available.
|  | 5.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | Actual Q4: 139; Actual Q1: 142; Actual Q2: 143; Actual Q3: 143; Actual Q4: 143 | 139 | 139 | 139 | Number of commercial customers | GIS is an as-built system, historical customer counts are not available.
|  | 5.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q4: 363; Actual Q1: 366; Actual Q2: 363; Actual Q3: 364; Actual Q4: 366 | 363 | 363 | 363 | Number of commercial customers | GIS is an as-built system, historical customer counts are not available.
| 6. AFN customers | 6.0.a.i | N/A | Non-HFTD | Urban | WUI | Actual Q4: 46089; Actual Q1: 46858; Actual Q2: 46116; Actual Q3: 46429; Actual Q4: 47132 | 46089 | 46089 | 46089 | Number of customers belonging to access and functional needs populations | GIS is an as-built system, historical customer counts are not available.
|  | 6.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | Actual Q4: 323802; Actual Q1: 325109; Actual Q2: 319330; Actual Q3: 318149; Actual Q4: 316695 | 323802 | 323802 | 323802 | Number of customers belonging to access and functional needs populations | GIS is an as-built system, historical customer counts are not available.
|  | 6.0.b.i | N/A | Non-HFTD | Rural | WUI | Actual Q4: 8143; Actual Q1: 8267; Actual Q2: 8096; Actual Q3: 8074; Actual Q4: 8281 | 8143 | 8143 | 8143 | Number of customers belonging to access and functional needs populations | GIS is an as-built system, historical customer counts are not available.
|  | 6.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | Actual Q4: 9074; Actual Q1: 9216; Actual Q2: 9068; Actual Q3: 9119; Actual Q4: 9557 | 9074 | 9074 | 9074 | Number of customers belonging to access and functional needs populations | GIS is an as-built system, historical customer counts are not available.
|  | 6.0.c.i | N/A | Non-HFTD | Highly rural | WUI | Actual Q4: 301; Actual Q1: 298; Actual Q2: 297; Actual Q3: 299; Actual Q4: 318 | 301 | 301 | 301 | Number of customers belonging to access and functional needs populations | GIS is an as-built system, historical customer counts are not available.
|  | 6.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | Actual Q4: 451; Actual Q1: 440; Actual Q2: 438; Actual Q3: 434; Actual Q4: 435 | 451 | 451 | 451 | Number of customers belonging to access and functional needs populations | GIS is an as-built system, historical customer counts are not available.
|  | 6.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | Actual Q4: 14517; Actual Q1: 14818; Actual Q2: 14590; Actual Q3: 14719; Actual Q4: 14984 | 14517 | 14517 | 14517 | Number of customers belonging to access and functional needs populations | GIS is an as-built system, historical customer counts are not available.
|  | 6.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | Actual Q4: 5670; Actual Q1: 5663; Actual Q2: 5560; Actual Q3: 5531; Actual Q4: 5243 | 5670 | 5670 | 5670 | Number of customers belonging to access and functional needs populations | GIS is an as-built system, historical customer counts are not available.
|  | 6.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | Actual Q4: 11939; Actual Q1: 12174; Actual Q2: 11975; Actual Q3: 12101; Actual Q4: 12219 | 11939 | 11939 | 11939 | Number of customers belonging to access and functional needs populations | GIS is an as-built system, historical customer counts are not available.
|  | 6.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | Actual Q4: 4079; Actual Q1: 4179; Actual Q2: 4063; Actual Q3: 4113; Actual Q4: 4449 | 4079 | 4079 | 4079 | Number of customers belonging to access and functional needs populations | GIS is an as-built system, historical customer counts are not available.
|  | 6.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | Actual Q4: 94; Actual Q1: 95; Actual Q2: 93; Actual Q3: 95; Actual Q4: 99 | 94 | 94 | 94 | Number of customers belonging to access and functional needs populations | GIS is an as-built system, historical customer counts are not available.
|  | 6.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q4: 177; Actual Q1: 173; Actual Q2: 163; Actual Q3: 161; Actual Q4: 148 | 177 | 177 | 177 | Number of customers belonging to access and functional needs populations | GIS is an as-built system, historical customer counts are not available.
|  | 6.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | Actual Q4: 31; Actual Q1: 31; Actual Q2: 30; Actual Q3: 29; Actual Q4: 27 | 31 | 31 | 31 | Number of customers belonging to access and functional needs populations | GIS is an as-built system, historical customer counts are not available.
|  | 6.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | Actual Q4: 2; Actual Q1: 2; Actual Q2: 2; Actual Q3: 2; Actual Q4: 1 | 2 | 2 | 2 | Number of customers belonging to access and functional needs populations | GIS is an as-built system, historical customer counts are not available.
|  | 6.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | Actual Q4: 5213; Actual Q1: 5331; Actual Q2: 5211; Actual Q3: 5303; Actual Q4: 5525 | 5213 | 5213 | 5213 | Number of customers belonging to access and functional needs populations | GIS is an as-built system, historical customer counts are not available.
|  | 6.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | Actual Q4: 1885; Actual Q1: 1930; Actual Q2: 1884; Actual Q3: 1934; Actual Q4: 1965 | 1885 | 1885 | 1885 | Number of customers belonging to access and functional needs populations | GIS is an as-built system, historical customer counts are not available.
|  | 6.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | Actual Q4: 255; Actual Q1: 259; Actual Q2: 245; Actual Q3: 253; Actual Q4: 266 | 255 | 255 | 255 | Number of customers belonging to access and functional needs populations | GIS is an as-built system, historical customer counts are not available.
|  | 6.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q4: 243; Actual Q1: 240; Actual Q2: 238; Actual Q3: 239; Actual Q4: 204 | 243 | 243 | 243 | Number of customers belonging to access and functional needs populations | GIS is an as-built system, historical customer counts are not available.
| 7. Substations | 7.0.a.i | N/A | Non-HFTD | Urban | WUI | Actual Q1: 12; Actual Q2: 12; Actual Q3: 12; Actual Q4: 12; Actual Q1: 12; Actual Q2: 12; Actual Q3: 12; Actual Q4: 12 | 12 | 12 | 12 | Number of substations
|  | 7.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | Actual Q1: 66; Actual Q2: 66; Actual Q3: 66; Actual Q4: 66; Actual Q1: 66; Actual Q2: 66; Actual Q3: 66; Actual Q4: 66 | 66 | 66 | 66 | Number of substations
|  | 7.0.b.i | N/A | Non-HFTD | Rural | WUI | Actual Q1: 4; Actual Q2: 4; Actual Q3: 4; Actual Q4: 4; Actual Q1: 4; Actual Q2: 4; Actual Q3: 4; Actual Q4: 4 | 4 | 4 | 4 | Number of substations
|  | 7.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | Actual Q1: 26; Actual Q2: 26; Actual Q3: 26; Actual Q4: 26; Actual Q1: 26; Actual Q2: 26; Actual Q3: 26; Actual Q4: 26 | 26 | 26 | 26 | Number of substations
|  | 7.0.c.i | N/A | Non-HFTD | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations
|  | 7.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 3; Actual Q2: 3; Actual Q3: 3; Actual Q4: 3; Actual Q1: 3; Actual Q2: 3; Actual Q3: 3; Actual Q4: 3 | 3 | 3 | 3 | Number of substations
|  | 7.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | [16 empty] | 1 | 0 | 0 | Number of substations | bar: Actual Q1 to Actual Q4
|  | 7.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 5; Actual Q2: 5; Actual Q3: 5; Actual Q4: 5; Actual Q1: 5; Actual Q2: 5; Actual Q3: 5; Actual Q4: 5 | 5 | 5 | 5 | Number of substations
|  | 7.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | Actual Q1: 5; Actual Q2: 5; Actual Q3: 5; Actual Q4: 5; Actual Q1: 5; Actual Q2: 5; Actual Q3: 5; Actual Q4: 5 | 5 | 5 | 5 | Number of substations
|  | 7.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 23; Actual Q2: 23; Actual Q3: 23; Actual Q4: 23; Actual Q1: 23; Actual Q2: 23; Actual Q3: 23; Actual Q4: 23 | 23 | 21 | 21 | Number of substations
|  | 7.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations
|  | 7.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | [16 empty] | 1 | 1 | 1 | Number of substations | bar: Actual Q1 to Actual Q4
|  | 7.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations
|  | 7.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations
|  | 7.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations
|  | 7.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 11; Actual Q2: 11; Actual Q3: 11; Actual Q4: 11; Actual Q1: 11; Actual Q2: 11; Actual Q3: 11; Actual Q4: 11 | 11 | 11 | 11 | Number of substations
|  | 7.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations
|  | 7.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 2; Actual Q2: 2; Actual Q3: 2; Actual Q4: 2; Actual Q1: 2; Actual Q2: 2; Actual Q3: 2; Actual Q4: 2 | 2 | 2 | 2 | Number of substations
| 8. Weather stations | 8.0.a.i | N/A | Non-HFTD | Urban | WUI | Actual Q1: 3; Actual Q2: 3; Actual Q3: 3; Actual Q4: 3; Actual Q1: 3; Actual Q2: 3; Actual Q3: 3; Actual Q4: 3 | 3 | 3 | 3 | Number of weather stations
|  | 8.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | Actual Q1: 12; Actual Q2: 12; Actual Q3: 12; Actual Q4: 13; Actual Q1: 13; Actual Q2: 13; Actual Q3: 13; Actual Q4: 13 | 13 | 13 | 13 | Number of weather stations
|  | 8.0.b.i | N/A | Non-HFTD | Rural | WUI | [16 empty] | 1 | 1 | 1 | Number of weather stations | bar: Actual Q1 to Actual Q4
|  | 8.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | Actual Q1: 3; Actual Q2: 3; Actual Q3: 3; Actual Q4: 3; Actual Q1: 3; Actual Q2: 3; Actual Q3: 3; Actual Q4: 3 | 3 | 3 | 3 | Number of weather stations
|  | 8.0.c.i | N/A | Non-HFTD | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of weather stations
|  | 8.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 2; Actual Q2: 2; Actual Q3: 2; Actual Q4: 2; Actual Q1: 2; Actual Q2: 2; Actual Q3: 2; Actual Q4: 2 | 2 | 2 | 2 | Number of weather stations
|  | 8.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | Actual Q1: 2; Actual Q2: 2; Actual Q3: 2; Actual Q4: 2; Actual Q1: 2; Actual Q2: 2; Actual Q3: 2; Actual Q4: 2 | 2 | 2 | 2 | Number of weather stations
|  | 8.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 4; Actual Q2: 4; Actual Q3: 4; Actual Q4: 4; Actual Q1: 4; Actual Q2: 4; Actual Q3: 4; Actual Q4: 4 | 4 | 4 | 4 | Number of weather stations
|  | 8.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | Actual Q1: 12; Actual Q2: 12; Actual Q3: 16; Actual Q4: 16; Actual Q1: 16; Actual Q2: 16; Actual Q3: 16; Actual Q4: 16 | 16 | 16 | 16 | Number of weather stations
|  | 8.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 42; Actual Q2: 42; Actual Q3: 52; Actual Q4: 52; Actual Q1: 52; Actual Q2: 52; Actual Q3: 52; Actual Q4: 52 | 52 | 52 | 52 | Number of weather stations
|  | 8.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | [16 empty] | 1 | 1 | 1 | Number of weather stations | bar: Actual Q1 to Actual Q4
|  | 8.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 7; Actual Q2: 7; Actual Q3: 7; Actual Q4: 7; Actual Q1: 7; Actual Q2: 7; Actual Q3: 7; Actual Q4: 7 | 7 | 7 | 7 | Number of weather stations
|  | 8.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of weather stations
|  | 8.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of weather stations
|  | 8.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | Actual Q1: 11; Actual Q2: 11; Actual Q3: 12; Actual Q4: 11; Actual Q1: 11; Actual Q2: 11; Actual Q3: 11; Actual Q4: 11 | 11 | 11 | 11 | Number of weather stations
|  | 8.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 74; Actual Q2: 74; Actual Q3: 83; Actual Q4: 85; Actual Q1: 85; Actual Q2: 85; Actual Q3: 85; Actual Q4: 85 | 85 | 85 | 85 | Number of weather stations
|  | 8.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 2; Actual Q2: 2; Actual Q3: 2; Actual Q4: 2; Actual Q1: 2; Actual Q2: 2; Actual Q3: 2; Actual Q4: 2 | 2 | 2 | 2 | Number of weather stations
|  | 8.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 16; Actual Q2: 16; Actual Q3: 18; Actual Q4: 18; Actual Q1: 18; Actual Q2: 18; Actual Q3: 18; Actual Q4: 18 | 18 | 18 | 18 | Number of weather stations

## Table 8
Utility | SDG&E |  |  |  |  | Notes:
Table No. | 8 |  |  |  |  | Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV. Report net additions using positive numbers and net removals and undergrounding using negative numbers for circuit miles and numbers of substations. Only report changes expected within the target year.
Date Modified | 2024-02-01 |  |  |  |  | For example, if 20 net overhead circuit miles are planned for addition by 2023, with 15 being added by 2022 and 5 more added by 2023, then report “15” for 2022 and “5” for 2023. Do not report cumulative change across years. In this case, do not report “20” for 2023, but instead the number planned to be added for just that year, which is “5”.
[6 empty] | Actual | [15 empty] | Projected
Table 8: Location of utility equipment additions or removal | [5 empty] | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4
Metric type | # | Line Type | HFTD Tier | Area Type | WUI Status | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | 2024 | 2024 | 2024 | 2024 | 2025 | 2025 | 2025 | 2025 | 2023 | 2024 | 2025 | Unit(s) | Comments | Blank Meaning
1. Planned net addition (or removal) - overhead circuit miles | 1.d.0.a.i | Distribution | Non-HFTD | Urban | WUI | Actual Q1: -0.41402; Actual Q2: -0.58598; Actual Q3: -1.4; Actual Q4: -3.45; Actual Q1: -1.979; Actual Q2: -0.191; Actual Q3: -0.32; Actual Q4: -0.22 | 0 | -0.12 | 0 | Circuit miles
| 1.d.0.a.ii | Distribution | Non-HFTD | Urban | Non-WUI | Actual Q1: -0.79394; Actual Q2: -1.8061; Actual Q3: -4.3; Actual Q4: -6.28; Actual Q1: -0.401; Actual Q2: -0.369; Actual Q3: -2.21; Actual Q4: -2.69 | 0 | -0.34 | 0 | Circuit miles
| 1.d.0.b.i | Distribution | Non-HFTD | Rural | WUI | Actual Q1: -0.12481; Actual Q2: -1.6752; Actual Q3: -0.4; Actual Q4: -4.04; Actual Q1: 0.139; Actual Q2: 0.101; Actual Q3: -0.13; Actual Q4: -0.01 | 0 | 0 | 0 | Circuit miles
| 1.d.0.b.ii | Distribution | Non-HFTD | Rural | Non-WUI | Actual Q1: -0.14754; Actual Q2: -0.65246; Actual Q3: -0.6; Actual Q4: -2.38; Actual Q1: 1.824; Actual Q2: -0.794; Actual Q3: 0; Actual Q4: -1.2 | 0 | 0 | 0 | Circuit miles
| 1.d.0.c.i | Distribution | Non-HFTD | Highly rural | WUI | Actual Q1: -0.01875; Actual Q2: 0.01875; Actual Q3: 0; Actual Q4: -0.02; Actual Q1: 0.001; Actual Q2: 0.149; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
| 1.d.0.c.ii | Distribution | Non-HFTD | Highly rural | Non-WUI | Actual Q1: -0.096781; Actual Q2: -1.5032; Actual Q3: -0.1; Actual Q4: 0.09; Actual Q1: 0.106; Actual Q2: 0.114; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
| 1.d.2.a.i | Distribution | HFTD Tier 2 | Urban | WUI | Actual Q1: -0.10303; Actual Q2: 0.003031; Actual Q3: 0; Actual Q4: -4.34; Actual Q1: 0.158; Actual Q2: 0.032; Actual Q3: 0.18; Actual Q4: -0.05 | 0 | -0.15 | 0 | Circuit miles
| 1.d.2.a.ii | Distribution | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 0.007765; Actual Q2: -0.007765; Actual Q3: 0.6; Actual Q4: -2.63; Actual Q1: 0.039; Actual Q2: 0.461; Actual Q3: -0.04; Actual Q4: -0.04 | -0.2 | 0 | -0.44 | Circuit miles
| 1.d.2.b.i | Distribution | HFTD Tier 2 | Rural | WUI | Actual Q1: -1.0822; Actual Q2: 1.0822; Actual Q3: -0.9; Actual Q4: -3.96; Actual Q1: 0.048; Actual Q2: 0.812; Actual Q3: 0.51; Actual Q4: -0.39 | -12.28 | -0.09 | -55.41 | Circuit miles
| 1.d.2.b.ii | Distribution | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: -0.49602; Actual Q2: -0.50398; Actual Q3: -1.1; Actual Q4: -4.55; Actual Q1: -1.426; Actual Q2: -1.584; Actual Q3: 0.04; Actual Q4: -3.71 | -27.64 | -3.22 | -19.7 | Circuit miles
| 1.d.2.c.i | Distribution | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 0.07803; Actual Q2: -0.17803; Actual Q3: 0; Actual Q4: -0.03; Actual Q1: 0.005; Actual Q2: 0.125; Actual Q3: 0; Actual Q4: 0 | 0 | -4.72 | -1.33 | Circuit miles
| 1.d.2.c.ii | Distribution | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 0.57803; Actual Q2: -0.67803; Actual Q3: -0.3; Actual Q4: -0.22; Actual Q1: -0.656; Actual Q2: 0.586; Actual Q3: 0; Actual Q4: -0.02 | 0 | -46.05 | -7.6 | Circuit miles
| 1.d.3.a.i | Distribution | HFTD Tier 3 | Urban | WUI | Actual Q1: -0.039774; Actual Q2: 0.039774; Actual Q3: 0; Actual Q4: -0.53; Actual Q1: 0.006; Actual Q2: 0.124; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
| 1.d.3.a.ii | Distribution | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: -0.001136; Actual Q2: 0.001136; Actual Q3: 0; Actual Q4: -0.06; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
| 1.d.3.b.i | Distribution | HFTD Tier 3 | Rural | WUI | Actual Q1: -0.054168; Actual Q2: -1.2458; Actual Q3: -2; Actual Q4: -2; Actual Q1: -4.952; Actual Q2: 1.572; Actual Q3: -1.44; Actual Q4: -5.93 | -18.23 | -18.94 | -54.3 | Circuit miles
| 1.d.3.b.ii | Distribution | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 0.034091; Actual Q2: -0.93409; Actual Q3: -0.7; Actual Q4: -4.88; Actual Q1: -4.754; Actual Q2: 1.114; Actual Q3: 0.18; Actual Q4: -3.97 | -37.74 | -61.67 | -74.66 | Circuit miles
| 1.d.3.c.i | Distribution | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 0.070264; Actual Q2: 0.12974; Actual Q3: 0; Actual Q4: -1.38; Actual Q1: 0.001; Actual Q2: 0.099; Actual Q3: -0.49; Actual Q4: -0.02 | -1.76 | -0.8 | -4.16 | Circuit miles
| 1.d.3.c.ii | Distribution | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: -0.098295; Actual Q2: 0.99829; Actual Q3: -0.1; Actual Q4: -1.59; Actual Q1: -0.056; Actual Q2: 0.256; Actual Q3: -0.07; Actual Q4: 0 | -36.03 | -12.69 | -9.51 | Circuit miles
| 1.t.0.a.i | Transmission | Non-HFTD | Urban | WUI | Actual Q1: -0.27955; Actual Q2: -0.020454; Actual Q3: -0.7; Actual Q4: -8.59; Actual Q1: 1.724; Actual Q2: -0.004; Actual Q3: 0; Actual Q4: -0.03 | 0.5 | 0 | 0 | Circuit miles
| 1.t.0.a.ii | Transmission | Non-HFTD | Urban | Non-WUI | Actual Q1: 0.13826; Actual Q2: 0.061742; Actual Q3: 0.7; Actual Q4: -7.54; Actual Q1: 1.535; Actual Q2: -0.005; Actual Q3: -0.01; Actual Q4: -0.08 | 0 | 0 | 0 | Circuit miles
| 1.t.0.b.i | Transmission | Non-HFTD | Rural | WUI | Actual Q1: -0.033902; Actual Q2: 0.033902; Actual Q3: 0; Actual Q4: -6.04; Actual Q1: -0.025; Actual Q2: -0.005; Actual Q3: 0.05; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
| 1.t.0.b.ii | Transmission | Non-HFTD | Rural | Non-WUI | Actual Q1: -0.010985; Actual Q2: 0.010985; Actual Q3: 0; Actual Q4: -1.32; Actual Q1: -0.21; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | -0.9 | 0 | Circuit miles
| 1.t.0.c.i | Transmission | Non-HFTD | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
| 1.t.0.c.ii | Transmission | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 0.005681; Actual Q2: -0.005681; Actual Q3: 0; Actual Q4: 0.01; Actual Q1: -0.004; Actual Q2: 0.004; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
| 1.t.2.a.i | Transmission | HFTD Tier 2 | Urban | WUI | Actual Q1: -0.086932; Actual Q2: -0.013068; Actual Q3: 0; Actual Q4: -5.69; Actual Q1: 0.152; Actual Q2: 0.158; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
| 1.t.2.a.ii | Transmission | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: -0.05; Actual Q2: 0.05; Actual Q3: 0; Actual Q4: -7.88; Actual Q1: 1.279; Actual Q2: 0.001; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
| 1.t.2.b.i | Transmission | HFTD Tier 2 | Rural | WUI | Actual Q1: -0.20076; Actual Q2: 0.000758; Actual Q3: 0; Actual Q4: -9.31; Actual Q1: 0.033; Actual Q2: -0.123; Actual Q3: -2.51; Actual Q4: -0.01 | 0 | 0 | 0 | Circuit miles
| 1.t.2.b.ii | Transmission | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: -0.13864; Actual Q2: -0.66136; Actual Q3: -0.1; Actual Q4: -2.07; Actual Q1: 0.587; Actual Q2: 0.043; Actual Q3: -0.72; Actual Q4: 0.65 | 0 | 0 | 0 | Circuit miles
| 1.t.2.c.i | Transmission | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
| 1.t.2.c.ii | Transmission | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 0.025; Actual Q2: -0.025; Actual Q3: 0; Actual Q4: 0.02; Actual Q1: 0.005; Actual Q2: -0.005; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
| 1.t.3.a.i | Transmission | HFTD Tier 3 | Urban | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
| 1.t.3.a.ii | Transmission | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
| 1.t.3.b.i | Transmission | HFTD Tier 3 | Rural | WUI | Actual Q1: -0.11515; Actual Q2: 0.015153; Actual Q3: 0.1; Actual Q4: 0.12; Actual Q1: 0.006; Actual Q2: -0.006; Actual Q3: -0.58; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
| 1.t.3.b.ii | Transmission | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 0.11553; Actual Q2: -0.01553; Actual Q3: -0.1; Actual Q4: 1.29; Actual Q1: 0.005; Actual Q2: -0.005; Actual Q3: -3.26; Actual Q4: 0.01 | 0 | 0 | 0 | Circuit miles
| 1.t.3.c.i | Transmission | HFTD Tier 3 | Highly rural | WUI | Actual Q1: -0.038826; Actual Q2: 0.038826; Actual Q3: 0; Actual Q4: -0.08; Actual Q1: -0.003; Actual Q2: 0.003; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
| 1.t.3.c.ii | Transmission | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 0.050189; Actual Q2: -0.050189; Actual Q3: 0; Actual Q4: -0.02; Actual Q1: 0.005; Actual Q2: -0.005; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
2. Planned net addition (or removal) - underground circuit miles | 2.d.0.a.i | Distribution | Non-HFTD | Urban | WUI | Actual Q1: 1.4302; Actual Q2: 1.3661; Actual Q3: 3.3155; Actual Q4: -8.2779; Actual Q1: 0.625; Actual Q2: 1.825; Actual Q3: 2.98; Actual Q4: 2.9 | 0 | 0 | 0 | Circuit miles
| 2.d.0.a.ii | Distribution | Non-HFTD | Urban | Non-WUI | Actual Q1: 1.852; Actual Q2: 8.8264; Actual Q3: 9.4321; Actual Q4: -9.1997; Actual Q1: 3.361; Actual Q2: 5.399; Actual Q3: 8.34; Actual Q4: 5.52 | 0 | 0 | 0 | Circuit miles
| 2.d.0.b.i | Distribution | Non-HFTD | Rural | WUI | Actual Q1: 0.80729; Actual Q2: 0.25668; Actual Q3: 0.18354; Actual Q4: -22.4133; Actual Q1: 0.371; Actual Q2: 0.339; Actual Q3: 1.25; Actual Q4: 0.54 | 0 | 0 | 0 | Circuit miles
| 2.d.0.b.ii | Distribution | Non-HFTD | Rural | Non-WUI | Actual Q1: 1.972; Actual Q2: 2.3309; Actual Q3: 0.71496; Actual Q4: -27.7794; Actual Q1: 0.368; Actual Q2: 2.642; Actual Q3: 1.19; Actual Q4: 1.58 | 0 | 0 | 0 | Circuit miles
| 2.d.0.c.i | Distribution | Non-HFTD | Highly rural | WUI | Actual Q1: -0.032791; Actual Q2: -0.066138; Actual Q3: 0.0024013; Actual Q4: 0.35; Actual Q1: -0.002; Actual Q2: 0.002; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
| 2.d.0.c.ii | Distribution | Non-HFTD | Highly rural | Non-WUI | Actual Q1: -0.0014608; Actual Q2: -0.59078; Actual Q3: 0.10665; Actual Q4: -2.7082; Actual Q1: 0.482; Actual Q2: -0.002; Actual Q3: 0.19; Actual Q4: 0.31 | 0 | 0 | 0 | Circuit miles
| 2.d.2.a.i | Distribution | HFTD Tier 2 | Urban | WUI | Actual Q1: 0.82952; Actual Q2: 0.32788; Actual Q3: 0.60005; Actual Q4: -11.463; Actual Q1: 0.007; Actual Q2: -0.117; Actual Q3: 0.15; Actual Q4: 0.22 | 0.15 | 0 | 0 | Circuit miles
| 2.d.2.a.ii | Distribution | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 2.1101; Actual Q2: 0.24711; Actual Q3: 0.90699; Actual Q4: -1.75; Actual Q1: 0.038; Actual Q2: 0.322; Actual Q3: 1.98; Actual Q4: 1.27 | 0 | 0.05 | 0.25 | Circuit miles
| 2.d.2.b.i | Distribution | HFTD Tier 2 | Rural | WUI | Actual Q1: 4.8865; Actual Q2: 1.0861; Actual Q3: 2.5994; Actual Q4: -13.1766; Actual Q1: 0.368; Actual Q2: 8.662; Actual Q3: 1.59; Actual Q4: 2.69 | 20.2 | 0.02 | 64.4 | Circuit miles
| 2.d.2.b.ii | Distribution | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 4.3144; Actual Q2: 3.3513; Actual Q3: 4.7704; Actual Q4: 2.4883; Actual Q1: 2.104; Actual Q2: 2.656; Actual Q3: 3.52; Actual Q4: 6.1 | 27.36 | 0.08 | 12.71 | Circuit miles
| 2.d.2.c.i | Distribution | HFTD Tier 2 | Highly rural | WUI | Actual Q1: -0.010213; Actual Q2: 0.010166; Actual Q3: 0.00021707; Actual Q4: -0.0046889; Actual Q1: 0.001; Actual Q2: -0.001; Actual Q3: 0; Actual Q4: 0 | 0 | 11.35 | 1.37 | Circuit miles
| 2.d.2.c.ii | Distribution | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 0.030101; Actual Q2: 0.068041; Actual Q3: 0.001221; Actual Q4: 0.17237; Actual Q1: 0.003; Actual Q2: -0.003; Actual Q3: 0; Actual Q4: 0 | 0 | 52.2 | 8.23 | Circuit miles
| 2.d.3.a.i | Distribution | HFTD Tier 3 | Urban | WUI | Actual Q1: 0.064601; Actual Q2: 0.033724; Actual Q3: 0.00037987; Actual Q4: -2.1357; Actual Q1: -0.003; Actual Q2: 0.003; Actual Q3: 0; Actual Q4: 0.37 | 0.03 | 0 | 0 | Circuit miles
| 2.d.3.a.ii | Distribution | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: -9.8398e-07; Actual Q2: 9.8398e-07; Actual Q3: -1.205e-19; Actual Q4: 8.7413e-16; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
| 2.d.3.b.i | Distribution | HFTD Tier 3 | Rural | WUI | Actual Q1: 3.4649; Actual Q2: 0.85627; Actual Q3: 7.5202; Actual Q4: 14.9028; Actual Q1: 1.164; Actual Q2: 0.236; Actual Q3: 7.19; Actual Q4: 9.29 | 44.03 | 43.31 | 79.53 | Circuit miles
| 2.d.3.b.ii | Distribution | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 1.4559; Actual Q2: 3.3618; Actual Q3: 3.3659; Actual Q4: 3.1139; Actual Q1: 1.119; Actual Q2: 0.931; Actual Q3: 2.43; Actual Q4: 9.58 | 46.45 | 81.3 | 68.55 | Circuit miles
| 2.d.3.c.i | Distribution | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 0.1222; Actual Q2: -0.023989; Actual Q3: 0.78824; Actual Q4: 1.1571; Actual Q1: 0.005; Actual Q2: -0.005; Actual Q3: 1.67; Actual Q4: 0.21 | 10.81 | 6.84 | 5.53 | Circuit miles
| 2.d.3.c.ii | Distribution | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 0.034145; Actual Q2: 0.06351; Actual Q3: 0.2003; Actual Q4: 0.31656; Actual Q1: -0.374; Actual Q2: -0.026; Actual Q3: 1.2; Actual Q4: 0.44 | 41.26 | 21.35 | 8.04 | Circuit miles
| 2.t.0.a.i | Transmission | Non-HFTD | Urban | WUI | Actual Q1: 0.20881; Actual Q2: -0.10508; Actual Q3: -0.21547; Actual Q4: -5.0321; Actual Q1: -0.005; Actual Q2: 0.005; Actual Q3: 2.64; Actual Q4: 0.21 | 0 | 0 | 0 | Circuit miles
| 2.t.0.a.ii | Transmission | Non-HFTD | Urban | Non-WUI | Actual Q1: 0.50174; Actual Q2: -0.18018; Actual Q3: -0.53207; Actual Q4: -13.4803; Actual Q1: 0.001; Actual Q2: -0.081; Actual Q3: 2.98; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
| 2.t.0.b.i | Transmission | Non-HFTD | Rural | WUI | Actual Q1: 0.072826; Actual Q2: -0.036791; Actual Q3: -0.083535; Actual Q4: 0.05332; Actual Q1: 0.174; Actual Q2: -0.004; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
| 2.t.0.b.ii | Transmission | Non-HFTD | Rural | Non-WUI | Actual Q1: 0.1191; Actual Q2: -0.021953; Actual Q3: -0.11496; Actual Q4: 7.9994; Actual Q1: 0.031; Actual Q2: -0.001; Actual Q3: 0; Actual Q4: 0.03 | 0 | 0 | 0 | Circuit miles
| 2.t.0.c.i | Transmission | Non-HFTD | Highly rural | WUI | Actual Q1: 0.0011624; Actual Q2: -0.0022326; Actual Q3: -0.0024013; Actual Q4: -0.28; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
| 2.t.0.c.ii | Transmission | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 0.0058178; Actual Q2: -0.013582; Actual Q3: -0.006653; Actual Q4: -0.61182; Actual Q1: -0.002; Actual Q2: 0.002; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
| 2.t.2.a.i | Transmission | HFTD Tier 2 | Urban | WUI | Actual Q1: 0.089227; Actual Q2: -0.046628; Actual Q3: -0.10005; Actual Q4: 0.693; Actual Q1: -0.001; Actual Q2: 0.001; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
| 2.t.2.a.ii | Transmission | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 0.049037; Actual Q2: -0.0061966; Actual Q3: -0.0069943; Actual Q4: -1.12; Actual Q1: 0.002; Actual Q2: -0.002; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
| 2.t.2.b.i | Transmission | HFTD Tier 2 | Rural | WUI | Actual Q1: 0.17658; Actual Q2: -0.049205; Actual Q3: -0.099414; Actual Q4: -3.3134; Actual Q1: -0.005; Actual Q2: 0.005; Actual Q3: -0.23; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
| 2.t.2.b.ii | Transmission | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 0.10204; Actual Q2: 0.032259; Actual Q3: 0.029603; Actual Q4: 3.0517; Actual Q1: -0.005; Actual Q2: 0.005; Actual Q3: 0.05; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
| 2.t.2.c.i | Transmission | HFTD Tier 2 | Highly rural | WUI | Actual Q1: -1.3799e-05; Actual Q2: 6.1023e-05; Actual Q3: -0.00021707; Actual Q4: -0.025311; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
| 2.t.2.c.ii | Transmission | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 0.0013382; Actual Q2: 0.00052001; Actual Q3: -0.001221; Actual Q4: -0.14237; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
| 2.t.3.a.i | Transmission | HFTD Tier 3 | Urban | WUI | Actual Q1: 0.001309; Actual Q2: 0.00036619; Actual Q3: -0.00037987; Actual Q4: 0.89571; Actual Q1: -0.005; Actual Q2: 0.005; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
| 2.t.3.a.ii | Transmission | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: -1.6019e-08; Actual Q2: 1.6019e-08; Actual Q3: 1.205e-19; Actual Q4: 1.405e-17; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
| 2.t.3.b.i | Transmission | HFTD Tier 3 | Rural | WUI | Actual Q1: 0.084378; Actual Q2: -0.0055129; Actual Q3: 0.079813; Actual Q4: -0.37283; Actual Q1: -0.002; Actual Q2: 0.002; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
| 2.t.3.b.ii | Transmission | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 0.037091; Actual Q2: 0.045235; Actual Q3: 0.03406; Actual Q4: -0.30393; Actual Q1: -0.059; Actual Q2: -0.001; Actual Q3: 0; Actual Q4: 0.16 | 0 | 0 | 0 | Circuit miles
| 2.t.3.c.i | Transmission | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 0.0026089; Actual Q2: -0.00082153; Actual Q3: 0.01176; Actual Q4: -0.11706; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
| 2.t.3.c.ii | Transmission | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 0.0029764; Actual Q2: -0.00063121; Actual Q3: -0.00029561; Actual Q4: -0.40656; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
3. Planned net addition (or removal) - Substations | 3.0.a.i | N/A | Non-HFTD | Urban | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations
| 3.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations
| 3.0.b.i | N/A | Non-HFTD | Rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations
| 3.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations
| 3.0.c.i | N/A | Non-HFTD | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations
| 3.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations
| 3.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | -1 | 0 | Number of substations
| 3.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations
| 3.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 1; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations | Substation removals or addtions are sourced from businesses, table 7 is sourced from GIS database. A small difference is observed due to data digitizing processes.
| 3.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 0; Actual Q2: -1; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | -2 | 0 | Number of substations | Substation removals or addtions are sourced from businesses, table 7 is sourced from GIS database. A small difference is observed due to data digitizing processes.
| 3.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations
| 3.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations
| 3.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations
| 3.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations
| 3.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations
| 3.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations
| 3.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations
| 3.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations
4. Planned net addition (or removal) - Weather stations | 4.0.a.i | N/A | Non-HFTD | Urban | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of weather stations
| 4.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 1; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of weather stations
| 4.0.b.i | N/A | Non-HFTD | Rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of weather stations
| 4.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of weather stations
| 4.0.c.i | N/A | Non-HFTD | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of weather stations
| 4.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of weather stations
| 4.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of weather stations
| 4.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of weather stations
| 4.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 4; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of weather stations | GIS database was updated in 2022 Q3 to true up weather stations records. Addtional weather stations captured in the GIS system were active prior to 2022 submissions.
| 4.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 10; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of weather stations | GIS database was updated in 2022 Q3 to true up weather stations records. Addtional weather stations captured in the GIS system were active prior to 2022 submissions.
| 4.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of weather stations
| 4.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of weather stations
| 4.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of weather stations
| 4.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of weather stations
| 4.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | Actual Q1: -1; Actual Q2: 0; Actual Q3: 1; Actual Q4: -1; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of weather stations
| 4.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 1; Actual Q2: 0; Actual Q3: 9; Actual Q4: 2; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of weather stations | GIS database was updated in 2022 Q3 to true up weather stations records. Addtional weather stations captured in the GIS system were active prior to 2022 submissions.
| 4.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of weather stations
| 4.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 2; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of weather stations

## Table 9
| Utility | SDG&E
| Table No. | 9
| Date Modified | 2024-02-01
[7 empty] | Actual | [15 empty] | Projected
| Table 9: Location of utility infrastructure upgrades | [5 empty] | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4
| Metric type | # | Line Type | HFTD Tier | Area Type | WUI Status | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | 2024 | 2024 | 2024 | 2024 | 2025 | 2025 | 2025 | 2025 | 2023 | 2024 | 2025 | Unit(s) | Comments | Blank Meaning
x | 1. Number of overhead circuit miles planned for upgrade | 1.d.0.a.i | Distribution | Non-HFTD | Urban | WUI | Actual Q1: 0; Actual Q2: 0.25246; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
|  | 1.d.0.a.ii | Distribution | Non-HFTD | Urban | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
|  | 1.d.0.b.i | Distribution | Non-HFTD | Rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0.42918; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
|  | 1.d.0.b.ii | Distribution | Non-HFTD | Rural | Non-WUI | Actual Q1: 0.49743; Actual Q2: 0; Actual Q3: 0.25774; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
|  | 1.d.0.c.i | Distribution | Non-HFTD | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
|  | 1.d.0.c.ii | Distribution | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
|  | 1.d.2.a.i | Distribution | HFTD Tier 2 | Urban | WUI | Actual Q1: 0; Actual Q2: 0.074621; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
|  | 1.d.2.a.ii | Distribution | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0.28977 | 0 | 0.04 | 0 | Circuit miles
|  | 1.d.2.b.i | Distribution | HFTD Tier 2 | Rural | WUI | Actual Q1: 0.54848; Actual Q2: 0.49223; Actual Q3: 2.6024; Actual Q4: 1.5238; Actual Q1: 0.37798; Actual Q2: 4.0121; Actual Q3: 0; Actual Q4: 1.9392 | 5.92 | 19.85 | 2.13 | Circuit miles
|  | 1.d.2.b.ii | Distribution | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 2.4216; Actual Q2: 0; Actual Q3: 0.70887; Actual Q4: 1.2197; Actual Q1: 1.0682; Actual Q2: 4.7399; Actual Q3: 0; Actual Q4: 12.5409 | 17.81 | 40.33 | 7.47 | Circuit miles
|  | 1.d.2.c.i | Distribution | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 0.53804; Actual Q2: 0; Actual Q3: 0.42575; Actual Q4: 1.0501; Actual Q1: 0; Actual Q2: 0; Actual Q3: 5.5961; Actual Q4: 2.736 | 2.1 | 1.43 | 2.21 | Circuit miles
|  | 1.d.2.c.ii | Distribution | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 1.4629; Actual Q2: 0; Actual Q3: 2.2446; Actual Q4: 3.2761; Actual Q1: 0; Actual Q2: 0; Actual Q3: 3.14; Actual Q4: 1.554 | 1.51 | 10.03 | 25.26 | Circuit miles
|  | 1.d.3.a.i | Distribution | HFTD Tier 3 | Urban | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
|  | 1.d.3.a.ii | Distribution | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
|  | 1.d.3.b.i | Distribution | HFTD Tier 3 | Rural | WUI | Actual Q1: 2.2964; Actual Q2: 1.6555; Actual Q3: 6.7826; Actual Q4: 8.0351; Actual Q1: 2.7575; Actual Q2: 2.6576; Actual Q3: 12.1891; Actual Q4: 4.1037 | 19.96 | 13.67 | 15.33 | Circuit miles
|  | 1.d.3.b.ii | Distribution | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 3.2409; Actual Q2: 8.3985; Actual Q3: 4.27; Actual Q4: 15.5868; Actual Q1: 2.0167; Actual Q2: 10.8771; Actual Q3: 16.2834; Actual Q4: 9.6109 | 31.32 | 25.89 | 10.23 | Circuit miles
|  | 1.d.3.c.i | Distribution | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0.060281; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0.060356; Actual Q4: 0 | 0.69 | 0 | 0 | Circuit miles
|  | 1.d.3.c.ii | Distribution | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 0; Actual Q2: 0.13441; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0.46911; Actual Q3: 0; Actual Q4: 0 | 3.57 | 2.84 | 6.59 | Circuit miles
|  | 1.t.0.a.i | Transmission | Non-HFTD | Urban | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0.60204; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.0.a.ii | Transmission | Non-HFTD | Urban | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0.84735; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.0.b.i | Transmission | Non-HFTD | Rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.0.b.ii | Transmission | Non-HFTD | Rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.0.c.i | Transmission | Non-HFTD | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.0.c.ii | Transmission | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.2.a.i | Transmission | HFTD Tier 2 | Urban | WUI | Actual Q1: 0; Actual Q2: 0.18224; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0.1 | 0 | Circuit miles
|  | 1.t.2.a.ii | Transmission | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 1.1466; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0.28693 | 3.9 | 15.8 | 7.8 | Circuit miles
|  | 1.t.2.b.i | Transmission | HFTD Tier 2 | Rural | WUI | Actual Q1: 0; Actual Q2: 0.97931; Actual Q3: 0.058333; Actual Q4: 0.67723; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0.42538 | 0 | 0.2 | 0 | Circuit miles
|  | 1.t.2.b.ii | Transmission | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 1.447; Actual Q2: 0.81773; Actual Q3: 6.522; Actual Q4: 3.2301; Actual Q1: 3.3554; Actual Q2: 0; Actual Q3: 0.29151; Actual Q4: 11.389 | 32 | 53 | 13.4 | Circuit miles
|  | 1.t.2.c.i | Transmission | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.2.c.ii | Transmission | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.3.a.i | Transmission | HFTD Tier 3 | Urban | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.3.a.ii | Transmission | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.3.b.i | Transmission | HFTD Tier 3 | Rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0.14621; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.3.b.ii | Transmission | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 1.6268; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 10.3 | 1.8 | 0 | Circuit miles
|  | 1.t.3.c.i | Transmission | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
|  | 1.t.3.c.ii | Transmission | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit miles
| 2. Number of substations planned for upgrades | 2.0.a.i | N/A | Non-HFTD | Urban | WUI | Actual Q1: 1; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 1 | Number of substations
|  | 2.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 1 | 0 | 5 | Number of substations
|  | 2.0.b.i | N/A | Non-HFTD | Rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations
|  | 2.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations
|  | 2.0.c.i | N/A | Non-HFTD | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations
|  | 2.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations
|  | 2.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations
|  | 2.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 1 | Number of substations
|  | 2.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations
|  | 2.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 1; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations
|  | 2.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations
|  | 2.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations
|  | 2.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations
|  | 2.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations
|  | 2.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations
|  | 2.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 1 | 1 | 0 | 0 | Number of substations
|  | 2.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations
|  | 2.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of substations
| 3. Number of weather stations planned for upgrades | 3.0.a.i | N/A | Non-HFTD | Urban | WUI | Actual Q1: 0; Actual Q2: 2; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 1 | 0 | 0 | Number of weather stations
|  | 3.0.a.ii | N/A | Non-HFTD | Urban | Non-WUI | Actual Q1: 1; Actual Q2: 1; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of weather stations
|  | 3.0.b.i | N/A | Non-HFTD | Rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of weather stations
|  | 3.0.b.ii | N/A | Non-HFTD | Rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of weather stations
|  | 3.0.c.i | N/A | Non-HFTD | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of weather stations
|  | 3.0.c.ii | N/A | Non-HFTD | Highly rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 1; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 1 | 0 | 0 | Number of weather stations
|  | 3.2.a.i | N/A | HFTD Tier 2 | Urban | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of weather stations
|  | 3.2.a.ii | N/A | HFTD Tier 2 | Urban | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 1 | 0 | 0 | Number of weather stations
|  | 3.2.b.i | N/A | HFTD Tier 2 | Rural | WUI | Actual Q1: 1; Actual Q2: 3; Actual Q3: 0; Actual Q4: 1; Actual Q1: 0; Actual Q2: 0; Actual Q3: 1; Actual Q4: 0 | 1 | 0 | 0 | Number of weather stations
|  | 3.2.b.ii | N/A | HFTD Tier 2 | Rural | Non-WUI | Actual Q1: 4; Actual Q2: 9; Actual Q3: 0; Actual Q4: 3; Actual Q1: 4; Actual Q2: 0; Actual Q3: 5; Actual Q4: 0 | 1 | 0 | 0 | Number of weather stations
|  | 3.2.c.i | N/A | HFTD Tier 2 | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of weather stations
|  | 3.2.c.ii | N/A | HFTD Tier 2 | Highly rural | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 1; Actual Q3: 1; Actual Q4: 0 | 1 | 0 | 0 | Number of weather stations
|  | 3.3.a.i | N/A | HFTD Tier 3 | Urban | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of weather stations
|  | 3.3.a.ii | N/A | HFTD Tier 3 | Urban | Non-WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of weather stations
|  | 3.3.b.i | N/A | HFTD Tier 3 | Rural | WUI | Actual Q1: 1; Actual Q2: 1; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 2; Actual Q3: 1; Actual Q4: 0 | 3 | 0 | 0 | Number of weather stations
|  | 3.3.b.ii | N/A | HFTD Tier 3 | Rural | Non-WUI | Actual Q1: 6; Actual Q2: 7; Actual Q3: 2; Actual Q4: 3; Actual Q1: 0; Actual Q2: 5; Actual Q3: 4; Actual Q4: 0 | 5 | 0 | 0 | Number of weather stations
|  | 3.3.c.i | N/A | HFTD Tier 3 | Highly rural | WUI | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 1 | 0 | 0 | Number of weather stations
|  | 3.3.c.ii | N/A | HFTD Tier 3 | Highly rural | Non-WUI | Actual Q1: 2; Actual Q2: 2; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 2; Actual Q3: 0; Actual Q4: 0 | 5 | 0 | 0 | Number of weather stations

## Table 10
Utility | SDG&E |  | Notes:
Table No. | 10 |  | "PSPS" = Public Safety Power Shutoff
Date Modified | 2024-02-01 |  | In future submissions update planned upgrade numbers with actuals
|  |  |  | Actual | [15 empty] | Projected
Table 10: Recent use of PSPS and other PSPS metrics |  |  |  | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4
Metric type | # | Wind Warning Status | Metric name | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | 2024 | 2024 | 2024 | 2024 | 2025 | 2025 | 2025 | 2025 | 2023 | 2024 | 2025 | Unit(s) | Comments | Blank Meaning
1. Recent use of PSPS and fast-trip | 1.a. | RFW only | Frequency of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 2.632 | 2.471 | 2.324 | Number of instances where utility operating protocol requires de-energization of a circuit or portion thereof to reduce ignition probability, per year
|  | HWW only | Frequency of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Number of instances where utility operating protocol requires de-energization of a circuit or portion thereof to reduce ignition probability, per year
|  | HWW & RFW | Frequency of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 1.128 | 1.059 | 0.996 | Number of instances where utility operating protocol requires de-energization of a circuit or portion thereof to reduce ignition probability, per year
|  | All (regardless of RFW/HWW status) | Frequency of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 3.76 | 3.53 | 3.32 | Number of instances where utility operating protocol requires de-energization of a circuit or portion thereof to reduce ignition probability, per year
| 1.b. | RFW only | Scope of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 155.3722 | 137.116 | 121.2214 | Circuit-events, measured in number of events multiplied by number of circuits de-energized per year
|  | HWW only | Scope of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Circuit-events, measured in number of events multiplied by number of circuits de-energized per year
|  | HWW & RFW | Scope of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 66.5881 | 58.764 | 51.952 | Circuit-events, measured in number of events multiplied by number of circuits de-energized per year
|  | All (regardless of RFW/HWW status) | Scope of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 221.9603 | 195.88 | 173.1734 | Circuit-events, measured in number of events multiplied by number of circuits de-energized per year
| 1.c. | RFW only | Duration of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 1002733.1899 | 942577.9986 | 886026.6711 | Customer hours per year
|  | HWW only | Duration of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 0 | 0 | 0 | Customer hours per year
|  | HWW & RFW | Duration of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 429742.7957 | 403961.9994 | 379725.7162 | Customer hours per year
|  | All (regardless of RFW/HWW status) | Duration of PSPS events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 1432475.9856 | 1346539.9981 | 1265752.3874 | Customer hours per year
| 1.d. | RFW only | Frequency of fast-trip events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 |  |  |  | Number of events
|  | HWW only | Frequency of fast-trip events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 |  |  |  | Number of events
|  | HWW & RFW | Frequency of fast-trip events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 |  |  |  | Number of events
|  | None | Frequency of fast-trip events (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 7; Actual Q4: 6; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 5 |  |  |  | Number of events
| 1.e | RFW only | Circuit mile days with fast-trip settings enabled (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 |  |  |  | Circuit mile days
|  | HWW only | Circuit mile days with fast-trip settings enabled (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 |  |  |  | Circuit mile days
|  | HWW & RFW | Circuit mile days with fast-trip settings enabled (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 |  |  |  | Circuit mile days
|  | None | Circuit mile days with fast-trip settings enabled (total) | Actual Q1: 0; Actual Q2: 0; Actual Q3: 8983; Actual Q4: 4611; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 1206 |  |  |  | Circuit mile days
2. Customer hours of PSPS and other outages | 2.a. | N/A | Customer hours of planned outages including PSPS (total) | Actual Q1: 408495.7; Actual Q2: 430706.3833; Actual Q3: 463892.3; Actual Q4: 304450.85; Actual Q1: 264046.7667; Actual Q2: 374569.82; Actual Q3: 357165.32; Actual Q4: 290432 |  |  |  | Total customer hours of planned outages per year
| 2.b. | N/A | Customer hours of unplanned outages, not including PSPS or fast-trip (total) | Actual Q1: 333913.62; Actual Q2: 408887.22; Actual Q3: 569769.78; Actual Q4: 394783.6; Actual Q1: 676516.5; Actual Q2: 324041.7333; Actual Q3: 414481.65; Actual Q4: 204367.6 |  |  |  | Total customer hours of unplanned outages, not including PSPS or fast-trip, per year
| 2.c. | N/A | Customer hours of unplanned outages resulting from fast-trip | Actual Q1: 0; Actual Q2: 0; Actual Q3: 31334.17; Actual Q4: 20039.88; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 4930.2667 |  |  |  | Total customer hours of outages due to fast-trip per year
| 2.d. | N/A | System Average Interruption Duration Index (SAIDI) (including PSPS) | Actual Q1: 13.3631; Actual Q2: 16.3635; Actual Q3: 24.059; Actual Q4: 16.6011; Actual Q1: 26.83; Actual Q2: 12.85; Actual Q3: 16.44; Actual Q4: 8.3 |  |  |  | SAIDI index value = sum of all interruptions in time period where each interruption is defined as sum(duration of interruption * # of customer interruptions) / Total number of customers served
| 2.e. | N/A | System Average Interruption Duration Index (SAIDI) (excluding PSPS) | Actual Q1: 13.3631; Actual Q2: 16.3635; Actual Q3: 24.059; Actual Q4: 16.6011; Actual Q1: 26.83; Actual Q2: 12.85; Actual Q3: 16.44; Actual Q4: 8.3 |  |  |  | SAIDI index value = sum of all interruptions in time period where each interruption is defined as sum(duration of interruption * # of customer interruptions) / Total number of customers served
| 2.f. | N/A | System Average Interruption Frequency Index (SAIFI) (including PSPS) | Actual Q1: 0.10951; Actual Q2: 0.13023; Actual Q3: 0.18148; Actual Q4: 0.16995; Actual Q1: 0.217; Actual Q2: 0.103; Actual Q3: 0.15; Actual Q4: 0.0673 |  |  |  | SAIFI index value = sum of all interruptions in time period where each interruption is defined as (total # of customer interruptions) / (total # of customers served)
| 2.g. | N/A | System Average Interruption Frequency Index (SAIFI) (excluding PSPS) | Actual Q1: 0.10951; Actual Q2: 0.13023; Actual Q3: 0.18148; Actual Q4: 0.16995; Actual Q1: 0.217; Actual Q2: 0.103; Actual Q3: 0.15; Actual Q4: 0.0673 |  |  |  | SAIFI index value = sum of all interruptions in time period where each interruption is defined as (total # of customer interruptions) / (total # of customers served)
3. Critical infrastructure impacted by PSPS | 3.a. | N/A | Critical infrastructure impacted by PSPS | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 |  |  |  | Number of critical infrastructure (in accordance with D.19-05-042) locations impacted per hour multiplied by hours offline per year
4. Community outreach of PSPS metrics | 4.a. | N/A | # of customers impacted by PSPS | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 | 47857 | 44986 | 42287 | # of customers impacted by PSPS (if multiple PSPS events impact the same customer, count each event as a separate customer)
| 4.b. | N/A | # of medical baseline customers impacted by PSPS | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 |  |  |  | # of customers impacted by PSPS (if multiple PSPS events impact the same customer, count each event as a separate customer)
| 4.c. | N/A | # of customers notified prior to initiation of PSPS event | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 1109 |  |  |  | # of customers notified of PSPS event prior to initiation (if multiple PSPS events impact the same customer, count each event in which customer was notified as a separate customer)
| 4.d. | N/A | # of medical baseline customers notified prior to initiation of PSPS event | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 75 |  |  |  | # of customers notified of PSPS event prior to initiation (if multiple PSPS events impact the same customer, count each event in which customer was notified as a separate customer)
| 4.e. | N/A | # of customers notified prior to a PSPS event impacting them | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 |  |  |  | # of customers impacted customers who were notified prior to PSPS initiation (if multiple PSPS events impact the same customer, count each event in which customer was notified as a separate customer)
| 4.f. | N/A | # of medical baseline customers notified prior to a PSPS event impacting them | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 |  |  |  | # of customers impacted customers who were notified prior to PSPS initiation (if multiple PSPS events impact the same customer, count each event in which customer was notified as a separate customer)
5. Other PSPS metrics | 5.a. | N/A | Number of PSPS events in which a notification was sent but no de-energization occurred | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 1 |  |  |  | Number of events
| 5.b. | N/A | Average number of customers located on de-energized circuit | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 |  |  |  | Number of customers
| 5.c. | N/A | Customer hours of PSPS per RFW OH circuit mile day | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 |  |  |  | =1.c. / RFW OH circuit mile days in time period
|  | N/A | Customer hours of PSPS per HWW OH circuit mile day | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 |  |  |  | =1.c. / HWW OH circuit mile days in time period
|  | N/A | Customer hours of PSPS per high FPIOH circuit mile day | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 |  |  |  | =1.c. / FPI OH circuit mile days in time period
| 5.d. | N/A | Median time between de-energization, due to PSPS, and inspection of a circuit segment | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 |  |  |  | Time between de-energization and inspection on a circuit-segment basis in hours
| 5.e. | N/A | 95 percentile of time between de-energization, due to PSPS, and inspection of a circuit segment | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 |  |  |  | Time between de-energization and inspection on a circuit-segment basis in hours
| 5.f. | N/A | Median time between de-energization, due to fast-trip, and inspection of a circuit segment | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0.9; Actual Q4: 3.5; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0.85 |  |  |  | Time between de-energization and inspection on a circuit-segment basis in hours
| 5.g. | N/A | 95 percentile of time between de-energization, due to fast-trip, and inspection of a circuit segment | Actual Q1: 0; Actual Q2: 0; Actual Q3: 2.6; Actual Q4: 3.5; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 2.8892 |  |  |  | Time between de-energization and inspection on a circuit-segment basis in hours
| 5.h. | N/A | Number of risk events occurring on a de-energized circuit | Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0; Actual Q1: 0; Actual Q2: 0; Actual Q3: 0; Actual Q4: 0 |  |  |  | Number of risk events

## Table 11
Utility | SDG&E | Notes:
Table No. | 11 | Territory spend refers to the sum total of initiative spending across all areas, including HFTDs. HFTD spend refers to initiative spending applied to HFTDs, and is a subset of territory spend.
Date Modified | 2024-02-01 | CAPEX = Capital expenditure; OPEX = Operating expenditure.
|  | As data is submitted each reporting period, replace projections for the current reporting period with actuals. | [9 empty] | Actual | [19 empty] | Projected
The units for the spend data are thousands of dollars.
Table 11: Mitigation initiative financials | [11 empty] | CAPEX ($ thousands) |  | OPEX ($ thousands) |  | CAPEX ($ thousands) |  | OPEX ($ thousands) |  | CAPEX ($ thousands) |  | OPEX ($ thousands) |  | CAPEX ($ thousands) |  | OPEX ($ thousands) |  | CAPEX ($ thousands) |  | OPEX ($ thousands) |  | CAPEX ($ thousands) |  | OPEX ($ thousands) |  | CAPEX ($ thousands) |  | OPEX ($ thousands)
[12 empty] | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD | Territory | HFTD
WMPInitiativeCategory | WMPInitiativeActivity | UtilityInitiativeTrackingID | Primary driver targeted | Secondary driver targeted | Year initiated | If existing: most recent proceeding that has reviewed program | If new: memorandum account | Current compiance status - In / exceeding compliance with regulations | Associated rule(s) - if multiple, separate by semi-colon - ";" | If spend not disaggregated by category, note spend category or mark general operations | Comments | 2019 |  |  |  | 2020 |  |  |  | 2021 |  |  |  | 2022 |  |  |  | 2023 |  |  |  | 2024 |  |  |  | 2025 |  |  |  | Blank Meaning
Community Outreach and Engagement | Public outreach and education awareness program | WMP.527 | PSPS Vulnerability | NA | 2013 | NA | WMPMA | NA | NA | NA | NA | 743.0194 | 743.0194 | 3839.5252 | 3839.5252 | 4473.8742 | 4473.8742 | 8313 | 8313 | 5186.0761 | 5186.0761 | 4285.4756 | 4285.4756 | 5404.7718 | 5404.7718 | 3254.5689 | 3254.5689 | 724.4524 | 724.4524 | 5320.4599 | 5320.4599 | 1694.8504 | 1694.8504 | 4847 | 4847 | 1697.3745 | 1697.3745 | 4847 | 4847
Community Outreach and Engagement | Other | WMP.1337 | PSPS Vulnerability | NA | 2013 | NA | WMPMA | Exceeds | P.U. Code § 451 | NA | Community engagement | 0 | 0 | 4.718 | 4.718 | 0 | 0 | 448 | 448 | 0 | 0 | 579.4372 | 579.4372 | 0 | 0 | 398.248 | 398.248 | 0 | 0 | 435.499 | 435.499 | 0 | 0 | 579 | 579 | 0 | 0 | 579 | 579
Community Outreach and Engagement | Other | WMP.1198 | PSPS Vulnerability | NA | NA | NA | NA | NA | NA | NA | Engagement with access and functional needs populations | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Community Outreach and Engagement | Collaboration on local wildfire mitigation planning | WMP.1199 | PSPS Vulnerability | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Community Outreach and Engagement | Best practice sharing with other utilities | WMP.1200 | PSPS Vulnerability | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency Preparedness | Emergency preparedness plan | WMP.1008 | PSPS Vulnerability | NA | 2013 | NA | NA | NA | NA | NA | NA | 63.4349 | 63.4349 | 4726.8783 | 4726.8783 | 1874.4275 | 1874.4275 | 12214 | 12214 | 2963.9236 | 2963.9236 | 12907.1413 | 12907.1413 | 2765.5567 | 2765.5567 | 12381.7687 | 12381.7687 | 16243.2843 | 16243.2843 | 19458.8673 | 19458.8673 | 4443.3879 | 4443.3879 | 16309 | 16309 | 1728.8216 | 1728.8216 | 16566 | 16566
Emergency Preparedness | External collaboration and coordination | WMP.1201 | PSPS Vulnerability | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency Preparedness | Other | WMP.514 | Equipment failure | Other contact with object | 2009 | 2019 GRC | NA | Exceeds | P.U. Code § 451 | NA | Crew-accompanying ignition prevention and suppression resources and services | 0 | 0 | 1790.461 | 1790.461 | 0 | 0 | 2588 | 2588 | 0 | 0 | 3071.2439 | 3071.2439 | 0 | 0 | 3073.8674 | 3073.8674 | 0 | 0 | 4638.8782 | 4638.8782 | 0 | 0 | 3230 | 3230 | 0 | 0 | 3230 | 3230
Emergency Preparedness | Other | WMP.557 | Wildfire Spread | Other contact with object | 2008 | 2019 GRC | NA | Exceeds | P.U. Code § 451 | NA | Aviation Firefighting Program | 0 | 0 | 5166.4415 | 5166.4415 | 7092.4023 | 7092.4023 | 6766 | 6766 | 13464.0874 | 13464.0874 | 6850.0844 | 6850.0844 | 11437.0729 | 11437.0729 | 7396.2538 | 7396.2538 | 3553.2752 | 3553.2752 | 8014.1696 | 8014.1696 | 128.9676 | 128.9676 | 11539 | 11539 | 0 | 0 | 11539 | 11539
Emergency Preparedness | Public emergency communication strategy | WMP.563 | PSPS Vulnerability | NA | 2013 | 2019 GRC | NA | Exceeds | P.U. Code § 451 | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5922.2363 | 5922.2363 | 0 | 0 | 6223.2138 | 6223.2138 | 9650.5221 | 9650.5221 | 4807.1995 | 4807.1995 | 0 | 0 | 6381 | 6381 | 0 | 0 | 6381 | 6381
Emergency Preparedness | Preparedness and planning for service restoration | WMP.1009 | PSPS Vulnerability | NA | 2013 | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency Preparedness | Customer support in wildfire and PSPS emergencies | WMP.1007 | PSPS Vulnerability | NA | 2013 | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency Preparedness | Personnel work procedures and training in conditions of elevated fire risk | WMP.515 | Equipment failure | Other contact with object | 2008 | 2019 GRC | NA | Exceeds | P.U. Code § 451 | NA | NA | 11.3229 | 11.3229 | 0 | 0 | 663.1793 | 663.1793 | 0 | 0 | 175.8393 | 175.8393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Other grid topology improvements to minimize risk of ignitions | WMP.455 | Other contact with object | Equipment failure | 2020 | NA | WMPMA | Exceeds | G.O. 95 | NA | Covered conductor installation | 1463.1958 | 1463.1958 | 0 | 0 | 2086.4258 | 2086.4258 | 0 | 0 | 39282.2861 | 39282.2861 | 519.4094 | 519.4094 | 89511.8441 | 89511.8441 | 3220.847 | 3220.847 | 81552.9164 | 81552.9164 | 3319.066 | 3319.066 | 59217.2413 | 59217.2413 | 592 | 592 | 48245.7423 | 48245.7423 | 592 | 592
Grid Design, Operations, and Maintenance | Other grid topology improvements to minimize risk of ignitions | WMP.453 | Equipment failure | NA | 2016 | 2019 GRC | NA | Exceeds | G.O. 95 | NA | Capacitor Maintenance and replacement program (SCADA) | 0 | 0 | 0 | 0 | 991.5761 | 991.5761 | 0 | 0 | 1966.6405 | 1966.6405 | 0 | 0 | 3509.4251 | 3509.4251 | 0 | 0 | 1557.1041 | 207.6139 | 0 | 0 | 442.997 | 59.0663 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Other grid topology improvements to minimize risk of ignitions | WMP.459 | Equipment failure | NA | 2019 | NA | WMPMA | Exceeds | G.O. 95 | NA | Expulsion fuse replacement | 3716.2553 | 3716.2553 | 0 | 0 | 6520.6375 | 6520.6375 | 0 | 0 | 6488.6708 | 6488.6708 | 0 | 0 | 631.391 | 631.391 | 0 | 0 | 49.866 | 49.866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Other grid topology improvements to minimize risk of ignitions | WMP.464 | PSPS - for sectionalization, etc. | NA | 2019 | NA | WMPMA | Exceeds | G.O. 95 | NA | Maintenance, repair, and replacement of connectors, including hotline clamps | 0 | 0 | 921.9214 | 921.9214 | 0 | 0 | 3298.581 | 3298.581 | 0 | 0 | 3714.0213 | 3714.0213 | 0 | 0 | 1781.4036 | 1781.4036 | 0 | 0 | 1642.1431 | 1248.0288 | 0 | 0 | 365 | 350.4 | 0 | 0 | 120 | 115.2
Grid Design, Operations, and Maintenance | Other grid topology improvements to minimize risk of ignitions | WMP.550 | Equipment failure | NA | 2020 | NA | WMPMA | Exceeds | G.O. 95 | NA | Lightning arrester removal and replacement | 0 | 0 | 0 | 0 | 19.2033 | 19.2033 | 0 | 0 | 2029.5942 | 2029.5942 | 0 | 0 | 3296.7443 | 3296.7443 | 0 | 0 | 3431.5606 | 3223.5872 | 0 | 0 | 3422.0778 | 3214.6792 | 0 | 0 | 3482.6461 | 3271.5767 | 0 | 0
Grid Design, Operations, and Maintenance | Other grid topology improvements to minimize risk of ignitions | WMP.972 | Other contact with object | NA | 2022 | NA | WMPMA | NA | NA | NA | Avian Protection | 0 | 0 | 0 | 0 | 0.81277 | 0.73962 | 0 | 0 | 233.9531 | 212.8973 | 0 | 0 | 1850.8089 | 1684.2361 | 15.6481 | 14.2398 | 1434.5586 | 1147.6469 | 8.7435 | 6.9948 | 1488.221 | 1190.5768 | 60 | 48 | 1512.351 | 1209.8808 | 120 | 96
Grid Design, Operations, and Maintenance | Other grid topology improvements to minimize risk of ignitions | WMP.1189 | Equipment failure | NA | 2021 | NA | NA | NA | NA | NA | Strategic Pole Replacement Program | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.268 | 56.0567 | 0.29896 | 0.24913 | 6700.8 | 3685.44 | 492 | 270.6 | 6700.8 | 6533.28 | 506 | 493.35
Grid Design, Operations, and Maintenance | Other grid topology improvements to minimize risk of ignitions | WMP.449 | PSPS - for sectionalization, etc. | NA | 2011 | 2019 GRC | NA | Exceeds | P.U. Code § 451 | NA | Wireless Fault Indicators | 796.862 | 796.862 | 0 | 0 | 835.298 | 835.298 | 0 | 0 | 1104.3821 | 1104.3821 | 0 | 0 | 845.9703 | 845.9703 | 0 | 0 | 9.576 | 3.591 | 0 | 0 | 263.9237 | 98.9714 | 0 | 0 | 298.9969 | 112.1239 | 0 | 0
Grid Design, Operations, and Maintenance | Other grid topology improvements to mitigate or reduce PSPS events | WMP.461 | PSPS - for sectionalization, etc. | NA | 2019 | NA | WMPMA | Exceeds | G.O. 95 | NA | PSPS Sectionalizing Enhancements | 1321.3975 | 1321.3975 | 0 | 0 | 4933.0022 | 4933.0022 | 0 | 0 | 1912.8257 | 1912.8257 | 0 | 0 | 2382.6663 | 2382.6663 | 0 | 0 | 2035.1409 | 2035.1409 | 0 | 0 | 1858.381 | 1858.381 | 0 | 0 | 1881.105 | 1881.105 | 0 | 0
Grid Design, Operations, and Maintenance | Other grid topology improvements to mitigate or reduce PSPS events | WMP.468 | PSPS - for sectionalization, etc. | NA | 2020 | NA | WMPMA | Exceeds | P.U. Code § 451 | NA | Standby Power Programs | 0 | 0 | 592.0257 | 592.0257 | 0 | 0 | 1753.6305 | 1753.6305 | 0 | 0 | 8934.0423 | 8934.0423 | 0 | 0 | 12043.425 | 12043.425 | 0 | 0 | 12679.9652 | 12679.9652 | 0 | 0 | 10590 | 10590 | 0 | 0 | 10590 | 10590
Grid Design, Operations, and Maintenance | Other grid topology improvements to mitigate or reduce PSPS events | WMP.466 | PSPS - for sectionalization, etc. | NA | 2020 | NA | WMPMA | Exceeds | P.U. Code § 451 | NA | Generator Grant Program | 0 | 0 | 0 | 0 | 0 | 0 | 5075.892 | 5075.892 | 0 | 0 | 7892.791 | 7892.791 | 0 | 0 | 3550.3963 | 3550.3963 | 0 | 0 | 5407.1365 | 5407.1365 | 0 | 0 | 7550 | 7550 | 0 | 0 | 7550 | 7550
Grid Design, Operations, and Maintenance | Other grid topology improvements to mitigate or reduce PSPS events | WMP.467 | PSPS - for sectionalization, etc. | NA | 2020 | NA | WMPMA | Exceeds | P.U. Code § 451 | NA | Generator Assistance Program | 0 | 0 | 0 | 0 | 0 | 0 | 760.5866 | 760.5866 | 0 | 0 | 744.2966 | 744.2966 | 0 | 0 | 758.9914 | 758.9914 | 0 | 0 | 547.0827 | 547.0827 | 0 | 0 | 1828 | 1828 | 0 | 0 | 1828 | 1828
Grid Design, Operations, and Maintenance | Undergrounding of electric lines and/or equipment | WMP.473 | Other contact with object | Equipment failure | 2019 | NA | WMPMA | Exceeds | G.O. 95 | NA | Strategic Underground | 192.2288 | 192.2288 | 0 | 0 | 38853.0582 | 38853.0582 | 0 | 0 | 69690.6802 | 69690.6802 | 0 | 0 | 126675.0901 | 126675.0901 | 175.5502 | 175.5502 | 174778.4583 | 174778.4583 | 428.602 | 428.602 | 291932.6067 | 291932.6067 | 2921 | 2921 | 356653.9518 | 356653.9518 | 2921 | 2921
Grid Design, Operations, and Maintenance | Distribution pole replacements and reinforcements | WMP.458 | Equipment failure | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Transmission pole/tower replacements and reinforcements | WMP.472 | Equipment failure | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Traditional overhead hardening | WMP.475 | Equipment failure | Other contact with object | 2009 | 2019 GRC | NA | Exceeds | G.O. 95 | NA | Distribution OH System Hardening | 123171.9419 | 123171.9419 | 2161.705 | 2161.705 | 136714.8003 | 136714.8003 | 3446.1072 | 3446.1072 | 94315.5054 | 94315.5054 | 2596.4565 | 2596.4565 | 23267.6696 | 23267.6696 | 3249.0777 | 3249.0777 | 6068.6149 | 6068.6149 | 1168.0233 | 1168.0233 | 891.5755 | 891.5755 | 48 | 48 | 904.9492 | 904.9492 | 48 | 48
Grid Design, Operations, and Maintenance | Traditional overhead hardening | WMP.543 | Equipment failure | Other contact with object | 2009 | NA | NA | Exceeds | G.O. 95 | NA | Transmission OH Hardening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Traditional overhead hardening | WMP.545 | Equipment failure | Other contact with object | 2009 | 2019 GRC | NA | Exceeds | G.O. 95 | NA | Transmission OH Hardening - Distribution Underbuild | 2997.902 | 2997.902 | 0 | 0 | 5079.5032 | 5079.5032 | 0 | 0 | 5475.8655 | 5475.8655 | 0 | 0 | 3237.2128 | 3237.2128 | 0 | 0 | 14326.1788 | 14326.1788 | 0.38446 | 0.38446 | 14788.7428 | 14788.7428 | 0 | 0 | 4746.7071 | 4746.7071 | 0 | 0
Grid Design, Operations, and Maintenance | Microgrids | WMP.462 | PSPS - for sectionalization, etc. | NA | 2019 | NA | WMPMA | Exceeds | P.U. Code § 451 | NA | NA | 187.882 | 62.001 | 0 | 0 | 3541.9889 | 1168.8563 | 370.5416 | 122.2787 | 12996.0003 | 4288.6801 | 1378.1956 | 454.8046 | 2697.2991 | 890.1087 | 1304.02 | 430.3266 | 3197.2677 | 1065.7559 | 1104.7857 | 368.2619 | 23440.1226 | 7813.3742 | 1788 | 596 | 0 | 0 | 1788 | 596
Grid Design, Operations, and Maintenance | Installation of system automation equipment | WMP.463 | PSPS - for sectionalization, etc. | NA | 2011 | NA | WMPMA | Exceeds | P.U. Code § 451 | NA | Advanced Protection | 3479.8791 | 3479.8791 | 0 | 0 | 9072.44 | 9072.44 | 0 | 0 | 9103.7558 | 9103.7558 | 0 | 0 | 17263.0467 | 17263.0467 | 150.9458 | 150.9458 | 16297.8999 | 16297.8999 | 193.906 | 193.906 | 10187.695 | 10187.695 | 60 | 60 | 8194.27 | 8194.27 | 117 | 117
Grid Design, Operations, and Maintenance | Installation of system automation equipment | WMP.1195 | Wildfire Exposure | NA | 2023 | NA | NA | NA | NA | NA | Early Fault Detection | 0 | 0 | 0 | 0 | 44.1042 | 44.1042 | 0 | 0 | 1712.2662 | 1712.2662 | 0 | 0 | 6559.0685 | 6559.0685 | 1.3658 | 1.3658 | 6060.7074 | 6060.7074 | 3.591 | 3.591 | 3977.766 | 3977.766 | 67 | 67 | 4069.625 | 4069.625 | 67 | 67
Grid Design, Operations, and Maintenance | Installation of system automation equipment | WMP.549 | Wildfire Exposure Potential | PSPS exposure potential | 2010 | 2019 GRC | NA | NA | P.U. Code § 451 | NA | Distribution Communications Reliability Improvements | 8098.6358 | 8098.6358 | 0 | 0 | 35475.5218 | 35475.5218 | 0 | 0 | 49422.0916 | 49422.0916 | 0 | 0 | 45177.2599 | 45177.2599 | 714.393 | 714.393 | 75714.4907 | 60069.7326 | 910.0155 | 598.0102 | 59399.9618 | 59399.9618 | 878.616 | 878.616 | 67963.9565 | 67963.9565 | 878.616 | 878.616
Grid Design, Operations, and Maintenance | Line removals (in HFTD) | WMP.1202 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Other | WMP.1016 | Other contact with object | Equipment failure | 2009 | 2019 GRC | NA | Exceeds | G.O. 95 | NA | CNF(Distribution Underground) | 30559.1879 | 30559.1879 | 0 | 0 | 37981.9144 | 37981.9144 | 0 | 0 | 5653.3657 | 5653.3657 | 0 | 0 | 717.7558 | 717.7558 | 2212.349 | 2212.349 | 620.3237 | 620.3237 | 671.5984 | 671.5984 | 551.9928 | 551.9928 | 138 | 138 | 422.2582 | 422.2582 | 138 | 138
Grid Design, Operations, and Maintenance | Other | WMP.1017 | Equipment failure | Other contact with object | 2009 | 2019 GRC | NA | Exceeds | G.O. 95 | NA | CNF(Distribution Overhead) | 37237.2768 | 37237.2768 | 0 | 0 | 46282.0892 | 46282.0892 | 0 | 0 | 6888.7938 | 6888.7938 | 0 | 0 | 874.6067 | 874.6067 | 0 | 0 | 755.8829 | 755.8829 | 0 | 0 | 702.6197 | 702.6197 | 0 | 0 | 544.5341 | 544.5341 | 0 | 0
Grid Design, Operations, and Maintenance | Asset Inspections | WMP.478 | Equipment failure | NA | 1997 | 2019 GRC | NA | Meets | G.O. 95 | NA | Distribution Overhead Detailed Inspections | 9026.2832 | 2437.0965 | 567.0209 | 153.0957 | 8508.0474 | 2297.1728 | 179 | 48.33 | 9556.9955 | 2580.3888 | 1463.8372 | 395.236 | 8422.2256 | 2274.0009 | 1195.2993 | 322.7308 | 6538.2148 | 1744.5717 | 151.5283 | 40.4318 | 7055.7517 | 2403.7787 | 327 | 111.4035 | 7185.6338 | 2194.1182 | 327 | 99.8488
Grid Design, Operations, and Maintenance | Asset Inspections | WMP.479 | Equipment failure | NA | 1997 | NA | NA | Meets | G.O. 95 | NA | Transmission Overhead Detailed Inspections | 436.75 | 222.7425 | 0 | 0 | 896.8871 | 457.4124 | 0 | 0 | 393.3346 | 200.6007 | 0 | 0 | 489.8077 | 249.8019 | 0.03096 | 0.03096 | 1536.6345 | 777.272 | 35.4237 | 35.4237 | 756.9451 | 289.5418 | 60 | 60 | 406.3707 | 193.3191 | 108 | 108
Grid Design, Operations, and Maintenance | Asset Inspections | WMP.481 | Equipment failure | NA | 2020 | NA | WMPMA | Exceeds | P.U. Code § 451 | NA | Distribution Infrared Inspections | 0 | 0 | 98.1179 | 98.1179 | 0 | 0 | 175 | 175 | 0 | 0 | 145.6589 | 145.6589 | 0 | 0 | 158.9313 | 158.9313 | 0 | 0 | 305.257 | 257.6673 | 0 | 0 | 175 | 147.7241 | 0 | 0 | 175 | 147.7241
Grid Design, Operations, and Maintenance | Asset Inspections | WMP.482 | Equipment failure | NA | 2010 | NA | NA | Meets | P.U. Code § 451 | NA | Transmission Infrared Inspections | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Asset Inspections | WMP.483 | Equipment failure | NA | 1997 | 2019 GRC | NA | Meets | G.O. 95 | NA | Distribution Wood Pole Intrusive Inspections | 614.9179 | 614.9179 | 1249.4412 | 0 | 579.6129 | 579.6129 | 884 | 0 | 1941.966 | 1941.966 | 803.2821 | 0 | 1711.2722 | 1711.2722 | 39.4128 | 0 | 1328.4689 | 3.3717 | 97.1935 | 0.24668 | 1433.6248 | 0 | 126 | 0 | 1460.0149 | 0 | 126 | 0
Grid Design, Operations, and Maintenance | Asset Inspections | WMP.1190 | Equipment ignition likelihood | NA | NA | NA | NA | NA | NA | NA | Transmission Wood Pole Intrusive Inspections | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Asset Inspections | WMP.552 | Equipment failure | NA | 2019 | NA | WMPMA | Exceeds | G.O. 95 | NA | Distribution Drone Assessments | 270.803 | 270.803 | 13551.448 | 13551.448 | 15794.5937 | 15794.5937 | 51953 | 51953 | 12661.7294 | 12661.7294 | 33107.6919 | 33107.6919 | 51741.0148 | 51741.0148 | 45222.7097 | 45222.7097 | 75131.0654 | 74774.3959 | 52915.0832 | 52663.8795 | 63864 | 61948.08 | 12656 | 12276.32 | 20670 | 20049.9 | 12656 | 12276.32
Grid Design, Operations, and Maintenance | Asset Inspections | WMP.488 | Equipment failure | NA | 1997 | 2019 GRC | NA | Meets | G.O. 95 | NA | Distribution Overhead Patrol Inspections | 856.3925 | 856.3925 | 0 | 0 | 807.2235 | 807.2235 | 295 | 115.05 | 1162.0259 | 1162.0259 | 286.3571 | 111.6793 | 1023.8291 | 1023.8291 | 285.0592 | 111.1731 | 794.8035 | 309.3336 | 296.7088 | 115.4776 | 857.7167 | 332.8094 | 279 | 108.257 | 873.5056 | 339.4427 | 279 | 108.4189
Grid Design, Operations, and Maintenance | Asset Inspections | WMP.489 | Equipment failure | NA | 1997 | NA | NA | Meets | G.O. 95 | NA | Transmission Overhead Patrol Inspections | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Asset Inspections | WMP.555 | Equipment failure | NA | 2010 | NA | NA | Exceeds | G.O. 95 | NA | Transmission 69kV Tier 3 Visual Inspections | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Asset Inspections | WMP.492 | Equipment ignition likelihood | NA | 1997 | 2019 GRC | NA | NA | NA | NA | Substation defensible space | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Asset Inspections | WMP.484 | Equipment failure | NA | 2011 | 2019 GRC | NA | Exceeds | G.O. 95 | NA | LiDAR inspections of distribution electric lines and equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1150.5326 | 1150.5326 | 0 | 0 | 3000.1182 | 3000.1182 | 0 | 0 | 872.9935 | 872.9935 | 0 | 0 | 1500 | 1500 | 0 | 0 | 1500 | 1500
Grid Design, Operations, and Maintenance | Asset Inspections | WMP.551 | Equipment failure | NA | 2009 | 2019 GRC | NA | Exceeds | G.O. 95 | NA | HFTD Tier 3 Distribution Pole Inspections | 1354.3169 | 1354.3169 | 0 | 0 | 1276.56 | 1276.56 | 400 | 400 | 3140.3809 | 3140.3809 | 49.4829 | 49.4829 | 2767.5871 | 2767.5871 | 342.4239 | 342.4239 | 2148.4914 | 2148.4914 | 621.3598 | 621.3598 | 2318.5567 | 2318.5567 | 313 | 313 | 2361.2367 | 2361.2367 | 313 | 313
Grid Design, Operations, and Maintenance | Other | WMP.553 | Equipment failure | NA | 2019 | NA | WMPMA | Exceeds | G.O. 95 | NA | Circuit ownership | 671.6329 | 671.6329 | 0 | 0 | 41.2877 | 41.2877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Other | WMP.519 | NA | NA | 2019 | NA | WMPMA | Exceeds | P.U. Code § 451 | NA | Centralized repository for data | 18.9582 | 18.9582 | 0 | 0 | 7480.0281 | 7480.0281 | 0 | 0 | 14886.215 | 14886.215 | 0 | 0 | 14457.8051 | 14457.8051 | 1304.985 | 1304.985 | 10046.6941 | 10046.6941 | 1657.4767 | 1657.4767 | 8097.8199 | 8097.8199 | 1650 | 1650 | 7832.9253 | 7832.9253 | 1650 | 1650
Grid Design, Operations, and Maintenance | Secondary Assessment of Transmission Inspections | WMP.1191 | Equipment ignition likelihood | NA | 2023 | NA | NA | NA | NA | NA | QA/QC of Transmission Inspections | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Other | WMP.491 | Equipment ignition likelihood | NA | 2023 | NA | NA | NA | NA | NA | QA/QC of Distribution Detailed Inspections | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Other | WMP.1192 | Equipment ignition likelihood | NA | 2023 | NA | NA | NA | NA | NA | QA/QC of Distribution Drone Assessments | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Other | WMP.1193 | Equipment ignition likelihood | NA | 2023 | NA | NA | NA | NA | NA | QA/QC of Wood Pole Intrusive (Transmission & Distribution) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Other | WMP.1194 | Equipment ignition likelihood | NA | 2023 | NA | NA | NA | NA | NA | QA/QC of Substation Inspections | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Open work orders | WMP.1203 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Equipment Settings to Reduce Wildfire Risk (Grid Ops) | WMP.1204 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Grid Response Procedures and Notifications (Grid Ops) | WMP.1205 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Personnel Work Procedures and Training in Conditions of Elevated Fire Risk (Grid Ops) | WMP.515 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grid Design, Operations, and Maintenance | Workforce Planning | WMP.1206 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Overview of the Service Territory | Environmental compliance and permitting | WMP.493 | NA | NA | 1998 | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 872.1724 | 872.1724 | 0 | 0 | 1208.1944 | 1208.1944 | 0 | 0 | 1000 | 1000 | 0 | 0 | 1000 | 1000
Situational Awareness and Forecasting | Environmental monitoring systems (Advanced weather monitoring) | WMP.447 | NA | NA | 2010 | NA | WMPMA | Exceeds | P.U. Code § 451 | NA | NA | 564.3528 | 564.3528 | 0 | 0 | 1008.4265 | 1008.4265 | 0 | 0 | 389.7356 | 389.7356 | 0 | 0 | 211.259 | 211.259 | 0 | 0 | 206.4754 | 206.4754 | 0 | 0 | 428.6445 | 428.6445 | 0 | 0 | 436.7067 | 436.7067 | 0 | 0
Situational Awareness and Forecasting | Air Quality Index | WMP.970 | Wildfire Exposure Potential | NA | 2022 | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331.489 | 331.489 | 0 | 0 | 82.1098 | 82.1098 | 65.5319 | 65.5319 | 0 | 0 | 100 | 100 | 0 | 0 | 100 | 100
Situational Awareness and Forecasting | Cameras | WMP.971 | Wildfire Exposure Potential | Wildfire Spread | 2009 | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Situational Awareness and Forecasting | Ignition detection systems | WMP.558 | Wildfire Exposure Potential | Wildfire Spread | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Situational Awareness and Forecasting | Weather forecasting | WMP.443 | Wildfire Exposure Potential | Wildfire Spread | 2009 | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Situational Awareness and Forecasting | Fire potential index | WMP.450 | Wildfire Exposure Potential | NA | 2012 | 2019 GRC | NA | NA | NA | NA | NA | 270.3861 | 270.3861 | 0 | 0 | 1190.5993 | 1190.5993 | 0 | 0 | 1445.6221 | 1445.6221 | 0 | 0 | 1632.1322 | 1632.1322 | 1818.2253 | 1818.2253 | 1278.9826 | 1278.9826 | 4268.4589 | 4268.4589 | 2741.856 | 2741.856 | 2413 | 2413 | 2782.98 | 2782.98 | 2413 | 2413
Situational Awareness and Forecasting | High-performance computing infrastructure | WMP.541 | Wildfire Exposure Potential | Wildfire Spread | 2012 | NA | WMPMA | Exceeds | P.U. Code § 451 | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5224.3189 | 5224.3189 | 0 | 0 | 10.1173 | 10.1173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vegetation Management and Inspection | Vegetation Inspections | WMP.494 | Wildfire Exposure Potential | NA | 2002 | NA | NA | NA | NA | NA | NA | 0 | 0 | 34448.624 | 18257.7707 | 0 | 0 | 57791 | 30629.23 | 0 | 0 | 42016.2139 | 22268.5934 | 0 | 0 | 59775.6646 | 31779.469 | 0 | 0 | 67765.4702 | 35937.3449 | 0 | 0 | 45818.57 | 24368.6775 | 0 | 0 | 47540 | 25186.0239
Vegetation Management and Inspection | Fuels management (including slash management) | WMP.497 | Contact with vegetation | NA | 2019 | NA | WMPMA | Exceeds | P.U. Code § 451 | NA | NA | 0 | 0 | 5092.9455 | 5092.9455 | 0 | 0 | 5805 | 5805 | 0 | 0 | 4349.6381 | 4349.6381 | 0 | 0 | 7895.5263 | 7895.5263 | 0 | 0 | 4254.8585 | 4254.8585 | 0 | 0 | 6513 | 6513 | 0 | 0 | 6513 | 6513
Vegetation Management and Inspection | Pole clearing | WMP.512 | Other contact with object | NA | 1998 | 2019 GRC | NA | Meets | P.U. Code § 451 | NA | NA | 0 | 0 | 3884.028 | 3417.9446 | 0 | 0 | 5433 | 4781.04 | 0 | 0 | 5556.4784 | 4889.701 | 0 | 0 | 6104.9138 | 5372.3242 | 0 | 0 | 8003.9708 | 7034.0865 | 0 | 0 | 7267 | 6386.4184 | 0 | 0 | 7267 | 6386.4184
Vegetation Management and Inspection | Clearance | WMP.501 | Contact with vegetation | NA | 2019 | 2019 GRC | NA | Exceeds | P.U. Code § 451 | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 10235 | 10235 | 0 | 0 | 9955 | 9955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10235 | 10235 | 0 | 0 | 10235 | 10235
Vegetation Management and Inspection | Emergency response vegetation management | WMP.496 | Wildfire hazard | NA | 1998 | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vegetation Management and Inspection | Vegetation management enterprise system | WMP.511 | NA | NA | 2002 | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 880.0497 | 880.0497 | 0 | 0 | 2103.0801 | 2103.0801 | 0 | 0 | 0 | 0 | 0 | 0
Vegetation Management and Inspection | Quality assurance / quality control | WMP.505 | NA | NA | 1998 | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vegetation Management and Inspection | Open work orders | WMP.1207 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vegetation Management and Inspection | Workforce Planning | WMP.1208 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wildfire Mitigation Strategy Development | Wildfire Mitigation Strategy Development | WMP.1209 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wildfire Mitigation Strategy Development | Other | WMP.442 | NA | NA | 2012 | 2019 GRC | NA | Exceeds | P.U. Code § 451 | NA | A summarized risk map that shows the overall ignition probability and estimated wildfire consequence along the electric lines and equipment | 2.6259 | 2.6259 | 1727.5828 | 1727.5828 | 342.9754 | 342.9754 | 3363 | 3363 | 37.919 | 37.919 | 2811.5346 | 2811.5346 | 0 | 0 | 3734.865 | 3734.865 | 0 | 0 | 3871.5498 | 3871.5498 | 0 | 0 | 4017 | 4017 | 0 | 0 | 4017 | 4017
Wildfire Mitigation Strategy Development | Other | WMP.521 | NA | NA | 2020 | NA | WMPMA | Exceeds | P.U. Code § 451 | NA | Documentation and disclosure of wildfire-related data and algorithms | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2433.919 | 2433.919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wildfire Mitigation Strategy Development | Other | WMP.523 | NA | NA | 2019 | 2019 GRC | NA | Exceeds | P.U. Code § 451 | NA | Allocation methodology development and application | 0 | 0 | 369.327 | 369.327 | 1623.2195 | 1623.2195 | 3718 | 3718 | 1759.3041 | 1759.3041 | 5299.0615 | 5299.0615 | 5701.8328 | 5701.8328 | 3966.6296 | 3966.6296 | 5154.9289 | 5154.9289 | 5431.8454 | 5431.8454 | 7911.6632 | 7911.6632 | 7988 | 7988 | 7296.5786 | 7296.5786 | 7988 | 7988

## Table 12
Utility | SDG&E | Notes:
Table No. | 12
Date Modified | 2024-02-01
Table 12: WMP Midyear & End-of-Year Targets
Targets
[5 empty] | YTD end of Q2 | YTD end of Q3 | End of year | YTD end of Q2 | YTD end of Q3 | End of year | End of year
WMPInitiativeCategory | WMPInitiativeActivity | UtilityInitiativeTrackingID | TargetType | Units | 2023 | 2023 | 2023 | 2024 | 2024 | 2024 | 2025 | Method of Verification | Comments
Grid Design, Operations, and Maintenance | Covered Conductor Installation | WMP.455 | Quantitative | Miles | 33 | 45 | 60 | 0 | 0 | 60 | 40 | Quantitative | Distribution OH Hardening - Covered Conductor
Grid Design, Operations, and Maintenance | Undergrounding of electric lines and/or equipment | WMP.473 | Quantitative | Miles | 12.94 | 63.88 | 84.43 | 0 | 0 | 125 | 150 | Quantitative | Strategic Undergrounding
Grid Design, Operations, and Maintenance | Traditional overhead hardening | WMP.475 | Quantitative | Miles | 1.8 | 1.8 | 1.9 | 0 | 0 | 0 | 0.6 | Quantitative | Distribution OH System Hardening
Grid Design, Operations, and Maintenance | Traditional overhead hardening | WMP.543 | Quantitative | Miles | 7.8 | 8.8 | 14.1 | 10.2 | 10.2 | 10.2 | 10.2 | Quantitative | Transmission OH Hardening
Grid Design, Operations, and Maintenance | Traditional overhead hardening | WMP.545 | Quantitative | Miles | 2.7 | 2.7 | 7.1 | 0 | 1 | 1 | 3.4 | Quantitative | Transmission OH Hardening - Distribution Underbuild
Grid Design, Operations, and Maintenance | Microgrids | WMP.462 | Quantitative | Micogrids | 0 | 0 | 0 | 0 | 0 | 3 | 0 | Quantitative | Microgrids
Grid Design, Operations, and Maintenance | Installation of system automation equipment | WMP.463 | Quantitative | Circuits | 3 | 4 | 5 | 3 | 6 | 8 | 8 | Quantitative | Advanced Protection
Grid Design, Operations, and Maintenance | Installation of system automation equipment | WMP.1195 | Quantitative | Nodes | 20 | 40 | 60 | 30 | 52 | 60 | 60 | Quantitative | Early Fault Detection
Grid Design, Operations, and Maintenance | Installation of system automation equipment | WMP.549 | Quantitative | Base Stations | 10 | 17 | 35 | 20 | 40 | 60 | 90 | Quantitative | Distribution Communications Reliability Improvements
Grid Design, Operations, and Maintenance | Other grid topology improvements to minimize risk of ignitions | WMP.453 | Quantitative | Capacitors | 11 | 13 | 15 | 0 | 0 | 0 | 0 | Quantitative | Capacitor Maintenance and replacement program (SCADA)
Grid Design, Operations, and Maintenance | Other grid topology improvements to minimize risk of ignitions | WMP.459 | Quantitative | Fuses | 20 | 30 | 40 | 0 | 0 | 0 | 0 | Quantitative | Expulsion fuse replacement
Grid Design, Operations, and Maintenance | Other grid topology improvements to minimize risk of ignitions | WMP.464 | Quantitative | HLCs | 126 | 188 | 250 | 126 | 188 | 250 | 0 | Quantitative | Maintenance, repair, and replacement of connectors, including hotline clamps
Grid Design, Operations, and Maintenance | Other grid topology improvements to minimize risk of ignitions | WMP.550 | Quantitative | Arrestors | 1531 | 1715 | 1848 | 1531 | 1715 | 1848 | 1848 | Quantitative | Lightning arrester removal and replacement
Grid Design, Operations, and Maintenance | Other grid topology improvements to minimize risk of ignitions | WMP.972 | Quantitative | Poles | 50 | 150 | 200 | 50 | 150 | 200 | 0 | Quantitative | Avian Protection
Grid Design, Operations, and Maintenance | Other grid topology improvements to minimize risk of ignitions | WMP.1189 | Quantitative | Poles | 0 | 27 | 60 | 98 | 150 | 200 | 200 | Quantitative | Strategic Pole Replacement Program
Grid Design, Operations, and Maintenance | Other grid topology improvements to minimize risk of ignitions | WMP.449 | Quantitative | WFIs | 0 | 0 | 0 | 0 | 300 | 300 | 0 | Quantitative | Wireless Fault Indicators
Grid Design, Operations, and Maintenance | Other grid topology improvements to mitigate or reduce PSPS events | WMP.461 | Quantitative | Switches | 9 | 10 | 10 | 8 | 10 | 10 | 10 | Quantitative | PSPS Sectionalizing Enhancements
Grid Design, Operations, and Maintenance | Other grid topology improvements to mitigate or reduce PSPS events | WMP.468 | Quantitative | Generators | 100 | 250 | 300 | 100 | 150 | 300 | 300 | Quantitative | Fixed Power Backup
Grid Design, Operations, and Maintenance | Other grid topology improvements to mitigate or reduce PSPS events | WMP.466 | Quantitative | NA | NA | NA | NA | NA | NA | NA | NA | Qualitative | Generator Grant Program
Grid Design, Operations, and Maintenance | Other grid topology improvements to mitigate or reduce PSPS events | WMP.467 | Qualitative | NA | NA | NA | NA | NA | NA | NA | NA | Qualitative | Generator Assistance Program
Grid Design, Operations, and Maintenance | Asset Inspections | WMP.478 | Quantitative | Inspections | 8450 | 9650 | 11100 | 14850 | 15350 | 15450 | 13275 | Quantitative | Distribution Overhead Detailed Inspections
Grid Design, Operations, and Maintenance | Asset Inspections | WMP.479 | Quantitative | Inspections | 850 | 1672 | 2387 | 1121 | 1442 | 1960 | 1979 | Quantitative | Transmission Overhead Detailed Inspections
Grid Design, Operations, and Maintenance | Asset Inspections | WMP.481 | Quantitative | Inspections | 6343 | 8147 | 9578 | 4766 | 7149 | 9532 | 9532 | Quantitative | Distribution Infrared Inspections
Grid Design, Operations, and Maintenance | Asset Inspections | WMP.482 | Quantitative | Inspections | 0 | 0 | 6179 | 0 | 0 | 6179 | 6179 | Quantitative | Transmission Infrared Inspections
Grid Design, Operations, and Maintenance | Asset Inspections | WMP.483 | Quantitative | Inspections | 0 | 50 | 50 | 0 | 0 | 0 | 0 | Quantitative | Distribution Wood Pole Intrusive Inspections
Grid Design, Operations, and Maintenance | Asset Inspections | WMP.1190 | Quantitative | Inspections | 0 | 0 | 73 | 0 | 0 | 0 | 141 | Quantitative | Transmission Wood Pole Intrusive Inspections
Grid Design, Operations, and Maintenance | Asset Inspections | WMP.552 | Quantitative | Inspections | 6848 | 10270 | 13692 | 6753 | 10127 | 13500 | 13500 | Quantitative | Drone Assessments
Grid Design, Operations, and Maintenance | Asset Inspections | WMP.488 | Quantitative | Inspections | 61800 | 86500 | 86880 | 71047 | 83247 | 86197 | 86535 | Quantitative | Distribution Overhead Patrol Inspections
Grid Design, Operations, and Maintenance | Asset Inspections | WMP.489 | Quantitative | Structures | 6008 | 6008 | 6337 | 6008 | 6008 | 6337 | 6337 | Quantitative | Transmission Overhead Patrol Inspections
Grid Design, Operations, and Maintenance | Asset Inspections | WMP.555 | Quantitative | Structures | 0 | 1632 | 1632 | 0 | 1632 | 1632 | 1632 | Quantitative | Transmission 69kV Tier 3 Visual Inspections
Grid Design, Operations, and Maintenance | Asset Inspections | WMP.492 | Quantitative | Inspections | 192 | 281 | 384 | 192 | 281 | 384 | 384 | Quantitative | Substation Patrol inspections
Grid Design, Operations, and Maintenance | Quality assurance / quality control | WMP.1191 | Quantitative | Findings | 100% | 100% | 100% | 100% | 100% | 100% | 100% | Quantitative | QA/QC of Transmission Inspections
Grid Design, Operations, and Maintenance | Quality assurance / quality control | WMP.491 | Quantitative | Inspections | 0 | 0 | 160 | 0 | 0 | 77 | 66 | Quantitative | QA/QC of Distribution Detailed Inspections
Grid Design, Operations, and Maintenance | Quality assurance / quality control | WMP.1192 | Quantitative | Inspections | 6848 | 10270 | 13692 | 6753 | 10127 | 13500 | 13500 | Quantitative | QA/QC of Distribution Drone Assessments
Grid Design, Operations, and Maintenance | Quality assurance / quality control | WMP.1193 | Quantitative | Inspections | 0 | 0 | 12 | 0 | 0 | 0 | 14 | Quantitative | QA/QC of Wood Pole Intrusive (Transmission & Distribution)
Grid Design, Operations, and Maintenance | Quality assurance / quality control | WMP.1194 | Quantitative | Inspections | 9 | 9 | 18 | 9 | 9 | 18 | 18 | Quantitative | QA/QC of Substation Inspections
Situational Awareness and Forecasting | Enviornmental monitoring System | WMP.970 | Quantitative | Sensors | 6 | 6 | 6 | 3 | 6 | 6 | 6 | Quantitative | Air Quality Index
Vegetation Management and Inspection | Vegetation Management Inspection Program | WMP.494 | Quantitative | Inspections | 241800 | 374200 | 485400 | 241800 | 374200 | 485400 | 485400 | Quantitative | Detailed Inspections
Vegetation Management and Inspection | Vegetation Management Inspection Program | WMP.508 | Quantitative | VMAs | 9 | 106 | 106 | 9 | 106 | 106 | 106 | Quantitative | Off-Cycle Patrol
Vegetation Management and Inspection | Fuels management | WMP.497 | Quantitative | Poles | 100 | 200 | 500 | 100 | 200 | 500 | 500 | Quantitative | Fuels management
Vegetation Management and Inspection | Pole Clearing | WMP.512 | Quantitative | Poles | 25150 | 27890 | 33010 | 25150 | 27890 | 33010 | 33010 | Quantitative | Pole Clearing (Brushing)
Vegetation Management and Inspection | Clearance | WMP.501 | Quantitative | Trees Trimmed or Removed | 5890 | 8780 | 11200 | 5890 | 8780 | 11200 | 11200 | Quantitative | Clearance
Vegetation Management and Inspection | Quality assurance / quality control | WMP.505 | Quantitative | Inspections | 15% | 15% | 15% | 15% | 15% | 15% | 15% | Quantitative | QA/QC Vegetation Management

## Table 13
Utility | SDG&E |  | Note: Provide a listing (as rows) of all work orders / notifications for corrective work on electric circuits that were open as of the end of the quarter.
Table No. | 13
Date Modified | 2024-02-01
Table 13: Open work orders / notifications
a. Work order number | b. Equipment Type | c. HFTD Tier | d. Line type | e. Date the work order was originally opened | f. Due date of the original work order | g. GO 95 rule 18 priority level of the original work order | h. Optional utility-specific repair priority | i. Date(s) the work order was reinspected or modified (if applicable) | j. Due date of the work order after it was reinspected or modified (if applicable) | k. Priority of the work order after it was reinspected or modified (if applicable) | l. Reason for reinspection (if applicable)
100021274071 | Pole | Tier 2 | Distribution | 2022-01-28 | 2023-01-30 | Level 2 | N/A
100021274074 | Cross Arm | Tier 2 | Distribution | 2022-01-28 | 2023-01-30 | Level 2 | N/A
100021274526 | Pole | Tier 2 | Distribution | 2022-01-28 | 2023-01-30 | Level 2 | N/A
100021274527 | Cross Arm | Tier 2 | Distribution | 2022-01-28 | 2023-01-30 | Level 2 | N/A
100021274533 | Pole | Tier 2 | Distribution | 2022-01-28 | 2023-01-30 | Level 2 | N/A
100021276243 | Cross Arm | Tier 2 | Distribution | 2022-01-28 | 2023-01-30 | Level 2 | N/A
100021323361 | Pole | Tier 2 | Distribution | 2022-01-28 | 2023-01-30 | Level 2 | N/A
100021769467 | Pole | Tier 2 | Distribution | 2022-04-19 | 2023-04-28 | Level 2 | N/A
100023272451 | Pole | Tier 3 | Distribution | 2023-01-25 | 2023-07-31 | Level 2 | N/A
100023272452 | Pole | Tier 3 | Distribution | 2023-01-25 | 2023-07-31 | Level 2 | N/A
100023628727 | Pole | Tier 3 | Distribution | 2023-04-03 | 2023-10-31 | Level 2 | N/A
100023680015 | Cross Arm | Tier 3 | Distribution | 2023-04-13 | 2023-10-31 | Level 2 | N/A
100023870226 | Conductor | Tier 3 | Distribution | 2023-05-19 | 2023-11-30 | Level 2 | N/A
100023975510 | Pole | Tier 3 | Distribution | 2023-06-05 | 2023-12-31 | Level 2 | N/A
100024018907 | Pole | Tier 3 | Distribution | 2023-06-14 | 2023-12-31 | Level 2 | N/A
100024018908 | Pole | Tier 3 | Distribution | 2023-06-14 | 2023-12-31 | Level 2 | N/A
100024018909 | Pole | Tier 3 | Distribution | 2023-06-14 | 2023-12-31 | Level 2 | N/A
100024048034 | Conductor | Tier 3 | Distribution | 2023-06-20 | 2023-12-31 | Level 2 | N/A
100024093575 | Pole | Tier 3 | Distribution | 2023-06-26 | 2023-12-31 | Level 2 | N/A
100023177889 | Cross Arm | Tier 2 | Distribution | 2023-01-09 | 2024-01-30 | Level 2 | N/A
100023178174 | Pole | Tier 2 | Distribution | 2023-01-09 | 2024-01-30 | Level 2 | N/A
100023178177 | Pole | Tier 2 | Distribution | 2023-01-09 | 2024-01-30 | Level 2 | N/A
100023178178 | Pole | Tier 2 | Distribution | 2023-01-09 | 2024-01-30 | Level 2 | N/A
100023277261 | Cross Arm | Tier 2 | Distribution | 2023-01-24 | 2024-01-30 | Level 2 | N/A
100023318508 | Pole | Tier 2 | Distribution | 2023-02-01 | 2024-02-29 | Level 2 | N/A
100023318509 | Pole | Tier 2 | Distribution | 2023-02-01 | 2024-02-29 | Level 2 | N/A
100023345759 | Other | Tier 2 | Distribution | 2023-02-06 | 2024-02-29 | Level 2 | N/A
100023346444 | Pole | Tier 2 | Distribution | 2023-02-07 | 2024-02-29 | Level 2 | N/A
100023353477 | Pole | Tier 2 | Distribution | 2023-02-08 | 2024-02-29 | Level 2 | N/A
100024307884 | Pole | Tier 3 | Distribution | 2023-08-08 | 2024-02-29 | Level 2 | N/A
100024410679 | Other | Tier 3 | Distribution | 2023-08-25 | 2024-02-29 | Level 2 | N/A
100024410772 | Other | Tier 3 | Distribution | 2023-08-25 | 2024-02-29 | Level 2 | N/A
100023488423 | Conductor | Tier 2 | Distribution | 2023-03-06 | 2024-03-31 | Level 2 | N/A
100023502996 | Pole | Tier 2 | Distribution | 2023-03-09 | 2024-03-31 | Level 2 | N/A
100023529024 | Cross Arm | Tier 2 | Distribution | 2023-03-16 | 2024-03-31 | Level 2 | N/A
100023544924 | Pole | Tier 2 | Distribution | 2023-03-20 | 2024-03-31 | Level 2 | N/A
100023544925 | Pole | Tier 2 | Distribution | 2023-03-20 | 2024-03-31 | Level 2 | N/A
100023544926 | Pole | Tier 2 | Distribution | 2023-03-20 | 2024-03-31 | Level 2 | N/A
100023544927 | Pole | Tier 2 | Distribution | 2023-03-20 | 2024-03-31 | Level 2 | N/A
100023544928 | Pole | Tier 2 | Distribution | 2023-03-20 | 2024-03-31 | Level 2 | N/A
100023557482 | Pole | Tier 2 | Distribution | 2023-03-23 | 2024-03-31 | Level 2 | N/A
100023564405 | Pole | Tier 2 | Distribution | 2023-03-24 | 2024-03-31 | Level 2 | N/A
100023610179 | Pole | Tier 2 | Distribution | 2023-03-30 | 2024-03-31 | Level 2 | N/A
100023613612 | Other | Tier 2 | Distribution | 2023-03-30 | 2024-03-31 | Level 2 | N/A
100023613816 | Other | Tier 2 | Distribution | 2023-03-31 | 2024-03-31 | Level 2 | N/A
100023613817 | Other | Tier 2 | Distribution | 2023-03-31 | 2024-03-31 | Level 2 | N/A
100024562726 | Cross Arm | Tier 3 | Distribution | 2023-09-25 | 2024-03-31 | Level 2 | N/A
100023628728 | Pole | Tier 2 | Distribution | 2023-04-03 | 2024-04-29 | Level 2 | N/A
100023628729 | Pole | Tier 2 | Distribution | 2023-04-03 | 2024-04-29 | Level 2 | N/A
100023628750 | Pole | Tier 2 | Distribution | 2023-04-03 | 2024-04-29 | Level 2 | N/A
100023628994 | Pole | Tier 2 | Distribution | 2023-04-03 | 2024-04-29 | Level 2 | N/A
100023628995 | Pole | Tier 2 | Distribution | 2023-04-03 | 2024-04-29 | Level 2 | N/A
100023628997 | Pole | Tier 2 | Distribution | 2023-04-03 | 2024-04-29 | Level 2 | N/A
100023629574 | Pole | Tier 2 | Distribution | 2023-04-03 | 2024-04-29 | Level 2 | N/A
100023637416 | Pole | Tier 2 | Distribution | 2023-04-05 | 2024-04-29 | Level 2 | N/A
100023637417 | Pole | Tier 2 | Distribution | 2023-04-05 | 2024-04-29 | Level 2 | N/A
100023637418 | Pole | Tier 2 | Distribution | 2023-04-05 | 2024-04-29 | Level 2 | N/A
100023638716 | Cross Arm | Tier 2 | Distribution | 2023-04-05 | 2024-04-29 | Level 2 | N/A
100023642090 | Pole | Tier 2 | Distribution | 2023-04-05 | 2024-04-29 | Level 2 | N/A
100023642091 | Pole | Tier 2 | Distribution | 2023-04-05 | 2024-04-29 | Level 2 | N/A
100023642092 | Pole | Tier 2 | Distribution | 2023-04-05 | 2024-04-29 | Level 2 | N/A
100023642093 | Pole | Tier 2 | Distribution | 2023-04-05 | 2024-04-29 | Level 2 | N/A
100023642094 | Pole | Tier 2 | Distribution | 2023-04-05 | 2024-04-29 | Level 2 | N/A
100023656884 | Pole | Tier 2 | Distribution | 2023-04-10 | 2024-04-29 | Level 2 | N/A
100023656885 | Cross Arm | Tier 2 | Distribution | 2023-04-10 | 2024-04-29 | Level 2 | N/A
100023656886 | Pole | Tier 2 | Distribution | 2023-04-10 | 2024-04-29 | Level 2 | N/A
100023658385 | Other | Tier 2 | Distribution | 2023-04-10 | 2024-04-29 | Level 2 | N/A
100023658387 | Pole | Tier 2 | Distribution | 2023-04-10 | 2024-04-29 | Level 2 | N/A
100023658388 | Cross Arm | Tier 2 | Distribution | 2023-04-10 | 2024-04-29 | Level 2 | N/A
100023658389 | Pole | Tier 2 | Distribution | 2023-04-10 | 2024-04-29 | Level 2 | N/A
100023658561 | Other | Tier 2 | Distribution | 2023-04-10 | 2024-04-29 | Level 2 | N/A
100023659525 | Pole | Tier 2 | Distribution | 2023-04-10 | 2024-04-29 | Level 2 | N/A
100023663010 | Pole | Tier 2 | Distribution | 2023-04-10 | 2024-04-29 | Level 2 | N/A
100023664375 | Pole | Tier 2 | Distribution | 2023-04-11 | 2024-04-29 | Level 2 | N/A
100023664377 | Pole | Tier 2 | Distribution | 2023-04-11 | 2024-04-29 | Level 2 | N/A
100023664378 | Pole | Tier 2 | Distribution | 2023-04-11 | 2024-04-29 | Level 2 | N/A
100023664379 | Pole | Tier 2 | Distribution | 2023-04-11 | 2024-04-29 | Level 2 | N/A
100023664550 | Pole | Tier 2 | Distribution | 2023-04-11 | 2024-04-29 | Level 2 | N/A
100023664551 | Pole | Tier 2 | Distribution | 2023-04-11 | 2024-04-29 | Level 2 | N/A
100023664802 | Pole | Tier 2 | Distribution | 2023-04-11 | 2024-04-29 | Level 2 | N/A
100023672603 | Pole | Tier 2 | Distribution | 2023-04-12 | 2024-04-29 | Level 2 | N/A
100023672933 | Pole | Tier 2 | Distribution | 2023-04-12 | 2024-04-29 | Level 2 | N/A
100023672935 | Pole | Tier 2 | Distribution | 2023-04-12 | 2024-04-29 | Level 2 | N/A
100023672936 | Pole | Tier 2 | Distribution | 2023-04-12 | 2024-04-29 | Level 2 | N/A
100023672937 | Pole | Tier 2 | Distribution | 2023-04-12 | 2024-04-29 | Level 2 | N/A
100023686672 | Pole | Tier 2 | Distribution | 2023-04-14 | 2024-04-29 | Level 2 | N/A
100023686673 | Pole | Tier 2 | Distribution | 2023-04-14 | 2024-04-29 | Level 2 | N/A
100023686674 | Pole | Tier 2 | Distribution | 2023-04-14 | 2024-04-29 | Level 2 | N/A
100023693366 | Pole | Tier 2 | Distribution | 2023-04-17 | 2024-04-29 | Level 2 | N/A
100023693367 | Pole | Tier 2 | Distribution | 2023-04-17 | 2024-04-29 | Level 2 | N/A
100023693412 | Pole | Tier 2 | Distribution | 2023-04-17 | 2024-04-29 | Level 2 | N/A
100023698307 | Pole | Tier 2 | Distribution | 2023-04-18 | 2024-04-29 | Level 2 | N/A
100023699283 | Cross Arm | Tier 2 | Distribution | 2023-04-18 | 2024-04-29 | Level 2 | N/A
100023699287 | Cross Arm | Tier 2 | Distribution | 2023-04-18 | 2024-04-29 | Level 2 | N/A
100023699299 | Cross Arm | Tier 2 | Distribution | 2023-04-18 | 2024-04-29 | Level 2 | N/A
100023699936 | Pole | Tier 2 | Distribution | 2023-04-18 | 2024-04-29 | Level 2 | N/A
100023699937 | Pole | Tier 2 | Distribution | 2023-04-18 | 2024-04-29 | Level 2 | N/A
100023699938 | Pole | Tier 2 | Distribution | 2023-04-18 | 2024-04-29 | Level 2 | N/A
100023712846 | Pole | Tier 2 | Distribution | 2023-04-20 | 2024-04-29 | Level 2 | N/A
100023713766 | Pole | Tier 2 | Distribution | 2023-04-20 | 2024-04-29 | Level 2 | N/A
100023718309 | Pole | Tier 2 | Distribution | 2023-04-21 | 2024-04-29 | Level 2 | N/A
100023718340 | Pole | Tier 2 | Distribution | 2023-04-21 | 2024-04-29 | Level 2 | N/A
100023728754 | Other | Tier 2 | Distribution | 2023-04-24 | 2024-04-29 | Level 2 | N/A
100023728755 | Conductor | Tier 2 | Distribution | 2023-04-24 | 2024-04-29 | Level 2 | N/A
100023730063 | Cross Arm | Tier 2 | Distribution | 2023-04-24 | 2024-04-29 | Level 2 | N/A
100023730064 | Pole | Tier 2 | Distribution | 2023-04-24 | 2024-04-29 | Level 2 | N/A
100023730065 | Pole | Tier 2 | Distribution | 2023-04-24 | 2024-04-29 | Level 2 | N/A
100023730066 | Cross Arm | Tier 2 | Distribution | 2023-04-24 | 2024-04-29 | Level 2 | N/A
100023749393 | Cross Arm | Tier 2 | Distribution | 2023-04-25 | 2024-04-29 | Level 2 | N/A
100023749395 | Cross Arm | Tier 2 | Distribution | 2023-04-25 | 2024-04-29 | Level 2 | N/A
100023749424 | Other | Tier 2 | Distribution | 2023-04-25 | 2024-04-29 | Level 2 | N/A
100023749425 | Cross Arm | Tier 2 | Distribution | 2023-04-25 | 2024-04-29 | Level 2 | N/A
100023749653 | Anchor/Guy | Tier 2 | Distribution | 2023-04-25 | 2024-04-29 | Level 2 | N/A
100023749654 | Cross Arm | Tier 2 | Distribution | 2023-04-25 | 2024-04-29 | Level 2 | N/A
100023749656 | Pole | Tier 2 | Distribution | 2023-04-25 | 2024-04-29 | Level 2 | N/A
100023749693 | Pole | Tier 2 | Distribution | 2023-04-25 | 2024-04-29 | Level 2 | N/A
100023749695 | Pole | Tier 2 | Distribution | 2023-04-25 | 2024-04-29 | Level 2 | N/A
100023749767 | Pole | Tier 2 | Distribution | 2023-04-25 | 2024-04-29 | Level 2 | N/A
100023750652 | Pole | Tier 2 | Distribution | 2023-04-25 | 2024-04-29 | Level 2 | N/A
100023750655 | Pole | Tier 2 | Distribution | 2023-04-25 | 2024-04-29 | Level 2 | N/A
100023750656 | Conductor | Tier 2 | Distribution | 2023-04-25 | 2024-04-29 | Level 2 | N/A
100023750657 | Pole | Tier 2 | Distribution | 2023-04-25 | 2024-04-29 | Level 2 | N/A
100023751013 | Conductor | Tier 2 | Distribution | 2023-04-25 | 2024-04-29 | Level 2 | N/A
100023751015 | Conductor | Tier 2 | Distribution | 2023-04-25 | 2024-04-29 | Level 2 | N/A
100023751016 | Conductor | Tier 2 | Distribution | 2023-04-25 | 2024-04-29 | Level 2 | N/A
100023758749 | Conductor | Tier 2 | Distribution | 2023-04-26 | 2024-04-29 | Level 2 | N/A
100023758840 | Conductor | Tier 2 | Distribution | 2023-04-26 | 2024-04-29 | Level 2 | N/A
100023758841 | Conductor | Tier 2 | Distribution | 2023-04-26 | 2024-04-29 | Level 2 | N/A
100023762351 | Pole | Tier 2 | Distribution | 2023-04-27 | 2024-04-29 | Level 2 | N/A
100023762365 | Cross Arm | Tier 2 | Distribution | 2023-04-27 | 2024-04-29 | Level 2 | N/A
100023762497 | Pole | Tier 2 | Distribution | 2023-04-27 | 2024-04-29 | Level 2 | N/A
100023762690 | Pole | Tier 2 | Distribution | 2023-04-27 | 2024-04-29 | Level 2 | N/A
100023762746 | Pole | Tier 2 | Distribution | 2023-04-27 | 2024-04-29 | Level 2 | N/A
100023763046 | Pole | Tier 2 | Distribution | 2023-04-27 | 2024-04-29 | Level 2 | N/A
100023763047 | Pole | Tier 2 | Distribution | 2023-04-27 | 2024-04-29 | Level 2 | N/A
100023763437 | Pole | Tier 2 | Distribution | 2023-04-27 | 2024-04-29 | Level 2 | N/A
100023763453 | Pole | Tier 2 | Distribution | 2023-04-27 | 2024-04-29 | Level 2 | N/A
100023763598 | Pole | Tier 2 | Distribution | 2023-04-27 | 2024-04-29 | Level 2 | N/A
100023763599 | Conductor | Tier 2 | Distribution | 2023-04-27 | 2024-04-29 | Level 2 | N/A
100024672843 | Other | Tier 3 | Distribution | 2023-10-04 | 2024-04-30 | Level 2 | N/A
100023785294 | Cross Arm | Tier 2 | Distribution | 2023-05-01 | 2024-05-31 | Level 2 | N/A
100023788927 | Pole | Tier 2 | Distribution | 2023-05-02 | 2024-05-31 | Level 2 | N/A
100023789242 | Pole | Tier 2 | Distribution | 2023-05-02 | 2024-05-31 | Level 2 | N/A
100023793257 | Conductor | Tier 2 | Distribution | 2023-05-03 | 2024-05-31 | Level 2 | N/A
100023799316 | Other | Tier 2 | Distribution | 2023-05-04 | 2024-05-31 | Level 2 | N/A
100023799784 | Cross Arm | Tier 2 | Distribution | 2023-05-04 | 2024-05-31 | Level 2 | N/A
100023799785 | Pole | Tier 2 | Distribution | 2023-05-04 | 2024-05-31 | Level 2 | N/A
100023799786 | Pole | Tier 2 | Distribution | 2023-05-04 | 2024-05-31 | Level 2 | N/A
100023799808 | Pole | Tier 2 | Distribution | 2023-05-04 | 2024-05-31 | Level 2 | N/A
100023800069 | Pole | Tier 2 | Distribution | 2023-05-04 | 2024-05-31 | Level 2 | N/A
100023810818 | Other | Tier 2 | Distribution | 2023-05-08 | 2024-05-31 | Level 2 | N/A
100023810840 | Other | Tier 2 | Distribution | 2023-05-08 | 2024-05-31 | Level 2 | N/A
100023812229 | Pole | Tier 2 | Distribution | 2023-05-08 | 2024-05-31 | Level 2 | N/A
100023812763 | Pole | Tier 2 | Distribution | 2023-05-08 | 2024-05-31 | Level 2 | N/A
100023821622 | Pole | Tier 2 | Distribution | 2023-05-09 | 2024-05-31 | Level 2 | N/A
100023821698 | Pole | Tier 2 | Distribution | 2023-05-09 | 2024-05-31 | Level 2 | N/A
100023821699 | Pole | Tier 2 | Distribution | 2023-05-09 | 2024-05-31 | Level 2 | N/A
100023821764 | Other | Tier 2 | Distribution | 2023-05-09 | 2024-05-31 | Level 2 | N/A
100023821914 | Pole | Tier 2 | Distribution | 2023-05-09 | 2024-05-31 | Level 2 | N/A
100023821915 | Other | Tier 2 | Distribution | 2023-05-08 | 2024-05-31 | Level 2 | N/A
100023822497 | Anchor/Guy | Tier 2 | Distribution | 2023-05-09 | 2024-05-31 | Level 2 | N/A
100023822498 | Anchor/Guy | Tier 2 | Distribution | 2023-05-09 | 2024-05-31 | Level 2 | N/A
100023822611 | Pole | Tier 2 | Distribution | 2023-05-09 | 2024-05-31 | Level 2 | N/A
100023823250 | Other | Tier 2 | Distribution | 2023-05-09 | 2024-05-31 | Level 2 | N/A
100023823252 | Pole | Tier 2 | Distribution | 2023-05-09 | 2024-05-31 | Level 2 | N/A
100023834019 | Pole | Tier 2 | Distribution | 2023-05-11 | 2024-05-31 | Level 2 | N/A
100023834833 | Pole | Tier 2 | Distribution | 2023-05-11 | 2024-05-31 | Level 2 | N/A
100023834834 | Pole | Tier 2 | Distribution | 2023-05-11 | 2024-05-31 | Level 2 | N/A
100023834835 | Pole | Tier 2 | Distribution | 2023-05-11 | 2024-05-31 | Level 2 | N/A
100023834836 | Pole | Tier 2 | Distribution | 2023-05-11 | 2024-05-31 | Level 2 | N/A
100023834837 | Pole | Tier 2 | Distribution | 2023-05-11 | 2024-05-31 | Level 2 | N/A
100023838381 | Pole | Tier 2 | Distribution | 2023-05-12 | 2024-05-31 | Level 2 | N/A
100023838382 | Pole | Tier 2 | Distribution | 2023-05-12 | 2024-05-31 | Level 2 | N/A
100023838385 | Pole | Tier 2 | Distribution | 2023-05-12 | 2024-05-31 | Level 2 | N/A
100023838386 | Pole | Tier 2 | Distribution | 2023-05-12 | 2024-05-31 | Level 2 | N/A
100023845391 | Pole | Tier 2 | Distribution | 2023-05-15 | 2024-05-31 | Level 2 | N/A
100023845395 | Pole | Tier 2 | Distribution | 2023-05-15 | 2024-05-31 | Level 2 | N/A
100023845532 | Pole | Tier 2 | Distribution | 2023-05-15 | 2024-05-31 | Level 2 | N/A
100023845533 | Conductor | Tier 2 | Distribution | 2023-05-15 | 2024-05-31 | Level 2 | N/A
100023845848 | Pole | Tier 2 | Distribution | 2023-05-15 | 2024-05-31 | Level 2 | N/A
100023846226 | Pole | Tier 2 | Distribution | 2023-05-08 | 2024-05-31 | Level 2 | N/A
100023849339 | Conductor | Tier 2 | Distribution | 2023-05-16 | 2024-05-31 | Level 2 | N/A
100023849412 | Pole | Tier 2 | Distribution | 2023-05-16 | 2024-05-31 | Level 2 | N/A
100023849414 | Pole | Tier 2 | Distribution | 2023-05-16 | 2024-05-31 | Level 2 | N/A
100023849415 | Pole | Tier 2 | Distribution | 2023-05-16 | 2024-05-31 | Level 2 | N/A
100023851910 | Pole | Tier 2 | Distribution | 2023-05-16 | 2024-05-31 | Level 2 | N/A
100023856523 | Conductor | Tier 2 | Distribution | 2023-05-17 | 2024-05-31 | Level 2 | N/A
100023861221 | Pole | Tier 2 | Distribution | 2023-05-18 | 2024-05-31 | Level 2 | N/A
100023861222 | Conductor | Tier 2 | Distribution | 2023-05-18 | 2024-05-31 | Level 2 | N/A
100023861351 | Cross Arm | Tier 2 | Distribution | 2023-05-18 | 2024-05-31 | Level 2 | N/A
100023862143 | Other | Tier 2 | Distribution | 2023-05-18 | 2024-05-31 | Level 2 | N/A
100023870220 | Pole | Tier 2 | Distribution | 2023-05-19 | 2024-05-31 | Level 2 | N/A
100023870221 | Pole | Tier 2 | Distribution | 2023-05-19 | 2024-05-31 | Level 2 | N/A
100023870222 | Anchor/Guy | Tier 2 | Distribution | 2023-05-19 | 2024-05-31 | Level 2 | N/A
100023881199 | Pole | Tier 2 | Distribution | 2023-05-22 | 2024-05-31 | Level 2 | N/A
100023881290 | Pole | Tier 2 | Distribution | 2023-05-22 | 2024-05-31 | Level 2 | N/A
100023881291 | Conductor | Tier 2 | Distribution | 2023-05-22 | 2024-05-31 | Level 2 | N/A
100023881460 | Pole | Tier 2 | Distribution | 2023-05-22 | 2024-05-31 | Level 2 | N/A
100023881600 | Pole | Tier 2 | Distribution | 2023-05-22 | 2024-05-31 | Level 2 | N/A
100023881602 | Pole | Tier 2 | Distribution | 2023-05-22 | 2024-05-31 | Level 2 | N/A
100023882528 | Other | Tier 2 | Distribution | 2023-05-18 | 2024-05-31 | Level 2 | N/A
100024788796 | Cross Arm | Tier 3 | Distribution | 2023-11-09 | 2024-05-31 | Level 2 | N/A
100024788811 | Cross Arm | Tier 3 | Distribution | 2023-11-09 | 2024-05-31 | Level 2 | N/A
100024788813 | Pole | Tier 3 | Distribution | 2023-11-09 | 2024-05-31 | Level 2 | N/A
100024809344 | Other | Tier 3 | Distribution | 2023-11-14 | 2024-05-31 | Level 2 | N/A
100024809345 | Conductor | Tier 3 | Distribution | 2023-11-14 | 2024-05-31 | Level 2 | N/A
100024809346 | Pole | Tier 3 | Distribution | 2023-11-14 | 2024-05-31 | Level 2 | N/A
100024809347 | Cross Arm | Tier 3 | Distribution | 2023-11-14 | 2024-05-31 | Level 2 | N/A
100024809853 | Other | Tier 3 | Distribution | 2023-11-14 | 2024-05-31 | Level 2 | N/A
100024813275 | Conductor | Tier 3 | Distribution | 2023-11-14 | 2024-05-31 | Level 2 | N/A
100024813276 | Pole | Tier 3 | Distribution | 2023-11-14 | 2024-05-31 | Level 2 | N/A
100024813278 | Cross Arm | Tier 3 | Distribution | 2023-11-14 | 2024-05-31 | Level 2 | N/A
100024813880 | Cross Arm | Tier 3 | Distribution | 2023-11-14 | 2024-05-31 | Level 2 | N/A
100024826104 | Insulator and Bushing | Tier 3 | Distribution | 2023-11-16 | 2024-05-31 | Level 2 | N/A
100024826108 | Other | Tier 3 | Distribution | 2023-11-16 | 2024-05-31 | Level 2 | N/A
100024826109 | Anchor/Guy | Tier 3 | Distribution | 2023-11-16 | 2024-05-31 | Level 2 | N/A
100024826112 | Other | Tier 3 | Distribution | 2023-11-16 | 2024-05-31 | Level 2 | N/A
100024826113 | Anchor/Guy | Tier 3 | Distribution | 2023-11-16 | 2024-05-31 | Level 2 | N/A
100024845465 | Pole | Tier 3 | Distribution | 2023-11-20 | 2024-05-31 | Level 2 | N/A
100024848154 | Pole | Tier 3 | Distribution | 2023-11-21 | 2024-05-31 | Level 2 | N/A
100024848155 | Pole | Tier 3 | Distribution | 2023-11-21 | 2024-05-31 | Level 2 | N/A
100024848156 | Pole | Tier 3 | Distribution | 2023-11-21 | 2024-05-31 | Level 2 | N/A
100024848808 | Pole | Tier 3 | Distribution | 2023-11-21 | 2024-05-31 | Level 2 | N/A
100024851889 | Pole | Tier 3 | Distribution | 2023-11-22 | 2024-05-31 | Level 2 | N/A
100024892414 | Other | Tier 3 | Distribution | 2023-11-06 | 2024-05-31 | Level 2 | N/A
100024895461 | Anchor/Guy | Tier 3 | Distribution | 2023-11-27 | 2024-05-31 | Level 2 | N/A
100024895467 | Cross Arm | Tier 3 | Distribution | 2023-11-27 | 2024-05-31 | Level 2 | N/A
100024895468 | Pole | Tier 3 | Distribution | 2023-11-27 | 2024-05-31 | Level 2 | N/A
100024895469 | Pole | Tier 3 | Distribution | 2023-11-27 | 2024-05-31 | Level 2 | N/A
100024896751 | Pole | Tier 3 | Distribution | 2023-11-27 | 2024-05-31 | Level 2 | N/A
100023966817 | Pole | Tier 2 | Distribution | 2023-06-02 | 2024-06-30 | Level 2 | N/A
100023966818 | Pole | Tier 2 | Distribution | 2023-06-02 | 2024-06-30 | Level 2 | N/A
100023966819 | Pole | Tier 2 | Distribution | 2023-06-02 | 2024-06-30 | Level 2 | N/A
100024019315 | Conductor | Tier 2 | Distribution | 2023-06-14 | 2024-06-30 | Level 2 | N/A
100024019798 | Pole | Tier 2 | Distribution | 2023-06-14 | 2024-06-30 | Level 2 | N/A
100024019850 | Pole | Tier 2 | Distribution | 2023-06-14 | 2024-06-30 | Level 2 | N/A
100024019853 | Pole | Tier 2 | Distribution | 2023-06-14 | 2024-06-30 | Level 2 | N/A
100024019854 | Pole | Tier 2 | Distribution | 2023-06-14 | 2024-06-30 | Level 2 | N/A
100024024212 | Other | Tier 2 | Distribution | 2023-06-15 | 2024-06-30 | Level 2 | N/A
100024024215 | Other | Tier 2 | Distribution | 2023-06-15 | 2024-06-30 | Level 2 | N/A
100024029385 | Pole | Tier 2 | Distribution | 2023-06-16 | 2024-06-30 | Level 2 | N/A
100024029386 | Pole | Tier 2 | Distribution | 2023-06-16 | 2024-06-30 | Level 2 | N/A
100024029987 | Conductor | Tier 2 | Distribution | 2023-06-16 | 2024-06-30 | Level 2 | N/A
100024030643 | Conductor | Tier 2 | Distribution | 2023-06-16 | 2024-06-30 | Level 2 | N/A
100024030644 | Conductor | Tier 2 | Distribution | 2023-06-16 | 2024-06-30 | Level 2 | N/A
100024030871 | Pole | Tier 2 | Distribution | 2023-06-16 | 2024-06-30 | Level 2 | N/A
100024051608 | Pole | Tier 2 | Distribution | 2023-06-21 | 2024-06-30 | Level 2 | N/A
100024058450 | Pole | Tier 2 | Distribution | 2023-06-22 | 2024-06-30 | Level 2 | N/A
100024058451 | Cross Arm | Tier 2 | Distribution | 2023-06-22 | 2024-06-30 | Level 2 | N/A
100024058772 | Conductor | Tier 2 | Distribution | 2023-06-22 | 2024-06-30 | Level 2 | N/A
100024059016 | Cross Arm | Tier 2 | Distribution | 2023-06-22 | 2024-06-30 | Level 2 | N/A
100024099762 | Conductor | Tier 2 | Distribution | 2023-06-27 | 2024-06-30 | Level 2 | N/A
100024099763 | Conductor | Tier 2 | Distribution | 2023-06-27 | 2024-06-30 | Level 2 | N/A
100024100771 | Pole | Tier 2 | Distribution | 2023-06-27 | 2024-06-30 | Level 2 | N/A
100024100880 | Other | Tier 2 | Distribution | 2023-06-27 | 2024-06-30 | Level 2 | N/A
100024100989 | Conductor | Tier 2 | Distribution | 2023-06-27 | 2024-06-30 | Level 2 | N/A
100024101001 | Conductor | Tier 2 | Distribution | 2023-06-27 | 2024-06-30 | Level 2 | N/A
100024101003 | Conductor | Tier 2 | Distribution | 2023-06-27 | 2024-06-30 | Level 2 | N/A
100024101004 | Pole | Tier 2 | Distribution | 2023-06-27 | 2024-06-30 | Level 2 | N/A
100024101005 | Pole | Tier 2 | Distribution | 2023-06-27 | 2024-06-30 | Level 2 | N/A
100024108060 | Conductor | Tier 2 | Distribution | 2023-06-28 | 2024-06-30 | Level 2 | N/A
100024108061 | Pole | Tier 2 | Distribution | 2023-06-28 | 2024-06-30 | Level 2 | N/A
100024108062 | Pole | Tier 2 | Distribution | 2023-06-28 | 2024-06-30 | Level 2 | N/A
100024108063 | Conductor | Tier 2 | Distribution | 2023-06-28 | 2024-06-30 | Level 2 | N/A
100024108929 | Pole | Tier 2 | Distribution | 2023-06-28 | 2024-06-30 | Level 2 | N/A
100024108960 | Cross Arm | Tier 2 | Distribution | 2023-06-28 | 2024-06-30 | Level 2 | N/A
100024175296 | Pole | Tier 2 | Distribution | 2023-07-14 | 2024-07-31 | Level 2 | N/A
100024307885 | Pole | Tier 2 | Distribution | 2023-08-08 | 2024-08-30 | Level 2 | N/A
100024307886 | Pole | Tier 2 | Distribution | 2023-08-08 | 2024-08-30 | Level 2 | N/A
100024307887 | Pole | Tier 2 | Distribution | 2023-08-08 | 2024-08-30 | Level 2 | N/A
100024307888 | Pole | Tier 2 | Distribution | 2023-08-08 | 2024-08-30 | Level 2 | N/A
100024316358 | Pole | Tier 2 | Distribution | 2023-08-09 | 2024-08-30 | Level 2 | N/A
100024316359 | Pole | Tier 2 | Distribution | 2023-08-09 | 2024-08-30 | Level 2 | N/A
100024323672 | Pole | Tier 2 | Distribution | 2023-08-10 | 2024-08-30 | Level 2 | N/A
100024323674 | Pole | Tier 2 | Distribution | 2023-08-10 | 2024-08-30 | Level 2 | N/A
100024352320 | Pole | Tier 2 | Distribution | 2023-08-16 | 2024-08-30 | Level 2 | N/A
100024358432 | Pole | Tier 2 | Distribution | 2023-08-17 | 2024-08-30 | Level 2 | N/A
100024358830 | Cross Arm | Tier 2 | Distribution | 2023-08-17 | 2024-08-30 | Level 2 | N/A
100024484090 | Pole | Tier 2 | Distribution | 2023-09-08 | 2024-09-30 | Level 2 | N/A
100024492467 | Other | Tier 2 | Distribution | 2023-09-11 | 2024-09-30 | Level 2 | N/A
100024502928 | Pole | Tier 2 | Distribution | 2023-09-13 | 2024-09-30 | Level 2 | N/A
100024503480 | Pole | Tier 2 | Distribution | 2023-09-13 | 2024-09-30 | Level 2 | N/A
100024546546 | Pole | Tier 2 | Distribution | 2023-09-21 | 2024-09-30 | Level 2 | N/A
100024546547 | Cross Arm | Tier 2 | Distribution | 2023-09-21 | 2024-09-30 | Level 2 | N/A
100024552866 | Cross Arm | Tier 2 | Distribution | 2023-09-22 | 2024-09-30 | Level 2 | N/A
100024552931 | Cross Arm | Tier 2 | Distribution | 2023-09-22 | 2024-09-30 | Level 2 | N/A
100024552932 | Cross Arm | Tier 2 | Distribution | 2023-09-22 | 2024-09-30 | Level 2 | N/A
100024553654 | Pole | Tier 2 | Distribution | 2023-09-22 | 2024-09-30 | Level 2 | N/A
100024553655 | Pole | Tier 2 | Distribution | 2023-09-22 | 2024-09-30 | Level 2 | N/A
100024553902 | Pole | Tier 2 | Distribution | 2023-09-22 | 2024-09-30 | Level 2 | N/A
100024553903 | Pole | Tier 2 | Distribution | 2023-09-22 | 2024-09-30 | Level 2 | N/A
100024578317 | Pole | Tier 2 | Distribution | 2023-09-27 | 2024-09-30 | Level 2 | N/A
100024578767 | Pole | Tier 2 | Distribution | 2023-09-27 | 2024-09-30 | Level 2 | N/A
100024578768 | Pole | Tier 2 | Distribution | 2023-09-27 | 2024-09-30 | Level 2 | N/A
100024578769 | Pole | Tier 2 | Distribution | 2023-09-27 | 2024-09-30 | Level 2 | N/A
100024580025 | Pole | Tier 2 | Distribution | 2023-09-27 | 2024-09-30 | Level 2 | N/A
100024586415 | Pole | Tier 2 | Distribution | 2023-09-28 | 2024-09-30 | Level 2 | N/A
100024586416 | Other | Tier 2 | Distribution | 2023-09-28 | 2024-09-30 | Level 2 | N/A
100024586417 | Pole | Tier 2 | Distribution | 2023-09-28 | 2024-09-30 | Level 2 | N/A
100024607165 | Conductor | Tier 2 | Distribution | 2023-10-03 | 2024-10-31 | Level 2 | N/A
100024607240 | Pole | Tier 2 | Distribution | 2023-10-03 | 2024-10-31 | Level 2 | N/A
100024607585 | Pole | Tier 2 | Distribution | 2023-10-03 | 2024-10-31 | Level 2 | N/A
100024607586 | Insulator and Bushing | Tier 2 | Distribution | 2023-10-03 | 2024-10-31 | Level 2 | N/A
100024607587 | Cross Arm | Tier 2 | Distribution | 2023-10-03 | 2024-10-31 | Level 2 | N/A
100024607654 | Pole | Tier 2 | Distribution | 2023-10-03 | 2024-10-31 | Level 2 | N/A
100024607655 | Pole | Tier 2 | Distribution | 2023-10-03 | 2024-10-31 | Level 2 | N/A
100024608217 | Pole | Tier 2 | Distribution | 2023-10-03 | 2024-10-31 | Level 2 | N/A
100024636631 | Pole | Tier 2 | Distribution | 2023-10-10 | 2024-10-31 | Level 2 | N/A
100024636991 | Pole | Tier 2 | Distribution | 2023-10-10 | 2024-10-31 | Level 2 | N/A
100024636992 | Pole | Tier 2 | Distribution | 2023-10-10 | 2024-10-31 | Level 2 | N/A
100024705353 | Pole | Tier 2 | Distribution | 2023-10-23 | 2024-10-31 | Level 2 | N/A
100024705469 | Pole | Tier 2 | Distribution | 2023-10-23 | 2024-10-31 | Level 2 | N/A
100024783489 | Other | Tier 2 | Distribution | 2023-11-06 | 2024-11-30 | Level 2 | N/A
100024803658 | Pole | Tier 2 | Distribution | 2023-11-13 | 2024-11-30 | Level 2 | N/A
100024814817 | Other | Tier 2 | Distribution | 2023-11-15 | 2024-11-30 | Level 2 | N/A
100024814992 | Pole | Tier 2 | Distribution | 2023-11-15 | 2024-11-30 | Level 2 | N/A
100024815172 | Pole | Tier 2 | Distribution | 2023-11-15 | 2024-11-30 | Level 2 | N/A
100024830829 | Pole | Tier 2 | Distribution | 2023-11-17 | 2024-11-30 | Level 2 | N/A
100024892056 | Other | Tier 2 | Distribution | 2023-11-20 | 2024-11-30 | Level 2 | N/A
100024892058 | Other | Tier 2 | Distribution | 2023-11-15 | 2024-11-30 | Level 2 | N/A
100024892418 | Other | Tier 2 | Distribution | 2023-11-20 | 2024-11-30 | Level 2 | N/A
100025247078 | Other | Tier 2 | Distribution | 2023-12-28 | 2024-12-31 | Level 2 | N/A
P100104 | Pole | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P100379 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P100380 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P100383 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P100383 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P100520J | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P100556 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P100570 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P100571 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P100609 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P100759 | Cross Arm | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P100922 | Pole | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P100997 | Pole | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P10110 | Other | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P101106 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P10119 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P101230 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P101319J | Pole | Tier 2 | Distribution | 2022-03-15 | N/A | N/A | N/A
P101331 | Pole | Tier 2 | Distribution | 2022-03-04 | N/A | N/A | N/A
P10136 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P101614 | Pole | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P10166 | Other | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P10166 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P101766 | Other | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P10182 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P101899 | Pole | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P101900 | Cross Arm | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P10206 | Cross Arm | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P102142 | Pole | Tier 2 | Distribution | 2022-03-15 | N/A | N/A | N/A
P10223 | Cross Arm | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P10228 | Cross Arm | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P102346 | Cross Arm | Tier 2 | Distribution | 2022-05-13 | N/A | N/A | N/A
P10242 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P102518 | Pole | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P102519 | Pole | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P102597 | Cross Arm | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P102798 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P103128 | Cross Arm | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P103149 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P10317 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P103249 | Insulator and Bushing | Tier 2 | Distribution | 2021-10-26 | N/A | N/A | N/A
P10331J | Insulator and Bushing | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P103345 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P10337 | Other | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P10341 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P10350 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P103630 | Other | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P103671 | Pole | Tier 2 | Distribution | 2021-10-18 | N/A | N/A | N/A
P103782 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P10394 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P10394 | Fuse | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P10394 | Insulator and Bushing | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P10394 | Transformer | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P104031 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P104031 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P104031 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P104031 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P10412 | Pole | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P104132 | Insulator and Bushing | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P104982 | Cross Arm | Tier 2 | Distribution | 2021-07-17 | N/A | N/A | N/A
P104982 | Insulator and Bushing | Tier 2 | Distribution | 2021-07-17 | N/A | N/A | N/A
P104982 | Other | Tier 2 | Distribution | 2021-07-17 | N/A | N/A | N/A
P105077 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P105157 | Cross Arm | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P105157 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P105189 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P106015J | Pole | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P106016J | Pole | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P106139 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P106139 | Pole | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P106547 | Pole | Tier 2 | Distribution | 2021-11-20 | N/A | N/A | N/A
P10687J | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P107327 | Other | Tier 2 | Distribution | 2022-10-18 | N/A | N/A | N/A
P107351 | Transformer | Tier 2 | Distribution | 2021-10-26 | N/A | N/A | N/A
P107408 | Pole | Tier 2 | Distribution | 2022-03-14 | N/A | N/A | N/A
P107419 | Pole | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P10746 | Cross Arm | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P10747 | Cross Arm | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P107564 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P107652 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P107655 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P107659 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P107714 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P107715 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P107716 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P107716 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P107719 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P107728 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P107875 | Cross Arm | Tier 2 | Distribution | 2022-03-04 | N/A | N/A | N/A
P107975 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P107995 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P108130 | Pole | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P108134 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P108139 | Other | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P108153 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P108274 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P108277 | Other | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P108354 | Other | Tier 3 | Distribution | 2020-04-22 | N/A | N/A | N/A
P108381 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P108542 | Pole | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P108919 | Pole | Tier 2 | Distribution | 2022-03-09 | N/A | N/A | N/A
P109000 | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P109156 | Pole | Tier 2 | Distribution | 2021-07-17 | N/A | N/A | N/A
P109329 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P109459 | Pole | Tier 2 | Distribution | 2022-08-12 | N/A | N/A | N/A
P109477 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P109502 | Other | Tier 3 | Distribution | 2020-04-15 | N/A | N/A | N/A
P109502 | Pole | Tier 3 | Distribution | 2020-04-15 | N/A | N/A | N/A
P109522 | Other | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P109537 | Pole | Tier 2 | Distribution | 2022-03-14 | N/A | N/A | N/A
P109582 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P109611 | Pole | Tier 2 | Distribution | 2022-10-04 | N/A | N/A | N/A
P109705 | Pole | Tier 2 | Distribution | 2021-08-20 | N/A | N/A | N/A
P109812 | Pole | Tier 2 | Distribution | 2022-03-25 | N/A | N/A | N/A
P109851 | Pole | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P110132 | Anchor/Guy | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P110132 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P110202 | Cross Arm | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P110202 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P110206 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P110320 | Pole | Tier 2 | Distribution | 2022-03-23 | N/A | N/A | N/A
P110387 | Anchor/Guy | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P110394 | Pole | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P110414 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P110414 | Other | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P110433 | Cross Arm | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P110464 | Other | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P110511 | Cross Arm | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P110511 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P110605J | Conductor | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P110605J | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P110605J | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P110609 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P110640 | Pole | Tier 2 | Distribution | 2022-09-29 | N/A | N/A | N/A
P110783 | Cross Arm | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P110783 | Pole | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P110954 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P110993 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P110993 | Other | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P110995 | Pole | Tier 2 | Distribution | 2022-08-11 | N/A | N/A | N/A
P111019J | Cross Arm | Tier 2 | Distribution | 2021-08-20 | N/A | N/A | N/A
P111022 | Cross Arm | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P111022 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P111023 | Anchor/Guy | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P111113 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P111113 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P111170 | Transformer | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P111188 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P111245 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P111253 | Cross Arm | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P111262 | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P111324 | Cross Arm | Tier 2 | Distribution | 2022-04-21 | N/A | N/A | N/A
P111340 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P111345J | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P111368 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P111378 | Cross Arm | Tier 2 | Distribution | 2022-08-01 | N/A | N/A | N/A
P111380 | Pole | Tier 2 | Distribution | 2022-08-01 | N/A | N/A | N/A
P111381 | Other | Tier 2 | Distribution | 2022-10-25 | N/A | N/A | N/A
P111452 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P111452 | Insulator and Bushing | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P111470 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P111470 | Transformer | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P111474 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P111477 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P111482 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P111483 | Pole | Tier 2 | Distribution | 2022-12-12 | N/A | N/A | N/A
P111486 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P111505 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P111507 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P111508 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P111613 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P111625 | Pole | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P111755 | Pole | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P111809 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P111908 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P111956 | Other | Tier 2 | Distribution | 2021-10-18 | N/A | N/A | N/A
P112028 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P112067 | Cross Arm | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P112072 | Cross Arm | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P112080 | Pole | Tier 2 | Distribution | 2022-06-10 | N/A | N/A | N/A
P112081 | Pole | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P112085 | Pole | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P112086 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P112107 | Other | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P112107 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P112115 | Cross Arm | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P112183 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P112306 | Pole | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P112379 | Pole | Tier 3 | Distribution | 2020-02-25 | N/A | N/A | N/A
P112394 | Pole | Tier 2 | Distribution | 2022-11-01 | N/A | N/A | N/A
P112539 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P112541J | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P112542J | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P112547 | Pole | Tier 2 | Distribution | 2022-12-19 | N/A | N/A | N/A
P112683 | Pole | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P112684 | Cross Arm | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P112686 | Pole | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P112687 | Conductor | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P112687 | Pole | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P112689 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P112893 | Cross Arm | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P112893 | Insulator and Bushing | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P112893 | Pole | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P112951 | Pole | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P113017 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P113126 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P113187 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P113276 | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P113276 | Other | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P113356 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P113385 | Pole | Tier 2 | Distribution | 2022-12-08 | N/A | N/A | N/A
P113386 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P113400 | Cross Arm | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P113400 | Other | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P113400 | Pole | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P113425 | Pole | Tier 2 | Distribution | 2021-10-21 | N/A | N/A | N/A
P113443 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P113462 | Pole | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P113491 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P113566 | Cross Arm | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P113566 | Insulator and Bushing | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P113568 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P113657 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P113657 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P113699 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P113700 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P113776 | Pole | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P113777 | Pole | Tier 2 | Distribution | 2022-09-02 | N/A | N/A | N/A
P113778 | Cross Arm | Tier 2 | Distribution | 2022-08-30 | N/A | N/A | N/A
P113783 | Conductor | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P113929 | Other | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P113952 | Other | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P113963 | Other | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P113972 | Cross Arm | Tier 2 | Distribution | 2022-03-22 | N/A | N/A | N/A
P113985 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P113991 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P114118 | Other | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P114118 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P114203 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P114236 | Conductor | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P114236 | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P114309 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P114310 | Other | Tier 2 | Distribution | 2022-10-28 | N/A | N/A | N/A
P114527 | Cross Arm | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P114527 | Pole | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P114531 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P114532 | Anchor/Guy | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P114535 | Cross Arm | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P114542 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P114543J | Cross Arm | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P114543J | Other | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P114549 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P114563 | Cross Arm | Tier 2 | Distribution | 2022-03-24 | N/A | N/A | N/A
P114601 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P114629 | Cross Arm | Tier 2 | Distribution | 2022-03-28 | N/A | N/A | N/A
P114668 | Other | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P114668 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P114687 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P114687 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P114701 | Cross Arm | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P114841 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P114841 | Pole | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P114888 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P114906 | Cross Arm | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P114906 | Other | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P114906 | Other | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P114907 | Pole | Tier 2 | Distribution | 2022-03-31 | N/A | N/A | N/A
P115181 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P115184 | Other | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P115319 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P115350 | Cross Arm | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P115355 | Insulator and Bushing | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P115355 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P115355 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P115382 | Anchor/Guy | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P115405 | Transformer | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P115436 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P115604 | Pole | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P115622 | Pole | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P115635 | Cross Arm | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P115635 | Other | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P115792 | Other | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P115792 | Other | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P115849 | Pole | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P115881 | Cross Arm | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P115934 | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P116046 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P116051 | Cross Arm | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P116051 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P116053 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P116056 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P116060 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P116074 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P11624 | Cross Arm | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P11631 | Pole | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P116331 | Anchor/Guy | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P116352 | Pole | Tier 2 | Distribution | 2022-12-01 | N/A | N/A | N/A
P116372 | Cross Arm | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P116372 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P116373 | Cross Arm | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P116373 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P116420 | Transformer | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P116423 | Cross Arm | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P116426 | Cross Arm | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P116439 | Insulator and Bushing | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P116488 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P116498J | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P116498J | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P116499 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P116499 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P116505J | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P116505J | Transformer | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P116542 | Cross Arm | Tier 2 | Distribution | 2022-05-13 | N/A | N/A | N/A
P116548 | Pole | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P116639 | Transformer | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P116712 | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P116712 | Other | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P11683 | Cross Arm | Tier 3 | Distribution | 2022-10-12 | N/A | N/A | N/A
P11683 | Other | Tier 3 | Distribution | 2022-10-12 | N/A | N/A | N/A
P116848 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P116887 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P116887 | Other | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P116891 | Transformer | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P116894 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P116900 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P116938 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P116962 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P116987 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P117038 | Pole | Tier 2 | Distribution | 2022-11-18 | N/A | N/A | N/A
P117088 | Cross Arm | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P117088 | Other | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P117119 | Pole | Tier 2 | Distribution | 2022-03-23 | N/A | N/A | N/A
P117122 | Pole | Tier 2 | Distribution | 2022-12-28 | N/A | N/A | N/A
P117123 | Pole | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P117124 | Cross Arm | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P117125 | Pole | Tier 2 | Distribution | 2022-03-22 | N/A | N/A | N/A
P117132 | Anchor/Guy | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P117145 | Pole | Tier 2 | Distribution | 2022-03-15 | N/A | N/A | N/A
P117149 | Pole | Tier 2 | Distribution | 2022-03-17 | N/A | N/A | N/A
P117154 | Pole | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P117186 | Cross Arm | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P117257 | Cross Arm | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P117257 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P117257 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P117257 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P117257 | Transformer | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P117305 | Conductor | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P117305 | Cross Arm | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P117305 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P117305 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P117337 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P117343 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P117343 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P117345 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P117347 | Cross Arm | Tier 2 | Distribution | 2022-11-18 | N/A | N/A | N/A
P117351 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P117376 | Cross Arm | Tier 2 | Distribution | 2022-03-18 | N/A | N/A | N/A
P117378 | Cross Arm | Tier 2 | Distribution | 2022-03-24 | N/A | N/A | N/A
P117389J | Pole | Tier 2 | Distribution | 2022-03-18 | N/A | N/A | N/A
P117451 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P117486 | Cross Arm | Tier 2 | Distribution | 2022-06-27 | N/A | N/A | N/A
P117521 | Pole | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P117559 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P117587 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P117588 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P117589 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P117589 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P117595 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P117595 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P117596 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P117596 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P117597 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P117598 | Cross Arm | Tier 2 | Distribution | 2022-03-17 | N/A | N/A | N/A
P117600 | Other | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P117625 | Other | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P117625 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P117626 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P117629 | Insulator and Bushing | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P117629 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P117635 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P117636 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P117641 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P117654 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P117655 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P117656 | Cross Arm | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P117656 | Other | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P117656 | Other | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P117668 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P117800 | Cross Arm | Tier 2 | Distribution | 2022-12-12 | N/A | N/A | N/A
P117801 | Switch | Tier 2 | Distribution | 2022-12-12 | N/A | N/A | N/A
P117804 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P117807 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P117813 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P117813 | Other | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P117813 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P117823 | Pole | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P117824 | Pole | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P117825 | Pole | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P117831 | Pole | Tier 2 | Distribution | 2022-03-14 | N/A | N/A | N/A
P117859 | Pole | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P117877 | Pole | Tier 2 | Distribution | 2022-03-31 | N/A | N/A | N/A
P117878 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P117932 | Other | Tier 2 | Distribution | 2022-09-12 | N/A | N/A | N/A
P117952 | Cross Arm | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P118555 | Other | Tier 2 | Distribution | 2021-09-30 | N/A | N/A | N/A
P118647 | Other | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P118700 | Other | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P118700 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P118703 | Other | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P118754 | Cross Arm | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P118761 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P118811 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P118827 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P118859 | Pole | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P118868 | Transformer | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P118873 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P118940 | Cross Arm | Tier 2 | Distribution | 2022-06-27 | N/A | N/A | N/A
P118954 | Cross Arm | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P118955 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P118961 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P118969 | Pole | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P118972 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P118972 | Transformer | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P118973 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P118979 | Conductor | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P118979 | Cross Arm | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P118980 | Conductor | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P118980 | Pole | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P118982 | Cross Arm | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P119120 | Pole | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P119144 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P119155 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P119155 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P119178 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P119255 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P119255 | Insulator and Bushing | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P119258 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P119276 | Pole | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P119280 | Cross Arm | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P119333 | Cross Arm | Tier 2 | Distribution | 2021-08-20 | N/A | N/A | N/A
P119364 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P11939 | Cross Arm | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P119447 | Other | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P119476 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P119490 | Cross Arm | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P119492 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P119492 | Other | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P119519 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P119686 | Other | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P119686 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P119728 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P119728 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P119839 | Cross Arm | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P119896 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P120814 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P121060 | Other | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P121060 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P121647J | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P121649J | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P121934 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P122211 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P122212 | Pole | Tier 2 | Distribution | 2022-09-09 | N/A | N/A | N/A
P122573 | Other | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P123763 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P124095 | Anchor/Guy | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P124113 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P124118 | Pole | Tier 2 | Distribution | 2022-11-01 | N/A | N/A | N/A
P124119 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P124453 | Pole | Tier 2 | Distribution | 2022-11-05 | N/A | N/A | N/A
P124941J | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P124942J | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P124942J | Insulator and Bushing | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P124947J | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P125025 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P125653 | Conductor | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P125653 | Other | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P125653 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P125701J | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P126052 | Insulator and Bushing | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P126063 | Other | Tier 2 | Distribution | 2022-10-18 | N/A | N/A | N/A
P12609 | Pole | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P12653 | Pole | Tier 2 | Distribution | 2021-11-02 | N/A | N/A | N/A
P12662 | Anchor/Guy | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P12662 | Cross Arm | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P127013 | Cross Arm | Tier 2 | Distribution | 2022-10-31 | N/A | N/A | N/A
P127214J | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P12790 | Cross Arm | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P128403 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P128441 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P128450 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P128450 | Other | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P128450 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P128451 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P128454 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P128455 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P128456 | Other | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P128456 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P128463 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P128463 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P128869 | Pole | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P128871J | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P128871J | Pole | Tier 2 | Distribution | 2022-05-13 | N/A | N/A | N/A
P128906 | Cross Arm | Tier 2 | Distribution | 2022-08-17 | N/A | N/A | N/A
P129892 | Other | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P12993J | Anchor/Guy | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P130386 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P130439 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P130456 | Pole | Tier 2 | Distribution | 2022-08-31 | N/A | N/A | N/A
P130553 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P130612 | Pole | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P130679 | Other | Tier 3 | Distribution | 2020-09-09 | N/A | N/A | N/A
P130711 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P130711 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P130757 | Pole | Tier 2 | Distribution | 2022-12-14 | N/A | N/A | N/A
P130773 | Cross Arm | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P130773 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P13081 | Other | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P13081 | Transformer | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P13087 | Pole | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P13092 | Cross Arm | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P130925 | Cross Arm | Tier 2 | Distribution | 2021-11-20 | N/A | N/A | N/A
P130943 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P130943 | Pole | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P13097 | Other | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P130975 | Anchor/Guy | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P13098 | Anchor/Guy | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P13098 | Insulator and Bushing | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P13098 | Other | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P13101 | Insulator and Bushing | Tier 2 | Distribution | 2021-08-20 | N/A | N/A | N/A
P13102 | Other | Tier 2 | Distribution | 2021-08-20 | N/A | N/A | N/A
P131026 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P131085 | Other | Tier 2 | Distribution | 2022-10-27 | N/A | N/A | N/A
P131125 | Cross Arm | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P131156 | Cross Arm | Tier 2 | Distribution | 2022-03-31 | N/A | N/A | N/A
P131177 | Cross Arm | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P131178 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P13131 | Cross Arm | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P13131 | Other | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P13132 | Pole | Tier 2 | Distribution | 2022-10-27 | N/A | N/A | N/A
P131402 | Pole | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P131413 | Other | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P131413 | Transformer | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P131427 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P13145J | Cross Arm | Tier 2 | Distribution | 2021-11-23 | N/A | N/A | N/A
P13145J | Other | Tier 2 | Distribution | 2021-11-23 | N/A | N/A | N/A
P13145J | Other | Tier 2 | Distribution | 2021-11-23 | N/A | N/A | N/A
P13148 | Other | Tier 2 | Distribution | 2021-11-23 | N/A | N/A | N/A
P13149 | Other | Tier 2 | Distribution | 2022-12-03 | N/A | N/A | N/A
P13160 | Other | Tier 2 | Distribution | 2022-03-03 | N/A | N/A | N/A
P13160 | Pole | Tier 2 | Distribution | 2022-03-03 | N/A | N/A | N/A
P13165 | Cross Arm | Tier 2 | Distribution | 2022-06-27 | N/A | N/A | N/A
P13167 | Cross Arm | Tier 2 | Distribution | 2022-06-27 | N/A | N/A | N/A
P13175 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P13212 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P13212 | Insulator and Bushing | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P13285 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P132895 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P132897 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P13291 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P132911 | Cross Arm | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P13294 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P132945 | Cross Arm | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P132945 | Pole | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P132947 | Cross Arm | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P132947 | Other | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P13296 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P132977 | Transformer | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P132979 | Pole | Tier 2 | Distribution | 2022-11-02 | N/A | N/A | N/A
P13309 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P13310 | Pole | Tier 2 | Distribution | 2022-08-24 | N/A | N/A | N/A
P133147 | Pole | Tier 2 | Distribution | 2022-03-02 | N/A | N/A | N/A
P133148 | Cross Arm | Tier 2 | Distribution | 2022-03-02 | N/A | N/A | N/A
P133417 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P133456 | Other | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P133499 | Anchor/Guy | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P133499 | Other | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P13416 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P134638 | Cross Arm | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P13465 | Pole | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P134684 | Cross Arm | Tier 2 | Distribution | 2022-07-11 | N/A | N/A | N/A
P134687 | Other | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P134687 | Other | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P134687 | Pole | Tier 2 | Distribution | 2022-08-11 | N/A | N/A | N/A
P134730 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P134730 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P134731 | Insulator and Bushing | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P134731 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P134768 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P134836 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P134855 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P134856 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P134858 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P134864 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P134865 | Transformer | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P134997 | Pole | Tier 2 | Distribution | 2021-07-17 | N/A | N/A | N/A
P135039 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P135041 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P135067 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P135075 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P135086 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P135086 | Pole | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P135142 | Cross Arm | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P135199 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P135230 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P135230 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P13527 | Pole | Tier 2 | Distribution | 2022-06-15 | N/A | N/A | N/A
P135286 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P135325 | Pole | Tier 2 | Distribution | 2022-12-28 | N/A | N/A | N/A
P13597 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P13607 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P136166 | Other | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P136166 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P136199 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P136200 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P136273 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P136388 | Cross Arm | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P136388 | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P13639 | Pole | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P136390 | Cross Arm | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P136476 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P136565 | Pole | Tier 2 | Distribution | 2022-09-26 | N/A | N/A | N/A
P136601 | Pole | Tier 2 | Distribution | 2022-09-26 | N/A | N/A | N/A
P137761 | Pole | Tier 2 | Distribution | 2022-05-04 | N/A | N/A | N/A
P137836 | Cross Arm | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P13785 | Pole | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P13793 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P13794 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P137960 | Cross Arm | Tier 2 | Distribution | 2022-03-30 | N/A | N/A | N/A
P137967 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P137972 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P137990 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P138009 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P138010 | Cross Arm | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P138010 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P13831 | Other | Tier 2 | Distribution | 2021-08-20 | N/A | N/A | N/A
P13831 | Pole | Tier 2 | Distribution | 2021-08-20 | N/A | N/A | N/A
P13849 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P13849 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P13850 | Anchor/Guy | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P138656 | Pole | Tier 2 | Distribution | 2022-05-11 | N/A | N/A | N/A
P138676 | Pole | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P138693 | Pole | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P138747 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P138747 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P138748 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P139091 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P139135 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P13922 | Cross Arm | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P13923 | Pole | Tier 2 | Distribution | 2021-11-30 | N/A | N/A | N/A
P139511 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P13992 | Other | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P14208 | Pole | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P14413 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P14430 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P14430 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P14434 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P14439 | Cross Arm | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P14742 | Pole | Tier 2 | Distribution | 2022-08-22 | N/A | N/A | N/A
P14743 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P14766 | Other | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P14771 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P14791 | Cross Arm | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P14792 | Cross Arm | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P14901 | Cross Arm | Tier 2 | Distribution | 2022-11-14 | N/A | N/A | N/A
P14949 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P14956 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P14959 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P14985J | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P15084 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P15087 | Other | Tier 2 | Distribution | 2022-10-03 | N/A | N/A | N/A
P15137 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P15137 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P15285 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P15316 | Pole | Tier 2 | Distribution | 2022-04-04 | N/A | N/A | N/A
P15317 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P15317 | Transformer | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P15375 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P15429 | Cross Arm | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P15430 | Pole | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P15460 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P15461 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P15462J | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P15463J | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P15477 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P15479 | Other | Tier 2 | Distribution | 2022-11-09 | N/A | N/A | N/A
P15480 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P15535J | Other | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P15535J | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P15547 | Cross Arm | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P15548 | Other | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P15548 | Pole | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P15549 | Pole | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P15560 | Cross Arm | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P15569 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P15570 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P15574 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P15580 | Other | Tier 2 | Distribution | 2022-12-02 | N/A | N/A | N/A
P15615 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P15615 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P15804 | Cross Arm | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P15947 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P16001 | Cross Arm | Tier 2 | Distribution | 2022-03-02 | N/A | N/A | N/A
P16002 | Other | Tier 2 | Distribution | 2022-10-18 | N/A | N/A | N/A
P160114 | Pole | Tier 2 | Distribution | 2021-11-20 | N/A | N/A | N/A
P160183 | Cross Arm | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P16027 | Fuse | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P16027 | Other | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P16030 | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P16032 | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P16034 | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P160457 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P160468 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P160470 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P160512 | Pole | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P16058 | Other | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P16058 | Transformer | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P160603 | Pole | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P160919 | Pole | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P161050 | Cross Arm | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P161050 | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P161051 | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P161262 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P161286 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P16131 | Pole | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P161315 | Pole | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P161347 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P161380 | Pole | Tier 2 | Distribution | 2022-12-02 | N/A | N/A | N/A
P161398 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P161457 | Pole | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P161528 | Other | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P16163 | Cross Arm | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P16163 | Pole | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P16173 | Other | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P16174 | Cross Arm | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P16174 | Pole | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P161747 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P161754 | Pole | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P16176 | Cross Arm | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P16176 | Pole | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P161837 | Pole | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P161872 | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P161880 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P161948 | Other | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P162131 | Cross Arm | Tier 2 | Distribution | 2022-06-29 | N/A | N/A | N/A
P162131 | Other | Tier 2 | Distribution | 2022-06-29 | N/A | N/A | N/A
P162131 | Pole | Tier 2 | Distribution | 2022-06-29 | N/A | N/A | N/A
P162199 | Other | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P162199 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P162200 | Other | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P162209 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P162408 | Pole | Tier 2 | Distribution | 2022-05-03 | N/A | N/A | N/A
P162577 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P162772 | Pole | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P162793 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P162903 | Pole | Tier 2 | Distribution | 2022-11-21 | N/A | N/A | N/A
P163166 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P163362 | Pole | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P163400 | Pole | Tier 2 | Distribution | 2021-07-19 | N/A | N/A | N/A
P163408 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P163408 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P16346 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P163483 | Pole | Tier 2 | Distribution | 2022-05-26 | N/A | N/A | N/A
P16349 | Anchor/Guy | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P16349 | Other | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P16349 | Other | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P16350 | Other | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P16350 | Other | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P16353 | Cross Arm | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P16353 | Other | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P16354 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P163566 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P16358 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P16370 | Cross Arm | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P163711 | Other | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P16377 | Cross Arm | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P163800 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P16389 | Pole | Tier 2 | Distribution | 2022-03-31 | N/A | N/A | N/A
P16392 | Anchor/Guy | Tier 2 | Distribution | 2022-03-31 | N/A | N/A | N/A
P164022 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P164100 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P164112 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P164147 | Pole | Tier 2 | Distribution | 2022-03-23 | N/A | N/A | N/A
P164159 | Pole | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P164187 | Pole | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P164188 | Insulator and Bushing | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P164218 | Anchor/Guy | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P164218 | Other | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P164225 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P164263 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P164263 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P164336 | Pole | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P164345 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P164469 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P164512 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P164514 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P164601 | Insulator and Bushing | Tier 2 | Distribution | 2022-11-07 | N/A | N/A | N/A
P16469 | Pole | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P16471 | Anchor/Guy | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P164764 | Pole | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P164857 | Pole | Tier 2 | Distribution | 2022-12-21 | N/A | N/A | N/A
P164936 | Pole | Tier 2 | Distribution | 2021-10-26 | N/A | N/A | N/A
P165029 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P165037 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P165038 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P165153 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P165153 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P165158 | Cross Arm | Tier 2 | Distribution | 2022-03-23 | N/A | N/A | N/A
P165163 | Cross Arm | Tier 2 | Distribution | 2022-03-23 | N/A | N/A | N/A
P165166 | Cross Arm | Tier 2 | Distribution | 2022-03-23 | N/A | N/A | N/A
P165180 | Pole | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P165189 | Pole | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P165190 | Pole | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P165201 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P165203 | Pole | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P165216 | Pole | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P165224 | Pole | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P165225 | Other | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P165225 | Pole | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P165236 | Pole | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P165272 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P165296 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P165440 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P165454 | Other | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P165454 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P165603 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P165631 | Pole | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P165651 | Other | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P165651 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P165724 | Pole | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P165743 | Anchor/Guy | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P165743 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P165748 | Pole | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P165816 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P165821 | Anchor/Guy | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P165821 | Pole | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P165961 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P166026 | Cross Arm | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P166026 | Other | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P166116 | Pole | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P166128 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P166245 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P166469 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P166527 | Anchor/Guy | Tier 2 | Distribution | 2022-08-18 | N/A | N/A | N/A
P166529 | Pole | Tier 2 | Distribution | 2022-08-18 | N/A | N/A | N/A
P166530 | Other | Tier 2 | Distribution | 2022-08-18 | N/A | N/A | N/A
P166530 | Pole | Tier 2 | Distribution | 2022-08-18 | N/A | N/A | N/A
P166531 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P166907 | Anchor/Guy | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P166912 | Anchor/Guy | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P16697 | Pole | Tier 2 | Distribution | 2022-10-20 | N/A | N/A | N/A
P16699 | Cross Arm | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P16699 | Other | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P16703 | Cross Arm | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P16703 | Insulator and Bushing | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P167089 | Other | Tier 3 | Distribution | 2020-05-05 | N/A | N/A | N/A
P167162 | Switch | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P167223 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P167224 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P167558 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P167695 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P167696 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P167719 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P167731 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P167748 | Other | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P167748 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P167860 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P167863 | Insulator and Bushing | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P167863 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P167932 | Cross Arm | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P167953 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P167970 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P168057 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P168079 | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P168137 | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P168137 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P168223 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P168241 | Pole | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P168537 | Other | Tier 2 | Distribution | 2022-12-02 | N/A | N/A | N/A
P168537 | Pole | Tier 2 | Distribution | 2022-12-02 | N/A | N/A | N/A
P168594 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P16872 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P168743 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P168809 | Pole | Tier 2 | Distribution | 2022-08-18 | N/A | N/A | N/A
P168851 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P168904 | Pole | Tier 2 | Distribution | 2021-08-17 | N/A | N/A | N/A
P168925 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P16907 | Anchor/Guy | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P16907 | Cross Arm | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P16907 | Pole | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P169126 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P169264 | Other | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P16928J | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P16930J | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P16930J | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P16936 | Cross Arm | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P16936 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P169363 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P16938 | Anchor/Guy | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P16938 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P16938 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P169385 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P16939 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P16947 | Other | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P16951 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P169516 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P169550 | Insulator and Bushing | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P16959 | Other | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P16959 | Other | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P16975 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P170171 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P17023 | Cross Arm | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P17023 | Pole | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P17024 | Pole | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P17041 | Cross Arm | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P17041 | Other | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P170502 | Pole | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P170504 | Pole | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P17057 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P17059 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P17067 | Other | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P17067 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P17081 | Conductor | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P17081 | Insulator and Bushing | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P17081 | Pole | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P170883 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P170922 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P170922 | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P170922 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P17106 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P17130 | Other | Tier 2 | Distribution | 2022-12-16 | N/A | N/A | N/A
P17132 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P17137 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P17137 | Other | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P171426 | Pole | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P17148 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P172048 | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P172246 | Cross Arm | Tier 2 | Distribution | 2022-03-25 | N/A | N/A | N/A
P172246 | Pole | Tier 2 | Distribution | 2022-03-25 | N/A | N/A | N/A
P172255 | Transformer | Tier 2 | Distribution | 2022-09-20 | N/A | N/A | N/A
P172261 | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P172263 | Cross Arm | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P172268 | Other | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P172444 | Pole | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P172450 | Pole | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P172452 | Pole | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P172453 | Pole | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P172455J | Anchor/Guy | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P172466 | Other | Tier 2 | Distribution | 2022-02-10 | N/A | N/A | N/A
P172470 | Insulator and Bushing | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P172470 | Other | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P172471 | Anchor/Guy | Tier 2 | Distribution | 2022-02-10 | N/A | N/A | N/A
P172477 | Cross Arm | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P172479 | Other | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P172481 | Cross Arm | Tier 2 | Distribution | 2022-02-10 | N/A | N/A | N/A
P172484J | Other | Tier 2 | Distribution | 2022-02-10 | N/A | N/A | N/A
P172498 | Other | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P172499 | Cross Arm | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P172499 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P172508 | Pole | Tier 2 | Distribution | 2022-05-27 | N/A | N/A | N/A
P172514 | Pole | Tier 2 | Distribution | 2021-12-03 | N/A | N/A | N/A
P172516 | Cross Arm | Tier 2 | Distribution | 2021-12-03 | N/A | N/A | N/A
P172518 | Cross Arm | Tier 2 | Distribution | 2021-12-03 | N/A | N/A | N/A
P172525 | Cross Arm | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P172527 | Cross Arm | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P172527 | Pole | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P172541 | Pole | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P172762J | Cross Arm | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P172817 | Other | Tier 3 | Distribution | 2020-03-13 | N/A | N/A | N/A
P172820 | Pole | Tier 3 | Distribution | 2022-11-17 | N/A | N/A | N/A
P173315 | Cross Arm | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P173315 | Other | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P173316 | Cross Arm | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P173316 | Insulator and Bushing | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P173316 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P173345 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P173522 | Conductor | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P173522 | Cross Arm | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P173587 | Pole | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P173722 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P173722 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P173725 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P173856 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P17396 | Cross Arm | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P174018 | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P174018 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P17425 | Insulator and Bushing | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P174250 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P174255 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P174693 | Cross Arm | Tier 2 | Distribution | 2022-02-11 | N/A | N/A | N/A
P174695 | Cross Arm | Tier 2 | Distribution | 2022-02-11 | N/A | N/A | N/A
P174798 | Transformer | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P174808 | Other | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P17493 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P174997 | Insulator and Bushing | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P174997 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P175007 | Other | Tier 3 | Distribution | 2020-05-14 | N/A | N/A | N/A
P175013 | Cross Arm | Tier 2 | Distribution | 2022-08-31 | N/A | N/A | N/A
P175016J | Cross Arm | Tier 2 | Distribution | 2022-09-20 | N/A | N/A | N/A
P175184 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P175186 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P175188 | Pole | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P175198J | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P175199 | Cross Arm | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P175296J | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P175296J | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P175301J | Pole | Tier 2 | Distribution | 2022-08-19 | N/A | N/A | N/A
P175302 | Pole | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P175384 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P175399 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P17540 | Other | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P175417 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P17550 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P175525 | Cross Arm | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P175537 | Cross Arm | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P175537 | Insulator and Bushing | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P17561 | Pole | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P176022 | Cross Arm | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P176073 | Cross Arm | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P176074 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P176399 | Other | Tier 3 | Distribution | 2020-03-13 | N/A | N/A | N/A
P176417 | Other | Tier 3 | Distribution | 2020-03-13 | N/A | N/A | N/A
P176722 | Pole | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P177032 | Other | Tier 3 | Distribution | 2020-03-06 | N/A | N/A | N/A
P177248 | Insulator and Bushing | Tier 2 | Distribution | 2021-11-11 | N/A | N/A | N/A
P177248 | Other | Tier 2 | Distribution | 2021-11-11 | N/A | N/A | N/A
P177248 | Pole | Tier 2 | Distribution | 2021-11-11 | N/A | N/A | N/A
P177251 | Cross Arm | Tier 2 | Distribution | 2021-11-11 | N/A | N/A | N/A
P177251 | Insulator and Bushing | Tier 2 | Distribution | 2021-11-11 | N/A | N/A | N/A
P177251 | Other | Tier 2 | Distribution | 2021-11-11 | N/A | N/A | N/A
P177251 | Other | Tier 2 | Distribution | 2021-11-11 | N/A | N/A | N/A
P177251 | Pole | Tier 2 | Distribution | 2021-11-11 | N/A | N/A | N/A
P177252 | Pole | Tier 2 | Distribution | 2021-11-11 | N/A | N/A | N/A
P177253 | Cross Arm | Tier 2 | Distribution | 2021-11-11 | N/A | N/A | N/A
P177253 | Cross Arm | Tier 2 | Distribution | 2021-11-11 | N/A | N/A | N/A
P177253 | Insulator and Bushing | Tier 2 | Distribution | 2021-11-11 | N/A | N/A | N/A
P177340 | Conductor | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P177804 | Other | Tier 3 | Distribution | 2021-04-21 | N/A | N/A | N/A
P177857 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P177881 | Other | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P177881 | Other | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P177881 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P177886J | Pole | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P177897 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P177897 | Pole | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P177953 | Cross Arm | Tier 2 | Distribution | 2022-10-31 | N/A | N/A | N/A
P177956 | Pole | Tier 2 | Distribution | 2022-10-31 | N/A | N/A | N/A
P177960 | Pole | Tier 2 | Distribution | 2022-10-31 | N/A | N/A | N/A
P177961 | Anchor/Guy | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P178077 | Pole | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P178320 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P178521 | Cross Arm | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P178522 | Cross Arm | Tier 2 | Distribution | 2022-12-28 | N/A | N/A | N/A
P178595 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P178647 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P178650 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P178721 | Pole | Tier 2 | Distribution | 2022-12-12 | N/A | N/A | N/A
P178722 | Cross Arm | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P178866 | Pole | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P179275 | Pole | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P179846 | Pole | Tier 3 | Distribution | 2022-11-17 | N/A | N/A | N/A
P179870 | Other | Tier 2 | Distribution | 2022-03-23 | N/A | N/A | N/A
P179876 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P180761 | Other | Tier 2 | Distribution | 2022-12-14 | N/A | N/A | N/A
P18083 | Transformer | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P182005 | Insulator and Bushing | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P182005 | Transformer | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P18240 | Cross Arm | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P18241J | Other | Tier 2 | Distribution | 2022-12-14 | N/A | N/A | N/A
P18313 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P183607 | Insulator and Bushing | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P183607 | Pole | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P183767 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P18389 | Other | Tier 2 | Distribution | 2022-11-17 | N/A | N/A | N/A
P18401 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P18402 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P18404 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P18411 | Pole | Tier 2 | Distribution | 2022-03-04 | N/A | N/A | N/A
P18437 | Cross Arm | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P18437 | Other | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P18442 | Cross Arm | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P18446 | Conductor | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P18446 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P184755 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P18504 | Other | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P185622 | Anchor/Guy | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P18614 | Cross Arm | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P18642 | Cross Arm | Tier 2 | Distribution | 2022-05-26 | N/A | N/A | N/A
P18688 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P18695 | Anchor/Guy | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P18696 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P18734 | Cross Arm | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P18734 | Other | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P18764 | Insulator and Bushing | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P188638 | Cross Arm | Tier 2 | Distribution | 2022-11-21 | N/A | N/A | N/A
P189717 | Pole | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P189783 | Pole | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P190007 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P190193 | Transformer | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P19038 | Cross Arm | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P19047 | Cross Arm | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P19058 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P19065J | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P19069 | Cross Arm | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P190788 | Pole | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P190927 | Pole | Tier 2 | Distribution | 2022-03-28 | N/A | N/A | N/A
P190939 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P190977 | Pole | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P190981 | Pole | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P190982 | Pole | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P191121 | Cross Arm | Tier 2 | Distribution | 2022-11-21 | N/A | N/A | N/A
P19122 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P191227 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P19126 | Cross Arm | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P19126 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P19128 | Cross Arm | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P191512 | Pole | Tier 2 | Distribution | 2022-12-21 | N/A | N/A | N/A
P191636 | Anchor/Guy | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P191636 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P192111 | Other | Tier 2 | Distribution | 2021-10-25 | N/A | N/A | N/A
P192111 | Pole | Tier 2 | Distribution | 2021-10-25 | N/A | N/A | N/A
P192115 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P192637 | Cross Arm | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P192637 | Insulator and Bushing | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P193031 | Pole | Tier 2 | Distribution | 2022-12-02 | N/A | N/A | N/A
P193069 | Pole | Tier 2 | Distribution | 2022-03-14 | N/A | N/A | N/A
P193139 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P193245 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P193394 | Pole | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P19362J | Cross Arm | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P19362J | Other | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P193641 | Pole | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P19388J | Cross Arm | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P19389J | Pole | Tier 2 | Distribution | 2022-03-13 | N/A | N/A | N/A
P19390 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P19392 | Pole | Tier 2 | Distribution | 2022-09-14 | N/A | N/A | N/A
P19394 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P194022 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P194136 | Anchor/Guy | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P194136 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P194136 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P194228 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P195336 | Cross Arm | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P195368 | Pole | Tier 2 | Distribution | 2022-07-28 | N/A | N/A | N/A
P195384 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P195766 | Insulator and Bushing | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P195766 | Other | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P195766 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P196183 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P196251 | Pole | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P19642 | Cross Arm | Tier 2 | Distribution | 2021-08-16 | N/A | N/A | N/A
P196531 | Other | Tier 2 | Distribution | 2021-08-17 | N/A | N/A | N/A
P196531 | Pole | Tier 2 | Distribution | 2021-08-17 | N/A | N/A | N/A
P196545 | Pole | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P196546 | Pole | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P196549 | Pole | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P19655 | Cross Arm | Tier 2 | Distribution | 2022-06-29 | N/A | N/A | N/A
P196551 | Other | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P19665 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P19665 | Other | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P19665 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P19683 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P197376 | Anchor/Guy | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P197381 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P197476 | Anchor/Guy | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P197498J | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P197638 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P197863 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P19802J | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P19802J | Insulator and Bushing | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P19802J | Other | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P19807 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P198176 | Pole | Tier 2 | Distribution | 2022-12-05 | N/A | N/A | N/A
P198347 | Pole | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P198453 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P19854 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P19855 | Cross Arm | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P198633 | Cross Arm | Tier 3 | Distribution | 2022-04-25 | N/A | N/A | N/A
P198704 | Insulator and Bushing | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P198704 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P198803 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P19881 | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P19883 | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P198865 | Pole | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P198919 | Pole | Tier 3 | Distribution | 2022-12-02 | N/A | N/A | N/A
P198942 | Cross Arm | Tier 3 | Distribution | 2022-11-17 | N/A | N/A | N/A
P198942 | Pole | Tier 3 | Distribution | 2022-11-17 | N/A | N/A | N/A
P198943 | Pole | Tier 3 | Distribution | 2020-07-16 | N/A | N/A | N/A
P199071 | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P199095 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P199096 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P199107 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P199111 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P19923J | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P19923J | Other | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P19924J | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P199377 | Pole | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P199399 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P199642 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P199689 | Anchor/Guy | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P199689 | Pole | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P199815 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P199831 | Anchor/Guy | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P199834 | Pole | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P199888 | Pole | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P199945 | Pole | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P200143 | Pole | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P200150 | Pole | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P200225 | Pole | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P200246 | Pole | Tier 3 | Distribution | 2022-11-17 | N/A | N/A | N/A
P200284 | Pole | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P200317 | Pole | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P200319 | Pole | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P200459 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P200460 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P200502 | Pole | Tier 3 | Distribution | 2022-04-25 | N/A | N/A | N/A
P200533 | Pole | Tier 3 | Distribution | 2022-12-12 | N/A | N/A | N/A
P200982 | Pole | Tier 2 | Distribution | 2022-03-30 | N/A | N/A | N/A
P201372 | Pole | Tier 2 | Distribution | 2021-11-02 | N/A | N/A | N/A
P201384 | Other | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P201384 | Pole | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P201439 | Pole | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P201740 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P202052 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P202502 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P202593 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P202593 | Pole | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P202789 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P202813 | Pole | Tier 2 | Distribution | 2022-08-03 | N/A | N/A | N/A
P202815 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P203002 | Pole | Tier 2 | Distribution | 2022-05-09 | N/A | N/A | N/A
P203125 | Insulator and Bushing | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P203125 | Pole | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P203127 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P203597 | Pole | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P203850 | Pole | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P203851 | Other | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P203851 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P203885 | Other | Tier 2 | Distribution | 2022-11-07 | N/A | N/A | N/A
P204384 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P204729 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P205196 | Pole | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P205199 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P205331 | Pole | Tier 2 | Distribution | 2022-12-02 | N/A | N/A | N/A
P205387 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P205443 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P205483 | Other | Tier 2 | Distribution | 2022-12-14 | N/A | N/A | N/A
P205491 | Pole | Tier 2 | Distribution | 2022-11-16 | N/A | N/A | N/A
P205521 | Insulator and Bushing | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P205521 | Pole | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P205525 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P205547 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P206051 | Anchor/Guy | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P206051 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P206096 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P206096 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P206147 | Pole | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P206712 | Pole | Tier 2 | Distribution | 2022-03-30 | N/A | N/A | N/A
P206758 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P206809 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P206918 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P206918 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P206967 | Insulator and Bushing | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P206967 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P206967 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P207282 | Other | Tier 2 | Distribution | 2021-08-19 | N/A | N/A | N/A
P207282 | Pole | Tier 2 | Distribution | 2021-08-19 | N/A | N/A | N/A
P207292 | Pole | Tier 2 | Distribution | 2021-11-02 | N/A | N/A | N/A
P207298 | Pole | Tier 2 | Distribution | 2022-08-17 | N/A | N/A | N/A
P207665 | Anchor/Guy | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P208030 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P208524 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P209041 | Anchor/Guy | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P209042 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P209311 | Cross Arm | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P209592 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P210062 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P210121 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P210126 | Cross Arm | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P210144 | Pole | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P210148 | Pole | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P210149 | Pole | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P210151 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P210153 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P210154 | Cross Arm | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P210161 | Cross Arm | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P210161 | Pole | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P210165 | Pole | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P210167 | Cross Arm | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P210167 | Insulator and Bushing | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P210167 | Pole | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P210169 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P210214 | Cross Arm | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P210214 | Pole | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P210232 | Cross Arm | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P210234 | Cross Arm | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P210241 | Cross Arm | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P210241 | Cross Arm | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P210246 | Cross Arm | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P210248 | Cross Arm | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P210249 | Cross Arm | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P210257 | Cross Arm | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P210257 | Other | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P210258 | Pole | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P210259 | Pole | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P210277 | Cross Arm | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P210299 | Pole | Tier 2 | Distribution | 2022-05-18 | N/A | N/A | N/A
P210303 | Pole | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P210344J | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P210344J | Other | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P210366 | Pole | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P210406 | Pole | Tier 2 | Distribution | 2022-05-26 | N/A | N/A | N/A
P210420 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P210426 | Cross Arm | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P210433 | Pole | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P210445 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P210456 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P210457 | Cross Arm | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P210461 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P210488 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P210497 | Conductor | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P210497 | Pole | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P210547J | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P210548J | Cross Arm | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P210560 | Cross Arm | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P210560 | Pole | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P210561 | Pole | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P210715 | Pole | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P210771 | Cross Arm | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P210776 | Pole | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P210777 | Pole | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P210790 | Insulator and Bushing | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P210796 | Anchor/Guy | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P211042 | Cross Arm | Tier 2 | Distribution | 2021-11-02 | N/A | N/A | N/A
P211047 | Pole | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P211072 | Cross Arm | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P211073 | Cross Arm | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P211074 | Pole | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P211076 | Pole | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P211153 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P211211 | Anchor/Guy | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P211211 | Other | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P211211 | Pole | Tier 2 | Distribution | 2022-12-22 | N/A | N/A | N/A
P211272 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P211289 | Cross Arm | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P211336 | Cross Arm | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P211344 | Pole | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P211396 | Cross Arm | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P211454 | Anchor/Guy | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P211484 | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P211522 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P211547J | Pole | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P211561 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P211566 | Cross Arm | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P211567 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P211646 | Cross Arm | Tier 2 | Distribution | 2022-06-27 | N/A | N/A | N/A
P211730 | Pole | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P211748 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P211749 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P211749 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P211750 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P211750 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P211806 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P211817 | Cross Arm | Tier 2 | Distribution | 2022-04-22 | N/A | N/A | N/A
P211868 | Cross Arm | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P211906 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P211948 | Other | Tier 3 | Distribution | 2020-06-04 | N/A | N/A | N/A
P211974 | Pole | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P212011 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P212014 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P212073 | Cross Arm | Tier 2 | Distribution | 2022-03-25 | N/A | N/A | N/A
P212088 | Cross Arm | Tier 2 | Distribution | 2022-03-03 | N/A | N/A | N/A
P212088 | Other | Tier 2 | Distribution | 2022-03-03 | N/A | N/A | N/A
P212088 | Pole | Tier 2 | Distribution | 2022-03-03 | N/A | N/A | N/A
P212124 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P212317 | Other | Tier 3 | Distribution | 2020-04-06 | N/A | N/A | N/A
P212353 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P212398 | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P212398 | Other | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P212476 | Transformer | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P212480 | Cross Arm | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P212480 | Insulator and Bushing | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P212494 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P212497 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P212498 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P212539 | Anchor/Guy | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P212539 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P212546 | Cross Arm | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P212549 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P212651 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P212691 | Cross Arm | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P212693 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P212770 | Pole | Tier 2 | Distribution | 2022-03-09 | N/A | N/A | N/A
P212771 | Pole | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P212798 | Other | Tier 2 | Distribution | 2022-12-08 | N/A | N/A | N/A
P212802 | Pole | Tier 2 | Distribution | 2022-11-30 | N/A | N/A | N/A
P212803 | Pole | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P212806 | Cross Arm | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P212827 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P21284 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P21284 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P212940 | Cross Arm | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P212941 | Other | Tier 2 | Distribution | 2022-12-09 | N/A | N/A | N/A
P213041 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P213046 | Cross Arm | Tier 2 | Distribution | 2022-05-26 | N/A | N/A | N/A
P213047 | Pole | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P213049 | Transformer | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P213052 | Other | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P213052 | Pole | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P213061 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P213118 | Pole | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P213119 | Other | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P213119 | Pole | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P213126 | Pole | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P213142 | Pole | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P213296 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P213398 | Pole | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P213399 | Other | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P213399 | Pole | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P213445 | Other | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P213445 | Pole | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P213454 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P213461 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P213531 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P213531 | Other | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P213531 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P213580 | Pole | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P213781 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P213792 | Cross Arm | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P213799 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P213850 | Cross Arm | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P213852 | Pole | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P213933 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P213935 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P214000J | Other | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P214009 | Insulator and Bushing | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P214009 | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P214012 | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P214013 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P214015 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P214104 | Cross Arm | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P214104 | Insulator and Bushing | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P214104 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P214118 | Anchor/Guy | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P214118 | Insulator and Bushing | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P214135 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P214250 | Cross Arm | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P214282 | Cross Arm | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P214576 | Insulator and Bushing | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P214576 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P214634 | Anchor/Guy | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P214634 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P214667 | Cross Arm | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P214736 | Pole | Tier 2 | Distribution | 2021-11-30 | N/A | N/A | N/A
P214757 | Cross Arm | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P214763 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P214764 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P214764 | Pole | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P214765 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P214767 | Pole | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P214943 | Cross Arm | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P214952 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P214952 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P214954 | Pole | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P215041 | Other | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P215233 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P215245 | Anchor/Guy | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P215262 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P215262 | Insulator and Bushing | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P215383 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P215392 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P215475 | Anchor/Guy | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P215516 | Cross Arm | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P215520 | Cross Arm | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P215526 | Insulator and Bushing | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P215526 | Other | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P215526 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P215532 | Cross Arm | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P2155707J | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P215647 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P215647 | Insulator and Bushing | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P215648 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P215648 | Insulator and Bushing | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P215649 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P215650 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P215705 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P215721 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P215807 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P215879J | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P215879J | Other | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P215948 | Other | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P216073 | Pole | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P216144 | Pole | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P216145 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P216152 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P216153 | Other | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P216156 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P216180 | Cross Arm | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P216181 | Cross Arm | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P216183 | Anchor/Guy | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P216183 | Pole | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P216205 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P216205 | Insulator and Bushing | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P216213 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P216269 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P216286 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P216391 | Pole | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P216400 | Cross Arm | Tier 2 | Distribution | 2022-04-22 | N/A | N/A | N/A
P216400 | Transformer | Tier 2 | Distribution | 2022-04-22 | N/A | N/A | N/A
P216427J | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P216620 | Cross Arm | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P216677 | Insulator and Bushing | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P216692 | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P216698 | Cross Arm | Tier 2 | Distribution | 2021-11-02 | N/A | N/A | N/A
P216698 | Insulator and Bushing | Tier 2 | Distribution | 2021-11-02 | N/A | N/A | N/A
P216712 | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P216760 | Cross Arm | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P216761 | Cross Arm | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P216773 | Cross Arm | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P216777 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P216777 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P216777 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P216834 | Cross Arm | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P216834 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P216836 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P216841 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P216884 | Insulator and Bushing | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P216884 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P216925 | Anchor/Guy | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P217016 | Insulator and Bushing | Tier 2 | Distribution | 2021-11-02 | N/A | N/A | N/A
P217095 | Other | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P217117 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P217117 | Other | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P217117 | Pole | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P217121 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P217122 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P217139 | Conductor | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P217139 | Other | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P217139 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P217140 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P217218 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P217244 | Cross Arm | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P217244 | Pole | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P217245 | Cross Arm | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P217258 | Cross Arm | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P217259 | Other | Tier 2 | Distribution | 2022-10-21 | N/A | N/A | N/A
P217304 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P217319 | Cross Arm | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P217319 | Other | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P217319 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P217320 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P217350 | Pole | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P217400 | Cross Arm | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P217400 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P217413 | Other | Tier 2 | Distribution | 2022-12-14 | N/A | N/A | N/A
P217432 | Other | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P217433 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P217454 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P217513 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P217554 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P217594 | Cross Arm | Tier 2 | Distribution | 2022-03-04 | N/A | N/A | N/A
P217595 | Cross Arm | Tier 2 | Distribution | 2022-03-04 | N/A | N/A | N/A
P217615 | Pole | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P217669 | Transformer | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P217711 | Pole | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P217713 | Insulator and Bushing | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P217728 | Pole | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P217736 | Cross Arm | Tier 2 | Distribution | 2022-03-25 | N/A | N/A | N/A
P217757 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P217764 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P217778 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P217782 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P217783 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P217788 | Cross Arm | Tier 2 | Distribution | 2022-03-29 | N/A | N/A | N/A
P217793 | Pole | Tier 2 | Distribution | 2022-04-22 | N/A | N/A | N/A
P217796 | Pole | Tier 2 | Distribution | 2022-04-22 | N/A | N/A | N/A
P217820 | Cross Arm | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P217851 | Cross Arm | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P21786 | Switch | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P217909 | Other | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P217909 | Pole | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P217937 | Cross Arm | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P21806 | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P218061 | Cross Arm | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P218083 | Anchor/Guy | Tier 2 | Distribution | 2021-11-30 | N/A | N/A | N/A
P218186 | Cross Arm | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P218187 | Insulator and Bushing | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P218242 | Pole | Tier 2 | Distribution | 2022-12-08 | N/A | N/A | N/A
P218262 | Pole | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P218263 | Pole | Tier 2 | Distribution | 2022-04-07 | N/A | N/A | N/A
P218266 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P218267 | Pole | Tier 2 | Distribution | 2022-10-14 | N/A | N/A | N/A
P218353 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P218442 | Other | Tier 3 | Distribution | 2022-11-08 | N/A | N/A | N/A
P218445 | Other | Tier 3 | Distribution | 2022-11-08 | N/A | N/A | N/A
P218461 | Pole | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P218515 | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P218522 | Other | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P218532 | Cross Arm | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P218532 | Pole | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P218578 | Cross Arm | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P218684 | Cross Arm | Tier 2 | Distribution | 2021-09-08 | N/A | N/A | N/A
P218689 | Pole | Tier 2 | Distribution | 2021-09-08 | N/A | N/A | N/A
P218736 | Other | Tier 2 | Distribution | 2022-10-21 | N/A | N/A | N/A
P218848J | Cross Arm | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P218848J | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P218879 | Cross Arm | Tier 2 | Distribution | 2021-10-25 | N/A | N/A | N/A
P218879 | Pole | Tier 2 | Distribution | 2021-10-25 | N/A | N/A | N/A
P219014 | Insulator and Bushing | Tier 3 | Distribution | 2022-12-02 | N/A | N/A | N/A
P219014 | Other | Tier 3 | Distribution | 2022-12-02 | N/A | N/A | N/A
P219028 | Cross Arm | Tier 3 | Distribution | 2022-11-17 | N/A | N/A | N/A
P219035 | Cross Arm | Tier 3 | Distribution | 2022-11-17 | N/A | N/A | N/A
P219035 | Other | Tier 3 | Distribution | 2022-11-17 | N/A | N/A | N/A
P219035 | Transformer | Tier 3 | Distribution | 2022-11-17 | N/A | N/A | N/A
P219037 | Pole | Tier 3 | Distribution | 2022-11-17 | N/A | N/A | N/A
P219043 | Other | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P219045 | Cross Arm | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P219050 | Other | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P219056 | Cross Arm | Tier 3 | Distribution | 2022-12-12 | N/A | N/A | N/A
P219056 | Other | Tier 3 | Distribution | 2022-12-12 | N/A | N/A | N/A
P219056 | Pole | Tier 3 | Distribution | 2022-12-12 | N/A | N/A | N/A
P219062 | Other | Tier 3 | Distribution | 2022-11-08 | N/A | N/A | N/A
P219064 | Pole | Tier 3 | Distribution | 2022-11-08 | N/A | N/A | N/A
P219074 | Cross Arm | Tier 3 | Distribution | 2022-11-08 | N/A | N/A | N/A
P219452 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P219453 | Fuse | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P219485 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P219492 | Cross Arm | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P219611 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P219637 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P219643 | Cross Arm | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P219644 | Pole | Tier 2 | Distribution | 2022-03-09 | N/A | N/A | N/A
P219652 | Other | Tier 2 | Distribution | 2022-03-31 | N/A | N/A | N/A
P219683 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P219686 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P219964 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P219974 | Pole | Tier 2 | Distribution | 2022-05-26 | N/A | N/A | N/A
P220434 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P220530 | Other | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P220600 | Conductor | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P220690 | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P220951 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P220951 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P220984 | Transformer | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P221300 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P221407 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P221407 | Other | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P22159 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P221603 | Pole | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P221835 | Pole | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P221988 | Anchor/Guy | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P222485 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P222485 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P222486 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P222486 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P223327 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P224180 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P224189 | Anchor/Guy | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P224189 | Other | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P224209 | Anchor/Guy | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P224225 | Anchor/Guy | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P224242 | Pole | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P224292 | Pole | Tier 2 | Distribution | 2022-11-09 | N/A | N/A | N/A
P224330 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P224378 | Pole | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P224423 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P224437 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P224884 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P225174 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P225264 | Cross Arm | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P225405 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P225408 | Anchor/Guy | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P225928 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P225930 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P225932 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P226136 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P226675 | Other | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P226675 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P226793 | Conductor | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P226866 | Pole | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P227443 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P227453 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P227475 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P227481 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P227615 | Other | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P227663 | Cross Arm | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P227663 | Other | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P227979 | Pole | Tier 2 | Distribution | 2021-11-30 | N/A | N/A | N/A
P228082 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P228169 | Pole | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P228274 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P228276 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P228287 | Pole | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P228859 | Insulator and Bushing | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P228859 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P228875 | Insulator and Bushing | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P228885 | Other | Tier 2 | Distribution | 2021-10-25 | N/A | N/A | N/A
P228888 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P228894 | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P228894 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P228899 | Pole | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P228909 | Pole | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P228910 | Cross Arm | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P228935 | Pole | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P228952 | Insulator and Bushing | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P228959 | Pole | Tier 2 | Distribution | 2022-07-25 | N/A | N/A | N/A
P228960 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P229614 | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P230233 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P230234 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P230241 | Pole | Tier 2 | Distribution | 2021-11-02 | N/A | N/A | N/A
P230255 | Cross Arm | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P230295 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P233472 | Cross Arm | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P233472 | Other | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P233474 | Other | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P233474 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P233481 | Pole | Tier 2 | Distribution | 2022-08-15 | N/A | N/A | N/A
P233517 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P233518 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P233617 | Cross Arm | Tier 2 | Distribution | 2022-03-15 | N/A | N/A | N/A
P233731 | Pole | Tier 2 | Distribution | 2022-03-02 | N/A | N/A | N/A
P233732 | Cross Arm | Tier 2 | Distribution | 2022-03-02 | N/A | N/A | N/A
P233759 | Cross Arm | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P233759 | Other | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P233816 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P233850 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P233910 | Cross Arm | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P233911 | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P235901 | Conductor | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P235941 | Pole | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P235995 | Transformer | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P236602 | Anchor/Guy | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P236667 | Cross Arm | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P237475 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P237476 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P237729 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P237856 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P237856 | Other | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P237969 | Insulator and Bushing | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P238029 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P238029 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P238758 | Pole | Tier 2 | Distribution | 2022-04-06 | N/A | N/A | N/A
P238759 | Pole | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P238774 | Insulator and Bushing | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P238774 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P238929 | Insulator and Bushing | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P238929 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P238975 | Pole | Tier 2 | Distribution | 2021-08-19 | N/A | N/A | N/A
P239111 | Cross Arm | Tier 2 | Distribution | 2021-08-19 | N/A | N/A | N/A
P239111 | Pole | Tier 2 | Distribution | 2021-08-19 | N/A | N/A | N/A
P239114 | Pole | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P239196 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P239218 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P239231 | Pole | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P239257 | Pole | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P239281 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P239422 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P239785 | Other | Tier 2 | Distribution | 2021-11-02 | N/A | N/A | N/A
P245093 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P245100 | Pole | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P245104 | Pole | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P245111 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P245116 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P245499 | Pole | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P245667 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P246187 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P246241 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P246298 | Anchor/Guy | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P246310 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P246317 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P246363 | Anchor/Guy | Tier 2 | Distribution | 2021-07-19 | N/A | N/A | N/A
P246712 | Pole | Tier 2 | Distribution | 2022-02-07 | N/A | N/A | N/A
P246778 | Pole | Tier 3 | Distribution | 2022-08-11 | N/A | N/A | N/A
P246836 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P246955 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P247141 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P247434 | Anchor/Guy | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P247605 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P247739 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P247743 | Anchor/Guy | Tier 2 | Distribution | 2022-02-10 | N/A | N/A | N/A
P247743 | Pole | Tier 2 | Distribution | 2022-02-10 | N/A | N/A | N/A
P248283 | Anchor/Guy | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P248581 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P249068 | Anchor/Guy | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P249068 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P24981 | Transformer | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P25068 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P25222 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P25224 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P25303 | Other | Tier 2 | Distribution | 2022-11-05 | N/A | N/A | N/A
P25315 | Other | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P25319 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P25323 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P25331 | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P25333 | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P25335 | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P253370 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P253649 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P253650 | Anchor/Guy | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P253754 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P253947 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P253947 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P253974 | Pole | Tier 2 | Distribution | 2021-12-14 | N/A | N/A | N/A
P254172 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P254174 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P254174 | Insulator and Bushing | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P254677 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P254897 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P254906 | Anchor/Guy | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P254906 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P255350 | Pole | Tier 2 | Distribution | 2022-03-05 | N/A | N/A | N/A
P25589 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P25687 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P257644 | Conductor | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P257644 | Pole | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P26011 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P26391 | Transformer | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P26441 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P26442 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P26690 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P270022 | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P270022 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P270547 | Cross Arm | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P270547 | Pole | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P27088 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P271013 | Pole | Tier 2 | Distribution | 2022-05-25 | N/A | N/A | N/A
P271392 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P271398 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P271400 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P271402 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P271410 | Cross Arm | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P271535 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P272266 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P272266 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P272267 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P272269 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P272270 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P272273 | Pole | Tier 2 | Distribution | 2022-10-18 | N/A | N/A | N/A
P272280 | Conductor | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P272314J | Pole | Tier 2 | Distribution | 2022-12-01 | N/A | N/A | N/A
P272316 | Cross Arm | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P272317 | Cross Arm | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P272317 | Other | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P272320 | Cross Arm | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P27302 | Cross Arm | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P273064 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P273229J | Transformer | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P273446 | Pole | Tier 3 | Distribution | 2022-11-17 | N/A | N/A | N/A
P273582 | Pole | Tier 3 | Distribution | 2022-04-25 | N/A | N/A | N/A
P273583 | Pole | Tier 3 | Distribution | 2022-08-12 | N/A | N/A | N/A
P273605 | Pole | Tier 3 | Distribution | 2022-11-28 | N/A | N/A | N/A
P273613 | Cross Arm | Tier 3 | Distribution | 2022-11-17 | N/A | N/A | N/A
P273622 | Cross Arm | Tier 3 | Distribution | 2022-12-07 | N/A | N/A | N/A
P273622 | Other | Tier 3 | Distribution | 2022-12-07 | N/A | N/A | N/A
P273623 | Pole | Tier 3 | Distribution | 2022-12-07 | N/A | N/A | N/A
P273625 | Cross Arm | Tier 3 | Distribution | 2022-12-07 | N/A | N/A | N/A
P273626 | Pole | Tier 3 | Distribution | 2022-12-07 | N/A | N/A | N/A
P273629 | Cross Arm | Tier 3 | Distribution | 2022-12-07 | N/A | N/A | N/A
P273631 | Cross Arm | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P273631 | Other | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P273634 | Cross Arm | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P273635 | Cross Arm | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P273637 | Cross Arm | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P273638 | Cross Arm | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P273638 | Pole | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P273649 | Pole | Tier 3 | Distribution | 2022-12-07 | N/A | N/A | N/A
P273654 | Pole | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P273655 | Pole | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P273658 | Other | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P273658 | Pole | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P273668 | Other | Tier 3 | Distribution | 2020-04-07 | N/A | N/A | N/A
P273802 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P273805 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P273808 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P273957 | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P273957 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P274146 | Cross Arm | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P274677 | Pole | Tier 2 | Distribution | 2021-11-02 | N/A | N/A | N/A
P274848 | Anchor/Guy | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P275033 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P275125 | Anchor/Guy | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P275340 | Other | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P275435 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P275529J | Cross Arm | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P275536 | Other | Tier 3 | Distribution | 2020-11-10 | N/A | N/A | N/A
P276090 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P276202 | Insulator and Bushing | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P276245 | Cross Arm | Tier 2 | Distribution | 2022-02-11 | N/A | N/A | N/A
P276283 | Cross Arm | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P276284 | Cross Arm | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P276315 | Other | Tier 3 | Distribution | 2020-06-15 | N/A | N/A | N/A
P276432 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P276490 | Other | Tier 3 | Distribution | 2020-04-22 | N/A | N/A | N/A
P276512 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P276525 | Other | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P276778J | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P276969 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P277069 | Pole | Tier 3 | Distribution | 2022-11-17 | N/A | N/A | N/A
P277300J | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P277587 | Pole | Tier 3 | Distribution | 2022-04-25 | N/A | N/A | N/A
P277751 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P277753 | Conductor | Tier 3 | Distribution | 2022-12-07 | N/A | N/A | N/A
P277753 | Cross Arm | Tier 3 | Distribution | 2022-12-07 | N/A | N/A | N/A
P277807 | Cross Arm | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P277808 | Cross Arm | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P278079 | Cross Arm | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P278079 | Pole | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P278166 | Cross Arm | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P278270 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P278339 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P278346 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P278346 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P278346 | Transformer | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P278526 | Cross Arm | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P278612 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P278871J | Cross Arm | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P27896 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P27902 | Insulator and Bushing | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P27912 | Transformer | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P27995 | Cross Arm | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P27996 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P280407 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P28105 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P28105 | Other | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P28214 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P28301 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P28314 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P283531 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P283531 | Insulator and Bushing | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P283531 | Other | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P283531 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P283531 | Transformer | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P28377 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P28417 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P28512 | Pole | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P293718 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P294291J | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P30163 | Transformer | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P30234 | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P30234 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P30234 | Transformer | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P30243 | Cross Arm | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P30244 | Pole | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P30307 | Pole | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P30444 | Anchor/Guy | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P30792 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P30815 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P30963 | Transformer | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P310027 | Other | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P310027 | Other | Tier 2 | Distribution | 2022-08-29 | N/A | N/A | N/A
P310029 | Pole | Tier 2 | Distribution | 2022-05-13 | N/A | N/A | N/A
P310030 | Pole | Tier 2 | Distribution | 2022-10-17 | N/A | N/A | N/A
P310066 | Pole | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P310171 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P310428 | Pole | Tier 2 | Distribution | 2022-07-26 | N/A | N/A | N/A
P310506J | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P310587 | Cross Arm | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P310587 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P310605 | Insulator and Bushing | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P310628 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P310628 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P310648 | Pole | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P310654 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P310710 | Anchor/Guy | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P310710 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P310750 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P310750 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P310751 | Other | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P310752 | Conductor | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P310752 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P310809 | Cross Arm | Tier 2 | Distribution | 2022-03-15 | N/A | N/A | N/A
P310810 | Cross Arm | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P310831 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P310831 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P310908 | Cross Arm | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P310926 | Other | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P310951 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P310970 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P311024 | Cross Arm | Tier 2 | Distribution | 2022-11-02 | N/A | N/A | N/A
P311025 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P311026 | Other | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P311027 | Other | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P311093 | Transformer | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P3111460 | Cross Arm | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P311153 | Other | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P311153 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P311154 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P311155 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P311161 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P311162 | Other | Tier 2 | Distribution | 2022-07-20 | N/A | N/A | N/A
P311163 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P31123J | Pole | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P311297 | Cross Arm | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P311297 | Insulator and Bushing | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P311360 | Cross Arm | Tier 2 | Distribution | 2021-09-08 | N/A | N/A | N/A
P311360 | Pole | Tier 2 | Distribution | 2021-09-08 | N/A | N/A | N/A
P311361 | Cross Arm | Tier 2 | Distribution | 2021-09-08 | N/A | N/A | N/A
P311374 | Other | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P311374 | Pole | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P311375 | Other | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P311375 | Pole | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P311384 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P311384 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P311436 | Pole | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P311447 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P311618 | Cross Arm | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P311619 | Cross Arm | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P311619 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P311620 | Pole | Tier 2 | Distribution | 2022-05-09 | N/A | N/A | N/A
P311621 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P311621 | Pole | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P311639 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P311643 | Anchor/Guy | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P311643 | Insulator and Bushing | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P311670 | Other | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P311670 | Pole | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P311689 | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P31169 | Cross Arm | Tier 2 | Distribution | 2022-06-29 | N/A | N/A | N/A
P31169 | Pole | Tier 2 | Distribution | 2022-06-29 | N/A | N/A | N/A
P31171 | Cross Arm | Tier 2 | Distribution | 2022-06-29 | N/A | N/A | N/A
P31174 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P31177 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P311811 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P311817 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P311818 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P311823 | Cross Arm | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P311823 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P311828 | Cross Arm | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P311931 | Other | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P311931 | Other | Tier 2 | Distribution | 2022-12-21 | N/A | N/A | N/A
P312057 | Cross Arm | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P312065 | Pole | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P312066 | Pole | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P312185 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P312334 | Other | Tier 2 | Distribution | 2021-10-25 | N/A | N/A | N/A
P312334 | Pole | Tier 2 | Distribution | 2021-10-25 | N/A | N/A | N/A
P312408 | Pole | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P312447 | Pole | Tier 2 | Distribution | 2022-05-26 | N/A | N/A | N/A
P312449 | Cross Arm | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P312449 | Other | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P312476 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P312569 | Pole | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P312587 | Insulator and Bushing | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P312587 | Transformer | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P312600 | Pole | Tier 2 | Distribution | 2022-12-02 | N/A | N/A | N/A
P312638 | Cross Arm | Tier 2 | Distribution | 2022-12-12 | N/A | N/A | N/A
P312757 | Other | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P312757 | Other | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P312757 | Pole | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P312758 | Other | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P312758 | Other | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P312770 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P312770 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P312912 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P312938 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P313123 | Cross Arm | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P313123 | Other | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P313146 | Pole | Tier 2 | Distribution | 2022-03-30 | N/A | N/A | N/A
P313147 | Pole | Tier 2 | Distribution | 2022-03-30 | N/A | N/A | N/A
P313179 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P313195 | Cross Arm | Tier 2 | Distribution | 2021-11-30 | N/A | N/A | N/A
P313200 | Cross Arm | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P313399 | Cross Arm | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P313399 | Pole | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P313564 | Cross Arm | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P313564 | Other | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P314002 | Pole | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P315770 | Pole | Tier 2 | Distribution | 2021-09-14 | N/A | N/A | N/A
P315779 | Other | Tier 2 | Distribution | 2021-09-14 | N/A | N/A | N/A
P316199 | Pole | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P316346 | Pole | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P316509 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P316603 | Cross Arm | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P316685J | Other | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P316685J | Other | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P316685J | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P316765 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P316783 | Cross Arm | Tier 2 | Distribution | 2021-09-14 | N/A | N/A | N/A
P316783 | Insulator and Bushing | Tier 2 | Distribution | 2021-09-14 | N/A | N/A | N/A
P316791 | Cross Arm | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P316792 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P316893 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P316940 | Cross Arm | Tier 2 | Distribution | 2022-08-30 | N/A | N/A | N/A
P316941 | Cross Arm | Tier 2 | Distribution | 2022-08-30 | N/A | N/A | N/A
P316952 | Pole | Tier 2 | Distribution | 2022-08-30 | N/A | N/A | N/A
P316953 | Pole | Tier 2 | Distribution | 2022-08-30 | N/A | N/A | N/A
P316969 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P317008 | Cross Arm | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P317146 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P317760 | Pole | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P317762 | Pole | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P317784 | Pole | Tier 2 | Distribution | 2021-11-12 | N/A | N/A | N/A
P317784 | Transformer | Tier 2 | Distribution | 2021-11-12 | N/A | N/A | N/A
P317786 | Pole | Tier 2 | Distribution | 2021-11-12 | N/A | N/A | N/A
P317787 | Cross Arm | Tier 2 | Distribution | 2021-11-12 | N/A | N/A | N/A
P318073 | Other | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P318073 | Other | Tier 2 | Distribution | 2022-10-21 | N/A | N/A | N/A
P318079 | Cross Arm | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P318087 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P31815 | Cross Arm | Tier 2 | Distribution | 2022-03-14 | N/A | N/A | N/A
P31815 | Pole | Tier 2 | Distribution | 2022-03-14 | N/A | N/A | N/A
P318243 | Cross Arm | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P318271 | Cross Arm | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P318271 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P318633 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P318656 | Other | Tier 2 | Distribution | 2022-09-08 | N/A | N/A | N/A
P318657 | Pole | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P318666 | Cross Arm | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P318666 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P318667 | Pole | Tier 2 | Distribution | 2022-12-08 | N/A | N/A | N/A
P318795 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P318805 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P318870 | Other | Tier 2 | Distribution | 2022-08-24 | N/A | N/A | N/A
P318871 | Pole | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P318914 | Pole | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P319010J | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P319010J | Transformer | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P319045 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P319047 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P319272 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P319273 | Cross Arm | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P319274 | Cross Arm | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P319283 | Transformer | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P319313 | Cross Arm | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P319417 | Pole | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P319443 | Cross Arm | Tier 2 | Distribution | 2021-11-02 | N/A | N/A | N/A
P319444 | Cross Arm | Tier 2 | Distribution | 2021-11-02 | N/A | N/A | N/A
P319467J | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P319473 | Pole | Tier 2 | Distribution | 2022-03-29 | N/A | N/A | N/A
P319520 | Cross Arm | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P319553 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P319610 | Pole | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P319623 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P319633 | Pole | Tier 2 | Distribution | 2022-06-30 | N/A | N/A | N/A
P319634 | Cross Arm | Tier 2 | Distribution | 2022-06-30 | N/A | N/A | N/A
P319648 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P319648 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P319698J | Cross Arm | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P319825 | Pole | Tier 2 | Distribution | 2022-04-28 | N/A | N/A | N/A
P319838J | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P320129 | Insulator and Bushing | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P320776 | Cross Arm | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P321073 | Pole | Tier 2 | Distribution | 2022-07-25 | N/A | N/A | N/A
P321080 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P321097 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P321700 | Other | Tier 2 | Distribution | 2021-11-02 | N/A | N/A | N/A
P321700 | Pole | Tier 2 | Distribution | 2021-11-02 | N/A | N/A | N/A
P32182 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P32210 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P32216 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P32268 | Cross Arm | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P32272 | Cross Arm | Tier 2 | Distribution | 2022-03-05 | N/A | N/A | N/A
P323110 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P323113 | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P323113 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P323114 | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P323114 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P323117 | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P323123 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P32315 | Cross Arm | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P32315 | Other | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P32315 | Pole | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P323641 | Other | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P324144 | Other | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P324293 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P32452 | Pole | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P32501 | Cross Arm | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P32506 | Other | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P325271 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P325273 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P325273 | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P325281 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P325736 | Pole | Tier 2 | Distribution | 2022-06-13 | N/A | N/A | N/A
P32622 | Other | Tier 2 | Distribution | 2022-03-04 | N/A | N/A | N/A
P32785 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P32813 | Other | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P32813 | Pole | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P32842 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P32842 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P32912 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P32940 | Cross Arm | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P32941 | Cross Arm | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P32941 | Other | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P33611 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P33645 | Pole | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P33670 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P33763 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P33794 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P33813 | Pole | Tier 2 | Distribution | 2021-07-17 | N/A | N/A | N/A
P33814 | Pole | Tier 2 | Distribution | 2021-07-17 | N/A | N/A | N/A
P33869 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P34174 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P34872 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P34889 | Pole | Tier 2 | Distribution | 2022-10-03 | N/A | N/A | N/A
P34902 | Cross Arm | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P35036 | Insulator and Bushing | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P35982 | Other | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P36015J | Pole | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P36068 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P36068 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P36136 | Insulator and Bushing | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P36157 | Pole | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P36208 | Pole | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P36287 | Pole | Tier 2 | Distribution | 2022-04-22 | N/A | N/A | N/A
P36624 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P36625 | Cross Arm | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P36715 | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P36715 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P36719 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P36794 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P36794 | Pole | Tier 2 | Distribution | 2022-11-18 | N/A | N/A | N/A
P36982 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P370037 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P370044 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P370057 | Cross Arm | Tier 2 | Distribution | 2021-11-10 | N/A | N/A | N/A
P370060 | Other | Tier 2 | Distribution | 2021-11-10 | N/A | N/A | N/A
P370591 | Cross Arm | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P370599 | Anchor/Guy | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P370728 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P370728 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P370729 | Other | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P370729 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P370729 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P370804J | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P370805J | Other | Tier 2 | Distribution | 2022-12-28 | N/A | N/A | N/A
P370806J | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P370850 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P370853 | Pole | Tier 2 | Distribution | 2022-10-08 | N/A | N/A | N/A
P370855 | Cross Arm | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P370856 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P371076J | Other | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P371202 | Conductor | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P371202 | Conductor | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P371202 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P371204 | Cross Arm | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P371922 | Other | Tier 2 | Distribution | 2022-11-29 | N/A | N/A | N/A
P371925 | Cross Arm | Tier 2 | Distribution | 2021-12-14 | N/A | N/A | N/A
P372075J | Cross Arm | Tier 2 | Distribution | 2022-10-27 | N/A | N/A | N/A
P372329 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P372329 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P372493 | Cross Arm | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P372640 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P372812 | Other | Tier 2 | Distribution | 2022-08-09 | N/A | N/A | N/A
P372812 | Transformer | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P372813 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P372974 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P372975 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P373013 | Anchor/Guy | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P373106 | Pole | Tier 2 | Distribution | 2022-10-10 | N/A | N/A | N/A
P373107 | Transformer | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P373434 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P373713 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P373770 | Anchor/Guy | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P373770 | Cross Arm | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P373770 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P373950J | Cross Arm | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P374193 | Pole | Tier 2 | Distribution | 2021-11-02 | N/A | N/A | N/A
P374208 | Cross Arm | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P374319 | Pole | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P374930 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P375248 | Cross Arm | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P375269 | Other | Tier 3 | Distribution | 2020-03-10 | N/A | N/A | N/A
P375272J | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P375273J | Cross Arm | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P376052 | Pole | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P376053 | Pole | Tier 2 | Distribution | 2022-07-31 | N/A | N/A | N/A
P376054 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P376165 | Cross Arm | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P376255 | Other | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P376280J | Conductor | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P376280J | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P376325 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P376920J | Insulator and Bushing | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P377028 | Pole | Tier 2 | Distribution | 2022-08-30 | N/A | N/A | N/A
P377029 | Cross Arm | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P377030 | Cross Arm | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P377136 | Cross Arm | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P377349 | Other | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P377349 | Transformer | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P377415 | Other | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P377643 | Other | Tier 3 | Distribution | 2020-03-13 | N/A | N/A | N/A
P377753 | Other | Tier 2 | Distribution | 2022-08-09 | N/A | N/A | N/A
P377753 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P378281 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P378698 | Cross Arm | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P378702 | Cross Arm | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P378877 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P38798 | Pole | Tier 2 | Distribution | 2022-10-11 | N/A | N/A | N/A
P38799 | Other | Tier 2 | Distribution | 2022-07-28 | N/A | N/A | N/A
P38961 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P38992 | Pole | Tier 2 | Distribution | 2022-12-08 | N/A | N/A | N/A
P40754 | Other | Tier 2 | Distribution | 2021-07-19 | N/A | N/A | N/A
P40757 | Anchor/Guy | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P40759 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P40764 | Pole | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P40800 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P40800 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P410104J | Conductor | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P410104J | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P410105J | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P410119 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P410124 | Insulator and Bushing | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P410133 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P410135 | Anchor/Guy | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P410135 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P410135 | Other | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P410136 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P410334 | Pole | Tier 2 | Distribution | 2021-11-12 | N/A | N/A | N/A
P410391 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P410414 | Cross Arm | Tier 2 | Distribution | 2022-03-25 | N/A | N/A | N/A
P410415 | Pole | Tier 2 | Distribution | 2022-03-23 | N/A | N/A | N/A
P410439 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P41044 | Cross Arm | Tier 2 | Distribution | 2021-07-19 | N/A | N/A | N/A
P41052 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P41054 | Cross Arm | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P41054 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P410558 | Cross Arm | Tier 2 | Distribution | 2022-03-24 | N/A | N/A | N/A
P410588 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P410605 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P410606 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P410606 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P410617 | Cross Arm | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P410636 | Other | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P410636 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P410659 | Other | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P410744 | Other | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P410747 | Pole | Tier 2 | Distribution | 2021-11-23 | N/A | N/A | N/A
P410771 | Anchor/Guy | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P410772 | Conductor | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P410782 | Other | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P410782 | Other | Tier 2 | Distribution | 2022-08-04 | N/A | N/A | N/A
P410989 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P410990 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P411024 | Pole | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P411164 | Pole | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P41128 | Transformer | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P4112811 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P411420 | Cross Arm | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P411424 | Other | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P411426 | Pole | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P411447 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P411447 | Transformer | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P411475 | Pole | Tier 2 | Distribution | 2022-08-19 | N/A | N/A | N/A
P41159 | Anchor/Guy | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P411594 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P41163 | Pole | Tier 2 | Distribution | 2021-08-06 | N/A | N/A | N/A
P41165 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P411670 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P411719 | Cross Arm | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P41179 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P41179 | Transformer | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P41183 | Conductor | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P41183 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P411836 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P411836 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P411845 | Cross Arm | Tier 2 | Distribution | 2022-03-22 | N/A | N/A | N/A
P411860 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P411981 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P412012 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P412012 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P412020 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P412024 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P412028 | Pole | Tier 2 | Distribution | 2021-11-11 | N/A | N/A | N/A
P412029 | Pole | Tier 2 | Distribution | 2021-11-11 | N/A | N/A | N/A
P412030 | Cross Arm | Tier 2 | Distribution | 2021-11-11 | N/A | N/A | N/A
P412030 | Pole | Tier 2 | Distribution | 2021-11-11 | N/A | N/A | N/A
P412031 | Cross Arm | Tier 2 | Distribution | 2021-11-11 | N/A | N/A | N/A
P412032 | Pole | Tier 2 | Distribution | 2021-11-11 | N/A | N/A | N/A
P412035 | Pole | Tier 2 | Distribution | 2021-11-11 | N/A | N/A | N/A
P412044 | Pole | Tier 2 | Distribution | 2021-11-11 | N/A | N/A | N/A
P412047 | Pole | Tier 2 | Distribution | 2021-11-11 | N/A | N/A | N/A
P412164 | Cross Arm | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P412165 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P412217 | Pole | Tier 2 | Distribution | 2022-10-24 | N/A | N/A | N/A
P412361 | Cross Arm | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P412366 | Cross Arm | Tier 2 | Distribution | 2021-11-02 | N/A | N/A | N/A
P412368 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P412368 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P412373 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P412378J | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P412381 | Transformer | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P412699 | Cross Arm | Tier 2 | Distribution | 2021-08-19 | N/A | N/A | N/A
P412699 | Other | Tier 2 | Distribution | 2021-08-19 | N/A | N/A | N/A
P412941 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P412965 | Cross Arm | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P412969 | Transformer | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P412976 | Other | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P412989 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P41299 | Pole | Tier 2 | Distribution | 2021-07-19 | N/A | N/A | N/A
P412996 | Cross Arm | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P413032 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P413197 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P413453 | Conductor | Tier 2 | Distribution | 2021-11-02 | N/A | N/A | N/A
P413453 | Insulator and Bushing | Tier 2 | Distribution | 2021-11-02 | N/A | N/A | N/A
P413502 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P413502 | Insulator and Bushing | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P413505 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P413506 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P413507 | Insulator and Bushing | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P413507 | Other | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P413654 | Pole | Tier 2 | Distribution | 2022-11-08 | N/A | N/A | N/A
P413678 | Transformer | Tier 2 | Distribution | 2022-05-26 | N/A | N/A | N/A
P413724 | Insulator and Bushing | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P413724 | Pole | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P413725 | Other | Tier 2 | Distribution | 2022-12-05 | N/A | N/A | N/A
P413847 | Cross Arm | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P413850 | Pole | Tier 2 | Distribution | 2022-07-13 | N/A | N/A | N/A
P413896 | Pole | Tier 2 | Distribution | 2022-05-11 | N/A | N/A | N/A
P413925 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P413938 | Other | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P413981 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P41405 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P41406 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P41407 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P41412 | Cross Arm | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P41412 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P41413 | Cross Arm | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P41413 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P414137 | Other | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P41414 | Cross Arm | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P414156 | Cross Arm | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P41416 | Cross Arm | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P414198 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P41425 | Cross Arm | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P414326 | Cross Arm | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P414327 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P414381 | Transformer | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P414461 | Cross Arm | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P414461 | Pole | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P414462 | Cross Arm | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P414462 | Pole | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P414490 | Cross Arm | Tier 2 | Distribution | 2022-03-04 | N/A | N/A | N/A
P414490 | Insulator and Bushing | Tier 2 | Distribution | 2022-03-04 | N/A | N/A | N/A
P414495 | Cross Arm | Tier 2 | Distribution | 2022-03-22 | N/A | N/A | N/A
P414552 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P414552 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P41456 | Anchor/Guy | Tier 2 | Distribution | 2021-08-24 | N/A | N/A | N/A
P414563 | Cross Arm | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P414564 | Cross Arm | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P414564 | Pole | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P41458 | Anchor/Guy | Tier 2 | Distribution | 2021-08-24 | N/A | N/A | N/A
P41459 | Pole | Tier 2 | Distribution | 2021-08-24 | N/A | N/A | N/A
P41460 | Pole | Tier 2 | Distribution | 2021-08-24 | N/A | N/A | N/A
P41461 | Cross Arm | Tier 2 | Distribution | 2021-08-24 | N/A | N/A | N/A
P41462 | Pole | Tier 2 | Distribution | 2021-08-24 | N/A | N/A | N/A
P41463 | Pole | Tier 2 | Distribution | 2021-08-24 | N/A | N/A | N/A
P414635 | Pole | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P41464 | Pole | Tier 2 | Distribution | 2021-08-24 | N/A | N/A | N/A
P41466 | Pole | Tier 2 | Distribution | 2021-08-24 | N/A | N/A | N/A
P41467 | Pole | Tier 2 | Distribution | 2021-08-24 | N/A | N/A | N/A
P41469 | Cross Arm | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P41471 | Cross Arm | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P41478 | Cross Arm | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P41478 | Pole | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P41479 | Other | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P414839 | Pole | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P414841 | Cross Arm | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P41485 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P414858 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P41491 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P414971 | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P41498 | Other | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P41498 | Other | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P41498 | Pole | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P41502 | Cross Arm | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P41502 | Pole | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P41506 | Pole | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P41507 | Cross Arm | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P41507 | Other | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P41507 | Pole | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P41510 | Pole | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P415109 | Cross Arm | Tier 2 | Distribution | 2022-03-17 | N/A | N/A | N/A
P41511 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P415112 | Cross Arm | Tier 2 | Distribution | 2022-03-17 | N/A | N/A | N/A
P41512 | Pole | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P415177J | Pole | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P41518 | Cross Arm | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P41518 | Pole | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P41520 | Pole | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P41522 | Pole | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P415228 | Cross Arm | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P415228 | Other | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P41525 | Cross Arm | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P41526 | Cross Arm | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P41526 | Pole | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P41527 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P41528 | Cross Arm | Tier 2 | Distribution | 2022-01-24 | N/A | N/A | N/A
P41530 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P41531 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P41532 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P415334 | Cross Arm | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P41535 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P41539 | Cross Arm | Tier 2 | Distribution | 2021-08-20 | N/A | N/A | N/A
P415485 | Cross Arm | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P415486 | Cross Arm | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P41551 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P41552 | Other | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P41552 | Pole | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P415542 | Insulator and Bushing | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P415542 | Pole | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P41555 | Cross Arm | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P41555 | Other | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P41556 | Cross Arm | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P41557 | Cross Arm | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P415581 | Cross Arm | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P415582 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P415584 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P415585 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P41562 | Cross Arm | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P41562 | Pole | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P415672 | Cross Arm | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P415938 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P415939 | Pole | Tier 2 | Distribution | 2022-03-14 | N/A | N/A | N/A
P416002 | Pole | Tier 2 | Distribution | 2021-11-30 | N/A | N/A | N/A
P416246J | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P416272J | Cross Arm | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P416288J | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P416288J | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P416441 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P416442 | Other | Tier 2 | Distribution | 2022-07-18 | N/A | N/A | N/A
P416443 | Pole | Tier 2 | Distribution | 2022-05-12 | N/A | N/A | N/A
P416444 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P416447 | Pole | Tier 2 | Distribution | 2022-05-09 | N/A | N/A | N/A
P416448 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P416748 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P416815 | Pole | Tier 2 | Distribution | 2022-12-14 | N/A | N/A | N/A
P41683 | Pole | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P416984 | Cross Arm | Tier 2 | Distribution | 2022-08-30 | N/A | N/A | N/A
P417005 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P417005 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P417006 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P417062 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P417062 | Transformer | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P417177 | Cross Arm | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P417177 | Other | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P417220 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P417239 | Conductor | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P417239 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P417261 | Cross Arm | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P417261 | Pole | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P41728 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P41729 | Cross Arm | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P41729 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P417290 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P417290 | Insulator and Bushing | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P417317 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P41733 | Cross Arm | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P41733 | Pole | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P41735 | Anchor/Guy | Tier 2 | Distribution | 2021-08-24 | N/A | N/A | N/A
P41735 | Cross Arm | Tier 2 | Distribution | 2021-08-24 | N/A | N/A | N/A
P41735 | Pole | Tier 2 | Distribution | 2021-08-24 | N/A | N/A | N/A
P417448 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P417457 | Other | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P417457 | Pole | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P417459 | Cross Arm | Tier 2 | Distribution | 2022-08-30 | N/A | N/A | N/A
P417492 | Transformer | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P417548 | Pole | Tier 2 | Distribution | 2022-10-12 | N/A | N/A | N/A
P41755 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P41755 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P41756 | Pole | Tier 2 | Distribution | 2022-05-09 | N/A | N/A | N/A
P41759 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P41759 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P41759 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P41761 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P417716J | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P417723 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P417731 | Cross Arm | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P417766 | Insulator and Bushing | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P417782 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P417784 | Other | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P417784 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P417916 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P41807 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P418114 | Cross Arm | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P418157 | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P418201 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P418344 | Insulator and Bushing | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P418351 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P41838 | Pole | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P41839 | Cross Arm | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P41839 | Pole | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P418442 | Cross Arm | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P418443 | Pole | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P418488 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P418564 | Cross Arm | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P418564 | Insulator and Bushing | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P418565 | Pole | Tier 2 | Distribution | 2022-12-28 | N/A | N/A | N/A
P418566 | Cross Arm | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P418567 | Other | Tier 2 | Distribution | 2022-12-28 | N/A | N/A | N/A
P418703 | Insulator and Bushing | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P418706 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P418732 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P418845 | Other | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P418851 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P418872 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P418873 | Cross Arm | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P418873 | Pole | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P41899 | Cross Arm | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P419059 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P419116 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P419135 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P419160 | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P419160 | Insulator and Bushing | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P419191 | Cross Arm | Tier 2 | Distribution | 2022-08-19 | N/A | N/A | N/A
P419203 | Insulator and Bushing | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P419203 | Transformer | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P41925 | Pole | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P419297 | Other | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P419379 | Transformer | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P419380 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P419380 | Insulator and Bushing | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P419438 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P419549 | Cross Arm | Tier 2 | Distribution | 2022-06-27 | N/A | N/A | N/A
P419674 | Cross Arm | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P419711 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P419711 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P419977 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P42000 | Insulator and Bushing | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P42001 | Anchor/Guy | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P42001 | Pole | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P42110 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P42140 | Anchor/Guy | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P42168 | Transformer | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P42252 | Pole | Tier 2 | Distribution | 2022-10-19 | N/A | N/A | N/A
P42257 | Pole | Tier 2 | Distribution | 2022-09-14 | N/A | N/A | N/A
P42258 | Pole | Tier 2 | Distribution | 2022-08-24 | N/A | N/A | N/A
P42259 | Cross Arm | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P42260 | Cross Arm | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P42262 | Cross Arm | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P42262 | Pole | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P42268 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P42269 | Insulator and Bushing | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P42270 | Pole | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P42272 | Pole | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P42292 | Pole | Tier 2 | Distribution | 2022-04-01 | N/A | N/A | N/A
P42294 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P42296 | Pole | Tier 2 | Distribution | 2022-04-01 | N/A | N/A | N/A
P42297 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P42298 | Pole | Tier 2 | Distribution | 2022-04-01 | N/A | N/A | N/A
P42299 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P42300 | Pole | Tier 2 | Distribution | 2022-04-01 | N/A | N/A | N/A
P42301 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P42443J | Pole | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P42508 | Insulator and Bushing | Tier 3 | Distribution | 2020-05-06 | N/A | N/A | N/A
P42560 | Other | Tier 3 | Distribution | 2020-05-11 | N/A | N/A | N/A
P42622 | Transformer | Tier 3 | Distribution | 2020-05-06 | N/A | N/A | N/A
P42685 | Pole | Tier 3 | Distribution | 2020-05-06 | N/A | N/A | N/A
P42845 | Other | Tier 3 | Distribution | 2020-05-07 | N/A | N/A | N/A
P42894 | Cross Arm | Tier 3 | Distribution | 2020-05-21 | N/A | N/A | N/A
P42937 | Insulator and Bushing | Tier 3 | Distribution | 2020-05-21 | N/A | N/A | N/A
P42979 | Transformer | Tier 3 | Distribution | 2020-05-07 | N/A | N/A | N/A
P44309 | Conductor | Tier 2 | Distribution | 2021-08-24 | N/A | N/A | N/A
P44309 | Pole | Tier 2 | Distribution | 2021-08-24 | N/A | N/A | N/A
P44311 | Pole | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P44315 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P44315 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P44315 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P44617 | Cross Arm | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P44637 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P44647 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P44652 | Anchor/Guy | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P44652 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P44652 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P44652 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P44794 | Other | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P44794 | Pole | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P44800 | Pole | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P44816 | Other | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P44821 | Conductor | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P44821 | Cross Arm | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P44821 | Insulator and Bushing | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P44836 | Cross Arm | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P44843 | Pole | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P44845 | Cross Arm | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P44848 | Cross Arm | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P44849 | Pole | Tier 2 | Distribution | 2022-04-24 | N/A | N/A | N/A
P44859 | Pole | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P44870 | Pole | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P44874 | Cross Arm | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P44874 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P44879 | Anchor/Guy | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P44879 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P44884 | Cross Arm | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P44884 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P44884 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P44890 | Cross Arm | Tier 2 | Distribution | 2021-08-17 | N/A | N/A | N/A
P44891 | Other | Tier 2 | Distribution | 2021-08-17 | N/A | N/A | N/A
P44907 | Pole | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P44911 | Other | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P44911 | Pole | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P44914 | Insulator and Bushing | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P44914 | Other | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P44920 | Cross Arm | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P44922 | Cross Arm | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P44922 | Pole | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P44930 | Cross Arm | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P44938 | Pole | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P44942 | Pole | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P44946 | Cross Arm | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P44946 | Pole | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P44947 | Pole | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P44961 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P45004 | Cross Arm | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P45004 | Pole | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P45005 | Other | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P45006 | Pole | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P45008 | Pole | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P45011 | Pole | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P45012 | Pole | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P45014 | Other | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P45014 | Other | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P45014 | Other | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P45014 | Pole | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P45015 | Pole | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P45034 | Cross Arm | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P45034 | Other | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P45034 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P45035 | Cross Arm | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P45035 | Other | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P45035 | Pole | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P45077 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P45078 | Cross Arm | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P45080 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P45128 | Pole | Tier 2 | Distribution | 2021-08-20 | N/A | N/A | N/A
P45135 | Pole | Tier 2 | Distribution | 2021-08-20 | N/A | N/A | N/A
P45146 | Cross Arm | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P45146 | Pole | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P45153 | Cross Arm | Tier 2 | Distribution | 2021-08-20 | N/A | N/A | N/A
P45153 | Pole | Tier 2 | Distribution | 2021-08-20 | N/A | N/A | N/A
P45154 | Cross Arm | Tier 2 | Distribution | 2021-08-20 | N/A | N/A | N/A
P45174 | Other | Tier 2 | Distribution | 2021-07-17 | N/A | N/A | N/A
P45174 | Pole | Tier 2 | Distribution | 2021-07-17 | N/A | N/A | N/A
P45182 | Cross Arm | Tier 2 | Distribution | 2021-07-17 | N/A | N/A | N/A
P45189 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P45190 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P45210 | Other | Tier 3 | Distribution | 2020-03-17 | N/A | N/A | N/A
P45213 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P45223 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P45278 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P45333 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P45333 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P45334 | Cross Arm | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P45336 | Cross Arm | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P45336 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P45429 | Cross Arm | Tier 2 | Distribution | 2021-07-19 | N/A | N/A | N/A
P45460 | Cross Arm | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P45460 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P45523 | Pole | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P45524 | Pole | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P45535 | Pole | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P45542 | Pole | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P45580 | Other | Tier 3 | Distribution | 2020-05-07 | N/A | N/A | N/A
P45580 | Pole | Tier 3 | Distribution | 2020-05-07 | N/A | N/A | N/A
P45650 | Other | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P45653 | Pole | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P45665 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P45681 | Pole | Tier 2 | Distribution | 2021-08-24 | N/A | N/A | N/A
P45694 | Cross Arm | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P45726 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P45739 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P45740 | Other | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P45740 | Other | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P45740 | Pole | Tier 2 | Distribution | 2021-07-20 | N/A | N/A | N/A
P45749 | Pole | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P45798 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P45829 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P45837 | Pole | Tier 2 | Distribution | 2021-08-20 | N/A | N/A | N/A
P45842 | Pole | Tier 2 | Distribution | 2021-08-20 | N/A | N/A | N/A
P45850 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P45851 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P45852 | Other | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P45852 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P45866 | Cross Arm | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P45866 | Insulator and Bushing | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P45871 | Anchor/Guy | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P45871 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P45872 | Cross Arm | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P45872 | Insulator and Bushing | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P45872 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P45878 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P45880 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P45880 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P45881 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P45881 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P45883 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P45883 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P45885 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P45885 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P45885 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P45886 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P45886 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P45892 | Insulator and Bushing | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P45892 | Other | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P45892 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P45893 | Cross Arm | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P45893 | Insulator and Bushing | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P45893 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P45895 | Cross Arm | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P45895 | Other | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P45895 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P45896 | Cross Arm | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P45896 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P45897 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P45898 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P45901 | Cross Arm | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P45901 | Insulator and Bushing | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P45901 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P45904 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P45912 | Conductor | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P45912 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P45918 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P45919 | Pole | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P45931 | Pole | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P45933 | Other | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P45933 | Pole | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P45936 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P45936 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P45938J | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P45971 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P45972 | Conductor | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P45972 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P45973 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P45984 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P46002 | Pole | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P46003 | Other | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P46003 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P46027 | Pole | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P46028 | Pole | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P46047 | Cross Arm | Tier 2 | Distribution | 2021-08-20 | N/A | N/A | N/A
P46047 | Other | Tier 2 | Distribution | 2021-08-20 | N/A | N/A | N/A
P46048 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P46074 | Cross Arm | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46075 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46075 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46077 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46077 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46078 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46078 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46079 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46080 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46082 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46083 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46083 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46084 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46084 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46086 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46088 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46088 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46089 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46089 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46089 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46089 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46094 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P46099 | Pole | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P46129 | Other | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46129 | Pole | Tier 2 | Distribution | 2021-07-28 | N/A | N/A | N/A
P46132 | Cross Arm | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P46133 | Pole | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P46136 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P46137 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P46139 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P46141 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P46141 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P46142 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P46142 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P46143 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P46144 | Other | Tier 2 | Distribution | 2021-07-19 | N/A | N/A | N/A
P46176 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P46177 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P46178 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P46210 | Insulator and Bushing | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P46210 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P46213 | Cross Arm | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P46213 | Pole | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P46261J | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P46269 | Other | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P46269 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P46300 | Pole | Tier 2 | Distribution | 2021-07-22 | N/A | N/A | N/A
P46315 | Other | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P46315 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P46432 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P46438 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P46543 | Pole | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P46560 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P470081 | Insulator and Bushing | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P470081 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P470088 | Pole | Tier 2 | Distribution | 2021-11-20 | N/A | N/A | N/A
P470246 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P470566 | Pole | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P470601 | Transformer | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P470840 | Cross Arm | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P471201 | Cross Arm | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P471214 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P471214 | Insulator and Bushing | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P471215 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P471261 | Cross Arm | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P471261 | Other | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P471262 | Cross Arm | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P471264 | Cross Arm | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P471273 | Cross Arm | Tier 2 | Distribution | 2021-12-03 | N/A | N/A | N/A
P471274J | Pole | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P471599 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P471606 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P471899 | Cross Arm | Tier 3 | Distribution | 2019-11-20 | N/A | N/A | N/A
P471899 | Other | Tier 3 | Distribution | 2019-11-20 | N/A | N/A | N/A
P471899 | Pole | Tier 3 | Distribution | 2021-12-20 | N/A | N/A | N/A
P472572 | Insulator and Bushing | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P472574 | Cross Arm | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P472972 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P472983 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P473840 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P474084 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P474084 | Other | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P474095 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P474127 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P474171 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P474485 | Cross Arm | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P474502 | Cross Arm | Tier 2 | Distribution | 2021-12-14 | N/A | N/A | N/A
P474535 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P474936 | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P474988 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P474989 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P475568 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P475572 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P475994J | Cross Arm | Tier 2 | Distribution | 2021-11-02 | N/A | N/A | N/A
P476188 | Cross Arm | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P476469 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P476470 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P476707J | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P476711 | Pole | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P477031 | Cross Arm | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P477238 | Cross Arm | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P477238 | Other | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P477238 | Transformer | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P477971J | Cross Arm | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P478017 | Transformer | Tier 2 | Distribution | 2022-09-20 | N/A | N/A | N/A
P478022 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P478354 | Insulator and Bushing | Tier 2 | Distribution | 2022-12-12 | N/A | N/A | N/A
P478354 | Other | Tier 2 | Distribution | 2022-12-12 | N/A | N/A | N/A
P478371 | Insulator and Bushing | Tier 2 | Distribution | 2022-11-21 | N/A | N/A | N/A
P478373 | Insulator and Bushing | Tier 2 | Distribution | 2022-11-21 | N/A | N/A | N/A
P478373 | Other | Tier 2 | Distribution | 2022-11-21 | N/A | N/A | N/A
P478377 | Insulator and Bushing | Tier 2 | Distribution | 2022-11-21 | N/A | N/A | N/A
P478388 | Other | Tier 2 | Distribution | 2022-12-12 | N/A | N/A | N/A
P478390 | Other | Tier 2 | Distribution | 2022-12-12 | N/A | N/A | N/A
P510054 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P510054 | Transformer | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P510278 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P510310 | Other | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P510310 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P510319 | Cross Arm | Tier 2 | Distribution | 2021-10-25 | N/A | N/A | N/A
P510319 | Other | Tier 2 | Distribution | 2021-10-25 | N/A | N/A | N/A
P510387 | Transformer | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P510397 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P510562 | Insulator and Bushing | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P510562 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P510609 | Pole | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P510640 | Transformer | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P510695 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P510748 | Cross Arm | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P510748 | Other | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P510753 | Cross Arm | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P510901 | Cross Arm | Tier 2 | Distribution | 2022-03-25 | N/A | N/A | N/A
P510914 | Conductor | Tier 2 | Distribution | 2022-06-27 | N/A | N/A | N/A
P510934 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P511046 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P511046 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P511099 | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P511101 | Cross Arm | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P511122 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P511163 | Cross Arm | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P511281 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P511319 | Cross Arm | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P511324J | Pole | Tier 2 | Distribution | 2022-12-08 | N/A | N/A | N/A
P511327 | Anchor/Guy | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P511334 | Cross Arm | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P511335 | Cross Arm | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P511410J | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P511428 | Other | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P511474 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P511474 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P511476 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P511498 | Pole | Tier 2 | Distribution | 2022-11-05 | N/A | N/A | N/A
P511599 | Insulator and Bushing | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P511771 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P511838 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P511856 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P511862 | Cross Arm | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P511868 | Cross Arm | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P511872 | Other | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P511872 | Other | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P511897 | Fuse | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P511899 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P511957 | Cross Arm | Tier 2 | Distribution | 2022-03-22 | N/A | N/A | N/A
P511970 | Other | Tier 2 | Distribution | 2022-08-29 | N/A | N/A | N/A
P512003 | Other | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P512094 | Pole | Tier 2 | Distribution | 2022-12-14 | N/A | N/A | N/A
P512242 | Anchor/Guy | Tier 2 | Distribution | 2022-12-14 | N/A | N/A | N/A
P512297 | Anchor/Guy | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P512297 | Cross Arm | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P512300 | Cross Arm | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P512391 | Cross Arm | Tier 2 | Distribution | 2022-10-07 | N/A | N/A | N/A
P512420 | Pole | Tier 2 | Distribution | 2022-12-14 | N/A | N/A | N/A
P512472 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P512705 | Cross Arm | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P512756 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P512973 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P512974 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P512995 | Pole | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P512997 | Pole | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P513076 | Conductor | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P513076 | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P513079 | Cross Arm | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P513080 | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P513081 | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P513082 | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P513084 | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P513101 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P513106 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P513106 | Pole | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P513148 | Other | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P513148 | Pole | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P513155 | Pole | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P513187 | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P513187 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P513232 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P513232 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P513289 | Cross Arm | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P513405 | Pole | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P513415 | Insulator and Bushing | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P513454 | Cross Arm | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P513467 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P513573 | Other | Tier 2 | Distribution | 2021-09-15 | N/A | N/A | N/A
P513581 | Anchor/Guy | Tier 2 | Distribution | 2021-09-15 | N/A | N/A | N/A
P513581 | Other | Tier 2 | Distribution | 2021-09-15 | N/A | N/A | N/A
P513788 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P513872 | Cross Arm | Tier 2 | Distribution | 2022-03-05 | N/A | N/A | N/A
P513872 | Pole | Tier 2 | Distribution | 2022-03-05 | N/A | N/A | N/A
P513911 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P513918 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P513985 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P514022 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P514044 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P514144 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P514200 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P514274 | Cross Arm | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P514275 | Pole | Tier 2 | Distribution | 2022-09-23 | N/A | N/A | N/A
P514276 | Pole | Tier 2 | Distribution | 2022-03-07 | N/A | N/A | N/A
P514368 | Cross Arm | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P514368 | Other | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P514368 | Pole | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P514434 | Cross Arm | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P514435 | Cross Arm | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P514449 | Pole | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P514450 | Cross Arm | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P514450 | Pole | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P514459 | Conductor | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P514459 | Transformer | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P514463 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P514506 | Cross Arm | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P514535 | Pole | Tier 2 | Distribution | 2022-03-22 | N/A | N/A | N/A
P514696 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P514697 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P514697 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P514713 | Pole | Tier 2 | Distribution | 2021-11-30 | N/A | N/A | N/A
P514758 | Pole | Tier 2 | Distribution | 2022-08-11 | N/A | N/A | N/A
P514759 | Cross Arm | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P514760 | Other | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P514760 | Pole | Tier 2 | Distribution | 2022-08-05 | N/A | N/A | N/A
P514761 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P514787 | Transformer | Tier 2 | Distribution | 2021-11-30 | N/A | N/A | N/A
P514843 | Other | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P514903J | Pole | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P515037 | Cross Arm | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P515081 | Pole | Tier 2 | Distribution | 2022-05-11 | N/A | N/A | N/A
P515161 | Transformer | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P515212 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P515273 | Cross Arm | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P515319 | Pole | Tier 2 | Distribution | 2022-05-11 | N/A | N/A | N/A
P515359 | Other | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P515359 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P515364 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P515365 | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P515365 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P515366 | Other | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P515368 | Transformer | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P515371 | Insulator and Bushing | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P515371 | Pole | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P515372 | Cross Arm | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P515532 | Cross Arm | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P515532 | Other | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P515533 | Cross Arm | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P515595 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P515597 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P515604 | Anchor/Guy | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P515604 | Insulator and Bushing | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P515606 | Cross Arm | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P515628 | Other | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P515628 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P515862 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P515919J | Cross Arm | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P516044 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P516092 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P516117 | Cross Arm | Tier 2 | Distribution | 2022-08-30 | N/A | N/A | N/A
P516125 | Pole | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P516145 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P516145 | Insulator and Bushing | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P516145 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P516156 | Insulator and Bushing | Tier 2 | Distribution | 2022-03-14 | N/A | N/A | N/A
P516184 | Other | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P516184 | Transformer | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P516201 | Cross Arm | Tier 2 | Distribution | 2022-03-07 | N/A | N/A | N/A
P516205 | Pole | Tier 2 | Distribution | 2022-03-07 | N/A | N/A | N/A
P516303 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P516325 | Anchor/Guy | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P516325 | Pole | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P516377J | Pole | Tier 2 | Distribution | 2022-12-19 | N/A | N/A | N/A
P516378 | Insulator and Bushing | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P516378 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P516479 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P516522 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P516523 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P516523 | Other | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P516600 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P516602 | Cross Arm | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P516638 | Pole | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P516678 | Pole | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P516779 | Pole | Tier 2 | Distribution | 2022-03-03 | N/A | N/A | N/A
P516792 | Transformer | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P516828 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P516842 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P516887 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P516901 | Pole | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P516911 | Cross Arm | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P516911 | Other | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P516922 | Cross Arm | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P516925 | Cross Arm | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P516957 | Cross Arm | Tier 2 | Distribution | 2022-06-13 | N/A | N/A | N/A
P516958 | Cross Arm | Tier 2 | Distribution | 2022-06-13 | N/A | N/A | N/A
P516959 | Cross Arm | Tier 2 | Distribution | 2022-06-13 | N/A | N/A | N/A
P516961 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P516961 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P516962 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P517127 | Pole | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P517129 | Other | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P517129 | Pole | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P517183 | Pole | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P517302 | Other | Tier 2 | Distribution | 2022-11-15 | N/A | N/A | N/A
P517307 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P517448 | Pole | Tier 2 | Distribution | 2022-03-07 | N/A | N/A | N/A
P517453 | Pole | Tier 2 | Distribution | 2022-03-03 | N/A | N/A | N/A
P517768 | Cross Arm | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P517781 | Cross Arm | Tier 2 | Distribution | 2022-03-25 | N/A | N/A | N/A
P517782 | Pole | Tier 2 | Distribution | 2022-03-25 | N/A | N/A | N/A
P517797J | Pole | Tier 2 | Distribution | 2022-03-02 | N/A | N/A | N/A
P517803 | Other | Tier 2 | Distribution | 2022-03-02 | N/A | N/A | N/A
P517804 | Cross Arm | Tier 2 | Distribution | 2022-03-02 | N/A | N/A | N/A
P517962J | Pole | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P517981J | Pole | Tier 2 | Distribution | 2022-09-02 | N/A | N/A | N/A
P518012 | Pole | Tier 2 | Distribution | 2022-06-27 | N/A | N/A | N/A
P518023 | Pole | Tier 2 | Distribution | 2022-04-28 | N/A | N/A | N/A
P518024 | Other | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P518024 | Other | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P518024 | Pole | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P518158 | Conductor | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P518158 | Pole | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P518202 | Other | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P518202 | Pole | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P518210 | Pole | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P518211 | Cross Arm | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P518211 | Other | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P518212 | Transformer | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P518213 | Anchor/Guy | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P518213 | Pole | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P518258 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P518292 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P518299 | Cross Arm | Tier 2 | Distribution | 2022-03-22 | N/A | N/A | N/A
P518299 | Insulator and Bushing | Tier 2 | Distribution | 2022-03-22 | N/A | N/A | N/A
P518319 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P518339 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P518522 | Pole | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P518546 | Cross Arm | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P518575 | Pole | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P518625 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P518658 | Pole | Tier 2 | Distribution | 2022-03-07 | N/A | N/A | N/A
P518661 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P518670 | Transformer | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P518678 | Transformer | Tier 2 | Distribution | 2022-03-10 | N/A | N/A | N/A
P518691 | Cross Arm | Tier 2 | Distribution | 2022-05-09 | N/A | N/A | N/A
P518724 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P518725 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P518780 | Cross Arm | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P518781 | Cross Arm | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P518783 | Other | Tier 2 | Distribution | 2022-08-30 | N/A | N/A | N/A
P518783 | Pole | Tier 2 | Distribution | 2022-08-30 | N/A | N/A | N/A
P518785 | Cross Arm | Tier 2 | Distribution | 2022-08-30 | N/A | N/A | N/A
P518785 | Other | Tier 2 | Distribution | 2022-08-30 | N/A | N/A | N/A
P518785 | Pole | Tier 2 | Distribution | 2022-08-30 | N/A | N/A | N/A
P518786 | Pole | Tier 2 | Distribution | 2022-08-30 | N/A | N/A | N/A
P518787 | Pole | Tier 2 | Distribution | 2022-08-30 | N/A | N/A | N/A
P518799 | Pole | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P518885 | Transformer | Tier 2 | Distribution | 2022-11-05 | N/A | N/A | N/A
P518886 | Transformer | Tier 2 | Distribution | 2022-11-05 | N/A | N/A | N/A
P518889 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P518918 | Cross Arm | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P518938 | Cross Arm | Tier 2 | Distribution | 2022-08-19 | N/A | N/A | N/A
P518938 | Other | Tier 2 | Distribution | 2022-08-19 | N/A | N/A | N/A
P519061 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P519064 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P519325 | Cross Arm | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P519325 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P519327 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P519348 | Pole | Tier 2 | Distribution | 2022-12-09 | N/A | N/A | N/A
P519365 | Cross Arm | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P519405 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P519443 | Cross Arm | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P519443 | Other | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P519443 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P519456 | Cross Arm | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P519456 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P519456 | Pole | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P519464 | Pole | Tier 2 | Distribution | 2022-08-30 | N/A | N/A | N/A
P519468 | Cross Arm | Tier 2 | Distribution | 2022-08-30 | N/A | N/A | N/A
P519476 | Pole | Tier 2 | Distribution | 2022-03-18 | N/A | N/A | N/A
P519495 | Transformer | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P519499 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P519537 | Pole | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P519668 | Other | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P519668 | Other | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P519668 | Pole | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P519669 | Insulator and Bushing | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P519669 | Pole | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P519811 | Pole | Tier 2 | Distribution | 2022-11-18 | N/A | N/A | N/A
P519821 | Pole | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P519822 | Pole | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P519838 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P519838 | Other | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P519840 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P519851 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P519854 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P519890 | Pole | Tier 3 | Distribution | 2021-12-14 | N/A | N/A | N/A
P519941 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P519941 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P519977 | Pole | Tier 2 | Distribution | 2022-03-07 | N/A | N/A | N/A
P542452 | Cross Arm | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P570135 | Cross Arm | Tier 2 | Distribution | 2021-12-14 | N/A | N/A | N/A
P570135 | Transformer | Tier 2 | Distribution | 2021-12-14 | N/A | N/A | N/A
P570136 | Other | Tier 2 | Distribution | 2022-11-29 | N/A | N/A | N/A
P570137 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P570171 | Cross Arm | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P570546 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P570892 | Conductor | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P570892 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P570928 | Cross Arm | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P570928 | Other | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P570928 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P570929 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P570990J | Cross Arm | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P571380 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P571595 | Pole | Tier 2 | Distribution | 2022-10-20 | N/A | N/A | N/A
P571665 | Pole | Tier 2 | Distribution | 2022-03-18 | N/A | N/A | N/A
P571763 | Anchor/Guy | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P571971 | Pole | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P572015 | Anchor/Guy | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P572178 | Cross Arm | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P572179 | Cross Arm | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P572533 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P572537 | Cross Arm | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P572538 | Cross Arm | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P572539 | Cross Arm | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P572974 | Cross Arm | Tier 2 | Distribution | 2021-11-02 | N/A | N/A | N/A
P574296 | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P574572 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P575216 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P575222 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P575428 | Pole | Tier 2 | Distribution | 2021-11-08 | N/A | N/A | N/A
P576331 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P576341 | Cross Arm | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P576675 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P576743 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P576743 | Other | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P576744 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P576745 | Insulator and Bushing | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P576747 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P576749 | Pole | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P576750 | Pole | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P577067 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P577335 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P577335 | Other | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P577335 | Transformer | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P577745 | Pole | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P578769 | Cross Arm | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P578769 | Other | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P579767 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P591596 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P610027 | Other | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P610032 | Pole | Tier 2 | Distribution | 2022-12-02 | N/A | N/A | N/A
P610038 | Pole | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P610054 | Other | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P610054 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P610106 | Pole | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P610151 | Cross Arm | Tier 2 | Distribution | 2022-03-28 | N/A | N/A | N/A
P610228 | Pole | Tier 2 | Distribution | 2022-03-14 | N/A | N/A | N/A
P610246 | Pole | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P610256 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P610322 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P610381 | Other | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P610381 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P610382 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P610481 | Pole | Tier 2 | Distribution | 2022-03-25 | N/A | N/A | N/A
P610495 | Pole | Tier 3 | Distribution | 2020-02-12 | N/A | N/A | N/A
P610497 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P610525 | Cross Arm | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P610560 | Pole | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P610562 | Pole | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P610619 | Pole | Tier 2 | Distribution | 2022-03-23 | N/A | N/A | N/A
P610621 | Cross Arm | Tier 2 | Distribution | 2022-03-23 | N/A | N/A | N/A
P610628 | Pole | Tier 2 | Distribution | 2022-03-23 | N/A | N/A | N/A
P610696 | Pole | Tier 2 | Distribution | 2022-03-31 | N/A | N/A | N/A
P610762 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P610786 | Anchor/Guy | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P610786 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P610789 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P610841 | Insulator and Bushing | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P610841 | Pole | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P610912 | Cross Arm | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P610924 | Cross Arm | Tier 2 | Distribution | 2022-03-04 | N/A | N/A | N/A
P611025 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P611037 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P611063 | Cross Arm | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P611155 | Cross Arm | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P611155 | Fuse | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P611155 | Other | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P611155 | Other | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P611155 | Pole | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P611252 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P611253 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P611446 | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P611462 | Anchor/Guy | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P611479 | Cross Arm | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P611480 | Pole | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P611522 | Pole | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P611553 | Anchor/Guy | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P611553 | Other | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P611667 | Cross Arm | Tier 2 | Distribution | 2022-03-22 | N/A | N/A | N/A
P611669 | Cross Arm | Tier 2 | Distribution | 2022-03-22 | N/A | N/A | N/A
P611671 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P611695 | Transformer | Tier 2 | Distribution | 2021-08-20 | N/A | N/A | N/A
P611716 | Cross Arm | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P611754 | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P611788 | Insulator and Bushing | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P611798 | Other | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P611798 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P611815 | Conductor | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P611815 | Cross Arm | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P611856 | Cross Arm | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P611856 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P611856 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P611872 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P611923 | Pole | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P611966 | Other | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P611966 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P612020 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P612022 | Transformer | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P612025 | Other | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P612120 | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P612158 | Pole | Tier 2 | Distribution | 2022-07-13 | N/A | N/A | N/A
P612159 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P612333 | Cross Arm | Tier 2 | Distribution | 2021-11-30 | N/A | N/A | N/A
P612333 | Pole | Tier 2 | Distribution | 2021-11-30 | N/A | N/A | N/A
P612380 | Pole | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P612425 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P612426 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P612489 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P612541 | Cross Arm | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P612541 | Other | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P612541 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P612749 | Other | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P612749 | Other | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P612772 | Pole | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P612806 | Other | Tier 3 | Distribution | 2020-03-23 | N/A | N/A | N/A
P612860 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P612860 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P612865 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P612865 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P612873 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P612934 | Pole | Tier 2 | Distribution | 2022-08-29 | N/A | N/A | N/A
P612950 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P612951 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P612954 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P612980 | Pole | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P613039 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P613097 | Pole | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P613107 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P613182 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P613184 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P613192J | Pole | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P613223 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P613252 | Insulator and Bushing | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P613252 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P613318 | Pole | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P613319 | Pole | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P613320 | Pole | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P613321 | Pole | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P613542 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P613615 | Cross Arm | Tier 2 | Distribution | 2022-03-30 | N/A | N/A | N/A
P613643 | Cross Arm | Tier 2 | Distribution | 2022-08-01 | N/A | N/A | N/A
P613643 | Pole | Tier 2 | Distribution | 2022-08-01 | N/A | N/A | N/A
P613716 | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P613716 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P613723 | Other | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P613724 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P613733 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P613900 | Cross Arm | Tier 2 | Distribution | 2022-08-18 | N/A | N/A | N/A
P613946 | Other | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P613946 | Pole | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P613956 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P613994 | Pole | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P614114 | Cross Arm | Tier 2 | Distribution | 2022-04-21 | N/A | N/A | N/A
P614115 | Cross Arm | Tier 2 | Distribution | 2022-04-21 | N/A | N/A | N/A
P614170 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P614203 | Transformer | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P614239 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P614239 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P614498 | Transformer | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P614520J | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P614524 | Transformer | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P614777 | Pole | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P614790 | Pole | Tier 2 | Distribution | 2022-03-28 | N/A | N/A | N/A
P614816J | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P614816J | Other | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P614833 | Cross Arm | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P614884 | Pole | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P614987 | Pole | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P615062 | Transformer | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P615074 | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P615079 | Transformer | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P615176 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P615194 | Cross Arm | Tier 2 | Distribution | 2022-03-18 | N/A | N/A | N/A
P615216 | Pole | Tier 2 | Distribution | 2021-10-26 | N/A | N/A | N/A
P615234 | Pole | Tier 2 | Distribution | 2022-12-01 | N/A | N/A | N/A
P615235 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P615248 | Pole | Tier 2 | Distribution | 2022-03-03 | N/A | N/A | N/A
P615491 | Pole | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P615501 | Insulator and Bushing | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P615501 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P615526 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P615526 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P615527 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P615528 | Other | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P615528 | Transformer | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P615609 | Cross Arm | Tier 2 | Distribution | 2021-10-18 | N/A | N/A | N/A
P615611 | Cross Arm | Tier 2 | Distribution | 2021-10-18 | N/A | N/A | N/A
P615611 | Other | Tier 2 | Distribution | 2021-10-18 | N/A | N/A | N/A
P615612 | Other | Tier 2 | Distribution | 2021-10-18 | N/A | N/A | N/A
P615612 | Pole | Tier 2 | Distribution | 2021-10-18 | N/A | N/A | N/A
P615641 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P615720J | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P615761 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P615789 | Pole | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P615793 | Pole | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P615867 | Pole | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P615870 | Pole | Tier 2 | Distribution | 2022-11-28 | N/A | N/A | N/A
P615886 | Insulator and Bushing | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P615886 | Other | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P615922 | Transformer | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P615929 | Pole | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P616063 | Pole | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P616121 | Other | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P616179 | Cross Arm | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P616235 | Pole | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P616258 | Cross Arm | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P616416 | Cross Arm | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P616416 | Other | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P616497 | Pole | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P616509 | Pole | Tier 2 | Distribution | 2022-03-14 | N/A | N/A | N/A
P616702 | Cross Arm | Tier 2 | Distribution | 2022-10-04 | N/A | N/A | N/A
P616766 | Other | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P616766 | Pole | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P616769 | Cross Arm | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P616770 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P616877 | Pole | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P616885 | Pole | Tier 2 | Distribution | 2022-05-11 | N/A | N/A | N/A
P616886J | Other | Tier 2 | Distribution | 2022-12-03 | N/A | N/A | N/A
P616911 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P616954 | Pole | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P617108 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P617228 | Other | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P617377 | Other | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P617382 | Transformer | Tier 2 | Distribution | 2022-03-10 | N/A | N/A | N/A
P617445 | Pole | Tier 2 | Distribution | 2022-03-17 | N/A | N/A | N/A
P617546 | Pole | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P617548 | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P617551 | Conductor | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P617551 | Insulator and Bushing | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P617551 | Other | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P617576 | Other | Tier 2 | Distribution | 2022-08-27 | N/A | N/A | N/A
P617747 | Cross Arm | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P617898 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P617964 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P617966 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P617967 | Cross Arm | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P617979 | Anchor/Guy | Tier 2 | Distribution | 2022-03-04 | N/A | N/A | N/A
P617980 | Pole | Tier 2 | Distribution | 2022-03-04 | N/A | N/A | N/A
P618002 | Conductor | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P618002 | Other | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P618002 | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P618029 | Cross Arm | Tier 2 | Distribution | 2021-11-12 | N/A | N/A | N/A
P618053 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P618072 | Insulator and Bushing | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P618195 | Pole | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P618199J | Pole | Tier 2 | Distribution | 2022-10-07 | N/A | N/A | N/A
P618223 | Insulator and Bushing | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P618223 | Transformer | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P618278 | Pole | Tier 2 | Distribution | 2022-11-04 | N/A | N/A | N/A
P618293 | Cross Arm | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P618293 | Pole | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P618371 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P618406 | Other | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P618453 | Other | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P618519 | Pole | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P618522 | Pole | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P618621 | Pole | Tier 2 | Distribution | 2022-09-25 | N/A | N/A | N/A
P618728 | Pole | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P618736 | Other | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P618736 | Pole | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P618739 | Pole | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P618753 | Cross Arm | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P618785 | Other | Tier 2 | Distribution | 2022-06-27 | N/A | N/A | N/A
P618792 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P618838 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P618982 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P618987 | Pole | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P619040 | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P619100 | Other | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P619127 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P619152 | Pole | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P619173 | Insulator and Bushing | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P619231 | Other | Tier 2 | Distribution | 2022-08-27 | N/A | N/A | N/A
P619256 | Anchor/Guy | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P619276 | Cross Arm | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P619276 | Pole | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P619319 | Cross Arm | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P619319 | Other | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P619321 | Cross Arm | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P619346 | Pole | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P619455 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P619476 | Other | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P619476 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P619520 | Pole | Tier 2 | Distribution | 2022-03-30 | N/A | N/A | N/A
P619546 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P619548 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P619578 | Pole | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P619603 | Pole | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P619617 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P619617 | Insulator and Bushing | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P619617 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P619618 | Pole | Tier 2 | Distribution | 2022-04-18 | N/A | N/A | N/A
P619653 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P619713 | Pole | Tier 2 | Distribution | 2022-08-30 | N/A | N/A | N/A
P619718 | Pole | Tier 2 | Distribution | 2022-11-30 | N/A | N/A | N/A
P619756 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P619863 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P619893 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P619915 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P670057 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P670559 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P670882 | Conductor | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P670882 | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P670882 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P671410 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P671680 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P671690 | Cross Arm | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P671690 | Pole | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P671696 | Pole | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P672105 | Pole | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P672639 | Other | Tier 2 | Distribution | 2022-10-25 | N/A | N/A | N/A
P672640 | Other | Tier 2 | Distribution | 2022-10-25 | N/A | N/A | N/A
P672676 | Cross Arm | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P674058 | Pole | Tier 2 | Distribution | 2021-12-14 | N/A | N/A | N/A
P674250J | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P674250J | Pole | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P674283 | Conductor | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P674283 | Pole | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P675047 | Transformer | Tier 2 | Distribution | 2021-12-14 | N/A | N/A | N/A
P675307 | Cross Arm | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P675328 | Pole | Tier 2 | Distribution | 2022-06-27 | N/A | N/A | N/A
P675330 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P675528 | Cross Arm | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P676515J | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P676515J | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P676547 | Other | Tier 2 | Distribution | 2022-08-09 | N/A | N/A | N/A
P676547 | Transformer | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P676559 | Cross Arm | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P676559 | Other | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P676562 | Pole | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P676566 | Other | Tier 2 | Distribution | 2022-10-19 | N/A | N/A | N/A
P676567 | Pole | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P676869 | Pole | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P676870 | Conductor | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P676875 | Anchor/Guy | Tier 2 | Distribution | 2021-11-30 | N/A | N/A | N/A
P677097 | Cross Arm | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P677250 | Pole | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P677302 | Anchor/Guy | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P677546 | Cross Arm | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P677793 | Cross Arm | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P678124 | Pole | Tier 3 | Distribution | 2022-04-25 | N/A | N/A | N/A
P678516 | Cross Arm | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P678517 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P678530 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P678679 | Insulator and Bushing | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P678731 | Conductor | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P678731 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P679565 | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P679762 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P707069 | Cross Arm | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P707069 | Pole | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P710116J | Pole | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P710172 | Pole | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P710175 | Cross Arm | Tier 2 | Distribution | 2022-03-30 | N/A | N/A | N/A
P710175 | Pole | Tier 2 | Distribution | 2022-03-30 | N/A | N/A | N/A
P710257 | Pole | Tier 2 | Distribution | 2022-12-19 | N/A | N/A | N/A
P710259 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P710260 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P710264 | Cross Arm | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P710264 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P710267J | Cross Arm | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P710267J | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P710270 | Cross Arm | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P710270 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P710272 | Pole | Tier 2 | Distribution | 2022-05-13 | N/A | N/A | N/A
P710282 | Other | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P710295 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P710305 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P710324 | Cross Arm | Tier 2 | Distribution | 2022-08-30 | N/A | N/A | N/A
P710330 | Pole | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P710333 | Transformer | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P710336 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P710353 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P710361 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P710449 | Cross Arm | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P710453 | Pole | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P710504 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P710504 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P710543 | Transformer | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P710590 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P710591 | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P710602 | Cross Arm | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P710603 | Cross Arm | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P710615 | Pole | Tier 2 | Distribution | 2022-03-10 | N/A | N/A | N/A
P710702 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P710702 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P710731 | Cross Arm | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P710736 | Cross Arm | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P710736 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P710760 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P710761 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P710762 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P710763 | Pole | Tier 2 | Distribution | 2022-07-13 | N/A | N/A | N/A
P710764 | Other | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P710764 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P710766 | Other | Tier 2 | Distribution | 2022-07-28 | N/A | N/A | N/A
P710767 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P710794 | Pole | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P710837 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P710896 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P710920 | Transformer | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P711072 | Cross Arm | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P711090 | Cross Arm | Tier 2 | Distribution | 2022-03-15 | N/A | N/A | N/A
P711112 | Cross Arm | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P711134 | Cross Arm | Tier 2 | Distribution | 2022-06-27 | N/A | N/A | N/A
P711154 | Other | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P711154 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P711354 | Pole | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P711355 | Cross Arm | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P711415 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P711416 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P711445 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P711449 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P711450 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P711457 | Cross Arm | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P711465 | Cross Arm | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P711465 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P711465 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P711569 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P711744 | Pole | Tier 2 | Distribution | 2022-03-02 | N/A | N/A | N/A
P711751 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P711777 | Pole | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P711799 | Pole | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P711800 | Cross Arm | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P711800 | Other | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P711800 | Other | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P711808 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P711898 | Cross Arm | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P711899 | Cross Arm | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P711900 | Cross Arm | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P711901 | Cross Arm | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P711959J | Cross Arm | Tier 2 | Distribution | 2022-11-08 | N/A | N/A | N/A
P711960J | Pole | Tier 2 | Distribution | 2022-11-08 | N/A | N/A | N/A
P711972 | Cross Arm | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P711974 | Anchor/Guy | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P712001 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P712024 | Cross Arm | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P712024 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P712025 | Pole | Tier 2 | Distribution | 2022-03-22 | N/A | N/A | N/A
P712058 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P712127 | Cross Arm | Tier 2 | Distribution | 2022-06-15 | N/A | N/A | N/A
P712136 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P712144 | Cross Arm | Tier 2 | Distribution | 2022-03-15 | N/A | N/A | N/A
P712144 | Other | Tier 2 | Distribution | 2022-03-15 | N/A | N/A | N/A
P712201 | Transformer | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P712202 | Cross Arm | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P712202 | Pole | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P712203 | Cross Arm | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P712243 | Pole | Tier 2 | Distribution | 2022-06-16 | N/A | N/A | N/A
P712282 | Transformer | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P712344 | Cross Arm | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P712344 | Other | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P712344 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P712371 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P712382 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P712384 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P712428 | Cross Arm | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P712428 | Pole | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P712437 | Cross Arm | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P712437 | Pole | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P712438 | Cross Arm | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P712471 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P712474 | Anchor/Guy | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P712474 | Anchor/Guy | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P712573 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P712591 | Cross Arm | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P712591 | Other | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P712606 | Pole | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P712610 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P712622 | Pole | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P712639 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P712704 | Cross Arm | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P712726 | Cross Arm | Tier 2 | Distribution | 2022-03-04 | N/A | N/A | N/A
P712734 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P712742 | Other | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P712742 | Pole | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P712766 | Cross Arm | Tier 2 | Distribution | 2022-03-30 | N/A | N/A | N/A
P712887 | Anchor/Guy | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P712893 | Pole | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P712952 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P712966 | Cross Arm | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P713009 | Other | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P713009 | Pole | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P713027 | Cross Arm | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P713080 | Cross Arm | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P713092 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P713162 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P713162 | Other | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P713175 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P713175 | Other | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P713224 | Cross Arm | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P713224 | Fuse | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P713265 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P713267 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P713267 | Transformer | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P713268 | Other | Tier 2 | Distribution | 2022-10-12 | N/A | N/A | N/A
P713270 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P713271 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P713333 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P713335 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P713335 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P713378 | Pole | Tier 2 | Distribution | 2022-11-04 | N/A | N/A | N/A
P713379 | Insulator and Bushing | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P713379 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P713396 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P713396 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P713397 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P713412 | Cross Arm | Tier 2 | Distribution | 2022-06-27 | N/A | N/A | N/A
P713413 | Other | Tier 2 | Distribution | 2022-11-09 | N/A | N/A | N/A
P713414 | Cross Arm | Tier 2 | Distribution | 2022-06-27 | N/A | N/A | N/A
P713421 | Transformer | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P713524 | Anchor/Guy | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P713535 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P713669 | Other | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P713683 | Cross Arm | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P713708 | Pole | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P713719 | Transformer | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P713743 | Pole | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P713747 | Other | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P713747 | Pole | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P713785 | Other | Tier 2 | Distribution | 2021-10-26 | N/A | N/A | N/A
P713811 | Cross Arm | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P713811 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P713899 | Cross Arm | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P713899 | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P713903 | Insulator and Bushing | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P713903 | Other | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P713934 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P713934 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P713969 | Cross Arm | Tier 2 | Distribution | 2022-03-28 | N/A | N/A | N/A
P713971 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P713971 | Pole | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P714026 | Cross Arm | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P714030 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P714034 | Cross Arm | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P714045 | Cross Arm | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P714059 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P714081 | Pole | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P714191 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P714216 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P714238 | Pole | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P714501 | Cross Arm | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P714501 | Pole | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P714543 | Pole | Tier 2 | Distribution | 2022-01-06 | N/A | N/A | N/A
P714544 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P714545 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P714545 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P714566 | Cross Arm | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P714566 | Other | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P714609 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P714638J | Other | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P714638J | Pole | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P714651 | Transformer | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P714760 | Cross Arm | Tier 2 | Distribution | 2022-03-29 | N/A | N/A | N/A
P714770 | Cross Arm | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P714770 | Pole | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P714778 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P714800 | Pole | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P714801 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P714802 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P714814 | Pole | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P714842 | Pole | Tier 2 | Distribution | 2022-03-05 | N/A | N/A | N/A
P714848 | Cross Arm | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P714850 | Cross Arm | Tier 2 | Distribution | 2022-03-10 | N/A | N/A | N/A
P714975 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P714994 | Cross Arm | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P714995 | Pole | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P715009 | Pole | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P715097 | Cross Arm | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P715149 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P715170 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P715250 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P715289 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P715308 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P715526 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P715531 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P715532 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P715534 | Pole | Tier 2 | Distribution | 2022-08-22 | N/A | N/A | N/A
P715556 | Cross Arm | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P715557 | Cross Arm | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P715586 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P715634 | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P715640 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P715640 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P715641 | Pole | Tier 2 | Distribution | 2022-01-06 | N/A | N/A | N/A
P715644 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P715676 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P715698 | Other | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P715698 | Other | Tier 2 | Distribution | 2022-11-29 | N/A | N/A | N/A
P715699 | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P715700 | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P715705 | Pole | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P715708 | Other | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P715708 | Pole | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P715800 | Cross Arm | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P715800 | Transformer | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P715872J | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P715876 | Transformer | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P715894 | Cross Arm | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P716012 | Pole | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P716017 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P716026 | Other | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P716052 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P716055 | Cross Arm | Tier 2 | Distribution | 2022-08-30 | N/A | N/A | N/A
P716073 | Other | Tier 2 | Distribution | 2022-12-15 | N/A | N/A | N/A
P716089 | Other | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P716185 | Transformer | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P716199 | Other | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P716199 | Transformer | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P716291 | Pole | Tier 2 | Distribution | 2021-11-02 | N/A | N/A | N/A
P716309 | Cross Arm | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P716309 | Pole | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P716320 | Cross Arm | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P716353 | Pole | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P716364 | Pole | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P716371 | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P716386 | Transformer | Tier 3 | Distribution | 2020-02-19 | N/A | N/A | N/A
P716451 | Cross Arm | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P716451 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P716452 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P716461 | Pole | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P716521 | Cross Arm | Tier 2 | Distribution | 2022-05-13 | N/A | N/A | N/A
P716562 | Pole | Tier 2 | Distribution | 2022-03-09 | N/A | N/A | N/A
P716613 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P716658 | Pole | Tier 2 | Distribution | 2022-03-15 | N/A | N/A | N/A
P716746 | Cross Arm | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P716746 | Other | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P716811 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P716827 | Pole | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P716918J | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P716919J | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P716961 | Pole | Tier 2 | Distribution | 2021-11-30 | N/A | N/A | N/A
P716976 | Other | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P716977 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P716989 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P716991 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P717007J | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P717011 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P717011 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P717013 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P717023 | Cross Arm | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P717034 | Other | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P717034 | Pole | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P717046 | Transformer | Tier 2 | Distribution | 2022-09-20 | N/A | N/A | N/A
P717073 | Pole | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P717097 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P717218 | Other | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P717236 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P717236 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P717390 | Pole | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P717431 | Cross Arm | Tier 2 | Distribution | 2022-03-30 | N/A | N/A | N/A
P717480 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P717481 | Pole | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P717495 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P717495 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P717496 | Other | Tier 2 | Distribution | 2022-11-29 | N/A | N/A | N/A
P717622 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P717730 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P717780 | Transformer | Tier 2 | Distribution | 2022-06-27 | N/A | N/A | N/A
P717781 | Cross Arm | Tier 2 | Distribution | 2022-06-27 | N/A | N/A | N/A
P717795 | Cross Arm | Tier 2 | Distribution | 2022-04-22 | N/A | N/A | N/A
P717884 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P717885 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P717912 | Cross Arm | Tier 2 | Distribution | 2022-03-07 | N/A | N/A | N/A
P717923 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P718002 | Pole | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P718003 | Pole | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P718029 | Anchor/Guy | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P718033 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P718039 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P718053 | Pole | Tier 2 | Distribution | 2022-03-17 | N/A | N/A | N/A
P718078 | Pole | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P718094 | Pole | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P718107 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P718230 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P718421 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P718444 | Pole | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P718445 | Pole | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P718446 | Cross Arm | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P718446 | Other | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P718446 | Pole | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P718451 | Other | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P718555 | Pole | Tier 2 | Distribution | 2022-12-13 | N/A | N/A | N/A
P718573 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P718631 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P718734 | Pole | Tier 2 | Distribution | 2022-11-28 | N/A | N/A | N/A
P718781 | Cross Arm | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P718796 | Pole | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P718824 | Pole | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P718871 | Pole | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P718951 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P718979 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P718985 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P718995 | Other | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P718995 | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P719034 | Transformer | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P719072J | Cross Arm | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P719072J | Other | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P719083 | Pole | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P719296J | Cross Arm | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P719296J | Other | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P719301 | Cross Arm | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P719301 | Pole | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P719302 | Other | Tier 2 | Distribution | 2022-12-08 | N/A | N/A | N/A
P719304 | Anchor/Guy | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P719324 | Pole | Tier 2 | Distribution | 2022-03-29 | N/A | N/A | N/A
P719327 | Other | Tier 2 | Distribution | 2022-03-29 | N/A | N/A | N/A
P719327 | Pole | Tier 2 | Distribution | 2022-03-29 | N/A | N/A | N/A
P719336 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P719336 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P719361 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P719365 | Insulator and Bushing | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P719365 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P719397 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P719400 | Pole | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P719401 | Other | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P719478 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P719478 | Pole | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P719479 | Cross Arm | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P719479 | Pole | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P719480 | Cross Arm | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P719599 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P719599 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P719602J | Cross Arm | Tier 2 | Distribution | 2022-04-22 | N/A | N/A | N/A
P719616 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P719770 | Cross Arm | Tier 2 | Distribution | 2022-03-31 | N/A | N/A | N/A
P719778 | Other | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P719778 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P719779 | Pole | Tier 2 | Distribution | 2021-08-04 | N/A | N/A | N/A
P719787 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P719810 | Cross Arm | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P719814 | Cross Arm | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P719821 | Insulator and Bushing | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P719899 | Other | Tier 2 | Distribution | 2022-05-26 | N/A | N/A | N/A
P719900 | Other | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P719900 | Other | Tier 2 | Distribution | 2022-05-26 | N/A | N/A | N/A
P719901 | Other | Tier 2 | Distribution | 2022-05-26 | N/A | N/A | N/A
P719902 | Other | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P719902 | Pole | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P72676 | Other | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P72676 | Pole | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P72900 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P729623 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P73709 | Transformer | Tier 2 | Distribution | 2021-11-30 | N/A | N/A | N/A
P73879 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P74025 | Anchor/Guy | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P74169 | Cross Arm | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P74310 | Pole | Tier 2 | Distribution | 2022-02-15 | N/A | N/A | N/A
P74312 | Pole | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P74314 | Cross Arm | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P74315 | Cross Arm | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P74920 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P75048 | Other | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P75088 | Cross Arm | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P75489 | Other | Tier 2 | Distribution | 2021-11-08 | N/A | N/A | N/A
P75963 | Other | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P75966 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P75966 | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P75966 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P75975 | Transformer | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P75976 | Cross Arm | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P75979 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P76499 | Other | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P76499 | Other | Tier 2 | Distribution | 2022-11-29 | N/A | N/A | N/A
P77004 | Other | Tier 3 | Distribution | 2020-05-14 | N/A | N/A | N/A
P770180 | Pole | Tier 3 | Distribution | 2022-08-26 | N/A | N/A | N/A
P770248 | Cross Arm | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P770248 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P770269 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P770282 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P770413 | Cross Arm | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P770474 | Pole | Tier 3 | Distribution | 2022-12-02 | N/A | N/A | N/A
P770475 | Conductor | Tier 3 | Distribution | 2022-12-02 | N/A | N/A | N/A
P770475 | Pole | Tier 3 | Distribution | 2022-12-02 | N/A | N/A | N/A
P770737 | Pole | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P770791 | Pole | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P771179 | Transformer | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P771233 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P771359 | Pole | Tier 2 | Distribution | 2021-10-19 | N/A | N/A | N/A
P771533 | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P771739 | Other | Tier 3 | Distribution | 2020-03-18 | N/A | N/A | N/A
P771841 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P771923 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P771941 | Insulator and Bushing | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P771942 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P771962 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P771962 | Transformer | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P772394 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P772523 | Pole | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P772524 | Cross Arm | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P772524 | Pole | Tier 3 | Distribution | 2022-11-21 | N/A | N/A | N/A
P772766 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P772884 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P773211 | Pole | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P773213 | Other | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P773225 | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P773295 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P773566 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P773644 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P773645 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P773713 | Conductor | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P773713 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P773969 | Other | Tier 2 | Distribution | 2022-09-20 | N/A | N/A | N/A
P773970 | Other | Tier 3 | Distribution | 2021-04-07 | N/A | N/A | N/A
P774385 | Conductor | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P774385 | Other | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P774391 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P774412 | Pole | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P774424 | Other | Tier 2 | Distribution | 2022-11-29 | N/A | N/A | N/A
P774457 | Pole | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P774684 | Cross Arm | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P775020 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P775028 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P775097 | Conductor | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P775097 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P775345 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P775414 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P775612J | Pole | Tier 2 | Distribution | 2022-10-10 | N/A | N/A | N/A
P775633 | Pole | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P775638 | Other | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P775638 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P775643 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P775652 | Pole | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P776191J | Other | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P776191J | Other | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P776416 | Insulator and Bushing | Tier 2 | Distribution | 2022-02-15 | N/A | N/A | N/A
P776487 | Pole | Tier 3 | Distribution | 2022-04-25 | N/A | N/A | N/A
P777027 | Pole | Tier 2 | Distribution | 2022-09-20 | N/A | N/A | N/A
P777265 | Pole | Tier 2 | Distribution | 2022-12-14 | N/A | N/A | N/A
P777477 | Insulator and Bushing | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P778114 | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P778114 | Transformer | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P778741 | Pole | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P78976 | Cross Arm | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P810010 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P810068 | Pole | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P810077 | Cross Arm | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P810081 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P810081 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P810105 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P810173 | Other | Tier 2 | Distribution | 2022-04-22 | N/A | N/A | N/A
P810173 | Pole | Tier 2 | Distribution | 2022-04-22 | N/A | N/A | N/A
P810392 | Cross Arm | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P810562 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P810583 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P810622 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P810622 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P810646 | Cross Arm | Tier 2 | Distribution | 2022-07-05 | N/A | N/A | N/A
P810654 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P810696 | Other | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P810696 | Pole | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P810710 | Pole | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P810817 | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P810845 | Pole | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P810876 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P810880J | Cross Arm | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P810937J | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P810938J | Pole | Tier 2 | Distribution | 2022-06-22 | N/A | N/A | N/A
P810965 | Pole | Tier 2 | Distribution | 2022-03-17 | N/A | N/A | N/A
P810966 | Pole | Tier 2 | Distribution | 2022-03-17 | N/A | N/A | N/A
P810975 | Pole | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P811017 | Pole | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P811018 | Pole | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P811019 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P811087 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P811087 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P811087 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P811153 | Pole | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P811154 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P811155 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P811155 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P811169 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P811200 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P811229 | Pole | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P811413 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P811413 | Transformer | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P811447 | Pole | Tier 2 | Distribution | 2022-08-25 | N/A | N/A | N/A
P811471 | Cross Arm | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P811506 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P811506 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P811625 | Pole | Tier 2 | Distribution | 2022-03-04 | N/A | N/A | N/A
P811643 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P811644 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P811647 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P811648 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P811673 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P811740 | Transformer | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P811857 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P811857 | Other | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P811858 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P811858 | Other | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P811870 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P811871 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P811876 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P811876 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P811919 | Cross Arm | Tier 2 | Distribution | 2021-11-02 | N/A | N/A | N/A
P811928 | Pole | Tier 2 | Distribution | 2021-08-10 | N/A | N/A | N/A
P811934 | Cross Arm | Tier 2 | Distribution | 2022-04-19 | N/A | N/A | N/A
P811950 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P811951 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P811981 | Other | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P811981 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P811995 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P811995 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P811995 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P812009 | Cross Arm | Tier 2 | Distribution | 2022-03-28 | N/A | N/A | N/A
P812062 | Cross Arm | Tier 2 | Distribution | 2022-03-02 | N/A | N/A | N/A
P812189 | Insulator and Bushing | Tier 2 | Distribution | 2022-12-02 | N/A | N/A | N/A
P812192 | Pole | Tier 2 | Distribution | 2022-12-02 | N/A | N/A | N/A
P812202 | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P812202 | Other | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P812214 | Pole | Tier 2 | Distribution | 2022-06-29 | N/A | N/A | N/A
P812216 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P812250 | Pole | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P812262 | Other | Tier 2 | Distribution | 2021-11-12 | N/A | N/A | N/A
P812262 | Pole | Tier 2 | Distribution | 2021-11-12 | N/A | N/A | N/A
P812323 | Pole | Tier 2 | Distribution | 2022-07-20 | N/A | N/A | N/A
P812348 | Pole | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P812368 | Pole | Tier 2 | Distribution | 2021-09-11 | N/A | N/A | N/A
P812374 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P812423 | Other | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P812479 | Other | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P812527 | Pole | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P812541 | Anchor/Guy | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P812589 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P812590 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P812590 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P812612 | Cross Arm | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P812612 | Pole | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P812762 | Transformer | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P812767 | Pole | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P812773 | Pole | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P812774 | Other | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P812774 | Pole | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P812776 | Cross Arm | Tier 2 | Distribution | 2022-01-31 | N/A | N/A | N/A
P812815 | Other | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P812815 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P812915 | Insulator and Bushing | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P812918 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P812920 | Cross Arm | Tier 2 | Distribution | 2021-08-18 | N/A | N/A | N/A
P812934 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P812935 | Cross Arm | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P812955 | Cross Arm | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P812955 | Pole | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P812957 | Cross Arm | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P812957 | Pole | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P812960 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P812960 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P812960 | Pole | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P813002 | Cross Arm | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P813013 | Cross Arm | Tier 2 | Distribution | 2022-05-10 | N/A | N/A | N/A
P813228 | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P813231 | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P813231 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P813240 | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P813242 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P813298 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P813298 | Pole | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P813312 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P813513 | Pole | Tier 2 | Distribution | 2021-08-13 | N/A | N/A | N/A
P813524 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P813525 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P813541 | Other | Tier 2 | Distribution | 2022-12-02 | N/A | N/A | N/A
P813577 | Pole | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P813631 | Other | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P813631 | Pole | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P813632 | Other | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P813632 | Other | Tier 2 | Distribution | 2022-12-09 | N/A | N/A | N/A
P813633 | Cross Arm | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P813633 | Pole | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P813634 | Pole | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P813635 | Other | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P813635 | Pole | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P813663 | Pole | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P813697 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P813698 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P813699 | Pole | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P813707 | Cross Arm | Tier 2 | Distribution | 2022-09-20 | N/A | N/A | N/A
P813781 | Cross Arm | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P813791 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P813797 | Transformer | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P813904 | Pole | Tier 2 | Distribution | 2022-03-04 | N/A | N/A | N/A
P813971 | Other | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P813971 | Other | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P813971 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P813984 | Cross Arm | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P813984 | Other | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P813984 | Other | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P814032 | Other | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P814032 | Pole | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P814036 | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P814037 | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P814114 | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P814118 | Other | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P814118 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P814126 | Pole | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P814295 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P814305 | Cross Arm | Tier 2 | Distribution | 2022-07-08 | N/A | N/A | N/A
P814344 | Other | Tier 2 | Distribution | 2021-10-18 | N/A | N/A | N/A
P814364 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P814364 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P814404 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P814404 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P814410 | Cross Arm | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P814488 | Other | Tier 2 | Distribution | 2021-10-25 | N/A | N/A | N/A
P814488 | Pole | Tier 2 | Distribution | 2021-10-25 | N/A | N/A | N/A
P814594 | Other | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P814594 | Transformer | Tier 2 | Distribution | 2022-02-03 | N/A | N/A | N/A
P814609J | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P814611J | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P814615J | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P814623 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P814624 | Cross Arm | Tier 2 | Distribution | 2022-08-27 | N/A | N/A | N/A
P814636 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P814699 | Other | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P814699 | Pole | Tier 2 | Distribution | 2021-09-19 | N/A | N/A | N/A
P814701 | Cross Arm | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P814702 | Other | Tier 2 | Distribution | 2022-12-03 | N/A | N/A | N/A
P814736 | Other | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P814736 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P814737 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P814809 | Cross Arm | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P814821 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P814897 | Cross Arm | Tier 2 | Distribution | 2022-03-23 | N/A | N/A | N/A
P814968 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P814968 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P814989 | Pole | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P815142 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P815144 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P815145 | Pole | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P815203J | Pole | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P815206J | Pole | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
P815293J | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P815295J | Pole | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P815304 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P815330 | Pole | Tier 2 | Distribution | 2022-03-31 | N/A | N/A | N/A
P815354 | Other | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P815378 | Cross Arm | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P815433 | Other | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P815433 | Pole | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P815463 | Conductor | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P815463 | Cross Arm | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
P815512 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P815557 | Pole | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P815739 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P815746 | Pole | Tier 2 | Distribution | 2022-05-11 | N/A | N/A | N/A
P815747 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P815747 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P815748 | Pole | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
P815766 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P815767 | Other | Tier 2 | Distribution | 2022-06-10 | N/A | N/A | N/A
P815987 | Cross Arm | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P815987 | Other | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P816093 | Cross Arm | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P816093 | Pole | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P816178 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P816181 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P816181 | Other | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P816245 | Cross Arm | Tier 2 | Distribution | 2021-09-23 | N/A | N/A | N/A
P816317 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P816370 | Pole | Tier 2 | Distribution | 2021-08-27 | N/A | N/A | N/A
P816373 | Cross Arm | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P816414 | Cross Arm | Tier 2 | Distribution | 2022-08-01 | N/A | N/A | N/A
P816414 | Pole | Tier 2 | Distribution | 2022-08-01 | N/A | N/A | N/A
P816465 | Other | Tier 2 | Distribution | 2022-03-30 | N/A | N/A | N/A
P816465 | Other | Tier 2 | Distribution | 2022-03-30 | N/A | N/A | N/A
P816465 | Pole | Tier 2 | Distribution | 2022-03-30 | N/A | N/A | N/A
P816471 | Cross Arm | Tier 2 | Distribution | 2022-03-11 | N/A | N/A | N/A
P816510 | Other | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P816510 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P816516 | Pole | Tier 2 | Distribution | 2021-10-04 | N/A | N/A | N/A
P816532 | Cross Arm | Tier 2 | Distribution | 2022-04-14 | N/A | N/A | N/A
P816544 | Cross Arm | Tier 2 | Distribution | 2022-04-22 | N/A | N/A | N/A
P816586 | Cross Arm | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P816587 | Cross Arm | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P816587 | Other | Tier 2 | Distribution | 2022-03-08 | N/A | N/A | N/A
P816592 | Cross Arm | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P816592 | Pole | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P816593 | Cross Arm | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P816593 | Pole | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P816594 | Cross Arm | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P816594 | Pole | Tier 2 | Distribution | 2022-03-21 | N/A | N/A | N/A
P816615 | Cross Arm | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P816615 | Other | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P816615 | Pole | Tier 2 | Distribution | 2022-07-12 | N/A | N/A | N/A
P816640J | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P816642 | Insulator and Bushing | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P816654 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P816655 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P816707 | Pole | Tier 2 | Distribution | 2022-12-13 | N/A | N/A | N/A
P816708 | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P816724 | Cross Arm | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P816745J | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P816832 | Cross Arm | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P816916 | Cross Arm | Tier 2 | Distribution | 2022-04-20 | N/A | N/A | N/A
P816974 | Cross Arm | Tier 2 | Distribution | 2022-01-27 | N/A | N/A | N/A
P816975 | Pole | Tier 2 | Distribution | 2022-12-12 | N/A | N/A | N/A
P817036 | Cross Arm | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P817036 | Insulator and Bushing | Tier 2 | Distribution | 2021-12-29 | N/A | N/A | N/A
P817074 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P817075 | Other | Tier 2 | Distribution | 2022-11-16 | N/A | N/A | N/A
P817218 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P817254 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P817282 | Cross Arm | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P817287 | Cross Arm | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P817311 | Cross Arm | Tier 2 | Distribution | 2022-03-23 | N/A | N/A | N/A
P817403 | Cross Arm | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P817436 | Cross Arm | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P817447 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P817583 | Pole | Tier 2 | Distribution | 2021-10-10 | N/A | N/A | N/A
P817591 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P817623 | Cross Arm | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P817627 | Cross Arm | Tier 2 | Distribution | 2022-03-25 | N/A | N/A | N/A
P817729J | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P817734 | Cross Arm | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P817737 | Pole | Tier 2 | Distribution | 2022-03-01 | N/A | N/A | N/A
P818045 | Other | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P818045 | Pole | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P818057 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P818188 | Pole | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P818197 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P818198 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P818244 | Cross Arm | Tier 2 | Distribution | 2022-04-12 | N/A | N/A | N/A
P818336 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P818373 | Cross Arm | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P818373 | Insulator and Bushing | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P818373 | Other | Tier 2 | Distribution | 2022-04-25 | N/A | N/A | N/A
P818429 | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P818474 | Cross Arm | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P818474 | Other | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P818474 | Pole | Tier 2 | Distribution | 2022-06-02 | N/A | N/A | N/A
P818688 | Pole | Tier 2 | Distribution | 2022-11-08 | N/A | N/A | N/A
P818754 | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P818754 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P818800 | Pole | Tier 2 | Distribution | 2022-03-28 | N/A | N/A | N/A
P818837 | Cross Arm | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P818842 | Cross Arm | Tier 3 | Distribution | 2022-12-02 | N/A | N/A | N/A
P819071 | Other | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P819071 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P819104 | Cross Arm | Tier 2 | Distribution | 2022-07-21 | N/A | N/A | N/A
P819159 | Pole | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P819160 | Pole | Tier 2 | Distribution | 2022-05-11 | N/A | N/A | N/A
P819187 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P819188 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P819435 | Cross Arm | Tier 2 | Distribution | 2022-02-09 | N/A | N/A | N/A
P819678 | Pole | Tier 2 | Distribution | 2022-05-24 | N/A | N/A | N/A
P819845 | Other | Tier 2 | Distribution | 2022-11-23 | N/A | N/A | N/A
P831226 | Cross Arm | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P839764 | Pole | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P86042 | Pole | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P86045 | Pole | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P86051 | Pole | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P86054 | Pole | Tier 2 | Distribution | 2022-01-09 | N/A | N/A | N/A
P86056 | Other | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P870036 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P870040 | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P870040 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P870041 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P870055 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P870056 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P870060 | Insulator and Bushing | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P870065 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P870079 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P870335 | Pole | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P870336 | Pole | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P870355 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P870356 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P870382 | Pole | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P870400 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P870520 | Cross Arm | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P870522 | Pole | Tier 2 | Distribution | 2021-11-20 | N/A | N/A | N/A
P870586 | Other | Tier 3 | Distribution | 2020-05-05 | N/A | N/A | N/A
P870705 | Pole | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P870786 | Other | Tier 3 | Distribution | 2020-03-17 | N/A | N/A | N/A
P870946 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P871157 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P871189 | Pole | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P871560 | Pole | Tier 2 | Distribution | 2021-12-21 | N/A | N/A | N/A
P871970 | Other | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P872004 | Pole | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P872089 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P872093 | Cross Arm | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P872093 | Pole | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P872282 | Other | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P872282 | Pole | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P872282 | Transformer | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P872491 | Pole | Tier 2 | Distribution | 2022-01-14 | N/A | N/A | N/A
P872498 | Pole | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P872510 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P872511 | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P872511 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P872530 | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P872532J | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P872866 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P872976 | Other | Tier 3 | Distribution | 2020-03-06 | N/A | N/A | N/A
P873012 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P873021 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P873063 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P873253J | Pole | Tier 2 | Distribution | 2021-11-30 | N/A | N/A | N/A
P873282 | Pole | Tier 2 | Distribution | 2021-11-30 | N/A | N/A | N/A
P873370 | Other | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P873517J | Pole | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P873522 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P873522 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P873524 | Insulator and Bushing | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P873524 | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P873524 | Transformer | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P873526 | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P873526 | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P873539 | Insulator and Bushing | Tier 2 | Distribution | 2021-12-14 | N/A | N/A | N/A
P873540 | Pole | Tier 2 | Distribution | 2022-05-29 | N/A | N/A | N/A
P873551J | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P873591 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P873787 | Anchor/Guy | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P873886J | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P873898 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P873898 | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P873906 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P874020 | Cross Arm | Tier 3 | Distribution | 2020-05-29 | N/A | N/A | N/A
P874034 | Pole | Tier 2 | Distribution | 2022-09-20 | N/A | N/A | N/A
P874046 | Insulator and Bushing | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P874118 | Pole | Tier 2 | Distribution | 2021-10-15 | N/A | N/A | N/A
P874247 | Other | Tier 3 | Distribution | 2020-03-17 | N/A | N/A | N/A
P874438 | Pole | Tier 2 | Distribution | 2022-09-20 | N/A | N/A | N/A
P874533 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P874536 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P874538 | Other | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P874564 | Cross Arm | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P874576 | Other | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P874596 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P874626 | Other | Tier 3 | Distribution | 2020-05-08 | N/A | N/A | N/A
P874648 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P874695 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P874696 | Other | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P874696 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P874795J | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P874808 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P874923 | Cross Arm | Tier 3 | Distribution | 2020-11-19 | N/A | N/A | N/A
P875083 | Transformer | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P875166 | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P875166 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P875263 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P875263 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P875374 | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P875374 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P875411 | Pole | Tier 2 | Distribution | 2021-09-03 | N/A | N/A | N/A
P875463 | Other | Tier 3 | Distribution | 2020-04-23 | N/A | N/A | N/A
P875485 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P875488 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P875504 | Anchor/Guy | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P875507 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P875520 | Pole | Tier 2 | Distribution | 2021-11-20 | N/A | N/A | N/A
P875622 | Pole | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P875645 | Pole | Tier 2 | Distribution | 2022-08-16 | N/A | N/A | N/A
P875779 | Pole | Tier 2 | Distribution | 2021-11-30 | N/A | N/A | N/A
P875817 | Anchor/Guy | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P875817 | Other | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P875817 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P875924 | Pole | Tier 2 | Distribution | 2022-11-30 | N/A | N/A | N/A
P875960 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P875962 | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P876183 | Pole | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P876190 | Pole | Tier 2 | Distribution | 2021-12-10 | N/A | N/A | N/A
P876243 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P876244 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P876355 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P876357 | Other | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P876357 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P876358 | Other | Tier 2 | Distribution | 2022-12-01 | N/A | N/A | N/A
P876424J | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P876445 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P876544 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P876545 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P876562 | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P876562 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P876636 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P876643 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P876643 | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P876643 | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P876682 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P876685 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P876694 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P876694 | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P876694 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P876710 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P876729J | Pole | Tier 2 | Distribution | 2021-11-30 | N/A | N/A | N/A
P876753 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P876803 | Transformer | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P876848 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P876849 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P876849 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P876854 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P876928 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P877009 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P877036 | Insulator and Bushing | Tier 2 | Distribution | 2021-12-03 | N/A | N/A | N/A
P877083 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P877190 | Pole | Tier 2 | Distribution | 2021-11-20 | N/A | N/A | N/A
P877191 | Pole | Tier 2 | Distribution | 2021-11-20 | N/A | N/A | N/A
P877213 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P877247 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P877309 | Other | Tier 2 | Distribution | 2022-12-01 | N/A | N/A | N/A
P877322 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P877390J | Cross Arm | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P877394 | Pole | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P877442 | Other | Tier 3 | Distribution | 2020-05-21 | N/A | N/A | N/A
P877447 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P877655 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P877681 | Insulator and Bushing | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P877681 | Other | Tier 2 | Distribution | 2022-08-09 | N/A | N/A | N/A
P877681 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P877693 | Cross Arm | Tier 3 | Distribution | 2022-12-02 | N/A | N/A | N/A
P877746 | Pole | Tier 2 | Distribution | 2021-11-19 | N/A | N/A | N/A
P877765 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P877771 | Other | Tier 3 | Distribution | 2020-11-10 | N/A | N/A | N/A
P877901 | Cross Arm | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P877901 | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P878051 | Cross Arm | Tier 2 | Distribution | 2022-10-31 | N/A | N/A | N/A
P878101 | Pole | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P878117 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P878342J | Pole | Tier 2 | Distribution | 2022-02-23 | N/A | N/A | N/A
P878444 | Other | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P878444 | Pole | Tier 2 | Distribution | 2022-07-11 | N/A | N/A | N/A
P878456 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P878456 | Pole | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
P878857 | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P878857 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P878859 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P878938 | Other | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P878938 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P878939 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P90093 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P90093 | Insulator and Bushing | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P90093 | Insulator and Bushing | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P90093 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P90098 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P90147 | Insulator and Bushing | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P90147 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P910020 | Cross Arm | Tier 2 | Distribution | 2022-02-22 | N/A | N/A | N/A
P91438 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P91442 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P918703J | Pole | Tier 2 | Distribution | 2022-04-22 | N/A | N/A | N/A
P919091 | Cross Arm | Tier 2 | Distribution | 2022-05-31 | N/A | N/A | N/A
P92652 | Transformer | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P970147 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P970187J | Pole | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P970419 | Other | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P970419 | Pole | Tier 2 | Distribution | 2021-11-07 | N/A | N/A | N/A
P970731 | Pole | Tier 2 | Distribution | 2021-11-24 | N/A | N/A | N/A
P970786 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P970809 | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P971009 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P971017 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P971093 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P971176 | Transformer | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P971211 | Pole | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P971559 | Cross Arm | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P971660 | Pole | Tier 2 | Distribution | 2021-11-13 | N/A | N/A | N/A
P971663 | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P971966 | Cross Arm | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
P972009 | Cross Arm | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P972082 | Cross Arm | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P972084 | Pole | Tier 2 | Distribution | 2021-12-17 | N/A | N/A | N/A
P972137 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P972140 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P972150 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P972342 | Pole | Tier 2 | Distribution | 2021-11-02 | N/A | N/A | N/A
P972386 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P972435 | Cross Arm | Tier 2 | Distribution | 2021-11-04 | N/A | N/A | N/A
P972447 | Transformer | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P972520 | Pole | Tier 2 | Distribution | 2021-12-28 | N/A | N/A | N/A
P972601 | Pole | Tier 2 | Distribution | 2021-11-30 | N/A | N/A | N/A
P972666 | Cross Arm | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P972666 | Other | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P972666 | Pole | Tier 2 | Distribution | 2021-10-29 | N/A | N/A | N/A
P972699 | Insulator and Bushing | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P972740 | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P972747 | Cross Arm | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P972749 | Insulator and Bushing | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P977008J | Other | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P977008J | Pole | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P977015J | Other | Tier 3 | Distribution | 2020-04-17 | N/A | N/A | N/A
P977039 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P977085J | Pole | Tier 2 | Distribution | 2022-09-27 | N/A | N/A | N/A
P977140 | Cross Arm | Tier 2 | Distribution | 2022-08-02 | N/A | N/A | N/A
P977152 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
P977153 | Pole | Tier 2 | Distribution | 2022-08-08 | N/A | N/A | N/A
Z10216 | Other | Tier 2 | Distribution | 2021-10-22 | N/A | N/A | N/A
Z118300 | Cross Arm | Tier 2 | Distribution | 2021-08-30 | N/A | N/A | N/A
Z11978 | Cross Arm | Tier 2 | Distribution | 2021-11-02 | N/A | N/A | N/A
Z16579 | Cross Arm | Tier 2 | Distribution | 2021-12-08 | N/A | N/A | N/A
Z181660 | Insulator and Bushing | Tier 2 | Distribution | 2021-10-09 | N/A | N/A | N/A
Z188630 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
Z188630 | Other | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
Z219781 | Cross Arm | Tier 2 | Distribution | 2022-03-10 | N/A | N/A | N/A
Z219792 | Cross Arm | Tier 2 | Distribution | 2022-03-09 | N/A | N/A | N/A
Z271532 | Other | Tier 2 | Distribution | 2022-12-19 | N/A | N/A | N/A
Z31759 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
Z31760 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
Z31761 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
Z31762 | Cross Arm | Tier 2 | Distribution | 2022-01-04 | N/A | N/A | N/A
Z416194 | Cross Arm | Tier 2 | Distribution | 2022-03-16 | N/A | N/A | N/A
100023531321 | Cross Arm | Tier 2 | Distribution | 2023-03-17 | N/A | N/A | N/A
100023536529 | Cross Arm | Tier 2 | Distribution | 2023-03-18 | N/A | N/A | N/A
100023555687 | Other | Tier 3 | Distribution | 2023-03-23 | N/A | N/A | N/A
100023555718 | Cross Arm | Tier 2 | Distribution | 2023-03-23 | N/A | N/A | N/A
100023598897 | Other | Tier 2 | Distribution | 2023-03-28 | N/A | N/A | N/A
100023598898 | Anchor/Guy | Tier 2 | Distribution | 2023-03-28 | N/A | N/A | N/A
100023598982 | Pole | Tier 3 | Distribution | 2023-03-28 | N/A | N/A | N/A
100023598983 | Other | Tier 3 | Distribution | 2023-03-28 | N/A | N/A | N/A
100023598986 | Cross Arm | Tier 3 | Distribution | 2023-03-28 | N/A | N/A | N/A
100023598987 | Pole | Tier 3 | Distribution | 2023-03-28 | N/A | N/A | N/A
100023608561 | Pole | Tier 2 | Distribution | 2023-03-30 | N/A | N/A | N/A
100023608567 | Other | Tier 2 | Distribution | 2023-03-30 | N/A | N/A | N/A
100023608572 | Other | Tier 2 | Distribution | 2023-03-30 | N/A | N/A | N/A
100023608573 | Other | Tier 2 | Distribution | 2023-03-30 | N/A | N/A | N/A
100023608574 | Other | Tier 2 | Distribution | 2023-03-30 | N/A | N/A | N/A
100023608576 | Other | Tier 2 | Distribution | 2023-03-30 | N/A | N/A | N/A
100023608587 | Pole | Tier 2 | Distribution | 2023-03-30 | N/A | N/A | N/A
100023643842 | Conductor | Tier 2 | Distribution | 2023-04-06 | N/A | N/A | N/A
100023643843 | Other | Tier 2 | Distribution | 2023-04-06 | N/A | N/A | N/A
100023643844 | Other | Tier 2 | Distribution | 2023-04-06 | N/A | N/A | N/A
100023643845 | Cross Arm | Tier 2 | Distribution | 2023-04-06 | N/A | N/A | N/A
100023644092 | Other | Tier 2 | Distribution | 2023-04-06 | N/A | N/A | N/A
100023644100 | Conductor | Tier 2 | Distribution | 2023-04-06 | N/A | N/A | N/A
100023644106 | Other | Tier 2 | Distribution | 2023-04-06 | N/A | N/A | N/A
100023644109 | Anchor/Guy | Tier 2 | Distribution | 2023-04-06 | N/A | N/A | N/A
100023644110 | Conductor | Tier 2 | Distribution | 2023-04-06 | N/A | N/A | N/A
100023644117 | Cross Arm | Tier 2 | Distribution | 2023-04-06 | N/A | N/A | N/A
100023644120 | Other | Tier 2 | Distribution | 2023-04-06 | N/A | N/A | N/A
100023644121 | Anchor/Guy | Tier 2 | Distribution | 2023-04-06 | N/A | N/A | N/A
100023644122 | Other | Tier 2 | Distribution | 2023-04-06 | N/A | N/A | N/A
100023644124 | Other | Tier 2 | Distribution | 2023-04-06 | N/A | N/A | N/A
100023644125 | Cross Arm | Tier 2 | Distribution | 2023-04-06 | N/A | N/A | N/A
100023644126 | Other | Tier 2 | Distribution | 2023-04-06 | N/A | N/A | N/A
100023644131 | Pole | Tier 2 | Distribution | 2023-04-06 | N/A | N/A | N/A
100023644133 | Pole | Tier 2 | Distribution | 2023-04-06 | N/A | N/A | N/A
100023644138 | Conductor | Tier 2 | Distribution | 2023-04-06 | N/A | N/A | N/A
100023644150 | Insulator and Bushing | Tier 2 | Distribution | 2023-04-06 | N/A | N/A | N/A
100023644152 | Other | Tier 2 | Distribution | 2023-04-06 | N/A | N/A | N/A
100023644166 | Conductor | Tier 2 | Distribution | 2023-04-06 | N/A | N/A | N/A
100023644204 | Cross Arm | Tier 2 | Distribution | 2023-04-06 | N/A | N/A | N/A
100023644207 | Pole | Tier 2 | Distribution | 2023-04-06 | N/A | N/A | N/A
100023644209 | Pole | Tier 2 | Distribution | 2023-04-06 | N/A | N/A | N/A
100023644210 | Other | Tier 2 | Distribution | 2023-04-06 | N/A | N/A | N/A
100023644216 | Pole | Tier 2 | Distribution | 2023-04-06 | N/A | N/A | N/A
100023649234 | Pole | Tier 3 | Distribution | 2023-04-07 | N/A | N/A | N/A
100023649275 | Pole | Tier 2 | Distribution | 2023-04-07 | N/A | N/A | N/A
100023653907 | Pole | Tier 3 | Distribution | 2023-04-08 | N/A | N/A | N/A
100023653911 | Pole | Tier 2 | Distribution | 2023-04-08 | N/A | N/A | N/A
100023653912 | Cross Arm | Tier 2 | Distribution | 2023-04-08 | N/A | N/A | N/A
100023653914 | Other | Tier 2 | Distribution | 2023-04-08 | N/A | N/A | N/A
100023653916 | Pole | Tier 2 | Distribution | 2023-04-08 | N/A | N/A | N/A
100023653919 | Cross Arm | Tier 2 | Distribution | 2023-04-08 | N/A | N/A | N/A
100023654860 | Pole | Tier 3 | Distribution | 2023-04-09 | N/A | N/A | N/A
100023654866 | Other | Tier 3 | Distribution | 2023-04-09 | N/A | N/A | N/A
100023654872 | Other | Tier 3 | Distribution | 2023-04-09 | N/A | N/A | N/A
100023654877 | Anchor/Guy | Tier 2 | Distribution | 2023-04-09 | N/A | N/A | N/A
100023654883 | Pole | Tier 2 | Distribution | 2023-04-09 | N/A | N/A | N/A
100023654888 | Anchor/Guy | Tier 2 | Distribution | 2023-04-09 | N/A | N/A | N/A
100023662365 | Anchor/Guy | Tier 2 | Distribution | 2023-04-11 | N/A | N/A | N/A
100023662373 | Other | Tier 2 | Distribution | 2023-04-11 | N/A | N/A | N/A
100023662374 | Other | Tier 2 | Distribution | 2023-04-11 | N/A | N/A | N/A
100023662392 | Other | Tier 2 | Distribution | 2023-04-11 | N/A | N/A | N/A
100023662411 | Other | Tier 2 | Distribution | 2023-04-11 | N/A | N/A | N/A
100023662412 | Cross Arm | Tier 2 | Distribution | 2023-04-11 | N/A | N/A | N/A
100023662415 | Cross Arm | Tier 2 | Distribution | 2023-04-11 | N/A | N/A | N/A
100023662426 | Pole | Tier 2 | Distribution | 2023-04-11 | N/A | N/A | N/A
100023662427 | Other | Tier 2 | Distribution | 2023-04-11 | N/A | N/A | N/A
100023662432 | Other | Tier 2 | Distribution | 2023-04-11 | N/A | N/A | N/A
100023662433 | Pole | Tier 2 | Distribution | 2023-04-11 | N/A | N/A | N/A
100023662437 | Pole | Tier 2 | Distribution | 2023-04-11 | N/A | N/A | N/A
100023662442 | Other | Tier 2 | Distribution | 2023-04-11 | N/A | N/A | N/A
100023662444 | Pole | Tier 2 | Distribution | 2023-04-11 | N/A | N/A | N/A
100023662460 | Pole | Tier 2 | Distribution | 2023-04-11 | N/A | N/A | N/A
100023662461 | Other | Tier 2 | Distribution | 2023-04-11 | N/A | N/A | N/A
100023662464 | Other | Tier 2 | Distribution | 2023-04-11 | N/A | N/A | N/A
100023662468 | Pole | Tier 2 | Distribution | 2023-04-11 | N/A | N/A | N/A
100023662471 | Pole | Tier 2 | Distribution | 2023-04-11 | N/A | N/A | N/A
100023671402 | Other | Tier 2 | Distribution | 2023-04-12 | N/A | N/A | N/A
100023671403 | Other | Tier 2 | Distribution | 2023-04-12 | N/A | N/A | N/A
100023671424 | Insulator and Bushing | Tier 2 | Distribution | 2023-04-12 | N/A | N/A | N/A
100023671427 | Anchor/Guy | Tier 2 | Distribution | 2023-04-12 | N/A | N/A | N/A
100023671446 | Other | Tier 2 | Distribution | 2023-04-12 | N/A | N/A | N/A
100023671467 | Anchor/Guy | Tier 2 | Distribution | 2023-04-12 | N/A | N/A | N/A
100023671491 | Cross Arm | Tier 2 | Distribution | 2023-04-12 | N/A | N/A | N/A
100023671492 | Cross Arm | Tier 2 | Distribution | 2023-04-12 | N/A | N/A | N/A
100023671494 | Other | Tier 2 | Distribution | 2023-04-12 | N/A | N/A | N/A
100023671496 | Cross Arm | Tier 2 | Distribution | 2023-04-12 | N/A | N/A | N/A
100023671497 | Other | Tier 2 | Distribution | 2023-04-12 | N/A | N/A | N/A
100023671498 | Insulator and Bushing | Tier 2 | Distribution | 2023-04-12 | N/A | N/A | N/A
100023671503 | Other | Tier 2 | Distribution | 2023-04-12 | N/A | N/A | N/A
100023671507 | Other | Tier 2 | Distribution | 2023-04-12 | N/A | N/A | N/A
100023683980 | Other | Tier 2 | Distribution | 2023-04-14 | N/A | N/A | N/A
100023683982 | Pole | Tier 2 | Distribution | 2023-04-14 | N/A | N/A | N/A
100023683983 | Other | Tier 2 | Distribution | 2023-04-14 | N/A | N/A | N/A
100023683990 | Anchor/Guy | Tier 2 | Distribution | 2023-04-14 | N/A | N/A | N/A
100023684001 | Pole | Tier 2 | Distribution | 2023-04-14 | N/A | N/A | N/A
100023684015 | Other | Tier 2 | Distribution | 2023-04-14 | N/A | N/A | N/A
100023684090 | Cross Arm | Tier 2 | Distribution | 2023-04-14 | N/A | N/A | N/A
100023684096 | Pole | Tier 2 | Distribution | 2023-04-14 | N/A | N/A | N/A
100023684099 | Other | Tier 2 | Distribution | 2023-04-14 | N/A | N/A | N/A
100023684106 | Pole | Tier 2 | Distribution | 2023-04-14 | N/A | N/A | N/A
100023684109 | Pole | Tier 2 | Distribution | 2023-04-14 | N/A | N/A | N/A
100023689196 | Other | Tier 2 | Distribution | 2023-04-15 | N/A | N/A | N/A
100023689212 | Conductor | Tier 2 | Distribution | 2023-04-15 | N/A | N/A | N/A
100023689213 | Insulator and Bushing | Tier 2 | Distribution | 2023-04-15 | N/A | N/A | N/A
100023689215 | Cross Arm | Tier 2 | Distribution | 2023-04-15 | N/A | N/A | N/A
100023689248 | Pole | Tier 3 | Distribution | 2023-04-15 | N/A | N/A | N/A
100023689303 | Pole | Tier 3 | Distribution | 2023-04-15 | N/A | N/A | N/A
100023689376 | Pole | Tier 2 | Distribution | 2023-04-15 | N/A | N/A | N/A
100023689379 | Pole | Tier 2 | Distribution | 2023-04-15 | N/A | N/A | N/A
100023689387 | Cross Arm | Tier 2 | Distribution | 2023-04-15 | N/A | N/A | N/A
100023689391 | Other | Tier 2 | Distribution | 2023-04-15 | N/A | N/A | N/A
100023689399 | Other | Tier 2 | Distribution | 2023-04-15 | N/A | N/A | N/A
100023689400 | Pole | Tier 2 | Distribution | 2023-04-15 | N/A | N/A | N/A
100023690660 | Pole | Tier 2 | Distribution | 2023-04-16 | N/A | N/A | N/A
100023690687 | Other | Tier 2 | Distribution | 2023-04-16 | N/A | N/A | N/A
100023690689 | Other | Tier 2 | Distribution | 2023-04-16 | N/A | N/A | N/A
100023690699 | Cross Arm | Tier 2 | Distribution | 2023-04-16 | N/A | N/A | N/A
100023690701 | Conductor | Tier 2 | Distribution | 2023-04-16 | N/A | N/A | N/A
100023690704 | Other | Tier 2 | Distribution | 2023-04-16 | N/A | N/A | N/A
100023690717 | Cross Arm | Tier 2 | Distribution | 2023-04-16 | N/A | N/A | N/A
100023690723 | Other | Tier 2 | Distribution | 2023-04-16 | N/A | N/A | N/A
100023690724 | Pole | Tier 2 | Distribution | 2023-04-16 | N/A | N/A | N/A
100023690725 | Pole | Tier 2 | Distribution | 2023-04-16 | N/A | N/A | N/A
100023690736 | Other | Tier 2 | Distribution | 2023-04-16 | N/A | N/A | N/A
100023697380 | Pole | Tier 2 | Distribution | 2023-04-18 | N/A | N/A | N/A
100023697388 | Pole | Tier 2 | Distribution | 2023-04-18 | N/A | N/A | N/A
100023697403 | Insulator and Bushing | Tier 2 | Distribution | 2023-04-18 | N/A | N/A | N/A
100023697408 | Other | Tier 2 | Distribution | 2023-04-18 | N/A | N/A | N/A
100023697432 | Anchor/Guy | Tier 2 | Distribution | 2023-04-18 | N/A | N/A | N/A
100023697433 | Cross Arm | Tier 2 | Distribution | 2023-04-18 | N/A | N/A | N/A
100023697438 | Cross Arm | Tier 2 | Distribution | 2023-04-18 | N/A | N/A | N/A
100023697445 | Pole | Tier 2 | Distribution | 2023-04-18 | N/A | N/A | N/A
100023707515 | Other | Tier 2 | Distribution | 2023-04-19 | N/A | N/A | N/A
100023707527 | Other | Tier 2 | Distribution | 2023-04-19 | N/A | N/A | N/A
100023707534 | Other | Tier 2 | Distribution | 2023-04-19 | N/A | N/A | N/A
100023707536 | Conductor | Tier 2 | Distribution | 2023-04-19 | N/A | N/A | N/A
100023707537 | Other | Tier 2 | Distribution | 2023-04-19 | N/A | N/A | N/A
100023707538 | Other | Tier 2 | Distribution | 2023-04-19 | N/A | N/A | N/A
100023707543 | Anchor/Guy | Tier 2 | Distribution | 2023-04-19 | N/A | N/A | N/A
100023707573 | Cross Arm | Tier 2 | Distribution | 2023-04-19 | N/A | N/A | N/A
100023707574 | Other | Tier 2 | Distribution | 2023-04-19 | N/A | N/A | N/A
100023707580 | Pole | Tier 2 | Distribution | 2023-04-19 | N/A | N/A | N/A
100023707581 | Other | Tier 2 | Distribution | 2023-04-19 | N/A | N/A | N/A
100023707597 | Pole | Tier 3 | Distribution | 2023-04-19 | N/A | N/A | N/A
100023707598 | Pole | Tier 3 | Distribution | 2023-04-19 | N/A | N/A | N/A
100023707599 | Cross Arm | Tier 3 | Distribution | 2023-04-19 | N/A | N/A | N/A
100023707600 | Pole | Tier 3 | Distribution | 2023-04-19 | N/A | N/A | N/A
100023707615 | Other | Tier 2 | Distribution | 2023-04-19 | N/A | N/A | N/A
100023707616 | Cross Arm | Tier 2 | Distribution | 2023-04-19 | N/A | N/A | N/A
100023707633 | Other | Tier 2 | Distribution | 2023-04-19 | N/A | N/A | N/A
100023707637 | Pole | Tier 3 | Distribution | 2023-04-19 | N/A | N/A | N/A
100023707638 | Other | Tier 3 | Distribution | 2023-04-19 | N/A | N/A | N/A
100023707647 | Pole | Tier 3 | Distribution | 2023-04-19 | N/A | N/A | N/A
100023707648 | Pole | Tier 3 | Distribution | 2023-04-19 | N/A | N/A | N/A
100023707653 | Pole | Tier 3 | Distribution | 2023-04-19 | N/A | N/A | N/A
100023707657 | Other | Tier 3 | Distribution | 2023-04-19 | N/A | N/A | N/A
100023707659 | Pole | Tier 3 | Distribution | 2023-04-19 | N/A | N/A | N/A
100023712270 | Pole | Tier 2 | Distribution | 2023-04-20 | N/A | N/A | N/A
100023712312 | Other | Tier 2 | Distribution | 2023-04-20 | N/A | N/A | N/A
100023712313 | Pole | Tier 2 | Distribution | 2023-04-20 | N/A | N/A | N/A
100023712317 | Other | Tier 2 | Distribution | 2023-04-20 | N/A | N/A | N/A
100023712319 | Cross Arm | Tier 2 | Distribution | 2023-04-20 | N/A | N/A | N/A
100023712338 | Pole | Tier 2 | Distribution | 2023-04-20 | N/A | N/A | N/A
100023712340 | Pole | Tier 2 | Distribution | 2023-04-20 | N/A | N/A | N/A
100023712373 | Pole | Tier 2 | Distribution | 2023-04-20 | N/A | N/A | N/A
100023712374 | Cross Arm | Tier 2 | Distribution | 2023-04-20 | N/A | N/A | N/A
100023712375 | Pole | Tier 2 | Distribution | 2023-04-20 | N/A | N/A | N/A
100023712380 | Other | Tier 2 | Distribution | 2023-04-20 | N/A | N/A | N/A
100023712386 | Other | Tier 2 | Distribution | 2023-04-20 | N/A | N/A | N/A
100023712388 | Pole | Tier 2 | Distribution | 2023-04-20 | N/A | N/A | N/A
100023712391 | Cross Arm | Tier 2 | Distribution | 2023-04-20 | N/A | N/A | N/A
100023712413 | Pole | Tier 2 | Distribution | 2023-04-20 | N/A | N/A | N/A
100023712423 | Pole | Tier 2 | Distribution | 2023-04-20 | N/A | N/A | N/A
100023712426 | Insulator and Bushing | Tier 2 | Distribution | 2023-04-20 | N/A | N/A | N/A
100023712427 | Other | Tier 2 | Distribution | 2023-04-20 | N/A | N/A | N/A
100023712435 | Cross Arm | Tier 2 | Distribution | 2023-04-20 | N/A | N/A | N/A
100023716687 | Other | Tier 3 | Distribution | 2023-04-21 | N/A | N/A | N/A
100023716688 | Pole | Tier 3 | Distribution | 2023-04-21 | N/A | N/A | N/A
100023716704 | Pole | Tier 3 | Distribution | 2023-04-21 | N/A | N/A | N/A
100023716712 | Pole | Tier 3 | Distribution | 2023-04-21 | N/A | N/A | N/A
100023719379 | Other | Tier 2 | Distribution | 2023-04-22 | N/A | N/A | N/A
100023721049 | Pole | Tier 2 | Distribution | 2023-04-22 | N/A | N/A | N/A
100023721050 | Other | Tier 2 | Distribution | 2023-04-22 | N/A | N/A | N/A
100023721051 | Cross Arm | Tier 2 | Distribution | 2023-04-22 | N/A | N/A | N/A
100023721053 | Other | Tier 2 | Distribution | 2023-04-22 | N/A | N/A | N/A
100023721054 | Other | Tier 2 | Distribution | 2023-04-22 | N/A | N/A | N/A
100023721064 | Pole | Tier 2 | Distribution | 2023-04-22 | N/A | N/A | N/A
100023721074 | Other | Tier 2 | Distribution | 2023-04-22 | N/A | N/A | N/A
100023721083 | Conductor | Tier 2 | Distribution | 2023-04-22 | N/A | N/A | N/A
100023721086 | Other | Tier 2 | Distribution | 2023-04-22 | N/A | N/A | N/A
100023721091 | Anchor/Guy | Tier 2 | Distribution | 2023-04-22 | N/A | N/A | N/A
100023721093 | Anchor/Guy | Tier 2 | Distribution | 2023-04-22 | N/A | N/A | N/A
100023721095 | Anchor/Guy | Tier 2 | Distribution | 2023-04-22 | N/A | N/A | N/A
100023721112 | Insulator and Bushing | Tier 3 | Distribution | 2023-04-22 | N/A | N/A | N/A
100023721113 | Cross Arm | Tier 3 | Distribution | 2023-04-22 | N/A | N/A | N/A
100023721114 | Anchor/Guy | Tier 3 | Distribution | 2023-04-22 | N/A | N/A | N/A
100023721128 | Insulator and Bushing | Tier 2 | Distribution | 2023-04-22 | N/A | N/A | N/A
100023721585 | Cross Arm | Tier 2 | Distribution | 2023-04-23 | N/A | N/A | N/A
100023721652 | Cross Arm | Tier 2 | Distribution | 2023-04-23 | N/A | N/A | N/A
100023721679 | Conductor | Tier 2 | Distribution | 2023-04-23 | N/A | N/A | N/A
100023721706 | Cross Arm | Tier 2 | Distribution | 2023-04-23 | N/A | N/A | N/A
100023721828 | Cross Arm | Tier 2 | Distribution | 2023-04-23 | N/A | N/A | N/A
100023722080 | Cross Arm | Tier 2 | Distribution | 2023-04-23 | N/A | N/A | N/A
100023722086 | Anchor/Guy | Tier 2 | Distribution | 2023-04-23 | N/A | N/A | N/A
100023722088 | Other | Tier 2 | Distribution | 2023-04-23 | N/A | N/A | N/A
100023722090 | Other | Tier 2 | Distribution | 2023-04-23 | N/A | N/A | N/A
100023722101 | Insulator and Bushing | Tier 2 | Distribution | 2023-04-23 | N/A | N/A | N/A
100023722105 | Other | Tier 2 | Distribution | 2023-04-23 | N/A | N/A | N/A
100023722106 | Conductor | Tier 2 | Distribution | 2023-04-23 | N/A | N/A | N/A
100023722111 | Cross Arm | Tier 2 | Distribution | 2023-04-23 | N/A | N/A | N/A
100023722113 | Other | Tier 2 | Distribution | 2023-04-23 | N/A | N/A | N/A
100023722118 | Conductor | Tier 2 | Distribution | 2023-04-23 | N/A | N/A | N/A
100023722121 | Anchor/Guy | Tier 2 | Distribution | 2023-04-23 | N/A | N/A | N/A
100023722122 | Other | Tier 2 | Distribution | 2023-04-23 | N/A | N/A | N/A
100023722133 | Pole | Tier 2 | Distribution | 2023-04-23 | N/A | N/A | N/A
100023722146 | Pole | Tier 2 | Distribution | 2023-04-23 | N/A | N/A | N/A
100023722152 | Cross Arm | Tier 2 | Distribution | 2023-04-23 | N/A | N/A | N/A
100023722155 | Other | Tier 2 | Distribution | 2023-04-23 | N/A | N/A | N/A
100023722160 | Anchor/Guy | Tier 2 | Distribution | 2023-04-23 | N/A | N/A | N/A
100023722190 | Anchor/Guy | Tier 2 | Distribution | 2023-04-23 | N/A | N/A | N/A
100023722194 | Pole | Tier 2 | Distribution | 2023-04-23 | N/A | N/A | N/A
100023722196 | Pole | Tier 2 | Distribution | 2023-04-23 | N/A | N/A | N/A
100023722197 | Other | Tier 2 | Distribution | 2023-04-23 | N/A | N/A | N/A
100023722200 | Other | Tier 2 | Distribution | 2023-04-23 | N/A | N/A | N/A
100023745562 | Pole | Tier 2 | Distribution | 2023-04-25 | N/A | N/A | N/A
100023745600 | Conductor | Tier 2 | Distribution | 2023-04-25 | N/A | N/A | N/A
100023745621 | Other | Tier 2 | Distribution | 2023-04-25 | N/A | N/A | N/A
100023745623 | Conductor | Tier 2 | Distribution | 2023-04-25 | N/A | N/A | N/A
100023756473 | Anchor/Guy | Tier 2 | Distribution | 2023-04-26 | N/A | N/A | N/A
100023756474 | Anchor/Guy | Tier 2 | Distribution | 2023-04-26 | N/A | N/A | N/A
100023756479 | Anchor/Guy | Tier 2 | Distribution | 2023-04-26 | N/A | N/A | N/A
100023761851 | Pole | Tier 2 | Distribution | 2023-04-27 | N/A | N/A | N/A
100023761860 | Cross Arm | Tier 2 | Distribution | 2023-04-27 | N/A | N/A | N/A
100023761863 | Pole | Tier 2 | Distribution | 2023-04-27 | N/A | N/A | N/A
100023761864 | Pole | Tier 2 | Distribution | 2023-04-27 | N/A | N/A | N/A
100023761866 | Other | Tier 2 | Distribution | 2023-04-27 | N/A | N/A | N/A
100023761867 | Other | Tier 2 | Distribution | 2023-04-27 | N/A | N/A | N/A
100023761869 | Other | Tier 2 | Distribution | 2023-04-27 | N/A | N/A | N/A
100023761872 | Cross Arm | Tier 2 | Distribution | 2023-04-27 | N/A | N/A | N/A
100023761874 | Other | Tier 2 | Distribution | 2023-04-27 | N/A | N/A | N/A
100023761875 | Other | Tier 2 | Distribution | 2023-04-27 | N/A | N/A | N/A
100023767011 | Pole | Tier 2 | Distribution | 2023-04-28 | N/A | N/A | N/A
100023767012 | Other | Tier 2 | Distribution | 2023-04-28 | N/A | N/A | N/A
100023767014 | Cross Arm | Tier 2 | Distribution | 2023-04-28 | N/A | N/A | N/A
100023767015 | Other | Tier 2 | Distribution | 2023-04-28 | N/A | N/A | N/A
100023767028 | Cross Arm | Tier 2 | Distribution | 2023-04-28 | N/A | N/A | N/A
100023767055 | Cross Arm | Tier 2 | Distribution | 2023-04-28 | N/A | N/A | N/A
100023767066 | Conductor | Tier 2 | Distribution | 2023-04-28 | N/A | N/A | N/A
100023767072 | Conductor | Tier 2 | Distribution | 2023-04-28 | N/A | N/A | N/A
100023767076 | Insulator and Bushing | Tier 2 | Distribution | 2023-04-28 | N/A | N/A | N/A
100023767097 | Other | Tier 2 | Distribution | 2023-04-28 | N/A | N/A | N/A
100023767100 | Other | Tier 2 | Distribution | 2023-04-28 | N/A | N/A | N/A
100023767101 | Anchor/Guy | Tier 2 | Distribution | 2023-04-28 | N/A | N/A | N/A
100023767107 | Other | Tier 2 | Distribution | 2023-04-28 | N/A | N/A | N/A
100023767108 | Cross Arm | Tier 2 | Distribution | 2023-04-28 | N/A | N/A | N/A
100023772949 | Cross Arm | Tier 2 | Distribution | 2023-04-30 | N/A | N/A | N/A
100023773566 | Other | Tier 2 | Distribution | 2023-04-30 | N/A | N/A | N/A
100023773570 | Other | Tier 2 | Distribution | 2023-04-30 | N/A | N/A | N/A
100023773584 | Pole | Tier 2 | Distribution | 2023-04-30 | N/A | N/A | N/A
100023773586 | Other | Tier 2 | Distribution | 2023-04-30 | N/A | N/A | N/A
100023792904 | Other | Tier 2 | Distribution | 2023-05-03 | N/A | N/A | N/A
100023792907 | Cross Arm | Tier 2 | Distribution | 2023-05-03 | N/A | N/A | N/A
100023792908 | Cross Arm | Tier 2 | Distribution | 2023-05-03 | N/A | N/A | N/A
100023792909 | Anchor/Guy | Tier 2 | Distribution | 2023-05-03 | N/A | N/A | N/A
100023792912 | Cross Arm | Tier 2 | Distribution | 2023-05-03 | N/A | N/A | N/A
100023792917 | Other | Tier 2 | Distribution | 2023-05-03 | N/A | N/A | N/A
100023792921 | Cross Arm | Tier 2 | Distribution | 2023-05-03 | N/A | N/A | N/A
100023792923 | Cross Arm | Tier 2 | Distribution | 2023-05-03 | N/A | N/A | N/A
100023792931 | Cross Arm | Tier 2 | Distribution | 2023-05-03 | N/A | N/A | N/A
100023792933 | Anchor/Guy | Tier 2 | Distribution | 2023-05-03 | N/A | N/A | N/A
100023792934 | Pole | Tier 2 | Distribution | 2023-05-03 | N/A | N/A | N/A
100023792942 | Pole | Tier 2 | Distribution | 2023-05-03 | N/A | N/A | N/A
100023792951 | Other | Tier 2 | Distribution | 2023-05-03 | N/A | N/A | N/A
100023792953 | Pole | Tier 2 | Distribution | 2023-05-03 | N/A | N/A | N/A
100023792955 | Pole | Tier 2 | Distribution | 2023-05-03 | N/A | N/A | N/A
100023792962 | Pole | Tier 2 | Distribution | 2023-05-03 | N/A | N/A | N/A
100023792983 | Insulator and Bushing | Tier 2 | Distribution | 2023-05-03 | N/A | N/A | N/A
100023797589 | Other | Tier 2 | Distribution | 2023-05-04 | N/A | N/A | N/A
100023797602 | Other | Tier 2 | Distribution | 2023-05-04 | N/A | N/A | N/A
100023797603 | Cross Arm | Tier 2 | Distribution | 2023-05-04 | N/A | N/A | N/A
100023797606 | Cross Arm | Tier 2 | Distribution | 2023-05-04 | N/A | N/A | N/A
100023797649 | Other | Tier 2 | Distribution | 2023-05-04 | N/A | N/A | N/A
100023797652 | Anchor/Guy | Tier 2 | Distribution | 2023-05-04 | N/A | N/A | N/A
100023797654 | Other | Tier 2 | Distribution | 2023-05-04 | N/A | N/A | N/A
100023797655 | Cross Arm | Tier 2 | Distribution | 2023-05-04 | N/A | N/A | N/A
100023802799 | Other | Tier 2 | Distribution | 2023-05-05 | N/A | N/A | N/A
100023803383 | Cross Arm | Tier 2 | Distribution | 2023-05-05 | N/A | N/A | N/A
100023803384 | Pole | Tier 2 | Distribution | 2023-05-05 | N/A | N/A | N/A
100023803388 | Pole | Tier 2 | Distribution | 2023-05-05 | N/A | N/A | N/A
100023803395 | Insulator and Bushing | Tier 2 | Distribution | 2023-05-05 | N/A | N/A | N/A
100023803414 | Other | Tier 2 | Distribution | 2023-05-05 | N/A | N/A | N/A
100023803418 | Cross Arm | Tier 2 | Distribution | 2023-05-05 | N/A | N/A | N/A
100023803425 | Conductor | Tier 2 | Distribution | 2023-05-05 | N/A | N/A | N/A
100023803430 | Anchor/Guy | Tier 2 | Distribution | 2023-05-05 | N/A | N/A | N/A
100023803434 | Insulator and Bushing | Tier 2 | Distribution | 2023-05-05 | N/A | N/A | N/A
100023803448 | Pole | Tier 2 | Distribution | 2023-05-05 | N/A | N/A | N/A
100023803452 | Other | Tier 2 | Distribution | 2023-05-05 | N/A | N/A | N/A
100023803463 | Pole | Tier 2 | Distribution | 2023-05-05 | N/A | N/A | N/A
100023808432 | Other | Tier 2 | Distribution | 2023-05-06 | N/A | N/A | N/A
100023808440 | Cross Arm | Tier 2 | Distribution | 2023-05-06 | N/A | N/A | N/A
100023808444 | Pole | Tier 2 | Distribution | 2023-05-06 | N/A | N/A | N/A
100023808447 | Cross Arm | Tier 2 | Distribution | 2023-05-06 | N/A | N/A | N/A
100023808448 | Cross Arm | Tier 2 | Distribution | 2023-05-06 | N/A | N/A | N/A
100023808454 | Other | Tier 2 | Distribution | 2023-05-06 | N/A | N/A | N/A
100023808462 | Other | Tier 2 | Distribution | 2023-05-06 | N/A | N/A | N/A
100023808468 | Other | Tier 2 | Distribution | 2023-05-06 | N/A | N/A | N/A
100023808471 | Other | Tier 2 | Distribution | 2023-05-06 | N/A | N/A | N/A
100023808481 | Other | Tier 2 | Distribution | 2023-05-06 | N/A | N/A | N/A
100023808485 | Other | Tier 2 | Distribution | 2023-05-06 | N/A | N/A | N/A
100023808486 | Conductor | Tier 2 | Distribution | 2023-05-06 | N/A | N/A | N/A
100023808489 | Conductor | Tier 2 | Distribution | 2023-05-06 | N/A | N/A | N/A
100023808802 | Cross Arm | Tier 2 | Distribution | 2023-05-05 | N/A | N/A | N/A
100023815007 | Cross Arm | Tier 2 | Distribution | 2023-05-09 | N/A | N/A | N/A
100023820085 | Conductor | Tier 2 | Distribution | 2023-05-09 | N/A | N/A | N/A
100023820087 | Other | Tier 2 | Distribution | 2023-05-09 | N/A | N/A | N/A
100023820089 | Other | Tier 2 | Distribution | 2023-05-09 | N/A | N/A | N/A
100023820090 | Other | Tier 2 | Distribution | 2023-05-09 | N/A | N/A | N/A
100023820091 | Conductor | Tier 2 | Distribution | 2023-05-09 | N/A | N/A | N/A
100023820098 | Other | Tier 2 | Distribution | 2023-05-09 | N/A | N/A | N/A
100023820105 | Anchor/Guy | Tier 2 | Distribution | 2023-05-09 | N/A | N/A | N/A
100023820109 | Insulator and Bushing | Tier 2 | Distribution | 2023-05-09 | N/A | N/A | N/A
100023820119 | Pole | Tier 2 | Distribution | 2023-05-09 | N/A | N/A | N/A
100023820120 | Conductor | Tier 2 | Distribution | 2023-05-09 | N/A | N/A | N/A
100023820121 | Other | Tier 2 | Distribution | 2023-05-09 | N/A | N/A | N/A
100023820846 | Other | Tier 2 | Distribution | 2023-05-04 | N/A | N/A | N/A
100023825048 | Other | Tier 2 | Distribution | 2023-05-10 | N/A | N/A | N/A
100023825816 | Insulator and Bushing | Tier 2 | Distribution | 2023-05-10 | N/A | N/A | N/A
100023825817 | Insulator and Bushing | Tier 2 | Distribution | 2023-05-10 | N/A | N/A | N/A
100023825821 | Other | Tier 2 | Distribution | 2023-05-10 | N/A | N/A | N/A
100023825837 | Other | Tier 2 | Distribution | 2023-05-10 | N/A | N/A | N/A
100023825843 | Other | Tier 2 | Distribution | 2023-05-10 | N/A | N/A | N/A
100023825852 | Other | Tier 2 | Distribution | 2023-05-10 | N/A | N/A | N/A
100023825853 | Pole | Tier 2 | Distribution | 2023-05-10 | N/A | N/A | N/A
100023825870 | Other | Tier 2 | Distribution | 2023-05-10 | N/A | N/A | N/A
100023825881 | Other | Tier 2 | Distribution | 2023-05-10 | N/A | N/A | N/A
100023825884 | Other | Tier 2 | Distribution | 2023-05-10 | N/A | N/A | N/A
100023825885 | Other | Tier 2 | Distribution | 2023-05-10 | N/A | N/A | N/A
100023825886 | Pole | Tier 2 | Distribution | 2023-05-10 | N/A | N/A | N/A
100023825887 | Anchor/Guy | Tier 2 | Distribution | 2023-05-10 | N/A | N/A | N/A
100023825891 | Other | Tier 2 | Distribution | 2023-05-10 | N/A | N/A | N/A
100023825893 | Other | Tier 2 | Distribution | 2023-05-10 | N/A | N/A | N/A
100023825896 | Pole | Tier 2 | Distribution | 2023-05-10 | N/A | N/A | N/A
100023825902 | Pole | Tier 2 | Distribution | 2023-05-10 | N/A | N/A | N/A
100023825907 | Other | Tier 2 | Distribution | 2023-05-10 | N/A | N/A | N/A
100023825908 | Other | Tier 2 | Distribution | 2023-05-10 | N/A | N/A | N/A
100023831598 | Cross Arm | Tier 2 | Distribution | 2023-05-11 | N/A | N/A | N/A
100023831930 | Anchor/Guy | Tier 2 | Distribution | 2023-05-11 | N/A | N/A | N/A
100023831938 | Other | Tier 2 | Distribution | 2023-05-11 | N/A | N/A | N/A
100023837581 | Other | Tier 3 | Distribution | 2023-05-12 | N/A | N/A | N/A
100023837583 | Other | Tier 3 | Distribution | 2023-05-12 | N/A | N/A | N/A
100023837596 | Pole | Tier 3 | Distribution | 2023-05-12 | N/A | N/A | N/A
100023837604 | Other | Tier 3 | Distribution | 2023-05-12 | N/A | N/A | N/A
100023837625 | Other | Tier 2 | Distribution | 2023-05-12 | N/A | N/A | N/A
100023837627 | Conductor | Tier 2 | Distribution | 2023-05-12 | N/A | N/A | N/A
100023837628 | Other | Tier 2 | Distribution | 2023-05-12 | N/A | N/A | N/A
100023837629 | Cross Arm | Tier 2 | Distribution | 2023-05-12 | N/A | N/A | N/A
100023837630 | Other | Tier 2 | Distribution | 2023-05-12 | N/A | N/A | N/A
100023837633 | Other | Tier 2 | Distribution | 2023-05-12 | N/A | N/A | N/A
100023837634 | Other | Tier 3 | Distribution | 2023-05-12 | N/A | N/A | N/A
100023837647 | Cross Arm | Tier 3 | Distribution | 2023-05-12 | N/A | N/A | N/A
100023837650 | Conductor | Tier 3 | Distribution | 2023-05-12 | N/A | N/A | N/A
100023837659 | Cross Arm | Tier 2 | Distribution | 2023-05-12 | N/A | N/A | N/A
100023837663 | Other | Tier 2 | Distribution | 2023-05-12 | N/A | N/A | N/A
100023837674 | Pole | Tier 2 | Distribution | 2023-05-12 | N/A | N/A | N/A
100023837675 | Other | Tier 2 | Distribution | 2023-05-12 | N/A | N/A | N/A
100023837677 | Pole | Tier 2 | Distribution | 2023-05-12 | N/A | N/A | N/A
100023837678 | Cross Arm | Tier 2 | Distribution | 2023-05-12 | N/A | N/A | N/A
100023840805 | Cross Arm | Tier 3 | Distribution | 2023-05-13 | N/A | N/A | N/A
100023842634 | Anchor/Guy | Tier 3 | Distribution | 2023-05-13 | N/A | N/A | N/A
100023842640 | Cross Arm | Tier 3 | Distribution | 2023-05-13 | N/A | N/A | N/A
100023846646 | Cross Arm | Tier 2 | Distribution | 2023-05-15 | N/A | N/A | N/A
100023848355 | Other | Tier 2 | Distribution | 2023-05-15 | N/A | N/A | N/A
100023848357 | Pole | Tier 2 | Distribution | 2023-05-15 | N/A | N/A | N/A
100023848359 | Other | Tier 2 | Distribution | 2023-05-15 | N/A | N/A | N/A
100023848360 | Pole | Tier 2 | Distribution | 2023-05-15 | N/A | N/A | N/A
100023848362 | Other | Tier 2 | Distribution | 2023-05-15 | N/A | N/A | N/A
100023848363 | Other | Tier 2 | Distribution | 2023-05-15 | N/A | N/A | N/A
100023848364 | Cross Arm | Tier 2 | Distribution | 2023-05-15 | N/A | N/A | N/A
100023848368 | Conductor | Tier 2 | Distribution | 2023-05-15 | N/A | N/A | N/A
100023848369 | Pole | Tier 2 | Distribution | 2023-05-15 | N/A | N/A | N/A
100023848372 | Pole | Tier 2 | Distribution | 2023-05-15 | N/A | N/A | N/A
100023848373 | Cross Arm | Tier 2 | Distribution | 2023-05-15 | N/A | N/A | N/A
100023848379 | Pole | Tier 2 | Distribution | 2023-05-15 | N/A | N/A | N/A
100023848380 | Conductor | Tier 2 | Distribution | 2023-05-15 | N/A | N/A | N/A
100023848386 | Cross Arm | Tier 2 | Distribution | 2023-05-15 | N/A | N/A | N/A
100023848389 | Other | Tier 2 | Distribution | 2023-05-15 | N/A | N/A | N/A
100023848393 | Cross Arm | Tier 2 | Distribution | 2023-05-15 | N/A | N/A | N/A
100023848402 | Other | Tier 2 | Distribution | 2023-05-15 | N/A | N/A | N/A
100023848405 | Anchor/Guy | Tier 2 | Distribution | 2023-05-15 | N/A | N/A | N/A
100023848409 | Pole | Tier 2 | Distribution | 2023-05-15 | N/A | N/A | N/A
100023848414 | Pole | Tier 2 | Distribution | 2023-05-15 | N/A | N/A | N/A
100023848417 | Other | Tier 2 | Distribution | 2023-05-15 | N/A | N/A | N/A
100023848418 | Other | Tier 2 | Distribution | 2023-05-15 | N/A | N/A | N/A
100023848420 | Cross Arm | Tier 2 | Distribution | 2023-05-15 | N/A | N/A | N/A
100023848422 | Other | Tier 2 | Distribution | 2023-05-15 | N/A | N/A | N/A
100023848423 | Other | Tier 2 | Distribution | 2023-05-15 | N/A | N/A | N/A
100023848425 | Other | Tier 2 | Distribution | 2023-05-15 | N/A | N/A | N/A
100023848433 | Other | Tier 2 | Distribution | 2023-05-15 | N/A | N/A | N/A
100023854997 | Cross Arm | Tier 2 | Distribution | 2023-05-16 | N/A | N/A | N/A
100023854998 | Cross Arm | Tier 2 | Distribution | 2023-05-16 | N/A | N/A | N/A
100023854999 | Anchor/Guy | Tier 2 | Distribution | 2023-05-16 | N/A | N/A | N/A
100023855004 | Conductor | Tier 2 | Distribution | 2023-05-16 | N/A | N/A | N/A
100023855006 | Pole | Tier 2 | Distribution | 2023-05-16 | N/A | N/A | N/A
100023855009 | Pole | Tier 2 | Distribution | 2023-05-16 | N/A | N/A | N/A
100023855012 | Other | Tier 2 | Distribution | 2023-05-16 | N/A | N/A | N/A
100023855014 | Pole | Tier 2 | Distribution | 2023-05-16 | N/A | N/A | N/A
100023855021 | Other | Tier 2 | Distribution | 2023-05-16 | N/A | N/A | N/A
100023855027 | Cross Arm | Tier 2 | Distribution | 2023-05-16 | N/A | N/A | N/A
100023855030 | Other | Tier 2 | Distribution | 2023-05-16 | N/A | N/A | N/A
100023855039 | Pole | Tier 2 | Distribution | 2023-05-16 | N/A | N/A | N/A
100023855042 | Pole | Tier 2 | Distribution | 2023-05-16 | N/A | N/A | N/A
100023855043 | Pole | Tier 2 | Distribution | 2023-05-16 | N/A | N/A | N/A
100023855050 | Other | Tier 2 | Distribution | 2023-05-16 | N/A | N/A | N/A
100023855051 | Pole | Tier 2 | Distribution | 2023-05-16 | N/A | N/A | N/A
100023855053 | Other | Tier 2 | Distribution | 2023-05-16 | N/A | N/A | N/A
100023855056 | Other | Tier 2 | Distribution | 2023-05-16 | N/A | N/A | N/A
100023855057 | Anchor/Guy | Tier 2 | Distribution | 2023-05-16 | N/A | N/A | N/A
100023855059 | Other | Tier 2 | Distribution | 2023-05-16 | N/A | N/A | N/A
100023855061 | Anchor/Guy | Tier 2 | Distribution | 2023-05-16 | N/A | N/A | N/A
100023855062 | Cross Arm | Tier 2 | Distribution | 2023-05-16 | N/A | N/A | N/A
100023859663 | Anchor/Guy | Tier 2 | Distribution | 2023-05-17 | N/A | N/A | N/A
100023859672 | Pole | Tier 3 | Distribution | 2023-05-17 | N/A | N/A | N/A
100023859674 | Cross Arm | Tier 3 | Distribution | 2023-05-17 | N/A | N/A | N/A
100023859685 | Other | Tier 2 | Distribution | 2023-05-17 | N/A | N/A | N/A
100023859686 | Anchor/Guy | Tier 2 | Distribution | 2023-05-17 | N/A | N/A | N/A
100023859688 | Other | Tier 2 | Distribution | 2023-05-17 | N/A | N/A | N/A
100023859693 | Other | Tier 2 | Distribution | 2023-05-17 | N/A | N/A | N/A
100023859694 | Other | Tier 2 | Distribution | 2023-05-17 | N/A | N/A | N/A
100023859704 | Other | Tier 2 | Distribution | 2023-05-17 | N/A | N/A | N/A
100023859705 | Other | Tier 2 | Distribution | 2023-05-17 | N/A | N/A | N/A
100023859714 | Pole | Tier 2 | Distribution | 2023-05-17 | N/A | N/A | N/A
100023859735 | Cross Arm | Tier 3 | Distribution | 2023-05-17 | N/A | N/A | N/A
100023859742 | Cross Arm | Tier 2 | Distribution | 2023-05-17 | N/A | N/A | N/A
100023859751 | Pole | Tier 2 | Distribution | 2023-05-17 | N/A | N/A | N/A
100023859752 | Other | Tier 2 | Distribution | 2023-05-17 | N/A | N/A | N/A
100023859753 | Other | Tier 2 | Distribution | 2023-05-17 | N/A | N/A | N/A
100023859754 | Insulator and Bushing | Tier 2 | Distribution | 2023-05-17 | N/A | N/A | N/A
100023865018 | Pole | Tier 2 | Distribution | 2023-05-18 | N/A | N/A | N/A
100023865019 | Cross Arm | Tier 2 | Distribution | 2023-05-18 | N/A | N/A | N/A
100023865026 | Pole | Tier 2 | Distribution | 2023-05-18 | N/A | N/A | N/A
100023865039 | Other | Tier 2 | Distribution | 2023-05-18 | N/A | N/A | N/A
100023865041 | Conductor | Tier 2 | Distribution | 2023-05-18 | N/A | N/A | N/A
100023865042 | Pole | Tier 2 | Distribution | 2023-05-18 | N/A | N/A | N/A
100023865057 | Other | Tier 2 | Distribution | 2023-05-18 | N/A | N/A | N/A
100023865062 | Other | Tier 2 | Distribution | 2023-05-18 | N/A | N/A | N/A
100023865076 | Other | Tier 2 | Distribution | 2023-05-18 | N/A | N/A | N/A
100023865077 | Insulator and Bushing | Tier 2 | Distribution | 2023-05-18 | N/A | N/A | N/A
100023865079 | Other | Tier 2 | Distribution | 2023-05-18 | N/A | N/A | N/A
100023865104 | Conductor | Tier 2 | Distribution | 2023-05-18 | N/A | N/A | N/A
100023865123 | Other | Tier 2 | Distribution | 2023-05-18 | N/A | N/A | N/A
100023865138 | Cross Arm | Tier 2 | Distribution | 2023-05-18 | N/A | N/A | N/A
100023865169 | Pole | Tier 3 | Distribution | 2023-05-18 | N/A | N/A | N/A
100023878907 | Insulator and Bushing | Tier 2 | Distribution | 2023-05-19 | N/A | N/A | N/A
100023879016 | Anchor/Guy | Tier 2 | Distribution | 2023-05-19 | N/A | N/A | N/A
100023879018 | Other | Tier 2 | Distribution | 2023-05-19 | N/A | N/A | N/A
100023879034 | Other | Tier 2 | Distribution | 2023-05-19 | N/A | N/A | N/A
100023879037 | Other | Tier 2 | Distribution | 2023-05-19 | N/A | N/A | N/A
100023879039 | Pole | Tier 2 | Distribution | 2023-05-19 | N/A | N/A | N/A
100023879057 | Other | Tier 3 | Distribution | 2023-05-19 | N/A | N/A | N/A
100023879078 | Other | Tier 2 | Distribution | 2023-05-19 | N/A | N/A | N/A
100023879080 | Other | Tier 2 | Distribution | 2023-05-19 | N/A | N/A | N/A
100023879091 | Other | Tier 2 | Distribution | 2023-05-19 | N/A | N/A | N/A
100023885013 | Other | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885018 | Other | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885020 | Other | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885028 | Other | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885029 | Cross Arm | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885031 | Other | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885035 | Anchor/Guy | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885042 | Other | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885043 | Anchor/Guy | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885045 | Other | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885048 | Other | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885053 | Insulator and Bushing | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885059 | Cross Arm | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885062 | Anchor/Guy | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885064 | Pole | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885069 | Anchor/Guy | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885070 | Anchor/Guy | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885071 | Other | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885072 | Anchor/Guy | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885073 | Pole | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885074 | Pole | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885079 | Anchor/Guy | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885083 | Other | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885084 | Pole | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885085 | Conductor | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885091 | Other | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885095 | Conductor | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885114 | Other | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885115 | Pole | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885120 | Other | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885121 | Cross Arm | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885130 | Other | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885131 | Other | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885133 | Other | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885134 | Other | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885136 | Other | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885139 | Other | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885153 | Anchor/Guy | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885156 | Other | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885160 | Other | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885163 | Other | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885171 | Other | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885173 | Pole | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885178 | Pole | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885184 | Other | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885185 | Other | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885190 | Other | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885193 | Conductor | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885195 | Cross Arm | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023885201 | Other | Tier 2 | Distribution | 2023-05-22 | N/A | N/A | N/A
100023888719 | Switch | Tier 2 | Distribution | 2023-05-23 | N/A | N/A | N/A
100023890356 | Cross Arm | Tier 2 | Distribution | 2023-05-23 | N/A | N/A | N/A
100023890361 | Other | Tier 2 | Distribution | 2023-05-23 | N/A | N/A | N/A
100023890370 | Pole | Tier 2 | Distribution | 2023-05-23 | N/A | N/A | N/A
100023910869 | Anchor/Guy | Tier 2 | Distribution | 2023-05-24 | N/A | N/A | N/A
100023910878 | Other | Tier 2 | Distribution | 2023-05-24 | N/A | N/A | N/A
100023910890 | Other | Tier 2 | Distribution | 2023-05-24 | N/A | N/A | N/A
100023910897 | Other | Tier 2 | Distribution | 2023-05-24 | N/A | N/A | N/A
100023910899 | Pole | Tier 2 | Distribution | 2023-05-24 | N/A | N/A | N/A
100023910902 | Pole | Tier 2 | Distribution | 2023-05-24 | N/A | N/A | N/A
100023910908 | Other | Tier 2 | Distribution | 2023-05-24 | N/A | N/A | N/A
100023910924 | Cross Arm | Tier 2 | Distribution | 2023-05-24 | N/A | N/A | N/A
100023910929 | Other | Tier 2 | Distribution | 2023-05-24 | N/A | N/A | N/A
100023910949 | Pole | Tier 3 | Distribution | 2023-05-24 | N/A | N/A | N/A
100023910962 | Other | Tier 3 | Distribution | 2023-05-24 | N/A | N/A | N/A
100023910966 | Conductor | Tier 3 | Distribution | 2023-05-24 | N/A | N/A | N/A
100023910969 | Pole | Tier 3 | Distribution | 2023-05-24 | N/A | N/A | N/A
100023910970 | Other | Tier 3 | Distribution | 2023-05-24 | N/A | N/A | N/A
100023910972 | Pole | Tier 3 | Distribution | 2023-05-24 | N/A | N/A | N/A
100023910977 | Cross Arm | Tier 2 | Distribution | 2023-05-24 | N/A | N/A | N/A
100023910982 | Pole | Tier 2 | Distribution | 2023-05-24 | N/A | N/A | N/A
100023910986 | Other | Tier 2 | Distribution | 2023-05-24 | N/A | N/A | N/A
100023910993 | Conductor | Tier 3 | Distribution | 2023-05-24 | N/A | N/A | N/A
100023911015 | Pole | Tier 2 | Distribution | 2023-05-24 | N/A | N/A | N/A
100023911030 | Cross Arm | Tier 2 | Distribution | 2023-05-24 | N/A | N/A | N/A
100023911072 | Other | Tier 2 | Distribution | 2023-05-24 | N/A | N/A | N/A
100023925554 | Other | Tier 2 | Distribution | 2023-05-25 | N/A | N/A | N/A
100023925555 | Anchor/Guy | Tier 2 | Distribution | 2023-05-25 | N/A | N/A | N/A
100023925556 | Other | Tier 2 | Distribution | 2023-05-25 | N/A | N/A | N/A
100023925558 | Anchor/Guy | Tier 2 | Distribution | 2023-05-25 | N/A | N/A | N/A
100023925559 | Other | Tier 2 | Distribution | 2023-05-25 | N/A | N/A | N/A
100023925561 | Other | Tier 2 | Distribution | 2023-05-25 | N/A | N/A | N/A
100023925565 | Other | Tier 2 | Distribution | 2023-05-25 | N/A | N/A | N/A
100023925569 | Other | Tier 2 | Distribution | 2023-05-25 | N/A | N/A | N/A
100023925576 | Cross Arm | Tier 2 | Distribution | 2023-05-25 | N/A | N/A | N/A
100023925581 | Other | Tier 2 | Distribution | 2023-05-25 | N/A | N/A | N/A
100023925587 | Cross Arm | Tier 2 | Distribution | 2023-05-25 | N/A | N/A | N/A
100023925595 | Other | Tier 2 | Distribution | 2023-05-25 | N/A | N/A | N/A
100023925597 | Other | Tier 2 | Distribution | 2023-05-25 | N/A | N/A | N/A
100023925603 | Other | Tier 2 | Distribution | 2023-05-25 | N/A | N/A | N/A
100023925607 | Pole | Tier 2 | Distribution | 2023-05-25 | N/A | N/A | N/A
100023925611 | Pole | Tier 2 | Distribution | 2023-05-25 | N/A | N/A | N/A
100023925639 | Other | Tier 2 | Distribution | 2023-05-25 | N/A | N/A | N/A
100023925641 | Pole | Tier 2 | Distribution | 2023-05-25 | N/A | N/A | N/A
100023925646 | Cross Arm | Tier 2 | Distribution | 2023-05-25 | N/A | N/A | N/A
100023925649 | Other | Tier 2 | Distribution | 2023-05-25 | N/A | N/A | N/A
100023925665 | Other | Tier 2 | Distribution | 2023-05-25 | N/A | N/A | N/A
100023931580 | Other | Tier 2 | Distribution | 2023-05-26 | N/A | N/A | N/A
100023931585 | Anchor/Guy | Tier 2 | Distribution | 2023-05-26 | N/A | N/A | N/A
100023931596 | Pole | Tier 2 | Distribution | 2023-05-26 | N/A | N/A | N/A
100023931616 | Other | Tier 2 | Distribution | 2023-05-26 | N/A | N/A | N/A
100023931618 | Other | Tier 2 | Distribution | 2023-05-26 | N/A | N/A | N/A
100023931619 | Other | Tier 2 | Distribution | 2023-05-26 | N/A | N/A | N/A
100023931622 | Other | Tier 2 | Distribution | 2023-05-26 | N/A | N/A | N/A
100023931624 | Pole | Tier 2 | Distribution | 2023-05-26 | N/A | N/A | N/A
100023931625 | Other | Tier 2 | Distribution | 2023-05-26 | N/A | N/A | N/A
100023931631 | Anchor/Guy | Tier 2 | Distribution | 2023-05-26 | N/A | N/A | N/A
100023931641 | Other | Tier 2 | Distribution | 2023-05-26 | N/A | N/A | N/A
100023931642 | Cross Arm | Tier 2 | Distribution | 2023-05-26 | N/A | N/A | N/A
100023931644 | Insulator and Bushing | Tier 2 | Distribution | 2023-05-26 | N/A | N/A | N/A
100023931645 | Cross Arm | Tier 2 | Distribution | 2023-05-26 | N/A | N/A | N/A
100023931657 | Insulator and Bushing | Tier 2 | Distribution | 2023-05-26 | N/A | N/A | N/A
100023931658 | Pole | Tier 2 | Distribution | 2023-05-26 | N/A | N/A | N/A
100023931661 | Pole | Tier 2 | Distribution | 2023-05-26 | N/A | N/A | N/A
100023931669 | Pole | Tier 2 | Distribution | 2023-05-26 | N/A | N/A | N/A
100023931670 | Cross Arm | Tier 2 | Distribution | 2023-05-26 | N/A | N/A | N/A
100023931673 | Pole | Tier 2 | Distribution | 2023-05-26 | N/A | N/A | N/A
100023931678 | Other | Tier 2 | Distribution | 2023-05-26 | N/A | N/A | N/A
100023931681 | Pole | Tier 2 | Distribution | 2023-05-26 | N/A | N/A | N/A
100023931682 | Cross Arm | Tier 2 | Distribution | 2023-05-26 | N/A | N/A | N/A
100023931685 | Other | Tier 2 | Distribution | 2023-05-26 | N/A | N/A | N/A
100023931686 | Cross Arm | Tier 2 | Distribution | 2023-05-26 | N/A | N/A | N/A
100023931692 | Other | Tier 2 | Distribution | 2023-05-26 | N/A | N/A | N/A
100023931694 | Other | Tier 2 | Distribution | 2023-05-26 | N/A | N/A | N/A
100023931707 | Other | Tier 2 | Distribution | 2023-05-26 | N/A | N/A | N/A
100023931955 | Conductor | Tier 2 | Distribution | 2023-05-27 | N/A | N/A | N/A
100023931958 | Anchor/Guy | Tier 2 | Distribution | 2023-05-27 | N/A | N/A | N/A
100023932222 | Other | Tier 2 | Distribution | 2023-05-27 | N/A | N/A | N/A
100023932228 | Pole | Tier 2 | Distribution | 2023-05-27 | N/A | N/A | N/A
100023932250 | Pole | Tier 2 | Distribution | 2023-05-27 | N/A | N/A | N/A
100023932254 | Other | Tier 2 | Distribution | 2023-05-27 | N/A | N/A | N/A
100023932259 | Other | Tier 2 | Distribution | 2023-05-27 | N/A | N/A | N/A
100023932301 | Cross Arm | Tier 2 | Distribution | 2023-05-27 | N/A | N/A | N/A
100023932303 | Other | Tier 2 | Distribution | 2023-05-27 | N/A | N/A | N/A
100023938264 | Other | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938267 | Anchor/Guy | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938269 | Other | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938500 | Anchor/Guy | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938501 | Other | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938505 | Other | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938508 | Other | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938509 | Pole | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938512 | Insulator and Bushing | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938514 | Other | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938517 | Pole | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938518 | Pole | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938519 | Other | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938520 | Cross Arm | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938523 | Other | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938540 | Cross Arm | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938542 | Other | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938543 | Other | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938544 | Other | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938548 | Other | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938553 | Anchor/Guy | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938554 | Other | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938556 | Pole | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938557 | Insulator and Bushing | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938559 | Cross Arm | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938561 | Anchor/Guy | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938564 | Other | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938565 | Insulator and Bushing | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938569 | Other | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938572 | Pole | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938576 | Pole | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938579 | Other | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938583 | Pole | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938585 | Other | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938589 | Cross Arm | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938590 | Pole | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938592 | Other | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938595 | Pole | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938597 | Pole | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938601 | Pole | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938643 | Cross Arm | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938644 | Pole | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023938645 | Pole | Tier 2 | Distribution | 2023-05-30 | N/A | N/A | N/A
100023957352 | Cross Arm | Tier 2 | Distribution | 2023-05-31 | N/A | N/A | N/A
100023957370 | Other | Tier 2 | Distribution | 2023-05-31 | N/A | N/A | N/A
100023957372 | Other | Tier 2 | Distribution | 2023-05-31 | N/A | N/A | N/A
100023957373 | Cross Arm | Tier 2 | Distribution | 2023-05-31 | N/A | N/A | N/A
100023957377 | Other | Tier 2 | Distribution | 2023-05-31 | N/A | N/A | N/A
100023957378 | Pole | Tier 2 | Distribution | 2023-05-31 | N/A | N/A | N/A
100023957379 | Pole | Tier 2 | Distribution | 2023-05-31 | N/A | N/A | N/A
100023957385 | Other | Tier 2 | Distribution | 2023-05-31 | N/A | N/A | N/A
100023957386 | Pole | Tier 2 | Distribution | 2023-05-31 | N/A | N/A | N/A
100023957393 | Pole | Tier 2 | Distribution | 2023-05-31 | N/A | N/A | N/A
100023957411 | Pole | Tier 2 | Distribution | 2023-05-31 | N/A | N/A | N/A
100023957412 | Pole | Tier 2 | Distribution | 2023-05-31 | N/A | N/A | N/A
100023957414 | Pole | Tier 2 | Distribution | 2023-05-31 | N/A | N/A | N/A
100023965231 | Other | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965232 | Other | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965234 | Other | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965237 | Pole | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965246 | Pole | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965247 | Other | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965248 | Cross Arm | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965249 | Cross Arm | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965251 | Other | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965262 | Other | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965264 | Other | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965273 | Other | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965290 | Other | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965296 | Pole | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965297 | Cross Arm | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965300 | Other | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965301 | Anchor/Guy | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965302 | Pole | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965303 | Pole | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965304 | Other | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965305 | Cross Arm | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965307 | Other | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965310 | Pole | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965311 | Pole | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965313 | Conductor | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965315 | Other | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965316 | Cross Arm | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965317 | Cross Arm | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965320 | Cross Arm | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965322 | Cross Arm | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965325 | Other | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965329 | Insulator and Bushing | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965331 | Other | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965332 | Conductor | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965337 | Insulator and Bushing | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965339 | Pole | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965342 | Cross Arm | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965343 | Other | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023965344 | Other | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023969846 | Other | Tier 2 | Distribution | 2023-06-02 | N/A | N/A | N/A
100023969850 | Cross Arm | Tier 2 | Distribution | 2023-06-02 | N/A | N/A | N/A
100023969854 | Cross Arm | Tier 2 | Distribution | 2023-06-02 | N/A | N/A | N/A
100023969857 | Anchor/Guy | Tier 2 | Distribution | 2023-06-02 | N/A | N/A | N/A
100023969871 | Other | Tier 2 | Distribution | 2023-06-02 | N/A | N/A | N/A
100023969880 | Other | Tier 2 | Distribution | 2023-06-02 | N/A | N/A | N/A
100023969881 | Other | Tier 2 | Distribution | 2023-06-02 | N/A | N/A | N/A
100023969882 | Cross Arm | Tier 2 | Distribution | 2023-06-02 | N/A | N/A | N/A
100023969884 | Pole | Tier 2 | Distribution | 2023-06-02 | N/A | N/A | N/A
100023969886 | Other | Tier 2 | Distribution | 2023-06-02 | N/A | N/A | N/A
100023969887 | Other | Tier 2 | Distribution | 2023-06-02 | N/A | N/A | N/A
100023969891 | Cross Arm | Tier 2 | Distribution | 2023-06-02 | N/A | N/A | N/A
100023969892 | Pole | Tier 2 | Distribution | 2023-06-02 | N/A | N/A | N/A
100023969894 | Other | Tier 2 | Distribution | 2023-06-02 | N/A | N/A | N/A
100023969896 | Anchor/Guy | Tier 2 | Distribution | 2023-06-02 | N/A | N/A | N/A
100023969897 | Other | Tier 2 | Distribution | 2023-06-02 | N/A | N/A | N/A
100023969898 | Anchor/Guy | Tier 2 | Distribution | 2023-06-02 | N/A | N/A | N/A
100023969903 | Other | Tier 2 | Distribution | 2023-06-02 | N/A | N/A | N/A
100023969906 | Other | Tier 2 | Distribution | 2023-06-02 | N/A | N/A | N/A
100023969907 | Other | Tier 2 | Distribution | 2023-06-02 | N/A | N/A | N/A
100023969908 | Other | Tier 2 | Distribution | 2023-06-02 | N/A | N/A | N/A
100023969909 | Other | Tier 2 | Distribution | 2023-06-02 | N/A | N/A | N/A
100023969914 | Other | Tier 2 | Distribution | 2023-06-02 | N/A | N/A | N/A
100023974989 | Other | Tier 2 | Distribution | 2023-06-05 | N/A | N/A | N/A
100023975426 | Other | Tier 2 | Distribution | 2023-06-05 | N/A | N/A | N/A
100023975427 | Other | Tier 2 | Distribution | 2023-06-05 | N/A | N/A | N/A
100023975428 | Other | Tier 2 | Distribution | 2023-06-05 | N/A | N/A | N/A
100023975435 | Other | Tier 2 | Distribution | 2023-06-05 | N/A | N/A | N/A
100023975436 | Conductor | Tier 2 | Distribution | 2023-06-05 | N/A | N/A | N/A
100023975437 | Pole | Tier 2 | Distribution | 2023-06-05 | N/A | N/A | N/A
100023975440 | Other | Tier 2 | Distribution | 2023-06-05 | N/A | N/A | N/A
100023975457 | Anchor/Guy | Tier 3 | Distribution | 2023-06-05 | N/A | N/A | N/A
100023975458 | Anchor/Guy | Tier 2 | Distribution | 2023-06-05 | N/A | N/A | N/A
100023975462 | Other | Tier 2 | Distribution | 2023-06-05 | N/A | N/A | N/A
100023975463 | Other | Tier 2 | Distribution | 2023-06-05 | N/A | N/A | N/A
100023975464 | Cross Arm | Tier 2 | Distribution | 2023-06-05 | N/A | N/A | N/A
100023975467 | Other | Tier 2 | Distribution | 2023-06-05 | N/A | N/A | N/A
100023975468 | Other | Tier 2 | Distribution | 2023-06-05 | N/A | N/A | N/A
100023975471 | Other | Tier 2 | Distribution | 2023-06-05 | N/A | N/A | N/A
100023975479 | Conductor | Tier 2 | Distribution | 2023-06-05 | N/A | N/A | N/A
100023975491 | Other | Tier 2 | Distribution | 2023-06-05 | N/A | N/A | N/A
100023975500 | Other | Tier 2 | Distribution | 2023-06-05 | N/A | N/A | N/A
100023975508 | Other | Tier 2 | Distribution | 2023-06-05 | N/A | N/A | N/A
100023911061 | Anchor/Guy | Tier 2 | Distribution | 2023-05-24 | N/A | N/A | N/A
100023975516 | Cross Arm | Tier 3 | Distribution | 2023-06-05 | N/A | N/A | N/A
100023983041 | Other | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023983042 | Cross Arm | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023983047 | Other | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023983050 | Other | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023983055 | Conductor | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023983058 | Other | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023983064 | Other | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023983066 | Other | Tier 2 | Distribution | 2023-06-01 | N/A | N/A | N/A
100023983071 | Cross Arm | Tier 2 | Distribution | 2023-06-02 | N/A | N/A | N/A
100023983073 | Pole | Tier 2 | Distribution | 2023-06-02 | N/A | N/A | N/A
100023983075 | Other | Tier 2 | Distribution | 2023-06-02 | N/A | N/A | N/A
100023983088 | Other | Tier 2 | Distribution | 2023-06-02 | N/A | N/A | N/A
100023985687 | Conductor | Tier 2 | Distribution | 2023-06-06 | N/A | N/A | N/A
100023985691 | Pole | Tier 2 | Distribution | 2023-06-06 | N/A | N/A | N/A
100023985693 | Other | Tier 2 | Distribution | 2023-06-06 | N/A | N/A | N/A
100023985695 | Other | Tier 2 | Distribution | 2023-06-06 | N/A | N/A | N/A
100023985700 | Other | Tier 2 | Distribution | 2023-06-06 | N/A | N/A | N/A
100023985705 | Other | Tier 3 | Distribution | 2023-06-06 | N/A | N/A | N/A
100023985707 | Pole | Tier 3 | Distribution | 2023-06-06 | N/A | N/A | N/A
100023985714 | Pole | Tier 2 | Distribution | 2023-06-06 | N/A | N/A | N/A
100023985718 | Pole | Tier 3 | Distribution | 2023-06-06 | N/A | N/A | N/A
100023985719 | Pole | Tier 3 | Distribution | 2023-06-06 | N/A | N/A | N/A
100023985720 | Other | Tier 3 | Distribution | 2023-06-06 | N/A | N/A | N/A
100023985721 | Cross Arm | Tier 3 | Distribution | 2023-06-06 | N/A | N/A | N/A
100023985724 | Cross Arm | Tier 3 | Distribution | 2023-06-06 | N/A | N/A | N/A
100023985727 | Cross Arm | Tier 3 | Distribution | 2023-06-06 | N/A | N/A | N/A
100023985728 | Pole | Tier 3 | Distribution | 2023-06-06 | N/A | N/A | N/A
100023985751 | Pole | Tier 3 | Distribution | 2023-06-06 | N/A | N/A | N/A
100023985752 | Other | Tier 3 | Distribution | 2023-06-06 | N/A | N/A | N/A
100023985753 | Cross Arm | Tier 3 | Distribution | 2023-06-06 | N/A | N/A | N/A
100023985756 | Pole | Tier 3 | Distribution | 2023-06-06 | N/A | N/A | N/A
100023985777 | Cross Arm | Tier 2 | Distribution | 2023-06-06 | N/A | N/A | N/A
100023985778 | Pole | Tier 2 | Distribution | 2023-06-06 | N/A | N/A | N/A
100023985779 | Other | Tier 2 | Distribution | 2023-06-06 | N/A | N/A | N/A
100023985780 | Other | Tier 2 | Distribution | 2023-06-06 | N/A | N/A | N/A
100023985788 | Pole | Tier 2 | Distribution | 2023-06-06 | N/A | N/A | N/A
100023985789 | Other | Tier 2 | Distribution | 2023-06-06 | N/A | N/A | N/A
100023985790 | Cross Arm | Tier 2 | Distribution | 2023-06-06 | N/A | N/A | N/A
100023985795 | Pole | Tier 2 | Distribution | 2023-06-06 | N/A | N/A | N/A
100023985802 | Anchor/Guy | Tier 3 | Distribution | 2023-06-06 | N/A | N/A | N/A
100023985807 | Anchor/Guy | Tier 3 | Distribution | 2023-06-06 | N/A | N/A | N/A
100023985809 | Anchor/Guy | Tier 3 | Distribution | 2023-06-06 | N/A | N/A | N/A
100023985815 | Pole | Tier 3 | Distribution | 2023-06-06 | N/A | N/A | N/A
100023985816 | Other | Tier 3 | Distribution | 2023-06-06 | N/A | N/A | N/A
100023985819 | Anchor/Guy | Tier 3 | Distribution | 2023-06-06 | N/A | N/A | N/A
100023985820 | Pole | Tier 3 | Distribution | 2023-06-06 | N/A | N/A | N/A
100023994447 | Anchor/Guy | Tier 3 | Distribution | 2023-06-07 | N/A | N/A | N/A
100023998584 | Pole | Tier 3 | Distribution | 2023-06-09 | N/A | N/A | N/A
100023998947 | Conductor | Tier 3 | Distribution | 2023-06-09 | N/A | N/A | N/A
100023998962 | Anchor/Guy | Tier 3 | Distribution | 2023-06-09 | N/A | N/A | N/A
100024003434 | Anchor/Guy | Tier 3 | Distribution | 2023-06-11 | N/A | N/A | N/A
100024004014 | Anchor/Guy | Tier 3 | Distribution | 2023-06-11 | N/A | N/A | N/A
100024004023 | Anchor/Guy | Tier 3 | Distribution | 2023-06-11 | N/A | N/A | N/A
100024008923 | Conductor | Tier 3 | Distribution | 2023-06-12 | N/A | N/A | N/A
100024009374 | Other | Tier 3 | Distribution | 2023-06-12 | N/A | N/A | N/A
100024009375 | Pole | Tier 3 | Distribution | 2023-06-12 | N/A | N/A | N/A
100024009396 | Anchor/Guy | Tier 3 | Distribution | 2023-06-12 | N/A | N/A | N/A
100024009400 | Anchor/Guy | Tier 3 | Distribution | 2023-06-12 | N/A | N/A | N/A
100024009415 | Pole | Tier 3 | Distribution | 2023-06-12 | N/A | N/A | N/A
100024009425 | Cross Arm | Tier 3 | Distribution | 2023-06-12 | N/A | N/A | N/A
100024009441 | Other | Tier 3 | Distribution | 2023-06-12 | N/A | N/A | N/A
100024009442 | Cross Arm | Tier 3 | Distribution | 2023-06-12 | N/A | N/A | N/A
100024009473 | Pole | Tier 2 | Distribution | 2023-06-12 | N/A | N/A | N/A
100024009478 | Pole | Tier 2 | Distribution | 2023-06-12 | N/A | N/A | N/A
100024009481 | Pole | Tier 2 | Distribution | 2023-06-12 | N/A | N/A | N/A
100024009482 | Anchor/Guy | Tier 2 | Distribution | 2023-06-12 | N/A | N/A | N/A
100024009495 | Anchor/Guy | Tier 2 | Distribution | 2023-06-12 | N/A | N/A | N/A
100024009498 | Cross Arm | Tier 2 | Distribution | 2023-06-12 | N/A | N/A | N/A
100024009511 | Anchor/Guy | Tier 3 | Distribution | 2023-06-12 | N/A | N/A | N/A
100024009522 | Pole | Tier 3 | Distribution | 2023-06-12 | N/A | N/A | N/A
100024009523 | Other | Tier 3 | Distribution | 2023-06-12 | N/A | N/A | N/A
100024009547 | Anchor/Guy | Tier 3 | Distribution | 2023-06-12 | N/A | N/A | N/A
100024014893 | Cross Arm | Tier 3 | Distribution | 2023-06-14 | N/A | N/A | N/A
100024014898 | Pole | Tier 3 | Distribution | 2023-06-14 | N/A | N/A | N/A
100024016960 | Pole | Tier 3 | Distribution | 2023-06-14 | N/A | N/A | N/A
100024016968 | Anchor/Guy | Tier 3 | Distribution | 2023-06-14 | N/A | N/A | N/A
100024016971 | Anchor/Guy | Tier 3 | Distribution | 2023-06-14 | N/A | N/A | N/A
100024016972 | Anchor/Guy | Tier 3 | Distribution | 2023-06-14 | N/A | N/A | N/A
100024016982 | Anchor/Guy | Tier 3 | Distribution | 2023-06-14 | N/A | N/A | N/A
100024016993 | Pole | Tier 3 | Distribution | 2023-06-14 | N/A | N/A | N/A
100024017000 | Cross Arm | Tier 3 | Distribution | 2023-06-14 | N/A | N/A | N/A
100024017005 | Pole | Tier 3 | Distribution | 2023-06-14 | N/A | N/A | N/A
100024017006 | Cross Arm | Tier 3 | Distribution | 2023-06-14 | N/A | N/A | N/A
100024017008 | Pole | Tier 3 | Distribution | 2023-06-14 | N/A | N/A | N/A
100024017009 | Cross Arm | Tier 3 | Distribution | 2023-06-14 | N/A | N/A | N/A
100024017013 | Other | Tier 3 | Distribution | 2023-06-14 | N/A | N/A | N/A
100024017014 | Other | Tier 3 | Distribution | 2023-06-14 | N/A | N/A | N/A
100024017016 | Conductor | Tier 3 | Distribution | 2023-06-14 | N/A | N/A | N/A
100024022462 | Anchor/Guy | Tier 3 | Distribution | 2023-06-14 | N/A | N/A | N/A
100024022476 | Anchor/Guy | Tier 3 | Distribution | 2023-06-14 | N/A | N/A | N/A
100024022486 | Anchor/Guy | Tier 3 | Distribution | 2023-06-14 | N/A | N/A | N/A
100024022494 | Anchor/Guy | Tier 3 | Distribution | 2023-06-14 | N/A | N/A | N/A
100024022519 | Other | Tier 3 | Distribution | 2023-06-14 | N/A | N/A | N/A
100024022521 | Cross Arm | Tier 3 | Distribution | 2023-06-14 | N/A | N/A | N/A
100024028118 | Pole | Tier 2 | Distribution | 2023-06-15 | N/A | N/A | N/A
100024028119 | Other | Tier 2 | Distribution | 2023-06-15 | N/A | N/A | N/A
100024028124 | Pole | Tier 2 | Distribution | 2023-06-15 | N/A | N/A | N/A
100024028126 | Pole | Tier 2 | Distribution | 2023-06-15 | N/A | N/A | N/A
100024028128 | Insulator and Bushing | Tier 2 | Distribution | 2023-06-15 | N/A | N/A | N/A
100024028129 | Other | Tier 2 | Distribution | 2023-06-15 | N/A | N/A | N/A
100024028131 | Anchor/Guy | Tier 2 | Distribution | 2023-06-15 | N/A | N/A | N/A
100024028132 | Cross Arm | Tier 2 | Distribution | 2023-06-15 | N/A | N/A | N/A
100024028134 | Other | Tier 2 | Distribution | 2023-06-15 | N/A | N/A | N/A
100024028137 | Pole | Tier 2 | Distribution | 2023-06-15 | N/A | N/A | N/A
100024028141 | Cross Arm | Tier 2 | Distribution | 2023-06-15 | N/A | N/A | N/A
100024028142 | Anchor/Guy | Tier 2 | Distribution | 2023-06-15 | N/A | N/A | N/A
100024032788 | Pole | Tier 2 | Distribution | 2023-06-16 | N/A | N/A | N/A
100024032791 | Other | Tier 2 | Distribution | 2023-06-16 | N/A | N/A | N/A
100024032800 | Other | Tier 2 | Distribution | 2023-06-16 | N/A | N/A | N/A
100024032803 | Other | Tier 2 | Distribution | 2023-06-16 | N/A | N/A | N/A
100024032808 | Insulator and Bushing | Tier 2 | Distribution | 2023-06-16 | N/A | N/A | N/A
100024032809 | Other | Tier 2 | Distribution | 2023-06-16 | N/A | N/A | N/A
100024032812 | Pole | Tier 2 | Distribution | 2023-06-16 | N/A | N/A | N/A
100024032815 | Pole | Tier 2 | Distribution | 2023-06-16 | N/A | N/A | N/A
100024032820 | Anchor/Guy | Tier 2 | Distribution | 2023-06-16 | N/A | N/A | N/A
100024032821 | Other | Tier 2 | Distribution | 2023-06-16 | N/A | N/A | N/A
100024032825 | Pole | Tier 2 | Distribution | 2023-06-16 | N/A | N/A | N/A
100024032826 | Insulator and Bushing | Tier 2 | Distribution | 2023-06-16 | N/A | N/A | N/A
100024032829 | Other | Tier 2 | Distribution | 2023-06-16 | N/A | N/A | N/A
100024032830 | Cross Arm | Tier 2 | Distribution | 2023-06-16 | N/A | N/A | N/A
100024032831 | Pole | Tier 2 | Distribution | 2023-06-16 | N/A | N/A | N/A
100024032833 | Anchor/Guy | Tier 2 | Distribution | 2023-06-16 | N/A | N/A | N/A
100024032835 | Conductor | Tier 2 | Distribution | 2023-06-16 | N/A | N/A | N/A
100024032837 | Pole | Tier 2 | Distribution | 2023-06-16 | N/A | N/A | N/A
100024032841 | Other | Tier 2 | Distribution | 2023-06-16 | N/A | N/A | N/A
100024032893 | Pole | Tier 3 | Distribution | 2023-06-16 | N/A | N/A | N/A
100024032897 | Anchor/Guy | Tier 3 | Distribution | 2023-06-16 | N/A | N/A | N/A
100024032900 | Other | Tier 3 | Distribution | 2023-06-16 | N/A | N/A | N/A
100024032901 | Other | Tier 3 | Distribution | 2023-06-16 | N/A | N/A | N/A
100024044714 | Other | Tier 2 | Distribution | 2023-06-19 | N/A | N/A | N/A
100024044715 | Other | Tier 2 | Distribution | 2023-06-19 | N/A | N/A | N/A
100024044716 | Anchor/Guy | Tier 2 | Distribution | 2023-06-19 | N/A | N/A | N/A
100024044720 | Pole | Tier 2 | Distribution | 2023-06-19 | N/A | N/A | N/A
100024044724 | Anchor/Guy | Tier 2 | Distribution | 2023-06-19 | N/A | N/A | N/A
100024044729 | Other | Tier 2 | Distribution | 2023-06-19 | N/A | N/A | N/A
100024044742 | Other | Tier 2 | Distribution | 2023-06-19 | N/A | N/A | N/A
100024044811 | Conductor | Tier 2 | Distribution | 2023-06-19 | N/A | N/A | N/A
100024044812 | Cross Arm | Tier 2 | Distribution | 2023-06-19 | N/A | N/A | N/A
100024044814 | Pole | Tier 2 | Distribution | 2023-06-19 | N/A | N/A | N/A
100024044823 | Other | Tier 2 | Distribution | 2023-06-19 | N/A | N/A | N/A
100024044824 | Cross Arm | Tier 2 | Distribution | 2023-06-19 | N/A | N/A | N/A
100024044846 | Pole | Tier 2 | Distribution | 2023-06-19 | N/A | N/A | N/A
100024044847 | Cross Arm | Tier 2 | Distribution | 2023-06-19 | N/A | N/A | N/A
100024049623 | Anchor/Guy | Tier 2 | Distribution | 2023-06-20 | N/A | N/A | N/A
100024049634 | Other | Tier 2 | Distribution | 2023-06-20 | N/A | N/A | N/A
100024049636 | Other | Tier 2 | Distribution | 2023-06-20 | N/A | N/A | N/A
100024049637 | Other | Tier 2 | Distribution | 2023-06-20 | N/A | N/A | N/A
100024049638 | Anchor/Guy | Tier 2 | Distribution | 2023-06-20 | N/A | N/A | N/A
100024049642 | Anchor/Guy | Tier 2 | Distribution | 2023-06-20 | N/A | N/A | N/A
100024049643 | Anchor/Guy | Tier 2 | Distribution | 2023-06-20 | N/A | N/A | N/A
100024049644 | Anchor/Guy | Tier 2 | Distribution | 2023-06-20 | N/A | N/A | N/A
100024057457 | Other | Tier 2 | Distribution | 2023-06-21 | N/A | N/A | N/A
100024106674 | Cross Arm | Tier 2 | Distribution | 2023-06-27 | N/A | N/A | N/A
100024106687 | Anchor/Guy | Tier 3 | Distribution | 2023-06-27 | N/A | N/A | N/A
100024106691 | Anchor/Guy | Tier 3 | Distribution | 2023-06-27 | N/A | N/A | N/A
100024106733 | Other | Tier 3 | Distribution | 2023-06-27 | N/A | N/A | N/A
100024106736 | Pole | Tier 3 | Distribution | 2023-06-27 | N/A | N/A | N/A
100024106755 | Pole | Tier 2 | Distribution | 2023-06-27 | N/A | N/A | N/A
100024106756 | Other | Tier 2 | Distribution | 2023-06-27 | N/A | N/A | N/A
100024106761 | Anchor/Guy | Tier 2 | Distribution | 2023-06-27 | N/A | N/A | N/A
100024106763 | Conductor | Tier 2 | Distribution | 2023-06-27 | N/A | N/A | N/A
100024116257 | Pole | Tier 3 | Distribution | 2023-06-29 | N/A | N/A | N/A
100024116259 | Pole | Tier 3 | Distribution | 2023-06-29 | N/A | N/A | N/A
100024116331 | Conductor | Tier 3 | Distribution | 2023-06-29 | N/A | N/A | N/A
100024116336 | Conductor | Tier 3 | Distribution | 2023-06-29 | N/A | N/A | N/A
100024116340 | Conductor | Tier 3 | Distribution | 2023-06-29 | N/A | N/A | N/A
100024116341 | Pole | Tier 3 | Distribution | 2023-06-29 | N/A | N/A | N/A
100024116344 | Other | Tier 3 | Distribution | 2023-06-29 | N/A | N/A | N/A
100024116345 | Conductor | Tier 3 | Distribution | 2023-06-29 | N/A | N/A | N/A
100024116349 | Anchor/Guy | Tier 3 | Distribution | 2023-06-29 | N/A | N/A | N/A
100024116350 | Cross Arm | Tier 3 | Distribution | 2023-06-29 | N/A | N/A | N/A
100024131912 | Anchor/Guy | Tier 3 | Distribution | 2023-06-30 | N/A | N/A | N/A
100024131913 | Other | Tier 3 | Distribution | 2023-06-30 | N/A | N/A | N/A
100024131915 | Pole | Tier 3 | Distribution | 2023-06-30 | N/A | N/A | N/A
100024131917 | Anchor/Guy | Tier 3 | Distribution | 2023-06-30 | N/A | N/A | N/A
100024131928 | Pole | Tier 3 | Distribution | 2023-06-30 | N/A | N/A | N/A
100024131940 | Pole | Tier 3 | Distribution | 2023-06-30 | N/A | N/A | N/A
100024131951 | Other | Tier 3 | Distribution | 2023-06-30 | N/A | N/A | N/A
100024131953 | Pole | Tier 3 | Distribution | 2023-06-30 | N/A | N/A | N/A
100024131955 | Pole | Tier 3 | Distribution | 2023-06-30 | N/A | N/A | N/A
100024137690 | Anchor/Guy | Tier 3 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137696 | Other | Tier 3 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137697 | Anchor/Guy | Tier 3 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137699 | Anchor/Guy | Tier 3 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137702 | Other | Tier 2 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137704 | Anchor/Guy | Tier 2 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137705 | Other | Tier 2 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137706 | Anchor/Guy | Tier 2 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137709 | Other | Tier 2 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137715 | Anchor/Guy | Tier 2 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137716 | Anchor/Guy | Tier 2 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137719 | Anchor/Guy | Tier 2 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137723 | Other | Tier 2 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137724 | Pole | Tier 2 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137733 | Other | Tier 2 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137739 | Other | Tier 2 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137740 | Cross Arm | Tier 2 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137741 | Anchor/Guy | Tier 2 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137742 | Other | Tier 2 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137745 | Other | Tier 2 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137746 | Other | Tier 2 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137770 | Anchor/Guy | Tier 3 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137776 | Anchor/Guy | Tier 3 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137778 | Anchor/Guy | Tier 3 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137779 | Anchor/Guy | Tier 3 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137781 | Anchor/Guy | Tier 3 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137783 | Anchor/Guy | Tier 3 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137790 | Anchor/Guy | Tier 3 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137792 | Anchor/Guy | Tier 3 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137812 | Other | Tier 3 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137815 | Other | Tier 3 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137816 | Pole | Tier 3 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137818 | Cross Arm | Tier 3 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137832 | Anchor/Guy | Tier 3 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137836 | Anchor/Guy | Tier 2 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137839 | Other | Tier 2 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137846 | Anchor/Guy | Tier 2 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024137847 | Anchor/Guy | Tier 2 | Distribution | 2023-07-03 | N/A | N/A | N/A
100024147463 | Conductor | Tier 3 | Distribution | 2023-07-06 | N/A | N/A | N/A
100024147507 | Cross Arm | Tier 2 | Distribution | 2023-07-06 | N/A | N/A | N/A
100024147518 | Anchor/Guy | Tier 3 | Distribution | 2023-07-06 | N/A | N/A | N/A
100024147529 | Other | Tier 3 | Distribution | 2023-07-06 | N/A | N/A | N/A
100024147540 | Other | Tier 3 | Distribution | 2023-07-06 | N/A | N/A | N/A
100024147541 | Cross Arm | Tier 3 | Distribution | 2023-07-06 | N/A | N/A | N/A
100024147546 | Pole | Tier 3 | Distribution | 2023-07-06 | N/A | N/A | N/A
100024147557 | Anchor/Guy | Tier 2 | Distribution | 2023-07-06 | N/A | N/A | N/A
100024147564 | Pole | Tier 2 | Distribution | 2023-07-06 | N/A | N/A | N/A
100024147630 | Cross Arm | Tier 3 | Distribution | 2023-07-06 | N/A | N/A | N/A
100024147676 | Anchor/Guy | Tier 2 | Distribution | 2023-07-06 | N/A | N/A | N/A
100024147679 | Anchor/Guy | Tier 2 | Distribution | 2023-07-06 | N/A | N/A | N/A
100024147683 | Anchor/Guy | Tier 2 | Distribution | 2023-07-06 | N/A | N/A | N/A
100024147689 | Other | Tier 2 | Distribution | 2023-07-06 | N/A | N/A | N/A
100024147729 | Transformer | Tier 2 | Distribution | 2023-07-06 | N/A | N/A | N/A
100024147735 | Other | Tier 2 | Distribution | 2023-07-06 | N/A | N/A | N/A
100024147742 | Insulator and Bushing | Tier 2 | Distribution | 2023-07-06 | N/A | N/A | N/A
100024147743 | Insulator and Bushing | Tier 2 | Distribution | 2023-07-06 | N/A | N/A | N/A
100024151808 | Other | Tier 2 | Distribution | 2023-07-07 | N/A | N/A | N/A
100024151833 | Cross Arm | Tier 2 | Distribution | 2023-07-07 | N/A | N/A | N/A
100024151834 | Cross Arm | Tier 2 | Distribution | 2023-07-07 | N/A | N/A | N/A
100024168089 | Pole | Tier 3 | Distribution | 2023-07-10 | N/A | N/A | N/A
100024168092 | Cross Arm | Tier 3 | Distribution | 2023-07-10 | N/A | N/A | N/A
100024168105 | Anchor/Guy | Tier 3 | Distribution | 2023-07-10 | N/A | N/A | N/A
100024168166 | Other | Tier 3 | Distribution | 2023-07-10 | N/A | N/A | N/A
100024168167 | Cross Arm | Tier 3 | Distribution | 2023-07-10 | N/A | N/A | N/A
100024168168 | Cross Arm | Tier 3 | Distribution | 2023-07-10 | N/A | N/A | N/A
100024168210 | Anchor/Guy | Tier 2 | Distribution | 2023-07-12 | N/A | N/A | N/A
100024168243 | Pole | Tier 3 | Distribution | 2023-07-12 | N/A | N/A | N/A
100024168255 | Conductor | Tier 3 | Distribution | 2023-07-12 | N/A | N/A | N/A
100024173416 | Pole | Tier 3 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173417 | Anchor/Guy | Tier 3 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173425 | Cross Arm | Tier 3 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173429 | Cross Arm | Tier 3 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173440 | Cross Arm | Tier 3 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173442 | Cross Arm | Tier 3 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173443 | Pole | Tier 3 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173449 | Pole | Tier 2 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173450 | Other | Tier 2 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173453 | Conductor | Tier 2 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173454 | Other | Tier 2 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173462 | Other | Tier 2 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173463 | Other | Tier 2 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173465 | Pole | Tier 2 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173467 | Other | Tier 2 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173469 | Other | Tier 2 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173472 | Other | Tier 2 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173476 | Pole | Tier 2 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173481 | Pole | Tier 2 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173484 | Anchor/Guy | Tier 2 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173485 | Pole | Tier 2 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173514 | Other | Tier 3 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173515 | Pole | Tier 3 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173520 | Anchor/Guy | Tier 2 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173527 | Other | Tier 2 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173531 | Pole | Tier 2 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173541 | Anchor/Guy | Tier 3 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173542 | Anchor/Guy | Tier 3 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173555 | Pole | Tier 2 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173559 | Other | Tier 2 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173561 | Cross Arm | Tier 2 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173565 | Anchor/Guy | Tier 2 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173595 | Anchor/Guy | Tier 2 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173598 | Other | Tier 3 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024173619 | Anchor/Guy | Tier 3 | Distribution | 2023-07-13 | N/A | N/A | N/A
100024178580 | Pole | Tier 2 | Distribution | 2023-07-14 | N/A | N/A | N/A
100024178594 | Other | Tier 2 | Distribution | 2023-07-14 | N/A | N/A | N/A
100024178624 | Anchor/Guy | Tier 3 | Distribution | 2023-07-14 | N/A | N/A | N/A
100024178639 | Pole | Tier 3 | Distribution | 2023-07-14 | N/A | N/A | N/A
100024178661 | Pole | Tier 3 | Distribution | 2023-07-14 | N/A | N/A | N/A
100024178672 | Pole | Tier 3 | Distribution | 2023-07-14 | N/A | N/A | N/A
100024178685 | Cross Arm | Tier 2 | Distribution | 2023-07-14 | N/A | N/A | N/A
100024178694 | Anchor/Guy | Tier 2 | Distribution | 2023-07-14 | N/A | N/A | N/A
100024178701 | Pole | Tier 3 | Distribution | 2023-07-14 | N/A | N/A | N/A
100024178727 | Pole | Tier 3 | Distribution | 2023-07-14 | N/A | N/A | N/A
100024178743 | Pole | Tier 3 | Distribution | 2023-07-14 | N/A | N/A | N/A
100024178745 | Other | Tier 3 | Distribution | 2023-07-14 | N/A | N/A | N/A
100024178750 | Anchor/Guy | Tier 3 | Distribution | 2023-07-14 | N/A | N/A | N/A
100024178752 | Anchor/Guy | Tier 3 | Distribution | 2023-07-14 | N/A | N/A | N/A
100024178758 | Other | Tier 3 | Distribution | 2023-07-14 | N/A | N/A | N/A
100024178759 | Other | Tier 3 | Distribution | 2023-07-14 | N/A | N/A | N/A
100024178777 | Pole | Tier 3 | Distribution | 2023-07-14 | N/A | N/A | N/A
100024178783 | Pole | Tier 3 | Distribution | 2023-07-14 | N/A | N/A | N/A
100024178787 | Pole | Tier 3 | Distribution | 2023-07-14 | N/A | N/A | N/A
100024178801 | Pole | Tier 3 | Distribution | 2023-07-14 | N/A | N/A | N/A
100024178808 | Other | Tier 3 | Distribution | 2023-07-14 | N/A | N/A | N/A
100024178816 | Conductor | Tier 3 | Distribution | 2023-07-14 | N/A | N/A | N/A
100024178817 | Other | Tier 3 | Distribution | 2023-07-14 | N/A | N/A | N/A
100024178818 | Pole | Tier 3 | Distribution | 2023-07-14 | N/A | N/A | N/A
100024178819 | Other | Tier 3 | Distribution | 2023-07-14 | N/A | N/A | N/A
100024178829 | Anchor/Guy | Tier 3 | Distribution | 2023-07-14 | N/A | N/A | N/A
100024178902 | Cross Arm | Tier 3 | Distribution | 2023-07-14 | N/A | N/A | N/A
100024178930 | Other | Tier 2 | Distribution | 2023-07-14 | N/A | N/A | N/A
100024178937 | Other | Tier 2 | Distribution | 2023-07-14 | N/A | N/A | N/A
100024178943 | Conductor | Tier 2 | Distribution | 2023-07-14 | N/A | N/A | N/A
100024179775 | Conductor | Tier 3 | Distribution | 2023-07-16 | N/A | N/A | N/A
100024179778 | Pole | Tier 3 | Distribution | 2023-07-16 | N/A | N/A | N/A
100024180166 | Cross Arm | Tier 3 | Distribution | 2023-07-16 | N/A | N/A | N/A
100024180169 | Conductor | Tier 3 | Distribution | 2023-07-16 | N/A | N/A | N/A
100024180314 | Pole | Tier 3 | Distribution | 2023-07-16 | N/A | N/A | N/A
100024180318 | Anchor/Guy | Tier 3 | Distribution | 2023-07-16 | N/A | N/A | N/A
100024180593 | Cross Arm | Tier 2 | Distribution | 2023-07-16 | N/A | N/A | N/A
100024180597 | Other | Tier 2 | Distribution | 2023-07-16 | N/A | N/A | N/A
100024180601 | Pole | Tier 2 | Distribution | 2023-07-16 | N/A | N/A | N/A
100024180602 | Pole | Tier 2 | Distribution | 2023-07-16 | N/A | N/A | N/A
100024180603 | Pole | Tier 2 | Distribution | 2023-07-16 | N/A | N/A | N/A
100024180607 | Cross Arm | Tier 2 | Distribution | 2023-07-16 | N/A | N/A | N/A
100024180608 | Conductor | Tier 2 | Distribution | 2023-07-16 | N/A | N/A | N/A
100024180612 | Other | Tier 2 | Distribution | 2023-07-16 | N/A | N/A | N/A
100024180613 | Pole | Tier 2 | Distribution | 2023-07-16 | N/A | N/A | N/A
100024180614 | Other | Tier 2 | Distribution | 2023-07-16 | N/A | N/A | N/A
100024180627 | Other | Tier 2 | Distribution | 2023-07-16 | N/A | N/A | N/A
100024180629 | Other | Tier 2 | Distribution | 2023-07-16 | N/A | N/A | N/A
100024180631 | Other | Tier 2 | Distribution | 2023-07-16 | N/A | N/A | N/A
100024185408 | Pole | Tier 3 | Distribution | 2023-07-17 | N/A | N/A | N/A
100024185427 | Pole | Tier 3 | Distribution | 2023-07-17 | N/A | N/A | N/A
100024201243 | Conductor | Tier 3 | Distribution | 2023-07-19 | N/A | N/A | N/A
100024201246 | Pole | Tier 3 | Distribution | 2023-07-19 | N/A | N/A | N/A
100024206338 | Pole | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208410 | Cross Arm | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208411 | Anchor/Guy | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208418 | Cross Arm | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208420 | Anchor/Guy | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208425 | Pole | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208436 | Other | Tier 2 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208440 | Pole | Tier 2 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208447 | Anchor/Guy | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208448 | Anchor/Guy | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208455 | Other | Tier 2 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208468 | Other | Tier 2 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208470 | Anchor/Guy | Tier 2 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208481 | Other | Tier 2 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208482 | Other | Tier 2 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208483 | Cross Arm | Tier 2 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208489 | Cross Arm | Tier 2 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208495 | Pole | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208497 | Other | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208504 | Anchor/Guy | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208520 | Pole | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208521 | Other | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208526 | Pole | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208531 | Other | Tier 2 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208533 | Other | Tier 2 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208544 | Other | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208546 | Anchor/Guy | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208548 | Anchor/Guy | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208549 | Pole | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208550 | Anchor/Guy | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208551 | Cross Arm | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208554 | Other | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208558 | Other | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208564 | Anchor/Guy | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208599 | Other | Tier 2 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208606 | Cross Arm | Tier 2 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208614 | Pole | Tier 2 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208669 | Pole | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208678 | Pole | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208679 | Cross Arm | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208685 | Cross Arm | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208693 | Pole | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208702 | Anchor/Guy | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208712 | Conductor | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208728 | Anchor/Guy | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208739 | Other | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208740 | Anchor/Guy | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208741 | Anchor/Guy | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208746 | Cross Arm | Tier 2 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208750 | Conductor | Tier 2 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208751 | Conductor | Tier 2 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208752 | Pole | Tier 2 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208754 | Anchor/Guy | Tier 2 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208755 | Other | Tier 2 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208771 | Other | Tier 2 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208776 | Anchor/Guy | Tier 2 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208781 | Pole | Tier 2 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208787 | Pole | Tier 2 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208795 | Cross Arm | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208796 | Anchor/Guy | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208803 | Cross Arm | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208812 | Pole | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208819 | Cross Arm | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024208832 | Cross Arm | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024213209 | Other | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024213697 | Cross Arm | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024213721 | Other | Tier 2 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024213729 | Anchor/Guy | Tier 2 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024213733 | Anchor/Guy | Tier 2 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024213744 | Other | Tier 2 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024213750 | Pole | Tier 2 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024213751 | Conductor | Tier 2 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024213752 | Conductor | Tier 2 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024213754 | Pole | Tier 2 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024213762 | Cross Arm | Tier 2 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024213766 | Pole | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024213767 | Cross Arm | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024213768 | Other | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024213776 | Cross Arm | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024213783 | Other | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024213785 | Pole | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024213791 | Anchor/Guy | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024213810 | Cross Arm | Tier 3 | Distribution | 2023-07-21 | N/A | N/A | N/A
100024225848 | Other | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024225850 | Cross Arm | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024225853 | Cross Arm | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024225856 | Cross Arm | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024225862 | Cross Arm | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024225863 | Cross Arm | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024225864 | Pole | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024225868 | Cross Arm | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024225876 | Cross Arm | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024225877 | Other | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024225885 | Anchor/Guy | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024225888 | Anchor/Guy | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024225889 | Anchor/Guy | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024225894 | Other | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024225895 | Pole | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024225896 | Other | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024225912 | Anchor/Guy | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024225914 | Pole | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024225915 | Other | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024225917 | Anchor/Guy | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024225918 | Other | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024225942 | Other | Tier 2 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024225944 | Pole | Tier 2 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024225946 | Other | Tier 2 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024225951 | Other | Tier 2 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024225952 | Pole | Tier 2 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024225953 | Anchor/Guy | Tier 2 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024225954 | Pole | Tier 2 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024225955 | Anchor/Guy | Tier 2 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024225957 | Other | Tier 2 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024225958 | Anchor/Guy | Tier 2 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024225962 | Other | Tier 2 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024225967 | Anchor/Guy | Tier 2 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024225992 | Other | Tier 2 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024225993 | Pole | Tier 2 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024225997 | Conductor | Tier 2 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024226019 | Other | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024226022 | Other | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024226023 | Cross Arm | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024226025 | Other | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024226047 | Other | Tier 2 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024226049 | Other | Tier 2 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024226050 | Other | Tier 2 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024226051 | Anchor/Guy | Tier 2 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024226053 | Other | Tier 2 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024226059 | Pole | Tier 2 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024226061 | Pole | Tier 2 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024226062 | Other | Tier 2 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024226065 | Other | Tier 2 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024226066 | Other | Tier 2 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024226069 | Pole | Tier 2 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024226071 | Pole | Tier 2 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024226082 | Pole | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024226086 | Anchor/Guy | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024226087 | Other | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024226090 | Pole | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024226100 | Conductor | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024226101 | Other | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024226103 | Anchor/Guy | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024226108 | Anchor/Guy | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024226111 | Anchor/Guy | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024226118 | Conductor | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024226126 | Cross Arm | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024226130 | Anchor/Guy | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024226131 | Other | Tier 3 | Distribution | 2023-07-24 | N/A | N/A | N/A
100024231937 | Other | Tier 2 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024243891 | Other | Tier 2 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024243901 | Pole | Tier 2 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024243921 | Pole | Tier 3 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024243922 | Cross Arm | Tier 3 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024243926 | Cross Arm | Tier 3 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024243941 | Cross Arm | Tier 3 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024243943 | Cross Arm | Tier 3 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024243946 | Cross Arm | Tier 3 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024243951 | Anchor/Guy | Tier 2 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024243953 | Other | Tier 2 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024243954 | Other | Tier 2 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024243958 | Anchor/Guy | Tier 2 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024243971 | Anchor/Guy | Tier 2 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024243974 | Other | Tier 2 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024243977 | Other | Tier 2 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024243978 | Other | Tier 2 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024243979 | Anchor/Guy | Tier 2 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024243980 | Pole | Tier 2 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024243982 | Pole | Tier 2 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024243983 | Other | Tier 2 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024243984 | Other | Tier 2 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024243986 | Pole | Tier 3 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024243988 | Pole | Tier 3 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024243989 | Other | Tier 3 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024243990 | Cross Arm | Tier 3 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024243993 | Pole | Tier 3 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024243994 | Cross Arm | Tier 3 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024244040 | Cross Arm | Tier 3 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024244044 | Other | Tier 3 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024244052 | Pole | Tier 2 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024244056 | Cross Arm | Tier 2 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024244059 | Other | Tier 2 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024244064 | Other | Tier 2 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024244065 | Cross Arm | Tier 2 | Distribution | 2023-07-25 | N/A | N/A | N/A
100024253960 | Pole | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024253961 | Anchor/Guy | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024253966 | Anchor/Guy | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024253972 | Anchor/Guy | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024253977 | Other | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024253981 | Insulator and Bushing | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024253982 | Pole | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254010 | Cross Arm | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254011 | Other | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254012 | Other | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254014 | Cross Arm | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254016 | Pole | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254017 | Cross Arm | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254019 | Other | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254020 | Other | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254022 | Insulator and Bushing | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254026 | Anchor/Guy | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254027 | Other | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254028 | Cross Arm | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254030 | Cross Arm | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254031 | Pole | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254032 | Insulator and Bushing | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254033 | Other | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254034 | Other | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254035 | Anchor/Guy | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254036 | Pole | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254041 | Anchor/Guy | Tier 2 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254046 | Pole | Tier 2 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254062 | Cross Arm | Tier 2 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254106 | Pole | Tier 2 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254110 | Other | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254111 | Other | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254114 | Cross Arm | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254115 | Other | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254116 | Other | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254121 | Cross Arm | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254122 | Other | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254125 | Other | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254126 | Other | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254132 | Other | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254133 | Cross Arm | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254134 | Cross Arm | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254136 | Other | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024254137 | Anchor/Guy | Tier 3 | Distribution | 2023-07-26 | N/A | N/A | N/A
100024263992 | Pole | Tier 3 | Distribution | 2023-07-01 | N/A | N/A | N/A
100024266567 | Cross Arm | Tier 3 | Distribution | 2023-07-28 | N/A | N/A | N/A
100024266568 | Other | Tier 3 | Distribution | 2023-07-28 | N/A | N/A | N/A
100024266569 | Pole | Tier 3 | Distribution | 2023-07-28 | N/A | N/A | N/A
100024267091 | Cross Arm | Tier 3 | Distribution | 2023-07-28 | N/A | N/A | N/A
100024267092 | Pole | Tier 3 | Distribution | 2023-07-28 | N/A | N/A | N/A
100024267135 | Cross Arm | Tier 3 | Distribution | 2023-07-28 | N/A | N/A | N/A
100024267144 | Other | Tier 2 | Distribution | 2023-07-28 | N/A | N/A | N/A
100024267149 | Pole | Tier 2 | Distribution | 2023-07-28 | N/A | N/A | N/A
100024267150 | Insulator and Bushing | Tier 2 | Distribution | 2023-07-28 | N/A | N/A | N/A
100024267168 | Other | Tier 2 | Distribution | 2023-07-28 | N/A | N/A | N/A
100024267175 | Pole | Tier 2 | Distribution | 2023-07-28 | N/A | N/A | N/A
100024267177 | Cross Arm | Tier 2 | Distribution | 2023-07-28 | N/A | N/A | N/A
100024267182 | Other | Tier 2 | Distribution | 2023-07-28 | N/A | N/A | N/A
100024267184 | Other | Tier 2 | Distribution | 2023-07-28 | N/A | N/A | N/A
100024267186 | Other | Tier 2 | Distribution | 2023-07-28 | N/A | N/A | N/A
100024267187 | Pole | Tier 2 | Distribution | 2023-07-28 | N/A | N/A | N/A
100024267191 | Anchor/Guy | Tier 2 | Distribution | 2023-07-28 | N/A | N/A | N/A
100024267192 | Other | Tier 2 | Distribution | 2023-07-28 | N/A | N/A | N/A
100024267197 | Anchor/Guy | Tier 2 | Distribution | 2023-07-28 | N/A | N/A | N/A
100024288851 | Fuse | Tier 2 | Distribution | 2023-08-01 | N/A | N/A | N/A
100024315802 | Pole | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315804 | Other | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315818 | Cross Arm | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315821 | Insulator and Bushing | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315822 | Pole | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315823 | Insulator and Bushing | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315825 | Other | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315831 | Other | Tier 3 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315838 | Other | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315851 | Pole | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315854 | Pole | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315856 | Cross Arm | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315858 | Pole | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315859 | Anchor/Guy | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315865 | Other | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315868 | Other | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315870 | Anchor/Guy | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315871 | Cross Arm | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315875 | Anchor/Guy | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315876 | Insulator and Bushing | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315877 | Anchor/Guy | Tier 3 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315891 | Anchor/Guy | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315897 | Other | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315905 | Other | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315907 | Pole | Tier 3 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315908 | Cross Arm | Tier 3 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315911 | Pole | Tier 3 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315912 | Pole | Tier 3 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315913 | Other | Tier 3 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315915 | Cross Arm | Tier 3 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315917 | Cross Arm | Tier 3 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315918 | Other | Tier 3 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315921 | Cross Arm | Tier 3 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315922 | Anchor/Guy | Tier 3 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315924 | Pole | Tier 3 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315928 | Cross Arm | Tier 3 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315932 | Anchor/Guy | Tier 3 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315944 | Pole | Tier 3 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315953 | Pole | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315964 | Other | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315967 | Anchor/Guy | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315968 | Other | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315975 | Other | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315982 | Other | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315983 | Other | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315985 | Insulator and Bushing | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315986 | Other | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024315987 | Other | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024316006 | Cross Arm | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024316007 | Other | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024316012 | Pole | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024316013 | Other | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024316017 | Other | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024316018 | Cross Arm | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024316020 | Other | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024316022 | Anchor/Guy | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024316027 | Pole | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024316033 | Other | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024316036 | Other | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024316038 | Other | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024316041 | Other | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024316046 | Other | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024316054 | Pole | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024316058 | Conductor | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024316059 | Cross Arm | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024316063 | Anchor/Guy | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024316069 | Other | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024316070 | Other | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024316074 | Pole | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024316076 | Anchor/Guy | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024316078 | Pole | Tier 2 | Distribution | 2023-08-09 | N/A | N/A | N/A
100024321199 | Other | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321211 | Pole | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321227 | Other | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321233 | Pole | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321235 | Pole | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321239 | Pole | Tier 3 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321240 | Other | Tier 3 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321241 | Cross Arm | Tier 3 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321242 | Cross Arm | Tier 3 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321245 | Pole | Tier 3 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321246 | Other | Tier 3 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321250 | Pole | Tier 3 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321253 | Pole | Tier 3 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321256 | Cross Arm | Tier 3 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321259 | Anchor/Guy | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321271 | Anchor/Guy | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321275 | Other | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321280 | Other | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321284 | Other | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321287 | Other | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321293 | Pole | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321295 | Other | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321297 | Anchor/Guy | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321298 | Anchor/Guy | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321300 | Anchor/Guy | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321306 | Anchor/Guy | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321308 | Other | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321314 | Cross Arm | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321315 | Other | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321316 | Other | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321319 | Other | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321321 | Pole | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321337 | Other | Tier 3 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321338 | Cross Arm | Tier 3 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321339 | Conductor | Tier 3 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321351 | Cross Arm | Tier 3 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321353 | Cross Arm | Tier 3 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321358 | Other | Tier 3 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321359 | Pole | Tier 3 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321364 | Other | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321367 | Cross Arm | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321368 | Anchor/Guy | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321372 | Conductor | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321382 | Other | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321387 | Anchor/Guy | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321391 | Anchor/Guy | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321392 | Other | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321393 | Anchor/Guy | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321394 | Anchor/Guy | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321403 | Other | Tier 3 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321405 | Pole | Tier 3 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321410 | Cross Arm | Tier 3 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321411 | Pole | Tier 3 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321417 | Pole | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321419 | Other | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321420 | Anchor/Guy | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321422 | Other | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321425 | Other | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321429 | Other | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321430 | Other | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321431 | Cross Arm | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321437 | Pole | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321439 | Conductor | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321442 | Pole | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321445 | Other | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321447 | Pole | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321450 | Other | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321457 | Conductor | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321458 | Conductor | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321464 | Pole | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321466 | Other | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321472 | Anchor/Guy | Tier 3 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321481 | Anchor/Guy | Tier 3 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321485 | Conductor | Tier 3 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321489 | Anchor/Guy | Tier 3 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321503 | Pole | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321506 | Other | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321507 | Conductor | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321520 | Other | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321522 | Anchor/Guy | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321525 | Anchor/Guy | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321526 | Anchor/Guy | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321527 | Other | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321529 | Other | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321532 | Other | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024321537 | Anchor/Guy | Tier 2 | Distribution | 2023-08-10 | N/A | N/A | N/A
100024327732 | Pole | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024327734 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024327735 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024327739 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328240 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328241 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328247 | Pole | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328251 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328252 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328253 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328256 | Anchor/Guy | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328259 | Anchor/Guy | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328261 | Pole | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328266 | Anchor/Guy | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328268 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328275 | Pole | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328278 | Pole | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328280 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328285 | Anchor/Guy | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328304 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328306 | Anchor/Guy | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328309 | Anchor/Guy | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328313 | Anchor/Guy | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328318 | Anchor/Guy | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328320 | Anchor/Guy | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328323 | Other | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328324 | Other | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328325 | Pole | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328326 | Cross Arm | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328329 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328332 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328337 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328344 | Conductor | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328350 | Anchor/Guy | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328352 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328355 | Anchor/Guy | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328357 | Other | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328358 | Other | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328365 | Pole | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328371 | Pole | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328373 | Cross Arm | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328374 | Pole | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328376 | Cross Arm | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328379 | Cross Arm | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328380 | Other | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328383 | Cross Arm | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328384 | Cross Arm | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328385 | Pole | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328386 | Cross Arm | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328389 | Other | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328391 | Cross Arm | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328392 | Pole | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328393 | Pole | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328399 | Anchor/Guy | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328400 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328404 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328410 | Anchor/Guy | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328414 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328419 | Anchor/Guy | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328425 | Other | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328428 | Other | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328438 | Pole | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328445 | Pole | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328447 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328452 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328453 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328455 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328457 | Cross Arm | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328458 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328461 | Cross Arm | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328470 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328473 | Cross Arm | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328479 | Pole | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328489 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328490 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328495 | Cross Arm | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328496 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328503 | Cross Arm | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328512 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328513 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328515 | Pole | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328518 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328526 | Anchor/Guy | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328527 | Anchor/Guy | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328529 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328530 | Pole | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328531 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328532 | Cross Arm | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328535 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328538 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328539 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328543 | Anchor/Guy | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328548 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328552 | Anchor/Guy | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328553 | Pole | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328554 | Anchor/Guy | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328559 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328562 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328570 | Other | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328572 | Other | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328573 | Pole | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328576 | Cross Arm | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328577 | Pole | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328581 | Cross Arm | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328583 | Cross Arm | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328585 | Cross Arm | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328590 | Pole | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328594 | Pole | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328595 | Pole | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328596 | Cross Arm | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328598 | Other | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328604 | Pole | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328605 | Other | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328606 | Anchor/Guy | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328607 | Pole | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328608 | Pole | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328611 | Anchor/Guy | Tier 2 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328616 | Pole | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328619 | Other | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328620 | Other | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024328622 | Pole | Tier 3 | Distribution | 2023-08-11 | N/A | N/A | N/A
100024333940 | Cross Arm | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024333941 | Transformer | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024333946 | Pole | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024333956 | Pole | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024333959 | Cross Arm | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024333968 | Cross Arm | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024333969 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024333973 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024333975 | Insulator and Bushing | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024333984 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024333988 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024333991 | Cross Arm | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024333993 | Cross Arm | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024333994 | Pole | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024333996 | Cross Arm | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024333997 | Pole | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024333998 | Cross Arm | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334003 | Pole | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334004 | Cross Arm | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334007 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334008 | Cross Arm | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334012 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334016 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334021 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334026 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334027 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334030 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334041 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334058 | Pole | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334066 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334067 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334068 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334071 | Cross Arm | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334085 | Anchor/Guy | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334086 | Insulator and Bushing | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334090 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334093 | Pole | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334105 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334107 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334108 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334112 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334114 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334117 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334118 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334124 | Pole | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334126 | Anchor/Guy | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334128 | Pole | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334141 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334144 | Pole | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334146 | Pole | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334160 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334161 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334163 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334166 | Conductor | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334167 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334171 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334173 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334174 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334175 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334178 | Pole | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334180 | Pole | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334188 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334199 | Pole | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334203 | Conductor | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334206 | Cross Arm | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334209 | Pole | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334211 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334213 | Pole | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334218 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334219 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334225 | Anchor/Guy | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334226 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334242 | Anchor/Guy | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024334245 | Anchor/Guy | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335215 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335230 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335232 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335233 | Cross Arm | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335234 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335236 | Cross Arm | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335238 | Cross Arm | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335256 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335257 | Pole | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335265 | Pole | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335283 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335287 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335312 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335316 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335333 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335334 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335335 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335336 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335338 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335350 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335352 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335455 | Cross Arm | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335521 | Pole | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335540 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335544 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335559 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335561 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335563 | Pole | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335569 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335573 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335577 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335579 | Anchor/Guy | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335584 | Pole | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335588 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335591 | Anchor/Guy | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335592 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335594 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335607 | Anchor/Guy | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335609 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335610 | Anchor/Guy | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335612 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335615 | Anchor/Guy | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335619 | Anchor/Guy | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335621 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335623 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335630 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335644 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335645 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335648 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335652 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335654 | Pole | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335656 | Anchor/Guy | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335658 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335664 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335667 | Anchor/Guy | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335670 | Other | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024335671 | Cross Arm | Tier 2 | Distribution | 2023-08-12 | N/A | N/A | N/A
100024343034 | Other | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343716 | Pole | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343736 | Other | Tier 3 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343745 | Cross Arm | Tier 3 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343748 | Pole | Tier 3 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343749 | Other | Tier 3 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343750 | Cross Arm | Tier 3 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343752 | Cross Arm | Tier 3 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343753 | Cross Arm | Tier 3 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343763 | Anchor/Guy | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343764 | Other | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343765 | Other | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343766 | Other | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343770 | Anchor/Guy | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343774 | Other | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343781 | Other | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343786 | Other | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343789 | Other | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343790 | Other | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343800 | Other | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343803 | Pole | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343804 | Other | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343812 | Other | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343813 | Anchor/Guy | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343816 | Other | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343823 | Pole | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343824 | Other | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343827 | Other | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343833 | Pole | Tier 3 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343837 | Cross Arm | Tier 3 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343846 | Other | Tier 3 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343847 | Other | Tier 3 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343853 | Cross Arm | Tier 3 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343862 | Cross Arm | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343866 | Other | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343879 | Anchor/Guy | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343880 | Conductor | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343883 | Other | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343893 | Other | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343896 | Other | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343899 | Other | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343903 | Anchor/Guy | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343910 | Pole | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343913 | Cross Arm | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343919 | Other | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343922 | Other | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343924 | Cross Arm | Tier 2 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343927 | Cross Arm | Tier 3 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343928 | Other | Tier 3 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343930 | Cross Arm | Tier 3 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343931 | Pole | Tier 3 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343935 | Cross Arm | Tier 3 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343939 | Pole | Tier 3 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343941 | Cross Arm | Tier 3 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343943 | Cross Arm | Tier 3 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343945 | Other | Tier 3 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343946 | Other | Tier 3 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343958 | Cross Arm | Tier 3 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343961 | Cross Arm | Tier 3 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343962 | Other | Tier 3 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343963 | Other | Tier 3 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343965 | Cross Arm | Tier 3 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343967 | Other | Tier 3 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343970 | Anchor/Guy | Tier 3 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343973 | Pole | Tier 3 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343976 | Anchor/Guy | Tier 3 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024343977 | Anchor/Guy | Tier 3 | Distribution | 2023-08-14 | N/A | N/A | N/A
100024351396 | Anchor/Guy | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351397 | Anchor/Guy | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351414 | Pole | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351421 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351430 | Pole | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351436 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351438 | Insulator and Bushing | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351441 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351451 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351452 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351453 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351455 | Insulator and Bushing | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351457 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351461 | Conductor | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351463 | Insulator and Bushing | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351478 | Pole | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351488 | Pole | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351495 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351503 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351524 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351526 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351527 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351532 | Cross Arm | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351538 | Cross Arm | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351548 | Other | Tier 3 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351553 | Other | Tier 3 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351554 | Anchor/Guy | Tier 3 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351560 | Other | Tier 3 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351562 | Anchor/Guy | Tier 3 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351564 | Other | Tier 3 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351565 | Anchor/Guy | Tier 3 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351566 | Anchor/Guy | Tier 3 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351570 | Anchor/Guy | Tier 3 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351573 | Anchor/Guy | Tier 3 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351578 | Anchor/Guy | Tier 3 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351579 | Anchor/Guy | Tier 3 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351608 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351614 | Conductor | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351619 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351620 | Conductor | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351623 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351625 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351630 | Conductor | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351631 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351632 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351637 | Cross Arm | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351642 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351643 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351644 | Cross Arm | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351646 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351647 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351649 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351653 | Anchor/Guy | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351658 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351662 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351664 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351667 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351668 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351676 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351679 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351686 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351694 | Conductor | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351695 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351696 | Cross Arm | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351701 | Cross Arm | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351703 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351708 | Other | Tier 3 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351719 | Insulator and Bushing | Tier 3 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351727 | Other | Tier 3 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351733 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351736 | Cross Arm | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351737 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351739 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351740 | Cross Arm | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351741 | Pole | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351742 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351744 | Pole | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351746 | Cross Arm | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351749 | Cross Arm | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351752 | Anchor/Guy | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351754 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351756 | Cross Arm | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351757 | Anchor/Guy | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351759 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351764 | Insulator and Bushing | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351765 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351766 | Cross Arm | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351767 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024351769 | Other | Tier 2 | Distribution | 2023-08-15 | N/A | N/A | N/A
100024356809 | Other | Tier 2 | Distribution | 2023-08-16 | N/A | N/A | N/A
100024356937 | Other | Tier 2 | Distribution | 2023-08-16 | N/A | N/A | N/A
100024356945 | Pole | Tier 2 | Distribution | 2023-08-16 | N/A | N/A | N/A
100024356950 | Other | Tier 2 | Distribution | 2023-08-16 | N/A | N/A | N/A
100024356952 | Other | Tier 2 | Distribution | 2023-08-16 | N/A | N/A | N/A
100024356959 | Anchor/Guy | Tier 2 | Distribution | 2023-08-16 | N/A | N/A | N/A
100024356960 | Other | Tier 2 | Distribution | 2023-08-16 | N/A | N/A | N/A
100024356961 | Anchor/Guy | Tier 2 | Distribution | 2023-08-16 | N/A | N/A | N/A
100024356963 | Anchor/Guy | Tier 2 | Distribution | 2023-08-16 | N/A | N/A | N/A
100024356967 | Cross Arm | Tier 2 | Distribution | 2023-08-16 | N/A | N/A | N/A
100024356971 | Anchor/Guy | Tier 2 | Distribution | 2023-08-16 | N/A | N/A | N/A
100024356972 | Other | Tier 2 | Distribution | 2023-08-16 | N/A | N/A | N/A
100024356973 | Anchor/Guy | Tier 2 | Distribution | 2023-08-16 | N/A | N/A | N/A
100024356975 | Other | Tier 2 | Distribution | 2023-08-16 | N/A | N/A | N/A
100024356976 | Other | Tier 2 | Distribution | 2023-08-16 | N/A | N/A | N/A
100024356977 | Other | Tier 2 | Distribution | 2023-08-16 | N/A | N/A | N/A
100024356979 | Other | Tier 2 | Distribution | 2023-08-16 | N/A | N/A | N/A
100024356980 | Anchor/Guy | Tier 2 | Distribution | 2023-08-16 | N/A | N/A | N/A
100024356992 | Other | Tier 2 | Distribution | 2023-08-16 | N/A | N/A | N/A
100024356997 | Other | Tier 2 | Distribution | 2023-08-16 | N/A | N/A | N/A
100024357008 | Anchor/Guy | Tier 3 | Distribution | 2023-08-16 | N/A | N/A | N/A
100024364155 | Other | Tier 2 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364160 | Other | Tier 2 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364163 | Other | Tier 2 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364164 | Other | Tier 2 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364165 | Anchor/Guy | Tier 2 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364167 | Cross Arm | Tier 2 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364168 | Anchor/Guy | Tier 2 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364173 | Pole | Tier 2 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364175 | Other | Tier 2 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364176 | Other | Tier 2 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364180 | Cross Arm | Tier 2 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364182 | Other | Tier 2 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364185 | Cross Arm | Tier 2 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364187 | Other | Tier 2 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364189 | Cross Arm | Tier 2 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364191 | Anchor/Guy | Tier 3 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364193 | Other | Tier 3 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364195 | Anchor/Guy | Tier 3 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364196 | Anchor/Guy | Tier 3 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364197 | Other | Tier 3 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364231 | Other | Tier 2 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364235 | Insulator and Bushing | Tier 2 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364238 | Other | Tier 2 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364239 | Other | Tier 2 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364244 | Other | Tier 2 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364246 | Other | Tier 2 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364255 | Other | Tier 2 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364261 | Anchor/Guy | Tier 2 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364262 | Anchor/Guy | Tier 2 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364263 | Anchor/Guy | Tier 2 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364265 | Pole | Tier 2 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364267 | Cross Arm | Tier 2 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364269 | Cross Arm | Tier 2 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364278 | Other | Tier 2 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024364279 | Other | Tier 2 | Distribution | 2023-08-17 | N/A | N/A | N/A
100024369030 | Pole | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369038 | Anchor/Guy | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369043 | Other | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369046 | Other | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369053 | Pole | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369054 | Other | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369058 | Other | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369059 | Cross Arm | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369061 | Other | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369064 | Other | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369066 | Cross Arm | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369067 | Other | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369068 | Other | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369072 | Cross Arm | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369087 | Other | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369090 | Anchor/Guy | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369092 | Cross Arm | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369100 | Anchor/Guy | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369105 | Anchor/Guy | Tier 3 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369106 | Other | Tier 3 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369109 | Cross Arm | Tier 3 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369119 | Cross Arm | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369120 | Insulator and Bushing | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369121 | Cross Arm | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369124 | Other | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369126 | Insulator and Bushing | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369129 | Cross Arm | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369130 | Cross Arm | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369132 | Cross Arm | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369136 | Other | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369140 | Cross Arm | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369141 | Other | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369143 | Pole | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369144 | Pole | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369146 | Cross Arm | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369147 | Pole | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369150 | Cross Arm | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369155 | Cross Arm | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369156 | Other | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369157 | Other | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369159 | Other | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369160 | Pole | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369161 | Anchor/Guy | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024369163 | Cross Arm | Tier 2 | Distribution | 2023-08-18 | N/A | N/A | N/A
100024380133 | Cross Arm | Tier 2 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380139 | Other | Tier 2 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380143 | Other | Tier 2 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380145 | Other | Tier 2 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380155 | Anchor/Guy | Tier 3 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380157 | Anchor/Guy | Tier 3 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380164 | Pole | Tier 3 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380165 | Other | Tier 3 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380166 | Conductor | Tier 3 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380168 | Pole | Tier 3 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380171 | Other | Tier 3 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380180 | Other | Tier 3 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380189 | Other | Tier 3 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380193 | Anchor/Guy | Tier 3 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380194 | Anchor/Guy | Tier 3 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380198 | Cross Arm | Tier 2 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380201 | Pole | Tier 2 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380209 | Anchor/Guy | Tier 2 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380219 | Cross Arm | Tier 2 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380227 | Other | Tier 2 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380231 | Anchor/Guy | Tier 2 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380235 | Other | Tier 2 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380254 | Other | Tier 2 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380256 | Anchor/Guy | Tier 2 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380258 | Anchor/Guy | Tier 2 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380263 | Pole | Tier 2 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380270 | Cross Arm | Tier 2 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380271 | Other | Tier 2 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380272 | Other | Tier 2 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380283 | Pole | Tier 2 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380284 | Other | Tier 2 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380293 | Cross Arm | Tier 2 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380295 | Other | Tier 2 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380296 | Other | Tier 2 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380302 | Anchor/Guy | Tier 2 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024380303 | Anchor/Guy | Tier 2 | Distribution | 2023-08-21 | N/A | N/A | N/A
100024394526 | Cross Arm | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024394528 | Cross Arm | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024394529 | Cross Arm | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396313 | Cross Arm | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396315 | Cross Arm | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396320 | Pole | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396322 | Cross Arm | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396324 | Cross Arm | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396325 | Pole | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396326 | Cross Arm | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396327 | Other | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396328 | Other | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396333 | Pole | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396334 | Other | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396349 | Anchor/Guy | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396350 | Other | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396353 | Other | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396361 | Other | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396368 | Pole | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396387 | Other | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396388 | Other | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396390 | Other | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396392 | Cross Arm | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396393 | Other | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396394 | Pole | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396398 | Cross Arm | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396399 | Other | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396400 | Other | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396401 | Pole | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396402 | Cross Arm | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396405 | Cross Arm | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396413 | Cross Arm | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396417 | Cross Arm | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396421 | Other | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396423 | Other | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396431 | Pole | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396432 | Cross Arm | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396437 | Other | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396439 | Cross Arm | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396452 | Other | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396453 | Cross Arm | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396461 | Cross Arm | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396466 | Cross Arm | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396468 | Cross Arm | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396469 | Anchor/Guy | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396470 | Cross Arm | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396476 | Other | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396477 | Other | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396479 | Other | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396481 | Other | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396482 | Other | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396483 | Other | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396485 | Other | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396486 | Other | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396487 | Pole | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396489 | Other | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396492 | Other | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396493 | Cross Arm | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396494 | Pole | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396495 | Pole | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396496 | Pole | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396499 | Cross Arm | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396501 | Pole | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396506 | Pole | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396511 | Anchor/Guy | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396513 | Other | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396514 | Cross Arm | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396517 | Pole | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396519 | Pole | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396522 | Cross Arm | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396524 | Cross Arm | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396525 | Pole | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396526 | Other | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396530 | Pole | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396531 | Cross Arm | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396532 | Anchor/Guy | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396537 | Pole | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396541 | Pole | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396543 | Other | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396546 | Anchor/Guy | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396554 | Anchor/Guy | Tier 3 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396565 | Anchor/Guy | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396576 | Other | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396580 | Pole | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396582 | Pole | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396585 | Anchor/Guy | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396587 | Anchor/Guy | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396591 | Cross Arm | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396596 | Cross Arm | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396597 | Other | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396601 | Pole | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396606 | Pole | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396610 | Pole | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396612 | Other | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396617 | Pole | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396618 | Cross Arm | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396624 | Other | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396629 | Cross Arm | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396631 | Pole | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396637 | Other | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396638 | Insulator and Bushing | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396641 | Other | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396647 | Cross Arm | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396648 | Cross Arm | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396649 | Cross Arm | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396654 | Other | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396659 | Cross Arm | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396671 | Pole | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024396672 | Other | Tier 2 | Distribution | 2023-08-23 | N/A | N/A | N/A
100024409404 | Pole | Tier 3 | Distribution | 2023-08-24 | N/A | N/A | N/A
100024409641 | Anchor/Guy | Tier 3 | Distribution | 2023-08-24 | N/A | N/A | N/A
100024409647 | Other | Tier 3 | Distribution | 2023-08-24 | N/A | N/A | N/A
100024409648 | Anchor/Guy | Tier 3 | Distribution | 2023-08-24 | N/A | N/A | N/A
100024409671 | Other | Tier 2 | Distribution | 2023-08-24 | N/A | N/A | N/A
100024409672 | Other | Tier 2 | Distribution | 2023-08-24 | N/A | N/A | N/A
100024409685 | Cross Arm | Tier 2 | Distribution | 2023-08-24 | N/A | N/A | N/A
100024409686 | Other | Tier 2 | Distribution | 2023-08-24 | N/A | N/A | N/A
100024409687 | Other | Tier 2 | Distribution | 2023-08-24 | N/A | N/A | N/A
100024409690 | Pole | Tier 2 | Distribution | 2023-08-24 | N/A | N/A | N/A
100024409694 | Other | Tier 2 | Distribution | 2023-08-24 | N/A | N/A | N/A
100024409707 | Other | Tier 2 | Distribution | 2023-08-24 | N/A | N/A | N/A
100024409723 | Other | Tier 2 | Distribution | 2023-08-24 | N/A | N/A | N/A
100024409724 | Pole | Tier 2 | Distribution | 2023-08-24 | N/A | N/A | N/A
100024409730 | Other | Tier 2 | Distribution | 2023-08-24 | N/A | N/A | N/A
100024434732 | Anchor/Guy | Tier 3 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434736 | Anchor/Guy | Tier 3 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434737 | Other | Tier 3 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434744 | Pole | Tier 2 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434749 | Anchor/Guy | Tier 2 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434750 | Anchor/Guy | Tier 2 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434751 | Other | Tier 2 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434752 | Other | Tier 2 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434754 | Cross Arm | Tier 2 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434755 | Other | Tier 2 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434756 | Other | Tier 2 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434760 | Conductor | Tier 2 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434761 | Anchor/Guy | Tier 2 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434762 | Other | Tier 2 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434763 | Other | Tier 2 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434765 | Pole | Tier 2 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434770 | Other | Tier 3 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434775 | Conductor | Tier 3 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434780 | Other | Tier 3 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434791 | Other | Tier 3 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434807 | Conductor | Tier 2 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434811 | Other | Tier 2 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434821 | Cross Arm | Tier 2 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434823 | Anchor/Guy | Tier 2 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434824 | Anchor/Guy | Tier 2 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434829 | Other | Tier 2 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434832 | Anchor/Guy | Tier 2 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434833 | Anchor/Guy | Tier 2 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434835 | Anchor/Guy | Tier 2 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434839 | Anchor/Guy | Tier 2 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434844 | Other | Tier 2 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434845 | Pole | Tier 2 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434869 | Anchor/Guy | Tier 3 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434872 | Insulator and Bushing | Tier 3 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434883 | Other | Tier 3 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434885 | Other | Tier 3 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024434897 | Other | Tier 2 | Distribution | 2023-08-28 | N/A | N/A | N/A
100024443703 | Anchor/Guy | Tier 3 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445290 | Other | Tier 3 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445294 | Other | Tier 3 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445296 | Conductor | Tier 3 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445298 | Other | Tier 3 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445303 | Cross Arm | Tier 3 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445304 | Cross Arm | Tier 3 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445309 | Other | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445311 | Other | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445320 | Other | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445321 | Other | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445324 | Pole | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445332 | Other | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445336 | Other | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445337 | Other | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445341 | Anchor/Guy | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445344 | Other | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445350 | Other | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445352 | Conductor | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445362 | Other | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445368 | Cross Arm | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445369 | Other | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445375 | Cross Arm | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445377 | Pole | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445379 | Other | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445382 | Cross Arm | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445384 | Cross Arm | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445385 | Other | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445386 | Cross Arm | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445387 | Cross Arm | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445388 | Cross Arm | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445391 | Conductor | Tier 3 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445395 | Insulator and Bushing | Tier 3 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445396 | Pole | Tier 3 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445401 | Other | Tier 3 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445402 | Pole | Tier 3 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445403 | Cross Arm | Tier 3 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445407 | Other | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445418 | Other | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445421 | Insulator and Bushing | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445426 | Other | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445429 | Other | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445430 | Other | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445440 | Other | Tier 2 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445462 | Cross Arm | Tier 3 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445468 | Cross Arm | Tier 3 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445469 | Cross Arm | Tier 3 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024445470 | Pole | Tier 3 | Distribution | 2023-08-30 | N/A | N/A | N/A
100024467982 | Other | Tier 3 | Distribution | 2023-09-05 | N/A | N/A | N/A
100024467983 | Pole | Tier 3 | Distribution | 2023-09-05 | N/A | N/A | N/A
100024481523 | Conductor | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024481525 | Cross Arm | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024481526 | Pole | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024481527 | Other | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024481528 | Cross Arm | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482111 | Conductor | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482117 | Pole | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482119 | Cross Arm | Tier 3 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482123 | Other | Tier 3 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482138 | Other | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482145 | Pole | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482146 | Pole | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482148 | Other | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482149 | Other | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482153 | Other | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482157 | Other | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482160 | Insulator and Bushing | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482165 | Other | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482166 | Other | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482177 | Anchor/Guy | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482181 | Anchor/Guy | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482182 | Anchor/Guy | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482184 | Anchor/Guy | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482188 | Other | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482191 | Other | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482192 | Anchor/Guy | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482195 | Pole | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482201 | Anchor/Guy | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482208 | Other | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482209 | Other | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482210 | Pole | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482211 | Other | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482212 | Other | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482214 | Anchor/Guy | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482216 | Anchor/Guy | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482217 | Other | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482220 | Anchor/Guy | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482222 | Other | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482223 | Other | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024482227 | Pole | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024487210 | Pole | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024487211 | Pole | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024487216 | Pole | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024487218 | Other | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024487226 | Other | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024487233 | Other | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024487249 | Pole | Tier 3 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024487255 | Conductor | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024487259 | Anchor/Guy | Tier 2 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024487267 | Insulator and Bushing | Tier 3 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024487272 | Pole | Tier 3 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024487280 | Anchor/Guy | Tier 3 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024487283 | Conductor | Tier 3 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024487286 | Insulator and Bushing | Tier 3 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024487287 | Insulator and Bushing | Tier 3 | Distribution | 2023-09-08 | N/A | N/A | N/A
100024489076 | Other | Tier 2 | Distribution | 2023-09-09 | N/A | N/A | N/A
100024489077 | Anchor/Guy | Tier 2 | Distribution | 2023-09-09 | N/A | N/A | N/A
100024489079 | Other | Tier 2 | Distribution | 2023-09-09 | N/A | N/A | N/A
100024489091 | Other | Tier 2 | Distribution | 2023-09-09 | N/A | N/A | N/A
100024489092 | Other | Tier 2 | Distribution | 2023-09-09 | N/A | N/A | N/A
100024489094 | Pole | Tier 2 | Distribution | 2023-09-09 | N/A | N/A | N/A
100024489101 | Cross Arm | Tier 2 | Distribution | 2023-09-09 | N/A | N/A | N/A
100024489102 | Cross Arm | Tier 2 | Distribution | 2023-09-09 | N/A | N/A | N/A
100024489103 | Pole | Tier 2 | Distribution | 2023-09-09 | N/A | N/A | N/A
100024489105 | Other | Tier 2 | Distribution | 2023-09-09 | N/A | N/A | N/A
100024489107 | Other | Tier 2 | Distribution | 2023-09-09 | N/A | N/A | N/A
100024489137 | Other | Tier 2 | Distribution | 2023-09-09 | N/A | N/A | N/A
100024489144 | Pole | Tier 2 | Distribution | 2023-09-09 | N/A | N/A | N/A
100024489151 | Cross Arm | Tier 2 | Distribution | 2023-09-09 | N/A | N/A | N/A
100024489159 | Other | Tier 2 | Distribution | 2023-09-09 | N/A | N/A | N/A
100024489168 | Conductor | Tier 2 | Distribution | 2023-09-09 | N/A | N/A | N/A
100024489175 | Conductor | Tier 2 | Distribution | 2023-09-09 | N/A | N/A | N/A
100024489176 | Anchor/Guy | Tier 2 | Distribution | 2023-09-09 | N/A | N/A | N/A
100024489181 | Pole | Tier 2 | Distribution | 2023-09-09 | N/A | N/A | N/A
100024489189 | Pole | Tier 2 | Distribution | 2023-09-09 | N/A | N/A | N/A
100024497174 | Other | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497175 | Pole | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497177 | Other | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497178 | Other | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497180 | Other | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497195 | Cross Arm | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497196 | Other | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497197 | Other | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497201 | Other | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497202 | Conductor | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497203 | Pole | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497204 | Other | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497207 | Other | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497208 | Other | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497211 | Pole | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497213 | Anchor/Guy | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497215 | Other | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497216 | Other | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497217 | Pole | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497230 | Other | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497233 | Other | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497236 | Pole | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497238 | Other | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497243 | Anchor/Guy | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497245 | Other | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497246 | Conductor | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497250 | Other | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497251 | Other | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497255 | Anchor/Guy | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497260 | Conductor | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497264 | Other | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497265 | Insulator and Bushing | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497266 | Other | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497269 | Other | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497270 | Other | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497272 | Other | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497277 | Other | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497279 | Pole | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497281 | Other | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497283 | Other | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497284 | Cross Arm | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497291 | Pole | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497293 | Pole | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497300 | Conductor | Tier 2 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497304 | Cross Arm | Tier 3 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497305 | Pole | Tier 3 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497308 | Pole | Tier 3 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497313 | Other | Tier 3 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024497321 | Other | Tier 3 | Distribution | 2023-09-11 | N/A | N/A | N/A
100024501784 | Other | Tier 3 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024501963 | Other | Tier 2 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024501969 | Pole | Tier 3 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024501972 | Pole | Tier 3 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024501976 | Pole | Tier 2 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024501977 | Cross Arm | Tier 2 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024501978 | Insulator and Bushing | Tier 2 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024501979 | Other | Tier 2 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024501980 | Cross Arm | Tier 2 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024501982 | Pole | Tier 2 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024501984 | Cross Arm | Tier 2 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024501985 | Cross Arm | Tier 2 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024501986 | Cross Arm | Tier 2 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024501987 | Cross Arm | Tier 2 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024501988 | Pole | Tier 2 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024501990 | Anchor/Guy | Tier 2 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024501993 | Cross Arm | Tier 2 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024501999 | Other | Tier 2 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024502001 | Pole | Tier 2 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024502002 | Cross Arm | Tier 2 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024502004 | Cross Arm | Tier 2 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024502005 | Pole | Tier 2 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024502009 | Cross Arm | Tier 2 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024502013 | Other | Tier 3 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024502015 | Other | Tier 3 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024502016 | Pole | Tier 3 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024502017 | Other | Tier 3 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024502020 | Anchor/Guy | Tier 3 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024502026 | Pole | Tier 3 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024502028 | Pole | Tier 3 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024502061 | Other | Tier 3 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024502062 | Anchor/Guy | Tier 3 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024502063 | Anchor/Guy | Tier 3 | Distribution | 2023-09-12 | N/A | N/A | N/A
100024505466 | Cross Arm | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024505468 | Pole | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507171 | Other | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507172 | Conductor | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507173 | Pole | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507174 | Other | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507175 | Other | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507177 | Other | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507180 | Cross Arm | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507183 | Cross Arm | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507184 | Other | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507191 | Cross Arm | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507196 | Other | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507197 | Pole | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507204 | Other | Tier 3 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507208 | Anchor/Guy | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507210 | Anchor/Guy | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507220 | Anchor/Guy | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507222 | Anchor/Guy | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507223 | Other | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507229 | Pole | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507234 | Anchor/Guy | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507238 | Other | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507239 | Other | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507243 | Other | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507249 | Conductor | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507252 | Other | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507253 | Anchor/Guy | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507260 | Anchor/Guy | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507263 | Other | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507264 | Other | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507265 | Other | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507267 | Anchor/Guy | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507270 | Conductor | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507272 | Other | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507277 | Conductor | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507279 | Other | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507284 | Other | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507286 | Pole | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507288 | Anchor/Guy | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507294 | Pole | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507297 | Other | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507301 | Other | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507308 | Other | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507318 | Other | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507326 | Other | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507328 | Conductor | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024507329 | Conductor | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024512418 | Pole | Tier 3 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024512421 | Pole | Tier 3 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024512423 | Pole | Tier 3 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024512442 | Cross Arm | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024512451 | Cross Arm | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024512455 | Other | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024512457 | Cross Arm | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024512460 | Cross Arm | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024512462 | Cross Arm | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024512463 | Cross Arm | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024512465 | Cross Arm | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024512467 | Other | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024512468 | Other | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024512473 | Cross Arm | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024512478 | Cross Arm | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024512479 | Other | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024512485 | Other | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024512486 | Other | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024512492 | Cross Arm | Tier 3 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024512496 | Pole | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024512504 | Pole | Tier 2 | Distribution | 2023-09-14 | N/A | N/A | N/A
100024519842 | Cross Arm | Tier 2 | Distribution | 2023-09-15 | N/A | N/A | N/A
100024519847 | Other | Tier 2 | Distribution | 2023-09-15 | N/A | N/A | N/A
100024521070 | Pole | Tier 2 | Distribution | 2023-09-15 | N/A | N/A | N/A
100024521077 | Other | Tier 2 | Distribution | 2023-09-15 | N/A | N/A | N/A
100024521079 | Cross Arm | Tier 2 | Distribution | 2023-09-15 | N/A | N/A | N/A
100024521082 | Cross Arm | Tier 2 | Distribution | 2023-09-15 | N/A | N/A | N/A
100024521084 | Cross Arm | Tier 2 | Distribution | 2023-09-15 | N/A | N/A | N/A
100024521087 | Other | Tier 2 | Distribution | 2023-09-15 | N/A | N/A | N/A
100024521089 | Other | Tier 2 | Distribution | 2023-09-15 | N/A | N/A | N/A
100024521090 | Other | Tier 2 | Distribution | 2023-09-15 | N/A | N/A | N/A
100024521091 | Other | Tier 2 | Distribution | 2023-09-15 | N/A | N/A | N/A
100024521092 | Pole | Tier 2 | Distribution | 2023-09-15 | N/A | N/A | N/A
100024521096 | Cross Arm | Tier 2 | Distribution | 2023-09-15 | N/A | N/A | N/A
100024521099 | Cross Arm | Tier 2 | Distribution | 2023-09-15 | N/A | N/A | N/A
100024521103 | Other | Tier 2 | Distribution | 2023-09-15 | N/A | N/A | N/A
100024521105 | Other | Tier 2 | Distribution | 2023-09-15 | N/A | N/A | N/A
100024521109 | Cross Arm | Tier 2 | Distribution | 2023-09-15 | N/A | N/A | N/A
100024532867 | Other | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533321 | Other | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533323 | Conductor | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533324 | Conductor | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533328 | Other | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533331 | Other | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533333 | Other | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533341 | Other | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533342 | Insulator and Bushing | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533344 | Other | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533345 | Insulator and Bushing | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533354 | Other | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533355 | Cross Arm | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533358 | Cross Arm | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533359 | Other | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533361 | Cross Arm | Tier 3 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533363 | Other | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533365 | Cross Arm | Tier 3 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533366 | Cross Arm | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533370 | Other | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533371 | Other | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533372 | Other | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533374 | Cross Arm | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533382 | Anchor/Guy | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533383 | Other | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533385 | Cross Arm | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533387 | Cross Arm | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533388 | Insulator and Bushing | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533391 | Pole | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533395 | Other | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533401 | Pole | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533404 | Other | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533408 | Cross Arm | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533410 | Other | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533411 | Cross Arm | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533413 | Other | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533414 | Conductor | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533415 | Cross Arm | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533417 | Cross Arm | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533421 | Pole | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533422 | Cross Arm | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533426 | Other | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533427 | Pole | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533428 | Anchor/Guy | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024533433 | Pole | Tier 2 | Distribution | 2023-09-18 | N/A | N/A | N/A
100024539684 | Other | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539685 | Other | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539687 | Cross Arm | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539688 | Other | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539693 | Anchor/Guy | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539694 | Pole | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539697 | Pole | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539702 | Other | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539712 | Other | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539718 | Cross Arm | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539720 | Insulator and Bushing | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539726 | Pole | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539730 | Cross Arm | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539732 | Other | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539733 | Anchor/Guy | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539734 | Pole | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539739 | Cross Arm | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539744 | Other | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539745 | Other | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539746 | Cross Arm | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539747 | Pole | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539756 | Pole | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539758 | Other | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539760 | Cross Arm | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539764 | Other | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539766 | Pole | Tier 3 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539772 | Cross Arm | Tier 3 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539778 | Conductor | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539781 | Other | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539782 | Cross Arm | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539785 | Other | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539788 | Other | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539789 | Conductor | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539793 | Other | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539795 | Pole | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539802 | Cross Arm | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539812 | Other | Tier 3 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539815 | Pole | Tier 3 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539826 | Other | Tier 3 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539828 | Other | Tier 3 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539831 | Other | Tier 3 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539836 | Cross Arm | Tier 3 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539837 | Other | Tier 3 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539839 | Other | Tier 3 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539843 | Other | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539847 | Cross Arm | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539850 | Cross Arm | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539853 | Cross Arm | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539854 | Cross Arm | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539855 | Pole | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539857 | Pole | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539858 | Other | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539859 | Other | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539862 | Other | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024539870 | Pole | Tier 2 | Distribution | 2023-09-19 | N/A | N/A | N/A
100024545142 | Conductor | Tier 2 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545146 | Cross Arm | Tier 2 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545148 | Anchor/Guy | Tier 2 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545389 | Other | Tier 2 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545392 | Other | Tier 2 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545397 | Cross Arm | Tier 2 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545401 | Conductor | Tier 2 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545406 | Cross Arm | Tier 3 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545407 | Cross Arm | Tier 3 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545408 | Cross Arm | Tier 3 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545409 | Pole | Tier 3 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545410 | Cross Arm | Tier 3 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545414 | Pole | Tier 3 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545416 | Cross Arm | Tier 3 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545419 | Cross Arm | Tier 3 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545420 | Other | Tier 3 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545423 | Cross Arm | Tier 3 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545467 | Cross Arm | Tier 3 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545468 | Pole | Tier 3 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545470 | Cross Arm | Tier 3 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545473 | Cross Arm | Tier 3 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545475 | Pole | Tier 3 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545476 | Other | Tier 3 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545478 | Cross Arm | Tier 3 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545479 | Cross Arm | Tier 3 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545480 | Cross Arm | Tier 3 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545481 | Cross Arm | Tier 3 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545486 | Pole | Tier 3 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545487 | Cross Arm | Tier 3 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545490 | Pole | Tier 2 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545497 | Anchor/Guy | Tier 2 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545504 | Anchor/Guy | Tier 2 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545509 | Other | Tier 2 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545510 | Conductor | Tier 2 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545512 | Other | Tier 2 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545513 | Cross Arm | Tier 2 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545565 | Other | Tier 3 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545566 | Other | Tier 3 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545569 | Other | Tier 3 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545570 | Other | Tier 3 | Distribution | 2023-09-20 | N/A | N/A | N/A
100024545571 | Other | Tier 3 | Distribution | 2023-09-20 | N/A | N/A | N/A
125650 | Complete Wood Pole | Tier 2 | Transmission | 2021-09-01 | 2023-08-02 | Level 2 | N/A
132888 | Pole Top | Tier 2 | Transmission | 2022-08-16 | 2023-08-16 | Level 2 | N/A
132889 | Complete Wood Pole | Tier 2 | Transmission | 2022-08-16 | 2023-08-16 | Level 2 | N/A
131168 | Shieldwire Attachment Point | Tier 2 | Transmission | 2023-01-09 | 2024-01-09 | Level 2 | N/A
129619 | Stub Pole - Wood | Tier 2 | Transmission | 2023-01-10 | 2024-01-10 | Level 2 | N/A
129621 | Stub Pole - Anchor Guy | Tier 2 | Transmission | 2023-01-10 | 2024-01-10 | Level 2 | N/A
129636 | Bolt(s) | Tier 2 | Transmission | 2023-01-10 | 2024-01-10 | Level 2 | N/A
129638 | Pole Butt | Tier 2 | Transmission | 2023-01-10 | 2024-01-10 | Level 2 | N/A
130388 | Complete Wood Pole | Tier 2 | Transmission | 2023-01-10 | 2024-01-10 | Level 2 | N/A
128494 | Pole Butt | Tier 2 | Transmission | 2023-01-12 | 2024-01-12 | Level 2 | N/A
129595 | Pole Butt | Tier 2 | Transmission | 2023-04-21 | 2024-01-21 | Level 2 | N/A
129596 | Cross Arms | Tier 2 | Transmission | 2023-04-21 | 2024-01-21 | Level 2 | N/A
129597 | Complete Wood Pole | Tier 2 | Transmission | 2023-04-21 | 2024-01-21 | Level 2 | N/A
130832 | Complete Wood Pole | Tier 2 | Transmission | 2023-04-21 | 2024-01-21 | Level 2 | N/A
133482 | Complete Wood Pole | Tier 2 | Transmission | 2023-01-22 | 2024-01-22 | Level 2 | N/A
130325 | Complete Wood Pole | Tier 2 | Transmission | 2023-01-27 | 2024-01-27 | Level 2 | N/A
128867 | Sign Warning (With Man) | Tier 2 | Transmission | 2023-02-02 | 2024-02-02 | Level 3 | N/A
127305 | Signs-Danger | Tier 2 | Transmission | 2023-02-10 | 2024-02-08 | Level 3 | N/A
127306 | Pole Ground (Wire) | Tier 2 | Transmission | 2023-02-10 | 2024-02-08 | Level 2 | N/A
127307 | Pole Ground (Wire) | Tier 2 | Transmission | 2023-02-10 | 2024-02-08 | Level 2 | N/A
127308 | Signs-Danger | Tier 2 | Transmission | 2023-02-10 | 2024-02-08 | Level 3 | N/A
127314 | Signs-Danger | Tier 2 | Transmission | 2023-02-10 | 2024-02-08 | Level 3 | N/A
127315 | Pole Ground (Wire) | Tier 2 | Transmission | 2023-02-10 | 2024-02-08 | Level 2 | N/A
127319 | Signs-Danger | Tier 2 | Transmission | 2023-02-10 | 2024-02-08 | Level 3 | N/A
127321 | Signs-Danger | Tier 2 | Transmission | 2023-02-10 | 2024-02-08 | Level 3 | N/A
127322 | Signs-Danger | Tier 2 | Transmission | 2023-02-10 | 2024-02-08 | Level 3 | N/A
127324 | Signs-Danger | Tier 2 | Transmission | 2023-02-10 | 2024-02-08 | Level 3 | N/A
127326 | Signs-Danger | Tier 2 | Transmission | 2023-02-09 | 2024-02-08 | Level 3 | N/A
127329 | Signs-Danger | Tier 2 | Transmission | 2023-02-09 | 2024-02-08 | Level 3 | N/A
127331 | Signs-Danger | Tier 2 | Transmission | 2023-02-09 | 2024-02-08 | Level 3 | N/A
127332 | Hardware | Tier 2 | Transmission | 2023-02-09 | 2024-02-08 | Level 2 | N/A
128803 | Guy Wire - OH | Tier 2 | Transmission | 2023-02-09 | 2024-02-09 | Level 2 | N/A
128805 | Cold End Clevis-Shackle | Tier 2 | Transmission | 2023-02-09 | 2024-02-09 | Level 2 | N/A
128806 | Hardware | Tier 2 | Transmission | 2023-02-09 | 2024-02-09 | Level 2 | N/A
128807 | Insulators-Ceramic, Standard, 20K | Tier 2 | Transmission | 2023-02-09 | 2024-02-09 | Level 2 | N/A
132821 | Pole Butt | Tier 2 | Transmission | 2023-02-09 | 2024-02-09 | Level 2 | N/A
132822 | Complete Wood Pole | Tier 2 | Transmission | 2023-02-09 | 2024-02-09 | Level 2 | N/A
121727 | Insulators-Ceramic, Standard, 50K | Tier 3 | Transmission | 2020-12-15 | 2024-02-15 | Level 2 | N/A
131396 | Shoe Pin-Bolt | Tier 3 | Transmission | 2023-08-17 | 2024-02-16 | Level 2 | N/A
131397 | Shoe Pin-Bolt | Tier 3 | Transmission | 2023-08-17 | 2024-02-16 | Level 2 | N/A
131416 | Shoe Pin-Bolt | Tier 3 | Transmission | 2023-08-17 | 2024-02-16 | Level 2 | N/A
132313 | Shieldwire Attachment Point | Tier 3 | Transmission | 2023-08-31 | 2024-02-29 | Level 2 | N/A
130537 | Anti-Climb Barrier | Tier 2 | Transmission | 2023-06-20 | 2024-03-19 | Level 2 | N/A
130538 | Jumper (Complete) | Tier 2 | Transmission | 2023-06-20 | 2024-03-19 | Level 2 | N/A
130539 | Complete Tower | Tier 2 | Transmission | 2023-06-20 | 2024-03-19 | Level 2 | N/A
130540 | Insulators-Ceramic, Standard, 20K | Tier 2 | Transmission | 2023-06-20 | 2024-03-19 | Level 2 | N/A
130541 | Conductor Strand(s) | Tier 2 | Transmission | 2023-06-20 | 2024-03-19 | Level 2 | N/A
130934 | Connectors | Tier 2 | Transmission | 2023-06-30 | 2024-03-19 | Level 2 | N/A
133529 | Complete Tower | Tier 2 | Transmission | 2023-07-07 | 2024-03-19 | Level 2 | N/A
129035 | Insulators-Post, NCI, 69kv, Long | Tier 2 | Transmission | 2023-03-24 | 2024-03-23 | Level 2 | N/A
129036 | Insulators-Post, NCI, 69kv, Long | Tier 2 | Transmission | 2023-03-24 | 2024-03-23 | Level 2 | N/A
130531 | Hardware | Tier 2 | Transmission | 2023-06-28 | 2024-03-27 | Level 2 | N/A
130532 | Insulators-NCI, 230kv | Tier 2 | Transmission | 2023-06-28 | 2024-03-27 | Level 2 | N/A
130533 | Cold End Cotter Key(s) | Tier 2 | Transmission | 2023-06-28 | 2024-03-27 | Level 2 | N/A
130534 | Shoe Nut(s) | Tier 2 | Transmission | 2023-06-28 | 2024-03-27 | Level 2 | N/A
130535 | Complete Tower | Tier 2 | Transmission | 2023-06-28 | 2024-03-27 | Level 2 | N/A
132874 | Insulators-Ceramic, Standard, 30K | Tier 2 | Transmission | 2023-09-27 | 2024-03-27 | Level 2 | N/A
133152 | Footings (Complete) | Tier 3 | Transmission | 2023-10-29 | 2024-03-28 | Level 2 | N/A
130489 | Footings (Complete) | Tier 2 | Transmission | 2023-08-15 | 2024-03-29 | Level 2 | N/A
130492 | Footings (Complete) | Tier 2 | Transmission | 2023-03-30 | 2024-03-29 | Level 2 | N/A
129107 | Preform Strand(s) | Tier 2 | Transmission | 2023-04-01 | 2024-04-01 | Level 2 | N/A
129108 | Preform | Tier 2 | Transmission | 2023-04-01 | 2024-04-01 | Level 2 | N/A
129110 | Corona Ring(s) | Tier 2 | Transmission | 2023-04-01 | 2024-04-01 | Level 2 | N/A
130573 | Footings (Complete) | Tier 2 | Transmission | 2023-04-10 | 2024-04-09 | Level 2 | N/A
132647 | Footings (Complete) | Tier 3 | Transmission | 2023-10-12 | 2024-04-11 | Level 2 | N/A
129618 | Insulators-Ceramic, Post, 69kv | Tier 2 | Transmission | 2023-04-21 | 2024-04-20 | Level 2 | N/A
129622 | Cross Arms | Tier 2 | Transmission | 2023-04-21 | 2024-04-20 | Level 2 | N/A
129640 | Guy Wire - OH | Tier 2 | Transmission | 2023-04-21 | 2024-04-20 | Level 2 | N/A
129641 | Complete Wood Pole | Tier 2 | Transmission | 2023-04-21 | 2024-04-20 | Level 2 | N/A
130829 | Complete Wood Pole | Tier 2 | Transmission | 2023-04-21 | 2024-04-20 | Level 2 | N/A
130831 | Complete Wood Pole | Tier 2 | Transmission | 2023-04-21 | 2024-04-20 | Level 2 | N/A
133401 | Pole Butt | Tier 3 | Transmission | 2023-11-21 | 2024-04-21 | Level 2 | N/A
133402 | Pole Butt | Tier 3 | Transmission | 2023-11-21 | 2024-04-21 | Level 2 | N/A
133404 | Pole Butt | Tier 3 | Transmission | 2023-11-21 | 2024-04-21 | Level 2 | N/A
133403 | Pole Butt | Tier 3 | Transmission | 2023-11-21 | 2024-05-01 | Level 2 | N/A
131169 | Shieldwire Attachment Point | Tier 2 | Transmission | 2023-05-10 | 2024-05-09 | Level 2 | N/A
130556 | Footings (Complete) | Tier 2 | Transmission | 2023-05-11 | 2024-05-10 | Level 2 | N/A
130574 | Footings (Complete) | Tier 2 | Transmission | 2023-05-17 | 2024-05-16 | Level 2 | N/A
130700 | Area Around Footer(s) | Tier 2 | Transmission | 2023-05-17 | 2024-05-16 | Level 2 | N/A
130371 | Shoe Nut(s) | Tier 2 | Transmission | 2023-05-19 | 2024-05-18 | Level 2 | N/A
130529 | Anti-Climb Barrier | Tier 2 | Transmission | 2023-06-20 | 2024-05-19 | Level 2 | N/A
130530 | Conductor Strand(s) | Tier 2 | Transmission | 2023-06-20 | 2024-05-19 | Level 2 | N/A
130595 | Coated Glass 30K | Tier 2 | Transmission | 2023-06-20 | 2024-05-19 | Level 2 | N/A
132106 | Area Around Structure | Tier 3 | Transmission | 2023-11-20 | 2024-05-20 | Level 2 | N/A
133399 | Pole Butt | Tier 3 | Transmission | 2023-11-21 | 2024-05-21 | Level 2 | N/A
133622 | Other(Specify) | Tier 2 | Transmission | 2023-05-25 | 2024-05-24 | Level 2 | N/A
133623 | Other(Specify) | Tier 2 | Transmission | 2023-05-25 | 2024-05-24 | Level 2 | N/A
129669 | Anchor Rods | Tier 2 | Transmission | 2023-05-23 | 2024-05-30 | Level 2 | N/A
129699 | Stub Pole - Anchor Guy | Tier 2 | Transmission | 2023-05-31 | 2024-05-30 | Level 2 | N/A
129700 | Stub Pole - Anchor Guy | Tier 2 | Transmission | 2023-05-31 | 2024-05-30 | Level 2 | N/A
131196 | Complete Wood Pole | Tier 2 | Transmission | 2023-05-31 | 2024-05-30 | Level 2 | N/A
133624 | Signs-High Voltage-At Top | Tier 2 | Transmission | 2023-10-06 | 2024-05-30 | Level 3 | N/A
133625 | Other(Specify) | Tier 2 | Transmission | 2023-05-31 | 2024-05-30 | Level 2 | N/A
129696 | Complete Wood Pole | Tier 2 | Transmission | 2023-06-02 | 2024-06-01 | Level 2 | N/A
130397 | Jumper (Complete) | Tier 2 | Transmission | 2023-06-02 | 2024-06-01 | Level 2 | N/A
131195 | Complete Wood Pole | Tier 2 | Transmission | 2023-06-02 | 2024-06-01 | Level 2 | N/A
130387 | Aerial Marker Sphere(s) | Tier 2 | Transmission | 2023-06-11 | 2024-06-10 | Level 2 | N/A
131176 | Jumper - Connector | Tier 2 | Transmission | 2023-06-11 | 2024-06-10 | Level 2 | N/A
131186 | Hot End Cotter Key(s) | Tier 2 | Transmission | 2023-06-11 | 2024-06-10 | Level 2 | N/A
131188 | Bolted Spacer | Tier 2 | Transmission | 2023-06-11 | 2024-06-10 | Level 2 | N/A
133700 | Bolted Spacer | Tier 2 | Transmission | 2023-06-11 | 2024-06-10 | Level 2 | N/A
130461 | Insulators-Ceramic, Standard, 30K | Tier 2 | Transmission | 2023-06-13 | 2024-06-12 | Level 2 | N/A
130466 | Conductor Strand(s) | Tier 2 | Transmission | 2023-06-13 | 2024-06-12 | Level 2 | N/A
130515 | Anti-Climb Barrier | Tier 2 | Transmission | 2023-06-13 | 2024-06-12 | Level 2 | N/A
130516 | Complete Tower | Tier 2 | Transmission | 2023-06-13 | 2024-06-12 | Level 2 | N/A
130520 | Member (Steel Tower) | Tier 2 | Transmission | 2023-06-13 | 2024-06-12 | Level 2 | N/A
128264 | Cold End Cotter Key(s) | Tier 2 | Transmission | 2023-06-20 | 2024-06-19 | Level 2 | N/A
128303 | Complete Wood Pole | Tier 2 | Transmission | 2023-06-20 | 2024-06-19 | Level 2 | N/A
128330 | Concrete | Tier 2 | Transmission | 2023-06-20 | 2024-06-19 | Level 2 | N/A
130598 | Aerial Marker Sphere(s) | Tier 2 | Transmission | 2023-06-20 | 2024-06-19 | Level 2 | N/A
130599 | Shieldwire Attachment Point | Tier 2 | Transmission | 2023-06-20 | 2024-06-19 | Level 2 | N/A
129893 | Footings (Complete) | Tier 2 | Transmission | 2022-12-24 | 2024-06-23 | Level 2 | N/A
130047 | Bolted Spacer | Tier 2 | Transmission | 2023-06-28 | 2024-06-27 | Level 2 | N/A
130846 | Shieldwire Attachment Point | Tier 2 | Transmission | 2023-06-30 | 2024-06-29 | Level 2 | N/A
130847 | Hardware | Tier 2 | Transmission | 2023-06-30 | 2024-06-29 | Level 2 | N/A
130848 | Damper (Complete) | Tier 2 | Transmission | 2023-06-30 | 2024-06-29 | Level 2 | N/A
133530 | Stub Angles | Tier 2 | Transmission | 2023-07-06 | 2024-07-05 | Level 2 | N/A
130050 | Other(Specify) | Tier 2 | Transmission | 2023-07-10 | 2024-07-09 | Level 2 | N/A
130055 | Conductor Weight(s) | Tier 2 | Transmission | 2023-07-10 | 2024-07-09 | Level 2 | N/A
130779 | Hot End Bolt(s) | Tier 2 | Transmission | 2023-07-17 | 2024-07-16 | Level 2 | N/A
128145 | Pole Butt | Tier 3 | Transmission | 2023-06-19 | 2024-07-19 | Level 2 | N/A
130296 | Insulators-Ceramic, Standard, 20K | Tier 2 | Transmission | 2023-07-28 | 2024-07-22 | Level 2 | N/A
133173 | Complete Steel Pole | Tier 3 | Transmission | 2023-07-24 | 2024-07-23 | Level 2 | N/A
131006 | Cold End Bolt(s) | Tier 2 | Transmission | 2023-07-26 | 2024-07-25 | Level 2 | N/A
128478 | Insulators-Ceramic, Standard, 30K | Tier 2 | Transmission | 2023-07-28 | 2024-07-27 | Level 2 | N/A
128452 | Insulators-Ceramic, Standard, 30K | Tier 2 | Transmission | 2023-07-30 | 2024-07-30 | Level 2 | N/A
133607 | Pole Butt | Tier 2 | Transmission | 2023-02-13 | 2024-08-13 | Level 2 | N/A
130471 | Cold End Pin(s) | Tier 2 | Transmission | 2023-08-15 | 2024-08-14 | Level 2 | N/A
130472 | Insulators-Ceramic, Standard, 30K | Tier 2 | Transmission | 2023-08-15 | 2024-08-14 | Level 2 | N/A
130486 | Complete Tower | Tier 2 | Transmission | 2023-08-15 | 2024-08-14 | Level 2 | N/A
130487 | Insulators-Ceramic, Standard, 20K | Tier 2 | Transmission | 2023-08-15 | 2024-08-14 | Level 2 | N/A
130398 | Insulators-Ceramic, Standard, 30K | Tier 2 | Transmission | 2023-08-16 | 2024-08-15 | Level 2 | N/A
130399 | Ground Grid Taps | Tier 2 | Transmission | 2023-08-16 | 2024-08-15 | Level 2 | N/A
132266 | Shieldwire Attachment Point | Tier 3 | Transmission | 2023-09-06 | 2024-09-05 | Level 2 | N/A
132314 | Ground Connection | Tier 3 | Transmission | 2023-09-06 | 2024-09-05 | Level 2 | N/A
128958 | Footings (Complete) | Tier 2 | Transmission | 2023-09-07 | 2024-09-06 | Level 2 | N/A
128964 | Insulators-NCI, 69kv | Tier 2 | Transmission | 2023-09-07 | 2024-09-06 | Level 2 | N/A
128980 | Insulators-Post, NCI, 69kv, Long | Tier 2 | Transmission | 2023-09-13 | 2024-09-12 | Level 2 | N/A
128981 | Pole Butt | Tier 2 | Transmission | 2023-09-13 | 2024-09-12 | Level 2 | N/A
128993 | Fiberglass Rod | Tier 2 | Transmission | 2023-09-13 | 2024-09-12 | Level 2 | N/A
128994 | Insulators-Post, NCI, 69kv, Long | Tier 2 | Transmission | 2023-09-13 | 2024-09-12 | Level 2 | N/A
128997 | Anchor Rods | Tier 2 | Transmission | 2023-09-13 | 2024-09-12 | Level 2 | N/A
128998 | Anchor Rods | Tier 2 | Transmission | 2023-09-13 | 2024-09-12 | Level 2 | N/A
128999 | Anchor Rods | Tier 2 | Transmission | 2023-09-13 | 2024-09-12 | Level 2 | N/A
129000 | Armor Rod Strand(s) | Tier 2 | Transmission | 2023-09-13 | 2024-09-12 | Level 2 | N/A
129001 | Fiberglass Rod | Tier 2 | Transmission | 2023-09-13 | 2024-09-12 | Level 2 | N/A
129002 | Insulators-Post, NCI, 69kv, Long | Tier 2 | Transmission | 2023-09-13 | 2024-09-12 | Level 2 | N/A
129003 | Pole Butt | Tier 2 | Transmission | 2023-09-13 | 2024-09-12 | Level 2 | N/A
129010 | Insulators-Post, NCI, 69kv, Long | Tier 2 | Transmission | 2023-09-13 | 2024-09-12 | Level 2 | N/A
129032 | Bolt(s) | Tier 2 | Transmission | 2023-09-13 | 2024-09-12 | Level 2 | N/A
129039 | Pole Butt | Tier 2 | Transmission | 2023-09-13 | 2024-09-12 | Level 2 | N/A
129067 | Complete Steel Pole | Tier 2 | Transmission | 2023-09-13 | 2024-09-12 | Level 2 | N/A
129084 | Complete Steel Pole | Tier 2 | Transmission | 2023-09-13 | 2024-09-12 | Level 2 | N/A
129129 | Fiberglass Rod | Tier 2 | Transmission | 2023-09-13 | 2024-09-12 | Level 2 | N/A
129130 | Cold End Cotter Key(s) | Tier 2 | Transmission | 2023-09-13 | 2024-09-12 | Level 2 | N/A
132763 | Complete Steel Pole | Tier 2 | Transmission | 2023-09-13 | 2024-09-12 | Level 2 | N/A
132764 | Complete Steel Pole | Tier 2 | Transmission | 2023-09-13 | 2024-09-12 | Level 2 | N/A
130549 | Footings (Complete) | Tier 2 | Transmission | 2023-09-14 | 2024-09-13 | Level 2 | N/A
130550 | Cable (Complete) | Tier 2 | Transmission | 2023-09-14 | 2024-09-13 | Level 2 | N/A
130551 | Area Around Footer(s) | Tier 2 | Transmission | 2023-09-14 | 2024-09-13 | Level 2 | N/A
130552 | Complete Tower | Tier 2 | Transmission | 2023-09-14 | 2024-09-13 | Level 2 | N/A
130553 | Ground Grid Taps | Tier 2 | Transmission | 2023-09-14 | 2024-09-13 | Level 2 | N/A
130589 | Pole Top | Tier 2 | Transmission | 2023-09-15 | 2024-09-14 | Level 2 | N/A
130674 | Other(Specify) | Tier 2 | Transmission | 2023-09-15 | 2024-09-14 | Level 2 | N/A
130802 | Insulators-NCI, 138kv | Tier 2 | Transmission | 2023-09-15 | 2024-09-14 | Level 2 | N/A
130701 | Anti-Climb Barrier | Tier 2 | Transmission | 2023-09-18 | 2024-09-17 | Level 2 | N/A
129134 | Signs-High Voltage-At Top | Tier 2 | Transmission | 2023-09-22 | 2024-09-21 | Level 3 | N/A
133609 | Complete Steel Pole | Tier 2 | Transmission | 2023-03-29 | 2024-09-26 | Level 2 | N/A
130778 | Hot End Cotter Key(s) | Tier 2 | Transmission | 2023-06-29 | 2024-09-28 | Level 2 | N/A
131865 | Shoe Pin-Bolt | Tier 3 | Transmission | 2023-10-02 | 2024-10-01 | Level 2 | N/A
131876 | Shoe Pin-Bolt | Tier 3 | Transmission | 2023-10-02 | 2024-10-01 | Level 2 | N/A
129376 | Shoe (Complete) | Tier 2 | Transmission | 2023-10-04 | 2024-10-03 | Level 2 | N/A
129385 | Stub Pole - Anchor Guy | Tier 2 | Transmission | 2023-10-04 | 2024-10-03 | Level 2 | N/A
129386 | Shoe (Complete) | Tier 2 | Transmission | 2023-10-04 | 2024-10-03 | Level 2 | N/A
129387 | Stub Pole - Anchor Guy | Tier 2 | Transmission | 2023-10-04 | 2024-10-03 | Level 2 | N/A
129388 | Pole Ground (Wire) | Tier 2 | Transmission | 2023-10-04 | 2024-10-03 | Level 2 | N/A
129392 | Preform | Tier 2 | Transmission | 2023-10-04 | 2024-10-03 | Level 2 | N/A
129393 | Hardware | Tier 2 | Transmission | 2023-10-04 | 2024-10-03 | Level 2 | N/A
129394 | Nuts | Tier 2 | Transmission | 2023-10-04 | 2024-10-03 | Level 2 | N/A
129395 | Preform | Tier 2 | Transmission | 2023-10-04 | 2024-10-03 | Level 2 | N/A
129416 | Footings (Complete) | Tier 2 | Transmission | 2023-10-04 | 2024-10-03 | Level 2 | N/A
129459 | Tieline Identification Tags | Tier 2 | Transmission | 2023-10-04 | 2024-10-03 | Level 2 | N/A
129462 | Footings (Complete) | Tier 2 | Transmission | 2023-10-04 | 2024-10-03 | Level 2 | N/A
129464 | Preform | Tier 2 | Transmission | 2023-10-04 | 2024-10-03 | Level 2 | N/A
129468 | Insulators-Post, NCI, 69kv, Long | Tier 2 | Transmission | 2023-10-04 | 2024-10-03 | Level 2 | N/A
129469 | Pole Butt | Tier 2 | Transmission | 2023-10-04 | 2024-10-03 | Level 2 | N/A
129470 | Anchor Rods | Tier 2 | Transmission | 2023-10-04 | 2024-10-03 | Level 2 | N/A
129471 | Pole Butt | Tier 2 | Transmission | 2023-10-04 | 2024-10-03 | Level 2 | N/A
129514 | Anchor Rods | Tier 2 | Transmission | 2023-10-04 | 2024-10-03 | Level 2 | N/A
129516 | Preform | Tier 2 | Transmission | 2023-10-04 | 2024-10-03 | Level 2 | N/A
129517 | Anchor Rods | Tier 2 | Transmission | 2023-10-04 | 2024-10-03 | Level 2 | N/A
129518 | Connectors | Tier 2 | Transmission | 2023-10-04 | 2024-10-03 | Level 2 | N/A
129519 | Cross Arms | Tier 2 | Transmission | 2023-10-04 | 2024-10-03 | Level 2 | N/A
129520 | Shoe Nut(s) | Tier 2 | Transmission | 2023-10-04 | 2024-10-03 | Level 2 | N/A
129521 | Pole Top | Tier 2 | Transmission | 2023-10-04 | 2024-10-03 | Level 2 | N/A
129574 | Bolt(s) | Tier 2 | Transmission | 2023-10-04 | 2024-10-03 | Level 2 | N/A
129633 | Anchor Rods | Tier 2 | Transmission | 2023-10-04 | 2024-10-03 | Level 2 | N/A
129634 | Pole Butt | Tier 2 | Transmission | 2023-10-04 | 2024-10-03 | Level 2 | N/A
129635 | Pole Butt | Tier 2 | Transmission | 2023-10-04 | 2024-10-03 | Level 2 | N/A
131116 | Armor Rod - Shieldwire | Tier 2 | Transmission | 2023-10-05 | 2024-10-04 | Level 2 | N/A
131117 | Armor Rod - Shieldwire | Tier 2 | Transmission | 2023-10-05 | 2024-10-04 | Level 2 | N/A
131174 | Complete Tower | Tier 2 | Transmission | 2023-10-07 | 2024-10-06 | Level 2 | N/A
131175 | Hardware | Tier 2 | Transmission | 2023-10-07 | 2024-10-06 | Level 2 | N/A
131295 | Anti-Climb Barrier | Tier 2 | Transmission | 2023-10-07 | 2024-10-06 | Level 2 | N/A
131297 | Anti-Climb Barrier | Tier 2 | Transmission | 2023-10-07 | 2024-10-06 | Level 2 | N/A
130834 | Ground Grid Taps | Tier 2 | Transmission | 2023-10-08 | 2024-10-07 | Level 2 | N/A
130987 | Complete Tower | Tier 2 | Transmission | 2023-10-08 | 2024-10-07 | Level 2 | N/A
130988 | Hardware | Tier 2 | Transmission | 2023-10-08 | 2024-10-07 | Level 2 | N/A
130990 | Aerial Marker Sphere(s) | Tier 2 | Transmission | 2023-10-08 | 2024-10-07 | Level 2 | N/A
130991 | Bolted Spacer | Tier 2 | Transmission | 2023-10-08 | 2024-10-07 | Level 2 | N/A
130993 | Bolted Spacer | Tier 2 | Transmission | 2023-10-08 | 2024-10-07 | Level 2 | N/A
131026 | Bolted Spacer | Tier 2 | Transmission | 2023-10-08 | 2024-10-07 | Level 2 | N/A
131027 | Bolted Spacer | Tier 2 | Transmission | 2023-10-08 | 2024-10-07 | Level 2 | N/A
131030 | Bolted Spacer | Tier 2 | Transmission | 2023-10-08 | 2024-10-07 | Level 2 | N/A
131031 | Bolted Spacer | Tier 2 | Transmission | 2023-10-08 | 2024-10-07 | Level 2 | N/A
131070 | Armor Rod - Shieldwire | Tier 2 | Transmission | 2023-10-05 | 2024-10-07 | Level 2 | N/A
131088 | Bolted Spacer | Tier 2 | Transmission | 2023-10-08 | 2024-10-07 | Level 2 | N/A
131090 | Bolted Spacer | Tier 2 | Transmission | 2023-10-08 | 2024-10-07 | Level 2 | N/A
131092 | Coated Glass 30K | Tier 2 | Transmission | 2023-10-08 | 2024-10-07 | Level 2 | N/A
131106 | Bolted Spacer | Tier 2 | Transmission | 2023-10-08 | 2024-10-07 | Level 2 | N/A
131107 | Bolted Spacer | Tier 2 | Transmission | 2023-10-08 | 2024-10-07 | Level 2 | N/A
131108 | Bolted Spacer | Tier 2 | Transmission | 2023-10-08 | 2024-10-07 | Level 2 | N/A
131143 | Damper (Complete) | Tier 2 | Transmission | 2023-10-08 | 2024-10-07 | Level 2 | N/A
131146 | Shieldwire Attachment Point | Tier 2 | Transmission | 2023-10-08 | 2024-10-07 | Level 2 | N/A
131148 | Hardware | Tier 2 | Transmission | 2023-10-08 | 2024-10-07 | Level 2 | N/A
131151 | Damper (Complete) | Tier 2 | Transmission | 2023-10-08 | 2024-10-07 | Level 2 | N/A
131155 | Conductor Strand(s) | Tier 2 | Transmission | 2023-10-08 | 2024-10-07 | Level 2 | N/A
131156 | Bird Discourager | Tier 2 | Transmission | 2023-10-08 | 2024-10-07 | Level 2 | N/A
131157 | Hot End Yoke Plate | Tier 2 | Transmission | 2023-10-08 | 2024-10-07 | Level 2 | N/A
131158 | FAA Light(s) | Tier 2 | Transmission | 2023-10-08 | 2024-10-07 | Level 2 | N/A
131178 | Shoe Nut(s) | Tier 2 | Transmission | 2023-10-08 | 2024-10-07 | Level 2 | N/A
131179 | Bolted Spacer | Tier 2 | Transmission | 2023-10-08 | 2024-10-07 | Level 2 | N/A
132518 | Footings (Complete) | Tier 3 | Transmission | 2023-10-09 | 2024-10-08 | Level 2 | N/A
133176 | Footings (Complete) | Tier 3 | Transmission | 2023-10-16 | 2024-10-15 | Level 2 | N/A
129654 | Stub Pole - Anchor Guy | Tier 2 | Transmission | 2023-10-22 | 2024-10-21 | Level 2 | N/A
129655 | Preform | Tier 2 | Transmission | 2023-10-22 | 2024-10-21 | Level 2 | N/A
129657 | Bolt(s) | Tier 2 | Transmission | 2023-10-22 | 2024-10-21 | Level 2 | N/A
129658 | Insulators-Ceramic, Post, 69kv | Tier 2 | Transmission | 2023-10-22 | 2024-10-21 | Level 2 | N/A
129667 | Pole Butt | Tier 2 | Transmission | 2023-10-22 | 2024-10-21 | Level 2 | N/A
129680 | Bolt(s) | Tier 2 | Transmission | 2023-10-22 | 2024-10-21 | Level 2 | N/A
129684 | Pole Top | Tier 2 | Transmission | 2023-10-22 | 2024-10-21 | Level 2 | N/A
129685 | Pole Butt | Tier 2 | Transmission | 2023-10-22 | 2024-10-21 | Level 2 | N/A
129691 | Stub Pole - Anchor Guy | Tier 2 | Transmission | 2023-10-22 | 2024-10-21 | Level 2 | N/A
133306 | Complete Wood Pole | Tier 2 | Transmission | 2023-10-22 | 2024-10-21 | Level 2 | N/A
133307 | Complete Wood Pole | Tier 2 | Transmission | 2023-10-22 | 2024-10-21 | Level 2 | N/A
132312 | Shoe Pin-Bolt | Tier 3 | Transmission | 2023-10-28 | 2024-10-24 | Level 2 | N/A
132368 | Shoe Pin-Bolt | Tier 3 | Transmission | 2023-10-28 | 2024-10-24 | Level 2 | N/A
133551 | Pole Butt | Tier 2 | Transmission | 2023-12-04 | 2024-12-03 | Level 2 | N/A
131463 | Signs-High Voltage-At Top | Tier 2 | Transmission | 2023-12-12 | 2024-12-11 | Level 3 | N/A
133565 | Footings (Complete) | Tier 2 | Transmission | 2023-12-13 | 2024-12-12 | Level 2 | N/A
133828 | Cold End Clevis-Shackle | Tier 3 | Transmission | 2023-12-13 | 2024-12-12 | Level 2 | N/A
133829 | Other(Specify) | Tier 3 | Transmission | 2023-12-13 | 2024-12-12 | Level 2 | N/A
130693 | Area Around Structure | Tier 2 | Transmission | 2023-12-14 | 2024-12-13 | Level 2 | N/A
131613 | Insulators-Post, NCI, 69kv, Long | Tier 2 | Transmission | 2023-12-15 | 2024-12-14 | Level 2 | N/A
131614 | Signs-High Voltage-At Top | Tier 2 | Transmission | 2023-12-15 | 2024-12-14 | Level 3 | N/A
131632 | Insulators-Post, NCI, 69kv, Short | Tier 2 | Transmission | 2023-12-15 | 2024-12-14 | Level 2 | N/A
131634 | Signs-High Voltage-At Top | Tier 2 | Transmission | 2023-12-15 | 2024-12-14 | Level 3 | N/A
131894 | Connectors | Tier 2 | Transmission | 2023-12-18 | 2024-12-17 | Level 2 | N/A
131945 | Insulators-Ceramic, Standard, 20K | Tier 2 | Transmission | 2023-12-18 | 2024-12-17 | Level 2 | N/A
131948 | Hardware | Tier 2 | Transmission | 2023-12-18 | 2024-12-17 | Level 2 | N/A
131989 | Conductor (Complete) | Tier 2 | Transmission | 2023-12-18 | 2024-12-17 | Level 2 | N/A
131994 | Shoe (Complete) | Tier 2 | Transmission | 2023-12-18 | 2024-12-17 | Level 2 | N/A
132107 | Signs-High Voltage-At Top | Tier 3 | Transmission | 2023-12-27 | 2024-12-26 | Level 3 | N/A
132108 | Insulators-Post, NCI, 69kv, Short | Tier 3 | Transmission | 2023-12-27 | 2024-12-26 | Level 2 | N/A
133707 | Complete Wood Pole | Tier 2 | Transmission | 2023-12-28 | 2024-12-27 | Level 2 | N/A
128488 | Concrete | Tier 2 | Transmission | 2023-01-10 | 2025-01-09 | Level 2 | N/A
128489 | Footings (Complete) | Tier 2 | Transmission | 2023-01-10 | 2025-01-09 | Level 2 | N/A

## Table 14
Utility | SDG&E
Table No. | 14
Date Modified | 2024-02-01
Table 14: HFTD Area Risk Summary
*EC to add all other risk categories to right of last required category.
HFTD Area | Overall Utility Risk | Ignition Risk | PSPS Risk | Ignition Likelihood | Equipment Likelihood of Ignition | Contact from Vegetation Likelihood of Ignition | Contact from Object Likelihood of Ignition | Burn Probability | PSPS Likelihood | Wildfire Consequence | Wildfire Hazard Intensity | Wildfire Exposure Potential | Wildfire Vulnerability | PSPS Consequence | PSPS Exposure Potential | Vulnerability of Community to PSPS
Non-HFTD Distribution
HFTD 2 Distribution | 0.053209 | 0.031982 | 0.021227 | 0.013222 | 0.03454 | 0.025 | 0.02837 |  | 0.13207 | 542.8529 |  |  |  | 49.944
HFTD 3 Distribution | 0.14927 | 0.13119 | 0.018074 | 0.03971 | 0.06088 | 0.02857 | 0.05228 |  | 0.16993 | 719.6897 |  |  |  | 22.8632
Non-HFTD Transmission
HFTD 2 Transmission
HFTD 3 Transmission

## Table 15
Utility | SDG&E
Table No. | 15
Date Modified | 2024-02-01
Table 15 Top Risk Circuit Scores
*EC to add all other risk categories to right of last required category.
Top- Risk Circuit/ Segment/ Span ID | Risk Granularity | Line Class | Circuit/ Segment/ Span Length (mi) | Inclusion Reason | HFTD Area | Overall Utility Risk | Ignition Risk | PSPS Risk | Ignition Likelihood | Equipment Likelihood of Ignition | Contact from Vegetation Likelihood of Ignition | Contact from Object Likelihood of Ignition | Burn Probability | PSPS Likelihood | Wildfire Consequence | Wildfire Hazard Intensity | Wildfire Exposure Potential | Wildfire Vulnerability | PSPS Consequence | PSPS Exposure Potential | Vulnerability of Community to PSPS
237-30R | Segment Level | Primary Overhead Conductor | 31.7027 | Top 5% highest risk | 3 | 0.0070808 | 0.0070124 | 6.85e-05 | 0.0015737 | 0.05575 | 0 | 0.0361 |  | 0.0011699 | 4.456 |  |  |  | 0.058521
909-805R | Segment Level | Primary Overhead Conductor | 17.9655 | Top 5% highest risk | 3 | 0.007059 | 0.0069859 | 7.3e-05 | 0.0011743 | 0.03717 | 0.00533 | 0.02166 |  | 0.0015093 | 5.9492 |  |  |  | 0.048378
222-1401R | Segment Level | Primary Overhead Conductor | 24.7428 | Top 5% highest risk | 3 | 0.006763 | 0.006763 | 0 | 0.0011834 | 0.04646 | 0.00533 | 0.02166 |  | 0 | 5.7151 |  |  |  | 0.043931
524-69R | Segment Level | Primary Overhead Conductor | 30.7449 | Top 5% highest risk | 3 | 0.0054904 | 0.0053589 | 0.0001315 | 0.00069999 | 0.06504 | 0 | 0.0361 |  | 0.0019914 | 7.6557 |  |  |  | 0.066033
222-1364R | Segment Level | Primary Overhead Conductor | 29.0487 | Top 5% highest risk | 3 | 0.0051917 | 0.0045724 | 0.00061932 | 0.0012567 | 0.05575 | 0.00533 | 0.02166 |  | 0.0032191 | 3.6384 |  |  |  | 0.19239
448-11R | Segment Level | Primary Overhead Conductor | 26.0403 | Top 5% highest risk | 3 | 0.0034632 | 0.0030746 | 0.00038857 | 0.001268 | 0.02787 | 0.00533 | 0.01444 |  | 0.0068389 | 2.4248 |  |  |  | 0.056817
217-983R | Segment Level | Primary Overhead Conductor | 6.8258 | Top 5% highest risk | 3 | 0.0029754 | 0.0029499 | 2.55e-05 | 0.0004178 | 0 | 0 | 0 |  | 0.0013775 | 7.0605 |  |  |  | 0.018506
222-1370R | Segment Level | Primary Overhead Conductor | 13.7777 | Top 5% highest risk | 3 | 0.0033279 | 0.0028076 | 0.00052029 | 0.00055786 | 0.01858 | 0 | 0.02888 |  | 0.0042102 | 5.0329 |  |  |  | 0.12358
358-682F | Segment Level | Primary Overhead Conductor | 10.4536 | Top 5% highest risk | 3 | 0.0029374 | 0.0027387 | 0.00019876 | 0.00057108 | 0.00929 | 0.01067 | 0.02888 |  | 0.0050155 | 4.7956 |  |  |  | 0.039629
157-81R | Segment Level | Primary Overhead Conductor | 28.2803 | Top 5% highest risk | 3 | 0.0025341 | 0.0024851 | 4.9e-05 | 0.00055707 | 0.01858 | 0 | 0.04331 |  | 0.00075106 | 4.4611 |  |  |  | 0.06528
1030-989R | Segment Level | Primary Overhead Conductor | 18.3203 | Top 5% highest risk | 3 | 0.0024432 | 0.0024432 | 0 | 0.00093193 | 0.01858 | 0 | 0.01444 |  | 0 | 2.6216 |  |  |  | 0.025923
79-808R | Segment Level | Primary Overhead Conductor | 10.257 | Top 5% highest risk | 3 | 0.0022327 | 0.002219 | 1.37e-05 | 0.00058203 | 0.01858 | 0 | 0.00722 |  | 0.00083772 | 3.8126 |  |  |  | 0.016324
73-643R | Segment Level | Primary Overhead Conductor | 12.4727 | Top 5% highest risk | 3 | 0.0024254 | 0.0022098 | 0.00021558 | 0.000619 | 0.00929 | 0 | 0.00722 |  | 0.0013324 | 3.5699 |  |  |  | 0.1618
237-1765R | Segment Level | Primary Overhead Conductor | 7.3028 | Top 5% highest risk | 3 | 0.0022368 | 0.0021647 | 7.21e-05 | 0.00034129 | 0.03717 | 0 | 0.00722 |  | 0.0023164 | 6.3428 |  |  |  | 0.031106
214-1122R | Segment Level | Primary Overhead Conductor | 17.9733 | Top 5% highest risk | 3 | 0.0022693 | 0.0021261 | 0.00014325 | 0.00094677 | 0.03717 | 0 | 0.00722 |  | 0.001995 | 2.2456 |  |  |  | 0.071804
1215-32R | Segment Level | Primary Overhead Conductor | 11.565 | Top 5% highest risk | 3 | 0.0019926 | 0.0019926 | 0 | 0.00071302 | 0.00929 | 0 | 0.02166 |  | 0 | 2.7946 |  |  |  | 0.013981
237-17R | Segment Level | Primary Overhead Conductor | 13.629 | Top 5% highest risk | 2 | 0.0018932 | 0.0018932 | 0 | 0.00031356 | 0.06504 | 0 | 0.0361 |  | 0 | 6.0376 |  |  |  | 0.2868
220-298R | Segment Level | Primary Overhead Conductor | 32.6462 | Top 5% highest risk | 3 | 0.0018868 | 0.0018868 | 0 | 0.0016389 | 0 | 0 | 0.04331 |  | 0 | 1.1513 |  |  |  | 0.030897
217-837R | Segment Level | Primary Overhead Conductor | 11.5797 | Top 5% highest risk | 3 | 0.0022038 | 0.0017697 | 0.00043406 | 0.0005441 | 0.00929 | 0 | 0.0361 |  | 0.0015707 | 3.2526 |  |  |  | 0.27634
73-683R | Segment Level | Primary Overhead Conductor | 9.9674 | Top 5% highest risk | 3 | 0.0017472 | 0.0017472 | 0 | 0.00047296 | 0 | 0 | 0.00722 |  | 0 | 3.6942 |  |  |  | 0.093583
157-232R | Segment Level | Primary Overhead Conductor | 10.3659 | Top 5% highest risk | 3 | 0.0020553 | 0.0017153 | 0.00034005 | 0.00056298 | 0.03717 | 0 | 0.02166 |  | 0.0029663 | 3.0468 |  |  |  | 0.11464
445-1311R | Segment Level | Primary Overhead Conductor | 11.4862 | Top 5% highest risk | 3 | 0.001547 | 0.001547 | 0 | 0.00069027 | 0 | 0 | 0.01444 |  | 0 | 2.2412 |  |  |  | 0.02432
235-899R | Segment Level | Primary Overhead Conductor | 9.8138 | Top 5% highest risk | 2 | 0.0015266 | 0.0015266 | 0 | 0.00022114 | 0.01858 | 0 | 0.02888 |  | 0 | 6.9033 |  |  |  | 0.38667
222-2013R | Segment Level | Primary Overhead Conductor | 15.1184 | Top 5% highest risk | 3 | 0.0014909 | 0.0014909 | 0 | 0.00079337 | 0.02787 | 0 | 0.00722 |  | 0 | 1.8792 |  |  |  | 0.038893
521-14R | Segment Level | Primary Overhead Conductor | 11.8083 | Top 5% highest risk | 3 | 0.0016641 | 0.0014883 | 0.00017582 | 0.00027393 | 0.01858 | 0 | 0.01444 |  | 0.0035693 | 5.4331 |  |  |  | 0.049258
970-1341R | Segment Level | Primary Overhead Conductor | 4.1301 | Top 5% highest risk | 3 | 0.0018662 | 0.0013957 | 0.00047054 | 0.00021206 | 0.02787 | 0 | 0 |  | 0.0023164 | 6.5818 |  |  |  | 0.20314
217-835R | Segment Level | Primary Overhead Conductor | 17.6886 | Top 5% highest risk | 3 | 0.0013957 | 0.0013957 | 0 | 0.00027313 | 0.00929 | 0 | 0 |  | 0 | 5.1099 |  |  |  | 0.035488
216-1857 | Segment Level | Primary Overhead Conductor | 6.5295 | Top 5% highest risk | 3 | 0.0014398 | 0.0013795 | 6.03e-05 | 0.0004345 | 0 | 0 | 0.00722 |  | 0.0019896 | 3.1749 |  |  |  | 0.030311