## 2023-2024
UNPLANNED DISTRIBUTION SUSTAINED OUTAGES: (WMP DISCOVERY ¦OEIS_016 (2023-2024)
DISTRIBUTION CIRCUIT & TRANSFORMER-ONLY OUTAGES | [12 empty] | Equipment Failure/Involved | 4524
(Excluding Planned Outages) | [12 empty] | Vegetation | 7790
Division | District Name | Feeder Name | Feeder # | Device | Oper # | Out Date | FNL | In Date | In Time | OIS # | Duration | Outage Level | Basic Cause | Supplemental Cause | CESO | C Min | Open Point Latitude | Open Point Longitude | ME Day | Weather | Failed Equipment | Failed Equipment Condition | Event # | Const Type | Sus/Mom | PM# | Region | Month | Fault Type | NR C Min | Fire Mitigation | Wire-Down Outage | Wire-Down Energized | Out # | Single Phase | EPSS Ckt | FTS | Year | Target
CENTRAL COAST | COAST | WATSONVILLE 2101 | 83332101 | FUSE | 11787 | 20230101 | 4 | 20230101 | 1656 | 1907590 | 1012 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 7084 | 36.9042 | -121.703 | No | Clear;32-90 F |  |  | 23-0004508 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1795108 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO 2201 | 182852201 | OCB | 2201/2 | 20230101 | 126 | 20230101 | 2039 | 1907661 | 1153 | Distribution Circuit | Vegetation | Tree - fell into line | 461 | 141493 | 36.5786 | -121.9085 | No | Clear;32-90F | Conductor- Overhead | Broken | 23-0004241 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1794834 | 0 | EPSS Ckt | N | 2023 | A-B- TIME
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 88094 | 20230101 | 157 | 20230101 | 1507 | 1907856 | 790 | Distribution Circuit | Equipment Failure/Involved | Underground | 225 | 177750 | 36.5966 | -121.9409 | No | Clear;32-90F | Transformer (UG) | Failed/Faulted | 23-0004349 | UG | Sus | 35419189 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1794943 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON 1101 | 182291101 | TRANSFORMER | 411479045843 | 20230101 | 221 | 20230101 | 2137 | 1907705 | 1156 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 1156 | 36.5571 | -121.903 | No | Clear;32-90F |  |  | 23-0004618 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1795222 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES 1111 | 182371111 | FUSE | 9539 | 20230101 | 238 | 20230102 | 150 | 1907711 | 1392 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 8352 | 36.3717 | -121.5854 | No | Clear;32-90F |  |  | 23-0004633 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1795248 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER 2102 | 182492102 | OCB | 2102/2 | 20230101 | 327 | 20230101 | 742 | 1907754 | 255 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 103 | 26265 | 36.8629 | -121.4059 | No | Clear;32-90F |  |  | 23-0004270 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1794864 | 0 | EPSS Ckt | N | 2023 | PH OC TIME
CENTRAL COAST | HOLLISTER | HOLLISTER 2106 | 182492106 | FUSE | 43809 | 20230101 | 657 | 20230101 | 923 | 1907898 | 146 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 46 | 6070 | 36.8073 | -121.4119 | No | Clear;32-90F |  |  | 23-0004307 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1794903 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0423 | 182440423 | TRANSFORMER | 411435348198 | 20230101 | 1008 | 20230101 | 1228 | 1908193 | 140 | Transformer only | Vegetation | Tree - branch fell on line | 24 | 3360 | 36.6212 | -121.9207 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0004393 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1794988 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | FORT ORD 1101 | 182401101 | TRANSFORMER | 411787850154 | 20230101 | 1049 | 20230101 | 1340 | 1908639 | 171 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 2223 | 36.678 | -121.8024 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0004428 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1795026 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS 2106 | 83622106 | FUSE | 3317 | 20230101 | 1107 | 20230102 | 1628 | 1908305 | 1761 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3522 | 37.0644 | -121.9832 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004427 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1795025 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | FORT ORD 2106 | 182402106 | TRANSFORMER | 411760848394 | 20230101 | 1316 | 20230101 | 1339 | 1908331 | 23 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 322 | 36.6299 | -121.8089 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0004413 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1795009 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER 2104 | 182492104 | FUSE | 4407 | 20230101 | 1330 | 20230102 | 1142 | 1908613 | 1332 | Distribution Circuit | Vegetation | Tree - fell into line | 107 | 46896 | 36.9026 | -121.3627 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0004456 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1795054 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN 1101 | 82841101 | FUSE | 2989 | 20230101 | 1340 | 20230102 | 915 | 1908633 | 1175 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 4700 | 37.1639 | -122.0767 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004682 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1795290 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY 2103 | 83192103 | FUSE | 1391 | 20230101 | 1442 | 20230102 | 1409 | 1908728 | 1407 | Distribution Circuit | 3rd Party | Aircraft | 144 | 93546 | 36.9408 | -121.7821 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0004470 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1795069 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN 1102 | 82841102 | JUMPER | JUMPERS 1 SPAN E/OF 315176225924 | 20230101 | 1555 | 20230102 | 1728 | 1908421 | 1533 | Distribution Circuit | Environmental/External | Flood/Erosion | 2 | 3066 | 37.1996 | -122.1563 | No | Clear;32-90 F | Pole-Wood | On Ground | 23-0004481 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | Yes | 1795080 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | SAN JUSTO 1101 | 183181101 | TRANSFORMER | 412823054022 | 20230101 | 1646 | 20230101 | 1845 | 1908940 | 119 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 119 | 36.793 | -121.4536 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0004555 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1795154 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE 2105 | 182222105 | SWITCH | 40029 | 20230101 | 2105 | 20230101 | 2113 | 1909226 | 8 | Distribution Circuit | Company Initiated | Return Circuit Normal | 198 | 1584 | 36.6183 | -121.9342 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0004241 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1795204 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | FUSE | 9539 | 20230102 | 712 | 20230102 | 1206 | 1909546 | 294 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1764 | 36.3717 | -121.5854 | No | Clear;32-90F |  |  | 23-0004757 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1795359 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | OTHER | WIRE DOWN 3 SPANS NORTH OF CGC 315700521449 | 20230102 | 754 | 20230102 | 1205 | 1909579 | 251 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 502 | 37.0813 | -121.9754 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004655 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | Yes | No | 1795270 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY 2101 | 83192101 | FUSE | 6597 | 20230102 | 1313 | 20230102 | 1320 | 1910084 | 7 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 42 | 36.9966 | -121.7163 | No | Clear;32-90F |  |  | 23-0004763 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1795365 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 5217 | 20230102 | 1319 | 20230102 | 1627 | 1910086 | 188 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 2820 | 37.0373 | -122.0664 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0004800 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1795404 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO 2202 | 182852202 | FUSE | T85021 | 20230102 | 1324 | 20230103 | 116 | 1910099 | 711 | Distribution Circuit | Equipment Failure/Involved | Underground | 60 | 33321 | 36.5897 | -121.9193 | No | Clear;32-90F | Conductor- Underground | Broken | 23-0004851 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1795455 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 6033 | 20230102 | 1326 | 20230102 | 1712 | 1910100 | 226 | Distribution Circuit | Vegetation | Tree - bark fell into line | 82 | 18532 | 37.081 | -122.0049 | No | Clear;32-90F | Pole-Wood | Normal | 23-0004767 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1795368 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY 2104 | 83692104 | TRANSFORMER | 316136717116 | 20230102 | 1440 | 20230102 | 2300 | 1910206 | 500 | Transformer only | Vegetation | Tree - fell into line | 5 | 2500 | 36.9625 | -121.8232 | No | Clear;32-90F | Service conductor | Broken | 23-0004808 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1795412 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN 1101 | 182331101 | RECLOSER | 3090 | 20230102 | 1852 | 20230103 | 925 | 1910538 | 873 | Distribution Circuit | 3rd Party | Vehicle | 1770 | 216365 | 36.7322 | -121.61 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004844 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1795447 | 0 | EPSS Ckt | N | 2023 | A-GRD
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 1447 | 20230102 | 1909 | 20230105 | 1751 | 1910559 | 4242 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 38178 | 36.565 | -121.9568 | No | Clear;32-90F | Pole-Wood | Broken- wire on object | 23-0004848 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | Yes | No | 1795451 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS 2105 | 83622105 | FUSE | 7201 | 20230102 | 2019 | 20230103 | 1313 | 1910613 | 1014 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 2028 | 37.1132 | -122.0204 | No | Clear;32-90F | Conductor- Overhead | Broken | 23-0004858 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1795463 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | FUSE | 2945 | 20230102 | 2148 | 20230102 | 2324 | 1910815 | 96 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 256 | 36.4634 | -121.7176 | No | Clear;32-90F |  |  | 23-0004927 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1795531 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND 0401 | 83040401 | FUSE | 5143 | 20230102 | 2245 | 20230103 | 1240 | 1910812 | 835 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 4295 | 37.0994 | -122.0868 | No | Clear;32-90F | Transformer (OH) | Broken | 23-0004939 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1795544 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET 2107 | 83252107 | TRANSFORMER | T1492 | 20230103 | 651 | 20230103 | 734 | 1910989 | 43 | Transformer only | Equipment Failure/Involved | Underground | 1 | 43 | 36.9699 | -121.9999 | No | Clear;32-90F | Transformer (UG) | Failed/Faulted | 23-0004976 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1795571 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY 2105 | 83692105 | RECLOSER | 5090 | 20230103 | 700 | 20230103 | 921 | 1910993 | 141 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 434 | 61194 | 36.9804 | -121.892 | No | Clear;32-90F |  |  | 23-0004964 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1795567 | 0 | EPSS Ckt | N | 2023 | B C & GRD
CENTRAL COAST | SALINAS | GONZALES 1104 | 182131104 | FUSE | 23351 | 20230103 | 815 | 20230107 | 1411 | 1911063 | 6116 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 24464 | 36.529 | -121.4753 | No | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0005053 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1795615 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE 1110 | 182961110 | TRANSFORMER | 412300654758 | 20230103 | 858 | 20230103 | 1308 | 1911142 | 250 | Transformer only | Vegetation | Tree - fell into line | 4 | 1000 | 36.8087 | -121.6318 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0005169 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1795698 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 8625 | 20230103 | 916 | 20230103 | 1322 | 1911181 | 246 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1230 | 37.0783 | -122.0803 | No | Clear;32-90F | Other | Broken | 23-0005047 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1795611 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET 2102 | 83252102 | FUSE | 2277 | 20230103 | 925 | 20230103 | 1051 | 1911194 | 83 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 996 | 36.9624 | -122.0465 | No | Clear;32-90F | Secondary | Broken | 23-0005030 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1795604 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | JUMPER | B PHASE BURNT OPEN JUMPER | 20230103 | 937 | 20230103 | 1504 | 1911212 | 327 | Distribution Circuit | Equipment Failure/Involved | Overhead | 87 | 23849 | 37.0238 | -121.8833 | No | Clear;32-90F | Jumper | Burned Open | 23-0005139 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1795688 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON 1102 | 182291102 | SWITCH | 40469 | 20230103 | 1028 | 20230103 | 1034 | 1911302 | 6 | Distribution Circuit | Company Initiated | Return Circuit Normal | 307 | 1842 | 36.5423 | -121.9141 | No | Clear;32-90F | Conductor- Overhead | Normal | 22-0142531 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1795616 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | FUSE | 2945 | 20230103 | 1113 | 20230103 | 1242 | 1911490 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 356 | 36.4634 | -121.7176 | No | Clear;32-90F |  |  | 23-0005123 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1795675 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | TRANSFORMER | 315291018790 | 20230103 | 1124 | 20230104 | 311 | 1911399 | 947 | Transformer only | Vegetation | Tree - fell into line | 1 | 947 | 37.0047 | -122.1139 | No | Clear;32-90F | Transformer (OH) | Broken- wire on ground | 23-0005238 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1795737 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | PANOCHE 1103 | 253671103 | TRANSFORMER | 414472046981 | 20230103 | 1141 | 20230103 | 1536 | 1911428 | 235 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 235 | 36.6092 | -120.8855 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0005247 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1795744 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | TRANSFORMER | 411550847333 | 20230103 | 1205 | 20230103 | 1340 | 1911463 | 95 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 1330 | 36.5985 | -121.8801 | No | Clear;32-90F | Crossarm- Wood | Broken | 23-0005111 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1795668 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRIP-SAVER | 82789 | 20230103 | 1245 | 20230103 | 1816 | 1911506 | 331 | Distribution Circuit | Vegetation | Other ground vegetation | 37 | 12247 | 36.8534 | -121.6337 | No | Clear;32-90F | Pole-Wood | Normal | 23-0005131 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1795680 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 5819 | 20230103 | 1248 | 20230103 | 1331 | 1911544 | 43 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 2580 | 37.0449 | -121.8139 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0005167 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1795697 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 9449 | 20230103 | 1258 | 20230103 | 1459 | 1911649 | 121 | Distribution Circuit | Animal | Bird found | 1 | 121 | 37.0783 | -122.0589 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0005199 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1795712 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | T1326 | 20230103 | 1721 | 20230104 | 1459 | 1911955 | 1298 | Transformer only | Equipment Failure/Involved | Underground | 8 | 10384 | 36.8184 | -121.6587 | No | Clear;32-90 F | Service conductor | Failed/Faulted | 23-0005300 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1795781 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 6969 | 20230103 | 2300 | 20230104 | 311 | 1912015 | 251 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 251 | 37.0046 | -122.1164 | No | Clear;32-90F | Transformer (OH) | Broken | 23-0005287 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1795770 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 2667 | 20230104 | 713 | 20230104 | 1746 | 1912398 | 633 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3798 | 37.0258 | -121.7751 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0005599 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796048 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 2913 | 20230104 | 727 | 20230112 | 1800 | 1912442 | 12153 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 24931 | 37.1752 | -122.1446 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0005656 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796084 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | FUSE | 25511 | 20230104 | 728 | 20230106 | 1518 | 1912444 | 3350 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 16750 | 36.5506 | -121.4993 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0005718 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796129 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | RECLOSER | 3090 | 20230104 | 743 | 20230105 | 1341 | 1912511 | 1798 | Distribution Circuit | Vegetation | Tree - fell into line | 1772 | 144529 | 36.7322 | -121.61 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0005571 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1796029 | 0 | EPSS Ckt | N | 2023 | ABC
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 5997 | 20230104 | 813 | 20230104 | 1537 | 1912638 | 444 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 7104 | 36.7882 | -121.6799 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0005733 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1796137 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | FUSE | 5561 | 20230104 | 828 | 20230104 | 1713 | 1912668 | 525 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 10500 | 36.7763 | -121.5987 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0005735 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1796139 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SPENCE 1104 | 182201104 | TRANSFORMER | 412802746743 | 20230104 | 833 | 20230104 | 1255 | 1912690 | 262 | Transformer only | Environmental/External | Water | 3 | 786 | 36.5915 | -121.4518 | Yes | Clear;32-90 F | Transformer | Broken | 23-0005666 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796091 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | OTHER | 6689 | 20230104 | 836 | 20230105 | 1140 | 1912707 | 1624 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 17864 | 36.8881 | -121.8071 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0005692 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1796108 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRANSFORMER | 315233224330 | 20230104 | 912 | 20230104 | 928 | 1912952 | 16 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 64 | 37.1561 | -122.136 | Yes | Clear;32-90F | Secondary | Broken | 23-0005673 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1796096 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6711 | 20230104 | 921 | 20230105 | 1706 | 1912949 | 1905 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 93345 | 36.9982 | -121.8687 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0005867 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796248 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD 1101 | 182381101 | FUSE | 4319 | 20230104 | 939 | 20230104 | 1718 | 1913332 | 459 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 54 | 24798 | 36.8349 | -121.725 | Yes | Clear;32-90F |  |  | 23-0006303 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796606 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 9271 | 20230104 | 948 | 20230104 | 1435 | 1913089 | 287 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 3731 | 37.036 | -121.86 | Yes | Clear;32-90F |  |  | 23-0006105 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796428 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER 1101 | 182941101 | JUMPER | 1275 | 20230104 | 949 | 20230104 | 1231 | 1913054 | 161 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 1288 | 36.3992 | -121.8779 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0005958 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796313 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 9665 | 20230104 | 957 | 20230104 | 1133 | 1913093 | 96 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 672 | 36.8549 | -121.7925 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0005828 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796222 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD 1102 | 182731102 | FUSE | 23113 | 20230104 | 1005 | 20230104 | 1457 | 1913132 | 292 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1753 | 36.5963 | -121.621 | Yes | Clear;32-90F | Cutout- fuse holder | Broken | 23-0005760 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1796162 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | TRANSFORMER | 316630013770 | 20230104 | 1019 | 20230105 | 1210 | 1913184 | 1551 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 3952 | 36.8725 | -121.6534 | Yes | Clear;32-90F | Transformer (OH) | Broken | 23-0006000 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796343 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9783 | 20230104 | 1026 | 20230108 | 1611 | 1913389 | 6105 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 153665 | 37.1573 | -122.1336 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0005900 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796269 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE 1107 | 182961107 | RECLOSER | 22232 | 20230104 | 1031 | 20230104 | 1205 | 1913241 | 94 | Distribution Circuit | Vegetation | Tree - fell into line | 1669 | 156886 | 36.7323 | -121.6561 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0005747 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | No | No | 1796153 | 0 | EPSS Ckt | N | 2023 | ABC
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 3495 | 20230104 | 1033 | 20230104 | 1120 | 1913276 | 47 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 1739 | 36.7755 | -121.6732 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0005812 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796208 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 1421 | 20230104 | 1045 | 20230104 | 1128 | 1913317 | 43 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 860 | 36.5743 | -121.9483 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0005791 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796192 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | INDUSTRIAL ACRES-0413 | 182300413 | JUMPER | BURNT ROAD JUMPER | 20230104 | 1053 | 20230104 | 1800 | 1914704 | 427 | Distribution Circuit | Equipment Failure/Involved | Overhead | 613 | 183151 | 36.6707 | -121.6356 | Yes | Clear;32-90F | Jumper | Burned Open | 23-0006107 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1796430 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1102 | 182011102 | RECLOSER | 97880 | 20230104 | 1055 | 20230104 | 1736 | 1913352 | 401 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1304 | 109449 | 36.6883 | -121.6199 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0005774 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1796174 | 0 | Non-EPSS | N | 2023 | BC GRD
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | FUSE | 25529 | 20230104 | 1056 | 20230107 | 1702 | 1913336 | 4686 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 19641 | 36.5537 | -121.4759 | Yes | Clear;32-90F | Pole-Wood | Deteriorated | 23-0005871 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1796252 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | OTHER | TREE THRU LINE | 20230104 | 1104 | 20230104 | 1654 | 1913417 | 340 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1905 | 36.8891 | -121.8296 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0005885 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | Yes | Yes | 1796258 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SAN BENITO 2104 | 182742104 | FUSE | 409 | 20230104 | 1123 | 20230104 | 1240 | 1913467 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 1309 | 36.8918 | -121.6439 | Yes | Clear;32-90F |  |  | 23-0005891 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796262 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 8015 | 20230104 | 1124 | 20230108 | 1137 | 1933098 | 5773 | Distribution Circuit | Vegetation | Tree - fell into line | 139 | 802447 | 37.1536 | -122.1615 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010012 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1799857 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS 2104 | 83622104 | FUSE | 6085 | 20230104 | 1125 | 20230105 | 1556 | 1913501 | 1711 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 24193 | 37.0636 | -122.0348 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0005865 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796246 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | JUMPER | OJ CGC 315233021245 | 20230104 | 1129 | 20230107 | 1741 | 1922060 | 4692 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 9384 | 37.0718 | -122.1342 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0007361 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1797615 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | JUMPER | OJS @ CGC 315246920980 | 20230104 | 1129 | 20230108 | 1200 | 1927756 | 5791 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 5791 | 37.0646 | -122.1303 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009025 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798852 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 90678 | 20230104 | 1134 | 20230108 | 1329 | 1916624 | 5875 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 505250 | 37.0954 | -122.1281 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006380 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796677 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 11739 | 20230104 | 1134 | 20230107 | 1832 | 1927272 | 4738 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 37904 | 37.0654 | -122.1256 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008944 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798780 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 1421 | 20230104 | 1139 | 20230104 | 1513 | 1913563 | 214 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 4280 | 36.5743 | -121.9483 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0005838 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796228 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI 1101 | 82931101 | SWITCH | 77303 | 20230104 | 1141 | 20230107 | 924 | 1914874 | 4183 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 75294 | 37.0865 | -122.2603 | Yes | Clear;32-90F | Conductor- Underground | Normal | 23-0006133 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1796454 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 47627 | 20230104 | 1141 | 20230109 | 33 | 1921977 | 6532 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 19596 | 37.0704 | -122.2311 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007340 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1797597 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | SWITCH | 252963 | 20230104 | 1141 | 20230107 | 924 | 1922474 | 4183 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 150588 | 37.0764 | -122.2417 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007489 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797711 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 5277 | 20230104 | 1142 | 20230104 | 1806 | 1913573 | 384 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 14976 | 36.7758 | -121.6878 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0005852 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796238 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | SWITCH | 6847 | 20230104 | 1143 | 20230106 | 1329 | 1913577 | 2947 | Distribution Circuit | Vegetation | Tree - fell into line | 217 | 546128 | 36.5581 | -121.9164 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0005893 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796264 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 1427 | 20230104 | 1144 | 20230106 | 1500 | 1924718 | 3076 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 169180 | 37.0823 | -122.0914 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0008240 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1798292 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO 2203 | 182852203 | RECLOSER | 2628 | 20230104 | 1145 | 20230105 | 253 | 1913588 | 908 | Distribution Circuit | Vegetation | Tree - fell into line | 1615 | 416596 | 36.5603 | -121.919 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0005844 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1796232 | 0 | EPSS Ckt | N | 2023 | AC GRD
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | SWITCH | 510967 | 20230104 | 1211 | 20230108 | 1317 | 1926627 | 5826 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 332082 | 37.0928 | -122.1267 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008788 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798664 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | RECLOSER | 557716 | 20230104 | 1211 | 20230104 | 1854 | 1913713 | 403 | Distribution Circuit | Vegetation | Tree - fell into line | 333 | 77177 | 36.831 | -121.6794 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0005890 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796261 | 0 | EPSS Ckt | N | 2023 | BC
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 8577 | 20230104 | 1221 | 20230107 | 1259 | 1923462 | 4358 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4358 | 37.0465 | -122.152 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007814 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797977 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 9005 | 20230104 | 1221 | 20230107 | 1655 | 1925515 | 4594 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 101068 | 37.0318 | -122.1369 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008543 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798469 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | JUMPER | JUMPERS @ CGC 3151713324614 | 20230104 | 1225 | 20230113 | 1042 | 1944452 | 12857 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 12857 | 37.1642 | -122.1583 | Yes | Clear;32-90 F | Insulator | Broken | 23-0012187 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1801950 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRIP-SAVER | 2253 | 20230104 | 1227 | 20230107 | 1700 | 1923199 | 4593 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 55116 | 37.1709 | -122.1652 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0007717 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1797898 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 5457 | 20230104 | 1227 | 20230108 | 1027 | 1924587 | 5640 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 101520 | 37.1376 | -122.1414 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008191 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798268 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 10254 | 20230104 | 1229 | 20230107 | 1612 | 1924948 | 4543 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 31369 | 37.1392 | -122.1787 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0005964 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1798356 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | JUMPER | OJ CGC 315160024838 | 20230104 | 1229 | 20230112 | 1710 | 1925103 | 11801 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 70806 | 37.17 | -122.1623 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008406 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1798374 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9761 | 20230104 | 1229 | 20230108 | 1723 | 1925115 | 6054 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 18162 | 37.1729 | -122.1638 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008415 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1798377 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9763 | 20230104 | 1229 | 20230108 | 1006 | 1925126 | 5617 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 112340 | 37.1767 | -122.1629 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0008420 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798379 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 1607 | 20230104 | 1229 | 20230108 | 1408 | 1925493 | 5859 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 76167 | 37.1931 | -122.156 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008534 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1798463 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 5066 | 20230104 | 1229 | 20230112 | 1620 | 1926798 | 11751 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 305526 | 37.1706 | -122.1655 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0005964 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1798692 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRIP-SAVER | 6219 | 20230104 | 1229 | 20230108 | 1735 | 1933618 | 6066 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 133452 | 37.1841 | -122.1409 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010156 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1800006 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | JUMPER | OJ 1 NE/OF 2913 | 20230104 | 1229 | 20230112 | 1619 | 1933622 | 11750 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 35250 | 37.1753 | -122.1443 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010160 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1800010 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 2945 | 20230104 | 1229 | 20230112 | 1959 | 1933627 | 11970 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 598500 | 37.1733 | -122.1442 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010163 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1800013 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND 1101 | 83041101 | FUSE | 9309 | 20230104 | 1233 | 20230108 | 1912 | 1924000 | 6159 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 843783 | 37.1187 | -122.1154 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008027 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | Yes | No | 1798158 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | SWITCH | 143589 | 20230104 | 1233 | 20230108 | 1910 | 1926157 | 6157 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 258594 | 37.1171 | -122.1147 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008542 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798566 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | FUSE | 5177 | 20230104 | 1233 | 20230108 | 1326 | 1932874 | 5813 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 93008 | 37.1063 | -122.1062 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008936 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1799780 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | FUSE | 688471 | 20230104 | 1233 | 20230108 | 1410 | 1932974 | 5857 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 99569 | 37.1101 | -122.1102 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0009966 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1799815 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS 2101 | 183582101 | OCB | 2101/2 | 20230104 | 1233 | 20230108 | 1910 | 1913795 | 6053 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1740 | 1523651 | 37.0953 | -122.1437 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0005914 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796280 | 0 | EPSS Ckt | N | 2023 | A B & GRD
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 7799 | 20230104 | 1233 | 20230107 | 1230 | 1923005 | 4317 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 263337 | 37.091 | -122.1396 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007660 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797857 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 39126 | 20230104 | 1233 | 20230107 | 1741 | 1926272 | 4628 | Distribution Circuit | Vegetation | Tree - fell into line | 126 | 583128 | 37.0778 | -122.1322 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008558 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1798594 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5435 | 20230104 | 1239 | 20230108 | 943 | 1926487 | 5584 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 39088 | 37.1175 | -122.1214 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008754 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1798633 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1102 | 182011102 | FUSE | 20201 | 20230104 | 1239 | 20230104 | 1445 | 1913822 | 126 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 66 | 8316 | 36.697 | -121.61 | Yes | Clear;32-90F |  |  | 23-0006085 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796413 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | JUMPER | OJ NE/OF CGC 315171324614 | 20230104 | 1240 | 20230113 | 1809 | 1951698 | 13289 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 146179 | 37.1647 | -122.1575 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0015201 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1804226 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 12838 | 20230104 | 1241 | 20230107 | 1225 | 1913841 | 4304 | Distribution Circuit | Vegetation | Tree - fell into line | 232 | 998528 | 37.1272 | -122.1236 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0005921 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | No | No | 1796283 | 0 | EPSS Ckt | N | 2023 | A B C
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9765 | 20230104 | 1241 | 20230108 | 1627 | 1926561 | 5986 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 83804 | 37.1269 | -122.1291 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008784 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1798652 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 699 | 20230104 | 1258 | 20230108 | 1210 | 1926461 | 5712 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 17136 | 37.049 | -122.1382 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0008742 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798623 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 9827 | 20230104 | 1258 | 20230109 | 413 | 1926875 | 6675 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 220275 | 37.0797 | -122.1385 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008850 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798709 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | OCB | 1102/2 | 20230104 | 1300 | 20230110 | 109 | 1913974 | 6269 | Distribution Circuit | Vegetation | Tree - fell into line | 2045 | 7153968 | 37.1312 | -122.1723 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0005964 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796315 | 0 | EPSS Ckt | N | 2023 | A GRD
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 393582 | 20230104 | 1301 | 20230108 | 1440 | 1913924 | 5859 | Distribution Circuit | Vegetation | Tree - fell into line | 509 | 292611 | 37.1284 | -122.1222 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0005954 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1796310 | 0 | EPSS Ckt | N | 2023 | A B C T
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 8125 | 20230104 | 1303 | 20230107 | 1057 | 1922129 | 4194 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 79686 | 37.099 | -122.1424 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007384 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797633 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 7773 | 20230104 | 1303 | 20230108 | 1558 | 1924724 | 5935 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 207725 | 37.1881 | -122.1581 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008243 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798294 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 40411 | 20230104 | 1303 | 20230105 | 851 | 1913955 | 1188 | Distribution Circuit | Vegetation | Tree - bark fell into line | 155 | 184140 | 36.4918 | -121.938 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006404 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796701 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 8217 | 20230104 | 1304 | 20230112 | 1620 | 1924908 | 11716 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 11716 | 37.1719 | -122.1715 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008337 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798343 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 7289 | 20230104 | 1304 | 20230114 | 1519 | 1925183 | 14535 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 87210 | 37.1711 | -122.1812 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008440 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1798387 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 3729 | 20230104 | 1304 | 20230108 | 1441 | 1925497 | 5857 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 17571 | 37.199 | -122.1535 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008535 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1798464 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | OTHER | 5235 | 20230104 | 1308 | 20230105 | 1122 | 1913960 | 1334 | Distribution Circuit | Vegetation | Tree - branch fell on line | 60 | 74357 | 37.0596 | -122.0793 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006178 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1796494 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 6353 | 20230104 | 1308 | 20230105 | 1532 | 1913964 | 1584 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 53856 | 37.0376 | -122.0665 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0006089 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1796415 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 11105 | 20230104 | 1321 | 20230105 | 1027 | 1914040 | 1266 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 7596 | 37.0113 | -122.0752 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006037 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796375 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | KING CITY 1103 | 182031103 | RECLOSER | 7038 | 20230104 | 1331 | 20230104 | 2215 | 1914100 | 524 | Distribution Circuit | Equipment Failure/Involved | Overhead | 793 | 408108 | 36.1935 | -121.1442 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0005991 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796336 | 0 | EPSS Ckt | N | 2023 | A & G
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 2725 | 20230104 | 1334 | 20230105 | 1237 | 1916877 | 1383 | Distribution Circuit | Vegetation | Tree - branch fell on line | 206 | 153698 | 36.5453 | -121.9281 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006477 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1796774 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS 2103 | 83622103 | RECLOSER | 5402 | 20230104 | 1335 | 20230105 | 1300 | 1913931 | 1381 | Distribution Circuit | Vegetation | Tree - fell into line | 951 | 45373 | 37.0104 | -122.0341 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0005992 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1796337 | 0 | EPSS Ckt | N | 2023 | NA
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 65444 | 20230104 | 1336 | 20230107 | 1415 | 1924386 | 4359 | Distribution Circuit | Vegetation | Tree - fell into line | 500 | 2175608 | 37.1278 | -122.1229 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008135 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1798227 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5511 | 20230104 | 1336 | 20230107 | 1417 | 1925107 | 4361 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 187523 | 37.1499 | -122.1363 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0008411 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1798376 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 595388 | 20230104 | 1336 | 20230113 | 1156 | 1926746 | 12860 | Distribution Circuit | Vegetation | Tree - fell into line | 179 | 2301940 | 37.1517 | -122.136 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006011 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798685 | 0 | EPSS Ckt | N | 2023 | NA
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | JUMPER | OJ 2 P/ SS OF CGC313149720656 | 20230104 | 1336 | 20230109 | 147 | 1926400 | 6491 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 6491 | 37.0547 | -122.1636 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008730 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1798613 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | JUMPER | OJ 1 SPAN SS OF CGC 315206520800 | 20230104 | 1336 | 20230107 | 1630 | 1926698 | 4494 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4494 | 37.06 | -122.1447 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008810 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1798668 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 5397 | 20230104 | 1346 | 20230108 | 1019 | 1926705 | 5553 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 127719 | 37.076 | -122.1429 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0008813 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1798671 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | OTHER | 6995 | 20230104 | 1350 | 20230106 | 1828 | 1914258 | 3158 | Distribution Circuit | Vegetation | Tree - fell into line | 99 | 162162 | 36.4883 | -121.9379 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006136 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | Yes | Yes | 1796457 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 8917 | 20230104 | 1413 | 20230106 | 1059 | 1915460 | 2686 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 56406 | 36.5771 | -121.9274 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006230 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796536 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | OCB | 2202/2 | 20230104 | 1413 | 20230104 | 1513 | 1914380 | 60 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6098 | 365880 | 36.5786 | -121.9085 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006036 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | No | No | 1796374 | 0 | EPSS Ckt | N | 2023 | A-B-C
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | JUMPER | OUTAGE BEYOND SW 6169 | 20230104 | 1417 | 20230108 | 1326 | 1933118 | 5709 | Distribution Circuit | Vegetation | Tree - fell into line | 357 | 2038113 | 37.0969 | -122.0975 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0005914 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1799860 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | RECLOSER | 563516 | 20230104 | 1420 | 20230106 | 1409 | 1914510 | 2869 | Distribution Circuit | Vegetation | Tree - fell into line | 1779 | 1149720 | 36.5785 | -121.9279 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006055 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1796389 | 0 | EPSS Ckt | N | 2023 | B-GRD
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 7605 | 20230104 | 1426 | 20230104 | 1640 | 1914459 | 134 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 2144 | 37.0866 | -122.0058 | Yes | Clear;32-90F |  |  | 23-0006132 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796453 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | PACIFIC GROVE 0422 | 182440422 | FUSE | 2581 | 20230104 | 1426 | 20230105 | 1342 | 1914453 | 1396 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 44627 | 36.5918 | -121.9454 | Yes | Clear;32-90 F |  |  | 23-0007514 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797731 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 5159 | 20230104 | 1440 | 20230107 | 1706 | 1914889 | 4466 | Distribution Circuit | Vegetation | Tree - branch fell on line | 102 | 455532 | 37.0814 | -122.0846 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006141 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796461 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 8929 | 20230104 | 1455 | 20230105 | 2004 | 1916037 | 1749 | Distribution Circuit | Equipment Failure/Involved | Overhead | 57 | 86319 | 37.0661 | -122.0844 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007209 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797484 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | JUMPER | 6185 HIGH SIDE JPR | 20230104 | 1505 | 20230106 | 1841 | 1922177 | 3096 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 15480 | 36.5688 | -121.9288 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006055 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797645 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | RECLOSER | 9542 | 20230104 | 1507 | 20230106 | 1841 | 1914701 | 3094 | Distribution Circuit | Vegetation | Tree - fell into line | 567 | 789512 | 36.5614 | -121.9199 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006106 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1796429 | 0 | EPSS Ckt | N | 2023 | A-B-C
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 6183 | 20230104 | 1507 | 20230106 | 1127 | 1917258 | 2660 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 69160 | 36.5648 | -121.9229 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006439 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1796737 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 6187 | 20230104 | 1507 | 20230107 | 21 | 1924879 | 3434 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 82416 | 36.5677 | -121.9288 | Yes | Clear;32-90F | Pole-Wood | Deteriorated | 23-0008327 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1798339 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 2145 | 20230104 | 1507 | 20230107 | 1612 | 1925532 | 4385 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 13155 | 36.5682 | -121.9289 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008544 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798470 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | BUENA VISTA-1104 | 182261104 | TRANSFORMER | 412325549581 | 20230104 | 1516 | 20230104 | 1639 | 1914745 | 83 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 83 | 36.6664 | -121.618 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006253 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796557 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | OTHER | WIRE DOWN @ CGC 315257524060 | 20230104 | 1526 | 20230107 | 1415 | 1925227 | 4249 | Distribution Circuit | Equipment Failure/Involved | Overhead | 75 | 307135 | 37.1485 | -122.1278 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008465 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1798400 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5225 | 20230104 | 1531 | 20230105 | 1713 | 1915066 | 1542 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 13878 | 37.0496 | -122.0856 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0006274 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796579 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 5951 | 20230104 | 1555 | 20230106 | 1431 | 1914978 | 2796 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 21805 | 36.7916 | -121.7148 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006315 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1796615 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 2765 | 20230104 | 1609 | 20230105 | 1812 | 1915081 | 1563 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 24 | 37512 | 36.5574 | -121.9253 | Yes | Clear;32-90 F |  |  | 23-0007831 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797995 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 11237 | 20230104 | 1610 | 20230106 | 843 | 1915085 | 2433 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 9732 | 37.0904 | -121.9645 | Yes | Clear;32-90F |  |  | 23-0008115 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798215 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 9302 | 20230104 | 1614 | 20230104 | 2008 | 1915183 | 234 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 99 | 23166 | 36.4379 | -121.7943 | Yes | Clear;32-90F |  |  | 23-0006524 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796822 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 8269 | 20230104 | 1618 | 20230105 | 2153 | 1918197 | 1775 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 65675 | 36.5555 | -121.9122 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006763 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797065 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | OCB | 2101/2 | 20230104 | 1629 | 20230105 | 1438 | 1915323 | 1329 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9745 | 608688 | 36.9521 | -121.76 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006215 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796522 | 0 | EPSS Ckt | N | 2023 | PH OC TIME GRD OC INST
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 11004 | 20230104 | 1651 | 20230105 | 1025 | 1915520 | 1054 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 220 | 231880 | 37.0793 | -122.0771 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0006244 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796549 | 0 | EPSS Ckt | N | 2023 | AB
CENTRAL COAST | SALINAS | SPENCE-1104 | 182201104 | FUSE | 5319 | 20230104 | 1657 | 20230105 | 1000 | 1916074 | 1023 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 9207 | 36.5823 | -121.4982 | Yes | Clear;32-90 F |  |  | 23-0007223 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1797497 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | JUMPER | OJ 1 SPAN S/O CGC 315318422514 | 20230104 | 1704 | 20230108 | 1326 | 1927215 | 5542 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 44336 | 37.1072 | -122.1048 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008936 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798775 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 374675 | 20230104 | 1707 | 20230107 | 1425 | 1925478 | 4158 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 49896 | 37.0953 | -122.0854 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008529 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798458 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 287 | 20230104 | 1707 | 20230107 | 1646 | 1925487 | 4299 | Distribution Circuit | Vegetation | Tree - grew into line | 16 | 68784 | 37.0905 | -122.0856 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0008530 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798459 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | BL 1101 | 20230104 | 1707 | 20230108 | 1326 | 1915976 | 5342 | Distribution Circuit | Vegetation | Tree - fell into line | 1809 | 4984930 | 37.0926 | -122.0966 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006310 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1796612 | 0 | EPSS Ckt | N | 2023 | B & C PHASE
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 5269 | 20230104 | 1715 | 20230104 | 2025 | 1915788 | 190 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1582 | 36.9894 | -122.0312 | Yes | Clear;32-90F |  |  | 23-0006478 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796775 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | JUMPER | OUTAGE FOR LR 698634 | 20230104 | 1720 | 20230108 | 1422 | 1933200 | 5582 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 686586 | 37.0954 | -122.0857 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0005914 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1799882 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 7315 | 20230104 | 1726 | 20230106 | 1110 | 1920647 | 2504 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 38330 | 37.0406 | -122.0817 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006996 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797298 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | FUSE | 9593 | 20230104 | 1729 | 20230105 | 1014 | 1916028 | 1005 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 32128 | 36.8134 | -121.3951 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006401 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796698 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 12590 | 20230104 | 1730 | 20230106 | 1558 | 1916088 | 2788 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1264 | 237189 | 37.0633 | -122.0798 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006326 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796625 | 0 | EPSS Ckt | N | 2023 | BC
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | RECLOSER | 94948 | 20230104 | 1735 | 20230104 | 1926 | 1916169 | 111 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 4244 | 469530 | 36.9677 | -121.9985 | Yes | Clear;32-90F | Sectionalizer | Normal | 23-0006385 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796682 | 0 | EPSS Ckt | N | 2023 | A & GRD
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | SWITCH | 10769 | 20230104 | 1737 | 20230107 | 1743 | 1923223 | 4326 | Distribution Circuit | Vegetation | Tree - fell into line | 241 | 1042566 | 37.0631 | -122.1224 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007722 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797904 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 66253 | 20230104 | 1737 | 20230107 | 1545 | 1922860 | 4208 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 50496 | 37.096 | -122.0136 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007605 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797812 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 6087 | 20230104 | 1738 | 20230107 | 1421 | 1916283 | 4123 | Distribution Circuit | Vegetation | Tree - branch fell on line | 174 | 530594 | 37.0665 | -122.0336 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007122 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797410 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5621 | 20230104 | 1740 | 20230106 | 925 | 1916233 | 2385 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 66491 | 37.1016 | -122.0524 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007447 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797684 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER 1102 | 182941102 | RECLOSER | 2002 | 20230104 | 1743 | 20230108 | 1601 | 1916292 | 5658 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 537695 | 36.2248 | -121.7587 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006342 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1796640 | 0 | EPSS Ckt | N | 2023 | A-B
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 5351 | 20230104 | 1745 | 20230105 | 1752 | 1916289 | 1447 | Distribution Circuit | Vegetation | Tree - bark fell into line | 20 | 28940 | 37.0009 | -122.0209 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0007606 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1797813 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 4693 | 20230104 | 1745 | 20230106 | 1731 | 1916338 | 2866 | Distribution Circuit | Equipment Failure/Involved | Overhead | 63 | 157185 | 36.7255 | -121.2676 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0007101 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1797395 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 8833 | 20230104 | 1747 | 20230105 | 2251 | 1924028 | 1744 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 3488 | 36.3822 | -121.8634 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0008040 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1798171 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 3469 | 20230104 | 1748 | 20230105 | 1128 | 1916619 | 1060 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 10600 | 37.0336 | -121.998 | Yes | Clear;32-90 F |  |  | 23-0007326 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797585 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 10214 | 20230104 | 1748 | 20230105 | 1805 | 1916336 | 1457 | Distribution Circuit | Vegetation | Tree - branch fell on line | 219 | 319083 | 37.0909 | -122.0439 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0006349 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796647 | 0 | EPSS Ckt | N | 2023 | B & C
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 5020 | 20230104 | 1750 | 20230105 | 2254 | 1916376 | 1339 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 293 | 292634 | 37.1024 | -121.9847 | Yes | Clear;32-90F |  |  | 23-0006351 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | No | No | 1796650 | 0 | EPSS Ckt | N | 2023 | BC GRD
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 3979 | 20230104 | 1751 | 20230105 | 931 | 1916357 | 940 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 20680 | 37.0209 | -122.0097 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0007155 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797439 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 11829 | 20230104 | 1751 | 20230105 | 827 | 1921105 | 876 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 3504 | 37.009 | -122.0756 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0007077 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797371 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 1655 | 20230104 | 1752 | 20230105 | 1506 | 1916372 | 1274 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 12740 | 37.1027 | -122.0482 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0007609 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1797816 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 4473 | 20230104 | 1757 | 20230105 | 1552 | 1916486 | 1315 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 22355 | 37.003 | -122.0141 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006581 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796879 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 75993 | 20230104 | 1813 | 20230104 | 2117 | 1916751 | 184 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 92 | 16928 | 36.9799 | -122.0316 | Yes | Clear;32-90F |  |  | 23-0006558 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796856 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1105 | 182011105 | OCB | 1105/2 | 20230104 | 1816 | 20230104 | 1953 | 1916787 | 97 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 7350 | 701982 | 36.6828 | -121.6513 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006396 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796694 | 0 | Non-EPSS | N | 2023 | B & C
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | TRANSFORMER | 315950918803 | 20230104 | 1826 | 20230105 | 924 | 1916845 | 898 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 898 | 37.0082 | -121.8877 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0007105 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797399 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 11821 | 20230104 | 1845 | 20230105 | 1316 | 1917148 | 1111 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 2222 | 37.0051 | -122.0736 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006584 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | Yes | No | 1796882 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | RECLOSER | 2012 | 20230104 | 1855 | 20230106 | 1708 | 1916351 | 2773 | Distribution Circuit | Equipment Failure/Involved | Overhead | 380 | 1053740 | 36.3306 | -121.8831 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0006449 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1796747 | 0 | EPSS Ckt | N | 2023 | A-B-C
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | RECLOSER | 10952 | 20230104 | 1905 | 20230105 | 1948 | 1917507 | 1483 | Distribution Circuit | Vegetation | Tree - fell into line | 360 | 52035 | 36.8841 | -121.7552 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006492 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1796791 | 0 | EPSS Ckt | N | 2023 | B-C-GRD
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 11865 | 20230104 | 1910 | 20230107 | 1459 | 1917506 | 4069 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 245674 | 37.001 | -121.7398 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0007062 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1797359 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | FUSE | 23113 | 20230104 | 1914 | 20230106 | 1355 | 1917672 | 2561 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 23049 | 36.5963 | -121.621 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0007058 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1797355 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | RECLOSER | 3062 | 20230104 | 1916 | 20230104 | 2236 | 1917547 | 200 | Distribution Circuit | Vegetation | Tree - bark fell into line | 175 | 35000 | 36.7753 | -121.6728 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006468 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796765 | 0 | EPSS Ckt | N | 2023 | BC
CENTRAL COAST | SALINAS | SALINAS-1109 | 182011109 | FUSE | 3173 | 20230104 | 1920 | 20230106 | 1422 | 1917566 | 2582 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 24111 | 36.6609 | -121.5904 | Yes | Clear;32-90 F |  |  | 23-0007143 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797429 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1103 | 182201103 | FUSE | 5125 | 20230104 | 1920 | 20230106 | 1838 | 1917592 | 2838 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 67760 | 36.6543 | -121.5594 | Yes | Clear;32-90F | Pole-Wood | Deteriorated | 23-0006863 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1797165 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | OCB | 1101/2 | 20230104 | 1923 | 20230105 | 1848 | 1917682 | 1405 | Distribution Circuit | Vegetation | Tree - fell into line | 2065 | 344365 | 36.8001 | -121.769 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006502 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796801 | 0 | EPSS Ckt | N | 2023 | B GRD
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | FUSE | 9853 | 20230104 | 1924 | 20230105 | 930 | 1917707 | 846 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 10998 | 36.8069 | -121.5075 | Yes | Clear;32-90 F |  |  | 23-0007181 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1797462 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | SAN BENITO 2101 | 182742101 | RECLOSER | 355426 | 20230104 | 1931 | 20230105 | 1100 | 1917748 | 224 | Distribution Circuit | Equipment Failure/Involved | Overhead | 382 | 85568 | 36.8411 | -121.5145 | Yes | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0006513 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796810 | 0 | EPSS Ckt | N | 2023 | A & C
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | FUSE | 5561 | 20230104 | 1942 | 20230106 | 1308 | 1918578 | 2486 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 49720 | 36.7763 | -121.5987 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007287 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1797551 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1103 | 182031103 | JUMPER | BURNT OJ 1 N/OF 30077 | 20230104 | 1945 | 20230104 | 2204 | 1917834 | 139 | Distribution Circuit | Equipment Failure/Involved | Overhead | 582 | 7318 | 36.1956 | -121.1432 | Yes | Clear;32-90F | Jumper | Burned Open | 23-0006518 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1796815 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | INDUSTRIAL ACRES-0413 | 182300413 | TRANSFORMER | 412275149844 | 20230104 | 1955 | 20230105 | 2231 | 1917887 | 1596 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 23940 | 36.6734 | -121.6354 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0007065 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797362 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 2845 | 20230104 | 1956 | 20230105 | 1134 | 1917912 | 938 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 86296 | 36.5397 | -121.8652 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006806 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1797108 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 6997 | 20230104 | 1956 | 20230106 | 1649 | 1917894 | 2693 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 45781 | 36.4918 | -121.9388 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006635 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796936 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | RECLOSER | 440 | 20230104 | 1957 | 20230105 | 851 | 1917999 | 774 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 106 | 82044 | 36.4389 | -121.9203 | Yes | Clear;32-90F |  |  | 23-0006750 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797052 | 0 | EPSS Ckt | N | 2023 | SGF
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | TRANSFORMER | 316402514006 | 20230104 | 2004 | 20230105 | 1439 | 1922067 | 1115 | Transformer only | Vegetation | Tree - branch fell on line | 4 | 4460 | 36.8781 | -121.731 | Yes | Clear;32-90 F | Service conductor | Broken | 23-0007366 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797619 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | TRANSFORMER | 315410817040 | 20230104 | 2008 | 20230105 | 1742 | 1918038 | 1294 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 3882 | 36.9576 | -122.071 | Yes | Clear;32-90 F | Transformer (OH) | Broken | 23-0007142 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797428 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER 2105 | 182492105 | RECLOSER | 4040 | 20230104 | 2009 | 20230105 | 1327 | 1917837 | 1038 | Distribution Circuit | Equipment Failure/Involved | Overhead | 461 | 441879 | 36.7535 | -121.2907 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006550 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796847 | 0 | EPSS Ckt | N | 2023 | C & GRD
CENTRAL COAST | KING CITY | SAN ARDO 1101 | 182191101 | FUSE | 7099 | 20230104 | 2023 | 20230106 | 1203 | 1918258 | 2380 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 30940 | 36.0566 | -121.0005 | Yes | Clear;32-90F |  |  | 23-0007068 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1797364 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | OTHER | 1 WIRE DWN SE/OF 8137 | 20230104 | 2028 | 20230106 | 1316 | 1918292 | 2406 | Distribution Circuit | Vegetation | Tree - fell into line | 232 | 106684 | 37.0576 | -121.9802 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007133 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | Yes | Yes | 1797419 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 4717 | 20230104 | 2033 | 20230105 | 903 | 1918275 | 750 | Distribution Circuit | Vegetation | Tree - fell into line | 147 | 110250 | 36.9206 | -121.3709 | Yes | Clear;32-90F | Conductor- Overhead | Bent or Twisted | 23-0006572 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1796869 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | RECLOSER | 648928 | 20230104 | 2122 | 20230105 | 104 | 1918782 | 222 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 412 | 91034 | 36.5332 | -121.9152 | Yes | Clear;32-90F |  |  | 23-0006648 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796949 | 0 | EPSS Ckt | N | 2023 | A-B
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | JUMPER | WIRE DOWN | 20230104 | 2127 | 20230106 | 1226 | 1921758 | 2339 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 37660 | 37.1202 | -122.0513 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007271 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1797537 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS 2103 | 182082103 | JUMPER | 64348 | 20230104 | 2129 | 20230105 | 2112 | 1918908 | 1423 | Distribution Circuit | Equipment Failure/Involved | Overhead | 205 | 291715 | 36.3307 | -121.2258 | Yes | Clear;32-90F | Jumper | Burned Open | 23-0006764 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1797066 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | RECLOSER | 9104 | 20230104 | 2136 | 20230105 | 1606 | 1918958 | 1110 | Distribution Circuit | Vegetation | Tree - fell into line | 750 | 189696 | 36.5869 | -121.9142 | Yes | Clear;32-90F | Crossarm- Wood | Broken | 23-0006857 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1797160 | 0 | EPSS Ckt | N | 2023 | AB
CENTRAL COAST | KING CITY | OILFIELDS-1103 | 182391103 | FUSE | 9217 | 20230104 | 2142 | 20230105 | 1555 | 1919021 | 1093 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 10930 | 35.8758 | -120.8871 | Yes | Clear;32-90 F |  |  | 23-0007173 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1797457 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 141 | 20230104 | 2219 | 20230105 | 907 | 1920866 | 648 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 9072 | 37.048 | -122.0648 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0007124 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1797411 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | OCB | 1101/2 | 20230104 | 2236 | 20230107 | 308 | 1919483 | 3152 | Distribution Circuit | Vegetation | Tree - fell into line | 505 | 126604 | 36.5569 | -121.8976 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006791 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1797092 | 0 | EPSS Ckt | N | 2023 | A-C-GRD
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | TRANSFORMER | 316398713560 | 20230104 | 2321 | 20230105 | 1036 | 1919738 | 675 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 6075 | 36.8659 | -121.7321 | Yes | Clear;32-90 F | Fuse | Failed/Faulted | 23-0007267 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797533 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | RECLOSER | 2014 | 20230104 | 2337 | 20230107 | 1358 | 1919812 | 3741 | Distribution Circuit | Vegetation | Tree - fell into line | 125 | 79683 | 36.5776 | -121.9523 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0006849 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1797153 | 0 | EPSS Ckt | N | 2023 | A-B
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 2179 | 20230105 | 4 | 20230105 | 1010 | 1919952 | 606 | Distribution Circuit | Vegetation | Tree - branch fell on line | 83 | 50298 | 36.5423 | -121.9165 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0007254 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1797523 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | TRANSFORMER | 315643120355 | 20230105 | 17 | 20230105 | 1954 | 1920011 | 1177 | Transformer only | Vegetation | Tree - branch fell on line | 3 | 3531 | 37.0487 | -121.994 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007463 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797691 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 11384 | 20230105 | 20 | 20230105 | 856 | 1920036 | 516 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 430 | 221880 | 37.0534 | -122.0438 | Yes | Clear;32-90F |  |  | 23-0006889 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1797189 | 0 | EPSS Ckt | N | 2023 | A-B
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 9527 | 20230105 | 22 | 20230105 | 1833 | 1920946 | 1091 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 6546 | 37.009 | -122.0098 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0007224 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797498 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 5209 | 20230105 | 26 | 20230105 | 1328 | 1920034 | 782 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 15640 | 37.0373 | -122.0723 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0007138 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797423 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 8799 | 20230105 | 41 | 20230107 | 643 | 1920080 | 1285 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 129830 | 36.5607 | -121.9181 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006991 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797293 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 6037 | 20230105 | 110 | 20230106 | 1451 | 1920160 | 2261 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 56525 | 37.073 | -122.0159 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006992 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797294 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | OCB | 2202/2 | 20230105 | 118 | 20230105 | 2014 | 1919851 | 1136 | Distribution Circuit | Vegetation | Tree - fell into line | 6181 | 1420580 | 36.5786 | -121.9085 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0006912 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | No | No | 1797212 | 0 | EPSS Ckt | N | 2023 | A-B-C
CENTRAL COAST | COAST | SEACLIFF 0401 | 83500401 | RECLOSER | 929132 | 20230105 | 125 | 20230106 | 1416 | 1920250 | 2211 | Distribution Circuit | Vegetation | Tree - fell into line | 127 | 280797 | 36.9919 | -121.927 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0007060 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797357 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | MONTEREY | VIEJO 2204 | 182852204 | FUSE | 6409 | 20230105 | 230 | 20230105 | 1942 | 1920381 | 1032 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 111456 | 36.59 | -121.9115 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0007028 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1797329 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 11337 | 20230105 | 248 | 20230105 | 1815 | 1921281 | 927 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 8343 | 37.0177 | -121.8918 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0007111 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797404 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 45255 | 20230105 | 407 | 20230105 | 852 | 1920559 | 285 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 11115 | 36.5862 | -121.9149 | Yes | Clear;32-90F |  |  | 23-0007082 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797375 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | FUSE | 9079 | 20230105 | 538 | 20230105 | 1400 | 1920659 | 502 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 1004 | 36.8376 | -121.4551 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0007341 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1797598 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 11461 | 20230105 | 716 | 20230105 | 1430 | 1920856 | 434 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 3118 | 36.8678 | -121.76 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0007315 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797575 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | SWITCH | 23349 | 20230105 | 731 | 20230107 | 952 | 1920681 | 3021 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 3309 | 36.6431 | -121.6487 | Yes | Clear;32-90F | Transformer (OH) | Arcing | 23-0007037 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1797337 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | TRANSFORMER | 411330247140 | 20230105 | 800 | 20230107 | 1340 | 1921057 | 3220 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 3220 | 36.5913 | -121.9551 | Yes | Clear;32-90F | Transformer (OH) | Normal | 23-0008800 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1798662 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1103 | 182011103 | FUSE | 5343 | 20230105 | 809 | 20230107 | 650 | 1921092 | 2801 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 2801 | 36.6976 | -121.654 | Yes | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0007856 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798020 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | TRANSFORMER | 315625620712 | 20230105 | 812 | 20230105 | 1603 | 1921139 | 471 | Transformer only | Vegetation | Tree - branch fell on line | 11 | 5181 | 37.0588 | -121.9986 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0007691 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797878 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | BUENA VISTA-1102 | 182261102 | TRANSFORMER | 412280048813 | 20230105 | 832 | 20230106 | 126 | 1920864 | 1014 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1014 | 36.645 | -121.6326 | Yes | Clear;32-90 F | Jumper | Broken | 23-0007090 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797384 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | TRANSFORMER | 412377951890 | 20230105 | 912 | 20230106 | 1801 | 1921366 | 1969 | Transformer only | Vegetation | Tree - grew into line | 4 | 7876 | 36.7309 | -121.6031 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007227 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797501 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 40411 | 20230105 | 914 | 20230105 | 1332 | 1921464 | 258 | Distribution Circuit | Vegetation | Tree - bark fell into line | 155 | 39990 | 36.4918 | -121.938 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0007473 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1797699 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 12775 | 20230105 | 927 | 20230106 | 1146 | 1921325 | 1542 | Distribution Circuit | Environmental/External | Flood/Erosion | 243 | 368766 | 36.9691 | -121.9048 | Yes | Clear;32-90 F | Other | Normal | 23-0007163 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1797448 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 1909 | 20230105 | 1001 | 20230105 | 1332 | 1921592 | 211 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1055 | 37.0978 | -121.9771 | Yes | Clear;32-90 F |  |  | 23-0007491 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797712 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 412118254715 | 20230105 | 1032 | 20230107 | 1721 | 1921798 | 3289 | Transformer only | Environmental/External | Water | 1 | 3289 | 36.8069 | -121.6946 | Yes | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0007379 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797629 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | SWITCH | 10795 | 20230105 | 1043 | 20230105 | 1141 | 1921769 | 58 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2190 | 125242 | 36.9346 | -121.774 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0007290 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1797554 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET 2104 | 83252104 | SWITCH | 10341 | 20230105 | 1055 | 20230111 | 1002 | 1921783 | 8587 | Distribution Circuit | Environmental/External | Flood/Erosion | 619 | 1129909 | 36.9738 | -121.9602 | Yes | Clear;32-90 F | Transformer (UG) | Normal | 23-0007282 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1797547 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 4709 | 20230105 | 1057 | 20230105 | 1630 | 1921835 | 333 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 2 | 776 | 36.6877 | -121.3445 | Yes | Clear;32-90 F |  |  | 23-0007305 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1797566 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 3911 | 20230105 | 1115 | 20230107 | 1630 | 1921909 | 3195 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 35895 | 36.8132 | -121.7035 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007469 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1797696 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 88183 | 20230105 | 1204 | 20230107 | 936 | 1922107 | 2732 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 24588 | 36.5987 | -121.9396 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007714 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797896 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 95871 | 20230105 | 1241 | 20230106 | 1420 | 1922237 | 1539 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1539 | 37.0155 | -122.0286 | Yes | Clear;32-90 F | Other | On Ground | 23-0007425 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1797666 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6151 | 20230105 | 1241 | 20230106 | 1217 | 1922232 | 1416 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 9912 | 36.9652 | -121.8293 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007678 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797870 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET 2109 | 83252109 | FUSE | 7491 | 20230105 | 1245 | 20230105 | 1430 | 1921907 | 105 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 2415 | 36.981 | -121.9285 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007427 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | Yes | No | 1797668 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 7747 | 20230105 | 1252 | 20230106 | 225 | 1924063 | 813 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 4878 | 36.5756 | -121.9707 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0008058 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1798185 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 2815 | 20230105 | 1302 | 20230106 | 1233 | 1922301 | 1411 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 8466 | 37.0535 | -121.9782 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007572 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797783 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | OTHER | MAINLINE DOWN AT 445933 | 20230105 | 1334 | 20230108 | 1440 | 1922496 | 4386 | Distribution Circuit | Vegetation | Tree - fell into line | 200 | 872760 | 37.1368 | -122.1004 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007498 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1797716 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRIP-SAVER | 6601 | 20230105 | 1410 | 20230105 | 1454 | 1922639 | 44 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 1540 | 36.9942 | -121.7176 | Yes | Clear;32-90 F |  |  | 23-0007587 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797797 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 5219 | 20230105 | 1435 | 20230105 | 2002 | 1922791 | 327 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 6213 | 37.0371 | -122.066 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007591 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | Yes | No | 1797801 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5485 | 20230105 | 1444 | 20230113 | 1751 | 1923028 | 11707 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 398038 | 37.1322 | -122.109 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0007666 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1797863 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | TRANSFORMER | 411383543303 | 20230105 | 1451 | 20230107 | 1514 | 1922828 | 2903 | Transformer only | Vegetation | Tree - fell into line | 5 | 14515 | 36.486 | -121.9322 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0007738 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797918 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | BORONDA-1101 | 182461101 | TRANSFORMER | 412167550958 | 20230105 | 1538 | 20230107 | 953 | 1922999 | 2535 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 15210 | 36.703 | -121.6731 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0007729 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797911 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 4473 | 20230105 | 1553 | 20230105 | 1701 | 1923059 | 68 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 1156 | 37.003 | -122.0141 | Yes | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0007752 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797927 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | TRANSFORMER | 411440845999 | 20230105 | 1647 | 20230106 | 636 | 1923271 | 829 | Transformer only | Environmental/External | Water | 9 | 7461 | 36.5613 | -121.9164 | Yes | Clear;32-90 F | Other | Together | 23-0007753 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797928 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | TRANSFORMER | 316415014280 | 20230105 | 1651 | 20230105 | 1708 | 1923274 | 17 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 34 | 36.8854 | -121.7268 | Yes | Clear;32-90 F | Connector or Splice (OH) | Burned/flashed | 23-0007737 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1797917 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | FUSE | 2667 | 20230105 | 1707 | 20230106 | 1744 | 1923549 | 1477 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 26586 | 36.3689 | -121.5292 | Yes | Clear;32-90F |  |  | 23-0008557 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1798482 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | TRANSFORMER | 316702013915 | 20230105 | 1712 | 20230106 | 1314 | 1923339 | 1202 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2404 | 36.8766 | -121.6287 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0007931 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798069 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 1447 | 20230105 | 1752 | 20230105 | 2005 | 1923464 | 133 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 399 | 36.565 | -121.9568 | Yes | Clear;32-90 F | Fuse | Failed/Faulted | 23-0007880 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1798042 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRANSFORMER | 315378120403 | 20230105 | 1811 | 20230106 | 1026 | 1923394 | 975 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1950 | 37.0495 | -122.0848 | Yes | Clear;32-90 F | Transformer (OH) | Deteriorated | 23-0007822 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797987 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 2689 | 20230105 | 1825 | 20230106 | 640 | 1923537 | 735 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 32 | 23520 | 37.1274 | -122.0181 | Yes | Clear;32-90F |  |  | 23-0008073 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798193 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | TRANSFORMER | 411452847168 | 20230105 | 2013 | 20230106 | 0 | 1923812 | 227 | Transformer only | Vegetation | Tree - fell into line | 7 | 1589 | 36.5931 | -121.9137 | Yes | Clear;32-90F | Secondary | Normal | 23-0007953 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798088 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 1441 | 20230105 | 2033 | 20230105 | 2230 | 1923854 | 117 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 3510 | 36.6008 | -121.9334 | Yes | Clear;32-90F |  |  | 23-0008015 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798148 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | TRANSFORMER | 411452847168 | 20230106 | 530 | 20230106 | 1835 | 1924115 | 785 | Transformer only | Vegetation | Tree - fell into line | 7 | 5495 | 36.5931 | -121.9137 | No | Clear;32-90F | Secondary | Arcing | 23-0008088 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798199 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 4899 | 20230106 | 821 | 20230106 | 1120 | 1924261 | 179 | Distribution Circuit | Equipment Failure/Involved | Underground | 54 | 9365 | 36.8816 | -121.3999 | No | Clear;32-90F | Elbow | Burned/flashed | 23-0008141 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798232 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1101 | 182011101 | TRANSFORMER | 412243749635 | 20230106 | 946 | 20230107 | 1422 | 1924432 | 1716 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2102 | 12221 | 36.6673 | -121.6463 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0008258 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798303 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | RECLOSER | 9490 | 20230106 | 950 | 20230106 | 2330 | 1924443 | 820 | Distribution Circuit | Equipment Failure/Involved | Underground | 67 | 54940 | 36.566 | -121.9352 | No | Clear;32-90F | Transformer (UG) | Failed/Faulted | 23-0008152 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798240 | 0 | EPSS Ckt | N | 2023 | A GRD
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 24947 | 20230106 | 956 | 20230107 | 1905 | 1924467 | 1989 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 1989 | 36.7394 | -121.7236 | No | Clear;32-90F |  |  | 23-0009035 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1798862 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 5020 | 20230106 | 1308 | 20230106 | 1418 | 1924905 | 41 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 293 | 16408 | 37.1024 | -121.9847 | No | Clear;32-90F |  |  | 23-0008358 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1798357 | 0 | EPSS Ckt | N | 2023 | B & C
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 316187016861 | 20230106 | 1358 | 20230107 | 1421 | 1925189 | 1463 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1463 | 36.9555 | -121.8061 | No | Clear;32-90F | Transformer (OH) | Broken | 23-0008712 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798596 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | KING CITY 1106 | 182031106 | JUMPER | BOJ 2 SPANS SW OF CGC 413914533208 | 20230106 | 1424 | 20230108 | 1343 | 1925079 | 2839 | Distribution Circuit | Equipment Failure/Involved | Overhead | 81 | 21427 | 36.2265 | -121.0642 | No | Clear;32-90 F | Jumper | Burned Open | 23-0010098 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1799945 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | FUSE | 5561 | 20230106 | 1450 | 20230106 | 1700 | 1925151 | 130 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 1734 | 36.7763 | -121.5987 | No | Clear;32-90F | Fuse | Broken | 23-0008531 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798460 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 623483 | 20230106 | 1531 | 20230106 | 1820 | 1925242 | 169 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 5408 | 36.9634 | -121.8959 | No | Clear;32-90F | Transformer (OH) | Deteriorated | 23-0008520 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1798448 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | SWITCH | 2685 | 20230106 | 1652 | 20230106 | 1957 | 1925303 | 185 | Distribution Circuit | Vegetation | Tree - grew into line | 37 | 6845 | 37.0286 | -121.8625 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0008488 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1798419 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | TRANSFORMER | 316349113835 | 20230106 | 1654 | 20230107 | 1454 | 1925264 | 1320 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 3960 | 36.8734 | -121.7494 | No | Clear;32-90 F | Transformer | Broken | 23-0008516 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1798442 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | JUMPER | WIRE DOWN S/E/OF 10421 | 20230106 | 1712 | 20230106 | 2324 | 1925445 | 372 | Distribution Circuit | Equipment Failure/Involved | Overhead | 82 | 30368 | 36.5658 | -121.9344 | No | Clear;32-90F | Connector or Splice (OH) | Broken- wire on ground | 23-0008523 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | Yes | Yes | 1798451 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | FUSE | 40251 | 20230106 | 1728 | 20230106 | 2002 | 1925505 | 154 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 59 | 9086 | 36.2415 | -121.7971 | No | Clear;32-90F |  |  | 23-0008574 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1798493 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | TRANSFORMER | 315291018790 | 20230106 | 1814 | 20230107 | 1543 | 1925536 | 1289 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 1289 | 37.0047 | -122.1139 | No | Clear;32-90 F | Transformer | Burned Open | 23-0008550 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798475 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | SWITCH | 11011 | 20230106 | 1917 | 20230107 | 314 | 1925405 | 477 | Distribution Circuit | Vegetation | Tree - fell into line | 711 | 37653 | 37.022 | -122.0214 | No | Clear;32-90F | Conductor- Overhead | Together | 23-0008562 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1798485 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 8929 | 20230107 | 454 | 20230107 | 638 | 1925962 | 104 | Distribution Circuit | Vegetation | Tree - branch fell on line | 57 | 5928 | 37.0661 | -122.0844 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0008661 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798553 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1103 | 182011103 | FUSE | 5343 | 20230107 | 725 | 20230107 | 2145 | 1926067 | 860 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 860 | 36.6976 | -121.654 | Yes | Clear;32-90F | Conductor- Underground | Burned/flashed | 23-0008693 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798575 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | RECLOSER | 2002 | 20230107 | 901 | 20230107 | 930 | 1926203 | 29 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 870 | 36.2248 | -121.7587 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0006449 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798580 | 0 | EPSS Ckt | N | 2023 | C & GRD
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRANSFORMER | 315491521810 | 20230107 | 906 | 20230107 | 935 | 1926257 | 29 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 145 | 37.0888 | -122.0465 | Yes | Clear;32-90F | Secondary | Broken | 23-0008706 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1798589 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1102 | 182011102 | JUMPER | FB 1 SPAN SS/O MTR 1008264561 | 20230107 | 1058 | 20230107 | 1539 | 1926414 | 281 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 5058 | 36.6944 | -121.6453 | Yes | Clear;32-90F | Secondary | Broken | 23-0008736 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1798618 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | TRANSFORMER | 411422046026 | 20230107 | 1218 | 20230107 | 2321 | 1926549 | 663 | Transformer only | Vegetation | Tree - branch fell on line | 12 | 7956 | 36.5615 | -121.9227 | Yes | Clear;32-90F | Secondary | Together | 23-0008781 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798650 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9769 | 20230107 | 1249 | 20230107 | 1731 | 1926605 | 282 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 9306 | 37.1293 | -122.1204 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008847 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798705 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 8515 | 20230107 | 1328 | 20230107 | 1533 | 1926820 | 125 | Distribution Circuit | Vegetation | Tree - bark fell into line | 106 | 13250 | 37.0483 | -122.1607 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0008846 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798704 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES 1112 | 182371112 | JUMPER | JUMPERS 1 SPAN SOUTH OF CGC 411959443034 | 20230107 | 1408 | 20230107 | 2239 | 1926779 | 511 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 7665 | 36.4838 | -121.7362 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0008829 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1798690 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | RECLOSER | 2010 | 20230107 | 1416 | 20230108 | 1615 | 1926812 | 1559 | Distribution Circuit | Equipment Failure/Involved | Overhead | 122 | 24967 | 36.5058 | -121.936 | Yes | Clear;32-90F | Anchor or Guy | Broken- wire on ground | 23-0008834 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798695 | 0 | EPSS Ckt | N | 2023 | C GRD
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5509 | 20230107 | 1428 | 20230108 | 1110 | 1926838 | 1242 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 24840 | 37.1532 | -122.1291 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0008907 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1798756 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 8915 | 20230107 | 1525 | 20230110 | 1528 | 1926955 | 4323 | Distribution Circuit | Vegetation | Tree - grew into line | 12 | 51876 | 37.1665 | -122.1671 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0012200 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | No | No | 1801964 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE 2104 | 182222104 | TRANSFORMER | 411666447421 | 20230107 | 1527 | 20230107 | 1742 | 1926957 | 135 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 1215 | 36.6017 | -121.841 | Yes | Clear;32-90F | Connector or Splice (OH) | Deteriorated | 23-0008965 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798797 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | TRANSFORMER | 315711518630 | 20230107 | 1534 | 20230108 | 1542 | 1927102 | 1448 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 1448 | 37.0025 | -121.9695 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008997 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798827 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 7299 | 20230107 | 1538 | 20230107 | 1954 | 1926995 | 256 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 3328 | 37.0308 | -122.0939 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0008882 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1798736 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | FUSE | 4245 | 20230107 | 1558 | 20230108 | 1340 | 1927189 | 1302 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 36456 | 36.8938 | -121.5972 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008924 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1798765 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | TRANSFORMER | 411423345520 | 20230107 | 1559 | 20230108 | 424 | 1927170 | 745 | Transformer only | Environmental/External | Water | 11 | 8195 | 36.5476 | -121.9217 | Yes | Clear;32-90 F | Transformer | Broken- wire on object | 23-0008929 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798768 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | TRANSFORMER | 412685145372 | 20230107 | 1606 | 20230108 | 1215 | 1932822 | 1209 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 4019 | 36.5539 | -121.491 | Yes | Clear;32-90F | Transformer (OH) | Broken | 23-0009913 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1799764 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | JUMPER | OJ 3 S/LD SIDE OF 5411 | 20230107 | 1625 | 20230115 | 945 | 1947477 | 11120 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 11120 | 37.0547 | -122.1635 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0013480 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1802988 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 8513 | 20230107 | 1625 | 20230109 | 1116 | 1947532 | 2571 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 41136 | 37.0549 | -122.1533 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0013496 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802998 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRIP-SAVER | 2253 | 20230107 | 1728 | 20230114 | 1430 | 1927316 | 9902 | Distribution Circuit | Environmental/External | Flood/Erosion | 12 | 118824 | 37.1709 | -122.1652 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0010093 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1799939 | 1 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 5159 | 20230107 | 1732 | 20230107 | 1852 | 1927367 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 102 | 8160 | 37.0814 | -122.0846 | Yes | Clear;32-90F |  |  | 23-0008993 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1798823 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | RECLOSER | 12662 | 20230107 | 1755 | 20230108 | 1527 | 1927427 | 1292 | Distribution Circuit | Vegetation | Tree - fell into line | 570 | 119050 | 36.8984 | -121.6906 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0008992 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1798822 | 0 | EPSS Ckt | N | 2023 | B & C
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 8017 | 20230107 | 1840 | 20230112 | 1344 | 1927645 | 6904 | Distribution Circuit | Vegetation | Tree - branch fell on line | 74 | 173534 | 37.1565 | -122.1617 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010243 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1800093 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 6689 | 20230107 | 1857 | 20230107 | 2136 | 1927722 | 159 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1749 | 36.8881 | -121.8071 | Yes | Clear;32-90F |  |  | 23-0009143 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1798970 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | TRANSFORMER | 315369721780 | 20230107 | 1926 | 20230108 | 922 | 1927905 | 836 | Transformer only | Unknown Cause | Patrol - found nothing | 5 | 4180 | 37.0874 | -122.0883 | Yes | Clear;32-90 F |  |  | 23-0009947 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1799797 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO-1101 | 182191101 | FUSE | 7099 | 20230107 | 1947 | 20230107 | 2139 | 1927939 | 112 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 13 | 1456 | 36.0566 | -121.0005 | Yes | Clear;32-90F |  |  | 23-0009139 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798967 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 3911 | 20230107 | 1949 | 20230109 | 1431 | 1927942 | 2562 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 30828 | 36.8132 | -121.7035 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0009169 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1798996 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | OCB | 2201/2 | 20230107 | 2035 | 20230107 | 2215 | 1928026 | 100 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 400 | 36.5786 | -121.9085 | Yes | Clear;32-90F | Insulator | Broken | 23-0009087 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1798916 | 0 | EPSS Ckt | N | 2023 | B-C-GRD
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 7567 | 20230107 | 2133 | 20230107 | 2247 | 1928125 | 74 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 1184 | 36.5783 | -121.9041 | Yes | Clear;32-90F |  |  | 23-0009279 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1799110 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 1391 | 20230107 | 2133 | 20230108 | 1618 | 1928450 | 1125 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4500 | 36.5761 | -121.8998 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0009283 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1799114 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SOLEDAD 2104 | 182052104 | RECLOSER | 413916 | 20230107 | 2143 | 20230107 | 2255 | 1928140 | 72 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 33 | 2376 | 36.4469 | -121.3318 | Yes | Clear;32-90 F |  |  | 23-0009168 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1798995 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | KING CITY | SOLEDAD 2105 | 182052105 | FUSE | 8709 | 20230107 | 2158 | 20230108 | 1730 | 1928191 | 1172 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 10548 | 36.4525 | -121.3575 | Yes | Clear;32-90F | Conductor- Overhead | On Ground | 23-0009393 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1799226 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 1013 | 20230107 | 2223 | 20230108 | 1404 | 1928793 | 941 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 19324 | 36.8382 | -121.7843 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009884 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1799733 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | BORONDA-1102 | 182461102 | OCB | 1102/2 | 20230107 | 2230 | 20230108 | 1354 | 1928402 | 924 | Distribution Circuit | Equipment Failure/Involved | Overhead | 117 | 55377 | 36.6906 | -121.6793 | Yes | Clear;32-90F | Connector or Splice (OH) | Broken- wire on ground | 23-0009260 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1799090 | 0 | Non-EPSS | N | 2023 | C GRD
CENTRAL COAST | SALINAS | BORONDA-1101 | 182461101 | FUSE | 23707 | 20230107 | 2233 | 20230107 | 2357 | 1928408 | 84 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 1793 | 36.702 | -121.6753 | Yes | Clear;32-90F |  |  | 23-0009446 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1799279 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SALINAS 1104 | 182011104 | RECLOSER | 55450 | 20230107 | 2233 | 20230107 | 2329 | 1928415 | 56 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 1198 | 67088 | 36.6761 | -121.663 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0009265 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1799095 | 0 | EPSS Ckt | N | 2023 | BC
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 1491 | 20230107 | 2255 | 20230108 | 2116 | 1928586 | 1341 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 53640 | 36.5057 | -121.9352 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009578 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1799410 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 4693 | 20230107 | 2301 | 20230108 | 810 | 1928823 | 549 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 11517 | 36.7255 | -121.2676 | Yes | Clear;32-90 F |  |  | 23-0009971 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1799819 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | FUSE | 9977 | 20230107 | 2302 | 20230108 | 1146 | 1928693 | 764 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 15797 | 36.7755 | -121.4753 | Yes | Clear;32-90 F |  |  | 23-0010104 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1799953 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 4439 | 20230107 | 2327 | 20230108 | 1505 | 1929262 | 938 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2814 | 36.7754 | -121.6769 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010018 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1799863 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 5277 | 20230107 | 2329 | 20230108 | 450 | 1931355 | 321 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 12519 | 36.7758 | -121.6878 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0009814 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1799655 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | TRANSFORMER | 412174853586 | 20230107 | 2330 | 20230108 | 1007 | 1929311 | 637 | Transformer only | Vegetation | Tree - branch fell on line | 3 | 1911 | 36.7757 | -121.6741 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0009796 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1799635 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | FUSE | 994287 | 20230107 | 2331 | 20230113 | 1229 | 1932633 | 7978 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 21055 | 36.8402 | -121.463 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0009965 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | No | No | 1799814 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 6851 | 20230107 | 2333 | 20230108 | 1829 | 1929414 | 1136 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 7187 | 36.5569 | -121.9156 | Yes | Clear;32-90 F | Fuse | Broken | 23-0010283 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1800132 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 2181 | 20230107 | 2342 | 20230108 | 1510 | 1929509 | 928 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 84 | 77952 | 36.4895 | -121.9363 | Yes | Clear;32-90 F |  |  | 23-0010264 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1800112 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | RECLOSER | 2012 | 20230107 | 2342 | 20230108 | 1602 | 1929530 | 980 | Distribution Circuit | Equipment Failure/Involved | Overhead | 445 | 433859 | 36.3306 | -121.8831 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0009409 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1799242 | 0 | EPSS Ckt | N | 2023 | B-GRD
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | RECLOSER | 12662 | 20230107 | 2355 | 20230108 | 1932 | 1930057 | 1177 | Distribution Circuit | Vegetation | Tree - fell into line | 524 | 421558 | 36.8984 | -121.6906 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009441 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1799274 | 0 | EPSS Ckt | N | 2023 | AB GRD
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 8163 | 20230107 | 2356 | 20230108 | 818 | 1930038 | 502 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 132 | 66264 | 36.9659 | -121.8953 | Yes | Clear;32-90F |  |  | 23-0009850 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1799702 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 4319 | 20230108 | 0 | 20230108 | 510 | 1930303 | 310 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 54 | 16748 | 36.8349 | -121.725 | Yes | Clear;32-90F |  |  | 23-0009821 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1799661 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 7873 | 20230108 | 2 | 20230110 | 1123 | 1930450 | 3561 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 106690 | 36.5773 | -121.9451 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009694 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1799528 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 1433 | 20230108 | 3 | 20230108 | 1834 | 1931364 | 1111 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 35552 | 36.567 | -121.9568 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0010161 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1800011 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 1445 | 20230108 | 7 | 20230108 | 1836 | 1930410 | 1109 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 13308 | 36.5735 | -121.9108 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009789 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1799628 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SOLEDAD 2101 | 182052101 | FUSE | 7484 | 20230108 | 15 | 20230108 | 2156 | 1930674 | 1301 | Distribution Circuit | Equipment Failure/Involved | Underground | 121 | 92741 | 36.4391 | -121.3168 | Yes | Clear;32-90 F | Elbow | Failed/Faulted | 23-0010008 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1799853 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 40577 | 20230108 | 15 | 20230108 | 1040 | 1930680 | 625 | Distribution Circuit | Vegetation | Tree - fell into line | 360 | 39390 | 36.5673 | -121.9167 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009544 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1799376 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE 2103 | 182222103 | FUSE | 6737 | 20230108 | 19 | 20230108 | 1105 | 1932450 | 646 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 12047 | 36.5709 | -121.8861 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0010060 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1799903 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 23517 | 20230108 | 31 | 20230108 | 1755 | 1931043 | 1044 | Distribution Circuit | Vegetation | Tree - fell into line | 226 | 235944 | 36.7888 | -121.694 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009830 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1799672 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | BUENA VISTA-1103 | 182261103 | FUSE | 5101 | 20230108 | 59 | 20230108 | 359 | 1931397 | 180 | Distribution Circuit | Equipment Failure/Involved | Overhead | 126 | 22680 | 36.6533 | -121.6484 | Yes | Clear;32-90F | Crossarm- Wood | Broken | 23-0009486 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1799475 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 5711 | 20230108 | 103 | 20230108 | 828 | 1931503 | 445 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 5340 | 36.7978 | -121.7366 | Yes | Strong Winds-Clear;32-90F | Conductor- Overhead | Annealed | 23-0009827 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1799668 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 9291 | 20230108 | 104 | 20230108 | 1841 | 1934225 | 1057 | Distribution Circuit | Equipment Failure/Involved | Overhead | 62 | 65534 | 36.6162 | -121.9348 | Yes | Clear;32-90 F | Jumper | Broken | 23-0010370 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1800219 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 5203 | 20230108 | 105 | 20230126 | 1627 | 1931486 | 26842 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 678858 | 37.0394 | -122.0817 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009833 | OH | Sus | 35419572 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1799677 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 8895 | 20230108 | 106 | 20230108 | 1442 | 1931497 | 816 | Distribution Circuit | Vegetation | Tree - branch fell on line | 144 | 99272 | 36.5891 | -121.9104 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009843 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1799693 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 23653 | 20230108 | 109 | 20230109 | 1323 | 1932875 | 2174 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 4348 | 36.7971 | -121.7481 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0009929 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1799779 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 2809 | 20230108 | 120 | 20230108 | 852 | 1932593 | 452 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 39 | 17628 | 36.5196 | -121.8082 | Yes | Clear;32-90F |  |  | 23-0009903 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1799753 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 1563 | 20230108 | 125 | 20230108 | 937 | s1799813 | 492 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 1476 | 37.045 | -122.0754 | Yes | Clear;32-90 F |  |  | 23-0009962 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1799813 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 2993 | 20230108 | 127 | 20230108 | 730 | 1931805 | 363 | Distribution Circuit | Vegetation | Tree - branch fell on line | 319 | 115797 | 36.9722 | -122.0306 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0009847 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1799699 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 1143 | 20230108 | 129 | 20230108 | 1807 | 1931781 | 998 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 13972 | 37.0043 | -122.0202 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010216 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1800067 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | RECLOSER | 9120 | 20230108 | 153 | 20230108 | 1223 | 1931919 | 630 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2636 | 1104456 | 36.6022 | -121.9359 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0009670 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1799503 | 0 | EPSS Ckt | N | 2023 | A-B-C-GRD
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 183 | 20230108 | 158 | 20230108 | 748 | 1931988 | 350 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 19250 | 36.9293 | -121.8586 | Yes | Clear;32-90F |  |  | 23-0009868 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1799719 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 5997 | 20230108 | 219 | 20230108 | 1029 | 1932425 | 490 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 7840 | 36.7882 | -121.6799 | Yes | Clear;32-90 F |  |  | 23-0010023 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1799868 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | FUSE | 6433 | 20230108 | 809 | 20230108 | 1841 | 1932920 | 632 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 632 | 36.6 | -121.8775 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0009954 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1799804 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 6465 | 20230108 | 809 | 20230109 | 147 | 1933845 | 1058 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2116 | 37.0541 | -122.1697 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010242 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1800092 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | TRANSFORMER | 411422046026 | 20230108 | 816 | 20230108 | 1451 | 1932680 | 395 | Transformer only | Company Initiated | Other Circuits | 12 | 4740 | 36.5615 | -121.9227 | Yes | Clear;32-90 F | Transformer (OH) |  | 23-0010246 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1800097 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1102 | 182011102 | FUSE | 24681 | 20230108 | 925 | 20230108 | 1600 | 1932916 | 395 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 9875 | 36.6987 | -121.6482 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0009952 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | No | No | 1799802 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 2811 | 20230108 | 948 | 20230108 | 1228 | 1932990 | 160 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 3200 | 36.5143 | -121.8127 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010081 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1799927 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 6689 | 20230108 | 1042 | 20230108 | 1315 | 1933182 | 153 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1683 | 36.8881 | -121.8071 | Yes | Clear;32-90 F |  |  | 23-0010171 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1800022 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9763 | 20230108 | 1045 | 20230108 | 1614 | 1933986 | 329 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 6580 | 37.1767 | -122.1629 | Yes | Clear;32-90 F |  |  | 23-0010313 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1800159 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | OTHER | 2319 | 20230108 | 1338 | 20230112 | 1745 | 1933738 | 6007 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 30035 | 37.096 | -122.1005 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0010199 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1800051 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 7681 | 20230108 | 1355 | 20230108 | 1831 | 1933716 | 276 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 2760 | 36.5832 | -121.865 | Yes | Clear;32-90 F | Conductor- Overhead | On Ground | 23-0010256 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1800105 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 35874 | 20230108 | 1359 | 20230109 | 413 | 1932631 | 854 | Distribution Circuit | Equipment Failure/Involved | Overhead | 604 | 434094 | 37.0312 | -122.1882 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Regulator | Leaking | 23-0010193 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1800045 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 35874 | 20230108 | 1359 | 20230109 | 413 | 1932631 | 854 | Distribution Circuit | Equipment Failure/Involved | Overhead | 604 | 434094 | 37.0312 | -122.1882 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Regulator | Leaking | 23-0010193 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1800045 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 5151 | 20230108 | 1453 | 20230120 | 1147 | 1933852 | 17094 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 85470 | 37.111 | -122.0899 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0010321 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1800169 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | OCB | 2101/2 | 20230108 | 1517 | 20230108 | 1528 | 1933750 | 11 | Distribution Circuit | Equipment Failure/Involved | Overhead | 676 | 7436 | 37.0953 | -122.1437 | Yes | Clear;32-90 F | Crossarm- Wood | Burned/flashed | 23-0010262 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1800110 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9775 | 20230108 | 1556 | 20230114 | 1557 | 1935241 | 8641 | Distribution Circuit | Vegetation | Tree - branch fell on line | 38 | 328358 | 37.141 | -122.0902 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011641 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | Yes | 1801406 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SOLEDAD-2105 | 182052105 | FUSE | 8747 | 20230108 | 1625 | 20230108 | 1753 | 1934086 | 85 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 3400 | 36.4322 | -121.3336 | Yes | Clear;32-90 F | Cutout- fuse holder | Failed/Faulted | 23-0010400 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1800247 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRANSFORMER | 315254824345 | 20230108 | 1627 | 20230112 | 1814 | 1934091 | 5867 | Transformer only | Vegetation | Tree - fell into line | 5 | 29335 | 37.1574 | -122.1267 | Yes | Clear;32-90 F | Transformer | Broken | 23-0010409 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1800256 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | SWITCH | 8945 | 20230108 | 1655 | 20230108 | 1716 | 1934247 | 21 | Distribution Circuit | Company Initiated | Return Circuit Normal | 74 | 770 | 36.5004 | -121.934 | Yes | Clear;32-90 F | Switch (OH) | Normal | 23-0008834 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1800224 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | TRANSFORMER | 411355746624 | 20230108 | 1702 | 20230111 | 740 | 1934198 | 3758 | Transformer only | Vegetation | Tree - fell into line | 5 | 18790 | 36.5774 | -121.9459 | Yes | Clear;32-90 F | Other | Broken- wire on ground | 23-0010391 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1800238 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | OCB | 2202/2 | 20230108 | 1914 | 20230110 | 1402 | 1934547 | 2568 | Distribution Circuit | Vegetation | Tree - fell into line | 6157 | 746396 | 36.5786 | -121.9085 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010443 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1800287 | 0 | EPSS Ckt | N | 2023 | ABC
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | RECLOSER | 95690 | 20230108 | 1943 | 20230112 | 2033 | 1935054 | 312 | Distribution Circuit | Vegetation | Tree - fell into line | 3252 | 226286 | 37.1249 | -122.125 | Yes | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0010666 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1800523 | 0 | EPSS Ckt | N | 2023 | AC
CENTRAL COAST | KING CITY | KING CITY-1106 | 182031106 | RECLOSER | 500 | 20230108 | 2026 | 20230112 | 1753 | 1934739 | 5607 | Distribution Circuit | Equipment Failure/Involved | Overhead | 81 | 437913 | 36.2185 | -121.0846 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010480 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1800328 | 0 | EPSS Ckt | N | 2023 | A & C
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | FUSE | 647 | 20230108 | 2102 | 20230112 | 1745 | 1948256 | 5563 | Distribution Circuit | Company Initiated | Return Circuit Normal | 4 | 22252 | 36.1794 | -121.6953 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0013746 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1803144 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | OTHER | SO-ND266260 | 20230108 | 2159 | 20230109 | 32 | 1934881 | 153 | Distribution Circuit | Company Initiated | Return Circuit Normal | 13 | 1866 | 37.0312 | -122.188 | Yes | Overcast-Heavy Rain;32-90 F | Regulator | Normal | 23-0010193 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1800429 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1101 | 182011101 | RECLOSER | 22052 | 20230108 | 2204 | 20230109 | 208 | 1934884 | 244 | Distribution Circuit | Vegetation | Tree - fell into line | 2102 | 113866 | 36.6807 | -121.6511 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0010582 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1800436 | 0 | Non-EPSS | N | 2023 | NONE
CENTRAL COAST | SALINAS | SALINAS-1107 | 182011107 | FUSE | 4873 | 20230108 | 2302 | 20230109 | 1453 | 1934943 | 951 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 12 | 11412 | 36.6652 | -121.6411 | Yes | Clear;32-90F | Other | Burned/flashed | 23-0010656 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1800513 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 8895 | 20230109 | 35 | 20230109 | 155 | 1935104 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 152 | 12160 | 36.5891 | -121.9104 | Yes | Clear;32-90F |  |  | 23-0010683 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1800541 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | FUSE | 5957 | 20230109 | 102 | 20230109 | 1454 | 1935154 | 832 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 2220 | 36.5417 | -121.4661 | Yes | Clear;32-90 F | Jumper | Burned Open | 23-0011305 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1801083 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 9101 | 20230109 | 149 | 20230109 | 340 | 1935195 | 108 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 10476 | 36.42 | -121.7812 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0010748 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1800614 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 5459 | 20230109 | 152 | 20230112 | 1711 | 1936781 | 5239 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 106200 | 37.1385 | -122.1432 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011449 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801207 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | OCB | 2201/2 | 20230109 | 216 | 20230109 | 2300 | 1935800 | 1244 | Distribution Circuit | Vegetation | Tree - fell into line | 1289 | 1601657 | 36.5786 | -121.9085 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010786 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1800647 | 0 | EPSS Ckt | N | 2023 | A-C
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 766491 | 20230109 | 216 | 20230110 | 1853 | 1939766 | 2437 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 26807 | 36.5663 | -121.9354 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011688 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1801450 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 90678 | 20230109 | 234 | 20230111 | 1024 | 1935326 | 3350 | Distribution Circuit | Vegetation | Tree - fell into line | 582 | 261930 | 37.0954 | -122.1281 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010723 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1800584 | 0 | EPSS Ckt | N | 2023 | C GRD
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | FUSE | 8175 | 20230109 | 235 | 20230110 | 1623 | 1935320 | 2268 | Distribution Circuit | Environmental/External | Flood/Erosion | 382 | 231720 | 36.9758 | -121.9172 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0010983 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1800820 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SPENCE 1102 | 182201102 | RECLOSER | 321000 | 20230109 | 237 | 20230113 | 1505 | 1935344 | 6508 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 64556 | 36.6105 | -121.4925 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010726 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1800588 | 0 | EPSS Ckt | N | 2023 | C & GRD
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | SWITCH | 1285 | 20230109 | 239 | 20230111 | 1840 | 1938921 | 3841 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 503171 | 36.4906 | -121.9368 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010734 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | Yes | No | 1801200 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 1385 | 20230109 | 239 | 20230112 | 1709 | 1947935 | 5190 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 15570 | 36.4823 | -121.9303 | Yes | Clear;32-90 F |  |  | 23-0013623 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1803076 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 457 | 20230109 | 239 | 20230113 | 1619 | 1947937 | 6580 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 125020 | 36.4927 | -121.9335 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0013625 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1803079 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 9467 | 20230109 | 241 | 20230110 | 2025 | 1937786 | 2504 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 10016 | 36.5391 | -121.8706 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011101 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1800913 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 8895 | 20230109 | 246 | 20230110 | 45 | 1935353 | 1319 | Distribution Circuit | Vegetation | Tree - branch fell on line | 152 | 200488 | 36.5891 | -121.9104 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0011299 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801078 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | TRANSFORMER | 411413445618 | 20230109 | 307 | 20230109 | 1917 | 1936851 | 970 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 17460 | 36.5501 | -121.9251 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0010886 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1800735 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | RECLOSER | 440 | 20230109 | 308 | 20230110 | 2230 | 1935403 | 2602 | Distribution Circuit | Vegetation | Tree - branch fell on line | 223 | 525316 | 36.4389 | -121.9203 | Yes | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0010734 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1800597 | 0 | EPSS Ckt | N | 2023 | SGF
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 1421 | 20230109 | 316 | 20230110 | 1325 | 1935411 | 2049 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 40980 | 36.5743 | -121.9483 | Yes | Clear;32-90 F |  |  | 23-0012498 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802197 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | OTHER | WIRE DOWN 2 SS OF CGC # 411422047652 | 20230109 | 321 | 20230109 | 1457 | 1935911 | 696 | Distribution Circuit | Equipment Failure/Involved | Overhead | 145 | 21391 | 36.6057 | -121.9245 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010799 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | Yes | Yes | 1800660 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 8047 | 20230109 | 325 | 20230110 | 1750 | 1935436 | 2305 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 57625 | 36.5029 | -121.9336 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011644 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1801409 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | PACIFIC GROVE SUB | 18244 | OCB | 423/2 | 20230109 | 333 | 20230109 | 1752 | 1935458 | 859 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 534 | 458706 | 36.6171 | -121.9192 | Yes | Clear;32-90F |  |  | 23-0010794 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1800656 | 0 | Non-EPSS | N | 2023 | GRD (INST)
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 627 | 20230109 | 337 | 20230109 | 2117 | 1935465 | 1060 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 23320 | 36.5489 | -121.8966 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011010 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1800841 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 1491 | 20230109 | 338 | 20230110 | 1548 | 1935476 | 2170 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 86800 | 36.5057 | -121.9352 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0011623 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801386 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | PACIFIC GROVE SUB | 18244 | OCB | 422/2 | 20230109 | 339 | 20230110 | 1758 | 1935477 | 2299 | Distribution Circuit | Vegetation | Tree - fell into line | 785 | 981540 | 36.6171 | -121.9193 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010793 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1800655 | 0 | Non-EPSS | N | 2023 | GRD (TIME)
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0424 | 182440424 | TRANSFORMER | 411418448168 | 20230109 | 345 | 20230109 | 1806 | 1935499 | 861 | Transformer only | Vegetation | Tree - fell into line | 9 | 7749 | 36.6203 | -121.9264 | Yes | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0011163 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1800965 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | RECLOSER | 648928 | 20230109 | 351 | 20230111 | 1335 | 1935517 | 3464 | Distribution Circuit | Vegetation | Tree - fell into line | 347 | 637646 | 36.5332 | -121.9152 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010750 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1800616 | 0 | EPSS Ckt | N | 2023 | A C
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 3567 | 20230109 | 358 | 20230109 | 829 | 1935528 | 271 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 180 | 48780 | 36.8799 | -121.6939 | Yes | Clear;32-90 F |  |  | 23-0010884 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1800733 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRIP-SAVER | 6219 | 20230109 | 405 | 20230109 | 1734 | 1938878 | 809 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 17798 | 37.1841 | -122.1409 | Yes | Clear;32-90 F |  |  | 23-0011434 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801193 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 8331 | 20230109 | 408 | 20230109 | 1441 | 1938468 | 623 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 3115 | 37.0579 | -121.9734 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0011315 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN |  | 0 | No | No | No | 1801092 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 6851 | 20230109 | 418 | 20230111 | 1150 | 1935599 | 3332 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 43052 | 36.5569 | -121.9156 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0011443 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801202 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 173 | 20230109 | 425 | 20230115 | 1842 | 1936058 | 9497 | Distribution Circuit | Environmental/External | Flood/Erosion | 3 | 28491 | 37.0566 | -122.0326 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0011033 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1800857 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 6087 | 20230109 | 425 | 20230117 | 1714 | 1935618 | 12289 | Distribution Circuit | Vegetation | Tree - fell into line | 186 | 1419693 | 37.0665 | -122.0336 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0011171 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1800975 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | JUMPER | 32886 CENTER PHASE JPR | 20230109 | 435 | 20230109 | 1059 | 1935647 | 380 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4163 | 1299816 | 36.5944 | -121.866 | Yes | Overcast-Rain;32-90 F | Jumper | Burned/flashed | 23-0010761 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1800627 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | OTHER | SO-ND266260 | 20230109 | 441 | 20230109 | 701 | 1935659 | 140 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 669 | 93465 | 37.0312 | -122.188 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 23-0010789 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1800651 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 6081 | 20230109 | 455 | 20230110 | 1753 | 1935709 | 2218 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 19258 | 37.0577 | -122.0333 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011321 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801100 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | OCB | 2202/2 | 20230109 | 458 | 20230110 | 51 | 1935715 | 1193 | Distribution Circuit | Vegetation | Tree - fell into line | 2895 | 3439908 | 36.5786 | -121.9085 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010771 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1800635 | 0 | EPSS Ckt | N | 2023 | B GRD
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | TRANSFORMER | 412387252152 | 20230109 | 505 | 20230109 | 1713 | 1935729 | 728 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 2184 | 36.7382 | -121.6004 | Yes | Clear;32-90 F | Transformer | Broken | 23-0010887 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1800736 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | TRIP-SAVER | 5291 | 20230109 | 507 | 20230110 | 705 | 1935738 | 1558 | Distribution Circuit | Vegetation | Tree - fell into line | 420 | 654360 | 36.9756 | -122.0584 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0010858 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1800707 | 0 | EPSS Ckt | N | 2023 | ABC
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 7637 | 20230109 | 507 | 20230109 | 1116 | 1935735 | 369 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 9963 | 37.0078 | -121.9385 | Yes | Clear;32-90 F |  |  | 23-0010981 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1800819 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 1823 | 20230109 | 508 | 20230110 | 2232 | 1935752 | 2484 | Distribution Circuit | Vegetation | Tree - fell into line | 212 | 463124 | 36.9797 | -122.0426 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0011128 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1800937 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 33542 | 20230109 | 511 | 20230113 | 1646 | 1936570 | 6455 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 606770 | 37.0906 | -122.0456 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011104 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1800916 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 10433 | 20230109 | 511 | 20230117 | 1955 | 1950955 | 12404 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 99232 | 37.1051 | -122.0469 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0014805 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | Yes | No | 1803919 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5629 | 20230109 | 511 | 20230117 | 1955 | 1951770 | 12404 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 248080 | 37.1128 | -122.048 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0015237 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1804238 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | JUMPER | 10294 NEW OIS | 20230109 | 511 | 20230117 | 1955 | 1957816 | 12404 | Distribution Circuit | Vegetation | Tree - fell into line | 140 | 1736560 | 37.0993 | -122.0531 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011724 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805839 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 11851 | 20230109 | 514 | 20230109 | 1046 | 1935773 | 332 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1992 | 36.8781 | -121.6687 | Yes | Clear;32-90 F |  |  | 23-0011041 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1800865 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 5335 | 20230109 | 516 | 20230109 | 1403 | 1935959 | 527 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 12986 | 37.0281 | -121.9871 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0011280 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801057 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | RECLOSER | 5400 | 20230109 | 518 | 20230109 | 1448 | 1935806 | 570 | Distribution Circuit | Environmental/External | Flood/Erosion | 9 | 5130 | 37.0801 | -122.0838 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010784 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1800648 | 0 | EPSS Ckt | N | 2023 | ABC GRD
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 10996 | 20230109 | 518 | 20230109 | 1233 | 1935780 | 435 | Distribution Circuit | Environmental/External | Flood/Erosion | 257 | 111795 | 37.0748 | -122.0845 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0010784 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1800645 | 0 | EPSS Ckt | N | 2023 | ABC GRD
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 121 | 20230109 | 518 | 20230117 | 1205 | 1936700 | 11927 | Distribution Circuit | Environmental/External | Flood/Erosion | 8 | 95416 | 37.0514 | -122.0688 | Yes | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0010872 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1800723 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 5300 | 20230109 | 518 | 20230117 | 1627 | 1945041 | 12189 | Distribution Circuit | Vegetation | Tree - fell into line | 351 | 4278339 | 37.0383 | -122.0708 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012395 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1802120 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | RECLOSER | 944178 | 20230109 | 519 | 20230109 | 1156 | 1935777 | 397 | Distribution Circuit | Equipment Failure/Involved | Overhead | 754 | 299338 | 37.0926 | -122.0964 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0010782 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | No | No | 1800644 | 0 | EPSS Ckt | N | 2023 | ABC GRD
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | JUMPER | OPEN/CREATE FOR LR 698634 | 20230109 | 519 | 20230109 | 1422 | 1938059 | 543 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 43440 | 37.0955 | -122.0856 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010782 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1800966 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 9125 | 20230109 | 519 | 20230113 | 1643 | 1938398 | 6444 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 244872 | 37.1004 | -122.086 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010782 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801061 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET 2106 | 83252106 | RECLOSER | 5178 | 20230109 | 524 | 20230109 | 1324 | 1935790 | 480 | Distribution Circuit | Vegetation | Tree - fell into line | 267 | 99296 | 37.0324 | -121.9467 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010785 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1800646 | 0 | EPSS Ckt | N | 2023 | B-C-GRD
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 46831 | 20230109 | 525 | 20230109 | 1928 | 1935795 | 843 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 9273 | 37.0131 | -122.0305 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0011218 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801014 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6671 | 20230109 | 529 | 20230111 | 1929 | 1935961 | 3720 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 126480 | 36.9652 | -121.8484 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010985 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1800822 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | PANOCHE-1103 | 253671103 | RECLOSER | 4008 | 20230109 | 531 | 20230109 | 1449 | 1935817 | 558 | Distribution Circuit | Vegetation | Tree - branch fell on line | 118 | 42833 | 36.6116 | -120.9293 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010788 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1800649 | 0 | EPSS Ckt | N | 2023 | C-GRD
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 5269 | 20230109 | 532 | 20230109 | 1106 | 1935890 | 334 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 2781 | 36.9894 | -122.0312 | Yes | Clear;32-90 F |  |  | 23-0010869 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1800721 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 5090 | 20230109 | 535 | 20230114 | 1023 | 1935839 | 7488 | Distribution Circuit | Vegetation | Tree - branch fell on line | 422 | 533549 | 36.9804 | -121.892 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010790 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1800652 | 0 | EPSS Ckt | N | 2023 | ABC-GRD
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 871 | 20230109 | 539 | 20230109 | 945 | 1935852 | 246 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 1476 | 36.8187 | -121.6857 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0010987 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1800823 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 426822 | 20230109 | 540 | 20230109 | 1648 | 1935872 | 668 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1336 | 37.1016 | -122.0324 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011431 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801190 | 0 | EPSS Ckt | N | 2023 | C & GRD
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 6161 | 20230109 | 540 | 20230116 | 1805 | 1950604 | 10825 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 248975 | 37.1187 | -122.0198 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0014706 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1803860 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 601610 | 20230109 | 540 | 20230117 | 1248 | 1956171 | 11948 | Distribution Circuit | Vegetation | Tree - branch fell on line | 44 | 525712 | 37.1117 | -122.0207 | Yes | Clear;32-90 F | Conductor- Overhead | On Ground | 23-0011724 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1805448 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 2689 | 20230109 | 540 | 20230117 | 1835 | 1959608 | 12295 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 393440 | 37.1274 | -122.0181 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0017656 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1806213 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 2917 | 20230109 | 542 | 20230109 | 828 | 1935873 | 166 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 3206 | 36.9542 | -122.0311 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0010840 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1800697 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 1699 | 20230109 | 542 | 20230109 | 954 | 1935898 | 252 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 2268 | 36.9707 | -121.797 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0010963 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1800801 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 5901 | 20230109 | 543 | 20230116 | 1234 | 1935875 | 10491 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 167856 | 37.0944 | -121.9716 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011357 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801129 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 11028 | 20230109 | 547 | 20230110 | 1233 | 1935896 | 1846 | Distribution Circuit | Vegetation | Tree - fell into line | 1237 | 783536 | 36.9714 | -121.8908 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010795 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1800657 | 0 | EPSS Ckt | N | 2023 | B GRD
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 5569 | 20230109 | 551 | 20230109 | 1528 | 1937032 | 577 | Distribution Circuit | Environmental/External | Flood/Erosion | 53 | 28180 | 37.0503 | -122.0672 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0010904 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1800749 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE 1101 | 182221101 | TRANSFORMER | 411673247530 | 20230109 | 553 | 20230111 | 1259 | 1935965 | 3306 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 59508 | 36.6046 | -121.8387 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0012551 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802238 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 934561 | 20230109 | 557 | 20230112 | 1705 | 1935951 | 4988 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 124700 | 37.012 | -121.8249 | Yes | Clear;32-90 F |  |  | 23-0011409 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801174 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | FUSE | 95569 | 20230109 | 602 | 20230109 | 1131 | 1935967 | 329 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1645 | 36.988 | -121.9385 | Yes | Clear;32-90 F |  |  | 23-0011111 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1800922 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 3917 | 20230109 | 608 | 20230109 | 858 | 1936020 | 170 | Distribution Circuit | Vegetation | Tree - bark fell into line | 16 | 2720 | 36.9516 | -121.8502 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0010919 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1800763 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | OTHER | WIRE DOWN 1 S/E OF 10445 | 20230109 | 617 | 20230118 | 1431 | 1950950 | 13454 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 100324 | 37.1062 | -122.0428 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0014801 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | Yes | Yes | 1803915 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | RECLOSER | 16010 | 20230109 | 618 | 20230111 | 1618 | 1947936 | 3480 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 116 | 403680 | 37.0886 | -122.0874 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 23-0011734 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1803078 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6647 | 20230109 | 621 | 20230122 | 1524 | 1938406 | 19263 | Distribution Circuit | Environmental/External | Flood/Erosion | 21 | 404523 | 37.0266 | -121.7801 | Yes | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0011290 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1801065 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5625 | 20230109 | 625 | 20230117 | 1955 | 1957913 | 12330 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 1380960 | 37.105 | -122.0512 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017162 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1805849 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 5825 | 20230109 | 629 | 20230112 | 1418 | 1936098 | 4789 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 244239 | 37.0127 | -121.7935 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010882 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1800731 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | OCB | 2101/2 | 20230109 | 632 | 20230109 | 1900 | 1936289 | 748 | Distribution Circuit | Vegetation | Tree - grew into line | 9090 | 467384 | 36.9521 | -121.76 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010817 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1800675 | 0 | EPSS Ckt | N | 2023 | GRD OC INST
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 1721 | 20230109 | 634 | 20230110 | 1838 | 1936205 | 2164 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 196577 | 37.056 | -121.9972 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011036 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1800859 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 7837 | 20230109 | 634 | 20230110 | 1210 | 1936407 | 1776 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1776 | 36.9617 | -121.7898 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0010883 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1800732 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 8419 | 20230109 | 642 | 20230110 | 1949 | 1936527 | 2227 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 73491 | 36.5693 | -121.7917 | Yes | Clear;32-90 F | Conductor- Overhead | Contaminated | 23-0011595 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801359 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | FUSE | 6949 | 20230109 | 648 | 20230109 | 1400 | 1936302 | 432 | Distribution Circuit | Vegetation | Tree - fell into line | 200 | 27999 | 36.602 | -121.9019 | Yes | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0010900 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1800747 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 287578 | 20230109 | 649 | 20230109 | 930 | 1936300 | 161 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 966 | 37.0438 | -122.0755 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0010818 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1800676 | 0 | EPSS Ckt | N | 2023 | AB
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 8187 | 20230109 | 654 | 20230109 | 1813 | 1936018 | 679 | Distribution Circuit | Vegetation | Tree - branch fell on line | 84 | 57036 | 36.9701 | -121.8856 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010853 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1800703 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 974520 | 20230109 | 655 | 20230112 | 1719 | 1936328 | 4944 | Distribution Circuit | Vegetation | Tree - fell into line | 252 | 468655 | 36.9908 | -121.8063 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010822 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1800680 | 0 | EPSS Ckt | N | 2023 | A PH GRD
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | SWITCH | 464844 | 20230109 | 655 | 20230112 | 1705 | 1937797 | 4930 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 34510 | 37.0157 | -121.82 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010822 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1800915 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | SWITCH | 588930 | 20230109 | 655 | 20230113 | 1807 | 1937916 | 6432 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 237984 | 37.0169 | -121.8198 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010822 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1800942 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | SWITCH | 56893 | 20230109 | 655 | 20230113 | 1028 | 1950690 | 5973 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 53757 | 37.0633 | -121.8278 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0014729 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1803867 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 6775 | 20230109 | 657 | 20230109 | 1030 | 1936349 | 213 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 74 | 15762 | 36.8813 | -121.6414 | Yes | Clear;32-90 F |  |  | 23-0010975 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1800815 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1104 | 182201104 | FUSE | 5319 | 20230109 | 712 | 20230109 | 930 | 1936411 | 138 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1242 | 36.5823 | -121.4982 | Yes | Clear;32-90 F |  |  | 23-0010969 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1800809 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DEL MONTE-2104 | 182222104 | FUSE | 20461 | 20230109 | 717 | 20230109 | 1250 | 1936444 | 333 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 3663 | 36.5384 | -121.7252 | Yes | Clear;32-90 F |  |  | 23-0012351 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1802091 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | OTHER | SO-ND266260 | 20230109 | 717 | 20230109 | 1200 | 1937462 | 283 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 669 | 171293 | 37.0312 | -122.188 | Yes | Overcast-Heavy Rain;32-90 F |  |  | 23-0011031 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1800855 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6559 | 20230109 | 726 | 20230109 | 1718 | 1939038 | 592 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 18352 | 36.9267 | -121.7459 | Yes | Clear;32-90 F |  |  | 23-0011472 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801230 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2103 | 182492103 | FUSE | 9445 | 20230109 | 734 | 20230109 | 905 | 1936559 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 67 | 6097 | 36.8339 | -121.3815 | Yes | Clear;32-90 F |  |  | 23-0010942 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1800780 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 891361 | 20230109 | 747 | 20230109 | 1840 | 1938880 | 653 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 11754 | 37.1891 | -122.1431 | Yes | Clear;32-90 F |  |  | 23-0011432 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801191 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 11044 | 20230109 | 801 | 20230109 | 854 | 1936658 | 53 | Distribution Circuit | Company Initiated | Coordination failure | 2034 | 107802 | 37.0401 | -122.0297 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Fuse | Normal | 23-0010868 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1800720 | 0 | EPSS Ckt | N | 2023 | A GRD
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8383 | 20230109 | 801 | 20230109 | 950 | 1936991 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 4247 | 37.0396 | -122.0302 | Yes | Clear;32-90 F |  |  | 23-0010897 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1800745 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 2705 | 20230109 | 802 | 20230117 | 1710 | 1936745 | 12068 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 325836 | 37.0005 | -121.7403 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011658 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801422 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | OTHER | WIRE DOWN 4 LD SIDE OF 937291 | 20230109 | 806 | 20230126 | 1335 | 1938106 | 24809 | Distribution Circuit | Environmental/External | Flood/Erosion | 13 | 113658 | 37.1194 | -121.9637 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0012123 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1801895 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 23883 | 20230109 | 810 | 20230109 | 1728 | 1936717 | 558 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 4464 | 36.8081 | -121.7038 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0011287 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801062 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 12429 | 20230109 | 819 | 20230112 | 1340 | 1944768 | 4641 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 69615 | 37.1378 | -122.1423 | Yes | Clear;32-90F |  |  | 23-0014553 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803784 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | BUENA VISTA-1103 | 182261103 | FUSE | 23253 | 20230109 | 820 | 20230109 | 1416 | 1936849 | 356 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 712 | 36.6551 | -121.6301 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011055 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | Yes | 1800877 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 2923 | 20230109 | 844 | 20230112 | 1324 | 1937044 | 4600 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 202400 | 37.1737 | -122.1456 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011098 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1800910 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 2809 | 20230109 | 845 | 20230109 | 1933 | 1937047 | 648 | Distribution Circuit | Vegetation | Tree - branch fell on line | 39 | 25272 | 36.5196 | -121.8082 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0011565 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801327 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 6689 | 20230109 | 845 | 20230109 | 859 | 1935568 | 14 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 154 | 36.8881 | -121.8071 | Yes | Clear;32-90 F |  |  | 23-0010917 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1800761 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | OCB | 1102/2 | 20230109 | 854 | 20230109 | 2026 | 1937124 | 692 | Distribution Circuit | Equipment Failure/Involved | Underground | 3469 | 1581950 | 36.5569 | -121.8976 | Yes | Clear;32-90 F | Switch (UG) | Failed/Faulted | 23-0010930 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1800770 | 0 | EPSS Ckt | N | 2023 | B GRD
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 5209 | 20230109 | 918 | 20230117 | 1627 | 1937218 | 11949 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 238980 | 37.0373 | -122.0723 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011608 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801371 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 8593 | 20230109 | 920 | 20230110 | 1520 | 1937240 | 1800 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 45000 | 36.9667 | -121.8694 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011037 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1800860 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 9813 | 20230109 | 920 | 20230112 | 1355 | 1937190 | 4595 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 10405 | 36.861 | -121.6873 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011136 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1800944 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | RECLOSER | 3710 | 20230109 | 922 | 20230109 | 1508 | 1937316 | 346 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 7958 | 36.7284 | -121.7844 | Yes | Clear;32-90 F |  |  | 23-0011279 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801056 | 0 | Non-EPSS | N | 2023 | N/A
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 42086 | 20230109 | 931 | 20230112 | 1424 | 1937304 | 4584 | Distribution Circuit | Vegetation | Tree - fell into line | 177 | 397782 | 36.9036 | -121.7361 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011097 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1800909 | 0 | EPSS Ckt | N | 2023 | B & GRD
CENTRAL COAST | COAST | SOQUEL-0402 | 83300402 | OTHER | WIRE DOWN E/OF CGC 315765317548 | 20230109 | 931 | 20230109 | 1810 | 1935838 | 519 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 16608 | 36.9732 | -121.9487 | Yes | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0010976 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | Yes | Yes | 1800816 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 705 | 20230109 | 955 | 20230111 | 1401 | 1945061 | 3126 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 12504 | 37.0523 | -122.1381 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012405 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802131 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SOLEDAD-2105 | 182052105 | FUSE | 7863 | 20230109 | 1003 | 20230109 | 1604 | 1935359 | 361 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 841 | 36.4581 | -121.3733 | Yes | Clear;32-90 F | Jumper | Burned Open | 23-0011401 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1801167 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 2029 | 20230109 | 1006 | 20230125 | 1343 | 1937490 | 23257 | Distribution Circuit | Environmental/External | Flood/Erosion | 9 | 163005 | 37.0155 | -121.7542 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0011450 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801208 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | TRANSFORMER | 316463613665 | 20230109 | 1117 | 20230109 | 1315 | 1937809 | 118 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 472 | 36.8692 | -121.7086 | Yes | Clear;32-90 F | Service conductor | Broken | 23-0011183 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1800984 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 141 | 20230109 | 1130 | 20230109 | 1610 | 1937863 | 280 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1305 | 37.048 | -122.0648 | Yes | Clear;32-90 F |  |  | 23-0011345 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801120 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 5413 | 20230109 | 1136 | 20230111 | 1344 | 1937893 | 3008 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 105280 | 37.0443 | -122.1497 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011190 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1800990 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 68191 | 20230109 | 1156 | 20230109 | 1521 | 1937988 | 205 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 3895 | 36.9816 | -121.9026 | Yes | Clear;32-90 F | Conductor- Overhead | On Ground | 23-0011143 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | Yes | No | 1800949 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | FUSE | 9031 | 20230109 | 1309 | 20230109 | 1929 | 1937249 | 380 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 3800 | 36.6234 | -121.9286 | Yes | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0011228 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | Yes | 1801020 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0422 | 182440422 | FUSE | 2581 | 20230109 | 1343 | 20230110 | 1335 | 1938357 | 1432 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 96 | 137472 | 36.5918 | -121.9454 | Yes | Clear;32-90 F |  |  | 23-0012400 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802127 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 12775 | 20230109 | 1349 | 20230123 | 1710 | 1938360 | 20361 | Distribution Circuit | Environmental/External | Flood/Erosion | 111 | 183261 | 36.9691 | -121.9048 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0011344 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1801119 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 5711 | 20230109 | 1418 | 20230109 | 1759 | 1938073 | 221 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 2652 | 36.7978 | -121.7366 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0011168 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1800972 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | SWITCH | 2351 | 20230109 | 1452 | 20230111 | 1657 | 1938417 | 3005 | Distribution Circuit | Equipment Failure/Involved | Overhead | 74 | 166778 | 36.9878 | -121.9534 | Yes | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0011328 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1801104 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | OTHER | 1445 | 20230109 | 1505 | 20230111 | 1842 | 1938560 | 3097 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 37164 | 36.5735 | -121.9108 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011557 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | Yes | No | 1801320 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 6085 | 20230109 | 1540 | 20230123 | 1810 | 1938694 | 20310 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 223410 | 37.0636 | -122.0348 | Yes | Clear;32-90 F | Pole-Wood | Normal | 23-0011506 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801263 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | SWITCH | 117919 | 20230109 | 1705 | 20230111 | 855 | 1945362 | 2390 | Distribution Circuit | Vegetation | Tree - fell into line | 99 | 236610 | 36.4378 | -121.7942 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012531 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1802227 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 5955 | 20230109 | 1728 | 20230109 | 2208 | 1939060 | 280 | Distribution Circuit | Vegetation | Tree - fell into line | 167 | 46760 | 37.0022 | -121.942 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0011478 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1801236 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 8183 | 20230109 | 1733 | 20230109 | 1854 | 1939032 | 81 | Distribution Circuit | Vegetation | Tree - fell into line | 102 | 8262 | 36.9646 | -121.8903 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0011470 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1801227 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6639 | 20230109 | 1743 | 20230112 | 1820 | 1939369 | 4357 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 102991 | 37.0075 | -121.809 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0011542 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801304 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRANSFORMER | 315251824206 | 20230109 | 1746 | 20230113 | 1221 | 1946332 | 5435 | Transformer only | Vegetation | Tree - fell into line | 6 | 32610 | 37.1538 | -122.1277 | Yes | Clear;32-90 F | Transformer | Broken | 23-0006011 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802500 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRANSFORMER | 315219225321 | 20230109 | 1746 | 20230111 | 1336 | 1946329 | 2630 | Transformer only | Unknown Cause | Patrol - found nothing | 13 | 34190 | 37.1838 | -122.1421 | Yes | Clear;32-90 F |  |  | 23-0006011 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1802498 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 2885 | 20230109 | 1903 | 20230110 | 1201 | 1939399 | 1018 | Distribution Circuit | Vegetation | Tree - branch fell on line | 78 | 79404 | 36.5423 | -121.93 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0011550 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1801313 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRANSFORMER | 315147924751 | 20230109 | 1946 | 20230113 | 1936 | 1939749 | 5750 | Transformer only | Vegetation | Tree - fell into line | 1 | 5750 | 37.1679 | -122.1664 | Yes | Clear;32-90 F | Transformer | Leaking | 23-0011693 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801455 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | FUSE | 2065 | 20230109 | 2007 | 20230110 | 1015 | 1939530 | 848 | Distribution Circuit | Equipment Failure/Involved | Overhead | 51 | 43248 | 36.6157 | -121.9147 | Yes | Clear;32-90F | Cutout- fuse holder | Burned/flashed | 23-0011669 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801433 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | RECLOSER | 4048 | 20230109 | 2028 | 20230114 | 1158 | 1939593 | 6690 | Distribution Circuit | Environmental/External | Flood/Erosion | 126 | 26440 | 36.719 | -121.2811 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0011692 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1801454 | 0 | EPSS Ckt | N | 2023 | AB GRD
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 6753 | 20230109 | 2045 | 20230112 | 1436 | 1939606 | 3951 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 51527 | 36.5659 | -121.8876 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012148 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801917 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | RECLOSER | 2000 | 20230109 | 2343 | 20230112 | 1515 | 1939812 | 3812 | Distribution Circuit | Vegetation | Tree - fell into line | 279 | 153912 | 36.5852 | -121.8743 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0011703 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801463 | 0 | EPSS Ckt | N | 2023 | C GRD
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0422 | 182440422 | OTHER | WIRE DOWN 1 W/OF 9546 | 20230110 | 5 | 20230110 | 1214 | 1939831 | 729 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 14433 | 36.6046 | -121.9308 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011704 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | Yes | Yes | 1801464 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 67520 | 20230110 | 6 | 20230113 | 1559 | 1940557 | 5273 | Distribution Circuit | Vegetation | Tree - fell into line | 2703 | 2020347 | 36.9577 | -121.8525 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0011765 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801525 | 0 | EPSS Ckt | N | 2023 | A B
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 7259 | 20230110 | 29 | 20230111 | 1512 | 1945493 | 2323 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 104535 | 36.5752 | -121.9365 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012584 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1802260 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1106 | 182011106 | FUSE | 25149 | 20230110 | 39 | 20230110 | 940 | 1943601 | 541 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 6856 | 36.6645 | -121.6543 | Yes | Clear;32-90 F | Jumper | Burned Open | 23-0012109 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1801882 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRIP-SAVER | 5401 | 20230110 | 156 | 20230113 | 1024 | 1941448 | 4828 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 82076 | 37.0647 | -122.1232 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0011848 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | Yes | No | 1801612 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8497 | 20230110 | 156 | 20230114 | 1627 | 1949225 | 6629 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 79548 | 37.0579 | -122.1233 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0014218 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1803569 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 1995 | 20230110 | 156 | 20230114 | 1930 | 1949949 | 6814 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 13628 | 37.0556 | -122.1209 | Yes | Clear;32-90F |  |  | 23-0014429 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1803721 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 1819 | 20230110 | 156 | 20230112 | 1352 | 1949953 | 3596 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 7192 | 37.0607 | -122.1217 | Yes | Clear;32-90F |  |  | 23-0014433 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1803724 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 57499 | 20230110 | 156 | 20230115 | 1250 | 1949958 | 7854 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 7854 | 37.0725 | -122.1279 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0014435 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1803726 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 415734 | 20230110 | 156 | 20230111 | 1335 | 1939992 | 2139 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 96 | 205344 | 37.0316 | -122.1893 | Yes | Clear;32-90 F |  |  | 23-0011727 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801487 | 0 | EPSS Ckt | N | 2023 | A-B
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 10726 | 20230110 | 156 | 20230111 | 1401 | 1940044 | 2165 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 230 | 497950 | 37.061 | -122.1493 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0011735 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801495 | 0 | EPSS Ckt | N | 2023 | A-GRD
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 3927 | 20230110 | 157 | 20230110 | 800 | 1939887 | 363 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 40 | 14520 | 36.7889 | -121.6784 | Yes | Clear;32-90 F |  |  | 23-0012022 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801804 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | JUMPER | JUMPERS @ CGC 315260821038 | 20230110 | 158 | 20230114 | 1540 | 1951777 | 6582 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 342502 | 37.0666 | -122.1255 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0015242 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1804239 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 10718 | 20230110 | 158 | 20230112 | 1622 | 1939933 | 3744 | Distribution Circuit | Vegetation | Tree - branch fell on line | 100 | 354412 | 37.036 | -122.1068 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0011722 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801482 | 0 | EPSS Ckt | N | 2023 | A & C PHASE
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 9257 | 20230110 | 158 | 20230112 | 1258 | 1949943 | 3540 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 81420 | 37.0539 | -122.1168 | Yes | Clear;32-90F |  |  | 23-0011734 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1803720 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 12763 | 20230110 | 158 | 20230112 | 1314 | 1949950 | 3556 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 14224 | 37.057 | -122.1226 | Yes | Clear;32-90F |  |  | 23-0014430 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1803722 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | JUMPER | OJ E/OF 12763 | 20230110 | 158 | 20230112 | 1427 | 1949951 | 3629 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 10887 | 37.057 | -122.1225 | Yes | Clear;32-90F |  |  | 23-0014431 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1803723 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 5403 | 20230110 | 158 | 20230113 | 1534 | 1949956 | 5136 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 66768 | 37.0667 | -122.1226 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0014434 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1803725 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8359 | 20230110 | 158 | 20230112 | 1558 | 1949961 | 3720 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 66960 | 37.0781 | -122.1334 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0014436 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1803727 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8355 | 20230110 | 158 | 20230113 | 1739 | 1950534 | 5261 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 568188 | 37.0457 | -122.1099 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0014678 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1803838 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 2487 | 20230110 | 158 | 20230113 | 1659 | 1950538 | 5221 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 104420 | 37.0454 | -122.1097 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0014679 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1803839 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 5241 | 20230110 | 158 | 20230114 | 1415 | 1950853 | 6497 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 25988 | 37.0699 | -122.0843 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0014776 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1803898 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | OTHER | WIRE DOWN 2 SP LD SIDE OF CGC 315230919988 | 20230110 | 158 | 20230112 | 1317 | 1947512 | 3559 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 68260 | 37.0364 | -122.1355 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0013489 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1802993 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | OTHER | WIRE DOWN 2 SP LD SIDE OF CGC 315230919988 | 20230110 | 158 | 20230112 | 1317 | 1947512 | 3559 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 68260 | 37.0364 | -122.1355 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0013489 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1802993 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 36514 | 20230110 | 158 | 20230111 | 1700 | 1948200 | 2342 | Distribution Circuit | Company Initiated | Other Circuits | 58 | 135836 | 37.0395 | -122.1518 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0013768 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1803161 | 0 | EPSS Ckt | N | 2023 | AB
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | RECLOSER | 944178 | 20230110 | 159 | 20230111 | 1321 | 1947009 | 2122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 310 | 657820 | 37.0926 | -122.0964 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0011734 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1802906 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | SWITCH | 11027 | 20230110 | 159 | 20230113 | 1754 | 1947020 | 5275 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 67 | 353425 | 37.1021 | -122.0573 | Yes | Clear;32-90 F |  |  | 23-0011734 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1802909 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | RECLOSER | 698634 | 20230110 | 159 | 20230113 | 1547 | 1947944 | 5148 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 80 | 411840 | 37.0954 | -122.0857 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0011734 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1803081 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | RECLOSER | 5144 | 20230110 | 159 | 20230113 | 1701 | 1947947 | 5222 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 125328 | 37.0911 | -122.0774 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011734 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1803083 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | SWITCH | 10226 | 20230110 | 159 | 20230112 | 1341 | 1947950 | 3582 | Distribution Circuit | Vegetation | Tree - fell into line | 144 | 515808 | 37.0887 | -122.0882 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011734 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1803084 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 9421 | 20230110 | 159 | 20230115 | 1550 | 1949844 | 8031 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 240930 | 37.077 | -122.0862 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0014383 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1803696 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | JUMPER | OJ 1 W/OF CGC 315366321785 | 20230110 | 159 | 20230115 | 1257 | 1950269 | 7858 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 110012 | 37.0874 | -122.0903 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0014585 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1803798 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | SWITCH | 1927 | 20230110 | 159 | 20230116 | 1143 | 1952017 | 9224 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 534992 | 37.1065 | -122.0569 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011734 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1804288 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | RECLOSER | BL 2101 | 20230110 | 159 | 20230111 | 1314 | 1947013 | 2115 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 460 | 972900 | 37.0926 | -122.0964 | Yes | Clear;32-90F |  |  | 23-0011734 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1802907 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | RECLOSER | 96738 | 20230110 | 159 | 20230112 | 2033 | 1947684 | 3994 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 91862 | 37.1111 | -122.1142 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011734 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1803035 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | FUSE | 6215 | 20230110 | 159 | 20230112 | 2033 | 1948281 | 3994 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 123814 | 37.1127 | -122.1158 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0013751 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1803148 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | OCB | 2105/2 | 20230110 | 159 | 20230112 | 1647 | 1939968 | 3768 | Distribution Circuit | Vegetation | Tree - fell into line | 1888 | 1387474 | 37.0417 | -122.0255 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0011724 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801484 | 0 | EPSS Ckt | N | 2023 | ABC
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 8929 | 20230110 | 159 | 20230117 | 1701 | 1944700 | 10982 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 398734 | 37.0661 | -122.0844 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012248 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802008 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | SWITCH | 11001 | 20230110 | 159 | 20230113 | 1845 | 1944975 | 3480 | Distribution Circuit | Vegetation | Tree - fell into line | 936 | 1076838 | 37.0801 | -122.0776 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011724 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1802105 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5223 | 20230110 | 159 | 20230116 | 1640 | 1944988 | 9521 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 390361 | 37.0515 | -122.0782 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0012378 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1802109 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | JUMPER | OJ 1 N/OF CGC 315393820807 | 20230110 | 159 | 20230110 | 1333 | 1945026 | 694 | Distribution Circuit | Vegetation | Tree - fell into line | 292 | 202648 | 37.0611 | -122.0799 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011724 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802118 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | JUMPER | 9033 | 20230110 | 159 | 20230116 | 1344 | 1945703 | 9345 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 127588 | 37.0722 | -122.0754 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012665 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802317 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5243 | 20230110 | 159 | 20230113 | 1807 | 1946053 | 5288 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 142776 | 37.0713 | -122.0841 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012838 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802419 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 11087 | 20230110 | 159 | 20230112 | 933 | 1949638 | 3334 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 68 | 226712 | 37.0885 | -122.0847 | Yes | Clear;32-90F |  |  | 23-0014311 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1803640 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | JUMPER | OJS 1 POLE SSD OF 315385521774 | 20230110 | 159 | 20230116 | 1450 | 1949644 | 9411 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 103521 | 37.0873 | -122.0828 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0014312 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1803641 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5157 | 20230110 | 159 | 20230112 | 1601 | 1949998 | 3722 | Distribution Circuit | Vegetation | Tree - fell into line | 168 | 625296 | 37.0839 | -122.089 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0014459 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1803744 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | JUMPER | OJ CGC 315370221553 | 20230110 | 159 | 20230115 | 1550 | 1950552 | 8031 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 16062 | 37.0812 | -122.0873 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0014686 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1803848 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 287578 | 20230110 | 159 | 20230110 | 1511 | 1940269 | 792 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 137 | 108504 | 37.0438 | -122.0755 | Yes | Overcast-Rain;32-90 F |  |  | 23-0011749 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801510 | 0 | EPSS Ckt | N | 2023 | B TIME
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 737512 | 20230110 | 159 | 20230112 | 1900 | 1940282 | 3901 | Distribution Circuit | Vegetation | Tree - fell into line | 299 | 314819 | 37.0467 | -122.074 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011753 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1801514 | 0 | EPSS Ckt | N | 2023 | AB
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 5205 | 20230110 | 159 | 20230116 | 1626 | 1943820 | 9507 | Distribution Circuit | Vegetation | Tree - fell into line | 236 | 970680 | 37.0417 | -122.0728 | Yes | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0012053 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | Yes | No | 1801834 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 7315 | 20230110 | 159 | 20230118 | 1142 | 1944410 | 12103 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 447520 | 37.0406 | -122.0817 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012182 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801946 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | SWITCH | 130936 | 20230110 | 159 | 20230116 | 1551 | 1945245 | 9472 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 56832 | 37.0354 | -122.0867 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012478 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1802181 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 393582 | 20230110 | 202 | 20230115 | 1552 | 1940003 | 8030 | Distribution Circuit | Vegetation | Tree - fell into line | 521 | 2979064 | 37.1284 | -122.1222 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011730 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1801490 | 0 | EPSS Ckt | N | 2023 | AC GRD
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9779 | 20230110 | 202 | 20230115 | 1552 | 1948947 | 8030 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 48180 | 37.1548 | -122.0829 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0013944 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1803298 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | OCB | 2101/2 | 20230110 | 202 | 20230111 | 1346 | 1940042 | 2144 | Distribution Circuit | Vegetation | Tree - bark fell into line | 163 | 219589 | 37.0953 | -122.1437 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011734 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801494 | 0 | EPSS Ckt | N | 2023 | ABC
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 91034 | 20230110 | 202 | 20230110 | 1952 | 1940203 | 1070 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 101 | 108070 | 37.0944 | -122.1411 | Yes | Clear;32-90 F |  |  | 23-0011742 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1801503 | 0 | EPSS Ckt | N | 2023 | B GRD
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 11044 | 20230110 | 202 | 20230110 | 620 | 1939903 | 258 | Distribution Circuit | Vegetation | Tree - fell into line | 515 | 132870 | 37.0401 | -122.0297 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011726 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1801486 | 0 | EPSS Ckt | N | 2023 | AB GRD
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | SWITCH | 11008 | 20230110 | 202 | 20230110 | 1449 | 1942969 | 767 | Distribution Circuit | Vegetation | Tree - branch fell on line | 423 | 129242 | 37.0546 | -122.0742 | Yes | Overcast-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0011726 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1801715 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | SWITCH | 11025 | 20230110 | 202 | 20230110 | 1053 | 1943868 | 531 | Distribution Circuit | Company Initiated | Return Circuit Normal | 172 | 91332 | 37.0508 | -122.0677 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011726 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1801839 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | SWITCH | 1891 | 20230110 | 202 | 20230110 | 1125 | 1944604 | 563 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 213 | 119919 | 37.0479 | -122.0743 | Yes | Overcast-Rain;32-90 F |  |  | 23-0011726 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1801984 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | JUMPER | JUMPERS @ CGC# 315660323101 | 20230110 | 206 | 20230117 | 1640 | 1945894 | 10954 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 56587 | 37.1248 | -121.9894 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012783 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802376 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 18441 | 20230110 | 206 | 20230114 | 1807 | 1945911 | 6721 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 33605 | 37.1289 | -121.9772 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012795 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802383 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 6265 | 20230110 | 207 | 20230114 | 1737 | s1802002 | 6690 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 207390 | 37.1285 | -122.1208 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011730 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1802002 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | RECLOSER | 12990 | 20230110 | 208 | 20230111 | 2332 | 1940201 | 2724 | Distribution Circuit | Vegetation | Tree - fell into line | 989 | 489806 | 37.039 | -122.0214 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011759 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801519 | 0 | EPSS Ckt | N | 2023 | C GRD
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | RECLOSER | 5096 | 20230110 | 208 | 20230111 | 1216 | 1940239 | 2048 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 394 | 618022 | 37.0509 | -122.0368 | Yes | Clear;32-90 F |  |  | 23-0011762 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801522 | 0 | EPSS Ckt | N | 2023 | B GRD
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 2283 | 20230110 | 208 | 20230111 | 230 | 1940047 | 1462 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 138890 | 36.5564 | -121.9087 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011819 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1801580 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 12069 | 20230110 | 209 | 20230110 | 1004 | 1940063 | 475 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 15675 | 37.1239 | -122.1197 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0012122 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | No | No | 1801894 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 891361 | 20230110 | 210 | 20230113 | 1110 | 1946685 | 4860 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 87480 | 37.1891 | -122.1431 | Yes | Clear;32-90F |  |  | 23-0015217 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1804230 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 5020 | 20230110 | 210 | 20230110 | 1718 | 1940281 | 908 | Distribution Circuit | Vegetation | Tree - branch fell on line | 284 | 257872 | 37.1024 | -121.9847 | Yes | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0011756 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801517 | 0 | EPSS Ckt | N | 2023 | C GRD T
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5511 | 20230110 | 211 | 20230114 | 1137 | 1944880 | 6326 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 272018 | 37.1499 | -122.1363 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006011 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802068 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 5269 | 20230110 | 211 | 20230110 | 1032 | 1944120 | 501 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 4171 | 36.9894 | -122.0312 | Yes | Clear;32-90 F |  |  | 23-0012195 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801959 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 12838 | 20230110 | 212 | 20230110 | 1340 | 1940308 | 688 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 243 | 167184 | 37.1272 | -122.1236 | Yes | Clear;32-90 F |  |  | 23-0011754 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801515 | 0 | EPSS Ckt | N | 2023 | BC
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9375 | 20230110 | 212 | 20230114 | 1401 | 1945134 | 6469 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 19407 | 37.1334 | -122.1377 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012417 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1802138 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | RECLOSER | 80246 | 20230110 | 213 | 20230111 | 212 | 1940270 | 1439 | Distribution Circuit | Vegetation | Tree - fell into line | 1093 | 626057 | 36.9896 | -121.934 | Yes | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0011748 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801509 | 0 | EPSS Ckt | N | 2023 | AB GRD
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | RECLOSER | 63868 | 20230110 | 214 | 20230112 | 1738 | 1940714 | 3804 | Distribution Circuit | Vegetation | Tree - fell into line | 410 | 1548832 | 36.264 | -121.7952 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011771 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1801531 | 0 | EPSS Ckt | N | 2023 | A B
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 11851 | 20230110 | 214 | 20230111 | 854 | 1940688 | 1840 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 11040 | 36.8781 | -121.6687 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0013401 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1802936 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 802733 | 20230110 | 215 | 20230111 | 1818 | 1944697 | 2403 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 21627 | 36.9383 | -121.8636 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012245 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802005 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SOQUEL-0402 | 83300402 | OCB | 402/2 | 20230110 | 216 | 20230110 | 418 | s1835034 | 122 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1398 | 170556 | 36.9866 | -121.9505 | Yes | Overcast-Fog-Rain;32-90 F | Switch (OH) | Normal | 23-0011748 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1835034 | 0 | Non-EPSS | N | 2023 | GRD TIME
CENTRAL COAST | COAST | 83500401 | 83500401 | FUSE | 6005 | 20230110 | 217 | 20230114 | 1131 | 1940331 | 6314 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 126280 | 36.9959 | -121.9233 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012067 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1801845 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 9661 | 20230110 | 220 | 20230115 | 1712 | 1946230 | 8092 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 16184 | 36.8599 | -121.7947 | Yes | Clear;32-90 F | Conductor- Overhead | On Ground | 23-0012901 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1802470 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 12333 | 20230110 | 220 | 20230110 | 1800 | 1941027 | 940 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 940 | 36.8597 | -121.7947 | Yes | Clear;32-90 F |  |  | 23-0012917 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802484 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 6121 | 20230110 | 221 | 20230110 | 1444 | 1940502 | 743 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 109 | 80987 | 36.9835 | -121.8848 | Yes | Clear;32-90 F |  |  | 23-0012658 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1802313 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | SWITCH | 11231 | 20230110 | 223 | 20230113 | 1622 | 1940732 | 5159 | Distribution Circuit | Vegetation | Tree - fell into line | 418 | 1277738 | 36.989 | -121.8046 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011773 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1801533 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 10930 | 20230110 | 223 | 20230110 | 1541 | 1940695 | 798 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 279 | 200892 | 36.964 | -121.8086 | Yes | Clear;32-90 F |  |  | 23-0011774 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | No | No | 1801534 | 0 | EPSS Ckt | N | 2023 | ABC
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 3029 | 20230110 | 224 | 20230112 | 1627 | 1940597 | 3723 | Distribution Circuit | Equipment Failure/Involved | Overhead | 47 | 174981 | 36.9641 | -121.8172 | Yes | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0012770 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802372 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 11865 | 20230110 | 225 | 20230110 | 2153 | 1940802 | 1168 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 22559 | 37.001 | -121.7398 | Yes | Clear;32-90 F |  |  | 23-0013003 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802561 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 6137 | 20230110 | 226 | 20230112 | 1512 | 1940677 | 3646 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 59118 | 36.9729 | -121.9031 | Yes | Clear;32-90 F | Secondary | Broken | 23-0012288 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1802044 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 2667 | 20230110 | 228 | 20230115 | 1819 | 1946659 | 8151 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 48906 | 37.0258 | -121.7751 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0013087 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802642 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 3889 | 20230110 | 228 | 20230110 | 1412 | 1940738 | 704 | Distribution Circuit | 3rd Party | Other | 70 | 49280 | 36.9487 | -121.8523 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0012545 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802234 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 8193 | 20230110 | 228 | 20230110 | 816 | 1940743 | 348 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 40 | 13920 | 36.9817 | -121.8969 | Yes | Clear;32-90 F |  |  | 23-0012024 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801806 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9709 | 20230110 | 229 | 20230110 | 1318 | 1940744 | 649 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 9735 | 37.1163 | -122.1184 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0012450 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1802162 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 11943 | 20230110 | 229 | 20230110 | 1447 | 1940753 | 738 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 79 | 58302 | 37.0112 | -122.0442 | Yes | Clear;32-90 F |  |  | 23-0012604 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802275 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 5765 | 20230110 | 229 | 20230115 | 1310 | 1946396 | 7841 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 47046 | 36.8895 | -121.8299 | Yes | Clear;32-90 F | Crossarm- Wood | Broken | 23-0012957 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802524 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 4319 | 20230110 | 237 | 20230111 | 1446 | 1940931 | 2169 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 126036 | 36.8349 | -121.725 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0011970 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1801750 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DEL MONTE-2104 | 182222104 | FUSE | 5919 | 20230110 | 246 | 20230110 | 1000 | 1943339 | 434 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 13454 | 36.5295 | -121.7008 | Yes | Clear;32-90 F |  |  | 23-0012346 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802087 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER 2101 | 182492101 | FUSE | 9467 | 20230110 | 300 | 20230110 | 705 | 1941100 | 245 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 296 | 72520 | 36.8403 | -121.4147 | Yes | Clear;32-90 F |  |  | 23-0011968 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801748 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 4407 | 20230110 | 304 | 20230110 | 812 | 1941111 | 308 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 36 | 10974 | 36.9026 | -121.3627 | Yes | Clear;32-90 F |  |  | 23-0012019 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801800 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2103 | 182492103 | FUSE | 9445 | 20230110 | 307 | 20230110 | 838 | 1941120 | 331 | Distribution Circuit | Vegetation | Tree - grew into line | 67 | 22177 | 36.8339 | -121.3815 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0012030 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801812 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | FUSE | 7133 | 20230110 | 336 | 20230113 | 1901 | 1941249 | 5245 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 41960 | 36.5087 | -121.4499 | Yes | Clear;32-90 F |  |  | 23-0014737 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1803871 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO-1101 | 182191101 | OCB | 1101/2 | 20230110 | 336 | 20230112 | 1520 | 1941330 | 3584 | Distribution Circuit | Environmental/External | Flood/Erosion | 149 | 152884 | 36.0734 | -120.9364 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0011840 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1801604 | 0 | EPSS Ckt | N | 2023 | AC
CENTRAL COAST | HOLLISTER | HOLLISTER-2103 | 182492103 | RECLOSER | 4402 | 20230110 | 337 | 20230110 | 1603 | 1941272 | 746 | Distribution Circuit | Vegetation | Tree - fell into line | 884 | 125911 | 36.8564 | -121.3971 | Yes | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Together | 23-0011834 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801597 | 0 | Non-EPSS | N | 2023 | A B
CENTRAL COAST | SALINAS | SALINAS-1103 | 182011103 | JUMPER | 24669 | 20230110 | 427 | 20230110 | 1020 | 1941988 | 353 | Distribution Circuit | Equipment Failure/Involved | Overhead | 101 | 30003 | 36.6964 | -121.6584 | Yes | Clear;32-90 F | Jumper | Burned Open | 23-0011982 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1801762 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 5557 | 20230110 | 526 | 20230114 | 1756 | 1943547 | 6510 | Distribution Circuit | Equipment Failure/Involved | Overhead | 52 | 338520 | 36.9823 | -122.1442 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012118 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801890 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 5561 | 20230110 | 526 | 20230114 | 1757 | 1945766 | 6511 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 117198 | 37.0111 | -122.1224 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012697 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802336 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6559 | 20230110 | 607 | 20230110 | 928 | 1942926 | 201 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 6231 | 36.9267 | -121.7459 | Yes | Clear;32-90 F |  |  | 23-0012097 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801871 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 5188 | 20230110 | 646 | 20230110 | 1047 | 1943387 | 241 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 4579 | 37.0757 | -122.0568 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011724 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801784 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | SWITCH | 5232 | 20230110 | 646 | 20230113 | 1642 | 1943435 | 4916 | Distribution Circuit | Vegetation | Tree - fell into line | 170 | 835720 | 37.0752 | -122.054 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0011724 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801794 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 9071 | 20230110 | 646 | 20230113 | 1845 | 1943753 | 5039 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 157744 | 37.0595 | -122.0588 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0011724 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801826 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 9449 | 20230110 | 646 | 20230118 | 1740 | 1944545 | 12174 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 12174 | 37.0783 | -122.0589 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012204 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801967 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 555726 | 20230110 | 646 | 20230110 | 1119 | 1944591 | 273 | Distribution Circuit | Vegetation | Tree - fell into line | 220 | 60060 | 37.0858 | -122.0674 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011724 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801979 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | JUMPER | OIS FOR 10214 | 20230110 | 646 | 20230115 | 1713 | 1949593 | 7827 | Distribution Circuit | Vegetation | Tree - fell into line | 119 | 931413 | 37.0911 | -122.0438 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0014310 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1803639 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 7593 | 20230110 | 650 | 20230115 | 1614 | 1946548 | 7764 | Distribution Circuit | Vegetation | Tree - branch fell on line | 68 | 527952 | 37.1057 | -121.9724 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0013487 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802992 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | FUSE | 9607 | 20230110 | 658 | 20230112 | 1339 | s1803791 | 3281 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 16405 | 36.32 | -120.7121 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0014566 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1803791 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | RECLOSER | 774760 | 20230110 | 711 | 20230113 | 1949 | 1943213 | 5078 | Distribution Circuit | Vegetation | Tree - fell into line | 271 | 120833 | 36.9896 | -122.0693 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012129 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1801901 | 0 | EPSS Ckt | N | 2023 | A-B-C
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5577 | 20230110 | 714 | 20230112 | 1831 | 1943232 | 3557 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 345029 | 37.0487 | -122.0616 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012031 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1801813 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 167 | 20230110 | 718 | 20230113 | 1708 | 1943255 | 4910 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 73650 | 37.0536 | -122.044 | Yes | Overcast-Fog-Rain;32-90 F | Other | Broken- wire on ground | 23-0012062 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | Yes | Yes | 1801842 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 8799 | 20230110 | 718 | 20230112 | 2106 | 1939847 | 3708 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 200232 | 36.5607 | -121.9181 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0012016 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | Yes | No | 1801797 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5631 | 20230110 | 721 | 20230115 | 2200 | 1943219 | 8079 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 341076 | 37.049 | -122.0627 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0012110 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801883 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9749 | 20230110 | 733 | 20230112 | 1731 | 1943322 | 3478 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 24346 | 37.1489 | -122.157 | Yes | Clear;32-90F |  |  | 23-0013404 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1802938 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | FUSE | 483 | 20230110 | 733 | 20230110 | 2010 | 1945532 | 757 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 1514 | 36.3106 | -121.8892 | Yes | Clear;32-90 F |  |  | 23-0012599 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1802271 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | OTHER | 5365 | 20230110 | 807 | 20230113 | 1924 | 1943497 | 4997 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 109934 | 36.9946 | -122.0283 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012266 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1802023 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 9229 | 20230110 | 808 | 20230113 | 1846 | 1943593 | 4958 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 257816 | 37.0693 | -122.0577 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0012038 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801820 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 65444 | 20230110 | 813 | 20230110 | 1959 | s1801867 | 706 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1083 | 746618 | 37.1278 | -122.1229 | Yes | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0006011 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801867 | 0 | EPSS Ckt | N | 2023 | SGF
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 8015 | 20230110 | 813 | 20230110 | 1124 | 1943525 | 191 | Distribution Circuit | Vegetation | Tree - branch fell on line | 139 | 26549 | 37.1536 | -122.1615 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0012275 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1802033 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 9911 | 20230110 | 815 | 20230110 | 2149 | 1946492 | 814 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 10300 | 36.8548 | -121.6937 | Yes | Clear;32-90 F |  |  | 23-0013000 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802559 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | RECLOSER | 9538 | 20230110 | 819 | 20230110 | 2144 | 1943578 | 731 | Distribution Circuit | Vegetation | Tree - fell into line | 821 | 660084 | 36.5839 | -121.8492 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0012036 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801818 | 0 | EPSS Ckt | N | 2023 | B&GRD
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 9811 | 20230110 | 820 | 20230112 | 1355 | 1943613 | 3215 | Distribution Circuit | Vegetation | Tree - fell into line | 164 | 207388 | 36.8591 | -121.6955 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012280 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1802038 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 10209 | 20230110 | 821 | 20230110 | 1116 | 1943792 | 175 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1225 | 36.5226 | -121.8035 | Yes | Clear;32-90 F |  |  | 23-0012253 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1802012 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 565 | 20230110 | 824 | 20230112 | 1822 | 1950540 | 3478 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 73038 | 37.0422 | -122.1064 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0014681 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1803841 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE 2104 | 182352104 | RECLOSER | 5004 | 20230110 | 824 | 20230112 | 1458 | 1943664 | 3274 | Distribution Circuit | Equipment Failure/Involved | Overhead | 59 | 193166 | 36.7504 | -121.7422 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0012042 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1801824 | 0 | EPSS Ckt | N | 2023 | ABC- GROUND- TIME OC
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | FUSE | 23843 | 20230110 | 831 | 20230112 | 1232 | 1946422 | 3121 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 9363 | 36.7221 | -121.6785 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0012967 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802533 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1105 | 182011105 | TRANSFORMER | 412279750929 | 20230110 | 835 | 20230111 | 309 | 1943886 | 1114 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 12254 | 36.703 | -121.6352 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0012463 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802173 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 7213 | 20230110 | 839 | 20230115 | 2128 | 1943851 | 7969 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 39845 | 37.033 | -121.9822 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012680 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802325 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | OTHER | 3905 | 20230110 | 844 | 20230111 | 1356 | 1943887 | 1752 | Distribution Circuit | Vegetation | Tree - fell into line | 591 | 78184 | 36.8001 | -121.6948 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012072 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1801849 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | FUSE | 4309 | 20230110 | 850 | 20230110 | 2213 | 1943937 | 803 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 30514 | 36.8419 | -121.4723 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012099 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801873 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2103 | 182492103 | FUSE | 9445 | 20230110 | 904 | 20230110 | 925 | 1944005 | 21 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 1407 | 36.8339 | -121.3815 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0012125 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801897 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9373 | 20230110 | 912 | 20230110 | 929 | 1944067 | 17 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 578 | 37.1261 | -122.1218 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0012115 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1801886 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | FUSE | 9901 | 20230110 | 927 | 20230110 | 1730 | 1944151 | 483 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 44 | 21252 | 36.2687 | -121.394 | Yes | Clear;32-90 F |  |  | 23-0012941 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1802505 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 12025 | 20230110 | 936 | 20230111 | 910 | s1802949 | 1414 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 1414 | 36.9759 | -121.7428 | Yes | Clear;32-90 F |  |  | 23-0013420 |  | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802949 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 24893 | 20230110 | 1008 | 20230112 | 2353 | 1944389 | 3705 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 11115 | 36.8059 | -121.7229 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0012380 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1802110 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | TRANSFORMER | 411399646423 | 20230110 | 1017 | 20230112 | 957 | 1944444 | 2860 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 11440 | 36.5722 | -121.9305 | Yes | Clear;32-90 F | Secondary | Together | 23-0012691 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802331 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | OTHER | WIRE DOWN 6 SPANS LD SIDE OF CGC 315716222412 | 20230110 | 1028 | 20230126 | 1734 | 1944488 | 23466 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 117330 | 37.1065 | -121.9692 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012518 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1802215 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | OTHER | HOT WIRE DOWN @ 244 MCKEE | 20230110 | 1037 | 20230117 | 1558 | 1947623 | 10401 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 23844 | 37.0363 | -122.069 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0013524 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | Yes | Yes | 1803017 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 51053 | 20230110 | 1044 | 20230111 | 1647 | 1944584 | 1803 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 5409 | 36.6195 | -121.2226 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0012690 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1802329 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 53965 | 20230110 | 1045 | 20230111 | 1936 | 1944592 | 1971 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 53637 | 36.8153 | -121.6402 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0013062 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1802617 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 6187 | 20230110 | 1058 | 20230116 | 1715 | 1946919 | 9017 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 81153 | 37.0776 | -122.0584 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0013357 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802905 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 2145 | 20230110 | 1103 | 20230112 | 1725 | 1944688 | 3262 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 9786 | 36.5682 | -121.9289 | Yes | Clear;32-90 F | Conductor- Overhead | On Ground | 23-0012695 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802334 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO 1102 | 182191102 | RECLOSER | 83166 | 20230110 | 1116 | 20230111 | 1215 | 1944761 | 1499 | Distribution Circuit | Environmental/External | Flood/Erosion | 339 | 98693 | 36.0754 | -120.9379 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0012289 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1802045 | 0 | EPSS Ckt | N | 2023 | A & B- GROUND
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 1613 | 20230110 | 1125 | 20230110 | 1258 | 1944919 | 93 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 121 | 11253 | 37.0467 | -122.0758 | Yes | Clear;32-90 F |  |  | 23-0012424 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802144 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRIP-SAVER | 834583 | 20230110 | 1125 | 20230110 | 1328 | 1945145 | 123 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 4059 | 37.0442 | -122.0777 | Yes | Clear;32-90 F |  |  | 23-0012425 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1802145 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 2465 | 20230110 | 1132 | 20230112 | 1203 | 1944834 | 2911 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 29684 | 36.9382 | -121.8619 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012307 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802057 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 9443 | 20230110 | 1134 | 20230113 | 2104 | 1944827 | 4741 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 191259 | 37.0818 | -122.0734 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012430 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802149 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | JUMPER | FLYING BELLS @ 700 PEDRO | 20230110 | 1134 | 20230114 | 1730 | 1952592 | 6116 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 18348 | 37.09 | -122.0729 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0012430 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1804396 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 9337 | 20230110 | 1141 | 20230110 | 1330 | 1944884 | 109 | Distribution Circuit | Vegetation | Tree - branch fell on line | 46 | 5014 | 36.9399 | -121.8573 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0013376 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802914 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | OTHER | HOT WIRE DOWN @ 315 MOOSEHEAD DR | 20230110 | 1150 | 20230112 | 1535 | 1944607 | 3105 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 73155 | 36.9743 | -121.9022 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012489 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | Yes | Yes | 1802190 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 9333 | 20230110 | 1207 | 20230120 | 1450 | 1944965 | 14563 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 305823 | 36.9423 | -121.8574 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0013700 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1803116 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | SWITCH | 9893 | 20230110 | 1219 | 20230110 | 1523 | 1944478 | 184 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 5704 | 36.5798 | -121.932 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0012193 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1801958 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5233 | 20230110 | 1333 | 20230115 | 1510 | 1945310 | 7297 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 39106 | 37.0577 | -122.0763 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012516 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802213 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5235 | 20230110 | 1343 | 20230115 | 1345 | 1945448 | 7202 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 122200 | 37.0596 | -122.0793 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012570 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1802250 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DEL MONTE-2104 | 182222104 | FUSE | 20461 | 20230110 | 1347 | 20230110 | 1620 | 1945332 | 153 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1683 | 36.5384 | -121.7252 | Yes | Clear;32-90 F |  |  | 23-0012800 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802388 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6559 | 20230110 | 1516 | 20230110 | 1848 | 1945691 | 212 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 6572 | 36.9267 | -121.7459 | Yes | Clear;32-90 F |  |  | 23-0012925 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1802491 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 10189 | 20230110 | 1528 | 20230110 | 1737 | 1945741 | 129 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 516 | 36.5056 | -121.9365 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012684 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | Yes | No | 1802327 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 6895 | 20230110 | 1600 | 20230113 | 1916 | 1947715 | 4516 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 9032 | 36.8382 | -121.7668 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0013552 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1803031 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 8255 | 20230110 | 1603 | 20230110 | 2048 | 1945838 | 285 | Distribution Circuit | Vegetation | Tree - grew into line | 15 | 4275 | 36.577 | -121.9703 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0012750 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1802362 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | TRANSFORMER | 316367514971 | 20230110 | 1608 | 20230113 | 1042 | 1945876 | 3994 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 19970 | 36.9044 | -121.7433 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0012981 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802543 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 9429 | 20230110 | 1624 | 20230114 | 1519 | 1945896 | 5695 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 153765 | 37.0743 | -122.0826 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012810 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802397 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5239 | 20230110 | 1745 | 20230112 | 1805 | 1946198 | 2900 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 118900 | 37.0682 | -122.0827 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012890 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802461 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 10021 | 20230110 | 1832 | 20230111 | 253 | 1946261 | 501 | Distribution Circuit | Environmental/External | Flood/Erosion | 7 | 3507 | 36.8984 | -121.8211 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0012912 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1802480 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8137 | 20230110 | 1835 | 20230110 | 2318 | 1946299 | 283 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 3396 | 37.0581 | -121.9802 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0013079 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802634 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | JUMPER | JUMPERS @ CGC # 100000077803 | 20230110 | 1835 | 20230116 | 957 | 1946722 | 8122 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 16244 | 37.0615 | -121.9802 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0013191 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802746 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 1721 | 20230110 | 1848 | 20230110 | 1857 | 1946336 | 9 | Distribution Circuit | Company Initiated | Return Circuit Normal | 39 | 351 | 37.056 | -121.9972 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0011036 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1802513 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 8419 | 20230110 | 2033 | 20230111 | 1617 | 1948457 | 1184 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 39072 | 36.5693 | -121.7917 | Yes | Clear;32-90 F |  |  | 23-0013788 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1803184 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 2913 | 20230110 | 2037 | 20230111 | 1210 | 1946498 | 933 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 4665 | 37.1752 | -122.1446 | Yes | Clear;32-90 F |  |  | 23-0013696 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803113 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | FUSE | 6713 | 20230110 | 2043 | 20230110 | 2315 | 1946509 | 152 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 95 | 14440 | 36.4702 | -121.7242 | Yes | Clear;32-90F |  |  | 23-0013117 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802672 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | FUSE | 51017 | 20230110 | 2308 | 20230111 | 1024 | 1946719 | 676 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 19604 | 36.8492 | -121.4724 | Yes | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0013500 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1803001 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS 2102 | 182082102 | OCB | 2102/2 | 20230110 | 2328 | 20230112 | 1550 | 1946744 | 308 | Distribution Circuit | Equipment Failure/Involved | Overhead | 231 | 57412 | 36.2938 | -121.1999 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0013213 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1802768 | 0 | EPSS Ckt | N | 2023 | TIME OC
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | OCB | 1102/2 | 20230111 | 415 | 20230111 | 949 | 1946954 | 334 | Distribution Circuit | Vegetation | Tree - branch fell on line | 463 | 149510 | 37.1312 | -122.1723 | No | Clear;32-90F | Conductor- Overhead | Broken | 23-0013345 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | No | No | 1802897 | 0 | EPSS Ckt | N | 2023 | ABC
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | SWITCH | 3669 | 20230111 | 415 | 20230112 | 1344 | 1947362 | 2009 | Distribution Circuit | Vegetation | Tree - fell into line | 389 | 781501 | 37.1583 | -122.1622 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0013345 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1802962 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5445 | 20230111 | 743 | 20230114 | 1800 | 1947677 | 4937 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 44433 | 37.1301 | -122.1341 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0016330 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1805088 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | TRANSFORMER | 411464845868 | 20230111 | 814 | 20230112 | 14 | 1947135 | 960 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 2880 | 36.5576 | -121.9081 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0013735 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803136 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | TRANSFORMER | 411437845930 | 20230111 | 908 | 20230111 | 1800 | 1947283 | 532 | Transformer only | Vegetation | Tree - fell into line | 22 | 11704 | 36.559 | -121.9173 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0013711 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803123 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | TRANSFORMER | 316413014220 | 20230111 | 915 | 20230115 | 1145 | 1947299 | 5910 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 29550 | 36.8841 | -121.7276 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0014701 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803857 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | JUMPER | OJ @ CGC 315162020590 | 20230111 | 1020 | 20230111 | 1355 | 1947494 | 215 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 4300 | 37.0537 | -122.159 | No | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0013483 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802990 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | JUMPER | OJ @ CGC 315162020590 | 20230111 | 1020 | 20230111 | 1355 | 1947494 | 215 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 4300 | 37.0537 | -122.159 | No | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0013483 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802990 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRIP-SAVER | 6219 | 20230111 | 1030 | 20230111 | 1323 | 1947523 | 173 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 3806 | 37.1841 | -122.1409 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0013493 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1802995 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | FUSE | 12265 | 20230111 | 1050 | 20230111 | 1243 | 1947605 | 113 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 24 | 2709 | 36.9588 | -121.9805 | No | Clear;32-90 F |  |  | 23-0013626 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803080 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | LOS COCHES 1102 | 182151102 | FUSE | 8505 | 20230111 | 1051 | 20230113 | 1151 | 1947685 | 2940 | Distribution Circuit | Environmental/External | Flood/Erosion | 16 | 32792 | 36.3756 | -121.2578 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0014731 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1803869 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 9435 | 20230111 | 1152 | 20230111 | 1215 | 1947819 | 23 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 322 | 37.0741 | -122.0804 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0013624 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1803077 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | TRANSFORMER | 411638047201 | 20230111 | 1218 | 20230111 | 2229 | 1947885 | 611 | Transformer only | Equipment Failure/Involved | Overhead | 60 | 36660 | 36.5957 | -121.8505 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0013767 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803160 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | FORT ORD 2107 | 182402107 | FUSE | 6325 | 20230111 | 1249 | 20230111 | 2030 | 1947999 | 461 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 8298 | 36.6796 | -121.7855 | No | Clear;32-90 F | Cutout- fuse holder | Failed/Faulted | 23-0013954 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803308 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 5131 | 20230111 | 1342 | 20230112 | 1840 | 1948160 | 1738 | Distribution Circuit | Vegetation | Tree - branch fell on line | 112 | 176452 | 37.0902 | -122.0899 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0013770 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1803165 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | RECLOSER | 5018 | 20230111 | 1348 | 20230111 | 1758 | 1948173 | 250 | Distribution Circuit | Equipment Failure/Involved | Overhead | 508 | 75260 | 36.7629 | -121.7347 | No | Clear;32-90 F | Jumper | Burned Open | 23-0013720 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1803130 | 0 | Non-EPSS | N | 2023 | BC
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315410120143 | 20230111 | 1352 | 20230113 | 1838 | 1948185 | 3166 | Transformer only | Vegetation | Tree - branch fell on line | 15 | 47490 | 37.0424 | -122.0737 | No | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0015176 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1804213 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | TRANSFORMER | MTR#1010349731 | 20230111 | 1352 | 20230111 | 1535 | 1948188 | 103 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 1854 | 36.9582 | -121.9802 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0013830 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803210 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 631879 | 20230111 | 1352 | 20230115 | 1158 | 1948189 | 5646 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 101628 | 36.9599 | -121.8912 | No | Clear;32-90 F | Cutout- fuse holder | Failed/Faulted | 23-0013900 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803262 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 7371 | 20230111 | 1521 | 20230111 | 1900 | 1948460 | 219 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1095 | 37.0585 | -122.142 | No | Clear;32-90 F |  |  | 23-0013951 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1803305 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 6809 | 20230111 | 1525 | 20230112 | 956 | 1948468 | 1111 | Distribution Circuit | Vegetation | Tree - grew into line | 181 | 21667 | 36.573 | -121.9271 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0013777 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1803185 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 6355 | 20230111 | 1616 | 20230112 | 1510 | 1950379 | 1374 | Distribution Circuit | Vegetation | Tree - branch fell on line | 44 | 60456 | 37.0506 | -122.0593 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0014644 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1803817 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 6355 | 20230111 | 1616 | 20230112 | 1510 | 1950379 | 1374 | Distribution Circuit | Vegetation | Tree - branch fell on line | 44 | 60456 | 37.0506 | -122.0593 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0014644 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1803817 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | TRANSFORMER | 315212021599 | 20230111 | 1624 | 20230111 | 1850 | 1948627 | 146 | Transformer only | Vegetation | Tree - branch fell on line | 4 | 584 | 37.0815 | -122.1426 | No | Clear;32-90 F | Conductor- Overhead | Burned/flashed | 23-0013970 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803321 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 5409 | 20230111 | 1710 | 20230112 | 1413 | 1948796 | 1263 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 8841 | 37.0657 | -122.152 | No | Overcast-Heavy Rain;32-90 F |  |  | 23-0013901 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1803263 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 9551 | 20230111 | 1710 | 20230112 | 944 | 1948801 | 994 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1988 | 37.0603 | -122.159 | No | Clear;32-90 F | Lightning Arrestor | Failed/Faulted | 23-0013905 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803267 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 6465 | 20230111 | 1711 | 20230115 | 1828 | 1948757 | 5837 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 11674 | 37.0541 | -122.1697 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0013983 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1803330 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5587 | 20230111 | 1726 | 20230114 | 1620 | 1948795 | 4254 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 34032 | 37.0672 | -122.0586 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0013902 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1803264 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5587 | 20230111 | 1726 | 20230114 | 1620 | 1948795 | 4254 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 34032 | 37.0672 | -122.0586 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0013902 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1803264 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | TRANSFORMER | 316180016000 | 20230111 | 1728 | 20230115 | 1405 | 1948799 | 5557 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 5557 | 36.9321 | -121.8074 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0013935 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803289 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 7681 | 20230111 | 1750 | 20230111 | 1807 | 1948890 | 17 | Distribution Circuit | Company Initiated | Improper Construction | 10 | 170 | 36.5832 | -121.865 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 23-0013928 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1803285 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | TRANSFORMER | 315810518717 | 20230111 | 1810 | 20230119 | 850 | 1948887 | 10960 | Transformer only | Vegetation | Tree - fell into line | 2 | 21920 | 37.005 | -121.9355 | No | Clear;32-90 F | Transformer | Broken | 23-0013955 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803309 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315673222766 | 20230111 | 1824 | 20230113 | 611 | 1948906 | 2147 | Transformer only | Vegetation | Tree - fell into line | 7 | 15029 | 37.1157 | -121.9851 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0014811 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803926 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | FUSE | 5023 | 20230111 | 1959 | 20230112 | 1056 | 1949019 | 897 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 41262 | 37.0134 | -121.9635 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0013984 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1803335 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-1101 | 182221101 | FUSE | 488145 | 20230111 | 2133 | 20230111 | 2217 | 1949120 | 44 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 1452 | 36.6192 | -121.8336 | No | Clear;32-90F |  |  | 23-0014095 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1803441 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316283817270 | 20230111 | 2214 | 20230114 | 1540 | 1949139 | 3926 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 3926 | 36.9673 | -121.7729 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0014289 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803628 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-1101 | 182221101 | TRANSFORMER | 411688648071 | 20230112 | 11 | 20230112 | 342 | 1949212 | 211 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 2110 | 36.6197 | -121.8337 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0014216 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803567 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 1021 | 20230112 | 143 | 20230112 | 826 | 1949232 | 403 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 4836 | 36.9951 | -121.8512 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0014277 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803617 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 4393 | 20230112 | 317 | 20230112 | 1007 | 1949293 | 410 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 62 | 25433 | 37.1199 | -122.1209 | No | Clear;32-90F |  |  | 23-0014347 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803663 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9791 | 20230112 | 641 | 20230112 | 902 | 1949397 | 141 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 7755 | 37.1851 | -122.1414 | No | Clear;32-90F | Secondary | Broken- wire on ground | 23-0014330 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803654 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | FUSE | 2155 | 20230112 | 749 | 20230113 | 400 | 1949476 | 870 | Distribution Circuit | Equipment Failure/Involved | Underground | 249 | 51523 | 36.7018 | -121.8009 | No | Clear;32-90F | Transformer (UG) | Failed/Faulted | 23-0014525 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803773 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | TRANSFORMER | 411399546598 | 20230112 | 826 | 20230112 | 1109 | 1949562 | 163 | Transformer only | Unknown Cause | Patrol - found nothing | 6 | 978 | 36.5771 | -121.9306 | No | Clear;32-90 F |  |  | 23-0014355 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1803670 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CAMPHORA 1101 | 182071101 | FUSE | 7857 | 20230112 | 940 | 20230113 | 1412 | 1950012 | 1712 | Distribution Circuit | Environmental/External | Flood/Erosion | 9 | 15408 | 36.4343 | -121.4192 | No | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0014466 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1803749 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | TRANSFORMER | T1178 | 20230112 | 1015 | 20230112 | 1210 | 1949777 | 115 | Transformer only | 3rd Party | Dig in- 3rd party | 29 | 3335 | 36.9645 | -121.9791 | No | Clear;32-90F | Secondary | Broken | 23-0014521 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803771 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315363221283 | 20230112 | 1045 | 20230117 | 1640 | 1949847 | 7555 | Transformer only | Vegetation | Tree - bark fell into line | 2 | 15110 | 37.0743 | -122.0901 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0014384 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1803697 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | SWITCH | 3747 | 20230112 | 1052 | 20230115 | 1433 | 1949857 | 4341 | Distribution Circuit | Environmental/External | Flood/Erosion | 155 | 133178 | 36.5545 | -121.5456 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0014389 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1803700 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2101 | 182492101 | JUMPER | OJ @ DDE @ CGC 412926355304 | 20230112 | 1053 | 20230112 | 1518 | 1949870 | 265 | Distribution Circuit | Environmental/External | Flood/Erosion | 28 | 7420 | 36.8277 | -121.4185 | No | Clear;32-90F | Pole-Wood | Broken | 23-0014397 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1803703 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | TRANSFORMER | 315781918678 | 20230112 | 1053 | 20230114 | 1147 | 1949866 | 2934 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 2934 | 37.0039 | -121.9456 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0014589 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803799 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 2889 | 20230112 | 1057 | 20230112 | 1450 | 1949878 | 233 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 233 | 36.5876 | -121.8661 | No | Clear;32-90F | Secondary | Normal | 23-0014400 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1803706 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | BORONDA-1101 | 182461101 | TRANSFORMER | 412148451068 | 20230112 | 1120 | 20230112 | 2009 | 1949945 | 529 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 529 | 36.706 | -121.6801 | No | Clear;32-90F | Cutout- fuse holder | Broken | 23-0014522 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803772 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316372817541 | 20230112 | 1227 | 20230112 | 1518 | 1950100 | 171 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 171 | 36.9753 | -121.7431 | No | Clear;32-90 F |  |  | 23-0014575 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1803793 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | FUSE | 483 | 20230112 | 1229 | 20230112 | 1413 | 1950104 | 104 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 208 | 36.3106 | -121.8892 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0014505 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1803764 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | TRANSFORMER | 411367343677 | 20230112 | 1353 | 20230112 | 1432 | 1950033 | 39 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 312 | 36.4962 | -121.9378 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 23-0014626 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803808 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | TRANSFORMER | 411768444998 | 20230112 | 1403 | 20230113 | 1341 | 1950330 | 1418 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2836 | 36.5365 | -121.8032 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0014664 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803829 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GONZALES 1101 | 182131101 | TRANSFORMER | T2826 | 20230112 | 1427 | 20230113 | 1550 | 1950366 | 1518 | Distribution Circuit | Equipment Failure/Involved | Underground | 20 | 30360 | 36.5237 | -121.4443 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0014713 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803862 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411798951374 | 20230112 | 1454 | 20230113 | 1249 | 1950034 | 1315 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1315 | 36.7116 | -121.7988 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0014639 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803812 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | TRANSFORMER | T0535 | 20230112 | 1504 | 20230115 | 1307 | 1950429 | 4203 | Transformer only | Equipment Failure/Involved | Underground | 6 | 25218 | 36.5453 | -121.9057 | No | Clear;32-90F | Secondary | Deteriorated | 23-0016618 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805359 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 39126 | 20230112 | 1631 | 20230112 | 1822 | 1950613 | 111 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 132 | 14652 | 37.0778 | -122.1322 | No | Clear;32-90 F |  |  | 23-0014760 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1803885 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 5133 | 20230112 | 1635 | 20230114 | 730 | 1950623 | 2335 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 16345 | 37.0921 | -122.0917 | No | Clear;32-90F | Secondary | Normal | 23-0015879 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1804718 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | JUMPER | UN-NUMBERED SBCO 1 SPAN W OF 4355 | 20230112 | 1832 | 20230118 | 101 | 1952029 | 7589 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 83479 | 37.0601 | -122.0642 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0015379 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1804291 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 6979 | 20230112 | 1834 | 20230113 | 841 | 1950829 | 847 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 32 | 27104 | 36.6001 | -121.9046 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0014769 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1803891 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315380621215 | 20230112 | 1925 | 20230113 | 900 | 1950889 | 815 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 1630 | 37.0719 | -122.0842 | No | Clear;32-90F |  |  | 23-0015118 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1804186 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9309 | 20230112 | 2211 | 20230115 | 1642 | 1951061 | 3991 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 474521 | 37.1187 | -122.1154 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016184 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1804958 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | RECLOSER | 66936 | 20230113 | 149 | 20230113 | 1943 | 1951225 | 1074 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 51262 | 36.3067 | -121.3117 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015037 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1804147 | 0 | EPSS Ckt | N | 2023 | A
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 6973 | 20230113 | 154 | 20230113 | 2054 | 1951227 | 1131 | Distribution Circuit | Equipment Failure/Involved | Underground | 36 | 16236 | 36.5816 | -121.9216 | No | Clear;32-90F | Transformer (UG) | Contaminated | 23-0015045 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804155 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | SWITCH | 8203 | 20230113 | 252 | 20230114 | 1135 | 1954274 | 1941 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 125464 | 37.0268 | -121.963 | No | Clear;32-90 F | Conductor- Overhead | On Ground | 23-0015041 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | Yes | No | 1804941 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | FUSE | 2675 | 20230113 | 623 | 20230113 | 1521 | 1951295 | 187 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 187 | 36.2727 | -121.8141 | No | Clear;32-90F |  |  | 23-0015160 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1804205 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | JUMPER | OJ AT CGC 315162020590 | 20230113 | 812 | 20230115 | 1848 | 1951927 | 3516 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 70498 | 37.0537 | -122.159 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015340 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | Yes | No | 1804275 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 45255 | 20230113 | 905 | 20230113 | 1532 | 1951478 | 387 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 15093 | 36.5862 | -121.9149 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015199 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1804225 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | JUMPER | WIRE DOWN 1 SPAN LD SIDE OF CGC 411387846285 | 20230113 | 916 | 20230113 | 1840 | 1952035 | 564 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1170 | 36.5688 | -121.9341 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015385 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1804294 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | TRANSFORMER | 315426221720 | 20230113 | 924 | 20230113 | 1841 | 1951504 | 557 | Transformer only | Vegetation | Tree - branch fell on line | 8 | 4456 | 37.0859 | -122.0691 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0015534 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1804381 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | TRANSFORMER | 315803819039 | 20230113 | 957 | 20230116 | 1628 | 1951612 | 4711 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 5439 | 37.0132 | -121.9365 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0015219 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804231 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 4645 | 20230113 | 1034 | 20230113 | 1419 | 1951650 | 225 | Distribution Circuit | Equipment Failure/Involved | Underground | 40 | 2140 | 36.5668 | -121.7548 | No | Clear;32-90F | Secondary | Broken | 23-0014414 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1804216 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 316162719738 | 20230113 | 1157 | 20230117 | 1704 | 1951848 | 6067 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 2 | 12134 | 37.0346 | -121.8143 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0015462 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804335 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 10457 | 20230113 | 1200 | 20230118 | 1536 | 1951886 | 7416 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 118656 | 37.1086 | -122.0459 | No | Clear;32-90F | Crossarm- Wood | Broken | 23-0015309 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1804266 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 5219 | 20230113 | 1403 | 20230117 | 1417 | 1951533 | 5774 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 73370 | 37.0371 | -122.066 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken | 23-0015397 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1804301 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 291 | 20230113 | 1551 | 20230118 | 1510 | 1952240 | 7159 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 28636 | 37.1 | -122.0859 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015461 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1804334 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 8021 | 20230113 | 1557 | 20230113 | 1809 | 1952406 | 121 | Distribution Circuit | Company Initiated | Return Circuit Normal | 13 | 1573 | 37.1635 | -122.1621 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0015201 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1804383 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 764889 | 20230113 | 1612 | 20230114 | 1234 | 1952291 | 1222 | Distribution Circuit | Vegetation | Tree - fell into line | 343 | 419146 | 37.0019 | -122.0376 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015500 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1804355 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 10225 | 20230113 | 1654 | 20230113 | 2157 | 1952397 | 303 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 2121 | 37.0995 | -122.0494 | No | Clear;32-90 F |  |  | 23-0016252 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805011 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 9247 | 20230113 | 1657 | 20230114 | 1032 | 1952351 | 1055 | Distribution Circuit | Vegetation | Tree - bark fell into line | 36 | 37980 | 37.0898 | -122.0447 | No | Clear;32-90F | Cutout- fuse holder | Normal | 23-0016092 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804891 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 1699 | 20230113 | 1708 | 20230114 | 1514 | 1952371 | 1326 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 11934 | 36.9707 | -121.797 | No | Clear;32-90F | Connector or Splice (OH) | Burned Open | 23-0015509 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1804362 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5617 | 20230113 | 1713 | 20230118 | 1700 | 1952380 | 7187 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 25803 | 37.0986 | -122.0532 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016548 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805300 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | TRANSFORMER | 315678217024 | 20230113 | 1718 | 20230113 | 1916 | 1952389 | 118 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 2124 | 36.9582 | -121.9802 | No | Clear;32-90 F | Transformer | Broken | 23-0015504 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1804359 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 595388 | 20230113 | 1757 | 20230113 | 1911 | 1952462 | 74 | Distribution Circuit | Vegetation | Tree - fell into line | 179 | 13246 | 37.1517 | -122.136 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0015520 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1804368 | 0 | EPSS Ckt | N | 2023 | AC
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | TRANSFORMER | 315369021676 | 20230113 | 2111 | 20230116 | 653 | 1953764 | 3462 | Transformer only | Vegetation | Tree - branch fell on line | 13 | 45006 | 37.0845 | -122.0885 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0016273 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805032 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRANSFORMER | 315310523569 | 20230113 | 2127 | 20230114 | 1751 | 1952603 | 1224 | Transformer only | Vegetation | Tree - fell into line | 4 | 4896 | 37.1366 | -122.1078 | No | Clear;32-90 F | Transformer | Broken | 23-0015983 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804808 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | TRANSFORMER | 315373521681 | 20230114 | 319 | 20230116 | 1935 | 1954634 | 3856 | Transformer only | Unknown Cause | Patrol - found nothing | 13 | 50128 | 37.0846 | -122.088 | Yes | Clear;32-90 F |  |  | 23-0016274 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805033 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 6217 | 20230114 | 342 | 20230114 | 913 | 1952759 | 331 | Distribution Circuit | Vegetation | Tree - branch fell on line | 261 | 86391 | 37.0781 | -122.0793 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0015969 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804796 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 10726 | 20230114 | 432 | 20230114 | 447 | 1952783 | 15 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 233 | 3495 | 37.061 | -122.1493 | Yes | Clear;32-90F |  |  | 23-0015831 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1804676 | 0 | EPSS Ckt | N | 2023 | AB
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 5078 | 20230114 | 433 | 20230114 | 444 | 1952777 | 11 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 300 | 3300 | 37.0314 | -122.1879 | Yes | Clear;32-90F |  |  | 23-0015831 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1804675 | 0 | EPSS Ckt | N | 2023 | BC
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 11835 | 20230114 | 444 | 20230117 | 1903 | 1952785 | 5179 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 134654 | 36.9833 | -121.8841 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015850 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1804693 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9181 | 20230114 | 553 | 20230115 | 1450 | 1953378 | 1977 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 27678 | 37.2288 | -122.148 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016316 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805072 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | SWITCH | 8725 | 20230114 | 620 | 20230115 | 1821 | 1953249 | 2161 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 210733 | 37.0757 | -122.1431 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016006 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1804868 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 10621 | 20230114 | 638 | 20230114 | 955 | 1952830 | 197 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 985 | 37.0651 | -122.0174 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0015985 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804809 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | RECLOSER | 3080 | 20230114 | 713 | 20230115 | 2119 | 1952966 | 2286 | Distribution Circuit | Vegetation | Tree - fell into line | 383 | 310288 | 36.789 | -121.6749 | Yes | Clear;32-90F | Conductor- Overhead | On Ground | 23-0015870 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1804709 | 0 | EPSS Ckt | N | 2023 | AB
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 8021 | 20230114 | 715 | 20230115 | 1553 | 1952997 | 1958 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 12852 | 37.1635 | -122.1621 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0016081 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1804883 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 737512 | 20230114 | 715 | 20230114 | 1415 | 1952989 | 420 | Distribution Circuit | Vegetation | Tree - branch fell on line | 449 | 46452 | 37.0467 | -122.074 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015888 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1804723 | 0 | EPSS Ckt | N | 2023 | B- GRD
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | JUMPER | TREE THRU LINES | 20230114 | 726 | 20230114 | 1537 | 1953003 | 491 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 982 | 37.1402 | -122.0965 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016079 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1804881 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 5066 | 20230114 | 736 | 20230114 | 1519 | 1953044 | 463 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 12501 | 37.1706 | -122.1655 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0015877 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1804716 | 0 | EPSS Ckt | N | 2023 | AB
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 8183 | 20230114 | 745 | 20230114 | 1834 | 1953501 | 649 | Distribution Circuit | Vegetation | Tree - fell into line | 115 | 74635 | 36.9646 | -121.8903 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0015952 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | Yes | 1804782 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 5955 | 20230114 | 750 | 20230115 | 1617 | 1953122 | 1947 | Distribution Circuit | Vegetation | Tree - fell into line | 164 | 270623 | 37.0022 | -121.942 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015963 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1804790 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 7765 | 20230114 | 750 | 20230117 | 1552 | 1956111 | 4802 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 9604 | 37.0278 | -121.9313 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0016729 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1805440 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 12665 | 20230114 | 750 | 20230115 | 1400 | 1953115 | 1810 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 50680 | 36.8621 | -121.6879 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0015909 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | No | No | 1804741 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | RECLOSER | BL 1101 | 20230114 | 756 | 20230114 | 1321 | 1952906 | 321 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 317 | 56662 | 37.0926 | -122.0966 | Yes | Clear;32-90F |  |  | 23-0015890 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804725 | 0 | EPSS Ckt | N | 2023 | C GRD
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | RECLOSER | 885736 | 20230114 | 804 | 20230115 | 1215 | 1953166 | 1691 | Distribution Circuit | Vegetation | Tree - fell into line | 438 | 740658 | 36.9937 | -121.9776 | Yes | Clear;32-90F | Conductor- Overhead | On Ground | 23-0015897 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1804731 | 0 | EPSS Ckt | N | 2023 | C GRD TIME
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 6741 | 20230114 | 817 | 20230115 | 1313 | 1954555 | 1736 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 12152 | 36.5716 | -121.8844 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0016258 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805019 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | JOLON 1102 | 182981102 | FUSE | 9193 | 20230114 | 817 | 20230114 | 1426 | 1953216 | 369 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 738 | 35.9664 | -121.1324 | Yes | Clear;32-90 F |  |  | 23-0016142 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804928 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | OCB | 2202/2 | 20230114 | 830 | 20230114 | 1646 | 1953323 | 496 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6127 | 1068877 | 36.5786 | -121.9085 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0015917 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | No | No | 1804751 | 0 | EPSS Ckt | N | 2023 | A- B- C & GRD
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | OTHER | WIRE DOWN | 20230114 | 835 | 20230115 | 1200 | 1953646 | 1645 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 116460 | 37.0819 | -122.0829 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015994 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1804815 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON SUB | 18229 | OCB | 1101/2 | 20230114 | 836 | 20230115 | 6 | 1953363 | 930 | Distribution Circuit | Vegetation | Tree - fell into line | 505 | 136405 | 36.5569 | -121.8976 | Yes | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0015922 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1804756 | 0 | Non-EPSS | N | 2023 | ABC
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | JUMPER | OJ 315285520086 | 20230114 | 858 | 20230115 | 1330 | 1954046 | 1712 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 13696 | 37.0402 | -122.1162 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016085 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1804886 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 5945 | 20230114 | 859 | 20230114 | 1300 | 1953517 | 241 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 335 | 80735 | 36.7919 | -121.7232 | Yes | Clear;32-90 F |  |  | 23-0016196 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1804969 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 12613 | 20230114 | 900 | 20230116 | 1715 | 1953507 | 3375 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 13500 | 37.0971 | -121.9927 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016175 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1804952 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | OTHER | WIRE DOWN 1 S/OF 5455 | 20230114 | 902 | 20230114 | 1944 | 1953536 | 642 | Distribution Circuit | Vegetation | Tree - fell into line | 1094 | 286483 | 36.9773 | -121.9438 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016010 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | Yes | Yes | 1804827 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 5143 | 20230114 | 906 | 20230115 | 1835 | 1953560 | 2009 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 54243 | 37.0994 | -122.0868 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016107 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1804902 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SOQUEL SUB | 8330 | OCB | 402/2 | 20230114 | 916 | 20230114 | 1218 | 1953949 | 182 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1398 | 254436 | 36.9866 | -121.9505 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0016132 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804922 | 0 | Non-EPSS | N | 2023 | GRD
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 6217 | 20230114 | 934 | 20230114 | 1414 | 1953923 | 280 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 85 | 23776 | 37.0781 | -122.0793 | Yes | Clear;32-90 F |  |  | 23-0016249 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805009 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 20079 | 20230114 | 934 | 20230114 | 1359 | 1953679 | 265 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 795 | 36.8113 | -121.6738 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0016056 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804865 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5501 | 20230114 | 939 | 20230115 | 1424 | 1953707 | 1725 | Distribution Circuit | Vegetation | Tree - fell into line | 142 | 140162 | 37.1431 | -122.1318 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016127 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1804916 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 10714 | 20230114 | 939 | 20230114 | 1337 | 1953696 | 238 | Distribution Circuit | Vegetation | Tree - fell into line | 3105 | 359571 | 36.9779 | -121.8666 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0016011 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1804828 | 0 | EPSS Ckt | N | 2023 | A-B
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 8595 | 20230114 | 939 | 20230114 | 1356 | 1954050 | 257 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 11308 | 36.9661 | -121.8691 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0016088 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804888 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6543 | 20230114 | 939 | 20230114 | 1630 | s1804921 | 411 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 26 | 10686 | 36.9267 | -121.8459 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0016109 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1804921 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 361 | 20230114 | 955 | 20230115 | 1057 | 1953758 | 1502 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 7510 | 37.0455 | -122.1085 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016565 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN |  | 0 | No | Yes | No | 1805316 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | RECLOSER | 2000 | 20230114 | 959 | 20230115 | 257 | 1953257 | 1018 | Distribution Circuit | Vegetation | Tree - fell into line | 310 | 150826 | 36.5852 | -121.8743 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0016032 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1804847 | 0 | EPSS Ckt | N | 2023 | B & G
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 974520 | 20230114 | 1012 | 20230114 | 1137 | 1953736 | 85 | Distribution Circuit | Vegetation | Tree - fell into line | 222 | 18870 | 36.9908 | -121.8063 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016045 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1804856 | 0 | EPSS Ckt | N | 2023 | A&GRD
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | SWITCH | 216684 | 20230114 | 1012 | 20230115 | 1712 | 1954053 | 1860 | Distribution Circuit | Vegetation | Tree - fell into line | 106 | 197160 | 37.0197 | -121.8186 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0016045 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1804889 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 1491 | 20230114 | 1015 | 20230114 | 2210 | 1953903 | 715 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 15088 | 36.5057 | -121.9352 | Yes | Clear;32-90 F | Conductor- Overhead | On Ground | 23-0016178 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1804955 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | JUMPER | OJ 3 W/OF 905574 | 20230114 | 1017 | 20230114 | 1055 | 1953905 | 38 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 1368 | 36.8838 | -121.7303 | Yes | Clear;32-90F | Connector or Splice (OH) | Broken | 23-0016042 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1804855 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 9443 | 20230114 | 1030 | 20230115 | 1150 | 1953971 | 1520 | Distribution Circuit | Vegetation | Tree - branch fell on line | 96 | 9770 | 37.0818 | -122.0734 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016120 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1804910 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2101 | 182492101 | RECLOSER | 93404 | 20230114 | 1034 | 20230114 | 1601 | 1953992 | 327 | Distribution Circuit | Vegetation | Tree - bark fell into line | 800 | 43332 | 36.8573 | -121.4176 | Yes | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016096 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1804893 | 0 | EPSS Ckt | N | 2023 | B GRD
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | TRANSFORMER | 316209116033 | 20230114 | 1040 | 20230115 | 1346 | 1954020 | 1626 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 11382 | 36.9331 | -121.7982 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0016139 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804926 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 1827 | 20230114 | 1105 | 20230115 | 1503 | 1954076 | 1678 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 20136 | 37.2134 | -122.1558 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016599 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1805345 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2103 | 182492103 | FUSE | 9445 | 20230114 | 1123 | 20230114 | 1204 | 1954134 | 41 | Distribution Circuit | Equipment Failure/Involved | Overhead | 67 | 2747 | 36.8339 | -121.3815 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0016155 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN |  | 0 | No | No | No | 1804938 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | UN-NUMMBERED FUSE LD SIDE OF CGC 315545520871 | 20230114 | 1304 | 20230117 | 1345 | 1954846 | 4361 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 46098 | 37.0634 | -122.0267 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016335 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805093 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 9607 | 20230114 | 1308 | 20230114 | 1602 | 1954387 | 174 | Distribution Circuit | Vegetation | Tree - grew into line | 9 | 1566 | 36.5607 | -121.9164 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0016203 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1804971 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 12025 | 20230114 | 1335 | 20230114 | 1408 | 1954405 | 33 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 33 | 36.9759 | -121.7428 | Yes | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0016211 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1804978 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | FUSE | 688471 | 20230114 | 1337 | 20230116 | 1204 | 1954456 | 2787 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 20519 | 37.1101 | -122.1102 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016271 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805030 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | TRANSFORMER | 315351522797 | 20230114 | 1353 | 20230121 | 1601 | 1954479 | 10208 | Transformer only | Vegetation | Tree - fell into line | 1 | 10208 | 37.1155 | -122.0949 | Yes | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0016322 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805078 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9775 | 20230114 | 1603 | 20230114 | 1742 | 1954714 | 99 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 38 | 3762 | 37.141 | -122.0902 | Yes | Clear;32-90 F |  |  | 23-0016360 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1805115 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | TRANSFORMER | 411512146459 | 20230114 | 1641 | 20230114 | 1750 | 1954784 | 69 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 69 | 36.5742 | -121.8925 | Yes | Clear;32-90 F |  |  | 23-0016352 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1805108 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | FUSE | 8971 | 20230114 | 1657 | 20230114 | 1846 | 1954823 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 295 | 23555 | 36.4727 | -121.7254 | Yes | Clear;32-90 F |  |  | 23-0016349 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1805105 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DEL MONTE-2104 | 182222104 | FUSE | 23145 | 20230114 | 1726 | 20230114 | 1925 | 1954874 | 119 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1428 | 36.5686 | -121.7511 | Yes | Clear;32-90 F |  |  | 23-0016387 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805138 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | TRANSFORMER | 411450647671 | 20230114 | 1804 | 20230115 | 1525 | 1954934 | 1281 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 15372 | 36.607 | -121.915 | Yes | Clear;32-90 F | Crossarm- Wood | Broken | 23-0016351 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805107 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | OTHER | WIRE DOWN 1 SS OF 44531 | 20230114 | 1822 | 20230116 | 1726 | 1955094 | 2776 | Distribution Circuit | Vegetation | Tree - fell into line | 3175 | 153499 | 36.9544 | -121.8461 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016386 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | Yes | Yes | 1805137 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | FORT ORD-2106 | 182402106 | RECLOSER | 37286 | 20230114 | 1843 | 20230115 | 1320 | 1955061 | 1003 | Distribution Circuit | Equipment Failure/Involved | Underground | 2436 | 1021802 | 36.6436 | -121.7895 | Yes | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0016379 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805130 | 0 | EPSS Ckt | N | 2023 | A GRD
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | TRANSFORMER | 315296622954 | 20230114 | 2103 | 20230115 | 1840 | 1956217 | 1297 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 3891 | 37.1188 | -122.1141 | Yes | Clear;32-90F |  |  | 23-0016794 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805490 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | SWITCH | 5231 | 20230114 | 2212 | 20230115 | 1501 | 1955276 | 1009 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 33249 | 37.0543 | -122.074 | Yes | Clear;32-90F | Regulator | Arcing | 23-0016484 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805238 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1112 | 182371112 | RECLOSER | 562376 | 20230115 | 536 | 20230115 | 1635 | 1955492 | 659 | Distribution Circuit | Vegetation | Tree - fell into line | 490 | 114727 | 36.4845 | -121.7349 | No | Clear;32-90F | Conductor- Overhead | Together | 23-0016520 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | No | No | 1805278 | 0 | EPSS Ckt | N | 2023 | A-B-C
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 5078 | 20230115 | 715 | 20230115 | 853 | 1955549 | 98 | Distribution Circuit | Vegetation | Tree - branch fell on line | 451 | 43882 | 37.0314 | -122.1879 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0016541 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1805295 | 0 | EPSS Ckt | N | 2023 | B/C
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | OCB | 1101/2 | 20230115 | 806 | 20230115 | 935 | 1955597 | 85 | Distribution Circuit | Vegetation | Tree - fell into line | 815 | 69275 | 36.5569 | -121.8976 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 23-0016559 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805312 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | FUSE | 9657 | 20230115 | 824 | 20230115 | 1315 | 1955614 | 291 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 9021 | 36.2615 | -121.1796 | No | Clear;32-90F | Pole-Wood | Deteriorated | 23-0016564 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805315 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 36514 | 20230115 | 858 | 20230115 | 1117 | 1955762 | 139 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 77 | 10703 | 37.0395 | -122.1518 | No | Clear;32-90F |  |  | 23-0016638 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1805378 | 0 | EPSS Ckt | N | 2023 | A/B
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | TRANSFORMER | 315694518120 | 20230115 | 920 | 20230116 | 1230 | 1955707 | 1630 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 16300 | 36.988 | -121.974 | No | Clear;32-90F | Conductor- Overhead | Burned/flashed | 23-0016593 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1805339 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | JUMPER | 11527 HIGH SIDE JUMPERS | 20230115 | 940 | 20230115 | 1145 | 1955713 | 125 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 250 | 36.8844 | -121.7292 | No | Clear;32-90F | Crossarm- Wood | Broken | 23-0016595 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805341 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 5825 | 20230115 | 1024 | 20230115 | 1831 | 1955756 | 487 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 24837 | 37.0127 | -121.7935 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0016603 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805350 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6643 | 20230115 | 1029 | 20230116 | 1124 | 1955758 | 1495 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 46345 | 36.9998 | -121.7972 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0016626 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805366 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6543 | 20230115 | 1106 | 20230117 | 1251 | 1955840 | 2985 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 77610 | 36.9267 | -121.8459 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016669 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805403 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 11557 | 20230115 | 1220 | 20230116 | 1043 | 1955862 | 1343 | Distribution Circuit | Vegetation | Tree - grew into line | 1 | 1343 | 36.8641 | -121.7284 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0016668 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805402 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | TRANSFORMER | 316392613805 | 20230115 | 1442 | 20230115 | 1508 | 1956063 | 26 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 182 | 36.8726 | -121.7343 | No | Clear;32-90F | PGs- Kearneys | Deteriorated | 23-0016704 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805425 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | TRANSFORMER | 412624754859 | 20230115 | 1524 | 20230115 | 1641 | 1956107 | 77 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 385 | 36.8136 | -121.5208 | No | Clear;32-90F | Pole-Wood | Normal | 23-0016746 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805450 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5513 | 20230115 | 1557 | 20230116 | 2022 | 1956115 | 1705 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 51150 | 37.1516 | -122.1359 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0016742 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805445 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | TRANSFORMER | 413078058583 | 20230115 | 1603 | 20230116 | 103 | 1956151 | 540 | Transformer only | Equipment Failure/Involved | Underground | 2 | 1080 | 36.9188 | -121.369 | No | Clear;32-90 F | Service conductor | Failed/Faulted | 23-0016759 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805460 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 5141 | 20230115 | 1625 | 20230115 | 1814 | 1956176 | 109 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 1308 | 37.0947 | -122.0864 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016745 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | Yes | No | 1805449 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 2989 | 20230115 | 1633 | 20230118 | 1240 | 1956184 | 4087 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 16348 | 37.1639 | -122.0767 | No | Clear;32-90F |  |  | 23-0017681 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1806220 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6711 | 20230115 | 1644 | 20230118 | 1600 | 1956196 | 4276 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 209524 | 36.9982 | -121.8687 | No | Clear;32-90F | Pole-Wood | Broken | 23-0016757 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1805458 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 6975 | 20230115 | 1644 | 20230115 | 1741 | 1956197 | 57 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 949 | 36.5797 | -121.9204 | No | Clear;32-90F | Jumper | Burned/flashed | 23-0016762 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805463 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 5955 | 20230115 | 1645 | 20230115 | 1819 | 1956202 | 94 | Distribution Circuit | Equipment Failure/Involved | Overhead | 164 | 15416 | 37.0022 | -121.942 | No | Clear;32-90F | Connector or Splice (OH) | Broken- wire on ground | 23-0016750 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | Yes | No | 1805453 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | SWITCH | 5817 | 20230115 | 1727 | 20230116 | 1643 | 1956391 | 1396 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 127036 | 37.042 | -121.8179 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016765 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805493 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 974520 | 20230115 | 1744 | 20230115 | 2058 | 1956277 | 194 | Distribution Circuit | Vegetation | Tree - fell into line | 235 | 25830 | 36.9908 | -121.8063 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016765 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805465 | 0 | EPSS Ckt | N | 2023 | A & T
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6639 | 20230115 | 1839 | 20230118 | 1345 | 1956378 | 4026 | Distribution Circuit | Vegetation | Tree - branch fell on line | 35 | 100942 | 37.0075 | -121.809 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016765 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805489 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | RECLOSER | 2052 | 20230115 | 2026 | 20230116 | 133 | 1956373 | 307 | Distribution Circuit | Vegetation | Tree - fell into line | 585 | 44299 | 36.3999 | -121.9022 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016793 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805488 | 0 | EPSS Ckt | N | 2023 | SGF
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | FUSE | 6331 | 20230115 | 2039 | 20230116 | 947 | 1956379 | 788 | Distribution Circuit | Equipment Failure/Involved | Overhead | 145 | 33872 | 36.6932 | -121.796 | No | Clear;32-90F | Insulator | Broken | 23-0016847 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805545 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS COCHES-1102 | 182151102 | RECLOSER | 7046 | 20230115 | 2150 | 20230115 | 2358 | 1956417 | 128 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 4480 | 36.3728 | -121.2878 | No | Clear;32-90F | Conductor- Overhead | Broken | 23-0016844 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805542 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | FUSE | 23113 | 20230115 | 2159 | 20230116 | 925 | 1956419 | 686 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 6174 | 36.5963 | -121.621 | No | Clear;32-90F |  |  | 23-0016856 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805554 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | TRANSFORMER | 411410347570 | 20230115 | 2234 | 20230116 | 250 | 1956407 | 256 | Transformer only | Equipment Failure/Involved | Overhead | 21 | 5376 | 36.6038 | -121.9286 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0016850 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805548 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 264419 | 20230115 | 2347 | 20230117 | 1800 | 1956449 | 2533 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 10132 | 37.0738 | -122.0803 | No | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0016930 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805637 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 415734 | 20230115 | 2353 | 20230116 | 1025 | 1956451 | 632 | Distribution Circuit | Environmental/External | Flood/Erosion | 97 | 38667 | 37.0316 | -122.1893 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016852 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805550 | 0 | EPSS Ckt | N | 2023 | 51 (TIME)
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 6033 | 20230116 | 103 | 20230117 | 1321 | 1956499 | 2178 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 178596 | 37.081 | -122.0049 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0017109 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805801 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 2549 | 20230116 | 153 | 20230116 | 1033 | 1956529 | 520 | Distribution Circuit | Vegetation | Tree - grew into line | 16 | 5572 | 36.6017 | -121.9537 | Yes | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0016875 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805575 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 2487 | 20230116 | 201 | 20230116 | 1139 | 1956534 | 578 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3468 | 36.5845 | -121.8592 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016900 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805603 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 74170 | 20230116 | 204 | 20230116 | 654 | 1956498 | 290 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 231 | 66990 | 37.0883 | -122.0884 | Yes | Clear;32-90 F |  |  | 23-0016961 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805666 | 0 | EPSS Ckt | N | 2023 | B GRD
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | JUMPER | WIRE DOWN | 20230116 | 211 | 20230116 | 941 | 1956542 | 450 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 27288 | 36.9696 | -121.876 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017031 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805735 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 8125 | 20230116 | 215 | 20230117 | 1123 | 1956543 | 1988 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 37772 | 37.099 | -122.1424 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017073 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805770 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | TRIP-SAVER | 9031 | 20230116 | 225 | 20230116 | 833 | 1956559 | 368 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 12512 | 37.0726 | -122.0742 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0017029 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805733 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 65444 | 20230116 | 237 | 20230116 | 244 | 1956576 | 7 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 765 | 5355 | 37.1278 | -122.1229 | Yes | Clear;32-90 F |  |  | 23-0016876 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805578 | 0 | EPSS Ckt | N | 2023 | SGF
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6609 | 20230116 | 237 | 20230116 | 820 | 1957043 | 343 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 5831 | 36.9767 | -121.7763 | Yes | Clear;32-90 F |  |  | 23-0016965 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1805670 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | FUSE | 4775 | 20230116 | 239 | 20230116 | 841 | 1956571 | 362 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 88 | 31856 | 36.9768 | -121.9217 | Yes | Clear;32-90 F |  |  | 23-0017036 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805737 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 796388 | 20230116 | 239 | 20230117 | 1758 | 1956574 | 2359 | Distribution Circuit | Vegetation | Tree - fell into line | 269 | 634571 | 36.9818 | -121.901 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016877 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805577 | 0 | EPSS Ckt | N | 2023 | C PH & GRD
CENTRAL COAST | COAST | 83500401 | 83500401 | RECLOSER | 929132 | 20230116 | 240 | 20230116 | 1637 | 1956588 | 837 | Distribution Circuit | Vegetation | Tree - fell into line | 127 | 106299 | 36.9919 | -121.927 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016880 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1805581 | 0 | EPSS Ckt | N | 2023 | ABC
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | FUSE | 6001 | 20230116 | 244 | 20230117 | 1756 | 1956587 | 2352 | Distribution Circuit | Vegetation | Tree - fell into line | 332 | 146157 | 36.9898 | -121.9328 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016992 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1805697 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | TRANSFORMER | 411610746800 | 20230116 | 247 | 20230116 | 406 | 1956591 | 79 | Transformer only | Vegetation | Tree - fell into line | 1 | 79 | 36.5845 | -121.8591 | Yes | Clear;32-90 F | Fuse | Normal | 23-0016907 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805610 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 4397 | 20230116 | 249 | 20230117 | 1730 | 1956597 | 2321 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 111408 | 36.9719 | -121.8757 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017135 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805825 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 7593 | 20230116 | 250 | 20230116 | 1345 | 1956601 | 655 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 44540 | 37.1057 | -121.9724 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017049 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805748 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 8643 | 20230116 | 254 | 20230116 | 830 | 1956604 | 334 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 45 | 15030 | 37.01 | -121.8859 | Yes | Clear;32-90 F |  |  | 23-0017022 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1805726 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | OTHER | TREE THRU LINES | 20230116 | 257 | 20230117 | 1457 | 1956868 | 2160 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 85517 | 37.153 | -122.1235 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016935 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | Yes | Yes | 1805641 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 37210 | 20230116 | 307 | 20230116 | 1723 | 1958630 | 856 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 61 | 52216 | 37.0809 | -122.0047 | Yes | Clear;32-90 F |  |  | 23-0017331 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1806005 | 0 | EPSS Ckt | N | 2023 | AC
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 4407 | 20230116 | 313 | 20230116 | 540 | 1956660 | 147 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 107 | 15729 | 36.9026 | -121.3627 | Yes | Clear;32-90 F |  |  | 23-0016931 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805638 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 2175 | 20230116 | 321 | 20230116 | 1005 | 1956669 | 404 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 66 | 26664 | 36.8777 | -121.7341 | Yes | Clear;32-90 F |  |  | 23-0017085 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1805779 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | 83500401 | 83500401 | RECLOSER | 12946 | 20230116 | 324 | 20230116 | 1426 | 1956683 | 662 | Distribution Circuit | Vegetation | Tree - fell into line | 213 | 136302 | 36.9875 | -121.9186 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016893 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1805594 | 0 | EPSS Ckt | N | 2023 | A & C PHASE
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | FUSE | 4287 | 20230116 | 328 | 20230116 | 1210 | 1956681 | 522 | Distribution Circuit | Equipment Failure/Involved | Overhead | 183 | 95526 | 36.6802 | -121.6736 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016912 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805619 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | TRIP-SAVER | 3959 | 20230116 | 331 | 20230116 | 1808 | 1956718 | 877 | Distribution Circuit | Vegetation | Tree - fell into line | 374 | 327998 | 36.959 | -122.0316 | Yes | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0016916 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1805623 | 0 | EPSS Ckt | N | 2023 | NA
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 3359 | 20230116 | 331 | 20230117 | 404 | 1956713 | 1473 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 8838 | 36.7714 | -121.7113 | Yes | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0017352 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1806022 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 12106 | 20230116 | 332 | 20230116 | 747 | 1956577 | 255 | Distribution Circuit | Vegetation | Tree - branch fell on line | 995 | 253725 | 36.9718 | -121.7649 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0016897 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1805600 | 0 | EPSS Ckt | N | 2023 | A & C PHASE
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 737512 | 20230116 | 339 | 20230116 | 1626 | 1956732 | 767 | Distribution Circuit | Vegetation | Tree - fell into line | 465 | 312625 | 37.0467 | -122.074 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0016949 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1805654 | 0 | EPSS Ckt | N | 2023 | AB GRD
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | TRIP-SAVER | 25695 | 20230116 | 339 | 20230116 | 1300 | 1956730 | 561 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 157 | 88077 | 36.7493 | -121.6573 | Yes | Clear;32-90 F |  |  | 23-0017200 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1805878 | 0 | EPSS Ckt | N | 2023 | B & C
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 12840 | 20230116 | 341 | 20230117 | 1209 | 1956738 | 1948 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 100606 | 37.0538 | -121.9545 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016899 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805602 | 0 | EPSS Ckt | N | 2023 | B GRD
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 8917 | 20230116 | 342 | 20230116 | 1253 | 1956737 | 551 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 11571 | 36.5771 | -121.9274 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0016911 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805618 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 6753 | 20230116 | 353 | 20230116 | 1511 | 1956749 | 678 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 25764 | 36.5659 | -121.8876 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016927 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805634 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | RECLOSER | 22160 | 20230116 | 431 | 20230116 | 2057 | 1956786 | 986 | Distribution Circuit | Vegetation | Tree - fell into line | 1547 | 538150 | 36.7971 | -121.6669 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0016915 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1805622 | 0 | EPSS Ckt | N | 2023 | A- B & GRD
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315426820434 | 20230116 | 438 | 20230116 | 2112 | 1956710 | 994 | Transformer only | Vegetation | Tree - fell into line | 14 | 13916 | 37.0505 | -122.068 | Yes | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0016925 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805632 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 11384 | 20230116 | 518 | 20230116 | 1807 | 1956858 | 769 | Distribution Circuit | Vegetation | Tree - fell into line | 416 | 88568 | 37.0534 | -122.0437 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016929 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805636 | 0 | EPSS Ckt | N | 2023 | B GRD
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 11327 | 20230116 | 538 | 20230116 | 1700 | 1956873 | 682 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 682 | 36.9868 | -121.8846 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017064 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805762 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | INDUSTRIAL ACRES-0412 | 182300412 | SWITCH | 22454 | 20230116 | 555 | 20230116 | 2115 | 1956886 | 920 | Distribution Circuit | Equipment Failure/Involved | Overhead | 968 | 890560 | 36.6767 | -121.6261 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0016942 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805648 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 8883 | 20230116 | 712 | 20230117 | 1620 | 1957162 | 1988 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 7276 | 37.0832 | -122.0958 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017012 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805717 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | SWITCH | 11011 | 20230116 | 741 | 20230116 | 1540 | 1957050 | 479 | Distribution Circuit | Vegetation | Tree - fell into line | 515 | 49287 | 37.022 | -122.0214 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0017000 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805705 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 412094754121 | 20230116 | 743 | 20230116 | 1657 | 1957233 | 554 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 3878 | 36.7901 | -121.7016 | Yes | Clear;32-90 F | Transformer | Deteriorated | 23-0017168 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805856 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 3889 | 20230116 | 830 | 20230119 | 1715 | 1957319 | 4845 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 18957 | 36.9487 | -121.8523 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017025 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | Yes | Yes | 1805729 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 8171 | 20230116 | 841 | 20230116 | 1745 | 1957352 | 544 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1088 | 36.5445 | -121.8848 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017108 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1805800 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | OTHER | 3533 | 20230116 | 842 | 20230116 | 1720 | 1957355 | 436 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 2512 | 36.6914 | -121.7078 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017095 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805787 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 2405 | 20230116 | 854 | 20230116 | 1803 | 1957506 | 549 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1098 | 36.9142 | -121.6701 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017077 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | Yes | 1805773 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 11335 | 20230116 | 905 | 20230116 | 1149 | 1957402 | 164 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 984 | 37.014 | -121.8883 | Yes | Clear;32-90 F |  |  | 23-0017181 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1805867 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | OTHER | WIRE DOWN | 20230116 | 1007 | 20230116 | 1640 | 1957693 | 367 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1030 | 106958 | 36.9035 | -121.7818 | Yes | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0017120 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1805809 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 11054 | 20230116 | 1038 | 20230117 | 932 | 1957196 | 1374 | Distribution Circuit | Vegetation | Tree - fell into line | 274 | 97340 | 36.9775 | -121.7415 | Yes | Clear;32-90 F | Conductor- Overhead | Burned/flashed | 23-0017122 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805810 | 0 | EPSS Ckt | N | 2023 | NA
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | FUSE | 4767 | 20230116 | 1101 | 20230116 | 1706 | 1957638 | 365 | Distribution Circuit | Vegetation | Tree - branch fell on line | 35 | 12775 | 36.9779 | -121.917 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0017133 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805823 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | TRANSFORMER | 412135449183 | 20230116 | 1106 | 20230116 | 1845 | 1957765 | 459 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 459 | 36.6542 | -121.6825 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0017202 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805879 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 3541 | 20230116 | 1139 | 20230116 | 1419 | 1957899 | 160 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 4320 | 36.8789 | -121.6911 | Yes | Clear;32-90 F |  |  | 23-0017250 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1805924 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | TRANSFORMER | 316532013246 | 20230116 | 1322 | 20230116 | 1448 | 1958153 | 86 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 258 | 36.8574 | -121.6866 | Yes | Clear;32-90 F |  |  | 23-0017265 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1805940 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | TRANSFORMER | 315603318261 | 20230116 | 1326 | 20230116 | 1402 | 1946125 | 36 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 252 | 36.9915 | -122.0058 | Yes | Clear;32-90 F | Secondary | Deteriorated | 23-0017213 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805887 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 12629 | 20230116 | 1339 | 20230116 | 1442 | 1958175 | 63 | Distribution Circuit | Vegetation | Tree - grew into line | 403 | 25389 | 36.9412 | -121.8576 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0017201 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805895 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | FUSE | 50781 | 20230116 | 1450 | 20230116 | 1550 | 1958367 | 60 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 120 | 36.7888 | -121.3435 | Yes | Clear;32-90 F |  |  | 23-0017288 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805972 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | INDUSTRIAL ACRES SUB | 18230 | OCB | 412/2 | 20230116 | 1453 | 20230116 | 1524 | 1958372 | 31 | Distribution Circuit | Equipment Failure/Involved | Overhead | 731 | 22661 | 36.6641 | -121.6288 | Yes | Clear;32-90 F | Conductor- Overhead | Burned/flashed | 23-0017211 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805942 | 0 | Non-EPSS | N | 2023 | N/A
CENTRAL COAST | COAST | PAUL SWEET 2108 | 83252108 | TRANSFORMER | 315584417357 | 20230116 | 1501 | 20230116 | 1638 | 1958400 | 97 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 97 | 36.9664 | -122.0113 | Yes | Clear;32-90 F | Transformer (OH) | Normal | 23-0017245 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1805952 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 16000 | 20230116 | 1708 | 20230116 | 1716 | 1958614 | 8 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3177 | 25416 | 37.0464 | -122.0243 | Yes | Clear;32-90 F |  |  | 23-0017329 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1806004 | 0 | EPSS Ckt | N | 2023 | AC
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6793 | 20230116 | 1722 | 20230116 | 1931 | 1958637 | 129 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 387 | 36.9225 | -121.6794 | Yes | Clear;32-90 F | Crossarm- Wood | Broken | 23-0017334 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1806008 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315613621994 | 20230116 | 1740 | 20230116 | 2244 | 1958661 | 304 | Transformer only | Environmental/External | Flood/Erosion | 1 | 304 | 37.0943 | -122.0049 | Yes | Clear;32-90F | Transformer (OH) |  | 23-0017435 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806105 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 10977 | 20230116 | 1804 | 20230116 | 1837 | 1958679 | 33 | Distribution Circuit | Company Initiated | Return Circuit Normal | 14 | 462 | 37.0958 | -122.277 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0016852 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1806017 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 6163 | 20230116 | 1820 | 20230117 | 920 | 1959269 | 900 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 2700 | 37.0507 | -122.0799 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0017513 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1806153 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | TRANSFORMER | 411379447482 | 20230116 | 1900 | 20230117 | 240 | 1958781 | 460 | Transformer only | Vegetation | Tree - fell into line | 17 | 7820 | 36.6012 | -121.9388 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017384 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1806054 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 734605 | 20230116 | 1939 | 20230116 | 2144 | 1958830 | 125 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 250 | 36.9047 | -121.7802 | Yes | Clear;32-90F |  |  | 23-0017422 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806092 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | PAUL SWEET 2103 | 83252103 | TRANSFORMER | 315554917988 | 20230116 | 2243 | 20230117 | 204 | 1958988 | 201 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 2412 | 36.9836 | -122.0221 | Yes | Clear;32-90F | Secondary | Bent or Twisted | 23-0017443 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1806111 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | SWITCH | 8614 | 20230117 | 306 | 20230117 | 344 | 1959043 | 38 | Distribution Circuit | Company Initiated | Return Circuit Normal | 163 | 6194 | 36.5398 | -121.907 | No | Clear;32-90F | Conductor- Underground | Normal | 23-0017448 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1806116 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | TRANSFORMER | 412203051660 | 20230117 | 1028 | 20230117 | 1611 | 1959423 | 343 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 1715 | 36.7225 | -121.6634 | No | Clear;32-90F | Connector or Splice (OH) | Burned Open | 23-0017716 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806227 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | OTHER | WIRE DOWN SS OF 1715 | 20230117 | 1036 | 20230117 | 1252 | 1959541 | 136 | Distribution Circuit | Equipment Failure/Involved | Overhead | 294 | 36528 | 36.8895 | -121.7879 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0017618 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | Yes | Yes | 1806197 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412196754658 | 20230117 | 1059 | 20230117 | 1259 | 1959495 | 120 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 360 | 36.8055 | -121.6672 | No | Clear;32-90 F | Transformer | Normal | 23-0017655 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1806211 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | FUSE | 9541 | 20230117 | 1123 | 20230117 | 1350 | 1959534 | 147 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 294 | 36.2926 | -121.2875 | No | Clear;32-90F |  |  | 23-0017878 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806290 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 12473 | 20230117 | 1130 | 20230117 | 1223 | 1959557 | 53 | Distribution Circuit | Equipment Failure/Involved | Overhead | 83 | 4399 | 36.9718 | -121.8759 | No | Clear;32-90F | Transformer (OH) | Deteriorated | 23-0017624 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1806199 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | SWITCH | 1289 | 20230117 | 1224 | 20230117 | 1721 | 1959511 | 297 | Distribution Circuit | Vegetation | Tree - grew into line | 161 | 24975 | 36.9955 | -121.8498 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0017662 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1806214 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 12417 | 20230117 | 1309 | 20230118 | 1144 | 1959699 | 1355 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 10840 | 37.1377 | -122.0133 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0017754 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1806238 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO-1101 | 182191101 | FUSE | 9073 | 20230117 | 1509 | 20230118 | 1151 | 1960676 | 1242 | Distribution Circuit | Environmental/External | Flood/Erosion | 11 | 13662 | 36.0841 | -120.9783 | No | Clear;32-90F | Pole-Wood | On Ground | 23-0018168 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1806526 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | TRANSFORMER | 315902617367 | 20230117 | 1626 | 20230118 | 1039 | 1960110 | 1093 | Transformer only | Equipment Failure/Involved | Overhead | 23 | 25139 | 36.9684 | -121.9025 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0017859 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806278 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | TRANSFORMER | 315922018085 | 20230117 | 1950 | 20230118 | 734 | 1960315 | 704 | Transformer only | Vegetation | Tree - bark fell into line | 4 | 2816 | 36.9883 | -121.8974 | No | Clear;32-90 F | Transformer | Burned Open | 23-0017977 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806390 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | TRANSFORMER | 315381621640 | 20230118 | 26 | 20230120 | 659 | 1960403 | 3273 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 13092 | 37.0836 | -122.0837 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0018078 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806489 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | FUSE | 10090 | 20230118 | 137 | 20230118 | 334 | 1960421 | 117 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 189 | 22113 | 36.9873 | -121.9213 | No | Clear;32-90F |  |  | 23-0018070 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1806483 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRANSFORMER | 315477422392 | 20230118 | 503 | 20230120 | 658 | 1960482 | 2995 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 8985 | 37.1044 | -122.0518 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0018328 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806567 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 6771 | 20230118 | 712 | 20230118 | 830 | 1960527 | 78 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 1377 | 36.8682 | -121.6457 | No | Clear;32-90F |  |  | 23-0018133 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806506 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | JUMPER | R62 OPEN JMPR | 20230118 | 822 | 20230118 | 1250 | 1960792 | 268 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3061 | 88320 | 36.8758 | -121.7747 | No | Clear;32-90F | Jumper | Burned Open | 23-0018227 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1806548 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 11517 | 20230118 | 859 | 20230118 | 1146 | 1960615 | 167 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 1336 | 36.8924 | -121.714 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0018129 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1806504 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | TRANSFORMER | 412203051660 | 20230118 | 904 | 20230118 | 1401 | 1960642 | 297 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 1485 | 36.7225 | -121.6634 | No | Clear;32-90 F | Connector or Splice (OH) | Burned/flashed | 23-0018196 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806540 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | SWITCH | 40065 | 20230118 | 946 | 20230118 | 1734 | 1960710 | 468 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 34632 | 36.5837 | -121.9123 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0017858 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1806537 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-1101 | 182221101 | TRANSFORMER | 411705748079 | 20230118 | 1010 | 20230118 | 1349 | 1960780 | 219 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 3066 | 36.6199 | -121.8279 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0018266 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806552 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | JUMPER | OJ 1 SPAN E/O CGC 316185018840 | 20230118 | 1011 | 20230118 | 1733 | 1960640 | 442 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 442 | 37.011 | -121.8074 | No | Clear;32-90F | Anchor or Guy | Broken | 23-0018144 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1806512 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | FUSE | 12265 | 20230118 | 1101 | 20230118 | 1535 | 1960592 | 274 | Distribution Circuit | Equipment Failure/Involved | Overhead | 72 | 19728 | 36.9588 | -121.9805 | No | Clear;32-90F | Pole-Wood | Burned/flashed | 23-0018123 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1806497 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0424 | 182440424 | TRANSFORMER | 411418348620 | 20230118 | 1131 | 20230118 | 1209 | 1960890 | 38 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 456 | 36.6327 | -121.9268 | No | Clear;32-90F | Fuse | Burned Open | 23-0018347 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806574 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | FUSE | 3485 | 20230118 | 1144 | 20230118 | 1350 | 1960909 | 126 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 126 | 36.7181 | -121.6833 | No | Clear;32-90F |  |  | 23-0018435 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1806593 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | RECLOSER | 899037 | 20230118 | 1339 | 20230118 | 1458 | 1961052 | 79 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 333 | 26307 | 36.831 | -121.6793 | No | Clear;32-90F |  |  | 23-0018418 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806590 | 0 | EPSS Ckt | N | 2023 | A GRD
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | JUMPER | OJ 2 SPANS SS OF CGC# 412909341145 | 20230118 | 1616 | 20230119 | 1147 | 1961232 | 1171 | Distribution Circuit | Environmental/External | Flood/Erosion | 3 | 3513 | 36.4376 | -121.4126 | No | Clear;32-90F | Pole-Wood | Broken | 23-0018540 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1806622 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 9651 | 20230118 | 1627 | 20230118 | 2134 | 1961253 | 307 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1535 | 36.8577 | -121.7717 | No | Clear;32-90F |  |  | 23-0018627 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1806683 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | OTHER | WIRE DOWN AT 6147 | 20230118 | 1733 | 20230119 | 21 | 1961414 | 408 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6188 | 605581 | 36.5875 | -121.9434 | No | Clear;32-90F | Connector or Splice (OH) | Broken- wire on ground | 23-0018564 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | Yes | Yes | 1806639 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | TRANSFORMER | 315842017673 | 20230118 | 1837 | 20230120 | 1101 | 1961443 | 2424 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 14544 | 36.9766 | -121.9243 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0018570 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806642 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 2181 | 20230118 | 2112 | 20230119 | 305 | 1961507 | 353 | Distribution Circuit | Vegetation | Tree - fell into line | 84 | 29652 | 36.4895 | -121.9363 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0018633 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1806690 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | FUSE | 4545 | 20230119 | 157 | 20230119 | 710 | 1961755 | 313 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1878 | 36.5981 | -121.6416 | No | Clear;32-90F |  |  | 23-0018682 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1806729 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 5807 | 20230119 | 430 | 20230121 | 1246 | 1961782 | 3376 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 168800 | 36.9746 | -121.8839 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0018660 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1806724 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRANSFORMER | 315462820472 | 20230119 | 1522 | 20230120 | 919 | 1962559 | 1077 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 5385 | 37.0516 | -122.0557 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0019023 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806837 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | JUMPER | BURNT OPEN JPRS 1 SPAN SSD OF 6463 | 20230119 | 1625 | 20230120 | 419 | 1962800 | 708 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 3277 | 36.5674 | -121.7803 | No | Clear;32-90F | Jumper | Burned Open | 23-0019116 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1806889 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 6161 | 20230119 | 1701 | 20230119 | 1900 | 1962681 | 119 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 2737 | 37.1187 | -122.0198 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0019054 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1806850 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315561020257 | 20230119 | 2325 | 20230120 | 1032 | 1962813 | 667 | Transformer only | Environmental/External | Water | 8 | 5336 | 37.0464 | -122.022 | No | Clear;32-90 F | Transformer | Arcing | 23-0019184 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806956 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 12435 | 20230120 | 209 | 20230120 | 607 | 1962861 | 238 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 4046 | 37.1378 | -122.0133 | No | Clear;32-90F |  |  | 23-0019193 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806967 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9181 | 20230120 | 451 | 20230120 | 950 | 1962882 | 299 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 4186 | 37.2288 | -122.148 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0019336 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1807035 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 7005 | 20230120 | 951 | 20230120 | 1557 | 1963107 | 366 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 14640 | 36.9961 | -121.7994 | No | Clear;32-90F | Pole-Wood | Deteriorated | 23-0019313 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1807018 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRANSFORMER | 315079924942 | 20230120 | 1018 | 20230120 | 1627 | 1963144 | 369 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 738 | 37.1722 | -122.1911 | No | Clear;32-90 F | Transformer | Broken | 23-0019423 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807054 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | TRANSFORMER | 411681347512 | 20230120 | 1045 | 20230120 | 1605 | 1963184 | 320 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 3840 | 36.6042 | -121.8359 | No | Clear;32-90 F | Cutout- fuse holder | Failed/Faulted | 23-0019413 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807053 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | FORT ORD-2106 | 182402106 | FUSE | 9911 | 20230120 | 1621 | 20230120 | 1803 | 1963522 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 102 | 36.6379 | -121.8122 | No | Clear;32-90 F |  |  | 23-0019620 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807093 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | TRANSFORMER | 411487047739 | 20230120 | 1911 | 20230120 | 1939 | 1963623 | 28 | Transformer only | Equipment Failure/Involved | Underground | 35 | 980 | 36.6094 | -121.9029 | No | Clear;32-90 F | Connector or Splice (UG) | Burned/flashed | 23-0019623 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807097 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DEL MONTE-2104 | 182222104 | TRANSFORMER | 411924046128 | 20230120 | 2349 | 20230121 | 1630 | 1963520 | 1001 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1001 | 36.5685 | -121.7516 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0019668 | OH | Sus | 35422561 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807142 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | FUSE | 9707 | 20230121 | 102 | 20230122 | 1751 | 1963723 | 2449 | Distribution Circuit | Environmental/External | Flood/Erosion | 17 | 41633 | 36.0519 | -120.9213 | No | Clear;32-90F | Pole-Wood | Deteriorated | 23-0019671 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | No | No | 1807146 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | FUSE | 56451 | 20230121 | 108 | 20230122 | 1808 | 1964965 | 2460 | Distribution Circuit | Environmental/External | Flood/Erosion | 1 | 2460 | 36.0515 | -120.9217 | No | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0019927 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1807361 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 3921 | 20230121 | 659 | 20230121 | 916 | 1963769 | 137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 203 | 27811 | 36.8382 | -121.6835 | No | Clear;32-90F |  |  | 23-0019686 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1807161 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE 2102 | 182222102 | FUSE | 6101 | 20230121 | 840 | 20230121 | 950 | 1963853 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 422 | 29540 | 36.6076 | -121.852 | No | Clear;32-90F |  |  | 23-0019698 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1807178 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 5131 | 20230121 | 928 | 20230121 | 1422 | 1963829 | 294 | Distribution Circuit | Vegetation | Tree - grew into line | 112 | 32928 | 37.0902 | -122.0899 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0019691 | OH | Sus | 45646592 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1807169 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | TRANSFORMER | 413281551205 | 20230121 | 946 | 20230122 | 741 | 1963920 | 1315 | Transformer only | Company Initiated | Personnel- company | 1 | 1315 | 36.718 | -121.2935 | No | Clear;32-90 F | Transformer | Normal | 23-0007483 | OH | Sus | 35239080 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1807180 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | TRANSFORMER | 413300335758 | 20230121 | 1343 | 20230122 | 1028 | 1963983 | 1245 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2490 | 36.2939 | -121.2747 | No | Clear;32-90F | Jumper | Burned Open | 23-0019743 | OH | Sus | 45646942 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807214 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1109 | 182011109 | FUSE | 948327 | 20230121 | 1548 | 20230122 | 1714 | 1964195 | 1526 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 13734 | 36.6776 | -121.5908 | No | Clear;32-90F |  |  | 23-0019792 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807252 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | TRANSFORMER | 411363546431 | 20230122 | 843 | 20230122 | 2145 | 1964522 | 782 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1564 | 36.5721 | -121.943 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0019841 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807295 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | INDUSTRIAL ACRES-0415 | 182300415 | TRANSFORMER | 412298449431 | 20230122 | 1032 | 20230123 | 446 | 1964636 | 1094 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 3282 | 36.662 | -121.6274 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0019863 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807308 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 2705 | 20230122 | 1134 | 20230122 | 1409 | 1964674 | 155 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 26 | 4030 | 37.0005 | -121.7403 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0019882 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1807321 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | JUMPER | TREE ON WIRE ENER | 20230122 | 1429 | 20230122 | 2207 | 1964822 | 458 | Distribution Circuit | Vegetation | Tree - fell into line | 1193 | 33355 | 37.0834 | -122.0792 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0019904 | OH | Sus | 31634962 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807341 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | RECLOSER | 12662 | 20230122 | 1441 | 20230123 | 730 | 1964834 | 1009 | Distribution Circuit | Vegetation | Tree - fell into line | 211 | 156107 | 36.8984 | -121.6906 | No | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0019896 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1807333 | 0 | EPSS Ckt | N | 2023 | B&GRD
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5235 | 20230122 | 1549 | 20230122 | 1732 | 1964915 | 103 | Distribution Circuit | Vegetation | Tree - branch fell on line | 60 | 6180 | 37.0596 | -122.0793 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0019926 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807360 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9181 | 20230122 | 2004 | 20230123 | 1058 | 1965041 | 894 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 12516 | 37.2288 | -122.148 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0019970 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1807403 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 5529 | 20230122 | 2212 | 20230123 | 1640 | 1965085 | 1108 | Distribution Circuit | Vegetation | Tree - fell into line | 329 | 364532 | 36.9879 | -121.9467 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0019976 | OH | Sus | 45647011 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1807409 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 11461 | 20230122 | 2324 | 20230123 | 1547 | 1966138 | 983 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 10813 | 36.8678 | -121.76 | No | Clear;32-90F |  |  | 23-0020415 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807632 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 2689 | 20230122 | 2326 | 20230124 | 10 | 1965146 | 1484 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 47488 | 37.1274 | -122.0181 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0020240 | OH | Sus | 45647468 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1807596 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 32887 | 20230123 | 22 | 20230123 | 213 | 1965160 | 111 | Distribution Circuit | 3rd Party | Vehicle | 1 | 111 | 36.8541 | -121.3226 | No | Clear;32-90F | Cutout- fuse holder | Normal | 23-0019983 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807416 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 7309 | 20230123 | 41 | 20230123 | 558 | 1965163 | 317 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 5072 | 37.0328 | -122.0755 | No | Clear;32-90F |  |  | 23-0020005 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807437 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 1563 | 20230123 | 45 | 20230123 | 1418 | 1965164 | 813 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 2439 | 37.045 | -122.0754 | No | Clear;32-90F |  |  | 23-0020321 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807616 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 7959 | 20230123 | 47 | 20230123 | 1747 | 1965165 | 1020 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 28700 | 37.0696 | -122.0916 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0019984 | OH | Sus | 45647074 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1807417 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6851 | 20230123 | 54 | 20230124 | 1510 | 1965166 | 2296 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 25228 | 37.0421 | -121.8171 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0020283 | OH | Sus | 45647470 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1807609 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 7229 | 20230123 | 100 | 20230123 | 1153 | 1965169 | 653 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 3918 | 37.0691 | -122.0839 | No | Clear;32-90F |  |  | 23-0020205 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807580 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 39126 | 20230123 | 207 | 20230123 | 437 | 1965194 | 150 | Distribution Circuit | Vegetation | Tree - branch fell on line | 378 | 56700 | 37.0778 | -122.1322 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0019997 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1807429 | 0 | EPSS Ckt | N | 2023 | A & B
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 4933 | 20230123 | 303 | 20230123 | 2348 | 1965250 | 1245 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 23655 | 36.9265 | -121.816 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0019995 | OH | Sus | 45647105 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1807428 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | SWITCH | 6527 | 20230123 | 617 | 20230123 | 643 | 1965336 | 26 | Distribution Circuit | Company Initiated | Return Circuit Normal | 26 | 676 | 37.0045 | -121.7688 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0019882 | OH | Sus | 35422700 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1807440 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | TRANSFORMER | 412932042248 | 20230123 | 816 | 20230124 | 125 | 1965430 | 1029 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1029 | 36.4697 | -121.4053 | No | Clear;32-90 F | Jumper | Broken | 23-0020120 | OH | Sus | 45647275 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807557 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 7349 | 20230123 | 1010 | 20230123 | 1337 | 1965698 | 207 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 4 | 828 | 37.0565 | -121.942 | No | Clear;32-90F |  |  | 23-0020302 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807612 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | TRANSFORMER | 412909341145 | 20230123 | 1630 | 20230124 | 808 | 1966166 | 938 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 938 | 36.4386 | -121.4118 | No | Clear;32-90 F | Transformer | Broken | 23-0020454 | OH | Sus | 35422901 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807652 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 471 | 20230123 | 2005 | 20230124 | 422 | 1966318 | 497 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 4787 | 36.4954 | -121.9372 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0020464 | OH | Sus | 31635383 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1807661 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | TRANSFORMER | 316338215348 | 20230123 | 2234 | 20230124 | 232 | 1966306 | 238 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 1904 | 36.9149 | -121.7536 | No | Clear;32-90F | Connector or Splice (OH) | Burned Open | 23-0020484 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807679 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | SWITCH | 1189 | 20230124 | 28 | 20230124 | 40 | 1966371 | 12 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 180 | 37.0841 | -122.0221 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0020490 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1807688 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DEL MONTE-2104 | 182222104 | FUSE | 20461 | 20230124 | 659 | 20230124 | 1115 | 1966459 | 256 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 2816 | 36.5384 | -121.7252 | No | Clear;32-90F |  |  | 23-0020705 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807850 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | JUMPER | FB 1 E/OF 7629 | 20230124 | 902 | 20230124 | 1434 | 1966648 | 332 | Distribution Circuit | Vegetation | Tree - grew into line | 5 | 1660 | 36.9296 | -121.8559 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0020592 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1807772 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | TRANSFORMER | T3232 | 20230124 | 1110 | 20230126 | 421 | 1966934 | 2471 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 21159 | 36.9874 | -121.964 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0020725 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807862 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | FUSE | 5111 | 20230124 | 1128 | 20230124 | 1702 | 1966950 | 334 | Distribution Circuit | 3rd Party | Vehicle | 9 | 3006 | 36.6754 | -121.678 | No | Clear;32-90F | Pole-Wood | Broken | 23-0020780 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1807887 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | TRANSFORMER | 315508717440 | 20230124 | 1427 | 20230125 | 1549 | 1967148 | 1512 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 12096 | 36.9689 | -122.0383 | No | Clear;32-90F | Pole-Wood | Deteriorated | 23-0020916 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807924 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | TRANSFORMER | 412700042000 | 20230124 | 1634 | 20230125 | 1310 | 1967052 | 1236 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1236 | 36.4592 | -121.4824 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0020933 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807931 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 316062015615 | 20230125 | 103 | 20230125 | 955 | 1967479 | 532 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 1064 | 36.9209 | -121.8482 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0021001 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807976 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | TRANSFORMER | T0446 | 20230125 | 219 | 20230125 | 454 | 1967505 | 155 | Transformer only | Unknown Cause | Patrol - found nothing | 15 | 2325 | 36.7279 | -121.6502 | No | Clear;32-90F |  |  | 23-0021006 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1807979 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | TRANSFORMER | 412000952032 | 20230125 | 820 | 20230125 | 1951 | 1967611 | 691 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 691 | 36.731 | -121.731 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0021077 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1808025 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315649722088 | 20230125 | 828 | 20230125 | 1340 | 1967626 | 312 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 624 | 37.0971 | -121.9932 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0021205 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1808129 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0424 | 182440424 | FUSE | 1333 | 20230125 | 842 | 20230125 | 2121 | 1967655 | 759 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 22011 | 36.6333 | -121.9249 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0021330 | OH | Sus | 45649839 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1808163 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRANSFORMER | 315359721141 | 20230125 | 1256 | 20230125 | 1419 | 1968027 | 83 | Transformer only | Company Initiated | Return Circuit Normal | 3 | 249 | 37.0696 | -122.0915 | No | Clear;32-90F | Transformer (OH) | Normal | 23-0021255 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1808143 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | BUENA VISTA-1103 | 182261103 | TRANSFORMER | 412239149207 | 20230125 | 1409 | 20230125 | 1535 | 1968115 | 86 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 946 | 36.6555 | -121.6476 | No | Clear;32-90F | Transformer (OH) | Normal | 23-0021306 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1808159 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | TRANSFORMER | 316200613194 | 20230125 | 1520 | 20230125 | 1747 | 1968179 | 147 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 735 | 36.855 | -121.7997 | No | Clear;32-90F | Secondary | Burned/flashed | 23-0021363 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1808169 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 6087 | 20230125 | 1538 | 20230126 | 159 | 1968190 | 621 | Distribution Circuit | Vegetation | Tree - fell into line | 186 | 77984 | 37.0665 | -122.0336 | No | Clear;32-90F | Crossarm- Wood | Broken | 23-0021424 | OH | Sus | 31635378 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1808184 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1105 | 182031105 | SWITCH | 736663 | 20230125 | 1723 | 20230125 | 1729 | 1968290 | 6 | Distribution Circuit | Company Initiated | Return Circuit Normal | 95 | 570 | 36.2308 | -121.1412 | No | Clear;32-90F | Switch (OH) | Normal | 23-0013213 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1808186 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | TRANSFORMER | 315746319602 | 20230125 | 1800 | 20230126 | 845 | 1968304 | 885 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 885 | 37.0287 | -121.9561 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0021450 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1808198 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 12601 | 20230125 | 2038 | 20230126 | 300 | 1968383 | 382 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 21010 | 37.1578 | -122.166 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0021462 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1808205 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | FUSE | 50971 | 20230126 | 35 | 20230126 | 149 | 1968420 | 74 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 444 | 36.8994 | -121.4249 | No | Clear;32-90F |  |  | 23-0021522 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1808260 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9181 | 20230126 | 723 | 20230126 | 1011 | 1968519 | 168 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 2352 | 37.2288 | -122.148 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0021645 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1808367 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | TRANSFORMER | 412533845382 | 20230126 | 840 | 20230126 | 1400 | 1968607 | 320 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1280 | 36.5533 | -121.5428 | No | Clear;32-90F | Cutout- fuse holder | Broken | 23-0021701 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1808395 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | TRANSFORMER | 412402053575 | 20230126 | 1027 | 20230126 | 1711 | 1968796 | 404 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 404 | 36.7766 | -121.5957 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0021775 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1808423 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | FUSE | 9879 | 20230126 | 1302 | 20230126 | 1428 | 1968951 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 86 | 36.3185 | -121.2117 | No | Clear;32-90F |  |  | 23-0021913 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1808464 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 316153620517 | 20230126 | 1650 | 20230126 | 1818 | 1969187 | 88 | Transformer only | Vegetation | Tree - fell into line | 4 | 352 | 37.0555 | -121.8192 | No | Clear;32-90F | Pole-Wood | Broken | 23-0022010 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1808481 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | FUSE | 24649 | 20230127 | 18 | 20230127 | 305 | 1969333 | 167 | Distribution Circuit | Equipment Failure/Involved | Overhead | 147 | 15639 | 36.676 | -121.6772 | No | Clear;32-90F | Crossarm- Wood | Broken | 23-0022075 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1808528 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1104 | 182201104 | TRANSFORMER | 412573547045 | 20230127 | 1000 | 20230127 | 1550 | 1969640 | 350 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 350 | 36.5988 | -121.5308 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0022190 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1808641 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 2645 | 20230127 | 1030 | 20230127 | 1951 | 1969727 | 561 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1122 | 37.0233 | -121.8293 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0022204 | OH | Sus | 45653017 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1808646 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | JUMPER | 3 POLE SS OF CGC 316717514270 | 20230127 | 1121 | 20230127 | 1433 | 1969643 | 192 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 768 | 36.8876 | -121.6248 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0022161 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1808622 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | JUMPER | 1 POLE W/OF CGC 315546321731 | 20230127 | 1213 | 20230127 | 1733 | 1969722 | 320 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 960 | 37.0866 | -122.0279 | No | Clear;32-90F | Pole-Wood | Deteriorated | 23-0022202 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1808645 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | TRANSFORMER | 412082141661 | 20230127 | 1246 | 20230127 | 1836 | 1969917 | 350 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 350 | 36.4467 | -121.6922 | No | Clear;32-90 F | Fuse | Broken | 23-0022549 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1808730 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | SWITCH | 11803 | 20230127 | 1318 | 20230127 | 1733 | 1969952 | 255 | Distribution Circuit | Equipment Failure/Involved | Overhead | 110 | 28050 | 37.0782 | -122.0318 | No | Clear;32-90F | Pole-Wood | Broken | 23-0022248 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1808692 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | FUSE | 2713 | 20230127 | 1354 | 20230127 | 2304 | 1969919 | 550 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2200 | 36.2534 | -121.7853 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0022501 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1808709 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | JUMPER | WIRE DOWN 1 P LD SIDE OF 6153 | 20230127 | 1412 | 20230128 | 1330 | 1970137 | 1398 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 12582 | 36.9996 | -121.774 | No | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0022540 | OH | Sus | 31635764 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | Yes | No | 1808722 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 7705 | 20230128 | 417 | 20230128 | 712 | 1970248 | 175 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 103 | 18025 | 36.9888 | -121.9976 | No | Clear;32-90F |  |  | 23-0022584 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1808760 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 2223 | 20230128 | 637 | 20230128 | 844 | 1970266 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1016 | 36.8319 | -121.7798 | No | Clear;32-90 F |  |  | 23-0022610 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1808797 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | FUSE | 23101 | 20230128 | 652 | 20230128 | 905 | 1970271 | 133 | Distribution Circuit | Animal | Bird found | 25 | 3282 | 36.5833 | -121.6319 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0022613 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1808804 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | RECLOSER | 3030 | 20230128 | 758 | 20230128 | 2233 | 1970276 | 875 | Distribution Circuit | 3rd Party | Vehicle | 155 | 11940 | 36.5854 | -121.6002 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0022600 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1808769 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 6799 | 20230128 | 1023 | 20230128 | 1228 | 1970384 | 125 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 83 | 36.9042 | -121.7191 | No | Clear;32-90 F |  |  | 23-0022633 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1808826 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | TRANSFORMER | 412082141661 | 20230128 | 1644 | 20230128 | 1800 | 1970639 | 76 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 76 | 36.4467 | -121.6922 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0022658 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1808847 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 23299 | 20230128 | 2131 | 20230129 | 47 | 1970736 | 196 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 227 | 44492 | 36.7693 | -121.7545 | No | Clear;32-90 F |  |  | 23-0022692 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1808886 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRIP-SAVER | 9031 | 20230129 | 239 | 20230129 | 522 | 1970775 | 163 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 48 | 7824 | 37.0726 | -122.0742 | No | Clear;32-90 F |  |  | 23-0022703 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1808899 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 8183 | 20230129 | 951 | 20230129 | 1211 | 1970898 | 140 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 2240 | 36.6072 | -121.9407 | No | Clear;32-90 F |  |  | 23-0022727 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1808926 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | TRANSFORMER | 411379747651 | 20230129 | 1224 | 20230129 | 2041 | 1970955 | 497 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 3976 | 36.6059 | -121.939 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0022729 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1808927 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 8643 | 20230129 | 1934 | 20230130 | 1205 | 1971187 | 991 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 6110 | 37.01 | -121.8859 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0022779 | OH | Sus | 45653598 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1808979 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | TRANSFORMER | 315662219097 | 20230130 | 829 | 20230130 | 1036 | 1971484 | 127 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 254 | 37.0156 | -121.9863 | No | Clear;32-90 F |  |  | 23-0022905 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1809169 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 6085 | 20230130 | 1145 | 20230130 | 1727 | 1971892 | 342 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 3762 | 37.0636 | -122.0348 | No | Clear;32-90 F |  |  | 23-0023174 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1809258 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | TRANSFORMER | 411995342217 | 20230130 | 1647 | 20230131 | 200 | 1972198 | 553 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 2212 | 36.4618 | -121.7236 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0023185 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1809261 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 4959 | 20230131 | 16 | 20230131 | 213 | 1972320 | 117 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 585 | 36.9637 | -121.8096 | No | Clear;32-90F | Jumper | Deteriorated | 23-0023221 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1809293 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | FUSE | 50951 | 20230131 | 844 | 20230131 | 1900 | 1972492 | 565 | Distribution Circuit | 3rd Party | Vehicle | 176 | 44789 | 36.9584 | -121.4301 | No | Clear;32-90F | Pole-Wood | Broken | 23-0023339 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1809428 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 9525 | 20230131 | 921 | 20230201 | 240 | 1972561 | 1039 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2078 | 37.0096 | -122.0104 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0023584 | OH | Sus | 45655407 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1809515 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SOLEDAD-2104 | 182052104 | TRANSFORMER | 100000035497 | 20230131 | 1334 | 20230131 | 2236 | 1972568 | 542 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 542 | 36.4558 | -121.4004 | No | Clear;32-90F | Jumper | Broken | 23-0023500 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1809497 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | FUSE | 24557 | 20230131 | 1359 | 20230131 | 1418 | 1973008 | 19 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 51 | 36.4888 | -121.4248 | No | Clear;32-90F |  |  | 23-0023537 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1809505 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | TRANSFORMER | 411920552261 | 20230131 | 1422 | 20230201 | 28 | 1972983 | 606 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 606 | 36.7375 | -121.7592 | No | Clear;32-90F | Cutout- fuse holder | Broken | 23-0023550 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1809506 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | TRANSFORMER | 315971517493 | 20230131 | 1609 | 20230201 | 40 | 1973131 | 511 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1533 | 36.9722 | -121.88 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0023663 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1809533 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 4135 | 20230201 | 44 | 20230201 | 152 | 1973359 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 108 | 7344 | 36.9256 | -121.3776 | No | Clear;32-90 F |  |  | 23-0023728 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1809579 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | FUSE | 9435 | 20230201 | 122 | 20230201 | 250 | 1973363 | 88 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 352 | 36.2692 | -121.1807 | No | Clear;32-90F | Pole-Wood | Broken | 23-0023726 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1809576 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | TRANSFORMER | 315912217347 | 20230201 | 830 | 20230202 | 136 | 1973536 | 1026 | Transformer only | 3rd Party | Tree - cutting- 3rd party | 5 | 5130 | 36.968 | -121.9001 | No | Clear;32-90F | Secondary | Broken | 23-0023812 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1809699 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316494813608 | 20230201 | 849 | 20230201 | 1821 | 1973592 | 572 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 1144 | 36.868 | -121.6996 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0023863 | OH | Sus | 35424565 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1809740 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | TRANSFORMER | T0384 | 20230201 | 958 | 20230202 | 640 | 1973732 | 1242 | Transformer only | Environmental/External | Water | 17 | 21114 | 36.9976 | -121.9752 | No | Clear;32-90 F | Cable Termination(live front | Normal | 23-0023864 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1809741 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | JUMPER | OJ @ CLIFF DR & FLORENCE DR | 20230201 | 1016 | 20230202 | 134 | 1973756 | 918 | Distribution Circuit | Vegetation | Tree - grew into line | 12 | 11016 | 36.9678 | -121.8998 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0023860 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1809739 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 8021 | 20230201 | 1325 | 20230201 | 1931 | 1974084 | 366 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 15450 | 36.5868 | -121.9097 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0024000 | OH | Sus | 31636126 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1809799 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411798951374 | 20230201 | 1345 | 20230202 | 348 | 1974172 | 843 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 843 | 36.7116 | -121.7988 | No | Clear;32-90 F | Transformer | Leaking | 23-0024064 | OH | Sus | 35424612 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1809808 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | TRANSFORMER | 412643845325 | 20230201 | 1731 | 20230201 | 2230 | 1974282 | 299 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 598 | 36.5523 | -121.5049 | No | Clear;32-90F | Jumper | Broken | 23-0024135 | OH | Sus | 45656827 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1809831 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411985850145 | 20230202 | 848 | 20230202 | 1357 | 1974583 | 309 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 309 | 36.6792 | -121.735 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0024326 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1810009 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1105 | 182031105 | TRANSFORMER | 413680633125 | 20230202 | 853 | 20230202 | 1058 | 1974491 | 125 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 125 | 36.224 | -121.1433 | No | Clear;32-90 F | Transformer | Burned/flashed | 23-0024297 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1809971 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | SWITCH | 1147 | 20230202 | 1010 | 20230202 | 1545 | 1973973 | 335 | Distribution Circuit | Vegetation | Tree - grew into line | 41 | 13735 | 36.9903 | -122.0266 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0024298 | OH | Sus | 45656607 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1809972 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 11305 | 20230202 | 1200 | 20230202 | 1333 | 1974943 | 93 | Distribution Circuit | Vegetation | Tree - grew into line | 13 | 1209 | 37.0308 | -121.7862 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0024442 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1810051 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | JUMPER | OJ 2 W/OF MTR#1010070793 | 20230202 | 1259 | 20230202 | 1740 | 1975031 | 281 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 281 | 36.7612 | -121.6072 | No | Clear;32-90F | Jumper | Burned Open | 23-0024488 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1810067 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | FUSE | 9435 | 20230202 | 1325 | 20230202 | 1519 | 1975012 | 114 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 456 | 36.2692 | -121.1807 | No | Clear;32-90F | Pole-Wood | Broken | 23-0024476 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1810064 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | OTHER | 1 WIRE DOWN 1 LD SIDE OF 6799 | 20230202 | 1532 | 20230203 | 310 | 1975196 | 698 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 24430 | 36.5896 | -121.9579 | No | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0024581 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1810091 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 4427 | 20230202 | 1713 | 20230203 | 939 | 1975290 | 986 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 3944 | 36.9666 | -121.8471 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0024646 | OH | Sus | 45657521 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1810121 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | TRANSFORMER | 315482817009 | 20230202 | 1952 | 20230203 | 1258 | 1975395 | 1026 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 6156 | 36.956 | -122.0457 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 23-0024657 | OH | Sus | 31636149 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1810130 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | RECLOSER | 563516 | 20230202 | 2154 | 20230202 | 2200 | 1975428 | 6 | Distribution Circuit | Vegetation | Tree - grew into line | 233 | 1398 | 36.5785 | -121.9279 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0024680 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1810152 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | FUSE | 7107 | 20230203 | 125 | 20230203 | 220 | 1975469 | 55 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 935 | 36.1984 | -120.7147 | No | Clear;32-90F | Anchor or Guy | Broken | 23-0024698 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1810166 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 1529 | 20230203 | 308 | 20230203 | 428 | 1975579 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 720 | 37.0317 | -121.9345 | No | Clear;32-90F |  |  | 23-0024716 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1810186 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 5351 | 20230203 | 558 | 20230203 | 1035 | 1975621 | 277 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 5540 | 37.0009 | -122.0209 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0024777 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1810232 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 7357 | 20230203 | 919 | 20230203 | 1325 | 1975803 | 246 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 858 | 37.0682 | -121.9831 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0024874 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1810316 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | KING CITY 1104 | 182031104 | FUSE | 7227 | 20230203 | 1122 | 20230203 | 1315 | 1975925 | 113 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 452 | 35.9778 | -121.2147 | No | Clear;32-90F |  |  | 23-0024999 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1810356 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1102 | 182011102 | OTHER | J229 TWD T0702 | 20230203 | 1158 | 20230203 | 1204 | 1975930 | 6 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 1 | 6 | 36.6906 | -121.627 | No | Overcast;32-90 F | Conductor- Underground | Normal | 23-0024913 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1810326 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 3977 | 20230203 | 1223 | 20230203 | 1415 | 1975998 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 112 | 36.9046 | -121.7552 | No | Clear;32-90F |  |  | 23-0025020 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1810365 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | TRANSFORMER | 412155552202 | 20230204 | 1029 | 20230204 | 1657 | 1976552 | 388 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 388 | 36.737 | -121.6787 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0025195 | OH | Sus | 35424919 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1810502 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | RECLOSER | 4470 | 20230204 | 1158 | 20230204 | 1305 | 1976615 | 67 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1195 | 80065 | 36.8638 | -121.3637 | No | Clear;32-90F | Crossarm- Wood | Broken | 23-0025200 | OH | Sus | 31636304 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1810510 | 0 | EPSS Ckt | N | 2023 | A-B
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 347 | 20230204 | 1200 | 20230204 | 1315 | 1976616 | 75 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 30 | 2248 | 36.988 | -121.9426 | No | Overcast;32-90 F |  |  | 23-0025216 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1810525 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-1101 | 182221101 | RECLOSER | 38582 | 20230204 | 1255 | 20230204 | 1301 | 1976651 | 6 | Distribution Circuit | Equipment Failure/Involved | Overhead | 746 | 4476 | 36.6191 | -121.8249 | No | Clear;32-90F | Insulator | Broken | 23-0025208 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1810518 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 10229 | 20230204 | 1341 | 20230204 | 1426 | 1976704 | 45 | Distribution Circuit | Animal | Bird found | 3 | 150 | 36.9906 | -121.9422 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0025222 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1810533 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 12124 | 20230204 | 1541 | 20230205 | 943 | 1976724 | 1082 | Distribution Circuit | Vegetation | Tree - fell into line | 480 | 92359 | 37.1677 | -122.1662 | No | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0025226 | OH | Sus | 35425017 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1810537 | 0 | EPSS Ckt | N | 2023 | B- GRD
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 8951 | 20230204 | 1752 | 20230204 | 1814 | 1976780 | 22 | Distribution Circuit | Vegetation | Tree - grew into line | 50 | 1100 | 36.5674 | -121.9158 | No | Overcast-Drizzle;32-90 F | Secondary | Normal | 23-0025251 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1810552 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 974520 | 20230204 | 1937 | 20230204 | 2109 | 1976889 | 92 | Distribution Circuit | Vegetation | Tree - fell into line | 330 | 30360 | 36.9908 | -121.8063 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0025265 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1810567 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | RECLOSER | 94074 | 20230204 | 2126 | 20230205 | 1237 | 1977069 | 911 | Distribution Circuit | Equipment Failure/Involved | Overhead | 959 | 68332 | 36.5998 | -121.8904 | No | Overcast-Rain;32-90 F | Crossarm- Wood | Burned/flashed | 23-0025290 | OH | Sus | 35424877 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1810592 | 0 | EPSS Ckt | N | 2023 | A GRD
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | OCB | 2101/2 | 20230204 | 2152 | 20230205 | 1857 | 1977089 | 1265 | Distribution Circuit | Vegetation | Tree - bark fell into line | 2327 | 221195 | 37.0953 | -122.1437 | No | Clear;32-90F | Conductor- Overhead | Bent or Twisted | 23-0025296 | OH | Sus | 45658905 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1810598 | 0 | EPSS Ckt | N | 2023 | PH OC
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | JUMPER | 4197 | 20230204 | 2222 | 20230205 | 933 | 1977111 | 671 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 3338 | 36.7336 | -121.3845 | No | Clear;32-90F | Jumper | Burned Open | 23-0025320 | OH | Sus | 45658921 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1810624 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | RECLOSER | 42226 | 20230205 | 240 | 20230205 | 340 | 1977179 | 60 | Distribution Circuit | 3rd Party | Vehicle | 429 | 25740 | 36.5834 | -121.8569 | No | Clear;32-90F | Pole-Wood | Normal | 23-0025324 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1810627 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 12503 | 20230205 | 921 | 20230206 | 1145 | 1977395 | 0 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1584 | 37.0036 | -121.765 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0025381 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1810674 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | FUSE | 3699 | 20230205 | 945 | 20230205 | 1151 | 1977366 | 126 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 4448 | 36.9968 | -121.9371 | No | Clear;32-90F |  |  | 23-0025395 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1810688 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD 1101 | 182731101 | FUSE | 3971 | 20230205 | 1526 | 20230205 | 1627 | 1977550 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 79 | 4819 | 36.5948 | -121.7026 | No | Clear;32-90F |  |  | 23-0025430 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1810717 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 316067916182 | 20230205 | 2014 | 20230206 | 1325 | 1977709 | 1031 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1031 | 36.9364 | -121.8465 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0025526 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1810809 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | OCB | 2101/2 | 20230205 | 2046 | 20230206 | 1140 | 1977716 | 894 | Distribution Circuit | Vegetation | Tree - fell into line | 2327 | 139012 | 37.0953 | -122.1437 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0025475 | OH | Sus | 45658933 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1810759 | 0 | EPSS Ckt | N | 2023 | C GRD TIME
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 5217 | 20230206 | 656 | 20230206 | 945 | 1977862 | 169 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 2535 | 37.0373 | -122.0664 | No | Clear;32-90F |  |  | 23-0025619 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1810940 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 2455 | 20230206 | 742 | 20230206 | 1425 | 1977880 | 403 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 9672 | 37.0111 | -121.9871 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0025628 | OH | Sus | 45659348 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1810955 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | TRANSFORMER | 414281626915 | 20230206 | 839 | 20230206 | 1429 | 1977973 | 350 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 350 | 36.0569 | -120.9357 | No | Clear;32-90F | Secondary | Burned/flashed | 23-0025791 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1811017 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | FUSE | 2545 | 20230206 | 1608 | 20230207 | 241 | 1978547 | 633 | Distribution Circuit | Environmental/External | Flood/Erosion | 6 | 3234 | 36.2268 | -121.7603 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0025884 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1811036 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | SWITCH | 10987 | 20230206 | 1643 | 20230206 | 2205 | 1978494 | 322 | Distribution Circuit | Vegetation | Tree - fell into line | 984 | 49451 | 37.1149 | -121.9873 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0025895 | OH | Sus | 45659603 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1811038 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 445933 | 20230207 | 945 | 20230207 | 1419 | 1979013 | 274 | Distribution Circuit | Vegetation | Tree - branch fell on line | 56 | 9296 | 37.1372 | -122.1004 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0026094 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1811232 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | TRANSFORMER | 412192552658 | 20230207 | 1110 | 20230207 | 2017 | 1979171 | 547 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 2188 | 36.7504 | -121.6681 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0026258 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1811324 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 4415 | 20230207 | 1200 | 20230207 | 1221 | 1979247 | 21 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 21 | 36.7765 | -121.6952 | No | Clear;32-90 F |  |  | 23-0026239 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1811316 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1101 | 182131101 | TRANSFORMER | 412823044300 | 20230207 | 1229 | 20230208 | 204 | 1979028 | 815 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 815 | 36.5253 | -121.4437 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0026246 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1811319 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 12947 | 20230207 | 1411 | 20230208 | 303 | 1979340 | 772 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 4632 | 37.0128 | -122.0307 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0026358 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1811353 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 412027850630 | 20230207 | 1520 | 20230207 | 2213 | 1979412 | 413 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 413 | 36.693 | -121.7211 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0026362 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1811355 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | JUMPER | OJ 4 LD SIDE OF 3345 | 20230207 | 1530 | 20230207 | 2313 | 1979622 | 463 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 3241 | 36.7205 | -121.6173 | No | Clear;32-90 F | Jumper | Burned Open | 23-0026487 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1811415 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | TRANSFORMER | 316235213158 | 20230207 | 2309 | 20230208 | 212 | 1979618 | 183 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 366 | 36.8542 | -121.7881 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0026484 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1811413 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 52559 | 20230208 | 647 | 20230208 | 845 | 1979706 | 118 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 1180 | 36.8343 | -121.6603 | No | Clear;32-90 F |  |  | 23-0026558 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1811519 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SOLEDAD-2101 | 182052101 | TRANSFORMER | 413165040825 | 20230208 | 925 | 20230208 | 1101 | 1979906 | 96 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 1248 | 36.4321 | -121.3246 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 23-0020055 | OH | Sus | 31619764 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1811582 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | FUSE | 9655 | 20230208 | 1400 | 20230208 | 1546 | 1980113 | 106 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 3074 | 36.8999 | -121.5907 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0026682 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1811633 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1106 | 182031106 | FUSE | 7433 | 20230208 | 1709 | 20230208 | 1848 | 1980309 | 99 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 528 | 36.1909 | -120.9902 | No | Clear;32-90 F |  |  | 23-0026861 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1811675 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1101 | 182131101 | FUSE | 7603 | 20230208 | 1710 | 20230209 | 1537 | 1980315 | 1347 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 2694 | 36.5397 | -121.3991 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0026832 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1811662 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | TRANSFORMER | 411671047415 | 20230208 | 1733 | 20230209 | 15 | 1980325 | 402 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1206 | 36.6024 | -121.8389 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0026860 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1811674 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | TRANSFORMER | 315561119401 | 20230208 | 2121 | 20230209 | 224 | 1980398 | 303 | Transformer only | Animal | Bird found | 4 | 1212 | 37.0228 | -122.021 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0026902 | OH | Sus | 45661255 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1811709 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | TRANSFORMER | 412952255148 | 20230209 | 232 | 20230209 | 850 | 1980430 | 378 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 756 | 36.8235 | -121.4093 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0026906 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1811712 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6549 | 20230209 | 537 | 20230209 | 819 | 1980442 | 162 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 97 | 15714 | 36.8545 | -121.6393 | No | Clear;32-90 F |  |  | 23-0026965 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1811757 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | FUSE | 5233 | 20230209 | 637 | 20230209 | 947 | 1980465 | 190 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 91 | 17290 | 36.5694 | -121.7079 | No | Clear;32-90 F |  |  | 23-0026951 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1811737 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | FUSE | 2713 | 20230209 | 1314 | 20230209 | 1908 | 1981045 | 354 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 5862 | 36.2534 | -121.7853 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0027161 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1811948 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | RECLOSER | 428102 | 20230209 | 1518 | 20230209 | 1524 | 1981153 | 6 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 179 | 1074 | 36.9976 | -121.9515 | No | Clear;32-90 F |  |  | 23-0027247 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1811966 | 0 | EPSS Ckt | N | 2023 | B & GRD
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 411835155408 | 20230209 | 1552 | 20230210 | 210 | 1981379 | 618 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 618 | 36.824 | -121.7904 | No | Clear;32-90F | Transformer (OH) | Leaking | 23-0027353 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1812023 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316394617060 | 20230209 | 1711 | 20230209 | 1855 | 1981247 | 104 | Transformer only | 3rd Party | Other | 6 | 624 | 36.962 | -121.7351 | No | Clear;32-90 F | Service conductor | Normal | 23-0027315 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1811993 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 351054 | 20230209 | 2101 | 20230209 | 2224 | 1981348 | 83 | Distribution Circuit | Equipment Failure/Involved | Overhead | 732 | 60756 | 37.1971 | -122.1542 | No | Clear;32-90F | Recloser | Malfunctioning | 23-0027349 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1812019 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 2815 | 20230210 | 920 | 20230210 | 1415 | 1981476 | 295 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1770 | 37.0535 | -121.9782 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0027490 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1812176 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | SWITCH | 3154 | 20230210 | 1114 | 20230214 | 1515 | 1981798 | 6001 | Distribution Circuit | Equipment Failure/Involved | Underground | 184 | 12223 | 36.7255 | -121.6496 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0027508 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1812219 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | TRANSFORMER | 411796450142 | 20230210 | 1956 | 20230210 | 2130 | 1982134 | 94 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 1222 | 36.6778 | -121.7994 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 23-0027759 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1812317 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 1491 | 20230210 | 2210 | 20230211 | 111 | 1982163 | 181 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 40 | 7240 | 36.5057 | -121.9352 | No | Clear;32-90F |  |  | 23-0027774 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1812330 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2103 | 182492103 | FUSE | 4103 | 20230210 | 2226 | 20230211 | 1507 | 1982167 | 1001 | Distribution Circuit | 3rd Party | Vehicle | 99 | 12343 | 36.9433 | -121.4117 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 23-0027767 | OH | Sus | 35426101 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | Yes | No | 1812323 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 2199 | 20230210 | 2322 | 20230211 | 749 | 1982178 | 507 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 14196 | 36.9517 | -121.834 | No | Clear;32-90 F |  |  | 23-0027796 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1812349 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 6799 | 20230211 | 908 | 20230211 | 2045 | 1982297 | 697 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 24395 | 36.5903 | -121.9583 | No | Clear;32-90F | Pole-Wood | Broken | 23-0027812 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1812391 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | TRES PINOS 1111 | 183221111 | TRANSFORMER | MTR#1008836655 | 20230211 | 1315 | 20230211 | 1339 | 1982465 | 24 | Transformer only | Animal | Bird found | 1 | 24 | 36.7873 | -121.3673 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0027843 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1812431 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 3929 | 20230211 | 1404 | 20230211 | 1415 | 1982469 | 11 | Distribution Circuit | Vegetation | Tree - branch fell on line | 32 | 352 | 36.7891 | -121.6748 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0027849 | OH | Sus | 45668646 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1812435 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 6799 | 20230211 | 2156 | 20230213 | 1417 | 1982684 | 2421 | Distribution Circuit | Equipment Failure/Involved | Underground | 35 | 65350 | 36.5903 | -121.9583 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0027893 | UG | Sus | 31636660 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1812481 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 5955 | 20230212 | 54 | 20230212 | 351 | 1982719 | 177 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 167 | 29559 | 37.0022 | -121.942 | No | Clear;32-90F |  |  | 23-0027896 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1812485 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 9215 | 20230212 | 1242 | 20230212 | 1330 | 1982932 | 48 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 336 | 36.8586 | -121.6488 | No | Clear;32-90F |  |  | 23-0027934 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1812529 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 2835 | 20230212 | 1937 | 20230212 | 2320 | 1983099 | 223 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 7206 | 36.5861 | -121.8751 | No | Clear;32-90 F |  |  | 23-0027984 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1812580 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | OTHER | 1 MAINLINE WIRE DOWN @ 1789 | 20230212 | 1946 | 20230213 | 722 | 1983103 | 696 | Distribution Circuit | Equipment Failure/Involved | Overhead | 148 | 97390 | 36.9928 | -121.8132 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0027963 | OH | Sus | 45670075 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1812560 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 4135 | 20230213 | 205 | 20230213 | 420 | 1983188 | 135 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 107 | 14445 | 36.9256 | -121.3776 | No | Clear;32-90F |  |  | 23-0027998 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1812593 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 10369 | 20230213 | 448 | 20230213 | 513 | 1983200 | 25 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 750 | 36.5834 | -121.8792 | No | Clear;32-90F |  |  | 23-0027999 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1812594 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | OTHER | 1 WIRE DOWN SOURCE SIDE OF 9707 | 20230213 | 748 | 20230214 | 218 | 1983502 | 1110 | Distribution Circuit | Equipment Failure/Involved | Overhead | 314 | 58950 | 36.0533 | -120.9158 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0028092 | OH | Sus | 31636651 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1812747 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | FORT ORD-2107 | 182402107 | FUSE | 7141 | 20230213 | 915 | 20230213 | 934 | 1983374 | 19 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 874 | 36.6868 | -121.7957 | No | Clear;32-90 F | Cutout- fuse holder | Arcing | 23-0028064 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1812688 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411955153274 | 20230213 | 1925 | 20230214 | 126 | 1984083 | 361 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 2527 | 36.7656 | -121.7476 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0028351 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1812909 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 679 | 20230213 | 2000 | 20230214 | 308 | 1983114 | 428 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 5136 | 36.8624 | -121.6651 | No | Clear;32-90 F |  |  | 23-0027997 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1812592 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2102 | 182222102 | TRANSFORMER | 411648447878 | 20230213 | 2152 | 20230214 | 645 | 1984237 | 533 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 2665 | 36.6142 | -121.8472 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0028387 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1812941 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 6085 | 20230214 | 1308 | 20230214 | 1626 | 1984956 | 198 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 2178 | 37.0636 | -122.0348 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0028890 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1813249 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | OTHER | 555726 | 20230214 | 1325 | 20230214 | 2016 | 1985043 | 411 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1172 | 106702 | 37.0858 | -122.0674 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0028768 | OH | Sus | 45672040 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1813210 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | TRANSFORMER | 411458048137 | 20230214 | 1330 | 20230214 | 1415 | 1985058 | 45 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 675 | 36.6198 | -121.9129 | No | Clear-Strong Winds;32-90 F | Transformer (OH) | Failed/Faulted | 23-0028787 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1813213 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 4261 | 20230214 | 1653 | 20230215 | 100 | 1985325 | 487 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 8512 | 36.8091 | -121.6604 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0028926 | OH | Sus | 31636677 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1813274 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | JUMPER | BURNT OPEN B PHASE JUMPER 5 S/W/OF 7163 | 20230214 | 2035 | 20230216 | 325 | 1985497 | 1850 | Distribution Circuit | Equipment Failure/Involved | Overhead | 108 | 199282 | 36.3684 | -121.1035 | No | Clear;32-90 F | Jumper | Burned Open | 23-0028958 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1813297 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 737 | 20230215 | 120 | 20230215 | 1130 | 1985628 | 610 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 59 | 32350 | 37.0046 | -121.8551 | No | Clear;32-90F |  |  | 23-0028983 | OH | Sus | 45671984 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1813322 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | JUMPER | BURNT OJ LD SIDE OF 2249 | 20230215 | 133 | 20230215 | 715 | 1985647 | 342 | Distribution Circuit | Equipment Failure/Involved | Overhead | 177 | 60534 | 36.5968 | -121.8551 | No | Clear;32-90 F | Jumper | Burned Open | 23-0028980 | OH | Sus | 31636903 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1813319 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | FUSE | 50953 | 20230215 | 625 | 20230215 | 834 | 1985680 | 129 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 774 | 36.96 | -121.4309 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0029005 | OH | Sus | 45671985 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1813337 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | FUSE | 5233 | 20230215 | 629 | 20230215 | 830 | 1985684 | 121 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 91 | 11011 | 36.5694 | -121.7079 | No | Clear;32-90 F |  |  | 23-0029060 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1813401 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | FUSE | 23833 | 20230215 | 924 | 20230215 | 1028 | 1985960 | 64 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 64 | 36.7327 | -121.6739 | No | Clear;32-90 F |  |  | 23-0029145 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1813494 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | FORT ORD-2107 | 182402107 | SWITCH | 40073 | 20230215 | 1153 | 20230215 | 1842 | 1986124 | 409 | Distribution Circuit | 3rd Party | Vehicle | 45 | 18405 | 36.6725 | -121.766 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0029243 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1813521 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | INDUSTRIAL ACRES-0413 | 182300413 | TRANSFORMER | 412275149708 | 20230215 | 1459 | 20230215 | 1906 | 1986287 | 247 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 2223 | 36.6696 | -121.6356 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0029360 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1813554 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | INDUSTRIAL ACRES-0413 | 182300413 | TRANSFORMER | 412280349684 | 20230215 | 1501 | 20230215 | 1906 | 1986289 | 245 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 1715 | 36.6689 | -121.6338 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0029365 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1813555 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRIP-SAVER | 6601 | 20230215 | 2102 | 20230216 | 244 | 1986296 | 342 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 11970 | 36.9942 | -121.7176 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0029456 | OH | Sus | 45672775 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1813586 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315737020500 | 20230215 | 2135 | 20230215 | 2246 | 1986526 | 71 | Transformer only | 3rd Party | Vehicle | 1 | 71 | 37.0541 | -121.9619 | No | Clear;32-90F | Fuse | Normal | 23-0029499 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1813615 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | FORT ORD-2107 | 182402107 | FUSE | 2543 | 20230215 | 2136 | 20230216 | 1441 | 1986511 | 1025 | Distribution Circuit | Equipment Failure/Involved | Underground | 10 | 9898 | 36.6744 | -121.7826 | No | Clear;32-90F | Conductor- Underground | Broken | 23-0029497 | UG | Sus | 31636866 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1813613 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | FUSE | 1839 | 20230216 | 712 | 20230216 | 1243 | 1986605 | 331 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1324 | 36.9893 | -121.9789 | No | Clear;32-90F | Pothead(Riser Termination) | Broken | 23-0029597 | OH | Sus | 31636890 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1813712 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO-1101 | 182191101 | TRANSFORMER | 413886529485 | 20230216 | 1041 | 20230216 | 1446 | 1986846 | 245 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 245 | 36.1258 | -121.072 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0029666 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1813746 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | FUSE | 59387 | 20230216 | 1202 | 20230216 | 1845 | 1986872 | 403 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 5239 | 36.6825 | -121.5641 | No | Clear;32-90F | Pole-Wood | Deteriorated | 23-0029661 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1813747 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | RECLOSER | 606732 | 20230216 | 1517 | 20230217 | 135 | 1987096 | 618 | Distribution Circuit | 3rd Party | Vehicle | 31 | 19158 | 36.3304 | -121.258 | No | Clear;32-90F | Pole-Wood | Broken | 23-0029831 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1813777 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRANSFORMER | 315232124397 | 20230216 | 1544 | 20230217 | 137 | 1987138 | 593 | Transformer only | Vegetation | Tree - fell into line | 1 | 593 | 37.159 | -122.1343 | No | Clear;32-90F | Transformer (OH) | Broken- wire on ground | 23-0029916 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1813795 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412309254637 | 20230217 | 743 | 20230217 | 1601 | 1987347 | 498 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 498 | 36.805 | -121.6289 | No | Clear;32-90F | Conductor- Underground | Broken | 23-0030093 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1813985 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRANSFORMER | 315236624334 | 20230217 | 1246 | 20230217 | 1353 | 1987753 | 67 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 268 | 37.1571 | -122.1328 | No | Clear;32-90F | Secondary | Broken | 23-0030282 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1814045 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 8033 | 20230217 | 1710 | 20230218 | 1200 | 1987844 | 1130 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 9040 | 37.1035 | -122.2771 | No | Clear;32-90F | Conductor- Overhead | Together | 23-0030321 | OH | Sus | 45678248 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1814055 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 5725 | 20230217 | 1838 | 20230217 | 2355 | 1987938 | 317 | Distribution Circuit | Vegetation | Tree - grew into line | 14 | 4438 | 36.9902 | -121.7368 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0030331 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1814058 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1104 | 182201104 | TRANSFORMER | 412603046050 | 20230218 | 1018 | 20230218 | 1552 | 1988184 | 334 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 2004 | 36.5718 | -121.5198 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0030465 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1814197 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 6359 | 20230218 | 1500 | 20230218 | 1636 | 1988289 | 96 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 61 | 5856 | 36.8676 | -121.7489 | No | Clear;32-90F |  |  | 23-0030481 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1814213 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9597 | 20230219 | 1058 | 20230219 | 1356 | 1988593 | 178 | Distribution Circuit | Vegetation | Tree - grew into line | 5 | 890 | 37.1442 | -122.0895 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0030532 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1814282 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 1495 | 20230219 | 1725 | 20230219 | 1838 | 1989024 | 73 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 219 | 36.9762 | -121.7445 | Yes | Clear;32-90F |  |  | 23-0030572 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1814323 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316268318801 | 20230220 | 329 | 20230220 | 1430 | 1989163 | 661 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1322 | 37.0097 | -121.7795 | No | Clear;32-90F | Service conductor | Broken | 23-0030603 | OH | Sus | 45678909 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1814356 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 4339 | 20230220 | 731 | 20230220 | 855 | 1989195 | 84 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 1344 | 36.7945 | -121.7034 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0030625 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1814430 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 737512 | 20230220 | 1936 | 20230221 | 110 | 1989635 | 334 | Distribution Circuit | Equipment Failure/Involved | Overhead | 918 | 15960 | 37.0467 | -122.074 | No | Clear;32-90 F | Bushing | Arcing | 23-0030726 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1814501 | 0 | EPSS Ckt | N | 2023 | NA
CENTRAL COAST | KING CITY | OILFIELDS 1102 | 182391102 | FUSE | 559 | 20230221 | 746 | 20230221 | 1658 | 1989768 | 552 | Distribution Circuit | 3rd Party | Vehicle | 16 | 8832 | 35.9793 | -120.8779 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0030844 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | Yes | 1814641 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | JUMPER | BURNT OPEN JUMPER @ 2375 | 20230221 | 800 | 20230221 | 1525 | 1989777 | 445 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1335 | 36.5691 | -121.7851 | Yes | Clear;32-90F | Jumper | Burned Open | 23-0030941 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1814728 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | FUSE | 7169 | 20230221 | 1002 | 20230222 | 1335 | 1990056 | 1653 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 8 | 13761 | 36.4105 | -120.9532 | Yes | Clear;32-90 F |  |  | 23-0031609 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815230 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 81927 | 20230221 | 1100 | 20230221 | 1225 | 1990134 | 85 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 1105 | 37.0844 | -122.0889 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0031007 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1814758 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | RECLOSER | BL 1101 | 20230221 | 1224 | 20230224 | 2056 | 1990315 | 4832 | Distribution Circuit | Vegetation | Tree - fell into line | 621 | 2598624 | 37.0926 | -122.0966 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031021 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1814764 | 0 | EPSS Ckt | N | 2023 | A & C PHASE
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | FUSE | 688471 | 20230221 | 1224 | 20230224 | 2056 | 1992326 | 4832 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 82144 | 37.1101 | -122.1102 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0031338 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1814993 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | FUSE | 5183 | 20230221 | 1224 | 20230224 | 2056 | 2005334 | 4832 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 154624 | 37.108 | -122.1098 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034101 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1817045 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | FUSE | 509805 | 20230221 | 1224 | 20230225 | 1052 | 2005370 | 5668 | Distribution Circuit | Vegetation | Tree - branch fell on line | 39 | 221052 | 37.107 | -122.1096 | Yes | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0034108 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1817051 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | TRANSFORMER | 413483034155 | 20230221 | 1227 | 20230221 | 1427 | 1990504 | 120 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 120 | 36.2518 | -121.2151 | Yes | Partly Cloudy;32-90 F | Transformer | Normal | 23-0031191 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1814880 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRIP-SAVER | 9031 | 20230221 | 1233 | 20230223 | 1806 | 1990344 | 3213 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 67473 | 37.0726 | -122.0742 | Yes | Clear;32-90 F |  |  | 23-0031239 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1814910 | 0 | EPSS Ckt | N | 2023 | A PHASE
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | SWITCH | 9033 | 20230221 | 1233 | 20230223 | 1806 | 1998020 | 3213 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 86751 | 37.0722 | -122.0754 | Yes | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0032521 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815954 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 9691 | 20230221 | 1252 | 20230223 | 1621 | 1997751 | 3089 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 52513 | 37.095 | -122.1387 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0032401 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815879 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5447 | 20230221 | 1258 | 20230224 | 1924 | 1998487 | 4706 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 127062 | 37.1305 | -122.1348 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032690 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816073 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 445933 | 20230221 | 1321 | 20230224 | 1720 | 1990666 | 4559 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 169064 | 37.1372 | -122.1004 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031099 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1814810 | 0 | EPSS Ckt | N | 2023 | A & C
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9181 | 20230221 | 1321 | 20230223 | 1618 | 1990613 | 3057 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 42798 | 37.2288 | -122.148 | Yes | Clear;32-90 F |  |  | 23-0033308 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816387 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 8259 | 20230221 | 1322 | 20230228 | 1510 | 2008556 | 10138 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 182484 | 37.1594 | -122.1269 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035272 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818110 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 5188 | 20230221 | 1338 | 20230223 | 1806 | 1990865 | 3148 | Distribution Circuit | Vegetation | Tree - fell into line | 914 | 2876072 | 37.0757 | -122.0568 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031258 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1814923 | 0 | EPSS Ckt | N | 2023 | A & B PHASE
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | TRIP-SAVER | 25695 | 20230221 | 1338 | 20230221 | 2225 | 1990813 | 527 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 105 | 55187 | 36.7493 | -121.6573 | Yes | Clear;32-90F |  |  | 23-0031932 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815531 | 1 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | MONTEREY | FORT ORD-2106 | 182402106 | TRANSFORMER | 411750848380 | 20230221 | 1339 | 20230222 | 35 | 1990826 | 656 | Transformer only | Vegetation | Tree - fell into line | 8 | 5248 | 36.6296 | -121.8122 | Yes | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0031453 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815089 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | JUMPER | UN NUMBERED SBCO AT JACKSON AND COUNTRY CLUB | 20230221 | 1341 | 20230226 | 1111 | 1994942 | 7050 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 70059 | 37.0819 | -122.096 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031713 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815320 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | SWITCH | 383371 | 20230221 | 1341 | 20230226 | 1008 | 1998237 | 6987 | Distribution Circuit | Vegetation | Tree - fell into line | 105 | 733635 | 37.084 | -122.0886 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0032596 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816010 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1104 | 182201104 | FUSE | 269299 | 20230221 | 1355 | 20230222 | 1722 | 1991121 | 1647 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 21411 | 36.6108 | -121.5492 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0031424 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815060 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 39126 | 20230221 | 1358 | 20230225 | 1845 | 1991168 | 6047 | Distribution Circuit | Vegetation | Tree - branch fell on line | 307 | 1452509 | 37.0778 | -122.1322 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0031147 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | Yes | No | 1814846 | 0 | EPSS Ckt | N | 2023 | ABC GRD
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | TRIP-SAVER | 5401 | 20230221 | 1358 | 20230225 | 1742 | 2000082 | 5984 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 269280 | 37.0647 | -122.1232 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033343 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816405 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 11737 | 20230221 | 1358 | 20230225 | 1742 | 2005457 | 5984 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 143616 | 37.0695 | -122.1302 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034130 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1817064 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRIP-SAVER | 9773 | 20230221 | 1404 | 20230223 | 2015 | 1991229 | 3251 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 94279 | 37.1288 | -122.1143 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0033424 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816457 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 5090 | 20230221 | 1407 | 20230221 | 1445 | 1991279 | 38 | Distribution Circuit | Equipment Failure/Involved | Overhead | 325 | 12350 | 36.9804 | -121.892 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0031165 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1814859 | 0 | EPSS Ckt | N | 2023 | B GRD
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 6121 | 20230221 | 1407 | 20230221 | 2326 | 1991849 | 559 | Distribution Circuit | Equipment Failure/Involved | Overhead | 109 | 60931 | 36.9835 | -121.8848 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031165 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1814938 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 11967 | 20230221 | 1408 | 20230224 | 1253 | 1995927 | 4245 | Distribution Circuit | Vegetation | Tree - branch fell on line | 31 | 131595 | 37.029 | -122.0723 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031865 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1815463 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 866599 | 20230221 | 1408 | 20230222 | 1642 | 1998097 | 1594 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 14346 | 37.0352 | -122.0646 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0032556 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815976 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315420020038 | 20230221 | 1408 | 20230223 | 521 | 1998234 | 2353 | Transformer only | Vegetation | Tree - fell into line | 5 | 11765 | 37.0396 | -122.0702 | Yes | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0032595 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816009 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | JUMPER | OJ JNO CGC 315359219706 | 20230221 | 1408 | 20230226 | 1703 | 1998402 | 7375 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 7375 | 37.0309 | -122.0916 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032659 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1816052 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 12124 | 20230221 | 1409 | 20230223 | 1042 | 1991330 | 2673 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 431 | 1152063 | 37.1677 | -122.1662 | Yes | Clear;32-90 F |  |  | 23-0031180 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1814872 | 0 | EPSS Ckt | N | 2023 | B & GRD
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | JUMPER | OJ 1 SPAN N/OF CGC 315159224218 | 20230221 | 1409 | 20230226 | 1726 | 1997811 | 7397 | Distribution Circuit | Vegetation | Tree - fell into line | 139 | 17397 | 37.1536 | -122.1623 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0032425 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815890 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9753 | 20230221 | 1409 | 20230225 | 1543 | 1998129 | 5854 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 87810 | 37.1656 | -122.1639 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0032569 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1815991 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | JUMPER | OJ W/O CGC 315170524755 | 20230221 | 1409 | 20230225 | 1544 | 1998165 | 5855 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 40985 | 37.168 | -122.159 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0032578 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1815998 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 8021 | 20230221 | 1409 | 20230224 | 1703 | 1998313 | 4494 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 107856 | 37.1635 | -122.1621 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032625 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816028 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 12069 | 20230221 | 1412 | 20230223 | 1835 | 1991334 | 3143 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 103719 | 37.1239 | -122.1197 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0033391 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816431 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRIP-SAVER | 6219 | 20230221 | 1413 | 20230228 | 1650 | 2010360 | 10237 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 225214 | 37.1841 | -122.1409 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035839 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1818663 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 6085 | 20230221 | 1414 | 20230222 | 1857 | 1991350 | 1723 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 18953 | 37.0636 | -122.0348 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0032700 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816083 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9319 | 20230221 | 1415 | 20230227 | 1335 | 2010187 | 8600 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 17200 | 37.171 | -122.1373 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0035771 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1818601 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | FUSE | 837 | 20230221 | 1415 | 20230223 | 2255 | 1991367 | 3400 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 105400 | 37.038 | -121.9667 | Yes | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0031408 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815046 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | JUMPER | WIRE DOWN @ 7537 | 20230221 | 1416 | 20230222 | 1247 | 1991432 | 1351 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 16020 | 36.572 | -121.9056 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0031291 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1814950 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 4319 | 20230221 | 1418 | 20230222 | 1011 | 1991670 | 1193 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 96633 | 36.8349 | -121.725 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0031689 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | No | No | 1815299 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | FUSE | 3971 | 20230221 | 1424 | 20230221 | 1502 | 1991474 | 36 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 79 | 2844 | 36.5948 | -121.7026 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0031312 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1814965 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 35874 | 20230221 | 1426 | 20230224 | 1940 | 1991431 | 4634 | Distribution Circuit | Equipment Failure/Involved | Overhead | 487 | 244366 | 37.0312 | -122.1882 | Yes | Clear;32-90 F | Insulator | Broken | 23-0031154 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1814902 | 0 | EPSS Ckt | N | 2023 | B-C
CENTRAL COAST | SALINAS | SPENCE-1104 | 182201104 | FUSE | 23229 | 20230221 | 1427 | 20230221 | 1630 | 1991674 | 123 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 820 | 36.6146 | -121.5436 | Yes | Clear;32-90 F |  |  | 23-0031497 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815127 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1101 | 182011101 | FUSE | 24601 | 20230221 | 1430 | 20230221 | 1607 | 1991814 | 97 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 49 | 4753 | 36.6751 | -121.6456 | Yes | Clear;32-90 F |  |  | 23-0031395 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815035 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 601610 | 20230221 | 1434 | 20230228 | 1612 | 1991816 | 10178 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 388077 | 37.1117 | -122.0207 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031250 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1814931 | 0 | EPSS Ckt | N | 2023 | BC
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 2517 | 20230221 | 1434 | 20230228 | 1635 | 2012182 | 10201 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 40804 | 37.1361 | -122.0272 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0036359 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1819027 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 4285 | 20230221 | 1434 | 20230302 | 1730 | 2012203 | 13136 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 207969 | 37.1346 | -122.0242 | Yes |  | Conductor- Overhead | Broken- wire on ground | 23-0036369 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1819032 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6819 | 20230221 | 1439 | 20230221 | 1645 | 1992848 | 126 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 4662 | 36.9962 | -121.8656 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0031427 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815061 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 2287 | 20230221 | 1439 | 20230224 | 1513 | 1991778 | 4354 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 91434 | 36.9502 | -121.829 | Yes | Clear;32-90 F |  |  | 23-0034262 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1817154 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 1427 | 20230221 | 1442 | 20230226 | 1031 | 1999190 | 6949 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 382195 | 37.0823 | -122.0914 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033003 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816238 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | OCB | 2101/2 | 20230221 | 1443 | 20230223 | 2050 | 1991842 | 3247 | Distribution Circuit | Vegetation | Tree - fell into line | 1128 | 3304248 | 37.0953 | -122.1437 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031288 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | Yes | No | 1814946 | 0 | EPSS Ckt | N | 2023 | A B & C PH
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | TRANSFORMER | 411816550866 | 20230221 | 1446 | 20230222 | 1036 | 1991868 | 1190 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 5950 | 36.6979 | -121.793 | Yes | Clear;32-90F | Service conductor | Broken- wire on ground | 23-0032103 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815681 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | FUSE | 20171 | 20230221 | 1447 | 20230221 | 1613 | 1991999 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 1376 | 36.6679 | -121.5514 | Yes | Clear;32-90 F |  |  | 23-0031454 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815090 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 7799 | 20230221 | 1449 | 20230223 | 1536 | 1997111 | 2927 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 181474 | 37.091 | -122.1396 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032180 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815757 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1102 | 182201102 | FUSE | 4281 | 20230221 | 1454 | 20230221 | 1820 | 1992001 | 206 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 4120 | 36.6157 | -121.5627 | Yes | Overcast-Strong Winds;32-90 F |  |  | 23-0031704 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815311 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 10563 | 20230221 | 1502 | 20230223 | 1105 | 1997567 | 2643 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 50 | 132150 | 37.1097 | -122.0485 | Yes | Clear;32-90 F |  |  | 23-0033083 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816276 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | TRIP-SAVER | 6661 | 20230221 | 1506 | 20230224 | 1640 | 1992139 | 4414 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 54354 | 36.9247 | -121.8133 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031550 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815176 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 8183 | 20230221 | 1507 | 20230222 | 1251 | 1997581 | 1304 | Distribution Circuit | Vegetation | Tree - branch fell on line | 115 | 149960 | 36.9646 | -121.8903 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0032340 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | No | No | 1815845 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 68191 | 20230221 | 1507 | 20230222 | 1704 | 1992980 | 1557 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 29583 | 36.9816 | -121.9026 | Yes | Clear;32-90F |  |  | 23-0032598 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816012 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 6209 | 20230221 | 1510 | 20230227 | 1410 | 2010361 | 8580 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 25740 | 37.1793 | -122.1392 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035840 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1818664 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SOLEDAD-2105 | 182052105 | RECLOSER | 77978 | 20230221 | 1510 | 20230221 | 1941 | 1992230 | 271 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 248 | 67208 | 36.4795 | -121.4142 | Yes | Clear;32-90 F |  |  | 23-0031325 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1814979 | 0 | EPSS Ckt | N | 2023 | A & B PHASE
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 4235 | 20230221 | 1511 | 20230223 | 1321 | 1992661 | 2770 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2770 | 36.9919 | -121.8415 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032728 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816107 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | SWITCH | 11223 | 20230221 | 1512 | 20230225 | 1505 | 1992366 | 5753 | Distribution Circuit | Vegetation | Tree - fell into line | 1351 | 2455901 | 36.9485 | -121.8633 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0031348 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815003 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | RECLOSER | 36982 | 20230221 | 1514 | 20230221 | 1724 | 1992327 | 130 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 76 | 9880 | 36.5301 | -121.4747 | Yes | Clear;32-90 F |  |  | 23-0031339 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1814994 | 0 | EPSS Ckt | N | 2023 | B GRD
CENTRAL COAST | SALINAS | SALINAS-1102 | 182011102 | OTHER | WIRE DOWN HOT LD SIDE OF MTR 1008333899 | 20230221 | 1514 | 20230222 | 1319 | 1992246 | 1325 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2457 | 36777 | 36.6915 | -121.6112 | Yes |  | Secondary | Broken- wire on ground | 23-0031753 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | Yes | 1815355 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5501 | 20230221 | 1516 | 20230223 | 1139 | 1992623 | 2663 | Distribution Circuit | Vegetation | Tree - branch fell on line | 141 | 375483 | 37.1431 | -122.1318 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0033045 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816265 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2103 | 182492103 | FUSE | 9445 | 20230221 | 1518 | 20230221 | 1634 | 1992334 | 76 | Distribution Circuit | Equipment Failure/Involved | Overhead | 67 | 5092 | 36.8339 | -121.3815 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0031386 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815028 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | RECLOSER | 5178 | 20230221 | 1519 | 20230222 | 2016 | 1992363 | 1737 | Distribution Circuit | Vegetation | Tree - fell into line | 267 | 463779 | 37.0324 | -121.9467 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031346 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1815001 | 0 | EPSS Ckt | N | 2023 | AB
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 3933 | 20230221 | 1520 | 20230222 | 1415 | 1992354 | 1375 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 229 | 314875 | 36.561 | -121.7506 | Yes | Clear;32-90 F |  |  | 23-0032440 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815898 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 595388 | 20230221 | 1521 | 20230226 | 2008 | 2008274 | 7487 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 434246 | 37.1517 | -122.136 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035157 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818012 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5509 | 20230221 | 1521 | 20230227 | 1450 | 2008281 | 8609 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 172180 | 37.1532 | -122.1291 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035163 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818015 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRANSFORMER | 315239023772 | 20230221 | 1521 | 20230227 | 1937 | 2008561 | 8896 | Transformer only | Vegetation | Tree - branch fell on line | 3 | 26688 | 37.1419 | -122.1319 | Yes | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0035275 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818113 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | BUENA VISTA-1103 | 182261103 | FUSE | 23253 | 20230221 | 1521 | 20230222 | 904 | 1992375 | 1063 | Distribution Circuit | 3rd Party | Other | 2 | 2126 | 36.6551 | -121.6301 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0032019 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815618 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | TRANSFORMER | 412152549563 | 20230221 | 1522 | 20230222 | 1140 | 1992379 | 1218 | Transformer only | Vegetation | Tree - grew into line | 16 | 19488 | 36.6645 | -121.6772 | Yes | Clear;32-90 F | Transformer | Arcing | 23-0031438 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815072 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 287578 | 20230221 | 1525 | 20230222 | 1905 | 1992454 | 1660 | Distribution Circuit | Vegetation | Tree - fell into line | 213 | 52602 | 37.0438 | -122.0755 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031357 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1815010 | 0 | EPSS Ckt | N | 2023 | ABC T
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6711 | 20230221 | 1537 | 20230222 | 1924 | 1992560 | 1667 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 49 | 81683 | 36.9982 | -121.8687 | Yes | Clear;32-90F |  |  | 23-0032628 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816031 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 737 | 20230221 | 1538 | 20230222 | 1755 | 1992589 | 1577 | Distribution Circuit | Equipment Failure/Involved | Overhead | 59 | 93043 | 37.0046 | -121.8551 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 23-0032645 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | No | No | 1816042 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | FUSE | 3725 | 20230221 | 1540 | 20230222 | 125 | 1992617 | 0 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 2925 | 36.5547 | -121.5365 | Yes | Clear;32-90F |  |  | 23-0032008 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815607 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 236923 | 20230221 | 1542 | 20230223 | 1409 | 1992691 | 2787 | Distribution Circuit | Vegetation | Tree - branch fell on line | 123 | 279127 | 36.9929 | -121.7354 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031925 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815523 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 1645 | 20230221 | 1548 | 20230221 | 2300 | 1992725 | 432 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 7344 | 37.0217 | -121.7655 | Yes | Clear;32-90F |  |  | 23-0031963 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815559 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5625 | 20230221 | 1549 | 20230223 | 2040 | 1993027 | 3171 | Distribution Circuit | Vegetation | Tree - fell into line | 130 | 412230 | 37.105 | -122.0512 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032977 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1816225 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 796388 | 20230221 | 1557 | 20230223 | 426 | 1992851 | 2189 | Distribution Circuit | Vegetation | Tree - fell into line | 269 | 444571 | 36.9818 | -121.901 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031469 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815104 | 0 | EPSS Ckt | N | 2023 | C PH GRD
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 4407 | 20230221 | 1558 | 20230221 | 1705 | 1992890 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 107 | 7169 | 36.9026 | -121.3627 | Yes | Clear;32-90 F |  |  | 23-0031522 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815150 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 5335 | 20230221 | 1559 | 20230222 | 1846 | 1992915 | 1607 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 74 | 118918 | 37.0281 | -121.9871 | Yes | Partly Cloudy-Strong Winds;32-90 F |  |  | 23-0032651 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816047 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 11457 | 20230221 | 1604 | 20230222 | 1859 | 1992924 | 1615 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 16150 | 36.8546 | -121.8027 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0032694 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816077 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | ERTA-0404 | 83510404 | FUSE | 5731 | 20230221 | 1610 | 20230225 | 1404 | 1993002 | 5634 | Distribution Circuit | Equipment Failure/Involved | Overhead | 106 | 127434 | 36.9324 | -121.7646 | Yes | Strong Winds-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032263 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1815809 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1101 | 182131101 | FUSE | 7635 | 20230221 | 1612 | 20230224 | 1403 | 1993713 | 4191 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 12573 | 36.5325 | -121.408 | Yes | Partly Cloudy-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0031562 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815186 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1107 | 182011107 | TRANSFORMER | 412245949423 | 20230221 | 1615 | 20230222 | 1630 | 1993056 | 1455 | Transformer only | Vegetation | Tree - branch fell on line | 7 | 10185 | 36.6615 | -121.6454 | Yes | Clear;32-90F | Secondary | Bent or Twisted | 23-0032015 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815614 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 5465 | 20230221 | 1619 | 20230225 | 1858 | 1995784 | 5919 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 266355 | 37.139 | -122.1482 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031834 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1815432 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5437 | 20230221 | 1631 | 20230224 | 1322 | 1993270 | 4131 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 28917 | 37.1176 | -122.1197 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0032805 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1816154 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SOLEDAD 2102 | 182052102 | RECLOSER | 7008 | 20230221 | 1635 | 20230222 | 1420 | 1992976 | 1305 | Distribution Circuit | Equipment Failure/Involved | Overhead | 95 | 123275 | 36.4058 | -121.3538 | Yes | Clear-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0031477 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | No | No | 1815110 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 974520 | 20230221 | 1641 | 20230222 | 1015 | 1993339 | 1054 | Distribution Circuit | Vegetation | Tree - branch fell on line | 330 | 347820 | 36.9908 | -121.8063 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0031512 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | No | No | 1815140 | 0 | EPSS Ckt | N | 2023 | AB GRD T
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 12758 | 20230221 | 1658 | 20230222 | 1408 | 1991876 | 1270 | Distribution Circuit | Vegetation | Tree - fell into line | 232 | 294176 | 37.1486 | -122.1745 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Together | 23-0031540 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815165 | 0 | EPSS Ckt | N | 2023 | TIME OC A-B
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 7289 | 20230221 | 1701 | 20230227 | 1625 | 2010287 | 8604 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 51552 | 37.1711 | -122.1812 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035818 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1818637 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9793 | 20230221 | 1702 | 20230223 | 1425 | 1993722 | 2723 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 64 | 174272 | 37.196 | -122.1452 | Yes | Clear-Strong Winds;32-90 F |  |  | 23-0033262 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816359 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 2913 | 20230221 | 1710 | 20230223 | 1756 | 1993692 | 2926 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 20482 | 37.1752 | -122.1446 | Yes | Clear;32-90 F |  |  | 23-0033371 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816421 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | FORT ORD-2106 | 182402106 | RECLOSER | 9138 | 20230221 | 1716 | 20230222 | 1505 | 1990827 | 1309 | Distribution Circuit | Vegetation | Tree - branch fell on line | 453 | 72651 | 36.6413 | -121.8077 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031575 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815199 | 0 | EPSS Ckt | N | 2023 | SGF
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | JUMPER | WIRE DOWN HOT E/OF CGC#315700321525 | 20230221 | 1718 | 20230223 | 1941 | 1997782 | 3023 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 39958 | 37.0819 | -121.9754 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032409 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1815882 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | OILFIELDS-1102 | 182391102 | FUSE | 573 | 20230221 | 1721 | 20230223 | 1212 | 1993804 | 2571 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 28281 | 36.0109 | -120.8334 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031833 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1815431 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 8419 | 20230221 | 1724 | 20230222 | 1450 | 1994809 | 1286 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 42438 | 36.5693 | -121.7917 | Yes | Clear;32-90F |  |  | 23-0032448 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815901 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 12838 | 20230221 | 1726 | 20230224 | 1924 | 1991642 | 4438 | Distribution Circuit | Vegetation | Tree - fell into line | 219 | 698355 | 37.1272 | -122.1236 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031593 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1815214 | 0 | EPSS Ckt | N | 2023 | A-B
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 737512 | 20230221 | 1734 | 20230222 | 1823 | 1993432 | 1489 | Distribution Circuit | Vegetation | Tree - fell into line | 872 | 1244042 | 37.0467 | -122.074 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031660 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1815277 | 0 | EPSS Ckt | N | 2023 | BC
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316669012925 | 20230221 | 1734 | 20230225 | 1823 | 1994056 | 5809 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 11618 | 36.8496 | -121.6395 | Yes | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0032994 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816234 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 5090 | 20230221 | 1740 | 20230223 | 205 | 1994143 | 1945 | Distribution Circuit | Vegetation | Tree - fell into line | 279 | 432655 | 36.9804 | -121.892 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031647 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815265 | 0 | EPSS Ckt | N | 2023 | C-GRD
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | RECLOSER | 16006 | 20230221 | 1746 | 20230222 | 1939 | 1994622 | 1529 | Distribution Circuit | Vegetation | Tree - fell into line | 8569 | 2715920 | 36.9829 | -122.0492 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031657 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1815274 | 0 | EPSS Ckt | N | 2023 | A-B-C
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 5066 | 20230221 | 1747 | 20230226 | 1550 | 1994536 | 7083 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 191241 | 37.1706 | -122.1655 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031693 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815302 | 0 | EPSS Ckt | N | 2023 | C-GRD
CENTRAL COAST | KING CITY | KING CITY-1106 | 182031106 | FUSE | 589111 | 20230221 | 1751 | 20230223 | 954 | 1994352 | 2403 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 26433 | 36.193 | -121.0377 | Yes | Clear;32-90 F |  |  | 23-0031890 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815488 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 11044 | 20230221 | 1808 | 20230221 | 1851 | 1991261 | 43 | Distribution Circuit | Vegetation | Tree - fell into line | 610 | 26230 | 37.0401 | -122.0297 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0031668 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | No | No | 1815281 | 0 | EPSS Ckt | N | 2023 | ABC
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 5921 | 20230221 | 1811 | 20230225 | 926 | 2007919 | 5235 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 10470 | 36.961 | -122.0935 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0035083 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1817946 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 316055217998 | 20230221 | 1815 | 20230222 | 1822 | 1994886 | 1447 | Transformer only | Vegetation | Tree - fell into line | 1 | 1447 | 36.9864 | -121.8516 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032683 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816070 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | RECLOSER | 383718 | 20230221 | 1822 | 20230222 | 950 | 1993670 | 928 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 710 | 268820 | 36.5788 | -121.7198 | Yes | Clear;32-90 F |  |  | 23-0031697 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | No | No | 1815304 | 0 | EPSS Ckt | N | 2023 | ABC T
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 67520 | 20230221 | 1827 | 20230222 | 946 | 1992368 | 919 | Distribution Circuit | Vegetation | Tree - fell into line | 1387 | 1274653 | 36.9577 | -121.8525 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 23-0031714 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815321 | 0 | EPSS Ckt | N | 2023 | A GRD
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 12518 | 20230221 | 1829 | 20230222 | 1621 | 1994951 | 1312 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 527 | 686924 | 37.0791 | -122.0037 | Yes | Clear;32-90 F |  |  | 23-0031715 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815322 | 0 | EPSS Ckt | N | 2023 | A-GRD
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | JUMPER | WIRE DOWN 3P LOAD SIDE OF 10325 | 20230221 | 1838 | 20230227 | 1449 | 1996609 | 8411 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 8483 | 37.1586 | -122.1719 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032350 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815850 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 6103 | 20230221 | 1838 | 20230223 | 1530 | 1995030 | 2692 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 148060 | 37.0115 | -122.0121 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032771 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816141 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 2957 | 20230221 | 1838 | 20230223 | 1415 | 1995019 | 2617 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 65425 | 37.0536 | -122.0766 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0033232 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816345 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 9481 | 20230221 | 1840 | 20230224 | 1325 | 1995045 | 4005 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 33390 | 37.016 | -122.0281 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032317 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1815835 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 3279 | 20230221 | 1842 | 20230223 | 1148 | 1995086 | 2466 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 54252 | 37.0434 | -121.9977 | Yes | Clear;32-90F |  |  | 23-0033130 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816298 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 1617 | 20230221 | 1844 | 20230223 | 1351 | 1995092 | 2587 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 38805 | 37.0334 | -122.0091 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0033254 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816354 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 4677 | 20230221 | 1854 | 20230226 | 1120 | 2009834 | 6746 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 88 | 593648 | 36.9713 | -121.8229 | Yes | Clear;32-90 F |  |  | 23-0035666 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1818509 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 2199 | 20230221 | 1903 | 20230223 | 1644 | 1995334 | 2741 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 76748 | 36.9517 | -121.834 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0032230 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1815788 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 141 | 20230221 | 1906 | 20230222 | 1512 | 1996269 | 1206 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 5622 | 37.048 | -122.0648 | Yes | Partly Cloudy;32-90 F |  |  | 23-0032547 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815972 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | TRANSFORMER | 315519819369 | 20230221 | 1910 | 20230222 | 1310 | 1995388 | 1080 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 11880 | 37.0211 | -122.0352 | Yes | Clear;32-90F | Fuse | Broken | 23-0032392 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815874 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 169 | 20230221 | 1921 | 20230222 | 1945 | 1995460 | 1464 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 7320 | 37.054 | -122.0418 | Yes | Clear-Strong Winds;32-90 F |  |  | 23-0032725 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816105 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | FUSE | 3027 | 20230221 | 1926 | 20230221 | 2358 | 1995499 | 272 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 153 | 41616 | 36.2497 | -121.4319 | Yes | Clear;32-90F |  |  | 23-0031976 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815573 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | RECLOSER | 9100 | 20230221 | 1942 | 20230223 | 1606 | 1995631 | 2653 | Distribution Circuit | Vegetation | Tree - fell into line | 139 | 18050 | 36.6163 | -121.9248 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031803 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | Yes | No | 1815401 | 0 | EPSS Ckt | N | 2023 | B C GRD
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | FUSE | 7705 | 20230221 | 2000 | 20230223 | 1025 | 1995733 | 2305 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 16135 | 36.3249 | -121.2959 | Yes | Overcast-Drizzle;32-90 F |  |  | 23-0033025 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816248 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | TRANSFORMER | 411569746830 | 20230221 | 2003 | 20230222 | 1002 | 1995746 | 839 | Transformer only | Unknown Cause | Patrol - found nothing | 10 | 8390 | 36.5848 | -121.8731 | Yes | Overcast-Strong Winds;32-90 F |  |  | 23-0032185 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1815760 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 11331 | 20230221 | 2030 | 20230223 | 1111 | 1995887 | 2321 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 18568 | 36.9866 | -121.8871 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0032715 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816096 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | PANOCHE-1103 | 253671103 | RECLOSER | 4010 | 20230221 | 2033 | 20230223 | 1809 | 1995910 | 2736 | Distribution Circuit | Equipment Failure/Involved | Overhead | 205 | 423018 | 36.5951 | -120.7911 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0031867 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815465 | 0 | EPSS Ckt | N | 2023 | GRD TRGT
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 86397 | 20230221 | 2041 | 20230301 | 1231 | 1995919 | 11030 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 44120 | 37.0322 | -122.0148 | Yes | Clear;32-90F |  |  | 23-0038137 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1820380 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | TRANSFORMER | 411435046088 | 20230221 | 2042 | 20230223 | 1856 | 1996975 | 2774 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 8322 | 36.5633 | -121.9184 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0032650 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816046 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | TRANSFORMER | 411428746130 | 20230221 | 2044 | 20230223 | 856 | 1995926 | 2172 | Transformer only | Vegetation | Tree - fell into line | 12 | 26064 | 36.5644 | -121.9206 | Yes | Overcast-Strong Winds;32-90 F | Transformer (OH) | Normal | 23-0031908 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1815507 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | FUSE | 25757 | 20230221 | 2125 | 20230222 | 1700 | 1996039 | 1175 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 7050 | 36.5082 | -121.4786 | Yes | Clear;32-90F | Capacitor | Normal | 23-0032002 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815599 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 75993 | 20230221 | 2132 | 20230222 | 205 | 1996084 | 273 | Distribution Circuit | Vegetation | Tree - branch fell on line | 92 | 25116 | 36.9799 | -122.0316 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0032010 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815609 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 4473 | 20230221 | 2140 | 20230222 | 1246 | 1996082 | 906 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 15402 | 37.003 | -122.0141 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0032330 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815840 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | OTHER | 235219 | 20230221 | 2147 | 20230222 | 1340 | 1996105 | 953 | Distribution Circuit | Equipment Failure/Involved | Overhead | 77 | 73381 | 36.699 | -121.7924 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0031916 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1815514 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 332507 | 20230221 | 2320 | 20230222 | 1423 | 1996229 | 903 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 18963 | 37.0415 | -122.0899 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031969 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1815566 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | OCB | 2202/2 | 20230221 | 2346 | 20230224 | 2014 | 1996247 | 4047 | Distribution Circuit | Vegetation | Tree - fell into line | 6128 | 2526283 | 36.5786 | -121.9085 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0031981 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815578 | 0 | EPSS Ckt | N | 2023 | B-C GRD
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 1661 | 20230222 | 18 | 20230222 | 744 | 1996171 | 446 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 7582 | 36.9853 | -122.0302 | No | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031986 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815583 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 5585 | 20230222 | 118 | 20230222 | 1437 | 1996312 | 799 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 62 | 49538 | 37.0555 | -122.0609 | No | Clear;32-90 F |  |  | 23-0032495 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815936 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRIP-SAVER | 834583 | 20230222 | 146 | 20230222 | 1805 | 1996318 | 979 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 32307 | 37.0442 | -122.0777 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0032667 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816058 | 0 | EPSS Ckt | N | 2023 | NA
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | TRANSFORMER | MTR#1010848402 | 20230222 | 602 | 20230223 | 1330 | 1996436 | 1888 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 16992 | 36.5978 | -121.8884 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0032522 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815955 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | FUSE | 2751 | 20230222 | 635 | 20230223 | 1254 | 1996620 | 1819 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 44891 | 36.3856 | -121.5538 | No | Clear;32-90F |  |  | 23-0032231 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815789 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | TRANSFORMER | 411428846081 | 20230222 | 652 | 20230223 | 856 | 1996497 | 1564 | Transformer only | Vegetation | Tree - fell into line | 30 | 46920 | 36.5631 | -121.9206 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0032692 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816075 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9579 | 20230222 | 707 | 20230227 | 2223 | 2010364 | 8116 | Distribution Circuit | Vegetation | Tree - fell into line | 160 | 1298560 | 37.1732 | -122.1382 | No | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0035843 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1818666 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | TRANSFORMER | T2272 | 20230222 | 711 | 20230222 | 1257 | 1996579 | 346 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 346 | 36.9851 | -122.0364 | No | Clear;32-90F |  |  | 23-0032382 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1815868 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6667 | 20230222 | 800 | 20230222 | 1921 | 1996713 | 681 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 4086 | 36.9464 | -121.8211 | No | Clear;32-90 F |  |  | 23-0032662 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816055 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRIP-SAVER | 2253 | 20230222 | 836 | 20230223 | 1432 | 1998245 | 1796 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 21552 | 37.1709 | -122.1652 | No | Clear;32-90F |  |  | 23-0033192 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816323 | 0 | EPSS Ckt | N | 2023 | AB
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | FUSE | 25221 | 20230222 | 855 | 20230222 | 1040 | 1996896 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 210 | 36.4757 | -121.4713 | No | Clear;32-90F |  |  | 23-0032227 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815786 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | TRANSFORMER | 414300725419 | 20230222 | 945 | 20230222 | 1907 | 1996788 | 562 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 562 | 36.0164 | -120.9276 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0032189 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815764 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | FUSE | 7793 | 20230222 | 954 | 20230222 | 1755 | 1998255 | 478 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 2868 | 36.264 | -121.8001 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0032660 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816053 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | JUMPER | OPEN JUMPER @ 801 | 20230222 | 1116 | 20230223 | 1942 | 1997789 | 1790 | Distribution Circuit | Equipment Failure/Involved | Overhead | 59 | 23814 | 36.7369 | -121.7597 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 23-0032420 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1815887 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 2701 | 20230222 | 1210 | 20230223 | 2018 | 1997524 | 1928 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 1928 | 37.0215 | -121.8267 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0033420 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816453 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 8359 | 20230222 | 1352 | 20230223 | 1452 | 1997839 | 1500 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 25500 | 37.0781 | -122.1334 | No | Clear;32-90 F |  |  | 23-0033245 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816351 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | TRANSFORMER | 413139458042 | 20230222 | 1411 | 20230222 | 2325 | 1997877 | 554 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1662 | 36.9046 | -121.3479 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0032532 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815962 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | JUMPER | OJ 2 S/OF CGC 315224820640 | 20230222 | 1421 | 20230223 | 1915 | 1998240 | 1734 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3468 | 37.0539 | -122.138 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032599 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1816013 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 5411 | 20230222 | 1448 | 20230223 | 1810 | 1998003 | 1642 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 27914 | 37.0548 | -122.161 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0032505 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815943 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | KING CITY 1102 | 182031102 | FUSE | 7843 | 20230222 | 1455 | 20230223 | 938 | 1997958 | 1123 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 2246 | 36.2465 | -121.098 | No | Partly Cloudy;32-90 F | Insulator | Broken | 23-0032498 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1815938 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 6641 | 20230222 | 1500 | 20230222 | 1528 | 1998083 | 28 | Distribution Circuit | Equipment Failure/Involved | Overhead | 41 | 1148 | 36.6023 | -121.8968 | No | Overcast;32-90 F | Cutout- fuse holder | Broken | 23-0032553 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1815974 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | OTHER | WIRE DWN | 20230222 | 1531 | 20230224 | 1959 | 1998551 | 3148 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 144026 | 37.0621 | -122.1585 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032717 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | Yes | Yes | 1816098 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0422 | 182440422 | TRANSFORMER | 411357047296 | 20230222 | 1555 | 20230222 | 1732 | 1998143 | 97 | Transformer only | Unknown Cause | Patrol - found nothing | 6 | 582 | 36.5959 | -121.9462 | No | Clear;32-90 F |  |  | 23-0032635 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1816038 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 8525 | 20230222 | 1556 | 20230225 | 1824 | 1998147 | 4468 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 67412 | 37.0586 | -122.1473 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032574 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1815995 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 10025 | 20230222 | 1609 | 20230226 | 1350 | 2008689 | 5621 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 213598 | 37.1398 | -122.1525 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035286 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1818124 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 3017 | 20230222 | 1609 | 20230226 | 1640 | 2008692 | 5791 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1 | 5791 | 37.1423 | -122.1536 | No | Clear;32-90F |  |  | 23-0035289 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1818127 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 5461 | 20230222 | 1609 | 20230228 | 1551 | 2008696 | 8622 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 181062 | 37.1383 | -122.1436 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035291 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1818129 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 1847 | 20230222 | 1626 | 20230226 | 1044 | 1998239 | 5418 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 5418 | 37.0635 | -122.0696 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033221 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816339 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 9005 | 20230222 | 1627 | 20230223 | 1415 | 1998241 | 1308 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 28776 | 37.0318 | -122.1369 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0033222 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816340 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 7595 | 20230222 | 1635 | 20230222 | 1726 | 1998252 | 51 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 306 | 37.102 | -121.9819 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0032633 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816034 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 937291 | 20230222 | 1636 | 20230228 | 1918 | 1998271 | 8802 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 114426 | 37.1186 | -121.964 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032716 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816097 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 7307 | 20230222 | 1733 | 20230226 | 903 | 1998377 | 5250 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 31500 | 37.0385 | -122.0699 | No | Clear;32-90F |  |  | 23-0035599 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1818450 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 7295 | 20230222 | 1839 | 20230223 | 1602 | 1998484 | 1283 | Distribution Circuit | Equipment Failure/Involved | Overhead | 58 | 74414 | 37.0325 | -122.0872 | No | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Together | 23-0033290 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816377 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 4709 | 20230222 | 1938 | 20230222 | 2110 | 1998563 | 92 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 7 | 644 | 36.6877 | -121.3445 | No | Clear;32-90F |  |  | 23-0032781 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816149 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 11107 | 20230222 | 1938 | 20230224 | 1856 | 1998553 | 2838 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 70950 | 36.9797 | -122.0591 | No | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033039 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816260 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 11105 | 20230222 | 1940 | 20230224 | 1823 | 1998555 | 2803 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 16818 | 37.0113 | -122.0752 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033387 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816428 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 11829 | 20230222 | 2005 | 20230223 | 1859 | 1998576 | 1374 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 6870 | 37.009 | -122.0756 | No | Clear;32-90 F |  |  | 23-0033402 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816437 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 4233 | 20230223 | 149 | 20230224 | 1942 | 1998774 | 2513 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 5026 | 36.9908 | -121.8405 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0033085 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816277 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 8643 | 20230223 | 225 | 20230223 | 957 | 1999202 | 452 | Distribution Circuit | Vegetation | Tree - branch fell on line | 45 | 20340 | 37.01 | -121.8859 | Yes | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 23-0033007 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816242 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 4753 | 20230223 | 332 | 20230223 | 1708 | 1999222 | 813 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 8943 | 36.8856 | -121.6632 | Yes | Clear;32-90 F |  |  | 23-0033353 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816410 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 6477 | 20230223 | 334 | 20230223 | 629 | 1998795 | 175 | Distribution Circuit | Animal | Bird found | 425 | 74375 | 36.8655 | -121.7346 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0032845 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816183 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 6771 | 20230223 | 627 | 20230223 | 911 | 1998877 | 164 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 53 | 8692 | 36.8682 | -121.6457 | Yes | Clear;32-90F |  |  | 23-0032942 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816210 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 563 | 20230223 | 809 | 20230228 | 1640 | 2009096 | 7711 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 84821 | 37.0587 | -122.1418 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035430 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1818278 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 287578 | 20230223 | 839 | 20230223 | 1027 | 1999006 | 108 | Distribution Circuit | Vegetation | Tree - branch fell on line | 213 | 23004 | 37.0438 | -122.0755 | Yes | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0032933 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816203 | 0 | EPSS Ckt | N | 2023 | A-B
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 813 | 20230223 | 839 | 20230223 | 1312 | 1999005 | 273 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 2730 | 37.0474 | -122.1572 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0033223 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816341 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | FUSE | 7997 | 20230223 | 907 | 20230223 | 1010 | 1999060 | 63 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 126 | 36.4689 | -121.4609 | Yes | Clear;32-90F |  |  | 23-0033015 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816244 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 8315 | 20230223 | 909 | 20230223 | 1608 | 1999068 | 419 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 8799 | 37.0995 | -122.1181 | Yes | Clear;Below 32 F |  |  | 23-0033330 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816398 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | 83500401 | 83500401 | FUSE | 6007 | 20230223 | 1041 | 20230225 | 910 | 1999281 | 2789 | Distribution Circuit | Vegetation | Tree - branch fell on line | 53 | 147817 | 37.0029 | -121.9273 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033319 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1816392 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 11533 | 20230223 | 1135 | 20230223 | 2246 | 1999369 | 671 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 10736 | 36.8749 | -121.6884 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0033212 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816335 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | FUSE | 4099 | 20230223 | 1143 | 20230224 | 1252 | 1999518 | 1509 | Distribution Circuit | Vegetation | Tree - branch fell on line | 156 | 235404 | 36.8831 | -121.5598 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033177 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816314 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | RECLOSER | 9452 | 20230223 | 1314 | 20230223 | 1329 | 1999547 | 15 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 652 | 9780 | 36.5969 | -121.8855 | Yes | Overcast;32-90 F | Transformer (OH) | Normal | 23-0033180 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816316 | 0 | EPSS Ckt | N | 2023 | A-GRD
CENTRAL COAST | KING CITY | SOLEDAD-2102 | 182052102 | FUSE | 9703 | 20230223 | 1418 | 20230223 | 1923 | 1999647 | 305 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 305 | 36.408 | -121.3689 | Yes | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0033228 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1816343 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | PANOCHE-1103 | 253671103 | FUSE | 4189 | 20230223 | 1515 | 20230223 | 1745 | 1999799 | 150 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 150 | 36.492 | -120.8066 | Yes | Clear;32-90 F |  |  | 23-0033413 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816446 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | FORT ORD 2105 | 182402105 | TRANSFORMER | 411710448685 | 20230223 | 1820 | 20230224 | 1158 | 2000146 | 1058 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 6348 | 36.6374 | -121.8265 | Yes | Partly Cloudy;32-90 F | Transformer | Arcing | 23-0033383 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816426 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 9443 | 20230223 | 1823 | 20230224 | 1605 | 2000257 | 1302 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 99 | 128898 | 37.0818 | -122.0734 | Yes | Clear;32-90 F |  |  | 23-0034326 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1817201 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRIP-SAVER | 9031 | 20230223 | 1825 | 20230225 | 1243 | 2000240 | 2538 | Distribution Circuit | Vegetation | Tree - branch fell on line | 48 | 121824 | 37.0726 | -122.0742 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0034066 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1817015 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5163 | 20230223 | 1830 | 20230226 | 1134 | 2000246 | 3904 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 97600 | 37.0754 | -122.0803 | Yes | Clear;32-90 F |  |  | 23-0035684 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1818528 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316367514971 | 20230223 | 1923 | 20230225 | 1345 | 2000264 | 2542 | Transformer only | Vegetation | Tree - fell into line | 5 | 12710 | 36.9044 | -121.7433 | Yes | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0033406 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816440 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 16000 | 20230223 | 2055 | 20230223 | 2119 | 2000570 | 24 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 547 | 13128 | 37.0464 | -122.0243 | Yes | Partly Cloudy-Drizzle;32-90 F |  |  | 23-0033441 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816473 | 0 | EPSS Ckt | N | 2023 | BC
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | SWITCH | 934941 | 20230223 | 2055 | 20230228 | 1913 | 2004457 | 7098 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 276822 | 37.0969 | -121.9921 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033854 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1816864 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | JUMPER | OJ 1 SS OF CGC#315659721962 | 20230223 | 2055 | 20230301 | 1142 | 2016447 | 8087 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 16174 | 37.0933 | -121.9906 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037666 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1820004 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 9691 | 20230223 | 2109 | 20230224 | 2032 | 2006195 | 1403 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 23851 | 37.095 | -122.1387 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034357 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1817231 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 9703 | 20230223 | 2109 | 20230226 | 1152 | 2007004 | 3763 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 11289 | 37.0932 | -122.1293 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034558 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1817413 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 10727 | 20230223 | 2109 | 20230226 | 1253 | 2007022 | 3824 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 11472 | 37.093 | -122.1279 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034560 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1817415 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 2425 | 20230223 | 2109 | 20230226 | 1612 | 2007025 | 4023 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 20115 | 37.0921 | -122.1157 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034563 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1817418 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 753753 | 20230223 | 2109 | 20230227 | 1655 | 2007042 | 5506 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 11012 | 37.0994 | -122.1169 | Yes | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0034564 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1817419 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 8315 | 20230223 | 2109 | 20230226 | 1820 | 2007044 | 4151 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 86967 | 37.0995 | -122.1181 | Yes | Clear;32-90 F |  |  | 23-0034567 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1817422 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 8497 | 20230223 | 2154 | 20230226 | 1316 | 2005835 | 3802 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 45624 | 37.0579 | -122.1233 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034245 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1817137 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 52003 | 20230223 | 2154 | 20230226 | 1102 | 2008432 | 3668 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 7336 | 37.0933 | -122.1411 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035215 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818063 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 8359 | 20230223 | 2154 | 20230226 | 1010 | 2008438 | 3616 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 65088 | 37.0781 | -122.1334 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035219 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818067 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | JUMPER | OJ @ CGC#315201821865 | 20230223 | 2154 | 20230226 | 2207 | 2008439 | 4333 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4333 | 37.0889 | -122.146 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035224 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818068 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8161 | 20230223 | 2202 | 20230228 | 1918 | 2008545 | 7036 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 70360 | 37.1173 | -121.9748 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0035269 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1818107 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 7593 | 20230223 | 2202 | 20230228 | 1918 | 2009844 | 7036 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 541772 | 37.1057 | -121.9724 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035648 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818491 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5629 | 20230223 | 2316 | 20230225 | 2059 | 2000906 | 2743 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 54860 | 37.1128 | -122.048 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035563 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818410 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 8163 | 20230224 | 4 | 20230224 | 105 | 2001141 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 1830 | 36.5988 | -121.9389 | Yes | Clear;32-90 F |  |  | 23-0033546 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816578 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 12474 | 20230224 | 13 | 20230224 | 551 | 2001158 | 338 | Distribution Circuit | Vegetation | Tree - fell into line | 3041 | 672997 | 36.9713 | -121.8735 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken | 23-0033515 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816547 | 0 | EPSS Ckt | N | 2023 | AC
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 236923 | 20230224 | 18 | 20230224 | 1050 | 2001270 | 632 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 77736 | 36.9929 | -121.7354 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0033883 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816883 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5599 | 20230224 | 33 | 20230225 | 1105 | 2001626 | 2072 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 40250 | 37.0796 | -122.0513 | Yes | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0034277 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1817166 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 2273 | 20230224 | 129 | 20230224 | 1255 | 2001625 | 686 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 40474 | 36.5433 | -121.913 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033564 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816597 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 4471 | 20230224 | 211 | 20230224 | 1013 | 2001773 | 482 | Distribution Circuit | Vegetation | Tree - fell into line | 201 | 96882 | 37.0009 | -122.0142 | Yes | Clear;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0033953 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816935 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 6325 | 20230224 | 217 | 20230224 | 2346 | 2001808 | 1289 | Distribution Circuit | Vegetation | Tree - fell into line | 264 | 334146 | 36.9872 | -121.9604 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033758 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1816784 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | SWITCH | 6413 | 20230224 | 227 | 20230224 | 1013 | 2001854 | 466 | Distribution Circuit | Vegetation | Tree - branch fell on line | 150 | 69900 | 36.6235 | -121.9327 | Yes | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0033607 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1816643 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 6183 | 20230224 | 249 | 20230224 | 449 | 2002046 | 120 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 3120 | 36.5648 | -121.9229 | Yes | Overcast-Rain;32-90 F |  |  | 23-0033653 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816691 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8231 | 20230224 | 354 | 20230301 | 1024 | 2010180 | 7590 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 402270 | 37.116 | -121.9869 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035764 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818597 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8247 | 20230224 | 354 | 20230228 | 2140 | 2012828 | 6826 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 34130 | 37.1196 | -121.9772 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036577 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1819159 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 83711 | 20230224 | 354 | 20230228 | 1902 | 2013416 | 6668 | Distribution Circuit | Vegetation | Tree - bark fell into line | 15 | 100020 | 37.1087 | -121.9869 | Yes |  | Conductor- Overhead | Normal | 23-0036703 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1819263 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 7623 | 20230224 | 354 | 20230301 | 1024 | 2013578 | 7590 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 30360 | 37.1264 | -121.9836 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036732 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1819292 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRIP-SAVER | 6577 | 20230224 | 356 | 20230227 | 1223 | 2006080 | 4827 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 236523 | 37.0487 | -121.8085 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034330 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1817205 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 5781 | 20230224 | 357 | 20230226 | 1623 | 2006011 | 3626 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 36260 | 37.0449 | -121.8149 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0034314 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1817194 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6851 | 20230224 | 357 | 20230227 | 1823 | 2010124 | 5186 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 82976 | 37.0421 | -121.8171 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035741 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818574 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 5819 | 20230224 | 414 | 20230226 | 1644 | s1817085 | 3630 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 39930 | 37.0449 | -121.8139 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034174 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB |  | 0 | No | Yes | No | 1817085 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 6343 | 20230224 | 427 | 20230303 | 1734 | 2018402 | 10867 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 184739 | 37.2222 | -122.1451 | Yes | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038229 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1820453 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 695 | 20230224 | 430 | 20230225 | 1835 | 2002546 | 2285 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 9140 | 37.0575 | -122.1474 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034339 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1817215 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 8511 | 20230224 | 431 | 20230225 | 1830 | 2002527 | 2279 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 10495 | 37.0617 | -122.1474 | Yes | Clear;Below 32 F | Transformer (OH) | Failed/Faulted | 23-0034270 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1817160 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 66253 | 20230224 | 434 | 20230225 | 1308 | 2002537 | 1954 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 22473 | 37.096 | -122.0136 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034006 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816977 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 12518 | 20230224 | 438 | 20230228 | 2140 | 2001412 | 6782 | Distribution Circuit | Vegetation | Tree - fell into line | 332 | 1897671 | 37.0791 | -122.0037 | Yes | Overcast-Heavy Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0033647 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | Yes | No | 1816685 | 0 | EPSS Ckt | N | 2023 | BC GRD
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8833 | 20230224 | 438 | 20230228 | 2140 | 2010460 | 6782 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 345882 | 37.1203 | -121.9865 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035885 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818701 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 7619 | 20230224 | 438 | 20230228 | 1902 | 2013373 | 6624 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 46368 | 37.1129 | -121.9865 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036700 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1819260 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | RECLOSER | 3716 | 20230224 | 441 | 20230224 | 855 | 2002588 | 244 | Distribution Circuit | Vegetation | Tree - fell into line | 447 | 112644 | 36.8245 | -121.6753 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Together | 23-0033646 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816684 | 0 | EPSS Ckt | N | 2023 | A-B
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 1729 | 20230224 | 442 | 20230301 | 935 | 2013452 | 7493 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 29972 | 37.1238 | -121.9794 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036706 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1819266 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | OCB | 2101/2 | 20230224 | 500 | 20230224 | 2059 | 2002630 | 959 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1264 | 1179857 | 37.0953 | -122.1437 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033657 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816695 | 0 | EPSS Ckt | N | 2023 | B- GRD
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 5901 | 20230224 | 501 | 20230228 | 1740 | 2006910 | 6519 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 104304 | 37.0944 | -121.9716 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0034546 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1817399 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9791 | 20230224 | 503 | 20230228 | 1528 | 2010357 | 6385 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 351175 | 37.1851 | -122.1414 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035835 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818661 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 1909 | 20230224 | 503 | 20230228 | 1811 | 2008880 | 6548 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 32740 | 37.0978 | -121.9771 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035368 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818204 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8427 | 20230224 | 504 | 20230224 | 1406 | 2002696 | 0 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 49 | 26558 | 37.077 | -121.981 | Yes | Clear;32-90 F |  |  | 23-0034077 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1817025 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6647 | 20230224 | 520 | 20230224 | 1730 | 2006409 | 730 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 5840 | 37.0266 | -121.7801 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 23-0034570 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1817425 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 11305 | 20230224 | 529 | 20230225 | 1545 | 2002843 | 2056 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 26728 | 37.0308 | -121.7862 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 23-0034565 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1817420 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 5090 | 20230224 | 551 | 20230226 | 1827 | 2003057 | 3636 | Distribution Circuit | Vegetation | Tree - fell into line | 434 | 160555 | 36.9804 | -121.892 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033690 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1816727 | 0 | EPSS Ckt | N | 2023 | ABC
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 12758 | 20230224 | 555 | 20230226 | 1644 | 2003072 | 3497 | Distribution Circuit | Vegetation | Tree - fell into line | 318 | 657896 | 37.1486 | -122.1745 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033693 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1816730 | 0 | EPSS Ckt | N | 2023 | A B C 51 TIME
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 7017 | 20230224 | 607 | 20230228 | 2214 | 2010363 | 6727 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 235445 | 37.1756 | -122.1388 | Yes | Clear;Below 32 F | Conductor- Overhead | Normal | 23-0035842 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1818665 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 95690 | 20230224 | 612 | 20230225 | 1448 | 2003308 | 1956 | Distribution Circuit | Vegetation | Tree - fell into line | 1535 | 913296 | 37.1249 | -122.125 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033712 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816747 | 0 | EPSS Ckt | N | 2023 | SGF
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5501 | 20230224 | 619 | 20230227 | 1209 | 2008721 | 4670 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 658470 | 37.1431 | -122.1318 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035300 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818141 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9725 | 20230224 | 621 | 20230227 | 1230 | 2008269 | 4689 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 121914 | 37.1523 | -122.1367 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035154 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818010 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5521 | 20230224 | 621 | 20230227 | 1150 | 2010445 | 4649 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 46 | 213854 | 37.1577 | -122.1357 | Yes | Clear;32-90 F |  |  | 23-0035879 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1818697 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1104 | 182201104 | OCB | 1104/2 | 20230224 | 624 | 20230224 | 1344 | 2002994 | 440 | Distribution Circuit | Equipment Failure/Involved | Overhead | 682 | 127264 | 36.6139 | -121.5666 | Yes | Overcast-Rain;32-90 F | Switch (OH) | Arcing | 23-0033714 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1816749 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | SWITCH | 5817 | 20230224 | 626 | 20230226 | 1301 | s1817086 | 3275 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 16365 | 37.042 | -121.8179 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034176 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1817086 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 4915 | 20230224 | 627 | 20230225 | 1422 | 2003659 | 1915 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 65110 | 37.1032 | -122.0458 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034449 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1817303 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9733 | 20230224 | 635 | 20230228 | 1337 | 2010441 | 6182 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 302918 | 37.158 | -122.1357 | Yes | Clear;32-90 F | Capacitor | Broken | 23-0035876 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1818694 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 670217 | 20230224 | 640 | 20230226 | 1343 | 2006038 | 3303 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 184968 | 37.1578 | -122.166 | Yes | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0034323 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1817198 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 9569 | 20230224 | 650 | 20230224 | 1259 | 2003569 | 369 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 5038 | 36.9783 | -121.8269 | Yes | Overcast-Fog-Rain;32-90 F |  |  | 23-0034148 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1817076 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 12992 | 20230224 | 652 | 20230226 | 1640 | 2003171 | 3468 | Distribution Circuit | Vegetation | Tree - fell into line | 383 | 1322829 | 37.1991 | -122.1532 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033735 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1816764 | 0 | EPSS Ckt | N | 2023 | B-C
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 307348 | 20230224 | 658 | 20230303 | 1734 | 2002504 | 10716 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 21432 | 37.2109 | -122.1505 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033737 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | Yes | No | 1816765 | 0 | EPSS Ckt | N | 2023 | A-B-C-GRD
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 11895 | 20230224 | 703 | 20230303 | 1734 | 2019392 | 10711 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 10711 | 37.231 | -122.1491 | Yes | Clear;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0038575 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1820747 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | SWITCH | 11003 | 20230224 | 715 | 20230226 | 1701 | 2003460 | 3466 | Distribution Circuit | 3rd Party | Vehicle | 1703 | 225954 | 37.0383 | -122.0434 | Yes | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken | 23-0033750 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1816778 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | TRANSFORMER | 411571846742 | 20230224 | 718 | 20230224 | 818 | 2003416 | 60 | Transformer only | Vegetation | Tree - branch fell on line | 5 | 300 | 36.5824 | -121.8723 | Yes | Clear;32-90 F | Secondary | Arcing | 23-0033816 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1816827 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 2251 | 20230224 | 724 | 20230225 | 1319 | 2003760 | 1795 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 37695 | 37.1702 | -122.1646 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033870 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816873 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 891361 | 20230224 | 730 | 20230301 | 1310 | 2010353 | 7540 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 135720 | 37.1891 | -122.1431 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035834 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1818660 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6597 | 20230224 | 731 | 20230226 | 1320 | 2003802 | 3229 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 19374 | 36.9966 | -121.7163 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035353 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818193 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | FUSE | 5561 | 20230224 | 806 | 20230224 | 1727 | 2004087 | 561 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 11220 | 36.7763 | -121.5987 | Yes | Clear;32-90 F |  |  | 23-0034096 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1817041 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 4465 | 20230224 | 827 | 20230224 | 1028 | 2004229 | 121 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 1573 | 36.8327 | -121.3636 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0033948 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816932 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 809 | 20230224 | 847 | 20230224 | 1653 | 2004356 | 486 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 25 | 12150 | 36.8885 | -121.6456 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0034407 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1817265 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 8125 | 20230224 | 856 | 20230225 | 1901 | 2004462 | 2045 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 38855 | 37.099 | -122.1424 | Yes | Clear;32-90 F | Crossarm- Wood | Broken | 23-0034103 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1817046 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | RECLOSER | 3716 | 20230224 | 856 | 20230224 | 1450 | 2004418 | 325 | Distribution Circuit | Vegetation | Tree - fell into line | 447 | 61521 | 36.8245 | -121.6753 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0033646 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816861 | 0 | EPSS Ckt | N | 2023 | A-B
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | TRANSFORMER | 315320528735 | 20230224 | 920 | 20230226 | 1446 | 2004603 | 3206 | Transformer only | Environmental/External | Lightning | 1 | 3206 | 37.0029 | -122.1048 | Yes | Clear;32-90F | Transformer (OH) | Burned/flashed | 23-0035370 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1818206 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 3893 | 20230224 | 924 | 20230225 | 1245 | 2004648 | 1636 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 27812 | 36.9688 | -121.8551 | Yes | Clear;32-90F |  |  | 23-0035237 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1818078 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRANSFORMER | 315412519672 | 20230224 | 926 | 20230226 | 1858 | 2004656 | 3452 | Transformer only | Unknown Cause | Patrol - not conducted | 3 | 10356 | 37.0294 | -122.0729 | Yes | Clear;32-90F |  |  | 23-0035928 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1818741 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 8017 | 20230224 | 939 | 20230225 | 1835 | 2004844 | 1976 | Distribution Circuit | Vegetation | Tree - branch fell on line | 74 | 146224 | 37.1565 | -122.1617 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034020 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816983 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 12124 | 20230224 | 1016 | 20230224 | 1624 | 2003633 | 368 | Distribution Circuit | Vegetation | Tree - fell into line | 302 | 109141 | 37.1677 | -122.1662 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Burned/flashed | 23-0033965 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1816943 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | TRIP-SAVER | 4929 | 20230224 | 1040 | 20230228 | 1225 | 2005031 | 5865 | Distribution Circuit | Equipment Failure/Involved | Overhead | 133 | 8901 | 36.9129 | -121.8055 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Burned/flashed | 23-0034032 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1816993 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9763 | 20230224 | 1128 | 20230227 | 1026 | 2009233 | 4258 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 85160 | 37.1767 | -122.1629 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035454 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1818302 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 7773 | 20230224 | 1129 | 20230303 | 1610 | 2010192 | 10361 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 362635 | 37.1881 | -122.1581 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035775 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818604 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 1607 | 20230224 | 1134 | 20230228 | 1743 | 2010191 | 6129 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 79677 | 37.1931 | -122.156 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035774 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818603 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 7993 | 20230224 | 1134 | 20230225 | 1405 | 2005202 | 1591 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 63640 | 37.0284 | -121.7405 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0035225 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | No | No | 1818069 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRIP-SAVER | 5479 | 20230224 | 1140 | 20230226 | 1357 | 2005218 | 3017 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 42238 | 37.1292 | -122.1131 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035158 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818013 | 0 | EPSS Ckt | N | 2023 | AB
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRANSFORMER | 100000062433 | 20230224 | 1143 | 20230226 | 1140 | 2005227 | 2877 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 2877 | 37.1178 | -122.1534 | Yes | Clear;32-90F |  |  | 23-0035697 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1818538 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 3729 | 20230224 | 1158 | 20230301 | 1802 | 2009950 | 7564 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 22692 | 37.199 | -122.1535 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035694 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1818536 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 6689 | 20230224 | 1217 | 20230224 | 1442 | 2001827 | 145 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1595 | 36.8881 | -121.8071 | Yes | Overcast-Rain;32-90 F |  |  | 23-0034286 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1817173 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 4709 | 20230224 | 1220 | 20230224 | 1615 | 2005364 | 235 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1645 | 36.6877 | -121.3445 | Yes | Clear;32-90 F | Insulator | Broken | 23-0034187 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1817092 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 3119 | 20230224 | 1223 | 20230226 | 1733 | 2010278 | 3190 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 9570 | 37.172 | -122.1647 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035815 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818632 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 2989 | 20230224 | 1232 | 20230227 | 1604 | 2005387 | 4532 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 18128 | 37.1639 | -122.0767 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035317 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1818166 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | JUMPER | OJ 1 POLE SS OF FUCO 2975 | 20230224 | 1241 | 20230228 | 1343 | 2005156 | 5822 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 29110 | 37.1628 | -122.0778 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0035315 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1818164 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | TRIP-SAVER | 6617 | 20230224 | 1309 | 20230224 | 1834 | 2005591 | 325 | Distribution Circuit | Animal | Bird found | 101 | 32825 | 36.4027 | -121.6578 | Yes | Clear;32-90 F | Transformer (OH) | Normal | 23-0034425 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1817278 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | TRANSFORMER | 411392548006 | 20230224 | 1406 | 20230224 | 1604 | 2005128 | 118 | Transformer only | Equipment Failure/Involved | Overhead | 19 | 2242 | 36.616 | -121.9351 | Yes | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0034223 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1817121 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 12122 | 20230224 | 1503 | 20230225 | 1623 | 2005954 | 1520 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 94240 | 37.0666 | -122.2288 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034299 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1817185 | 0 | EPSS Ckt | N | 2023 | SGF DCD
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 5405 | 20230224 | 1545 | 20230226 | 1500 | 2006093 | 2835 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 28350 | 37.0671 | -122.141 | Yes | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0035084 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1817947 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | FUSE | 711393 | 20230224 | 1611 | 20230224 | 1700 | 2006202 | 49 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 196 | 36.6804 | -121.5569 | Yes | Clear;32-90 F |  |  | 23-0034422 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1817275 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 91034 | 20230224 | 1740 | 20230225 | 1606 | 2006514 | 1346 | Distribution Circuit | Vegetation | Tree - fell into line | 221 | 277096 | 37.0944 | -122.1411 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034448 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1817301 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9751 | 20230224 | 1747 | 20230301 | 1321 | 2006488 | 6934 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6934 | 37.1608 | -122.1628 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035635 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818480 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9747 | 20230224 | 1751 | 20230227 | 1141 | 2010697 | 3950 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 3950 | 37.1282 | -122.1326 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0035908 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1818721 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 5397 | 20230224 | 1851 | 20230226 | 1427 | 2006757 | 2616 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 60168 | 37.076 | -122.1429 | Yes | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034505 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1817355 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 8097 | 20230224 | 1852 | 20230227 | 2216 | 2006765 | 4524 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 76908 | 37.0785 | -122.139 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034507 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1817357 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 8397 | 20230224 | 1853 | 20230227 | 2002 | 2006766 | 4389 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 43890 | 37.0795 | -122.1393 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034508 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1817358 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 9827 | 20230224 | 1854 | 20230227 | 1140 | 2006769 | 3886 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 128238 | 37.0797 | -122.1385 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034509 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1817359 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1106 | 182011106 | TRANSFORMER | 412234749188 | 20230224 | 1930 | 20230224 | 2213 | 2006851 | 163 | Transformer only | Unknown Cause | Patrol - found nothing | 6 | 978 | 36.6549 | -121.649 | Yes | Overcast;32-90 F |  |  | 23-0034834 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1817694 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 4741 | 20230224 | 2054 | 20230227 | 1231 | 2007179 | 3817 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 19085 | 37.0908 | -122.105 | Yes | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0035125 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1817989 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 412012455204 | 20230224 | 2054 | 20230225 | 1235 | 2006799 | 941 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 941 | 36.8186 | -121.7295 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0034580 | OH | Sus | 35427333 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1817435 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 5143 | 20230224 | 2101 | 20230225 | 1910 | 2007187 | 1329 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 35883 | 37.0994 | -122.0868 | Yes | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0035072 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1817935 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 5151 | 20230224 | 2111 | 20230301 | 1407 | 2007197 | 6776 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 33880 | 37.111 | -122.0899 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0035655 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818498 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 6371 | 20230224 | 2133 | 20230225 | 909 | 2007228 | 696 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 7656 | 36.8639 | -121.7228 | Yes | Clear;32-90F |  |  | 23-0035086 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1817949 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 8593 | 20230224 | 2222 | 20230226 | 1733 | 2007301 | 2591 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 64775 | 36.9667 | -121.8694 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0035082 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1817945 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | FUSE | 9501 | 20230224 | 2247 | 20230302 | 1823 | 2018714 | 8376 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 50256 | 36.1841 | -120.6775 | Yes | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0038348 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1820540 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | RECLOSER | 896438 | 20230224 | 2248 | 20230302 | 1755 | 2007362 | 8347 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 271832 | 36.1701 | -120.7857 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034957 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1817822 | 0 | EPSS Ckt | N | 2023 | A GRD TIME
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | FUSE | 7107 | 20230224 | 2248 | 20230302 | 1809 | 2018710 | 8361 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 142137 | 36.1984 | -120.7147 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0038346 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1820538 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 5149 | 20230225 | 647 | 20230301 | 1211 | 2007745 | 6084 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 30420 | 37.1109 | -122.0899 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035115 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1817980 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 8799 | 20230225 | 818 | 20230225 | 1358 | 2007848 | 340 | Distribution Circuit | Vegetation | Tree - grew into line | 54 | 18360 | 36.5607 | -121.9181 | Yes | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Normal | 23-0035063 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1817926 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 7131 | 20230225 | 1031 | 20230225 | 1130 | 2008218 | 59 | Distribution Circuit | Vegetation | Other ground vegetation | 11 | 649 | 36.5861 | -121.8603 | Yes | Partly Cloudy;32-90 F | Transformer (UG) | Contaminated | 23-0035183 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1818032 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | TRANSFORMER | 315296422555 | 20230225 | 1039 | 20230225 | 1433 | 2008227 | 234 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 702 | 37.1089 | -122.1124 | Yes | Clear;32-90F |  |  | 23-0035301 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1818143 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 1827 | 20230225 | 1418 | 20230302 | 1523 | 2018133 | 7265 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 87180 | 37.2134 | -122.1558 | Yes | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038091 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | Yes | No | 1820354 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 1907 | 20230225 | 1446 | 20230301 | 1353 | 2008747 | 5707 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 68484 | 37.0973 | -121.9748 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035308 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1818154 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 7019 | 20230225 | 1606 | 20230301 | 919 | 2008874 | 5353 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 26765 | 37.0995 | -121.9775 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035366 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1818202 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 96986 | 20230225 | 1608 | 20230228 | 1510 | 1998614 | 1338 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 32407 | 37.1719 | -122.1648 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035377 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818214 | 0 | EPSS Ckt | N | 2023 | SGF
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | JUMPER | 5125 | 20230225 | 1621 | 20230225 | 1939 | 2008917 | 198 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 792 | 36.6543 | -121.5594 | Yes | Clear;32-90F | Jumper | Burned Open | 23-0035410 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1818253 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | OTHER | WIRE DOWN SSD CGC 3156912225 | 20230225 | 1653 | 20230228 | 1740 | 2011686 | 4367 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 216729 | 37.0886 | -121.9844 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036210 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | Yes | Yes | 1818940 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 6771 | 20230225 | 1707 | 20230225 | 1718 | 2008977 | 11 | Distribution Circuit | Company Initiated | Coordination failure | 53 | 583 | 36.8682 | -121.6457 | Yes | Clear;32-90F | Cutout- fuse holder | Normal | 23-0035386 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1818226 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 3347 | 20230225 | 1802 | 20230226 | 811 | 2009086 | 849 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 28866 | 36.8707 | -121.6898 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0035606 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1818456 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | TRANSFORMER | T2654 | 20230225 | 2041 | 20230226 | 1121 | 2009308 | 880 | Distribution Circuit | Equipment Failure/Involved | Underground | 44 | 19888 | 36.7112 | -121.6368 | Yes | Clear;32-90 F | Transformer (UG) | Broken | 23-0035510 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1818358 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | FUSE | 8981 | 20230226 | 304 | 20230226 | 1013 | 2009574 | 313 | Distribution Circuit | 3rd Party | Vehicle | 201 | 74027 | 36.3259 | -121.2421 | Yes | Clear;32-90 F | Anchor or Guy | Broken | 23-0035586 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1818439 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 4209 | 20230226 | 503 | 20230301 | 1705 | 2009845 | 5042 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 35294 | 37.1061 | -121.9723 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035650 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818493 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | RECLOSER | 9096 | 20230226 | 653 | 20230226 | 811 | 2009651 | 78 | Distribution Circuit | 3rd Party | Vehicle | 2672 | 208416 | 36.5951 | -121.8454 | Yes | Overcast;32-90 F | Anchor or Guy | Broken | 23-0035593 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1818445 | 0 | EPSS Ckt | N | 2023 | C-GRD
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 4619 | 20230226 | 754 | 20230226 | 1214 | 2009700 | 260 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 2600 | 37.0394 | -122.0314 | Yes | Overcast-Fog;32-90 F |  |  | 23-0035708 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1818547 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | TRANSFORMER | 315203320758 | 20230226 | 854 | 20230226 | 1223 | 2009745 | 209 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 418 | 37.0586 | -122.145 | Yes | Clear;32-90F |  |  | 23-0035723 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1818563 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 5351 | 20230226 | 855 | 20230226 | 1726 | 2009747 | 511 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 10220 | 37.0009 | -122.0209 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0035390 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1818464 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9771 | 20230226 | 930 | 20230226 | 1140 | 2009789 | 130 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 38 | 4940 | 37.1313 | -122.1209 | Yes | Overcast-Drizzle;32-90 F |  |  | 23-0035689 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1818532 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRANSFORMER | 315316324154 | 20230226 | 958 | 20230301 | 1621 | 2009818 | 4703 | Transformer only | Vegetation | Tree - fell into line | 1 | 4703 | 37.1515 | -122.1079 | Yes | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0036417 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1819060 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6647 | 20230226 | 1038 | 20230226 | 1515 | 2009862 | 277 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 5817 | 37.0266 | -121.7801 | Yes | Clear;32-90F | Pole-Wood | Deteriorated | 23-0035662 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1818505 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | TRANSFORMER | 412289939575 | 20230226 | 1050 | 20230227 | 1750 | 2010717 | 1860 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 3720 | 36.3914 | -121.6212 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0036051 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1818857 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRANSFORMER | 315163824880 | 20230226 | 1146 | 20230227 | 1519 | 2012628 | 1653 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 4959 | 37.1713 | -122.1609 | Yes | Clear;32-90F |  |  | 23-0036502 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1819106 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | OTHER | WIRE DOWN | 20230226 | 1420 | 20230227 | 312 | 2010197 | 772 | Distribution Circuit | Vegetation | Tree - branch fell on line | 112 | 80470 | 37.0034 | -121.9013 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035809 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | Yes | Yes | 1818626 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 51741 | 20230226 | 1516 | 20230226 | 1644 | 2010249 | 88 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 4 | 352 | 37.1746 | -122.1636 | Yes | Clear;32-90F |  |  | 23-0035852 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1818674 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9761 | 20230226 | 1525 | 20230227 | 1048 | 2010261 | 1163 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 3489 | 37.1729 | -122.1638 | Yes | Clear;32-90F |  |  | 23-0036251 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1818963 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 4749 | 20230226 | 1711 | 20230228 | 1345 | 2010411 | 2674 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 8022 | 37.0921 | -122.1146 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036168 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818914 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | RECLOSER | 11046 | 20230226 | 1802 | 20230227 | 1146 | 2010532 | 1064 | Distribution Circuit | Vegetation | Tree - branch fell on line | 353 | 148016 | 36.9995 | -122.0078 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035893 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1818707 | 0 | EPSS Ckt | N | 2023 | AB
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRANSFORMER | 315230624378 | 20230226 | 1829 | 20230228 | 1921 | 2010702 | 2932 | Transformer only | Vegetation | Tree - branch fell on line | 7 | 20524 | 37.1584 | -122.1349 | Yes | Overcast-Heavy Rain;32-90 F | Transformer | Broken- wire on ground | 23-0036227 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818949 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | FUSE | 43809 | 20230226 | 2104 | 20230226 | 2245 | 2010942 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 46 | 4646 | 36.8073 | -121.4119 | Yes | Overcast-Drizzle;32-90 F |  |  | 23-0036045 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1818850 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | SWITCH | 2881 | 20230227 | 329 | 20230227 | 337 | 2011142 | 8 | Distribution Circuit | Company Initiated | Return Circuit Normal | 7 | 56 | 37.018 | -121.8957 | Yes | Clear;32-90F | Switch (OH) | Normal | 23-0035809 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1818863 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 5143 | 20230227 | 1016 | 20230227 | 1213 | 2011752 | 117 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 3159 | 37.0994 | -122.0868 | Yes | Clear;32-90F |  |  | 23-0036373 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1819033 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | PANOCHE-1103 | 253671103 | OCB | 1103/2 | 20230227 | 1018 | 20230227 | 1316 | 2011796 | 178 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 209 | 37202 | 36.6512 | -120.5803 | Yes | Clear;32-90F |  |  | 23-0036261 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1818967 | 0 | EPSS Ckt | N | 2023 | A-C
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | TRANSFORMER | 411982942173 | 20230227 | 1106 | 20230228 | 1347 | 2011694 | 1601 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 9606 | 36.4614 | -121.7275 | Yes | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0036315 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1819004 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315766020335 | 20230227 | 1111 | 20230228 | 1725 | 2013501 | 1814 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 1889 | 37.0493 | -121.9521 | Yes | Clear;32-90F | Transformer (OH) | Normal | 23-0037143 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1819624 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | JUMPER | OPEN CIRCUIT BURNED OJ C PHASE @ 1275 | 20230227 | 1118 | 20230228 | 249 | 2012221 | 931 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1236 | 400474 | 36.9666 | -121.892 | Yes | Overcast-Fog-Rain;32-90 F | Jumper | Burned Open | 23-0036400 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1819050 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 9569 | 20230227 | 1132 | 20230228 | 1705 | 2012007 | 1773 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 72693 | 36.9783 | -121.8269 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036461 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1819085 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | FUSE | 4763 | 20230227 | 1144 | 20230227 | 1514 | 2012059 | 210 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1049 | 36.9852 | -121.9157 | Yes | Clear;32-90F |  |  | 23-0036567 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1819150 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1103 | 182131103 | TRANSFORMER | 412834143588 | 20230227 | 1250 | 20230227 | 2047 | 2012410 | 477 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 477 | 36.5056 | -121.4397 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0036563 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1819147 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 8045 | 20230227 | 1400 | 20230227 | 1550 | 2012609 | 110 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 110 | 36.5039 | -121.9353 | Yes | Clear;32-90F |  |  | 23-0036578 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1819162 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | OTHER | WIRE DOWN WEST OF 3415 | 20230227 | 1534 | 20230228 | 310 | 2012894 | 696 | Distribution Circuit | Equipment Failure/Involved | Overhead | 562 | 363253 | 36.9606 | -121.8866 | Yes | Overcast-Rain;32-90 F | Connector or Splice (OH) | Broken | 23-0036633 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1819205 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | TRANSFORMER | 411850133792 | 20230227 | 1558 | 20230227 | 1610 | 2012669 | 12 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 12 | 36.2322 | -121.7649 | Yes | Clear;32-90F | Bushing | Arcing | 23-0036620 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1819192 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | FUSE | 6713 | 20230227 | 1609 | 20230228 | 1549 | 2012964 | 1420 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 126380 | 36.4702 | -121.7242 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0036675 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1819239 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | MTR#1008451371 | 20230227 | 1849 | 20230228 | 1053 | 2013153 | 964 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 964 | 36.9947 | -121.7594 | Yes | Clear;32-90 F | Transformer | Arcing | 23-0036726 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1819286 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | OCB | 2201/2 | 20230227 | 1902 | 20230301 | 6 | 2013598 | 1744 | Distribution Circuit | Equipment Failure/Involved | Overhead | 859 | 161070 | 36.5786 | -121.9085 | Yes | Partly Cloudy-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0036739 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | Yes | No | 1819298 | 0 | EPSS Ckt | N | 2023 | AB GRD
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 6033 | 20230227 | 2020 | 20230228 | 1120 | 2013857 | 900 | Distribution Circuit | Vegetation | Tree - branch fell on line | 82 | 73800 | 37.081 | -122.0049 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036837 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1819381 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 412039054545 | 20230227 | 2038 | 20230228 | 1440 | 2014667 | 1082 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 1082 | 36.8017 | -121.7208 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0037210 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1819667 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 9423 | 20230227 | 2040 | 20230228 | 947 | 2013831 | 787 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 22036 | 37.077 | -122.0862 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0037186 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1819654 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 10294 | 20230228 | 24 | 20230302 | 1759 | 2014062 | 3935 | Distribution Circuit | Vegetation | Tree - fell into line | 306 | 198429 | 37.0992 | -122.053 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037039 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1819573 | 0 | EPSS Ckt | N | 2023 | B C
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 2443 | 20230228 | 341 | 20230228 | 348 | 2014099 | 7 | Distribution Circuit | Company Initiated | Return Circuit Normal | 589 | 4123 | 36.9574 | -121.8831 | Yes | Clear;32-90F | Fuse | Normal | 23-0036633 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1819583 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 5397 | 20230228 | 342 | 20230301 | 1252 | 2015251 | 1990 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 45770 | 37.076 | -122.1429 | Yes | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0037338 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1819751 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 6087 | 20230228 | 919 | 20230301 | 1009 | 2014635 | 1437 | Distribution Circuit | Vegetation | Tree - fell into line | 186 | 122981 | 37.0665 | -122.0336 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037242 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1819690 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 412037554546 | 20230228 | 935 | 20230228 | 1445 | 2014678 | 310 | Transformer only | Equipment Failure/Involved | Electrical Overload | 5 | 1550 | 36.8016 | -121.7213 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0037217 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1819671 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 12586 | 20230228 | 1022 | 20230228 | 2035 | 2014848 | 613 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1069 | 83697 | 36.9733 | -121.888 | Yes | Overcast-Fog-Drizzle;32-90 F | Insulator | Burned/flashed | 23-0037237 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1819684 | 0 | EPSS Ckt | N | 2023 | b ph grd
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRANSFORMER | 315207925801 | 20230228 | 1030 | 20230228 | 1512 | 2014867 | 282 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 282 | 37.1969 | -122.1462 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0037238 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1819688 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRANSFORMER | 315387520147 | 20230228 | 1116 | 20230228 | 2114 | 2014998 | 598 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 598 | 37.0426 | -122.0815 | Yes | Clear;32-90F |  |  | 23-0037765 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1820093 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 412066054677 | 20230228 | 1118 | 20230228 | 1520 | 2015001 | 242 | Transformer only | Equipment Failure/Involved | Electrical Overload | 5 | 1210 | 36.8039 | -121.7115 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0037396 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1819805 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 12758 | 20230228 | 1126 | 20230228 | 1326 | 2015031 | 120 | Distribution Circuit | Vegetation | Tree - branch fell on line | 256 | 30720 | 37.1486 | -122.1745 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0037278 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1819712 | 0 | EPSS Ckt | N | 2023 | UNKNOWN
CENTRAL COAST | COAST | BURNS SUB | 18358 | SWITCH | BURNS | 20230228 | 1205 | 20230228 | 1332 | 2015200 | 87 | Distribution Circuit | Vegetation | Tree - fell into line | 2568 | 223416 | 0 | 0 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036162 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1819747 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | POINT MORETTI SUB | 8293 | SWITCH | POINT MORETTI | 20230228 | 1206 | 20230228 | 1332 | 2015195 | 86 | Distribution Circuit | Vegetation | Tree - fell into line | 636 | 54696 | 0 | 0 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036162 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1819749 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 412081854485 | 20230228 | 1325 | 20230228 | 1731 | 2015637 | 246 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 246 | 36.7993 | -121.7061 | Yes | Lightening;32-90 F |  |  | 23-0037432 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1819829 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | FUSE | 553 | 20230228 | 1330 | 20230302 | 1433 | 2014955 | 2943 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 12161 | 36.0629 | -120.6454 | Yes | Clear;32-90F | Crossarm- Wood | Broken | 23-0037499 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1819870 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | RECLOSER | 11046 | 20230228 | 1345 | 20230228 | 1416 | 2015669 | 31 | Distribution Circuit | Vegetation | Tree - fell into line | 353 | 10643 | 36.9995 | -122.0078 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0037443 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1819831 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | KING CITY | KING CITY-1104 | 182031104 | TRANSFORMER | 413765131426 | 20230228 | 1448 | 20230301 | 1238 | 2015940 | 1310 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 2620 | 36.1791 | -121.1131 | Yes | Clear;32-90 F | Transformer | Burned/flashed | 23-0037632 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1819967 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 1831 | 20230228 | 1649 | 20230301 | 948 | 2016251 | 1019 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 43817 | 36.8143 | -121.7007 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037640 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1819977 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 5901 | 20230228 | 1753 | 20230301 | 915 | 2016435 | 922 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 14752 | 37.0944 | -121.9716 | Yes | Clear;32-90F | Fuse | Broken | 23-0038009 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1820305 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8161 | 20230228 | 1956 | 20230301 | 1550 | 2016725 | 1194 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 11940 | 37.1173 | -121.9748 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0037786 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1820114 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 9423 | 20230228 | 2019 | 20230228 | 2250 | 2016722 | 151 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 4228 | 37.077 | -122.0862 | Yes | Overcast-Rain;32-90 F |  |  | 23-0037848 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1820178 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9749 | 20230228 | 2213 | 20230228 | 2332 | 2017120 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 539 | 37.1489 | -122.157 | Yes | Clear;32-90F |  |  | 23-0037860 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1820188 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315708222583 | 20230228 | 2214 | 20230301 | 1240 | 2017121 | 866 | Transformer only | Vegetation | Tree - bark fell into line | 2 | 1732 | 37.1108 | -121.9727 | Yes | Clear;32-90 F | Transformer | Normal | 23-0038141 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1820383 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 6895 | 20230228 | 2318 | 20230303 | 1404 | 2017248 | 3766 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 7532 | 36.8382 | -121.7668 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0038016 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | Yes | No | 1820309 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 18441 | 20230301 | 36 | 20230301 | 53 | 2017346 | 17 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 85 | 37.1289 | -121.9772 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0037878 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1820210 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 6641 | 20230301 | 149 | 20230301 | 236 | 2017382 | 47 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 41 | 1927 | 36.6023 | -121.8968 | No | Partly Cloudy;32-90 F |  |  | 23-0037894 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1820227 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 1641 | 20230301 | 255 | 20230302 | 52 | 2017462 | 1317 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 68484 | 36.9326 | -121.8121 | No | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0037929 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1820259 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 316230318990 | 20230301 | 658 | 20230302 | 1117 | 2017672 | 1699 | Transformer only | Vegetation | Tree - fell into line | 3 | 5097 | 37.014 | -121.7923 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0038067 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1820334 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315728222828 | 20230301 | 800 | 20230301 | 1315 | 2017781 | 315 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 630 | 37.1177 | -121.9658 | No | Clear;32-90 F |  |  | 23-0038198 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1820428 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | FORT ORD-2107 | 182402107 | TRANSFORMER | 411821350143 | 20230301 | 1026 | 20230301 | 1341 | 2018023 | 195 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 195 | 36.6781 | -121.7911 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0038232 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1820458 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315663122934 | 20230301 | 1229 | 20230301 | 1246 | 2018178 | 17 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 17 | 37.1203 | -121.9881 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0038197 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1820427 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6641 | 20230301 | 1237 | 20230301 | 1535 | 2018269 | 178 | Distribution Circuit | Vegetation | Tree - branch fell on line | 77 | 13322 | 37.016 | -121.8161 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0038251 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1820472 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | SWITCH | 8737 | 20230301 | 1250 | 20230301 | 1358 | 2018279 | 68 | Distribution Circuit | Vegetation | Tree - grew into line | 918 | 56930 | 37.0447 | -122.0733 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0038172 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1820404 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 9923 | 20230301 | 1258 | 20230302 | 1526 | 2018327 | 1588 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2575 | 36.9399 | -121.3787 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0038216 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1820441 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | TRANSFORMER | 315326621786 | 20230301 | 1438 | 20230302 | 1141 | 2018473 | 1263 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 1263 | 37.0874 | -122.1029 | No | Clear;32-90 F | Transformer | Broken | 23-0038407 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1820605 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 7805 | 20230301 | 1603 | 20230303 | 1734 | 2018141 | 2971 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 5942 | 37.2144 | -122.1493 | No | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038093 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1820355 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 6875 | 20230301 | 1734 | 20230301 | 1946 | 2018870 | 132 | Distribution Circuit | Vegetation | Tree - fell into line | 102 | 13464 | 36.8864 | -121.6325 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0038317 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1820583 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | TRIP-SAVER | 2179 | 20230301 | 1829 | 20230301 | 2027 | 2018983 | 118 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 557 | 65726 | 36.6263 | -121.928 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0038394 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1820622 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 11237 | 20230301 | 1929 | 20230301 | 2220 | 2019123 | 171 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 684 | 37.0904 | -121.9645 | No | Clear;32-90F |  |  | 23-0038545 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1820728 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1106 | 182011106 | JUMPER | BELLS @ CGC 412179349287 | 20230301 | 1937 | 20230302 | 158 | 2019100 | 381 | Distribution Circuit | Vegetation | Tree - grew into line | 24 | 9144 | 36.6576 | -121.6678 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0038456 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1820645 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1103 | 182201103 | FUSE | 300151 | 20230301 | 2109 | 20230303 | 1210 | 2019216 | 2341 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 16387 | 36.6434 | -121.583 | No | Clear;32-90 F |  |  | 23-0039455 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1821301 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1102 | 182011102 | TRANSFORMER | T0364 | 20230301 | 2224 | 20230301 | 2259 | 2019265 | 35 | Transformer only | Equipment Failure/Involved | Underground | 27 | 945 | 36.6847 | -121.62 | No | Clear;32-90F | Secondary | Burned/flashed | 23-0038540 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1820723 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | TRANSFORMER | 315224521671 | 20230302 | 934 | 20230302 | 1437 | 2019555 | 303 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 303 | 37.0838 | -122.1385 | No | Clear;32-90F |  |  | 23-0038854 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1820894 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 12297 | 20230302 | 1002 | 20230302 | 1716 | 2019546 | 434 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 16058 | 37.0477 | -122.0239 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0038643 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1820774 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1104 | 182201104 | TRANSFORMER | 412360847146 | 20230302 | 1017 | 20230302 | 1855 | 2019606 | 518 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1036 | 36.5999 | -121.6036 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0038743 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1820830 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | SWITCH | 8509 | 20230302 | 1143 | 20230302 | 1151 | 2019736 | 8 | Distribution Circuit | Company Initiated | Return Circuit Normal | 294 | 2352 | 36.9483 | -121.8512 | No | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0031348 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1820824 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | LOS GATOS-1107 | 82021107 | FUSE | 5873 | 20230302 | 1329 | 20230307 | 1608 | 2020197 | 7359 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 14718 | 37.0872 | -121.8616 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0038946 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1820956 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | TRANSFORMER | 315149720656 | 20230302 | 1418 | 20230302 | 1521 | 2019991 | 63 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 63 | 37.0555 | -122.1634 | No | Clear;32-90F |  |  | 23-0038927 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1820942 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | FUSE | 23161 | 20230302 | 1512 | 20230302 | 1610 | 2020094 | 58 | Distribution Circuit | Animal | Bird found | 4 | 232 | 36.4984 | -121.5015 | No | Clear;32-90F | Cutout- fuse holder | Normal | 23-0038955 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1820962 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | SWITCH | 10090SW | 20230302 | 1755 | 20230303 | 555 | 2020276 | 720 | Distribution Circuit | Vegetation | Tree - branch fell on line | 189 | 12940 | 36.9873 | -121.9213 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0039006 | OH | Sus | 35427331 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1821006 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | RECLOSER | 885736 | 20230302 | 1802 | 20230302 | 2008 | 2020373 | 126 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 438 | 55188 | 36.9937 | -121.9776 | No | Clear;32-90F |  |  | 23-0039024 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1821018 | 0 | EPSS Ckt | N | 2023 | C&GRD
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 5245 | 20230302 | 1807 | 20230302 | 1826 | 2020401 | 11 | Distribution Circuit | Company Initiated | Return Circuit Normal | 306 | 1017 | 37.1049 | -122.0553 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0037039 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1821027 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | TRANSFORMER | 316052519953 | 20230302 | 2147 | 20230302 | 2155 | 2020582 | 8 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 8 | 37.0401 | -121.8538 | No | Clear;32-90F |  |  | 23-0039170 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1821155 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 3921 | 20230303 | 616 | 20230303 | 746 | 2020727 | 90 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 203 | 18270 | 36.8382 | -121.6835 | No | Clear;32-90F |  |  | 23-0039242 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1821190 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 2901 | 20230303 | 805 | 20230303 | 938 | 2020837 | 93 | Distribution Circuit | Animal | Bird found | 146 | 13578 | 36.9671 | -122.0079 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Normal | 23-0039305 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1821214 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI SUB | 8293 | SWITCH | POINT MORETTI | 20230303 | 834 | 20230303 | 1814 | 2020930 | 580 | Distribution Circuit | Vegetation | Tree - fell into line | 670 | 388600 | 0 | 0 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039287 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1821207 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | TRANSFORMER | 411452746964 | 20230303 | 1002 | 20230303 | 1714 | 2021050 | 432 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 3456 | 36.5874 | -121.9134 | No | Clear;32-90F | Pole-Wood | Broken | 23-0039352 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1821238 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | FUSE | 4505 | 20230303 | 1008 | 20230303 | 1103 | 2021034 | 55 | Distribution Circuit | Equipment Failure/Involved | Underground | 24 | 1320 | 36.5615 | -121.7287 | No | Clear;32-90F | Elbow | Failed/Faulted | 23-0039346 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1821235 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 58573 | 20230303 | 1144 | 20230303 | 1507 | 2021222 | 201 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 3417 | 36.8133 | -121.6882 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0039564 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1821359 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 12887 | 20230303 | 1204 | 20230303 | 1315 | 2021269 | 71 | Distribution Circuit | Vegetation | Tree - branch fell on line | 42 | 2979 | 37.0385 | -122.0681 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0039475 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1821314 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO-1101 | 182191101 | OCB | 1101/2 | 20230303 | 1219 | 20230304 | 1738 | 2021288 | 1759 | Distribution Circuit | Equipment Failure/Involved | Overhead | 149 | 58531 | 36.0734 | -120.9364 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0039454 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | Yes | No | 1821300 | 0 | EPSS Ckt | N | 2023 | SET A RLY
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | FUSE | 4073 | 20230303 | 1515 | 20230304 | 1053 | 2021585 | 1178 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1178 | 36.9652 | -121.9674 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0039560 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1821356 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | TRANSFORMER | 100000086693 | 20230303 | 1601 | 20230303 | 2218 | 2021632 | 377 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 377 | 36.7104 | -121.7101 | No | Clear;32-90 F | Transformer | Broken | 23-0039638 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1821414 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRANSFORMER | 315162025513 | 20230303 | 1932 | 20230304 | 1223 | 2021860 | 1011 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2022 | 37.1887 | -122.1616 | No | Clear;32-90 F | Secondary | Broken | 23-0039716 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1821475 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 4135 | 20230304 | 51 | 20230304 | 158 | 2022029 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 107 | 7169 | 36.9256 | -121.3776 | No | Clear;32-90F |  |  | 23-0039847 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1821622 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | RECLOSER | 3030 | 20230304 | 135 | 20230304 | 1245 | 2022034 | 670 | Distribution Circuit | Equipment Failure/Involved | Overhead | 132 | 45175 | 36.5854 | -121.6002 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0039845 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1821620 | 1 | EPSS Ckt | N | 2023 | C PHASE GRD
CENTRAL COAST | COAST | PAUL SWEET-2108 | 83252108 | FUSE | 64109 | 20230304 | 614 | 20230304 | 707 | 2022051 | 53 | Distribution Circuit | Animal | Bird found | 293 | 15529 | 36.969 | -122.0263 | No | Clear;32-90F | Fuse | Burned Open | 23-0039866 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1821636 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | RECLOSER | 16004 | 20230304 | 810 | 20230304 | 1407 | 2022142 | 357 | Distribution Circuit | Animal | Bird found | 2290 | 122280 | 36.9589 | -122.0306 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039873 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | Yes | No | 1821642 | 0 | EPSS Ckt | N | 2023 | AB GRD
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRANSFORMER | 315151925569 | 20230304 | 929 | 20230304 | 1407 | 2022201 | 278 | Transformer only | Vegetation | Tree - fell into line | 4 | 1112 | 37.1895 | -122.1656 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0039943 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1821700 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | TRANSFORMER | 411494647856 | 20230304 | 1026 | 20230304 | 1408 | 2022247 | 222 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 222 | 36.6129 | -121.8997 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0039953 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1821708 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 9423 | 20230304 | 1114 | 20230304 | 1335 | 2022306 | 141 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 3948 | 37.077 | -122.0862 | No | Overcast-Rain;32-90 F | Fuse | Normal | 23-0039997 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1821751 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412278455238 | 20230304 | 1143 | 20230304 | 1618 | 2022351 | 275 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 1650 | 36.8216 | -121.6398 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0039983 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1821739 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | OTHER | 11797 | 20230304 | 1150 | 20230304 | 1932 | 2022372 | 462 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 6920 | 36.8677 | -121.7087 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039986 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | Yes | 1821742 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRANSFORMER | 315162025513 | 20230304 | 1512 | 20230305 | 1353 | 2022588 | 1361 | Transformer only | Vegetation | Tree - fell into line | 2 | 2722 | 37.1887 | -122.1616 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0040065 | OH | Sus | 35427331 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1821808 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0422 | 182440422 | TRANSFORMER | 411458347972 | 20230304 | 1612 | 20230305 | 1013 | 2022552 | 1081 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 19458 | 36.6152 | -121.9127 | No | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0040031 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1821780 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | TRANSFORMER | 315540319150 | 20230304 | 1646 | 20230305 | 952 | 2022710 | 1026 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 4104 | 37.0154 | -122.028 | No | Clear;32-90 F |  |  | 23-0040043 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1821788 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | FUSE | 5615 | 20230304 | 1918 | 20230305 | 1002 | 2022954 | 884 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 125 | 110260 | 36.7281 | -121.6432 | No | Clear;32-90 F |  |  | 23-0040112 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1821859 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 6477 | 20230304 | 1939 | 20230304 | 2202 | 2022895 | 143 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 426 | 60918 | 36.8655 | -121.7346 | No | Clear;32-90 F |  |  | 23-0040164 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1821912 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 6891 | 20230304 | 2304 | 20230305 | 126 | 2022989 | 142 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 568 | 36.8847 | -121.7956 | No | Clear;32-90F |  |  | 23-0040184 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1821932 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 1153 | 20230305 | 342 | 20230305 | 800 | 2023182 | 258 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 146 | 37668 | 36.9786 | -121.8924 | No | Overcast-Fog-Rain;32-90 F |  |  | 23-0040229 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1821978 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 974520 | 20230305 | 424 | 20230305 | 836 | 2023204 | 252 | Distribution Circuit | Vegetation | Tree - branch fell on line | 330 | 80163 | 36.9908 | -121.8063 | No | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 23-0040211 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1821960 | 0 | EPSS Ckt | N | 2023 | BC
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 717229 | 20230305 | 447 | 20230305 | 1104 | 2023215 | 377 | Distribution Circuit | Equipment Failure/Involved | Overhead | 154 | 23545 | 36.873 | -121.8196 | No | Partly Cloudy-Heavy Rain;32-90 F | Connector or Splice (OH) | Broken | 23-0040299 | OH | Sus | 35427331 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1822037 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | RECLOSER | BL 1101 | 20230305 | 825 | 20230306 | 300 | 2023430 | 1115 | Distribution Circuit | Vegetation | Tree - fell into line | 743 | 107253 | 37.0926 | -122.0966 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0040252 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1822000 | 0 | EPSS Ckt | N | 2023 | C- GRD
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 1171 | 20230305 | 929 | 20230305 | 1311 | 2023510 | 222 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 222 | 37.0275 | -121.841 | No | Clear;32-90 F |  |  | 23-0040364 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1822089 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5501 | 20230305 | 1356 | 20230305 | 1530 | 2023811 | 94 | Distribution Circuit | Vegetation | Tree - branch fell on line | 142 | 13348 | 37.1431 | -122.1318 | No | Clear;32-90 F | Fuse | Normal | 23-0040400 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1822135 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2108 | 83252108 | FUSE | FUCO 90387 | 20230305 | 1705 | 20230305 | 1946 | 2024061 | 161 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1932 | 36.969 | -122.0238 | No | Clear;32-90F |  |  | 23-0040450 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1822184 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | SWITCH | 2681 | 20230306 | 141 | 20230306 | 415 | 2024199 | 154 | Distribution Circuit | Vegetation | Tree - fell into line | 199 | 30646 | 36.9905 | -121.8953 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0040533 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1822271 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 10427 | 20230306 | 312 | 20230306 | 2025 | 2024484 | 1033 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1033 | 37.1044 | -122.0502 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0040624 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1822328 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 412049654666 | 20230306 | 1157 | 20230306 | 1615 | 2024400 | 258 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 258 | 36.805 | -121.7174 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0040705 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1822362 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 9423 | 20230306 | 1911 | 20230306 | 2050 | 2025097 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 2492 | 37.077 | -122.0862 | No | Clear;32-90F |  |  | 23-0040972 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1822514 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | SWITCH | 6697 | 20230306 | 2257 | 20230307 | 338 | 2025168 | 281 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 843 | 36.8627 | -121.6303 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0040999 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1822534 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 5959 | 20230307 | 221 | 20230307 | 1515 | 2025192 | 774 | Distribution Circuit | Equipment Failure/Involved | Underground | 23 | 18069 | 36.8149 | -121.626 | No | Clear;32-90F | Conductor- Underground | Broken | 23-0041008 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1822546 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO-1101 | 182191101 | RECLOSER | 7054 | 20230307 | 1019 | 20230307 | 1527 | 2025457 | 308 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 6160 | 36.1127 | -121.0362 | No | Clear;32-90F | Pole-Wood | Broken | 23-0041108 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1822602 | 0 | EPSS Ckt | N | 2023 | C GRD
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | OTHER | HOT WIRE DOWN @ 14726 CASTROVILLE BLVD | 20230307 | 1205 | 20230308 | 150 | 2025570 | 825 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 825 | 36.7954 | -121.7183 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0041287 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | Yes | Yes | 1822654 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS COCHES-1102 | 182151102 | OTHER | 7717 | 20230307 | 1525 | 20230307 | 2315 | 2025654 | 470 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 3289 | 36.3588 | -121.2541 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0041299 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | Yes | Yes | 1822659 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | FUSE | 25489 | 20230307 | 1618 | 20230308 | 245 | 2025866 | 627 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 627 | 36.5234 | -121.4668 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0041332 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1822670 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 5411 | 20230307 | 2025 | 20230308 | 415 | 2026033 | 470 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 7990 | 37.0548 | -122.161 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0041393 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1822722 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 9423 | 20230307 | 2136 | 20230307 | 2327 | 2026061 | 111 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 3108 | 37.077 | -122.0862 | No | Clear;32-90F |  |  | 23-0041443 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1822773 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | FUSE | 50975 | 20230307 | 2302 | 20230308 | 1509 | 2026103 | 967 | Distribution Circuit | 3rd Party | Vehicle | 42 | 23754 | 36.8448 | -121.4566 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0041448 | OH | Sus | 35430946 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1822779 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 11427 | 20230308 | 701 | 20230309 | 330 | 2026262 | 1229 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 6145 | 37.0545 | -122.0222 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0041541 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1822837 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | TRANSFORMER | 315915717513 | 20230308 | 1643 | 20230308 | 2250 | 2026911 | 367 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 367 | 36.9723 | -121.8978 | No | Clear;32-90F | Connector or Splice (OH) | Burned Open | 23-0041809 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1822963 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 9423 | 20230308 | 1827 | 20230308 | 1934 | 2027006 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 1876 | 37.077 | -122.0862 | No | Clear;32-90F |  |  | 23-0041845 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1822985 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 4853 | 20230308 | 1829 | 20230308 | 2032 | 2027011 | 123 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1107 | 36.9751 | -121.8161 | No | Clear;32-90F |  |  | 23-0041850 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1822989 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | TRANSFORMER | 315289122075 | 20230308 | 2129 | 20230309 | 1057 | 2027106 | 808 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 808 | 37.0948 | -122.1143 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0041901 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823041 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS COCHES 1101 | 182151101 | RECLOSER | 625902 | 20230309 | 611 | 20230309 | 955 | 2027186 | 224 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 4032 | 36.3482 | -121.3219 | Yes | Clear;32-90F | Recloser | Burned/flashed | 23-0041916 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823052 | 0 | EPSS Ckt | N | 2023 | A & C PHASE
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 231 | 20230309 | 1026 | 20230309 | 1543 | 2027308 | 317 | Distribution Circuit | Vegetation | Tree - grew into line | 2 | 634 | 37.0512 | -121.9788 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0041991 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1823073 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 6477 | 20230309 | 1430 | 20230309 | 1528 | 2027780 | 58 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 425 | 24650 | 36.8655 | -121.7346 | Yes | Clear;32-90F |  |  | 23-0042276 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823162 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1109 | 182011109 | FUSE | 948327 | 20230309 | 1546 | 20230309 | 1645 | 2027945 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 531 | 36.6776 | -121.5908 | Yes | Clear;32-90F |  |  | 23-0042342 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823191 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 5997 | 20230309 | 1613 | 20230309 | 1730 | 2028012 | 77 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 1232 | 36.7882 | -121.6799 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 23-0042382 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823222 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 8087 | 20230309 | 1615 | 20230309 | 1703 | 2028015 | 48 | Distribution Circuit | Equipment Failure/Involved | Overhead | 70 | 3360 | 36.5284 | -121.9199 | Yes | Clear;32-90 F | Cutout- fuse holder | Normal | 23-0042338 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1823189 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 40581 | 20230309 | 1720 | 20230312 | 1221 | 2030980 | 4021 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 229197 | 36.5672 | -121.9132 | Yes | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043073 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823722 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | OCB | 1101/2 | 20230309 | 1727 | 20230312 | 1325 | 2028242 | 2847 | Distribution Circuit | Vegetation | Tree - fell into line | 3500 | 5747167 | 36.5569 | -121.8976 | Yes | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042371 | OH | Sus | 35431167 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823211 | 0 | EPSS Ckt | N | 2023 | B-GRD
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 40425 | 20230309 | 1727 | 20230311 | 1826 | 2032276 | 2939 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2939 | 36.5479 | -121.8968 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0043416 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1823983 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 629 | 20230309 | 1727 | 20230312 | 1459 | 2032302 | 4172 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 66752 | 36.5473 | -121.8977 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043419 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823985 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 627 | 20230309 | 1727 | 20230312 | 1424 | 2032306 | 4137 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 91014 | 36.5489 | -121.8966 | Yes | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0043420 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823986 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1109 | 182011109 | JUMPER | 3659 | 20230309 | 1727 | 20230309 | 2015 | 2028250 | 168 | Distribution Circuit | Equipment Failure/Involved | Overhead | 418 | 68693 | 36.6725 | -121.6165 | Yes | Overcast-Rain-Strong Winds;32-90 F | Jumper | Burned Open | 23-0042381 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1823221 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 45255 | 20230309 | 1732 | 20230311 | 2021 | 2028290 | 3049 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 118911 | 36.5862 | -121.9149 | Yes | Overcast;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0042435 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823268 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1101 | 182131101 | FUSE | 575199 | 20230309 | 1736 | 20230310 | 1007 | 2028618 | 991 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1982 | 36.5314 | -121.422 | Yes | Clear;32-90 F | Transformer (OH) | Broken | 23-0042502 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823325 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 1491 | 20230309 | 1736 | 20230313 | 1723 | 2032459 | 5747 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 229880 | 36.5057 | -121.9352 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043471 | OH | Sus | 35431167 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824026 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 8259 | 20230309 | 1742 | 20230313 | 1301 | 2033491 | 5479 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 136975 | 36.5764 | -121.968 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043771 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1824284 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | OCB | 2202/2 | 20230309 | 1745 | 20230311 | 2055 | 2028882 | 3070 | Distribution Circuit | Vegetation | Tree - fell into line | 5351 | 16139464 | 36.5786 | -121.9085 | Yes | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 23-0042465 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | Yes | No | 1823292 | 0 | EPSS Ckt | N | 2023 | A-B-C GRD
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 7101 | 20230309 | 1745 | 20230312 | 1242 | 2032175 | 4017 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 128544 | 36.5877 | -121.9125 | Yes | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043395 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1823962 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 1431 | 20230309 | 1745 | 20230313 | 2151 | 2032762 | 6006 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 54054 | 36.5682 | -121.9526 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043539 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824079 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | FUSE | 3279 | 20230309 | 1758 | 20230309 | 2220 | 2028434 | 262 | Distribution Circuit | Equipment Failure/Involved | Overhead | 143 | 37572 | 36.7102 | -121.6249 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Together | 23-0042436 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823269 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | RECLOSER | 648928 | 20230309 | 1759 | 20230312 | 1620 | 2028445 | 4221 | Distribution Circuit | Vegetation | Tree - fell into line | 291 | 954465 | 36.5332 | -121.9152 | Yes | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0042398 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | Yes | No | 1823236 | 0 | EPSS Ckt | N | 2023 | BC GRD
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | RECLOSER | 2010 | 20230309 | 1759 | 20230315 | 1958 | 2028313 | 8759 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 687648 | 36.5058 | -121.936 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0042398 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1823241 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | TRANSFORMER | 315828917874 | 20230309 | 1803 | 20230309 | 1918 | 2028451 | 75 | Transformer only | Vegetation | Tree - branch fell on line | 6 | 450 | 36.9819 | -121.928 | Yes | Overcast-Heavy Rain;32-90 F | Fuse | Normal | 23-0042494 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823318 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 5457 | 20230309 | 1804 | 20230309 | 2053 | 2028457 | 169 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 3042 | 37.1376 | -122.1414 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0042549 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823367 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 393582 | 20230309 | 1805 | 20230311 | 1155 | 2028462 | 2510 | Distribution Circuit | Vegetation | Tree - fell into line | 635 | 764971 | 37.1284 | -122.1222 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042406 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1823244 | 0 | EPSS Ckt | N | 2023 | ABC
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6541 | 20230309 | 1814 | 20230310 | 1818 | 2028494 | 1444 | Distribution Circuit | 3rd Party | Customer Equipment | 3 | 4332 | 36.9117 | -121.8303 | Yes | Clear;32-90 F | Fuse | Burned Open | 23-0042478 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823302 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 2553 | 20230309 | 1819 | 20230313 | 1904 | 2033542 | 5805 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 197370 | 36.5766 | -121.97 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043775 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824288 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | JUMPER | DDE @ CGC#411569746830 | 20230309 | 1825 | 20230312 | 1912 | 2031538 | 4367 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 52404 | 36.5847 | -121.873 | Yes | Partly Cloudy;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0043241 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823831 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | OCB | 2204/2 | 20230309 | 1837 | 20230311 | 2123 | 2028740 | 3046 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4884 | 6190135 | 36.5786 | -121.9084 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042443 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1823275 | 0 | EPSS Ckt | N | 2023 | TIME OC
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 2371 | 20230309 | 1837 | 20230311 | 1803 | 2029708 | 2846 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 136608 | 36.5818 | -121.9091 | Yes | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0042641 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1823451 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | SWITCH | 65671 | 20230309 | 1838 | 20230313 | 1018 | 2033174 | 5260 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 94680 | 36.603 | -121.942 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043669 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1824202 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | RECLOSER | 2634 | 20230309 | 1844 | 20230311 | 1316 | 2028648 | 2552 | Distribution Circuit | Vegetation | Tree - branch fell on line | 237 | 604824 | 36.5669 | -121.9134 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042442 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1823274 | 0 | EPSS Ckt | N | 2023 | AB
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | TRANSFORMER | 411436346256 | 20230309 | 1844 | 20230311 | 1716 | 2032330 | 2792 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 44672 | 36.568 | -121.9181 | Yes | Clear;32-90 F | Secondary | Broken | 23-0043431 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1823994 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 6809 | 20230309 | 1845 | 20230312 | 1921 | 2030540 | 4356 | Distribution Circuit | Vegetation | Tree - fell into line | 180 | 784080 | 36.573 | -121.9271 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 23-0042858 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823621 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 8917 | 20230309 | 1845 | 20230312 | 1927 | 2031107 | 4362 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 91602 | 36.5771 | -121.9274 | Yes | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0043129 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1823747 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | JUMPER | OJ @ CGC#411386246834 | 20230309 | 1845 | 20230313 | 1808 | 2031327 | 5723 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 22892 | 36.5831 | -121.9345 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0043187 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1823784 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 10421 | 20230309 | 1846 | 20230312 | 1927 | 2033166 | 4361 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 69776 | 36.5659 | -121.9346 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0043667 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1824201 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | RECLOSER | 573610 | 20230309 | 1846 | 20230313 | 56 | 2028642 | 4690 | Distribution Circuit | Vegetation | Tree - fell into line | 1098 | 5149620 | 36.5609 | -121.9196 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042434 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | Yes | No | 1823267 | 0 | EPSS Ckt | N | 2023 | ABC GRD
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | RECLOSER | 947314 | 20230309 | 1846 | 20230311 | 1713 | 2028674 | 2787 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 50166 | 36.5608 | -121.9196 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042437 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | Yes | No | 1823270 | 0 | EPSS Ckt | N | 2023 | ABC GRD
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 2881 | 20230309 | 1846 | 20230313 | 57 | 2031336 | 4691 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 417499 | 36.5419 | -121.9303 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043189 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1823785 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 2763 | 20230309 | 1846 | 20230313 | 57 | 2031414 | 4691 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 154803 | 36.5575 | -121.9252 | Yes | Partly Cloudy;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0043206 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1823799 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | SWITCH | 8283 | 20230309 | 1846 | 20230313 | 156 | 2031488 | 4750 | Distribution Circuit | Vegetation | Tree - fell into line | 745 | 3514108 | 36.5607 | -121.9207 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043229 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823819 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | TRANSFORMER | 411347546698 | 20230309 | 1848 | 20230312 | 2100 | 2031484 | 4452 | Transformer only | Environmental/External | Flood/Erosion | 5 | 22260 | 36.5793 | -121.9487 | Yes | Clear;32-90 F | Transformer | Broken | 23-0043226 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823817 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 2625 | 20230309 | 1849 | 20230311 | 1358 | 2029502 | 2589 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 196764 | 36.5921 | -121.9012 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042582 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823400 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | RECLOSER | 92792 | 20230309 | 1852 | 20230313 | 1725 | 2031477 | 5640 | Distribution Circuit | Vegetation | Tree - fell into line | 159 | 765694 | 36.5898 | -121.9457 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043224 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1823816 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | OCB | 2201/2 | 20230309 | 1853 | 20230312 | 1927 | 2028721 | 4354 | Distribution Circuit | Vegetation | Tree - branch fell on line | 938 | 417211 | 36.5786 | -121.9085 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042451 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1823280 | 0 | EPSS Ckt | N | 2023 | ABC
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 2799 | 20230309 | 1853 | 20230312 | 1927 | 2032456 | 4354 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 26124 | 36.5731 | -121.9443 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043469 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1824025 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | RECLOSER | 22160 | 20230309 | 1856 | 20230310 | 1311 | 2028760 | 1095 | Distribution Circuit | Vegetation | Tree - fell into line | 1548 | 792758 | 36.7971 | -121.6669 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0042446 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823276 | 0 | EPSS Ckt | N | 2023 | A B GRD
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | FUSE | 5561 | 20230309 | 1938 | 20230312 | 1048 | 2029032 | 3790 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 75800 | 36.7763 | -121.5987 | Yes | Clear;32-90 F |  |  | 23-0042606 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823419 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9765 | 20230309 | 1940 | 20230310 | 1220 | 2029043 | 1000 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 14000 | 37.1269 | -122.1291 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042537 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1823356 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 427 | 20230309 | 1944 | 20230310 | 2351 | 2031195 | 1687 | Distribution Circuit | Vegetation | Tree - fell into line | 440 | 742280 | 36.5224 | -121.806 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043155 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823761 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 10209 | 20230309 | 1944 | 20230311 | 1612 | 2031739 | 2668 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 18676 | 36.5226 | -121.8035 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0043317 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1823902 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | RECLOSER | 36720 | 20230309 | 1945 | 20230310 | 2351 | 2029114 | 1686 | Distribution Circuit | Vegetation | Tree - branch fell on line | 987 | 1664082 | 36.5217 | -121.7921 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042491 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823314 | 0 | EPSS Ckt | N | 2023 | A-GRD
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | RECLOSER | 9500 | 20230309 | 1946 | 20230310 | 1719 | 2029098 | 1293 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 270 | 349110 | 36.5582 | -121.7507 | Yes | Clear;32-90 F |  |  | 23-0042496 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823320 | 0 | EPSS Ckt | N | 2023 | A-GRD
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 6689 | 20230309 | 1954 | 20230310 | 902 | 2029126 | 788 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 8668 | 36.8881 | -121.8071 | Yes | Clear;32-90 F |  |  | 23-0042528 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823348 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 8625 | 20230309 | 1954 | 20230313 | 2029 | 2032200 | 5795 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 11590 | 36.5405 | -121.902 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0042519 | OH | Sus | 35431167 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823971 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | RECLOSER | 440 | 20230309 | 2007 | 20230310 | 1922 | 2028649 | 1395 | Distribution Circuit | Vegetation | Tree - fell into line | 378 | 155630 | 36.4389 | -121.9203 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0042504 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823327 | 0 | EPSS Ckt | N | 2023 | C GRD
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 869103 | 20230309 | 2019 | 20230310 | 1226 | 2029228 | 967 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 9670 | 36.8211 | -121.7285 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042638 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823448 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 2283 | 20230309 | 2019 | 20230312 | 849 | 2029179 | 3630 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 278034 | 36.5564 | -121.9087 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042510 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1823331 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | OCB | 1102/2 | 20230309 | 2022 | 20230313 | 2029 | 2029262 | 4403 | Distribution Circuit | Vegetation | Tree - fell into line | 1732 | 5258906 | 36.5569 | -121.8976 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042519 | OH | Sus | 35431167 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823338 | 0 | EPSS Ckt | N | 2023 | B-GRD
CENTRAL COAST | SALINAS | SALINAS-1103 | 182011103 | TRANSFORMER | 412212450621 | 20230309 | 2022 | 20230310 | 1926 | 2029237 | 1384 | Transformer only | Vegetation | Tree - grew into line | 12 | 16608 | 36.6941 | -121.6579 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0042550 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823368 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | FUSE | 23113 | 20230309 | 2023 | 20230310 | 914 | 2029240 | 771 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 6939 | 36.5963 | -121.621 | Yes | Overcast-Strong Winds;32-90 F |  |  | 23-0042570 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823389 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9181 | 20230309 | 2025 | 20230310 | 1255 | 2029821 | 990 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 13860 | 37.2288 | -122.148 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042690 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1823499 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | BORONDA-1101 | 182461101 | FUSE | 23707 | 20230309 | 2025 | 20230309 | 2128 | 2029255 | 63 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 32 | 2016 | 36.702 | -121.6753 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0042579 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823396 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412218854252 | 20230309 | 2034 | 20230310 | 1545 | 2029323 | 1151 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 1151 | 36.7943 | -121.6592 | Yes | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0042624 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823436 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | OCB | 2103/2 | 20230309 | 2047 | 20230313 | 1134 | 2028658 | 5207 | Distribution Circuit | Vegetation | Tree - fell into line | 4507 | 5417479 | 36.5991 | -121.8542 | Yes | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0042534 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823354 | 0 | EPSS Ckt | N | 2023 | B-GRD
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 5807 | 20230309 | 2053 | 20230310 | 1828 | 2029342 | 1295 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 64750 | 36.9746 | -121.8839 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0042614 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823427 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | RECLOSER | BL 1101 | 20230309 | 2057 | 20230309 | 2222 | 2029354 | 85 | Distribution Circuit | Vegetation | Tree - branch fell on line | 743 | 53035 | 37.0926 | -122.0966 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0042538 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823357 | 0 | EPSS Ckt | N | 2023 | B C
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | FUSE | 4623 | 20230309 | 2108 | 20230309 | 2217 | 2029383 | 69 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 154 | 10626 | 36.6753 | -121.6695 | Yes | Overcast-Strong Winds;32-90 F |  |  | 23-0042599 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823413 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | OCB | 2105/2 | 20230309 | 2119 | 20230311 | 807 | 2029420 | 2088 | Distribution Circuit | Vegetation | Tree - fell into line | 12820 | 21875760 | 36.5991 | -121.8541 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0042592 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1823409 | 0 | EPSS Ckt | N | 2023 | A-B-B
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRIP-SAVER | 6577 | 20230309 | 2131 | 20230309 | 2322 | 2029475 | 111 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 49 | 5439 | 37.0487 | -121.8085 | Yes | Clear;32-90 F |  |  | 23-0042617 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823429 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | SALINAS | SALINAS-1109 | 182011109 | FUSE | 948327 | 20230309 | 2151 | 20230312 | 1305 | 2029532 | 3794 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 34146 | 36.6776 | -121.5908 | Yes | Clear;32-90 F |  |  | 23-0042655 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823463 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 8821 | 20230309 | 2202 | 20230310 | 1210 | 2029667 | 848 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 848 | 36.5956 | -121.8594 | Yes | Clear;32-90 F | Pothead(Riser Termination) | Broken | 23-0042625 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823437 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | RECLOSER | 5178 | 20230309 | 2214 | 20230310 | 1650 | 2029536 | 1116 | Distribution Circuit | Vegetation | Tree - fell into line | 267 | 169854 | 37.0324 | -121.9467 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042597 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | Yes | No | 1823412 | 0 | EPSS Ckt | N | 2023 | ABC
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | FUSE | 4769 | 20230309 | 2222 | 20230309 | 2242 | 2029504 | 20 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 600 | 36.9772 | -121.9171 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0042602 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1823416 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | RECLOSER | 12990 | 20230309 | 2224 | 20230310 | 1847 | 2029554 | 1223 | Distribution Circuit | Vegetation | Tree - fell into line | 793 | 524069 | 37.039 | -122.0214 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 23-0042600 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | No | No | 1823414 | 0 | EPSS Ckt | N | 2023 | B-C-GRD
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | TRANSFORMER | 316375013515 | 20230309 | 2224 | 20230310 | 8 | 2029482 | 104 | Transformer only | Environmental/External | Water | 2 | 208 | 36.8646 | -121.7403 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0042610 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823423 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 8487 | 20230309 | 2311 | 20230310 | 752 | 2029661 | 521 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 140 | 72940 | 37.06 | -122.0016 | Yes | Clear;32-90 F |  |  | 23-0042794 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823586 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | OCB | 2103/2 | 20230309 | 2313 | 20230309 | 2357 | 2029664 | 44 | Distribution Circuit | Equipment Failure/Involved | Overhead | 988 | 43472 | 36.5991 | -121.8542 | Yes | Clear;32-90 F | Anchor or Guy | Broken | 23-0042622 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1823434 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 5459 | 20230309 | 2341 | 20230310 | 1014 | 2030573 | 633 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 18357 | 37.1385 | -122.1432 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0042915 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823656 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 1831 | 20230310 | 6 | 20230310 | 125 | 2029731 | 79 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 43 | 3397 | 36.8143 | -121.7007 | No | Clear;32-90 F |  |  | 23-0042680 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823488 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | OILFIELDS-1103 | 182391103 | FUSE | 7201 | 20230310 | 57 | 20230310 | 1508 | 2029830 | 851 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 29 | 24679 | 35.8996 | -120.9578 | No | Clear;32-90 F |  |  | 23-0042817 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823599 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | RECLOSER | 5096 | 20230310 | 113 | 20230310 | 1553 | 2029855 | 880 | Distribution Circuit | Vegetation | Tree - fell into line | 288 | 253440 | 37.0509 | -122.0368 | No | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 23-0042678 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823486 | 0 | EPSS Ckt | N | 2023 | A- GRD
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 6079 | 20230310 | 113 | 20230310 | 1700 | 2030430 | 947 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 49244 | 37.0556 | -122.0327 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042818 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823600 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 6087 | 20230310 | 113 | 20230311 | 1015 | 2030606 | 1982 | Distribution Circuit | Vegetation | Tree - fell into line | 186 | 160648 | 37.0665 | -122.0336 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042678 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823641 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 6189 | 20230310 | 123 | 20230310 | 1415 | 2029867 | 772 | Distribution Circuit | Vegetation | Tree - branch fell on line | 79 | 60988 | 36.9777 | -121.9026 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042936 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823667 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 5146 | 20230310 | 158 | 20230310 | 946 | 2029898 | 468 | Distribution Circuit | Vegetation | Tree - fell into line | 1855 | 868140 | 37.0578 | -122.0595 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0042688 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823496 | 0 | EPSS Ckt | N | 2023 | A-B
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 16000 | 20230310 | 208 | 20230310 | 635 | 2029917 | 267 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2795 | 746265 | 37.0464 | -122.0243 | No | Overcast-Fog-Heavy Rain;32-90 F |  |  | 23-0042692 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823501 | 0 | EPSS Ckt | N | 2023 | C-GRD INST
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 478670 | 20230310 | 210 | 20230310 | 712 | 2030187 | 302 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 66 | 19932 | 37.1031 | -121.9884 | No | Overcast-Rain;32-90 F |  |  | 23-0042692 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823571 | 0 | EPSS Ckt | N | 2023 | A GRD
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 40417 | 20230310 | 254 | 20230313 | 1825 | 2032370 | 5251 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 15753 | 36.4909 | -121.9362 | No | Partly Cloudy-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043443 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1824002 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 40419 | 20230310 | 254 | 20230313 | 2214 | 2032371 | 5480 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 104120 | 36.4907 | -121.9357 | No | Partly Cloudy-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043444 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1824003 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 8245 | 20230310 | 254 | 20230313 | 1827 | 2032372 | 5253 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 99807 | 36.4937 | -121.9343 | No | Partly Cloudy-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043445 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1824004 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 457 | 20230310 | 254 | 20230315 | 1841 | 2032379 | 7854 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 149226 | 36.4927 | -121.9335 | No | Partly Cloudy-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043448 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824007 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 2181 | 20230310 | 301 | 20230313 | 1827 | 2032384 | 5246 | Distribution Circuit | Vegetation | Tree - fell into line | 84 | 440664 | 36.4895 | -121.9363 | No | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043450 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1824009 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 5959 | 20230310 | 302 | 20230312 | 1958 | 2030021 | 3896 | Distribution Circuit | Equipment Failure/Involved | Underground | 35 | 136360 | 36.8149 | -121.626 | No | Overcast-Rain;32-90 F | Transformer (UG) | Failed/Faulted | 23-0043447 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824006 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 7005 | 20230310 | 302 | 20230310 | 920 | 2029985 | 378 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 5035 | 36.9961 | -121.7994 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0042861 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823623 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 4933 | 20230310 | 328 | 20230310 | 835 | 2030017 | 305 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 19 | 5795 | 36.9265 | -121.816 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0042831 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823607 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 974520 | 20230310 | 333 | 20230313 | 921 | 2030020 | 4668 | Distribution Circuit | Vegetation | Tree - fell into line | 290 | 704600 | 36.9908 | -121.8063 | No | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042715 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823527 | 0 | EPSS Ckt | N | 2023 | A-C
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6641 | 20230310 | 333 | 20230312 | 1501 | 2030795 | 3568 | Distribution Circuit | Environmental/External | Flood/Erosion | 40 | 142720 | 37.016 | -121.8161 | No | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042996 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1823690 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | RECLOSER | 4002 | 20230310 | 352 | 20230310 | 1334 | 2030033 | 582 | Distribution Circuit | Vegetation | Tree - fell into line | 170 | 97940 | 36.8322 | -121.5312 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042721 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1823533 | 0 | EPSS Ckt | N | 2023 | A-B-C
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | FUSE | 4775 | 20230310 | 423 | 20230318 | 1232 | 2030055 | 12009 | Distribution Circuit | Environmental/External | Flood/Erosion | 88 | 383006 | 36.9768 | -121.9217 | No | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0042957 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823676 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 5090 | 20230310 | 424 | 20230311 | 1437 | 2030058 | 2053 | Distribution Circuit | Vegetation | Tree - fell into line | 434 | 503698 | 36.9804 | -121.892 | No | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042731 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1823544 | 0 | EPSS Ckt | N | 2023 | A/B GRD
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | TRANSFORMER | 316670513870 | 20230310 | 425 | 20230310 | 805 | 2030056 | 220 | Transformer only | Vegetation | Tree - fell into line | 4 | 880 | 36.8752 | -121.6393 | No | Clear;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0042853 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823616 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 7807 | 20230310 | 505 | 20230311 | 1901 | 2030091 | 2276 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 38692 | 36.9884 | -121.7391 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042867 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1823628 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 3909 | 20230310 | 520 | 20230311 | 1131 | 2030099 | 1811 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 19784 | 36.8018 | -121.7009 | No | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042868 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823629 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 3649 | 20230310 | 640 | 20230311 | 1144 | 2030192 | 1744 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 13952 | 36.9864 | -121.8506 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043071 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823721 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | FUSE | 5557 | 20230310 | 647 | 20230312 | 2128 | 2030215 | 3761 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 104647 | 36.7876 | -121.5893 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0042886 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1823642 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | JUMPER | 412101855004 | 20230310 | 730 | 20230311 | 1440 | 2030331 | 1870 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3740 | 36.8139 | -121.6997 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042900 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823650 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1103 | 182031103 | FUSE | 2527 | 20230310 | 738 | 20230311 | 1618 | 2030342 | 1960 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 76440 | 36.147 | -121.199 | No | Clear;32-90 F | Insulator | Broken | 23-0042913 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823655 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | SWITCH | 3081 | 20230310 | 740 | 20230317 | 1510 | 2030334 | 10530 | Distribution Circuit | Environmental/External | Flood/Erosion | 328 | 194789 | 37.053 | -122.0245 | No | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken | 23-0042780 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1823580 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 40411 | 20230310 | 753 | 20230313 | 1827 | 2029971 | 4954 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 54494 | 36.4918 | -121.938 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Together | 23-0043441 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | No | No | 1824001 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 40383 | 20230310 | 813 | 20230313 | 1320 | 2030406 | 4627 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 13881 | 36.3934 | -121.9019 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043490 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824036 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 9569 | 20230310 | 906 | 20230311 | 1721 | 2030543 | 1935 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 95043 | 36.9783 | -121.8269 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042994 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1823689 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | SWITCH | 840759 | 20230310 | 915 | 20230310 | 1854 | 2030636 | 579 | Distribution Circuit | Environmental/External | Flood/Erosion | 306 | 50936 | 37.0994 | -122.0531 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0042688 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823652 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1101 | 182131101 | FUSE | 24369 | 20230310 | 935 | 20230310 | 2210 | 2030669 | 755 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2265 | 36.526 | -121.4458 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043093 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1823732 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 9333 | 20230310 | 943 | 20230311 | 1619 | 2030618 | 1836 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 38556 | 36.9423 | -121.8574 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043153 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823760 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 8429 | 20230310 | 946 | 20230310 | 2205 | 2030621 | 739 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2956 | 37.1092 | -122.0598 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0043086 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823728 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 2147 | 20230310 | 1003 | 20230311 | 2038 | 2030655 | 2075 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 6225 | 36.9302 | -121.812 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0043421 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823987 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | TRANSFORMER | 413022359283 | 20230310 | 1039 | 20230310 | 1159 | 2030508 | 80 | Transformer only | Equipment Failure/Involved | Fire- pole | 1 | 80 | 36.9382 | -121.3888 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0042960 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823678 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1101 | 182131101 | JUMPER | OJ AT 24465 | 20230310 | 1102 | 20230310 | 1908 | 2031569 | 486 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 2430 | 36.5113 | -121.4405 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 23-0043251 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1823838 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | RECLOSER | 2052 | 20230310 | 1137 | 20230312 | 2206 | 2030913 | 3509 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 480733 | 36.3999 | -121.9022 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043745 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824262 | 0 | EPSS Ckt | N | 2023 | UNKWN
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 9605 | 20230310 | 1153 | 20230310 | 1349 | 2031113 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 672 | 36.9836 | -121.778 | No | Clear;32-90 F |  |  | 23-0043132 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823748 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6647 | 20230310 | 1227 | 20230310 | 2229 | 2031016 | 602 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 1862 | 37.0266 | -121.7801 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043160 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1823766 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1101 | 182131101 | FUSE | 24367 | 20230310 | 1231 | 20230310 | 2235 | 2031072 | 604 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1812 | 36.5248 | -121.4444 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0043127 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823745 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | TRANSFORMER | 315652120545 | 20230310 | 1309 | 20230310 | 1510 | 2031031 | 121 | Transformer only | Animal | Squirrel | 2 | 242 | 37.0545 | -121.991 | No | Clear;32-90 F | Transformer | Normal | 23-0043128 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823746 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 42365 | 20230310 | 1513 | 20230312 | 1240 | 2031257 | 2727 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 16362 | 36.5829 | -121.9343 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0043167 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1823768 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | SWITCH | 905505 | 20230310 | 1520 | 20230312 | 1635 | 2031297 | 2955 | Distribution Circuit | Vegetation | Tree - fell into line | 133 | 393015 | 36.6057 | -121.9379 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043172 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1823781 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5629 | 20230310 | 1625 | 20230311 | 853 | 2031390 | 988 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 11505 | 37.1128 | -122.048 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043304 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | Yes | 1823890 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | FUSE | 4823 | 20230310 | 1804 | 20230310 | 1815 | 2031442 | 11 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 70 | 36.9428 | -121.4451 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 23-0043234 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823823 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 7231 | 20230310 | 1810 | 20230312 | 2020 | 2031518 | 3010 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 27090 | 36.6195 | -121.9297 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043236 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1823825 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 11465 | 20230310 | 1847 | 20230310 | 2015 | 2031565 | 88 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 704 | 36.8621 | -121.7526 | No | Clear;32-90 F |  |  | 23-0043268 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823853 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 2665 | 20230310 | 1926 | 20230312 | 1727 | 2031607 | 2761 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 112336 | 36.5897 | -121.8932 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 23-0043322 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823908 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 6753 | 20230310 | 1926 | 20230313 | 1708 | 2031616 | 4182 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 158916 | 36.5659 | -121.8876 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043426 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823990 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 2235 | 20230310 | 1927 | 20230312 | 1546 | 2031683 | 2659 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 101042 | 36.5753 | -121.8741 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043400 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823966 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 6737 | 20230310 | 1930 | 20230312 | 1800 | 2031659 | 2790 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 154173 | 36.5709 | -121.8861 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043394 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1823961 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | OCB | 1101/2 | 20230310 | 2226 | 20230311 | 1347 | 2031721 | 921 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 1842 | 36.8001 | -121.769 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0043310 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1823895 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412231054914 | 20230310 | 2246 | 20230311 | 1910 | 2031729 | 1224 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 3672 | 36.8123 | -121.6554 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0043385 | OH | Sus | 35431167 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823957 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | TRANSFORMER | 411686744854 | 20230311 | 130 | 20230312 | 351 | 2032064 | 1581 | Transformer only | Vegetation | Tree - branch fell on line | 4 | 6324 | 36.5316 | -121.8316 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0043622 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824162 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 4397 | 20230311 | 301 | 20230311 | 740 | 2031849 | 279 | Distribution Circuit | Vegetation | Tree - branch fell on line | 48 | 13392 | 36.9719 | -121.8757 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 23-0043356 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823936 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0422 | 182440422 | RECLOSER | 2608 | 20230311 | 346 | 20230312 | 1913 | 2031855 | 2367 | Distribution Circuit | Vegetation | Tree - fell into line | 297 | 449559 | 36.5912 | -121.9465 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043327 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1823913 | 0 | EPSS Ckt | N | 2023 | A-C
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0424 | 182440424 | JUMPER | OJ 2SS OF CGC 411413448679 | 20230311 | 420 | 20230313 | 1922 | 2032604 | 3782 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 52948 | 36.6344 | -121.9289 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043498 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824044 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 6973 | 20230311 | 457 | 20230311 | 1732 | 2031878 | 755 | Distribution Circuit | Vegetation | Tree - branch fell on line | 36 | 27180 | 36.5816 | -121.9216 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 23-0043538 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1824078 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | TRANSFORMER | 411435345932 | 20230311 | 545 | 20230313 | 1359 | 2031892 | 3374 | Transformer only | Vegetation | Tree - fell into line | 16 | 53984 | 36.559 | -121.9181 | No | Clear;32-90 F | Secondary | Together | 23-0043349 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823929 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 2811 | 20230311 | 549 | 20230313 | 1105 | 2032010 | 3196 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 63920 | 36.5143 | -121.8127 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043714 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824230 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | OTHER | WIRE DOWN AT CGC 411435245911 | 20230311 | 551 | 20230312 | 1927 | 2031893 | 2256 | Distribution Circuit | Vegetation | Tree - branch fell on line | 81 | 80109 | 36.5581 | -121.9175 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043652 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | Yes | 1824187 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0424 | 182440424 | FUSE | 8563 | 20230311 | 621 | 20230313 | 1735 | 2031880 | 3554 | Distribution Circuit | Vegetation | Tree - branch fell on line | 48 | 57600 | 36.6302 | -121.9265 | No | Clear;32-90 F | Conductor- Overhead | Burned/flashed | 23-0043341 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1823925 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 10714 | 20230311 | 628 | 20230311 | 640 | 2031918 | 12 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3175 | 38100 | 36.9779 | -121.8666 | No | Clear;32-90 F |  |  | 23-0043338 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823922 | 0 | EPSS Ckt | N | 2023 | AB
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | TRANSFORMER | 6341 | 20230311 | 633 | 20230313 | 1303 | 2031920 | 3270 | Distribution Circuit | Vegetation | Tree - branch fell on line | 36 | 117720 | 36.5631 | -121.9203 | No | Overcast-Fog;32-90 F | Secondary | Broken- wire on ground | 23-0043713 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824229 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 6677 | 20230311 | 658 | 20230313 | 1836 | 2031941 | 3578 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 125230 | 36.5489 | -121.9198 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043576 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824117 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 6851 | 20230311 | 702 | 20230312 | 1046 | 2031947 | 1664 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 31616 | 36.5569 | -121.9156 | No | Overcast-Fog;32-90 F |  |  | 23-0043688 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824214 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 11103 | 20230311 | 736 | 20230311 | 941 | 2031969 | 125 | Distribution Circuit | Vegetation | Tree - branch fell on line | 43 | 5375 | 36.9935 | -122.0701 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Together | 23-0043392 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | No | No | 1823960 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 2705 | 20230311 | 805 | 20230311 | 837 | 2031988 | 32 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 864 | 37.0005 | -121.7403 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0043359 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1823940 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | OCB | 2105/2 | 20230311 | 850 | 20230311 | 2129 | 2032021 | 749 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11226 | 4183489 | 36.5991 | -121.8541 | No | Overcast-Fog;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0043372 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823948 | 0 | EPSS Ckt | N | 2023 | A-C- GRD
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 6447 | 20230311 | 857 | 20230312 | 1719 | 2032037 | 1942 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 15536 | 36.5806 | -121.9194 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043545 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824085 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | SWITCH | 8025 | 20230311 | 902 | 20230313 | 1355 | 2032839 | 3173 | Distribution Circuit | Vegetation | Tree - fell into line | 740 | 917987 | 36.6081 | -121.9108 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 23-0043561 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1824101 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | JUMPER | OJ 1 SS/OF CGC# 411452945990 | 20230311 | 1037 | 20230312 | 1044 | 2032238 | 1447 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 18811 | 36.5609 | -121.9122 | No | Clear;32-90 F | Secondary | Broken | 23-0043515 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1824059 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | RECLOSER | 12760 | 20230311 | 1046 | 20230312 | 1724 | 2032262 | 1838 | Distribution Circuit | Vegetation | Tree - fell into line | 547 | 174984 | 37.0674 | -121.9966 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043413 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823978 | 0 | EPSS Ckt | N | 2023 | B GRD
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | SWITCH | 1353 | 20230311 | 1046 | 20230311 | 1755 | 2032224 | 429 | Distribution Circuit | 3rd Party | Vehicle | 76 | 32604 | 36.9514 | -121.7728 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0043383 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1823975 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 8241 | 20230311 | 1051 | 20230311 | 1632 | 2030949 | 341 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 4433 | 37.1179 | -121.9648 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0043396 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1823963 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 2155 | 20230311 | 1145 | 20230311 | 1223 | 2031974 | 38 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 190 | 36.9519 | -121.841 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0043427 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1823991 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | TRANSFORMER | 315735922324 | 20230311 | 1147 | 20230312 | 1427 | 2032328 | 1600 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1600 | 37.1037 | -121.9633 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0043530 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824072 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9781 | 20230311 | 1238 | 20230312 | 1552 | 2032391 | 1634 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 8170 | 37.1377 | -122.0975 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0043491 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1824038 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | FUSE | 9707 | 20230311 | 1256 | 20230416 | 1737 | 2032417 | 52121 | Distribution Circuit | Environmental/External | Flood/Erosion | 18 | 954 | 36.0519 | -120.9213 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0043472 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 937224 | No | Yes | No | 1824027 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0422 | 182440422 | FUSE | 2581 | 20230311 | 1449 | 20230311 | 2102 | 2032570 | 373 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 96 | 35808 | 36.5918 | -121.9454 | No | Clear;32-90 F |  |  | 23-0043551 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | No | No | 1824091 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | TRANSFORMER | 315231121735 | 20230311 | 1458 | 20230312 | 1015 | 2032564 | 1157 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 4628 | 37.0856 | -122.1362 | No | Clear;32-90 F |  |  | 23-0043527 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824069 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0422 | 182440422 | FUSE | 2215 | 20230311 | 1458 | 20230311 | 1924 | 2032563 | 266 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 7448 | 36.5915 | -121.9475 | No | Clear;32-90 F |  |  | 23-0043558 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824098 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 2179 | 20230311 | 1513 | 20230311 | 1752 | 2032662 | 159 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 8802 | 36.5423 | -121.9165 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0043526 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824068 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | SWITCH | 2795 | 20230311 | 1524 | 20230312 | 1140 | 2032609 | 1216 | Distribution Circuit | Vegetation | Tree - fell into line | 181 | 220096 | 36.5447 | -121.9101 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0043512 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1824057 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | SWITCH | 69163 | 20230311 | 1550 | 20230313 | 2151 | 2032621 | 3241 | Distribution Circuit | Vegetation | Tree - fell into line | 315 | 779601 | 36.5879 | -121.9463 | No | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0043503 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824049 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 24729 | 20230311 | 1648 | 20230311 | 1910 | 2032700 | 142 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 852 | 36.8117 | -121.6556 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0043523 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1824065 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | TRANSFORMER | 316320615771 | 20230311 | 1706 | 20230311 | 2214 | 2032707 | 308 | Transformer only | Vegetation | Tree - fell into line | 10 | 3080 | 36.9263 | -121.7597 | No | Clear;32-90 F | Secondary | Normal | 23-0043524 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1824066 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 1445 | 20230311 | 1840 | 20230313 | 1254 | 2033058 | 2534 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 30408 | 36.5735 | -121.9108 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043724 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | Yes | No | 1824240 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | TRANSFORMER | 411779650470 | 20230311 | 1949 | 20230313 | 1757 | 2032875 | 2768 | Transformer only | Equipment Failure/Involved | Underground | 6 | 16608 | 36.6866 | -121.8049 | No | Clear;32-90 F | Transformer | Burned/flashed | 23-0043760 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824275 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 1399 | 20230311 | 2123 | 20230312 | 1725 | 2032928 | 1202 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 49282 | 36.617 | -121.9279 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043696 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824217 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 88094 | 20230311 | 2125 | 20230312 | 1731 | 2033093 | 1206 | Distribution Circuit | Equipment Failure/Involved | Overhead | 249 | 207048 | 36.6006 | -121.9449 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on object | 23-0043641 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824177 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | TRANSFORMER | 411388447545 | 20230311 | 2241 | 20230313 | 1452 | 2032955 | 2411 | Transformer only | Vegetation | Tree - fell into line | 9 | 21699 | 36.6029 | -121.936 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0043689 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824215 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6609 | 20230311 | 2305 | 20230312 | 1824 | 2032958 | 1159 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 19703 | 36.9767 | -121.7763 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0043636 | OH | Sus | 35431165 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | No | No | 1824175 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS COCHES-1102 | 182151102 | RECLOSER | 75272 | 20230312 | 346 | 20230313 | 1806 | 2032999 | 2300 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 109412 | 36.3671 | -121.2776 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043623 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1824163 | 0 | EPSS Ckt | N | 2023 | ABC TIME
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 11006 | 20230312 | 546 | 20230312 | 715 | 2033047 | 89 | Distribution Circuit | Vegetation | Tree - branch fell on line | 104 | 9256 | 37.05 | -122.0657 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0043630 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1824172 | 0 | EPSS Ckt | N | 2023 | AB
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | FUSE | 4401 | 20230312 | 736 | 20230312 | 834 | 2033085 | 58 | Distribution Circuit | Animal | Squirrel | 25 | 1450 | 36.9881 | -121.9332 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 23-0043646 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824182 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 7749 | 20230312 | 758 | 20230312 | 934 | 2033096 | 96 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 101 | 9696 | 36.9979 | -121.9506 | No | Clear;32-90 F |  |  | 23-0043670 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824203 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | JUMPER | WIRE DOWN HOT 3 LD SIDE OF 6191 | 20230312 | 807 | 20230312 | 1603 | 2033136 | 476 | Distribution Circuit | Equipment Failure/Involved | Overhead | 93 | 43178 | 37.052 | -122.0633 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043710 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | Yes | 1824226 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1103 | 182131103 | RECLOSER | 727404 | 20230312 | 858 | 20230416 | 1234 | 2033133 | 50616 | Distribution Circuit | Environmental/External | Flood/Erosion | 15 | 1642 | 36.4982 | -121.4501 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 23-0043654 | OH | Sus | 35431167 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 100890 | No | Yes | No | 1824189 | 0 | Non-EPSS | N | 2023 | ABC G
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 9125 | 20230312 | 950 | 20230312 | 1819 | 2033178 | 509 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 10287 | 37.1004 | -122.086 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043712 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824228 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 6891 | 20230312 | 1045 | 20230312 | 1055 | 2033211 | 10 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 40 | 36.8847 | -121.7956 | No | Clear;32-90 F |  |  | 23-0043705 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1824222 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 9333 | 20230312 | 1115 | 20230313 | 1413 | 2033205 | 1618 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 33978 | 36.9423 | -121.8574 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043697 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1824218 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | SWITCH | 3747 | 20230312 | 1210 | 20230314 | 1345 | 2033251 | 2975 | Distribution Circuit | Environmental/External | Flood/Erosion | 28 | 83295 | 36.5545 | -121.5456 | No | Clear;32-90 F | Capacitor | Normal | 23-0043719 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1824235 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 6791 | 20230312 | 1221 | 20230313 | 1931 | 2033271 | 1870 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 35530 | 36.5618 | -121.9198 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0043725 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | No | No | 1824241 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | LLAGAS-2104 | 83182104 | TRANSFORMER | 316910014765 | 20230312 | 1226 | 20230313 | 1213 | 2033274 | 1427 | Transformer only | Environmental/External | Flood/Erosion | 2 | 2854 | 36.9005 | -121.5577 | No | Partly Cloudy;32-90 F | Customer Equipment | Contaminated | 23-0043730 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824246 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | SWITCH | 1279 | 20230312 | 1420 | 20230312 | 1828 | 2033362 | 248 | Distribution Circuit | 3rd Party | Vehicle | 94 | 23312 | 37.0124 | -121.9369 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0043737 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1824254 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | TRANSFORMER | 315709417066 | 20230312 | 1504 | 20230312 | 2334 | 2033401 | 510 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 5610 | 36.9591 | -121.9688 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Annealed | 23-0043917 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824431 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 5090 | 20230312 | 1624 | 20230313 | 1232 | 2033457 | 1208 | Distribution Circuit | Vegetation | Tree - fell into line | 434 | 280908 | 36.9804 | -121.892 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043763 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824278 | 0 | EPSS Ckt | N | 2023 | B & GRD
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 8087 | 20230312 | 1629 | 20230312 | 2131 | 2033443 | 302 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 47 | 14100 | 36.5284 | -121.9199 | No | Clear;32-90 F |  |  | 23-0043821 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824335 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 6037 | 20230312 | 1710 | 20230314 | 1300 | 2033485 | 2630 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 65750 | 37.073 | -122.0159 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0044117 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824526 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 6737 | 20230312 | 1746 | 20230312 | 2042 | 2033572 | 176 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 53 | 9328 | 36.5709 | -121.8861 | No | Clear;32-90 F |  |  | 23-0043810 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1824324 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | SWITCH | 8687 | 20230312 | 1832 | 20230312 | 2005 | s1853043 | 93 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 1651 | 153543 | 36.5558 | -121.8979 | No | Clear;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0042371 | OH | Sus | 35431167 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1853043 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | FUSE | 7857 | 20230312 | 1851 | 20230405 | 1220 | 2046458 | 34169 | Distribution Circuit | Environmental/External | Flood/Erosion | 9 | 549 | 36.4343 | -121.4192 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0046443 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 142650 | No | Yes | No | 1826222 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 2721 | 20230312 | 1900 | 20230313 | 1338 | 2033517 | 1118 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 10062 | 36.8803 | -121.6375 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0043788 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1824301 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | TRANSFORMER | 411411546675 | 20230312 | 1942 | 20230313 | 1246 | 2033672 | 1024 | Transformer only | Company Initiated | Return Circuit Normal | 6 | 6144 | 36.5793 | -121.9266 | No | Clear;32-90 F | Transformer | Normal | 23-0043936 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824451 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | TRANSFORMER | 411368744286 | 20230312 | 2141 | 20230313 | 1415 | 2033755 | 994 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1988 | 36.513 | -121.9378 | No | Clear;32-90F | Transformer (OH) | Broken | 23-0043913 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824427 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | JUMPER | 5232 | 20230312 | 2333 | 20230313 | 1813 | 2033805 | 1120 | Distribution Circuit | Vegetation | Tree - fell into line | 788 | 824296 | 37.0752 | -122.054 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043919 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | Yes | No | 1824433 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | TRANSFORMER | 411347546698 | 20230313 | 549 | 20230313 | 922 | 2033950 | 213 | Transformer only | Unknown Cause | Patrol - found nothing | 5 | 1065 | 36.5793 | -121.9487 | No | Clear;32-90F |  |  | 23-0044014 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1824492 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 2761 | 20230313 | 702 | 20230313 | 1325 | 2033986 | 383 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 49 | 18767 | 36.5514 | -121.9242 | No | Clear;32-90 F |  |  | 23-0044178 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824550 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | TRANSFORMER | 411435245911 | 20230313 | 719 | 20230313 | 1701 | 2034035 | 582 | Transformer only | Vegetation | Tree - fell into line | 20 | 11640 | 36.5581 | -121.9181 | No | Clear;32-90F | Secondary | Bent or Twisted | 23-0044232 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824565 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 67520 | 20230313 | 816 | 20230313 | 933 | 2034088 | 77 | Distribution Circuit | Vegetation | Tree - fell into line | 2717 | 209209 | 36.9577 | -121.8525 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0043977 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1824463 | 0 | EPSS Ckt | N | 2023 | A & C PHASE
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | JUMPER | OJ 3 POLES SOUTH OF CGC 411494745605 | 20230313 | 1013 | 20230313 | 1638 | 2034273 | 385 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1155 | 36.5503 | -121.8986 | No | Clear;32-90F | Pole-Wood | Deteriorated | 23-0044046 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1824503 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | JUMPER | WIRE DOWN HOT 2 SPANS LD SD OF 8171 | 20230313 | 1056 | 20230313 | 1551 | 2034389 | 295 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 590 | 36.5453 | -121.8849 | No | Clear;32-90F | Connector or Splice (OH) | Broken- wire on ground | 23-0044111 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | Yes | No | 1824522 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | TRANSFORMER | 411939640823 | 20230313 | 1131 | 20230313 | 1342 | 2034382 | 131 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 655 | 36.4235 | -121.7409 | No | Clear;32-90F | Jumper | Broken | 23-0044098 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1824518 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | TRANSFORMER | 411738444188 | 20230313 | 1236 | 20230314 | 1347 | 2034471 | 1511 | Transformer only | Environmental/External | Flood/Erosion | 1 | 1511 | 36.513 | -121.8121 | No | Clear;32-90 F | Transformer | Broken | 23-0044466 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824732 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 3549 | 20230313 | 1414 | 20230314 | 1522 | 2034598 | 1508 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1004 | 37.0663 | -122.0572 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0044311 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824598 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 8571 | 20230313 | 1416 | 20230313 | 1758 | 2034601 | 222 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 7548 | 36.6061 | -121.9186 | No | Overcast;32-90 F |  |  | 23-0044337 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824615 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | TRIP-SAVER | 25695 | 20230313 | 1506 | 20230313 | 1615 | 2034743 | 69 | Distribution Circuit | Equipment Failure/Involved | Overhead | 157 | 10833 | 36.7493 | -121.6573 | No | Clear;32-90 F | Anchor or Guy | Broken | 23-0044287 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824588 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 412041153997 | 20230313 | 1513 | 20230313 | 1917 | 2034070 | 244 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 1220 | 36.7869 | -121.7203 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0044254 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824576 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 40423 | 20230313 | 1541 | 20230313 | 2203 | 2034778 | 382 | Distribution Circuit | Vegetation | Tree - grew into line | 25 | 9550 | 36.5539 | -121.899 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0044261 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1824579 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 8557 | 20230313 | 1739 | 20230313 | 2120 | 2034918 | 221 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1326 | 36.5665 | -121.8863 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0044325 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1824610 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | RECLOSER | 2000 | 20230313 | 1741 | 20230314 | 2025 | 2034936 | 1604 | Distribution Circuit | Vegetation | Tree - fell into line | 217 | 61984 | 36.5852 | -121.8743 | No | Overcast;32-90 F | Switch (OH) | Broken- wire on ground | 23-0044330 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1824614 | 0 | EPSS Ckt | N | 2023 | B-C
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | JUMPER | 6753 OPEN HS JUMPERS | 20230313 | 1741 | 20230315 | 1758 | 2044641 | 2897 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 110086 | 36.5661 | -121.8873 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0045846 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1825768 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | TRANSFORMER | 411545547368 | 20230313 | 1746 | 20230314 | 828 | 2034045 | 882 | Transformer only | Equipment Failure/Involved | Overhead | 20 | 17640 | 36.5993 | -121.882 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0044329 | OH | Sus | 35431167 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824613 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 9813 | 20230313 | 1746 | 20230314 | 848 | 2034952 | 902 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 36 | 32472 | 36.861 | -121.6873 | No | Clear;32-90F |  |  | 23-0044528 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1824754 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 2451 | 20230313 | 1820 | 20230313 | 2234 | 2034978 | 254 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2032 | 36.5723 | -121.9406 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0044344 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1824617 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 426822 | 20230313 | 1823 | 20230313 | 1957 | 2034998 | 94 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 102 | 9588 | 37.1016 | -122.0324 | No | Clear;32-90 F |  |  | 23-0044355 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1824624 | 0 | EPSS Ckt | N | 2023 | TIME OC
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 8983 | 20230314 | 501 | 20230315 | 1727 | 2035167 | 2186 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 54230 | 37.0307 | -122.1429 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0044536 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824757 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | JUMPER | BLOWN JUMPER #2 | 20230314 | 602 | 20230314 | 1203 | 2035813 | 361 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 361 | 36.6787 | -121.735 | Yes | Clear;32-90F | Jumper | Burned Open | 23-0044671 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1824824 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 5819 | 20230314 | 629 | 20230315 | 1820 | 2035614 | 2151 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 129060 | 37.0449 | -121.8139 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044635 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824803 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | RECLOSER | 4002 | 20230314 | 708 | 20230314 | 1053 | 2035209 | 225 | Distribution Circuit | Equipment Failure/Involved | Overhead | 170 | 37890 | 36.8322 | -121.5312 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044503 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824746 | 0 | EPSS Ckt | N | 2023 | C & GRD
CENTRAL COAST | SALINAS | SALINAS-1109 | 182011109 | FUSE | 948327 | 20230314 | 720 | 20230316 | 1438 | 2035229 | 3318 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 29862 | 36.6776 | -121.5908 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0044614 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1824792 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 23385 | 20230314 | 755 | 20230314 | 1435 | 2035258 | 400 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 88 | 35200 | 36.8434 | -121.6756 | Yes | Overcast-Drizzle;32-90 F |  |  | 23-0045353 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825343 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | FUSE | 20181 | 20230314 | 757 | 20230314 | 1553 | 2035265 | 476 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 6985 | 36.5534 | -121.5036 | Yes | Clear;32-90 F | Jumper | Burned Open | 23-0045062 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825129 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0422 | 182440422 | RECLOSER | 2608 | 20230314 | 809 | 20230315 | 1931 | 2035488 | 2122 | Distribution Circuit | Vegetation | Tree - fell into line | 297 | 453354 | 36.5912 | -121.9465 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0044716 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824857 | 0 | EPSS Ckt | N | 2023 | B-C-GRD
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | RECLOSER | 258688 | 20230314 | 811 | 20230314 | 1739 | 2035296 | 568 | Distribution Circuit | Vegetation | Tree - fell into line | 553 | 30288 | 36.2774 | -121.2298 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044545 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1824759 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 6087 | 20230314 | 814 | 20230314 | 1946 | 2035330 | 692 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 63664 | 37.0665 | -122.0336 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0044612 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824790 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 655 | 20230314 | 823 | 20230315 | 1841 | 2035319 | 2058 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 45276 | 36.8785 | -121.6416 | Yes | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0044600 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824784 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6155 | 20230314 | 859 | 20230315 | 1404 | 2045924 | 1745 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 1745 | 37.0012 | -121.7711 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 23-0046237 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826103 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 12106 | 20230314 | 900 | 20230315 | 1328 | 2035396 | 1708 | Distribution Circuit | Vegetation | Tree - fell into line | 1037 | 213756 | 36.9718 | -121.7649 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044580 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824774 | 0 | EPSS Ckt | N | 2023 | A B & GRD
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 2181 | 20230314 | 900 | 20230316 | 1347 | 2046940 | 3167 | Distribution Circuit | Vegetation | Tree - fell into line | 84 | 266028 | 36.4895 | -121.9363 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046594 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1826314 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 5119 | 20230314 | 904 | 20230314 | 1414 | 2035404 | 310 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 2170 | 36.8178 | -121.6899 | Yes | Clear;32-90 F |  |  | 23-0045298 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825307 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | RECLOSER | 440 | 20230314 | 904 | 20230315 | 1943 | 2035394 | 2079 | Distribution Circuit | Vegetation | Tree - fell into line | 304 | 321442 | 36.4389 | -121.9203 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0044585 | OH | Sus | 35431808 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1824776 | 0 | EPSS Ckt | N | 2023 | A- C & GRD
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | JUMPER | JUMPERS @ 6749 TWD 861255 | 20230314 | 904 | 20230314 | 2029 | 2035402 | 685 | Distribution Circuit | Vegetation | Tree - grew into line | 18 | 12330 | 36.5607 | -121.9199 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0044722 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1824863 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 6851 | 20230314 | 907 | 20230314 | 1823 | 2035419 | 556 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 10564 | 36.5569 | -121.9156 | Yes | Clear;32-90 F |  |  | 23-0045679 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825620 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | OCB | 1101/2 | 20230314 | 909 | 20230315 | 1601 | 2035243 | 1852 | Distribution Circuit | Vegetation | Tree - fell into line | 1359 | 2304260 | 36.5569 | -121.8976 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044589 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1824778 | 0 | EPSS Ckt | N | 2023 | AB
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 2283 | 20230314 | 909 | 20230315 | 1601 | 2035856 | 1852 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 175940 | 36.5564 | -121.9087 | Yes | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0044685 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1824838 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | SWITCH | 8687 | 20230314 | 909 | 20230316 | 1526 | 2037483 | 3257 | Distribution Circuit | Vegetation | Tree - fell into line | 1687 | 3200536 | 36.5558 | -121.8979 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044589 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1824962 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | SWITCH | 570399 | 20230314 | 909 | 20230315 | 1841 | 2042177 | 2012 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 16096 | 36.5154 | -121.9354 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0045328 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1825327 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | SWITCH | 1461BP | 20230314 | 909 | 20230316 | 1417 | 2046638 | 3188 | Distribution Circuit | Equipment Failure/Involved | Overhead | 293 | 934084 | 36.557 | -121.9042 | Yes | Overcast-Drizzle;32-90 F | Lightning Arrestor | Burned/flashed | 23-0044589 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826256 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | SWITCH | 7215 | 20230314 | 909 | 20230315 | 1958 | 2040645 | 2089 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 189217 | 36.4998 | -121.937 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044589 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1825225 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 9005 | 20230314 | 912 | 20230314 | 1754 | 2035418 | 522 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 11484 | 37.0318 | -122.1369 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044704 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1824849 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 8187 | 20230314 | 915 | 20230314 | 1038 | 2035428 | 83 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 47 | 3901 | 36.6036 | -121.9434 | Yes | Clear;32-90F |  |  | 23-0044696 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824843 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 6975 | 20230314 | 919 | 20230316 | 1941 | 2036405 | 3502 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 175100 | 36.5797 | -121.9204 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044764 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | Yes | No | 1824894 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 422016 | 20230314 | 926 | 20230315 | 1320 | 2035478 | 1674 | Distribution Circuit | Vegetation | Tree - fell into line | 910 | 208707 | 36.964 | -121.8086 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044610 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | Yes | No | 1824788 | 0 | EPSS Ckt | N | 2023 | ABC G
CENTRAL COAST | SALINAS | SPENCE-1104 | 182201104 | JUMPER | BURNT OPEN FIELD PHASE JUMPER | 20230314 | 933 | 20230314 | 1221 | 2038205 | 168 | Distribution Circuit | Equipment Failure/Involved | Overhead | 683 | 81578 | 36.5719 | -121.5211 | Yes | Clear;32-90 F | Jumper | Burned Open | 23-0044952 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1825037 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 8269 | 20230314 | 934 | 20230315 | 1341 | 2035500 | 1687 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 62419 | 36.5555 | -121.9122 | Yes | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0044885 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824989 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | RECLOSER | 478670 | 20230314 | 938 | 20230315 | 1722 | 2038006 | 1904 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 66 | 125664 | 37.1031 | -121.9884 | Yes |  |  |  | 23-0044940 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825030 | 0 | EPSS Ckt | N | 2023 | B GRD
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | RECLOSER | 2014 | 20230314 | 944 | 20230317 | 1619 | 2035561 | 4715 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 37720 | 36.5776 | -121.9523 | Yes | Clear;32-90 F | Conductor- Overhead | On Ground | 23-0044624 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | Yes | No | 1824796 | 0 | EPSS Ckt | N | 2023 | ABC GRD
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | SWITCH | 2595 | 20230314 | 944 | 20230317 | 1619 | 2046554 | 4715 | Distribution Circuit | Vegetation | Tree - fell into line | 115 | 542225 | 36.5735 | -121.9592 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046476 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1826239 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9761 | 20230314 | 946 | 20230316 | 1740 | 2035567 | 3354 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 10062 | 37.1729 | -122.1638 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044773 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1824900 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | OCB | 1102/2 | 20230314 | 951 | 20230316 | 1221 | 2035617 | 3030 | Distribution Circuit | Vegetation | Tree - fell into line | 732 | 2007990 | 36.5569 | -121.8976 | Yes | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0044636 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824804 | 0 | EPSS Ckt | N | 2023 | A-B-C-GRD
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 1445 | 20230314 | 951 | 20230316 | 1511 | 2039649 | 3200 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 38400 | 36.5735 | -121.9108 | Yes | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045086 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825148 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | RECLOSER | 9120 | 20230314 | 955 | 20230318 | 605 | 2036098 | 5530 | Distribution Circuit | Vegetation | Tree - fell into line | 1209 | 553900 | 36.6022 | -121.9359 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044725 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824866 | 0 | EPSS Ckt | N | 2023 | C & GRD
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 495039 | 20230314 | 1000 | 20230316 | 1751 | 2035731 | 3351 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 35176 | 36.5692 | -121.9118 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045876 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1825800 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRIP-SAVER | 9773 | 20230314 | 1004 | 20230316 | 1743 | 2035737 | 3339 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 96831 | 37.1289 | -122.1142 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0044847 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1824956 | 0 | EPSS Ckt | N | 2023 | GRD
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 2303 | 20230314 | 1004 | 20230315 | 28 | 2035679 | 864 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 32224 | 36.5894 | -121.8975 | Yes | Overcast-Strong Winds;32-90 F | Secondary | Broken | 23-0046007 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825931 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 2695 | 20230314 | 1007 | 20230315 | 1902 | 2044096 | 1975 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 37525 | 36.5886 | -121.9082 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045733 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825669 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 8315 | 20230314 | 1010 | 20230314 | 1156 | 2035745 | 106 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 2226 | 37.0995 | -122.1181 | Yes | Clear;32-90 F |  |  | 23-0044877 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824983 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | OTHER | WIRE DOWN | 20230314 | 1014 | 20230316 | 1634 | 2045112 | 3260 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 55247 | 36.3999 | -121.8719 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046043 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | Yes | No | 1825961 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 1661 | 20230314 | 1014 | 20230314 | 1121 | 2035833 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 1139 | 36.9853 | -122.0302 | Yes | Clear;32-90F |  |  | 23-0044761 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1824891 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | PACIFIC GROVE SUB | 18244 | OCB | 423/2 | 20230314 | 1018 | 20230315 | 859 | 2036387 | 1361 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 526 | 715886 | 36.6171 | -121.9192 | Yes | Overcast-Strong Winds;32-90 F |  |  | 23-0046144 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826037 | 0 | Non-EPSS | N | 2023 | N/A
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 5269 | 20230314 | 1020 | 20230317 | 1740 | 2035865 | 4760 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 96915 | 36.9894 | -122.0312 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Together | 23-0045816 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825739 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | RECLOSER | 16006 | 20230314 | 1021 | 20230317 | 1018 | 2035850 | 247 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1566 | 386802 | 36.9829 | -122.0492 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044676 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1824828 | 0 | EPSS Ckt | N | 2023 | ABC
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 8097 | 20230314 | 1022 | 20230314 | 1630 | 2035864 | 368 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 6256 | 37.0785 | -122.139 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044931 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | Yes | 1825021 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5521 | 20230314 | 1023 | 20230316 | 1700 | 2046340 | 3277 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 128684 | 37.1577 | -122.1357 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0046394 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826194 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 8467 | 20230314 | 1025 | 20230315 | 1107 | 2035896 | 1482 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 109668 | 37.1418 | -122.0907 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045039 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1825110 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 11943 | 20230314 | 1028 | 20230316 | 1745 | 2035907 | 3317 | Distribution Circuit | Vegetation | Tree - branch fell on line | 79 | 151339 | 37.0112 | -122.0442 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044937 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825027 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | FUSE | 8971 | 20230314 | 1040 | 20230315 | 1908 | 2035295 | 1948 | Distribution Circuit | Vegetation | Tree - fell into line | 295 | 192673 | 36.4727 | -121.7254 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045289 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825300 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | FUSE | 5561 | 20230314 | 1043 | 20230316 | 1419 | 2036020 | 3096 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 61920 | 36.7763 | -121.5987 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0045324 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825323 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 6103 | 20230314 | 1048 | 20230315 | 847 | 2036146 | 1319 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 72545 | 37.0115 | -122.0121 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 23-0045461 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825434 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | RECLOSER | 431508 | 20230314 | 1048 | 20230317 | 1809 | 2036154 | 4705 | Distribution Circuit | Vegetation | Tree - fell into line | 601 | 2745374 | 36.5822 | -121.9204 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044729 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1824869 | 0 | EPSS Ckt | N | 2023 | ABC
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | TRANSFORMER | 411589646541 | 20230314 | 1050 | 20230315 | 1627 | 2036199 | 1777 | Transformer only | Vegetation | Tree - fell into line | 4 | 7108 | 36.5771 | -121.8661 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0046522 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826266 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | OCB | 2201/2 | 20230314 | 1053 | 20230314 | 1118 | 2036386 | 25 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 684 | 17100 | 36.5786 | -121.9085 | Yes | Overcast-Strong Winds;32-90 F |  |  | 23-0044778 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824905 | 0 | EPSS Ckt | N | 2023 | SET A TRIP/ T/OC
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | RECLOSER | 9118 | 20230314 | 1053 | 20230315 | 237 | 2036185 | 944 | Distribution Circuit | Vegetation | Tree - branch fell on line | 444 | 419136 | 36.6037 | -121.9359 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0044734 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824872 | 0 | EPSS Ckt | N | 2023 | C GRD
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 8183 | 20230314 | 1053 | 20230316 | 849 | 2045011 | 2756 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 44096 | 36.6072 | -121.9407 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0046023 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1825942 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | RECLOSER | 9698 | 20230314 | 1059 | 20230317 | 732 | s1824892 | 4113 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 127503 | 36.5726 | -121.9436 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044762 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824892 | 0 | EPSS Ckt | N | 2023 | A GRD
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 141 | 20230314 | 1101 | 20230314 | 1315 | 2036290 | 134 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 1876 | 37.048 | -122.0648 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 23-0045111 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825167 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 2689 | 20230314 | 1103 | 20230315 | 1142 | 2036490 | 1479 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 47328 | 37.1274 | -122.0181 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0046268 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826115 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 4915 | 20230314 | 1104 | 20230315 | 1650 | 2036318 | 1786 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 60724 | 37.1032 | -122.0458 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046305 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1826136 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 1623 | 20230314 | 1105 | 20230314 | 1739 | 2043836 | 394 | Distribution Circuit | Vegetation | Tree - branch fell on line | 44 | 17336 | 37.0478 | -122.0581 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Together | 23-0045670 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825612 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | OCB | 2203/2 | 20230314 | 1111 | 20230316 | 1956 | 2036645 | 3405 | Distribution Circuit | Vegetation | Tree - fell into line | 5195 | 1513102 | 36.5786 | -121.9085 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044789 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824913 | 0 | EPSS Ckt | N | 2023 | C GRD
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | JUMPER | OJ @ CGC#411396946391 | 20230314 | 1113 | 20230317 | 1349 | 2049322 | 4476 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 22380 | 36.5713 | -121.9318 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0047266 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826727 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | SWITCH | 833171 | 20230314 | 1113 | 20230317 | 1542 | 2049266 | 4589 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 165204 | 36.5949 | -121.9411 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0047253 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1826714 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 8485 | 20230314 | 1114 | 20230314 | 1836 | 2036614 | 442 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 177 | 78234 | 37.06 | -122.0013 | Yes | Overcast-Fog-Rain;32-90 F |  |  | 23-0045734 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825670 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5621 | 20230314 | 1117 | 20230315 | 1030 | 2036827 | 1393 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 45 | 62685 | 37.1016 | -122.0524 | Yes | Clear;32-90 F |  |  | 23-0046188 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826070 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 2453 | 20230314 | 1119 | 20230317 | 1851 | 2044386 | 4772 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 62036 | 36.5724 | -121.9397 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045780 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825706 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 7879 | 20230314 | 1119 | 20230317 | 1556 | 2047486 | 4597 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 73552 | 36.5783 | -121.9441 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046811 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826443 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | OCB | 2201/2 | 20230314 | 1121 | 20230317 | 1809 | 2036735 | 4728 | Distribution Circuit | Vegetation | Tree - branch fell on line | 631 | 2215378 | 36.5786 | -121.9085 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0044805 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1824925 | 0 | EPSS Ckt | N | 2023 | ABC
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | JUMPER | 7231 HS JMPRS | 20230314 | 1121 | 20230317 | 1833 | 2043420 | 4752 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 44109 | 36.6193 | -121.93 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045589 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1825540 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 9061 | 20230314 | 1124 | 20230315 | 1336 | 2036858 | 1572 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 33276 | 37.1188 | -122.0166 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0046344 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826164 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 1447 | 20230314 | 1127 | 20230318 | 1446 | 2049817 | 5959 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 53631 | 36.565 | -121.9568 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0047493 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826849 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | RECLOSER | 9120 | 20230314 | 1134 | 20230317 | 1542 | 2037286 | 4568 | Distribution Circuit | Vegetation | Tree - branch fell on line | 867 | 3960456 | 36.6022 | -121.9359 | Yes | Overcast-Strong Winds;32-90 F | Secondary | Broken | 23-0044843 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824953 | 0 | EPSS Ckt | N | 2023 | B & GRD
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 11939 | 20230314 | 1136 | 20230314 | 1318 | 2037443 | 102 | Distribution Circuit | Vegetation | Tree - branch fell on line | 71 | 7242 | 37.0106 | -122.0442 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 23-0044970 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825053 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 3583 | 20230314 | 1138 | 20230315 | 1939 | 2047073 | 1921 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 26894 | 37.1389 | -122.1011 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken | 23-0046617 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826332 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | FUSE | 441 | 20230314 | 1138 | 20230315 | 1645 | 2046768 | 1747 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 1747 | 36.4628 | -121.7113 | Yes | Clear;32-90 F |  |  | 23-0046539 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826278 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | OCB | 2202/2 | 20230314 | 1140 | 20230315 | 715 | 2037464 | 1158 | Distribution Circuit | Vegetation | Tree - fell into line | 1043 | 986748 | 36.5786 | -121.9085 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044869 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1824975 | 0 | EPSS Ckt | N | 2023 | ABC GRD
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 4295 | 20230314 | 1141 | 20230316 | 1353 | 2037377 | 3012 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 75300 | 37.033 | -122.0105 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045307 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1825314 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 737512 | 20230314 | 1141 | 20230314 | 1540 | 2037484 | 239 | Distribution Circuit | Vegetation | Tree - fell into line | 898 | 214622 | 37.0467 | -122.074 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044858 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1824967 | 0 | EPSS Ckt | N | 2023 | ABC
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | SWITCH | 8409 | 20230314 | 1141 | 20230315 | 1752 | 2041893 | 1811 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 38031 | 37.0672 | -122.0803 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Together | 23-0044853 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825302 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 10728 | 20230314 | 1142 | 20230315 | 1749 | 2037509 | 1807 | Distribution Circuit | Vegetation | Tree - fell into line | 149 | 269243 | 37.0665 | -122.0797 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044853 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824961 | 0 | EPSS Ckt | N | 2023 | A GRD
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 1661 | 20230314 | 1145 | 20230314 | 1623 | 2041982 | 278 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 4726 | 36.9853 | -122.0302 | Yes | Clear;32-90 F |  |  | 23-0045534 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825496 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 5981 | 20230314 | 1146 | 20230316 | 1051 | 2037603 | 2825 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 45200 | 37.0468 | -121.9526 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046398 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826197 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 5203 | 20230314 | 1148 | 20230317 | 1443 | 2037631 | 4495 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 121365 | 37.0394 | -122.0817 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045797 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825721 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 2371 | 20230314 | 1151 | 20230317 | 1345 | 2037688 | 4434 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 120517 | 36.5818 | -121.9091 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045999 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825923 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | RECLOSER | BL 1101 | 20230314 | 1154 | 20230314 | 1212 | 2037916 | 18 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 742 | 13356 | 37.0926 | -122.0966 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 23-0044953 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825038 | 0 | EPSS Ckt | N | 2023 | A GRD
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 5967 | 20230314 | 1155 | 20230314 | 1511 | 2037781 | 196 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 4508 | 37.0034 | -121.9547 | Yes | Clear;32-90 F |  |  | 23-0045408 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825392 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 10714 | 20230314 | 1158 | 20230317 | 1404 | 2037836 | 4446 | Distribution Circuit | Vegetation | Tree - fell into line | 3197 | 815438 | 36.9779 | -121.8666 | Yes | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0044910 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1825007 | 0 | EPSS Ckt | N | 2023 | ABC
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | FUSE | 23113 | 20230314 | 1159 | 20230314 | 1400 | 2037871 | 121 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1089 | 36.5963 | -121.621 | Yes | Partly Cloudy-Strong Winds;32-90 F |  |  | 23-0045273 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825290 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 8193 | 20230314 | 1159 | 20230314 | 1610 | 2037857 | 251 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 40 | 10040 | 36.9817 | -121.8969 | Yes | Clear;32-90 F |  |  | 23-0045554 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825510 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 65444 | 20230314 | 1200 | 20230314 | 1932 | 2035957 | 452 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 623 | 281596 | 37.1278 | -122.1229 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 23-0044927 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825017 | 0 | EPSS Ckt | N | 2023 | A GRD
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 9813 | 20230314 | 1200 | 20230315 | 1600 | 2037901 | 1680 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 60480 | 36.861 | -121.6873 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045368 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825356 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 8541 | 20230314 | 1204 | 20230315 | 1837 | 2038050 | 1833 | Distribution Circuit | Vegetation | Tree - fell into line | 99 | 181467 | 37.0684 | -121.9969 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045786 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1825711 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 8183 | 20230314 | 1205 | 20230315 | 800 | 2045450 | 1195 | Distribution Circuit | Vegetation | Tree - branch fell on line | 115 | 137425 | 36.9646 | -121.8903 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046104 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1826009 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SOQUEL-0402 | 83300402 | FUSE | 6339 | 20230314 | 1205 | 20230315 | 1441 | 2038067 | 1596 | Distribution Circuit | Vegetation | Tree - fell into line | 109 | 56354 | 36.9751 | -121.9496 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045689 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825629 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 5957 | 20230314 | 1206 | 20230314 | 1647 | 2038106 | 281 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 5620 | 37.0051 | -121.9393 | Yes | Clear;32-90 F |  |  | 23-0045584 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825535 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | RECLOSER | BL 1101 | 20230314 | 1213 | 20230314 | 1430 | 2038389 | 137 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 743 | 67638 | 37.0926 | -122.0966 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 23-0044977 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825059 | 0 | EPSS Ckt | N | 2023 | A GRD
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5485 | 20230314 | 1216 | 20230316 | 1011 | 2044621 | 2755 | Distribution Circuit | Vegetation | Tree - branch fell on line | 31 | 85405 | 37.1322 | -122.109 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046167 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826052 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRANSFORMER | 315198725708 | 20230314 | 1216 | 20230317 | 1523 | 2039769 | 4507 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4507 | 37.1944 | -122.1495 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Together | 23-0047100 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826610 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 6183 | 20230314 | 1216 | 20230316 | 1147 | 2044469 | 2851 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 17106 | 37.0079 | -121.8851 | Yes | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045807 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1825729 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 3753 | 20230314 | 1217 | 20230315 | 1509 | 2038402 | 1612 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 20956 | 37.0538 | -121.9526 | Yes | Overcast-Fog-Rain;32-90 F |  |  | 23-0046454 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826230 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | RECLOSER | 355426 | 20230314 | 1225 | 20230314 | 1746 | 2038870 | 321 | Distribution Circuit | Equipment Failure/Involved | Overhead | 382 | 27126 | 36.8411 | -121.5145 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0045018 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825090 | 0 | EPSS Ckt | N | 2023 | A/GRD T
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 6033 | 20230314 | 1229 | 20230315 | 1729 | 2039429 | 1740 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 57 | 99180 | 37.081 | -122.0049 | Yes | Clear;32-90 F |  |  | 23-0046559 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826290 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0422 | 182440422 | FUSE | 2581 | 20230314 | 1244 | 20230315 | 1109 | 2035998 | 1345 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 42997 | 36.5918 | -121.9454 | Yes | Clear;32-90 F |  |  | 23-0046231 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826100 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 2815 | 20230314 | 1245 | 20230315 | 1656 | 2039322 | 1691 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 10146 | 37.0535 | -121.9782 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 23-0046544 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826281 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | FORT ORD-2105 | 182402105 | RECLOSER | 31972 | 20230314 | 1248 | 20230315 | 1350 | 2039486 | 1502 | Distribution Circuit | Vegetation | Tree - branch fell on line | 914 | 1227386 | 36.6437 | -121.81 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045112 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825168 | 0 | EPSS Ckt | N | 2023 | A GRD
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRIP-SAVER | 6625 | 20230314 | 1250 | 20230316 | 1335 | 2039509 | 2925 | Distribution Circuit | Equipment Failure/Involved | Overhead | 126 | 51893 | 36.9558 | -121.7646 | Yes | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0045526 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825489 | 1 | EPSS Ckt | N | 2023 | GRD
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | FUSE | 5173 | 20230314 | 1253 | 20230316 | 1155 | 2039510 | 2822 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 169320 | 37.1011 | -122.1017 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046024 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825943 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 937291 | 20230314 | 1256 | 20230315 | 1911 | 2047109 | 1815 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 23595 | 37.1186 | -121.964 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 23-0046627 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826338 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 10209 | 20230314 | 1258 | 20230314 | 1529 | 2039690 | 151 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 705 | 36.5226 | -121.8035 | Yes | Clear;32-90 F |  |  | 23-0045462 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825435 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 6477 | 20230314 | 1258 | 20230314 | 1631 | 2039630 | 213 | Distribution Circuit | Equipment Failure/Involved | Overhead | 427 | 75347 | 36.8655 | -121.7346 | Yes | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0045084 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1825146 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 10717 | 20230314 | 1304 | 20230315 | 1216 | 2040166 | 1392 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 36192 | 37.0913 | -122.1045 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046229 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826099 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | SWITCH | UNNUM | 20230314 | 1304 | 20230317 | 1631 | 2043249 | 4527 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 31689 | 37.0014 | -122.0229 | Yes | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045553 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1825509 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 1527 | 20230314 | 1304 | 20230317 | 1115 | 2039844 | 4211 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 16844 | 37.0303 | -121.9339 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045728 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825665 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 10449 | 20230314 | 1305 | 20230315 | 1427 | 2039884 | 1522 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 10654 | 37.1105 | -122.047 | Yes | Clear;32-90 F |  |  | 23-0046405 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826200 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 7101 | 20230314 | 1305 | 20230316 | 1806 | 2045306 | 3181 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 101792 | 36.5877 | -121.9125 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046081 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825999 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 3875 | 20230314 | 1321 | 20230315 | 1018 | 2040402 | 1257 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 8799 | 36.9762 | -121.825 | Yes | Clear;32-90 F |  |  | 23-0046207 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826086 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 753753 | 20230314 | 1331 | 20230317 | 1016 | 2041628 | 3157 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 7300 | 37.0994 | -122.1169 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045564 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825518 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 7993 | 20230314 | 1336 | 20230315 | 956 | 2045374 | 1220 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 48800 | 37.0284 | -121.7405 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0046148 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826041 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 8427 | 20230314 | 1348 | 20230316 | 1720 | 2041086 | 3092 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 95336 | 37.077 | -121.981 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046217 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826095 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 1655 | 20230314 | 1411 | 20230315 | 1343 | 2041869 | 1412 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 14120 | 37.1027 | -122.0482 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0046350 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826166 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 869103 | 20230314 | 1418 | 20230315 | 1912 | 2041994 | 1734 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 17340 | 36.8211 | -121.7285 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045463 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825436 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 974520 | 20230314 | 1425 | 20230315 | 1754 | 2042241 | 1649 | Distribution Circuit | Vegetation | Tree - fell into line | 270 | 318384 | 36.9908 | -121.8063 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045500 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825468 | 0 | EPSS Ckt | N | 2023 | A GRD
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 12584 | 20230314 | 1428 | 20230316 | 1830 | 2043187 | 3122 | Distribution Circuit | Vegetation | Tree - fell into line | 2738 | 730756 | 36.9707 | -121.8718 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045539 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | Yes | No | 1825501 | 0 | EPSS Ckt | N | 2023 | ABC
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | TRANSFORMER | 411448247921 | 20230314 | 1447 | 20230316 | 1556 | 2041972 | 2949 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 23592 | 36.6138 | -121.916 | Yes | Partly Cloudy-Strong Winds;32-90 F | Transformer (OH) | Failed/Faulted | 23-0046071 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825993 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 6559 | 20230314 | 1500 | 20230315 | 935 | 2045681 | 1115 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 18955 | 36.9267 | -121.7459 | Yes | Overcast-Drizzle;32-90 F |  |  | 23-0046214 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826092 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | FUSE | 5179 | 20230314 | 1506 | 20230315 | 1420 | 2042610 | 1394 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 30683 | 37.1076 | -122.1077 | Yes | Overcast-Heavy Rain;32-90 F |  |  | 23-0046418 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826207 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 10209 | 20230314 | 1550 | 20230316 | 1810 | 2043015 | 3020 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 21140 | 36.5226 | -121.8035 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0046981 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826539 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 2725 | 20230314 | 1556 | 20230315 | 1234 | 2043070 | 1238 | Distribution Circuit | Vegetation | Tree - fell into line | 207 | 256266 | 36.5453 | -121.9281 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045726 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825663 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 6677 | 20230314 | 1608 | 20230316 | 956 | 2035978 | 2508 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 59400 | 36.5489 | -121.9198 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0045530 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1825492 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 5090 | 20230314 | 1613 | 20230314 | 2028 | 2042186 | 255 | Distribution Circuit | Vegetation | Tree - fell into line | 428 | 109140 | 36.9804 | -121.892 | Yes | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045535 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825497 | 0 | EPSS Ckt | N | 2023 | B GRD
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | TRANSFORMER | 411424045660 | 20230314 | 1637 | 20230316 | 1019 | 2043360 | 2502 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 25020 | 36.5519 | -121.921 | Yes |  | Cutout- fuse holder | Broken | 23-0046564 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826294 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 3823 | 20230314 | 1707 | 20230315 | 1650 | 2043662 | 1423 | Distribution Circuit | Equipment Failure/Involved | Overhead | 73 | 103879 | 36.9736 | -121.727 | Yes | Overcast-Fog-Rain;32-90 F | Cutout- fuse holder | Broken | 23-0045697 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825637 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | SWITCH | 40387 | 20230314 | 1800 | 20230314 | 1919 | 2044300 | 79 | Distribution Circuit | Vegetation | Tree - fell into line | 2738 | 216302 | 36.6144 | -121.9247 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045771 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1825699 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 737 | 20230314 | 1821 | 20230315 | 1352 | 2044095 | 202 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 11568 | 37.0046 | -121.8551 | Yes | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045877 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825801 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 9022 | 20230314 | 1854 | 20230315 | 1252 | 2045771 | 1078 | Distribution Circuit | Equipment Failure/Involved | Underground | 154 | 166012 | 36.5395 | -121.8712 | Yes | Overcast-Fog-Rain;32-90 F | Elbow | Failed/Faulted | 23-0046184 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826067 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 595388 | 20230314 | 1855 | 20230315 | 1833 | 2044303 | 1418 | Distribution Circuit | Vegetation | Tree - fell into line | 133 | 188594 | 37.1517 | -122.136 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045772 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825700 | 0 | EPSS Ckt | N | 2023 | ABC G
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | OCB | 2102/2 | 20230314 | 1920 | 20230408 | 2221 | 2044466 | 36181 | Distribution Circuit | Environmental/External | Flood/Erosion | 233 | 77386 | 36.2938 | -121.1999 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0045767 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1825733 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 6773 | 20230314 | 1922 | 20230315 | 1937 | 2044458 | 1455 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 128040 | 36.88 | -121.6403 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045891 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825814 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | FUSE | 8235 | 20230314 | 1932 | 20230315 | 1544 | 2044539 | 1212 | Distribution Circuit | Vegetation | Tree - branch fell on line | 66 | 78921 | 36.6254 | -121.9339 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0046463 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826233 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 823 | 20230314 | 1945 | 20230316 | 1304 | 2044531 | 2479 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 2479 | 37.044 | -122.1497 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046493 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826246 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 8163 | 20230314 | 1947 | 20230317 | 1542 | 2044540 | 4075 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 122250 | 36.5988 | -121.9389 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045823 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825745 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRANSFORMER | 315234423451 | 20230314 | 1955 | 20230315 | 1251 | 2045364 | 1016 | Transformer only | Vegetation | Tree - fell into line | 5 | 5080 | 37.1321 | -122.1357 | Yes | Clear;32-90 F | Secondary | Broken | 23-0046336 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826159 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5503 | 20230314 | 1956 | 20230315 | 1732 | 2044562 | 1296 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 50544 | 37.1461 | -122.1291 | Yes | Clear;32-90 F |  |  | 23-0046486 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826244 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | JUMPER | 8557 OPEN HS JUMPERS | 20230314 | 2010 | 20230315 | 1859 | 2044639 | 1369 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 8214 | 36.5663 | -121.8869 | Yes | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045844 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1825766 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 6737 | 20230314 | 2010 | 20230315 | 1457 | 2044653 | 1127 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 23667 | 36.5709 | -121.8861 | Yes | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045851 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1825772 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRANSFORMER | 315310123506 | 20230314 | 2012 | 20230317 | 1450 | 2048132 | 3998 | Transformer only | Vegetation | Tree - branch fell on line | 3 | 11994 | 37.1348 | -122.108 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0046941 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826514 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | OTHER | 9755 | 20230314 | 2025 | 20230316 | 1316 | 2044662 | 2451 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 24507 | 37.1665 | -122.1876 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045946 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825871 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 6657 | 20230314 | 2050 | 20230315 | 1123 | 2044731 | 873 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 38 | 33174 | 36.9712 | -121.7958 | Yes | Clear;32-90 F |  |  | 23-0046271 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826117 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | RECLOSER | 2606 | 20230314 | 2050 | 20230317 | 1624 | 2044702 | 4054 | Distribution Circuit | Vegetation | Tree - fell into line | 179 | 725666 | 36.577 | -121.9511 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0045866 | OH | Sus | 35431808 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1825789 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 3413 | 20230314 | 2057 | 20230316 | 1902 | 2044769 | 2765 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 16590 | 37.0301 | -121.8579 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046422 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826209 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1106 | 182031106 | FUSE | 7103 | 20230314 | 2311 | 20230317 | 1512 | 2044957 | 3841 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 49933 | 36.3107 | -120.9185 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046187 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826069 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 7371 | 20230314 | 2317 | 20230316 | 1605 | 2044960 | 2448 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 14688 | 37.0585 | -122.142 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046383 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1826189 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | FUSE | 9609 | 20230315 | 145 | 20230316 | 1903 | 2047050 | 2478 | Distribution Circuit | Vegetation | Tree - fell into line | 319 | 416065 | 36.2816 | -121.4563 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046611 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1826328 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRANSFORMER | 315171022968 | 20230315 | 726 | 20230315 | 2214 | 2045419 | 888 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 888 | 37.1191 | -122.1572 | No | Clear;32-90 F |  |  | 23-0046778 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1826430 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 7567 | 20230315 | 735 | 20230315 | 915 | 2045413 | 100 | Distribution Circuit | Vegetation | Tree - grew into line | 20 | 2000 | 37.0522 | -121.9295 | No | Fog;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0046103 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826008 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | FUSE | 3623 | 20230315 | 810 | 20230315 | 1044 | 2045492 | 154 | Distribution Circuit | Wildfire Mitigation | CWSP - Vegetation Removal | 93 | 14322 | 36.9882 | -121.9377 | No | Fog;32-90 F | Conductor- Overhead | Normal | 23-0046113 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1826013 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 10479 | 20230315 | 823 | 20230315 | 1853 | 2045531 | 630 | Distribution Circuit | Wildfire Mitigation | CWSP - Vegetation Removal | 89 | 56070 | 36.5643 | -121.9227 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0046124 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826025 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 5151 | 20230315 | 934 | 20230315 | 1632 | 2045706 | 418 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 2090 | 37.111 | -122.0899 | No | Clear;32-90 F |  |  | 23-0046546 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826282 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | RECLOSER | 75304 | 20230315 | 943 | 20230315 | 1004 | 2045740 | 21 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 874 | 18354 | 36.5245 | -121.8121 | No | Partly Cloudy;32-90 F |  |  | 23-0046175 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826058 | 0 | EPSS Ckt | N | 2023 | C GRD
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | SWITCH | 391980 | 20230315 | 1004 | 20230315 | 1029 | 2045789 | 25 | Distribution Circuit | Vegetation | Tree - branch fell on line | 49 | 1225 | 37.1469 | -122.0881 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0046193 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826074 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 4731 | 20230315 | 1014 | 20230316 | 839 | 2045816 | 1345 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 6725 | 37.0923 | -122.076 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0046890 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | No | No | 1826484 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1103 | 182031103 | FUSE | 2529 | 20230315 | 1156 | 20230315 | 1528 | 2046057 | 212 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 4242 | 36.1899 | -121.1514 | No | Clear;32-90 F |  |  | 23-0046445 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826223 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1101 | 182031101 | FUSE | 9603 | 20230315 | 1221 | 20230315 | 1416 | 2046127 | 115 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 379 | 43585 | 36.214 | -121.1268 | No | Clear;32-90 F |  |  | 23-0046341 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826163 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 5725 | 20230315 | 1225 | 20230315 | 1256 | 2045596 | 31 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 434 | 36.9902 | -121.7368 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0046322 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826150 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 8917 | 20230315 | 1227 | 20230317 | 1401 | 2049068 | 2974 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 62454 | 36.5771 | -121.9274 | No | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0047205 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826671 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 4879 | 20230315 | 1234 | 20230316 | 1503 | 2046146 | 1589 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 58793 | 36.9567 | -122.034 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0046324 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826151 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 3875 | 20230315 | 1316 | 20230315 | 1404 | 2046226 | 48 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 336 | 36.9762 | -121.825 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0046420 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826208 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRANSFORMER | 315479222480 | 20230315 | 1359 | 20230316 | 1726 | 2046875 | 1647 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1647 | 37.1067 | -122.0515 | No | Clear;32-90 F | Transformer | Burned Open | 23-0046568 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826298 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 6743 | 20230315 | 1400 | 20230316 | 1720 | 2046413 | 1640 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 57400 | 36.5711 | -121.8898 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046426 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1826211 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | OTHER | WIRE DOWN HOT 2 N/OF CGC# 316224819668 | 20230315 | 1421 | 20230316 | 1805 | 2046893 | 1664 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1664 | 37.0335 | -121.7947 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046580 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | Yes | No | 1826302 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0424 | 182440424 | TRANSFORMER | 411415648286 | 20230315 | 1428 | 20230315 | 2123 | 2046388 | 415 | Transformer only | Vegetation | Tree - palm frond fell into line | 9 | 3735 | 36.6234 | -121.9275 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046512 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826259 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | RECLOSER | 2070 | 20230315 | 1604 | 20230315 | 1749 | 2046658 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 766 | 80430 | 36.5447 | -121.9082 | No | Overcast-Rain;32-90 F |  |  | 23-0046510 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826258 | 0 | EPSS Ckt | N | 2023 | SGF
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316308118551 | 20230315 | 1618 | 20230315 | 1808 | 2046682 | 110 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 220 | 37.0029 | -121.7651 | No | Clear;32-90 F |  |  | 23-0046614 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1826330 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 2283 | 20230315 | 1626 | 20230315 | 2013 | 2046700 | 227 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 95 | 21565 | 36.5564 | -121.9087 | No | Clear;32-90 F |  |  | 23-0046668 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826357 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | OTHER | WIRE DOWN SS/OF 8979 | 20230315 | 1628 | 20230316 | 1530 | 2046681 | 1374 | Distribution Circuit | Equipment Failure/Involved | Overhead | 660 | 49879 | 36.5978 | -121.8891 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046561 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | Yes | 1826291 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | TRANSFORMER | 411589646541 | 20230315 | 1729 | 20230316 | 1814 | 2046874 | 1485 | Transformer only | Environmental/External | Water | 4 | 5940 | 36.5771 | -121.8661 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0046685 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826367 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | TRANSFORMER | 315468722485 | 20230315 | 1742 | 20230317 | 1552 | 2046907 | 2770 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2770 | 37.1067 | -122.0548 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0046586 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1826308 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 8703 | 20230315 | 1817 | 20230316 | 1103 | 2047032 | 1006 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 29174 | 36.541 | -121.9164 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046604 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826322 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 2875 | 20230315 | 2007 | 20230317 | 1438 | 2047262 | 2551 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 20408 | 36.4995 | -121.9313 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0047133 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826625 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 316169418886 | 20230315 | 2046 | 20230315 | 2146 | 2047278 | 60 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 120 | 37.0113 | -121.813 | No | Clear;32-90 F |  |  | 23-0046752 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1826405 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | TRANSFORMER | 411381743648 | 20230315 | 2112 | 20230317 | 1127 | 2047311 | 2295 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 11475 | 36.4956 | -121.9328 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Failed/Faulted | 23-0047512 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826865 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 629 | 20230315 | 2220 | 20230316 | 1745 | 2047283 | 1165 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 18640 | 36.5473 | -121.8977 | No | Clear;32-90 F | Conductor- Overhead | Burned/flashed | 23-0046751 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826404 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | JUMPER | WIRE DOWN HOT 2 N/OF CGC# 316247419310 | 20230316 | 24 | 20230316 | 1814 | 2047783 | 1070 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4003 | 37.0237 | -121.787 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0046885 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826480 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | TRANSFORMER | 411374043736 | 20230316 | 741 | 20230316 | 1009 | 2047746 | 148 | Transformer only | Vegetation | Tree - bark fell into line | 3 | 444 | 36.4979 | -121.9356 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0046935 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826511 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 10479 | 20230316 | 916 | 20230316 | 1325 | 2047947 | 249 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 22161 | 36.5643 | -121.9227 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0046914 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826500 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | JUMPER | OJ 2 POLES W/OF 411426546186 | 20230316 | 1130 | 20230316 | 1330 | 2047572 | 120 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 240 | 36.5654 | -121.9225 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0046942 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826516 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 1403 | 20230316 | 1306 | 20230316 | 1501 | 2048494 | 115 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 106 | 12190 | 36.5521 | -121.9031 | No | Clear;32-90 F |  |  | 23-0047069 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826595 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 8525 | 20230316 | 1346 | 20230316 | 1420 | 2048576 | 34 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 986 | 37.0586 | -122.1473 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0047054 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826587 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | TRANSFORMER | T0535 | 20230316 | 1533 | 20230317 | 1702 | 2048827 | 1529 | Distribution Circuit | Equipment Failure/Involved | Underground | 6 | 9174 | 36.5453 | -121.9057 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0047160 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826644 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0424 | 182440424 | TRANSFORMER | 411416648568 | 20230316 | 1553 | 20230316 | 1801 | 2048872 | 128 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 1280 | 36.6313 | -121.9274 | No | Clear;32-90 F | Secondary | Deteriorated | 23-0047141 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826631 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 412030855150 | 20230316 | 1601 | 20230318 | 1338 | 2048584 | 2737 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 5474 | 36.8184 | -121.7228 | No | Clear;32-90 F | Transformer | Deteriorated | 23-0047147 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826634 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 2710 | 20230316 | 1613 | 20230316 | 1651 | 2048865 | 38 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 50 | 1900 | 36.5316 | -121.8709 | No | Partly Cloudy;32-90 F |  |  | 23-0047186 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826662 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | SWITCH | 894556 | 20230316 | 1627 | 20230317 | 1044 | 2048929 | 1097 | Distribution Circuit | Environmental/External | Flood/Erosion | 8 | 2392 | 37.058 | -121.9416 | No | Clear;32-90 F | Pole-Wood | Normal | 23-0047164 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826646 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 412037554546 | 20230316 | 1640 | 20230317 | 1630 | 2048953 | 1430 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 7150 | 36.8016 | -121.7213 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0047177 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826654 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | JUMPER | OJ .5 POLE SS OF CGC 412050654513 | 20230316 | 1655 | 20230317 | 1630 | 2048991 | 1415 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1415 | 36.8021 | -121.718 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0047189 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1826663 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 1403 | 20230316 | 1753 | 20230317 | 1649 | 2049061 | 287 | Distribution Circuit | Equipment Failure/Involved | Underground | 100 | 23355 | 36.5521 | -121.9031 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0047252 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826713 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | TRANSFORMER | 315802421015 | 20230316 | 1806 | 20230317 | 1106 | 2049077 | 1020 | Transformer only | Vegetation | Tree - fell into line | 1 | 1020 | 37.0678 | -121.94 | No | Partly Cloudy;32-90 F | Transformer | Broken- wire on ground | 23-0047217 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826682 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 413490547650 | 20230316 | 1822 | 20230317 | 1400 | 2049105 | 1168 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 2676 | 36.6221 | -121.2199 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0047309 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1826770 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 2323 | 20230316 | 1958 | 20230317 | 1300 | 2049246 | 1022 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 51100 | 36.5822 | -121.9214 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0047396 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826804 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 6975 | 20230316 | 2000 | 20230317 | 1020 | 2049251 | 860 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 35950 | 36.5797 | -121.9204 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0047388 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | No | No | 1826798 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 10421 | 20230316 | 2202 | 20230317 | 404 | 2049367 | 362 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1929 | 36.5659 | -121.9346 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0047350 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826785 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 3045 | 20230317 | 655 | 20230318 | 1116 | 2049489 | 1701 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 5103 | 36.8684 | -121.6508 | No | Clear;32-90 F | Cutout- fuse holder | Failed/Faulted | 23-0047433 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826828 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0422 | 182440422 | TRANSFORMER | 411430647827 | 20230317 | 726 | 20230317 | 1720 | 2049512 | 594 | Transformer only | Vegetation | Tree - fell into line | 10 | 5940 | 36.6111 | -121.9217 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0047645 | OH | Sus | 35431808 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826926 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 40417 | 20230317 | 823 | 20230317 | 955 | 2049595 | 92 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 276 | 36.4909 | -121.9362 | No | Overcast-Fog;32-90 F |  |  | 23-0047452 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826838 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | JUMPER | WIRE DWN | 20230317 | 828 | 20230317 | 1630 | 2049606 | 482 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 3264 | 36.5691 | -121.9367 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0047403 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826806 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | TRANSFORMER | 315772517818 | 20230317 | 928 | 20230317 | 1857 | 2049719 | 569 | Transformer only | Vegetation | Tree - fell into line | 9 | 5121 | 36.9801 | -121.9475 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0047451 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826837 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | TRANSFORMER | 411477145504 | 20230317 | 935 | 20230317 | 1313 | 2049730 | 218 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 218 | 36.5477 | -121.9033 | No | Partly Cloudy;32-90 F |  |  | 23-0047608 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1826911 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 7259 | 20230317 | 1115 | 20230317 | 1851 | 2049920 | 456 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 14592 | 36.5752 | -121.9365 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0047534 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826876 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | BUENA VISTA-1106 | 182261106 | TRANSFORMER | T3243 | 20230317 | 1132 | 20230317 | 1531 | 2049944 | 239 | Transformer only | Equipment Failure/Involved | Electrical Overload | 5 | 1195 | 36.622 | -121.6299 | No | Overcast;32-90 F | Transformer | Deteriorated | 23-0047574 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826893 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | TRANSFORMER | 315723317357 | 20230317 | 1138 | 20230317 | 1618 | 2049650 | 280 | Transformer only | Vegetation | Tree - fell into line | 1 | 280 | 36.9675 | -121.965 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0047543 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826879 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | TRANSFORMER | 412268552201 | 20230317 | 1233 | 20230317 | 1830 | 2049852 | 357 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 1785 | 36.738 | -121.6405 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 23-0047579 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826894 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | SWITCH | 11029 | 20230317 | 1241 | 20230317 | 1524 | 2050094 | 163 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 15322 | 37.1929 | -122.1456 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0047060 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826904 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2102 | 182222102 | TRANSFORMER | 411673248095 | 20230317 | 1248 | 20230317 | 1324 | 2050091 | 36 | Transformer only | Vegetation | Tree - grew into line | 44 | 1584 | 36.6202 | -121.8389 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0047591 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826902 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 4941 | 20230317 | 1333 | 20230323 | 801 | 2050180 | 8308 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 8308 | 36.8973 | -121.746 | No | Clear;32-90 F | Transformer (UG) | Normal | 23-0047724 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1826969 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 805 | 20230317 | 1334 | 20230317 | 1726 | 2050184 | 232 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 232 | 36.8964 | -121.7445 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0047719 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826965 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | TRANSFORMER | T1882 | 20230317 | 1414 | 20230317 | 1754 | 2050242 | 220 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 440 | 36.5388 | -121.92 | No | Partly Cloudy;32-90 F | Transformer | Annealed | 23-0047693 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826944 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | SWITCH | 894556 | 20230317 | 1522 | 20230317 | 1911 | 2050253 | 229 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 1832 | 37.058 | -121.9416 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0047673 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826934 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | SWITCH | 1810 | 20230317 | 1523 | 20230317 | 1548 | 2050384 | 25 | Distribution Circuit | Company Initiated | Return Circuit Normal | 71 | 1775 | 37.0539 | -122.0257 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0042780 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1826945 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 6855 | 20230317 | 1558 | 20230317 | 1652 | 2050430 | 54 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 430 | 23220 | 36.5958 | -121.9421 | No | Partly Cloudy;32-90 F |  |  | 23-0047707 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826954 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 88094 | 20230317 | 1558 | 20230317 | 1758 | 2050606 | 120 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 89 | 10680 | 36.5966 | -121.9409 | No | Partly Cloudy;32-90 F |  |  | 23-0047728 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826974 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 1421 | 20230317 | 1644 | 20230317 | 2153 | 2050507 | 309 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 6180 | 36.5743 | -121.9483 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0047770 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827002 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | FUSE | 6029 | 20230317 | 1717 | 20230317 | 1857 | 2050561 | 100 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 111 | 11100 | 36.6089 | -121.9306 | No | Partly Cloudy;32-90 F |  |  | 23-0047747 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826988 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | TRANSFORMER | 411394847620 | 20230317 | 1721 | 20230317 | 1958 | 2050566 | 157 | Transformer only | Unknown Cause | Patrol - found nothing | 5 | 785 | 36.6051 | -121.9338 | No | Partly Cloudy;32-90 F |  |  | 23-0047753 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1826994 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | RECLOSER | 4060 | 20230317 | 1726 | 20230317 | 1733 | 2050576 | 7 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1002 | 7014 | 36.801 | -121.3379 | No | Partly Cloudy;32-90 F |  |  | 23-0047726 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826971 | 0 | EPSS Ckt | N | 2023 | GRD
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 4765 | 20230317 | 1728 | 20230318 | 1731 | 2050575 | 1147 | Distribution Circuit | Equipment Failure/Involved | Underground | 399 | 100835 | 36.8161 | -121.3641 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0047734 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826978 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 8171 | 20230317 | 1946 | 20230318 | 1805 | 2050727 | 1339 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2892 | 36.5445 | -121.8848 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0048307 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1827522 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 7259 | 20230317 | 2035 | 20230318 | 1006 | 2050748 | 811 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 45 | 36495 | 36.5752 | -121.9365 | No | Partly Cloudy;32-90 F |  |  | 23-0048077 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827310 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 48031 | 20230318 | 956 | 20230318 | 1635 | 2051010 | 399 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 4788 | 36.5994 | -121.9377 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0048271 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1827495 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | TRANSFORMER | 411403048067 | 20230318 | 1016 | 20230318 | 1333 | 2051028 | 197 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 1970 | 36.6175 | -121.9315 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 23-0048277 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827501 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1104 | 182031104 | RECLOSER | 7092 | 20230318 | 1339 | 20230318 | 1540 | 2051256 | 121 | Distribution Circuit | Environmental/External | Flood/Erosion | 57 | 6309 | 36.2036 | -121.1157 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 23-0048320 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1827529 | 0 | EPSS Ckt | N | 2023 | A C & GRD
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRANSFORMER | 315291623275 | 20230318 | 2108 | 20230319 | 1000 | 2051563 | 772 | Transformer only | Vegetation | Tree - fell into line | 6 | 4632 | 37.1288 | -122.1142 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0048412 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1827618 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1109 | 182011109 | FUSE | 948327 | 20230319 | 331 | 20230320 | 1306 | 2051648 | 2015 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 18135 | 36.6776 | -121.5908 | No | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0048451 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827661 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5617 | 20230319 | 410 | 20230319 | 645 | 2051663 | 155 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 1395 | 37.0986 | -122.0532 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0048439 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827647 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 2895 | 20230319 | 558 | 20230319 | 1943 | 2051714 | 825 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 825 | 36.8905 | -121.7181 | No | Overcast;32-90 F | Crossarm- Wood | Normal | 23-0048463 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827674 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 10728 | 20230319 | 739 | 20230319 | 912 | 2051782 | 93 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 149 | 13857 | 37.0665 | -122.0797 | No | Overcast-Drizzle;32-90 F |  |  | 23-0048444 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1827653 | 0 | EPSS Ckt | N | 2023 | A & B PHASE
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 6689 | 20230319 | 829 | 20230319 | 1130 | 2051809 | 181 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1991 | 36.8881 | -121.8071 | No | Overcast-Fog-Rain;32-90 F |  |  | 23-0048477 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827687 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | OTHER | WIRE DOWN @ CGC 315379321278 TWDS 7243 | 20230319 | 919 | 20230319 | 1742 | 2051860 | 503 | Distribution Circuit | Equipment Failure/Involved | Overhead | 170 | 76997 | 37.0728 | -122.0844 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0048469 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | Yes | Yes | 1827680 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 12435 | 20230319 | 1047 | 20230319 | 1908 | 2051950 | 501 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 8517 | 37.1378 | -122.0133 | No | Clear;32-90 F |  |  | 23-0048553 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827761 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | SWITCH | 4096 | 20230319 | 1111 | 20230319 | 1408 | s1827683 | 15 | Distribution Circuit | Equipment Failure/Involved | Underground | 42 | 414 | 0 | 0 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0048358 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1827683 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412203554060 | 20230319 | 1131 | 20230319 | 1645 | 2051977 | 314 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 628 | 36.7885 | -121.6638 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0048480 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827690 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 412022854446 | 20230319 | 1352 | 20230319 | 1933 | 2052048 | 341 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1364 | 36.7989 | -121.7262 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0048503 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827710 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 11877 | 20230319 | 1622 | 20230319 | 1842 | 2052032 | 140 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 3360 | 37.0433 | -122.1149 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0048507 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1827714 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | JUMPER | BURNT #3 OJ @ 7993 | 20230319 | 1654 | 20230320 | 116 | 2052253 | 502 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 20080 | 37.0284 | -121.7405 | No | Overcast-Fog-Drizzle;32-90 F | Jumper | Burned Open | 23-0048555 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1827763 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411935153385 | 20230319 | 1734 | 20230320 | 139 | 2052211 | 485 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 8245 | 36.7685 | -121.7547 | No | Overcast;32-90 F | Transformer (OH) | Deteriorated | 23-0048541 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827750 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5239 | 20230319 | 1758 | 20230319 | 2035 | 2052288 | 154 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 41 | 6314 | 37.0682 | -122.0827 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 23-0048557 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827765 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 4269 | 20230319 | 2003 | 20230320 | 1316 | 2052351 | 1033 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 34399 | 36.9143 | -121.6626 | No | Clear;32-90 F |  |  | 23-0048560 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827768 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 6875 | 20230319 | 2021 | 20230320 | 1320 | 2052358 | 1019 | Distribution Circuit | Vegetation | Tree - fell into line | 102 | 48239 | 36.8864 | -121.6325 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Together | 23-0048587 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | No | No | 1827795 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 6771 | 20230320 | 703 | 20230320 | 1243 | 2052591 | 340 | Distribution Circuit | Animal | Bird found | 53 | 18020 | 36.8682 | -121.6457 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0048860 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827916 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 593 | 20230320 | 706 | 20230320 | 917 | 2052592 | 129 | Distribution Circuit | Vegetation | Tree - branch fell on line | 87 | 11223 | 36.8071 | -121.7199 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0048700 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1827867 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | BUENA VISTA-1106 | 182261106 | JUMPER | #2 OJ HIGH SIDE OF 23235 | 20230320 | 750 | 20230320 | 1121 | 2052626 | 211 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 422 | 36.6404 | -121.6159 | No | Overcast;32-90 F | Jumper | Burned Open | 23-0048698 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1827866 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | TRANSFORMER | 411531646291 | 20230320 | 944 | 20230320 | 1108 | 2052809 | 84 | Transformer only | Vegetation | Tree - fell into line | 2 | 168 | 36.5697 | -121.886 | No | Overcast;32-90 F | Fuse | Normal | 23-0048765 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827898 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1103 | 182201103 | FUSE | 23491 | 20230320 | 1156 | 20230320 | 1410 | 2052988 | 134 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 804 | 36.635 | -121.5541 | No | Overcast;32-90 F |  |  | 23-0048929 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827933 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 40647 | 20230320 | 1238 | 20230321 | 259 | 2053036 | 861 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 9471 | 36.5721 | -121.9319 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 23-0048896 | OH | Sus | 35431808 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1827925 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SOLEDAD-2102 | 182052102 | TRANSFORMER | 413102539202 | 20230320 | 1434 | 20230321 | 1047 | 2053186 | 1213 | Transformer only | Environmental/External | Flood/Erosion | 1 | 1213 | 36.387 | -121.3444 | No | Overcast;32-90 F | Transformer | Broken | 23-0048947 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827942 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1106 | 182031106 | FUSE | 9301 | 20230320 | 1820 | 20230407 | 1101 | 2053494 | 25481 | Distribution Circuit | Environmental/External | Flood/Erosion | 4 | 1150 | 36.1661 | -121.0624 | No | Clear;32-90F | Pole-Wood | Broken | 23-0049050 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 90879 | No | No | No | 1828007 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6597 | 20230320 | 2116 | 20230320 | 2356 | 2053474 | 160 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 960 | 36.9966 | -121.7163 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0049021 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1827979 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | TRANSFORMER | 315751120712 | 20230321 | 255 | 20230325 | 1208 | 2053523 | 6313 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 12626 | 37.0597 | -121.9542 | Yes | Overcast-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 23-0049074 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828032 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 6121 | 20230321 | 627 | 20230322 | 1044 | 2053573 | 1697 | Distribution Circuit | Vegetation | Tree - fell into line | 109 | 184973 | 36.9835 | -121.8848 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 23-0049108 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828040 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | RECLOSER | 3030 | 20230321 | 703 | 20230321 | 1434 | 2053594 | 451 | Distribution Circuit | 3rd Party | Vehicle | 262 | 16271 | 36.5854 | -121.6002 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0049081 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1828036 | 0 | EPSS Ckt | N | 2023 | ABC
CENTRAL COAST | SALINAS | SALINAS-1109 | 182011109 | FUSE | 948327 | 20230321 | 714 | 20230321 | 1158 | 2053601 | 284 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 2556 | 36.6776 | -121.5908 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Normal | 23-0049143 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828055 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | FUSE | 40251 | 20230321 | 743 | 20230321 | 1225 | 2053631 | 282 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 59 | 16638 | 36.2415 | -121.7971 | Yes | Overcast-Drizzle;32-90 F |  |  | 23-0049465 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828231 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 9499 | 20230321 | 806 | 20230326 | 1352 | 2053644 | 7546 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 15092 | 37.0276 | -122.0241 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049597 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828341 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 3649 | 20230321 | 807 | 20230323 | 1334 | 2053645 | 3207 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 25656 | 36.9864 | -121.8506 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049420 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828194 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1109 | 182011109 | FUSE | 948327 | 20230321 | 813 | 20230323 | 1635 | 2054313 | 3382 | Distribution Circuit | Animal | Bird found | 9 | 30438 | 36.6776 | -121.5908 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0050051 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828730 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | JUMPER | 6371 LD SIDE BOJ POS #3 | 20230321 | 831 | 20230321 | 1005 | 2053869 | 94 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 1034 | 36.8638 | -121.7228 | Yes | Overcast-Fog-Rain;32-90 F | Jumper | Burned Open | 23-0049205 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1828085 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 95690 | 20230321 | 833 | 20230323 | 1028 | 2060226 | 2995 | Distribution Circuit | Vegetation | Tree - branch fell on line | 277 | 829615 | 37.1249 | -122.125 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0050062 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828740 | 0 | EPSS Ckt | N | 2023 | BC
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | SWITCH | 6185 | 20230321 | 833 | 20230322 | 1006 | 2060506 | 1533 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 124 | 190092 | 37.1304 | -122.1713 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 23-0049497 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1828785 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9771 | 20230321 | 833 | 20230325 | 1809 | 2062120 | 6336 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 221760 | 37.1313 | -122.1209 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050428 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829038 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 10720 | 20230321 | 833 | 20230322 | 1328 | 2062196 | 1735 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 32965 | 37.1085 | -122.1441 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0049497 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1829061 | 0 | EPSS Ckt | N | 2023 | NA
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5419 | 20230321 | 833 | 20230325 | 1621 | 2062460 | 6228 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 292716 | 37.1244 | -122.1281 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050584 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829117 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 8099 | 20230321 | 833 | 20230325 | 938 | 2062521 | 5825 | Distribution Circuit | Vegetation | Tree - bark fell into line | 108 | 392038 | 37.1245 | -122.1245 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050607 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829127 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 11867 | 20230321 | 833 | 20230322 | 1333 | 2062662 | 1740 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 45240 | 37.1248 | -122.1265 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 23-0050637 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1829146 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | SWITCH | 11035 | 20230321 | 833 | 20230323 | 1054 | 2062920 | 3021 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 30210 | 37.127 | -122.1227 | Yes | Overcast-Heavy Rain;32-90 F |  |  | 23-0049497 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1829214 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 65444 | 20230321 | 833 | 20230324 | 2146 | 2062931 | 5113 | Distribution Circuit | Vegetation | Tree - branch fell on line | 196 | 1002148 | 37.1278 | -122.1229 | Yes | Overcast-Heavy Rain;32-90 F | Secondary | Broken | 23-0049497 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1829216 | 0 | EPSS Ckt | N | 2023 | NA
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 12838 | 20230321 | 833 | 20230323 | 1730 | 2063062 | 3417 | Distribution Circuit | Vegetation | Tree - branch fell on line | 78 | 266526 | 37.1272 | -122.1236 | Yes | Overcast-Heavy Rain;32-90 F | Crossarm- Wood | Broken | 23-0049497 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1829252 | 0 | EPSS Ckt | N | 2023 | NA
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5435 | 20230321 | 833 | 20230324 | 948 | 2063152 | 4395 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 30765 | 37.1175 | -122.1214 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050837 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829267 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5509 | 20230321 | 833 | 20230325 | 1630 | 2063398 | 6237 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 124740 | 37.1532 | -122.1291 | Yes | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0050916 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829319 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | JUMPER | 9717 HIGH SIDE JMPRS | 20230321 | 833 | 20230325 | 938 | 2063453 | 5825 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 139800 | 37.1414 | -122.1289 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050930 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829331 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | JUMPER | JMPRS 1 LD SIDE OF 5497 | 20230321 | 833 | 20230325 | 1314 | 2063461 | 6041 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 42287 | 37.1403 | -122.1305 | Yes | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0050933 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829334 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | JUMPER | JMPRS 2 SOURCE SIDE OF CGC 315264823340 | 20230321 | 833 | 20230324 | 2140 | 2063478 | 5107 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 5107 | 37.129 | -122.1249 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050941 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829340 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9709 | 20230321 | 833 | 20230325 | 1723 | 2063622 | 6290 | Distribution Circuit | Vegetation | Tree - bark fell into line | 15 | 94350 | 37.1163 | -122.1184 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050970 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829362 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | SWITCH | 965617 | 20230321 | 833 | 20230325 | 1526 | 2064225 | 6173 | Distribution Circuit | Vegetation | Tree - fell into line | 161 | 993853 | 37.1284 | -122.1227 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051214 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829546 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 12069 | 20230321 | 833 | 20230324 | 1253 | 2064383 | 4580 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 151140 | 37.1239 | -122.1197 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051279 | OH | Sus | 35431731 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1829581 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | SWITCH | 8451 | 20230321 | 833 | 20230325 | 714 | 2064404 | 5681 | Distribution Circuit | Vegetation | Tree - fell into line | 142 | 806702 | 37.1463 | -122.1334 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0049497 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1829589 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5507 | 20230321 | 833 | 20230325 | 1423 | 2064683 | 6110 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 201630 | 37.1419 | -122.1319 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051394 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829645 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | JUMPER | JMPRS 2 POLES SOURCE SIDE OF CGC 315292524349 | 20230321 | 833 | 20230325 | 1600 | 2064716 | 6207 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 18621 | 37.1577 | -122.1172 | Yes | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051404 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829651 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5501 | 20230321 | 833 | 20230325 | 1610 | 2064820 | 6217 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 603049 | 37.1431 | -122.1318 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051431 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829668 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5503 | 20230321 | 833 | 20230325 | 1610 | 2064824 | 6217 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 242463 | 37.1461 | -122.1291 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051433 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829669 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 12359 | 20230321 | 833 | 20230325 | 1609 | 2064836 | 6216 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 12432 | 37.1569 | -122.12 | Yes | Overcast-Heavy Rain;32-90 F |  |  | 23-0051443 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1829672 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5445 | 20230321 | 833 | 20230326 | 1935 | 2064930 | 7862 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 70758 | 37.1301 | -122.1341 | Yes | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051486 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829691 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9747 | 20230321 | 833 | 20230327 | 1113 | 2064933 | 8800 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 8800 | 37.1282 | -122.1326 | Yes | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051489 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1829693 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 595388 | 20230321 | 833 | 20230326 | 2038 | 2064977 | 7925 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 459650 | 37.1517 | -122.136 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051505 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829704 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | SWITCH | 696141 | 20230321 | 833 | 20230325 | 1526 | 2064984 | 6173 | Distribution Circuit | Vegetation | Tree - fell into line | 158 | 975334 | 37.1328 | -122.1067 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051214 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829706 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9725 | 20230321 | 833 | 20230326 | 2038 | 2065562 | 7925 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 206050 | 37.1523 | -122.1367 | Yes | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051677 | OH | Sus | 35431731 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829823 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9733 | 20230321 | 833 | 20230326 | 2038 | 2065564 | 7925 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 388325 | 37.158 | -122.1357 | Yes | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051678 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829824 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5521 | 20230321 | 833 | 20230327 | 1737 | 2065565 | 9184 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 119392 | 37.1577 | -122.1357 | Yes | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051679 | OH | Sus | 35431731 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1829825 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 445933 | 20230321 | 833 | 20230325 | 1526 | 2065788 | 6173 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 345688 | 37.1372 | -122.1004 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051772 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829861 | 0 | EPSS Ckt | N | 2023 | NA
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9769 | 20230321 | 833 | 20230325 | 1526 | 2065817 | 6173 | Distribution Circuit | Vegetation | Tree - bark fell into line | 33 | 203709 | 37.1293 | -122.1204 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051782 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829869 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 1653 | 20230321 | 833 | 20230327 | 1737 | 2065864 | 9184 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 119392 | 37.1578 | -122.1392 | Yes | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051806 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829879 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9719 | 20230321 | 833 | 20230327 | 2018 | 2066067 | 9345 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 149520 | 37.1471 | -122.1341 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051886 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829913 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | JUMPER | JMPRS LD SDIE OF CGC 315275523524 | 20230321 | 833 | 20230326 | 1912 | 2066099 | 7839 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 23517 | 37.1353 | -122.1194 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051893 | OH | Sus | 35431731 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829918 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9777 | 20230321 | 833 | 20230325 | 1526 | 2066212 | 6163 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 80119 | 37.1428 | -122.0886 | Yes | Clear;32-90 F | Crossarm- Wood | Broken | 23-0051937 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1829938 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 8467 | 20230321 | 833 | 20230325 | 1526 | 2066228 | 6173 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 376553 | 37.1418 | -122.0907 | Yes | Overcast-Heavy Rain;32-90 F | Crossarm- Wood | Broken | 23-0051945 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1829941 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 2887 | 20230321 | 833 | 20230327 | 1057 | 2066420 | 8784 | Distribution Circuit | Vegetation | Tree - bark fell into line | 2 | 17568 | 37.1394 | -122.0948 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052002 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829971 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 8459 | 20230321 | 833 | 20230327 | 1220 | 2066485 | 8867 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 17734 | 37.1328 | -122.1035 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052015 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829983 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5477 | 20230321 | 833 | 20230326 | 1158 | 2066507 | 7405 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 370250 | 37.1292 | -122.1143 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052022 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829988 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5485 | 20230321 | 833 | 20230327 | 1802 | 2066568 | 9209 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 313106 | 37.1322 | -122.109 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0052038 | OH | Sus | 35431731 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1829999 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5511 | 20230321 | 833 | 20230326 | 1630 | 2066745 | 7677 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 330111 | 37.1499 | -122.1363 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken | 23-0052425 | OH | Sus | 35431731 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1830391 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 8455 | 20230321 | 833 | 20230326 | 1559 | 2066873 | 7646 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 206442 | 37.1316 | -122.1098 | Yes | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0052465 | OH | Sus | 35431731 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1830425 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 307348 | 20230321 | 833 | 20230325 | 1920 | 2055208 | 6407 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 172989 | 37.2109 | -122.1505 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049503 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | Yes | No | 1828261 | 0 | EPSS Ckt | N | 2023 | ABC G
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | JUMPER | OJ 3 POLES SW/OF 3483 FUCO | 20230321 | 833 | 20230326 | 1730 | 2067047 | 7737 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 54159 | 37.2417 | -122.1541 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052496 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1830455 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 1907 | 20230321 | 847 | 20230321 | 1138 | 2053699 | 171 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 2052 | 37.0973 | -121.9748 | Yes | Clear;32-90 F |  |  | 23-0049355 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828147 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 5090 | 20230321 | 851 | 20230321 | 1005 | 2053724 | 74 | Distribution Circuit | Vegetation | Tree - branch fell on line | 325 | 24050 | 36.9804 | -121.892 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 23-0049158 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828066 | 0 | EPSS Ckt | N | 2023 | A & C PHASE
CENTRAL COAST | SALINAS | SPENCE-1103 | 182201103 | TRANSFORMER | 412511748418 | 20230321 | 856 | 20230321 | 1248 | 2053730 | 232 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 232 | 36.6359 | -121.5534 | Yes | Overcast-Drizzle;32-90 F | Transformer (OH) | Broken | 23-0049149 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828060 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | RECLOSER | 2002 | 20230321 | 908 | 20230321 | 1421 | 2053762 | 313 | Distribution Circuit | Equipment Failure/Involved | Overhead | 120 | 37560 | 36.2248 | -121.7587 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Together | 23-0049166 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828073 | 0 | EPSS Ckt | N | 2023 | A-B
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 1909 | 20230321 | 920 | 20230321 | 1211 | 2053806 | 171 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 855 | 37.0978 | -121.9771 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0049399 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828177 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 33542 | 20230321 | 934 | 20230325 | 1914 | 2065976 | 6340 | Distribution Circuit | Vegetation | Tree - fell into line | 390 | 2449102 | 37.0906 | -122.0456 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051847 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829896 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | KING CITY | JOLON 1103 | 182981103 | FUSE | 7227 | 20230321 | 941 | 20230322 | 1345 | 2053847 | 1684 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 6736 | 35.9778 | -121.2147 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Together | 23-0049345 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828140 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | RECLOSER | 5178 | 20230321 | 945 | 20230323 | 1905 | 2053858 | 3440 | Distribution Circuit | Vegetation | Tree - fell into line | 267 | 116200 | 37.0324 | -121.9467 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049200 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828084 | 0 | EPSS Ckt | N | 2023 | A-C-GRD
CENTRAL COAST | MONTEREY | LAURELES-1112 | 182371112 | TRANSFORMER | 411960442816 | 20230321 | 956 | 20230321 | 1008 | 2053888 | 12 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 108 | 36.4782 | -121.7357 | Yes | Clear;32-90 F | Secondary | Broken | 23-0049210 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1828087 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | RECLOSER | 16006 | 20230321 | 1016 | 20230321 | 1843 | 2053930 | 507 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1566 | 275048 | 36.9829 | -122.0492 | Yes | Overcast-Fog-Rain;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0049236 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1828096 | 0 | EPSS Ckt | N | 2023 | A-C
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | SWITCH | 156208 | 20230321 | 1029 | 20230323 | 1842 | 2054030 | 3373 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6399 | 5983588 | 36.9845 | -122.0268 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049299 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828115 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1102 | 182031102 | SWITCH | 8717 | 20230321 | 1035 | 20230321 | 1618 | 2053952 | 343 | Distribution Circuit | Equipment Failure/Involved | Overhead | 89 | 30527 | 36.2204 | -121.1197 | Yes | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken | 23-0049247 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1828101 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 6689 | 20230321 | 1044 | 20230321 | 1234 | 2053997 | 110 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 403 | 36.8881 | -121.8071 | Yes | Overcast-Fog-Rain;32-90 F |  |  | 23-0049363 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828152 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | RECLOSER | 11056 | 20230321 | 1117 | 20230321 | 1245 | 2054715 | 88 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 106 | 9328 | 36.9937 | -122.0299 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0049457 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828223 | 0 | EPSS Ckt | N | 2023 | B & GRD
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 764889 | 20230321 | 1117 | 20230321 | 2121 | 2060156 | 604 | Distribution Circuit | Vegetation | Tree - branch fell on line | 343 | 207172 | 37.0019 | -122.0376 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0050043 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828726 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | OCB | 2201/2 | 20230321 | 1139 | 20230321 | 1148 | 2054153 | 9 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1372 | 12348 | 36.5786 | -121.9085 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0049352 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828145 | 0 | EPSS Ckt | N | 2023 | AC
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | FUSE | 5173 | 20230321 | 1158 | 20230327 | 1226 | 2063675 | 8668 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 466170 | 37.1011 | -122.1017 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0050991 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829378 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | FUSE | 5175 | 20230321 | 1158 | 20230326 | 1810 | 2065277 | 7572 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 219588 | 37.1057 | -122.1057 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051591 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829754 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | RECLOSER | 96738 | 20230321 | 1158 | 20230326 | 1942 | 2065867 | 7664 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 176272 | 37.1111 | -122.1142 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049467 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829883 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | FUSE | 5439 | 20230321 | 1158 | 20230326 | 1942 | 2065869 | 7664 | Distribution Circuit | Vegetation | Tree - branch fell on line | 200 | 1532800 | 37.1126 | -122.1143 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049467 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829884 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | FUSE | 6215 | 20230321 | 1158 | 20230327 | 1555 | 2066826 | 8877 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 275187 | 37.1127 | -122.1158 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052452 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1830410 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | TRANSFORMER | 315288123004 | 20230321 | 1158 | 20230327 | 1200 | 2067829 | 8642 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 17284 | 37.1202 | -122.1171 | Yes | Strong Winds-Rain-Overcast;32-90 F | Transformer | Deteriorated | 23-0052695 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1830631 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | JUMPER | OJ 1 S/OF & 1 SE/OF CGC#315316222418 | 20230321 | 1158 | 20230327 | 1452 | 2067875 | 8814 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 44070 | 37.1039 | -122.1071 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052706 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1830639 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | SWITCH | 89251 | 20230321 | 1158 | 20230327 | 1421 | 2067905 | 8783 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 131745 | 37.1183 | -122.1137 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0052709 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1830644 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | TRANSFORMER | 411975442569 | 20230321 | 1220 | 20230321 | 1853 | 2054322 | 393 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 1179 | 36.4721 | -121.7304 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0049711 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828433 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0422 | 182440422 | FUSE | 2581 | 20230321 | 1223 | 20230321 | 1656 | 2054337 | 273 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 8727 | 36.5918 | -121.9454 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Together | 23-0049473 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828239 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | 83500401 | 83500401 | RECLOSER | 929132 | 20230321 | 1225 | 20230324 | 1144 | 2054394 | 4279 | Distribution Circuit | Vegetation | Tree - fell into line | 127 | 543433 | 36.9919 | -121.927 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049422 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1828196 | 0 | EPSS Ckt | N | 2023 | B & C PHASE
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 6741 | 20230321 | 1226 | 20230322 | 1355 | 2054353 | 1529 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 10703 | 36.5716 | -121.8844 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0049565 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828317 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | FUSE | 867 | 20230321 | 1231 | 20230322 | 1131 | 2054395 | 1380 | Distribution Circuit | Vegetation | Tree - fell into line | 274 | 378120 | 36.9811 | -121.9663 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049619 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828359 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | RECLOSER | BL 1101 | 20230321 | 1237 | 20230325 | 1755 | 2054447 | 6078 | Distribution Circuit | Vegetation | Tree - fell into line | 293 | 1780854 | 37.0926 | -122.0966 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049432 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1828204 | 0 | EPSS Ckt | N | 2023 | A & B PHASE
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | FUSE | 5179 | 20230321 | 1237 | 20230327 | 1610 | 2067024 | 8853 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 256789 | 37.1076 | -122.1077 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0052491 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1830451 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | OTHER | HOT WIRE DOWN 1 S/LS CGC# 315292922407 | 20230321 | 1237 | 20230326 | 1800 | 2067042 | 7523 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 246879 | 37.105 | -122.1133 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052495 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | Yes | 1830454 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | JUMPER | OJ @ CGC# 315330022815 | 20230321 | 1237 | 20230327 | 2030 | 2067814 | 9113 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 118469 | 37.115 | -122.1028 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0052691 | OH | Sus | 35431731 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1830628 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | FUSE | 5743 | 20230321 | 1237 | 20230327 | 1315 | 2067879 | 8678 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 52068 | 37.1049 | -122.116 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken | 23-0052495 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1830640 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 7229 | 20230321 | 1238 | 20230322 | 2140 | 2061818 | 1982 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 11892 | 37.0691 | -122.0839 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050354 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1828996 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 8193 | 20230321 | 1238 | 20230321 | 1816 | 2054440 | 338 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 40 | 13520 | 36.9817 | -121.8969 | Yes | Overcast-Rain;32-90 F |  |  | 23-0050012 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828695 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 5133 | 20230321 | 1239 | 20230325 | 1801 | 2056182 | 6082 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 42574 | 37.0921 | -122.0917 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0049594 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828339 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | SWITCH | 10969 | 20230321 | 1239 | 20230326 | 745 | 2065571 | 6906 | Distribution Circuit | Vegetation | Tree - branch fell on line | 100 | 690600 | 37.1064 | -122.0572 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051684 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829829 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | RECLOSER | 944178 | 20230321 | 1239 | 20230325 | 1801 | 2065863 | 6082 | Distribution Circuit | Vegetation | Tree - fell into line | 289 | 1757698 | 37.0926 | -122.0964 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049467 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829881 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | RECLOSER | 16010 | 20230321 | 1239 | 20230325 | 1927 | 2065912 | 6168 | Distribution Circuit | Vegetation | Tree - fell into line | 116 | 715488 | 37.0886 | -122.0874 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049467 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829890 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 9423 | 20230321 | 1239 | 20230326 | 1725 | 2066979 | 7486 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 209608 | 37.077 | -122.0862 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052481 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1830441 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 5159 | 20230321 | 1239 | 20230325 | 1903 | 2066986 | 6144 | Distribution Circuit | Vegetation | Tree - branch fell on line | 74 | 454656 | 37.0814 | -122.0846 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0052484 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1830444 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 5167 | 20230321 | 1239 | 20230326 | 1250 | 2067041 | 7211 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 21633 | 37.0926 | -122.096 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0052494 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1830453 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 5151 | 20230321 | 1239 | 20230327 | 1300 | 2067628 | 8661 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 43305 | 37.111 | -122.0899 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052657 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1830598 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 5149 | 20230321 | 1239 | 20230327 | 1300 | 2067631 | 8661 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 43305 | 37.1109 | -122.0899 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052658 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1830599 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 5143 | 20230321 | 1239 | 20230326 | 1748 | 2067720 | 7509 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 202743 | 37.0994 | -122.0868 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052673 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1830615 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 75847 | 20230321 | 1239 | 20230326 | 1029 | 2062686 | 7070 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 21210 | 37.0965 | -122.1265 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050653 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829157 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 1859 | 20230321 | 1239 | 20230325 | 1415 | 2063898 | 5856 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 17568 | 37.0939 | -122.1443 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051041 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829423 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 91034 | 20230321 | 1239 | 20230325 | 1255 | 2065809 | 5776 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 38 | 219488 | 37.0944 | -122.1411 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0049467 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1829866 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 90678 | 20230321 | 1239 | 20230325 | 1933 | 2065812 | 6174 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 407484 | 37.0954 | -122.1281 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049467 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829868 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 7799 | 20230321 | 1239 | 20230325 | 1415 | 2066448 | 5856 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 322080 | 37.091 | -122.1396 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052008 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1829977 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 8315 | 20230321 | 1239 | 20230326 | 1732 | 2067178 | 7493 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 157353 | 37.0995 | -122.1181 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0052526 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1830477 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 11044 | 20230321 | 1239 | 20230322 | 2003 | 2054467 | 1884 | Distribution Circuit | Vegetation | Tree - fell into line | 2027 | 458551 | 37.0401 | -122.0297 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049444 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1828212 | 0 | EPSS Ckt | N | 2023 | BC
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 287578 | 20230321 | 1239 | 20230322 | 1547 | 2056043 | 1628 | Distribution Circuit | Vegetation | Tree - fell into line | 170 | 94096 | 37.0438 | -122.0755 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049578 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1828325 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 7315 | 20230321 | 1239 | 20230323 | 1356 | 2060484 | 2957 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 84329 | 37.0406 | -122.0817 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050112 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1828780 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 8511 | 20230321 | 1239 | 20230325 | 1742 | 2058809 | 6063 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 84882 | 37.0617 | -122.1474 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0049894 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1828587 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 5535 | 20230321 | 1239 | 20230326 | 1558 | 2064627 | 7399 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 51793 | 37.0662 | -122.2286 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051374 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829633 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 563 | 20230321 | 1239 | 20230326 | 1517 | 2066018 | 7358 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 80938 | 37.0587 | -122.1418 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051865 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1829902 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 815 | 20230321 | 1239 | 20230325 | 1534 | 2066805 | 5935 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 5935 | 37.0475 | -122.1565 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052445 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1830405 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | SWITCH | 8527 | 20230321 | 1239 | 20230325 | 1254 | 2066842 | 5775 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 36 | 207900 | 37.0529 | -122.154 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0049450 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1830417 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 39126 | 20230321 | 1240 | 20230323 | 1729 | 2054484 | 3130 | Distribution Circuit | Vegetation | Tree - branch fell on line | 378 | 843161 | 37.0778 | -122.1322 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken | 23-0049433 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828205 | 0 | EPSS Ckt | N | 2023 | A&GRD
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | JUMPER | HIGH SIDE JMPS @ 1217 | 20230321 | 1240 | 20230326 | 1629 | 2063033 | 7429 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 7429 | 37.0402 | -122.1065 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0050780 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829236 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 10443 | 20230321 | 1240 | 20230325 | 1914 | 2066208 | 6154 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 61540 | 37.1056 | -122.0431 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051935 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829937 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 12758 | 20230321 | 1241 | 20230325 | 1812 | 2054539 | 6091 | Distribution Circuit | Vegetation | Tree - fell into line | 160 | 974560 | 37.1486 | -122.1745 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0049448 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1828215 | 0 | EPSS Ckt | N | 2023 | ABC
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | SWITCH | 95719 | 20230321 | 1241 | 20230326 | 953 | 2063415 | 7032 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 232056 | 37.1381 | -122.1426 | Yes | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken | 23-0050885 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1829324 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 5459 | 20230321 | 1241 | 20230325 | 1812 | 2065021 | 6091 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 176639 | 37.1385 | -122.1432 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051520 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829715 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 5457 | 20230321 | 1241 | 20230326 | 956 | 2065359 | 7035 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 126630 | 37.1376 | -122.1414 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0051611 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1829768 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 3017 | 20230321 | 1241 | 20230325 | 1812 | 2066022 | 6091 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6091 | 37.1423 | -122.1536 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051867 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829903 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 10025 | 20230321 | 1241 | 20230326 | 1352 | 2066028 | 7271 | Distribution Circuit | Vegetation | Tree - branch fell on line | 38 | 276298 | 37.1398 | -122.1525 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051872 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829905 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 9333 | 20230321 | 1244 | 20230322 | 1745 | 2057000 | 1741 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 36561 | 36.9423 | -121.8574 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049726 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828447 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 869103 | 20230321 | 1245 | 20230321 | 1342 | 2054531 | 57 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 10 | 570 | 36.8211 | -121.7285 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0049555 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828310 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | FUSE | 12265 | 20230321 | 1245 | 20230321 | 1445 | 2054519 | 120 | Distribution Circuit | Equipment Failure/Involved | Overhead | 72 | 8640 | 36.9588 | -121.9805 | Yes | Overcast-Rain-Strong Winds;32-90 F | Anchor or Guy | Broken | 23-0049546 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828304 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 6559 | 20230321 | 1246 | 20230321 | 1506 | 2054558 | 140 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 4340 | 36.9267 | -121.7459 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0049674 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828403 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5233 | 20230321 | 1247 | 20230325 | 1112 | 2054676 | 5665 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 130295 | 37.0577 | -122.0763 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050523 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1829093 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 7605 | 20230321 | 1247 | 20230322 | 1145 | 2054671 | 1378 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 110 | 151580 | 37.0866 | -122.0058 | Yes | Clear;32-90 F |  |  | 23-0050574 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1829113 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 8183 | 20230321 | 1247 | 20230322 | 42 | 2061369 | 715 | Distribution Circuit | Vegetation | Tree - branch fell on line | 115 | 82225 | 36.9646 | -121.8903 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0050269 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828930 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 1447 | 20230321 | 1247 | 20230322 | 1429 | 2054576 | 1542 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 13878 | 36.565 | -121.9568 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049534 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828294 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 67520 | 20230321 | 1248 | 20230326 | 1801 | 2054599 | 7513 | Distribution Circuit | Equipment Failure/Involved | Overhead | 167 | 208542 | 36.9577 | -121.8525 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049660 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828390 | 0 | EPSS Ckt | N | 2023 | B GRD
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | SWITCH | 11223 | 20230321 | 1248 | 20230321 | 2107 | 2059703 | 499 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1304 | 650696 | 36.9485 | -121.8633 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0049660 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1828669 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6543 | 20230321 | 1248 | 20230323 | 1712 | 2060024 | 3144 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 81744 | 36.9267 | -121.8459 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050030 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828713 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 12582 | 20230321 | 1248 | 20230321 | 1927 | 2060356 | 399 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1220 | 486780 | 36.9513 | -121.8642 | Yes | Clear;32-90 F |  |  | 23-0049660 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1828764 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | RECLOSER | 11056 | 20230321 | 1249 | 20230325 | 1306 | 2055586 | 5713 | Distribution Circuit | Vegetation | Tree - fell into line | 449 | 106126 | 36.9937 | -122.0299 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050044 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828727 | 0 | EPSS Ckt | N | 2023 | AB GRD
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 42086 | 20230321 | 1249 | 20230322 | 1925 | 2055469 | 1836 | Distribution Circuit | Vegetation | Tree - fell into line | 178 | 160280 | 36.9036 | -121.7361 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049530 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828290 | 0 | EPSS Ckt | N | 2023 | B & GRD
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 8515 | 20230321 | 1249 | 20230325 | 1155 | s1830411 | 5706 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 107 | 610542 | 37.0483 | -122.1607 | Yes | Clear;32-90 F |  |  | 23-0049450 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1830411 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 5413 | 20230321 | 1249 | 20230325 | 1140 | 2066834 | 5691 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 199185 | 37.0443 | -122.1497 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0049450 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1830415 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 36514 | 20230321 | 1249 | 20230325 | 1523 | 2066839 | 5914 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 77 | 455378 | 37.0395 | -122.1518 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0049450 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1830416 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 737 | 20230321 | 1249 | 20230321 | 1602 | 2054669 | 193 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 59 | 11387 | 37.0046 | -121.8551 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0049790 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828497 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 11521 | 20230321 | 1249 | 20230324 | 1847 | 2060990 | 4678 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 27630 | 36.8869 | -121.7238 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050177 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828839 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 3899 | 20230321 | 1250 | 20230322 | 1547 | 2060898 | 1617 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 17787 | 36.948 | -121.8501 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050170 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828832 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 12820 | 20230321 | 1251 | 20230321 | 2219 | 2055240 | 568 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1115 | 633320 | 36.897 | -121.6784 | Yes | Overcast-Heavy Rain;32-90 F |  |  | 23-0049520 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828279 | 0 | EPSS Ckt | N | 2023 | B & GRD
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 23319 | 20230321 | 1252 | 20230321 | 1409 | 2054667 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 462 | 36.8126 | -121.7248 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F |  |  | 23-0049609 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828350 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | RECLOSER | 10932 | 20230321 | 1252 | 20230321 | 1643 | 2055115 | 231 | Distribution Circuit | Vegetation | Tree - fell into line | 1215 | 278855 | 36.938 | -121.7772 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049495 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1828257 | 0 | EPSS Ckt | N | 2023 | A B C PH
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | JUMPER | OJS 1 SPAN SSD OF 316209116033 | 20230321 | 1252 | 20230323 | 1810 | 2057492 | 3198 | Distribution Circuit | Vegetation | Tree - fell into line | 172 | 113096 | 36.9331 | -121.7988 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049796 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828502 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 1641 | 20230321 | 1252 | 20230323 | 1210 | 2058197 | 2838 | Distribution Circuit | Equipment Failure/Involved | Overhead | 52 | 85836 | 36.9326 | -121.8121 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0049847 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828548 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 5304 | 20230321 | 1252 | 20230323 | 1235 | 2054696 | 2863 | Distribution Circuit | Vegetation | Tree - fell into line | 107 | 254807 | 36.9731 | -121.8204 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049453 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828220 | 0 | EPSS Ckt | N | 2023 | B-GRD
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 12992 | 20230321 | 1253 | 20230326 | 723 | 2055316 | 6870 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 212970 | 37.1991 | -122.1532 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049511 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828271 | 0 | EPSS Ckt | N | 2023 | C GRD
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 10325 | 20230321 | 1253 | 20230325 | 1740 | 2062861 | 6047 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 18141 | 37.1583 | -122.1705 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050722 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829197 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 8915 | 20230321 | 1253 | 20230325 | 1740 | 2062870 | 6047 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 72564 | 37.1665 | -122.1671 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050725 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829201 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | SWITCH | 46429 | 20230321 | 1253 | 20230325 | 1828 | 2062873 | 6095 | Distribution Circuit | Vegetation | Tree - fell into line | 107 | 652165 | 37.167 | -122.1668 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049510 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829203 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9761 | 20230321 | 1253 | 20230326 | 1820 | 2063397 | 7527 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 22581 | 37.1729 | -122.1638 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050915 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829318 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRIP-SAVER | 2253 | 20230321 | 1253 | 20230325 | 1829 | 2063642 | 6096 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 73152 | 37.1709 | -122.1652 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0050976 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1829367 | 0 | EPSS Ckt | N | 2023 | A&C
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | SWITCH | 2293 | 20230321 | 1253 | 20230325 | 1740 | 2063744 | 6047 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 44593 | 37.1314 | -122.172 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049510 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829389 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 12383 | 20230321 | 1253 | 20230326 | 1728 | 2064401 | 7475 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 14950 | 37.1656 | -122.189 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051286 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1829588 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRIP-SAVER | 9741 | 20230321 | 1253 | 20230326 | 1332 | 2064736 | 7239 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 304038 | 37.157 | -122.1288 | Yes | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051409 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829656 | 0 | EPSS Ckt | N | 2023 | NA
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | SWITCH | 4111 | 20230321 | 1253 | 20230325 | 1658 | 2064740 | 6005 | Distribution Circuit | Vegetation | Tree - fell into line | 193 | 1158965 | 37.1754 | -122.1386 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051410 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829657 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | SWITCH | 11029 | 20230321 | 1253 | 20230326 | 807 | 2064807 | 6914 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 283474 | 37.1929 | -122.1456 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0051422 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1829665 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | JUMPER | JMPRS @ CGC 315179524405 | 20230321 | 1253 | 20230326 | 1125 | 2065103 | 7112 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 7112 | 37.1586 | -122.1555 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051539 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829725 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 4259 | 20230321 | 1253 | 20230325 | 1828 | 2065367 | 6095 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 30475 | 37.167 | -122.1872 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051616 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829772 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9133 | 20230321 | 1253 | 20230325 | 1830 | 2065683 | 6097 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 85358 | 37.1779 | -122.12 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051725 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829845 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9785 | 20230321 | 1253 | 20230325 | 1701 | 2065749 | 6008 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 96128 | 37.1571 | -122.1345 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051754 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829858 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 891361 | 20230321 | 1253 | 20230326 | 1215 | 2065832 | 7162 | Distribution Circuit | Vegetation | Tree - bark fell into line | 18 | 128916 | 37.1891 | -122.1431 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051791 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829874 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 7773 | 20230321 | 1253 | 20230326 | 1212 | 2065837 | 7159 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 250565 | 37.1881 | -122.1581 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051794 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829875 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9783 | 20230321 | 1253 | 20230325 | 1658 | 2065843 | 6005 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 198165 | 37.1573 | -122.1336 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051799 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829877 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 1071 | 20230321 | 1253 | 20230325 | 1657 | 2065979 | 6004 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 126084 | 37.1665 | -122.1353 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051849 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829897 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 1607 | 20230321 | 1253 | 20230326 | 1428 | 2065983 | 7295 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 94835 | 37.1931 | -122.156 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051850 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829898 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 6209 | 20230321 | 1253 | 20230326 | 1102 | 2066001 | 7089 | Distribution Circuit | Vegetation | Tree - bark fell into line | 3 | 21267 | 37.1793 | -122.1392 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051855 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829899 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRIP-SAVER | 6219 | 20230321 | 1253 | 20230326 | 1533 | 2066262 | 7360 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 161920 | 37.1841 | -122.1409 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Together | 23-0051961 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1829945 | 0 | EPSS Ckt | N | 2023 | NA
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 2945 | 20230321 | 1253 | 20230326 | 1232 | 2066285 | 7179 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 358950 | 37.1733 | -122.1442 | Yes | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051982 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829959 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 7017 | 20230321 | 1253 | 20230327 | 1137 | 2066455 | 8564 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 299740 | 37.1756 | -122.1388 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052012 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829980 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9793 | 20230321 | 1253 | 20230326 | 1337 | 2066472 | 7244 | Distribution Circuit | Vegetation | Tree - branch fell on line | 64 | 463616 | 37.196 | -122.1452 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052013 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829981 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 2923 | 20230321 | 1253 | 20230326 | 2029 | 2066521 | 7656 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 344520 | 37.1737 | -122.1456 | Yes | Overcast-Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0052024 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829989 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRANSFORMER | 315209724903 | 20230321 | 1253 | 20230326 | 1313 | 2066565 | 7220 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 64980 | 37.1728 | -122.1451 | Yes | Clear;32-90 F | Secondary | Broken | 23-0052037 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1829998 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 11054 | 20230321 | 1253 | 20230326 | 1400 | 2055230 | 5340 | Distribution Circuit | Vegetation | Tree - fell into line | 181 | 256478 | 36.9775 | -121.7415 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049553 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828309 | 0 | EPSS Ckt | N | 2023 | A & GRD
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | RECLOSER | 179744 | 20230321 | 1253 | 20230322 | 853 | 2060164 | 1200 | Distribution Circuit | Vegetation | Tree - branch fell on line | 152 | 182400 | 36.988 | -122.1583 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0050382 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1829009 | 0 | EPSS Ckt | N | 2023 | BC
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 5561 | 20230321 | 1253 | 20230323 | 1737 | 2055276 | 3164 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 30313 | 37.0111 | -122.1224 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050617 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1829133 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 5575 | 20230321 | 1254 | 20230325 | 1740 | 2062865 | 6046 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6046 | 37.1629 | -122.1685 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050724 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829199 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 8557 | 20230321 | 1254 | 20230322 | 1420 | 2054629 | 1526 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 9156 | 36.5665 | -121.8863 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0049447 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1828214 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | RECLOSER | 698634 | 20230321 | 1255 | 20230326 | 1815 | 2065919 | 7520 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 635445 | 37.0954 | -122.0857 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049467 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829892 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 12124 | 20230321 | 1255 | 20230326 | 1125 | 2054765 | 7110 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 349 | 2481390 | 37.1677 | -122.1662 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0049458 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | No | No | 1828224 | 0 | EPSS Ckt | N | 2023 | BC&GRD
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 12779 | 20230321 | 1255 | 20230326 | 1125 | 2062262 | 7110 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 106650 | 37.1599 | -122.1555 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050492 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829078 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 8021 | 20230321 | 1255 | 20230326 | 1125 | 2062789 | 7110 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 170640 | 37.1635 | -122.1621 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0050700 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1829181 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 670217 | 20230321 | 1255 | 20230326 | 1125 | 2064953 | 7110 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 398160 | 37.1578 | -122.166 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051495 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829698 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 12599 | 20230321 | 1255 | 20230326 | 1125 | 2064959 | 7110 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 92430 | 37.1532 | -122.164 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051497 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829701 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9753 | 20230321 | 1255 | 20230327 | 1420 | 2067637 | 8725 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 183225 | 37.1656 | -122.1639 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0052659 | OH | Sus | 35431731 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1830601 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5235 | 20230321 | 1255 | 20230322 | 1307 | 2054779 | 1452 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 60 | 87120 | 37.0596 | -122.0793 | Yes | Overcast-Rain;32-90 F |  |  | 23-0050706 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829186 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 627 | 20230321 | 1255 | 20230321 | 1936 | 2054707 | 401 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 8822 | 36.5489 | -121.8966 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049710 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1828432 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 3729 | 20230321 | 1256 | 20230326 | 1347 | 2066056 | 7251 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 21753 | 37.199 | -122.1535 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051884 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829911 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 4857 | 20230321 | 1259 | 20230325 | 1801 | 2065397 | 6062 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 66682 | 37.0909 | -122.0948 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051620 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829775 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9789 | 20230321 | 1259 | 20230326 | 1616 | 2066169 | 7397 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 29588 | 37.1835 | -122.141 | Yes | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051917 | OH | Sus | 35431731 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829927 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 2425 | 20230321 | 1259 | 20230327 | 1500 | 2064314 | 8761 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 34907 | 37.0921 | -122.1157 | Yes | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051238 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829565 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | SWITCH | 36516 | 20230321 | 1259 | 20230325 | 1616 | 2065819 | 5957 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 101269 | 37.0787 | -122.1336 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0049467 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1829870 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 9791 | 20230321 | 1259 | 20230328 | 923 | 2066089 | 9864 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 480120 | 37.1851 | -122.1414 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051889 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829916 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 10717 | 20230321 | 1259 | 20230325 | 1824 | 2066783 | 6085 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 158210 | 37.0913 | -122.1045 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052439 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1830398 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 3533 | 20230321 | 1259 | 20230322 | 1540 | 2054802 | 1601 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 37 | 59237 | 37.0016 | -122.0274 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0050830 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1829265 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | RECLOSER | 5144 | 20230321 | 1300 | 20230326 | 745 | 2065923 | 6885 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 48 | 330480 | 37.0911 | -122.0774 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0049467 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1829893 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 3307 | 20230321 | 1300 | 20230324 | 1233 | 2063166 | 4293 | Distribution Circuit | Vegetation | Tree - fell into line | 121 | 214933 | 37.066 | -122.0797 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050846 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829271 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ERTA SUB | 8351 | OCB | 403/2 | 20230321 | 1300 | 20230321 | 2310 | 2054819 | 610 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 478 | 291580 | 36.9307 | -121.7642 | Yes | Overcast-Rain;32-90 F |  |  | 23-0050252 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828911 | 0 | Non-EPSS | N | 2023 | A-GRD
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 10726 | 20230321 | 1300 | 20230325 | 1659 | 2065822 | 5999 | Distribution Circuit | Vegetation | Tree - fell into line | 209 | 1253791 | 37.061 | -122.1493 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049467 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829871 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 2009 | 20230321 | 1301 | 20230323 | 1906 | 2054841 | 3245 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 22130 | 36.9903 | -121.753 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049906 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828597 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 974520 | 20230321 | 1301 | 20230322 | 1038 | 2060238 | 1297 | Distribution Circuit | Vegetation | Tree - branch fell on line | 156 | 202332 | 36.9908 | -121.8063 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050064 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828742 | 0 | EPSS Ckt | N | 2023 | A GRD T
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6641 | 20230321 | 1301 | 20230323 | 1929 | 2062204 | 3268 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 251636 | 37.016 | -121.8161 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050466 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829065 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | SWITCH | 794081 | 20230321 | 1301 | 20230324 | 1138 | 2062285 | 4237 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 410989 | 37.0344 | -121.8205 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050510 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829087 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 10728 | 20230321 | 1302 | 20230322 | 1123 | 2055762 | 1341 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 144828 | 37.0665 | -122.0797 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0049883 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1828576 | 0 | EPSS Ckt | N | 2023 | NA
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 7811 | 20230321 | 1302 | 20230324 | 1655 | 2066330 | 4553 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 22765 | 36.9798 | -121.8002 | Yes | Overcast-Rain;32-90 F | Pole-Wood | Broken | 23-0051990 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1829964 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 422016 | 20230321 | 1303 | 20230324 | 1619 | 2054903 | 4516 | Distribution Circuit | Vegetation | Tree - fell into line | 635 | 491225 | 36.964 | -121.8086 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0049681 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828408 | 0 | EPSS Ckt | N | 2023 | BC GRD
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | SWITCH | 8729 | 20230321 | 1305 | 20230325 | 1904 | 2063594 | 6119 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 526234 | 37.0882 | -122.0884 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0049864 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829360 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | OTHER | WIRE DOWN HOT @ CGC# 315384221664 | 20230321 | 1305 | 20230322 | 1742 | 2054948 | 1717 | Distribution Circuit | Vegetation | Tree - fell into line | 203 | 315008 | 37.0843 | -122.0827 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0049864 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | Yes | Yes | 1828562 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 95050 | 20230321 | 1305 | 20230322 | 1830 | 2059347 | 1765 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 37 | 65305 | 37.0888 | -122.0877 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0049864 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1828621 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 74170 | 20230321 | 1305 | 20230325 | 1714 | 2063586 | 6009 | Distribution Circuit | Vegetation | Tree - fell into line | 239 | 1436151 | 37.0883 | -122.0884 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0049864 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829357 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | JUMPER | OJ @ CGC#315368021535 | 20230321 | 1305 | 20230326 | 1435 | 2067155 | 7290 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 36450 | 37.0809 | -122.0883 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049864 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1830471 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRANSFORMER | 315369021676 | 20230321 | 1305 | 20230326 | 1535 | 2067223 | 7350 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 95550 | 37.0845 | -122.0885 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Transformer (OH) | Failed/Faulted | 23-0049864 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1830484 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 4817 | 20230321 | 1305 | 20230326 | 1156 | 2054966 | 7131 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 156882 | 36.9653 | -121.7418 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050960 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1829354 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | TRANSFORMER | 315625320802 | 20230321 | 1308 | 20230324 | 1238 | 2055020 | 4290 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 42900 | 37.0611 | -121.9987 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0050883 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829298 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | RECLOSER | 12840 | 20230321 | 1313 | 20230324 | 1510 | 2054694 | 4437 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 221839 | 37.0538 | -121.9545 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049483 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1828249 | 0 | EPSS Ckt | N | 2023 | A C
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6611 | 20230321 | 1313 | 20230323 | 1804 | 2055099 | 3171 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 9513 | 36.9707 | -121.7709 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken | 23-0050107 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828776 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 2161 | 20230321 | 1313 | 20230326 | 1412 | 2064982 | 7259 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 29036 | 36.9969 | -121.7382 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051507 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1829705 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | TRANSFORMER | 316215413209 | 20230321 | 1314 | 20230322 | 1837 | 2055116 | 1763 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1763 | 36.8554 | -121.7947 | Yes | Overcast-Heavy Rain;32-90 F | Connector or Splice (OH) | Arcing | 23-0051030 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829411 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 5967 | 20230321 | 1314 | 20230322 | 853 | 2055534 | 1179 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 9030 | 37.0034 | -121.9547 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 23-0050399 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829016 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 7637 | 20230321 | 1314 | 20230322 | 1045 | 2056165 | 1291 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 34857 | 37.0078 | -121.9385 | Yes | Clear;32-90 F |  |  | 23-0050509 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829086 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 2003 | 20230321 | 1314 | 20230324 | 152 | 2056496 | 3638 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 3638 | 36.9726 | -121.8715 | Yes | Overcast-Rain;32-90 F | Pole-Wood | Broken | 23-0050791 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1829244 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 236923 | 20230321 | 1316 | 20230326 | 1738 | 2064992 | 7462 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 129717 | 36.9929 | -121.7354 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051511 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829707 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6911 | 20230321 | 1316 | 20230326 | 1438 | 2065267 | 7282 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 454584 | 37.0171 | -121.7217 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051586 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1829751 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 6659 | 20230321 | 1316 | 20230326 | 2058 | 2055144 | 7662 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 140174 | 36.959 | -121.786 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0050852 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1829275 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | RECLOSER | 607772 | 20230321 | 1316 | 20230323 | 1849 | 2055194 | 3213 | Distribution Circuit | Vegetation | Tree - fell into line | 149 | 279772 | 37.0124 | -121.9527 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049505 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1828263 | 0 | EPSS Ckt | N | 2023 | A-B
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | RECLOSER | 5178 | 20230321 | 1316 | 20230323 | 1905 | 2059148 | 3229 | Distribution Circuit | Vegetation | Tree - fell into line | 176 | 568304 | 37.0324 | -121.9467 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0049923 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1828610 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | SWITCH | 259971 | 20230321 | 1316 | 20230323 | 1905 | 2059650 | 3229 | Distribution Circuit | Vegetation | Tree - branch fell on line | 72 | 232488 | 37.0449 | -121.9383 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049923 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1828657 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 1081 | 20230321 | 1316 | 20230322 | 1010 | 2055126 | 1254 | Distribution Circuit | Vegetation | Tree - fell into line | 220 | 35130 | 36.7872 | -121.6668 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049599 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1828343 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 9509 | 20230321 | 1317 | 20230322 | 1902 | 2055161 | 1785 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 8925 | 37.0346 | -122.0176 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0050984 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829374 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8699 OPEN/CREATE | 20230321 | 1317 | 20230325 | 1208 | 2064952 | 5691 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 102438 | 37.0568 | -121.9554 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0049074 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1829697 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5631 | 20230321 | 1318 | 20230323 | 1900 | 2055173 | 3222 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 144990 | 37.049 | -122.0627 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050619 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829135 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | TRANSFORMER | 316375013515 | 20230321 | 1318 | 20230324 | 1626 | 2058012 | 4508 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 9016 | 36.8646 | -121.7403 | Yes | Overcast-Drizzle;32-90 F |  |  | 23-0050888 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829302 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | RECLOSER | 885736 | 20230321 | 1318 | 20230321 | 2337 | 2055655 | 619 | Distribution Circuit | Vegetation | Tree - fell into line | 438 | 271122 | 36.9937 | -121.9776 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049767 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828477 | 0 | EPSS Ckt | N | 2023 | C-GRD
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | OTHER | WIRE DOWN @ 8853 TO THE SOUTH | 20230321 | 1318 | 20230323 | 1707 | 2061518 | 3000 | Distribution Circuit | Vegetation | Tree - fell into line | 267 | 328326 | 36.9626 | -121.852 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050308 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828970 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 6081 | 20230321 | 1319 | 20230324 | 1224 | 2055196 | 4265 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 27200 | 37.0577 | -122.0333 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049822 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828526 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 8215 | 20230321 | 1319 | 20230322 | 933 | 2055229 | 1214 | Distribution Circuit | Vegetation | Tree - bark fell into line | 59 | 71626 | 37.062 | -122.032 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0050426 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829037 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 6775 | 20230321 | 1319 | 20230322 | 1424 | 2055198 | 1505 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 111370 | 36.8813 | -121.6414 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050434 | OH | Sus | 45704997 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829043 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 69255 | 20230321 | 1321 | 20230324 | 1500 | 2055269 | 4419 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 22095 | 37.02 | -121.9924 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050271 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828932 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 937291 | 20230321 | 1324 | 20230323 | 840 | 2055334 | 2596 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 33748 | 37.1186 | -121.964 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0050979 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829369 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | SWITCH | UNNUM | 20230321 | 1325 | 20230323 | 1611 | 2055355 | 3046 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 21322 | 37.0014 | -122.0229 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0049916 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828604 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1102 | 182201102 | TRANSFORMER | 412489247735 | 20230321 | 1325 | 20230321 | 1648 | 2054340 | 203 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 203 | 36.6172 | -121.5602 | Yes | Overcast-Heavy Rain;32-90 F | Transformer | Broken | 23-0049519 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828278 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | 83500401 | 83500401 | OTHER | HOT WIRE DOWN SS B78929 | 20230321 | 1329 | 20230322 | 1122 | 2055462 | 1313 | Distribution Circuit | Vegetation | Tree - fell into line | 213 | 276861 | 36.9893 | -121.9169 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049937 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | Yes | Yes | 1828625 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | FUSE | 8175 | 20230321 | 1336 | 20230321 | 2303 | 2055552 | 567 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 383 | 217161 | 36.9758 | -121.9172 | Yes | Overcast-Rain;32-90 F |  |  | 23-0050246 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828906 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 5090 | 20230321 | 1338 | 20230323 | 1341 | 2055695 | 2883 | Distribution Circuit | Vegetation | Tree - fell into line | 279 | 233187 | 36.9804 | -121.892 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049589 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828336 | 0 | EPSS Ckt | N | 2023 | C PH GRD
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5239 | 20230321 | 1340 | 20230322 | 1443 | 2062254 | 1503 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 41 | 61623 | 37.0682 | -122.0827 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 23-0050488 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829075 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 12760 | 20230321 | 1340 | 20230326 | 1752 | 2055845 | 7452 | Distribution Circuit | Vegetation | Tree - fell into line | 214 | 523386 | 37.0674 | -121.9966 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0049583 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828330 | 0 | EPSS Ckt | N | 2023 | B-GRD
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5225 | 20230321 | 1341 | 20230324 | 1730 | 2056720 | 4549 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 40301 | 37.0496 | -122.0856 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050568 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829110 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 2615 | 20230321 | 1344 | 20230324 | 1726 | 2062794 | 4542 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 13626 | 37.0346 | -121.9969 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050702 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829182 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | JUMPER | OJ S SPAN S/W OF CGC 315684019860 | 20230321 | 1344 | 20230324 | 1558 | 2062809 | 4454 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 26724 | 37.0362 | -121.9802 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050708 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829189 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 5559 | 20230321 | 1354 | 20230324 | 1507 | 2056036 | 4393 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 96646 | 37.0125 | -122.1223 | Yes | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken | 23-0051028 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1829409 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 5020 | 20230321 | 1357 | 20230322 | 1810 | 2056185 | 1693 | Distribution Circuit | Vegetation | Tree - fell into line | 294 | 389288 | 37.1024 | -121.9847 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049605 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828348 | 0 | EPSS Ckt | N | 2023 | A GRD
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 737512 | 20230321 | 1358 | 20230322 | 1056 | 2056359 | 1258 | Distribution Circuit | Vegetation | Tree - fell into line | 900 | 1045470 | 37.0467 | -122.074 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0049613 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828354 | 0 | EPSS Ckt | N | 2023 | C-GRD
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 11849 | 20230321 | 1358 | 20230322 | 925 | 2062092 | 1167 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 10503 | 37.0392 | -122.0787 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0050420 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1829034 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | FUSE | 7495 | 20230321 | 1358 | 20230323 | 1522 | 2056307 | 2964 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 115212 | 36.9828 | -121.9278 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050363 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829001 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 931192 | 20230321 | 1418 | 20230323 | 1815 | 2054506 | 3117 | Distribution Circuit | Vegetation | Tree - fell into line | 1053 | 2971010 | 36.9754 | -121.8942 | Yes | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0049633 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1828370 | 0 | EPSS Ckt | N | 2023 | A-C
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 6477 | 20230321 | 1419 | 20230322 | 1141 | 2056408 | 1282 | Distribution Circuit | Vegetation | Tree - fell into line | 426 | 546132 | 36.8655 | -121.7346 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0050602 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829125 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 1051 | 20230321 | 1422 | 20230322 | 1547 | 2061475 | 1525 | Distribution Circuit | Vegetation | Tree - fell into line | 101 | 154025 | 36.9541 | -121.847 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050298 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828960 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 6753 | 20230321 | 1426 | 20230321 | 2125 | 2056682 | 419 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 15922 | 36.5659 | -121.8876 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049798 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828504 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 869103 | 20230321 | 1429 | 20230322 | 350 | 2056569 | 801 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 3170 | 36.8211 | -121.7285 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0049949 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828636 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | SWITCH | 7841 | 20230321 | 1438 | 20230321 | 1831 | 2056520 | 233 | Distribution Circuit | Equipment Failure/Involved | Overhead | 67 | 15161 | 36.5682 | -121.9548 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on object | 23-0049642 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828377 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 796388 | 20230321 | 1444 | 20230322 | 1534 | 2056641 | 1490 | Distribution Circuit | Vegetation | Tree - branch fell on line | 232 | 345680 | 36.9818 | -121.901 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken | 23-0050126 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | No | No | 1828793 | 0 | EPSS Ckt | N | 2023 | ABC G
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 125 | 20230321 | 1444 | 20230322 | 2239 | 2062798 | 1915 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 70855 | 37.0115 | -121.9009 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050704 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1829183 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1103 | 182031103 | FUSE | 8937 | 20230321 | 1448 | 20230322 | 1303 | 2055109 | 1335 | Distribution Circuit | Equipment Failure/Involved | Overhead | 48 | 8472 | 36.189 | -121.1477 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Deteriorated | 23-0049651 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1828389 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | RECLOSER | 22158 | 20230321 | 1501 | 20230322 | 34 | 2056811 | 573 | Distribution Circuit | Equipment Failure/Involved | Overhead | 912 | 110348 | 36.7999 | -121.6992 | Yes | Overcast-Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken | 23-0049715 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828438 | 0 | EPSS Ckt | N | 2023 | AC
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | RECLOSER | 55638 | 20230321 | 1503 | 20230322 | 1614 | 2054975 | 1511 | Distribution Circuit | Vegetation | Tree - fell into line | 205 | 309755 | 37.0139 | -122.0341 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0049706 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828428 | 0 | EPSS Ckt | N | 2023 | AB
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 68191 | 20230321 | 1504 | 20230323 | 1032 | 2060507 | 2608 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 49552 | 36.9816 | -121.9026 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050201 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | Yes | 1828861 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | FUSE | 10261 | 20230321 | 1531 | 20230324 | 1429 | 2057118 | 4258 | Distribution Circuit | Vegetation | Tree - fell into line | 1229 | 666242 | 36.9672 | -121.9853 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0050046 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1828739 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | TRANSFORMER | 411815245721 | 20230321 | 1543 | 20230321 | 1745 | 2057333 | 122 | Transformer only | Vegetation | Tree - branch fell on line | 8 | 976 | 36.5562 | -121.7883 | Yes | Strong Winds-Rain-Overcast;32-90 F | Service conductor | Broken- wire on ground | 23-0049777 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1828485 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 6409 | 20230321 | 1547 | 20230321 | 1937 | 2057274 | 230 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 24840 | 36.59 | -121.9115 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0049761 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1828473 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 11237 | 20230321 | 1550 | 20230322 | 1911 | 2057397 | 1641 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 6564 | 37.0904 | -121.9645 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0050989 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829377 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 11829 | 20230321 | 1550 | 20230324 | 1246 | 2057394 | 4136 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 20680 | 37.009 | -122.0756 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0050709 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829190 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | OTHER | BROKEN POLE @ 6153 | 20230321 | 1554 | 20230324 | 1243 | 2057461 | 4129 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 89741 | 36.9995 | -121.7739 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051022 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | Yes | Yes | 1829403 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | OTHER | FB 1 LD SIDE OF 1653 ON MAIN LINE | 20230321 | 1630 | 20230328 | 1146 | 2069128 | 9796 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 186520 | 37.1578 | -122.1394 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0053104 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1830876 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | JUMPER | JMPRS LD SIDE OF 1653 | 20230321 | 1639 | 20230328 | 1146 | 2069142 | 9787 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 9787 | 37.1577 | -122.1391 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0053104 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1830877 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRANSFORMER | 315396720520 | 20230321 | 1703 | 20230322 | 1735 | 2058947 | 1472 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 2944 | 37.0527 | -122.0784 | Yes | Clear;32-90 F |  |  | 23-0050949 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1829346 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 78252 | 20230321 | 1715 | 20230321 | 1721 | 2059222 | 6 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 946 | 5676 | 37.0495 | -122.0634 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0049935 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828623 | 0 | EPSS Ckt | N | 2023 | A GRD
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 5146 | 20230321 | 1724 | 20230324 | 1413 | 2059431 | 4129 | Distribution Circuit | Vegetation | Tree - fell into line | 1265 | 1395902 | 37.0578 | -122.0595 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049942 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | Yes | No | 1828630 | 0 | EPSS Ckt | N | 2023 | BC GRD
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | OTHER | WIRE DOWN @ MTR# 1008772753 | 20230321 | 1728 | 20230325 | 1149 | 2062522 | 5421 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 52141 | 37.0434 | -122.0775 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050608 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | Yes | Yes | 1829128 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | FUSE | 10511 | 20230321 | 1730 | 20230322 | 1155 | 2059845 | 1105 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1105 | 36.2968 | -121.8649 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050005 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828689 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 3721 | 20230321 | 1738 | 20230323 | 2017 | 2059571 | 3039 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 57741 | 37.0685 | -122.0584 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049959 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1828644 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRIP-SAVER | 9031 | 20230321 | 1748 | 20230323 | 1839 | 2062182 | 2931 | Distribution Circuit | Vegetation | Tree - branch fell on line | 48 | 99444 | 37.0726 | -122.0742 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Together | 23-0050453 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1829057 | 0 | EPSS Ckt | N | 2023 | ABC
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 9463 | 20230321 | 1803 | 20230323 | 1548 | 2059762 | 2745 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 164700 | 37.0697 | -122.0714 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050244 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828904 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 9071 | 20230321 | 1804 | 20230322 | 1425 | 2061234 | 1221 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 42692 | 37.0595 | -122.0588 | Yes | Clear;32-90 F |  |  | 23-0050758 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829224 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 20123 | 20230321 | 1816 | 20230321 | 1850 | 2059746 | 34 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 363 | 36.7912 | -121.651 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0050040 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828723 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2102 | 182222102 | FUSE | 8935 | 20230321 | 1822 | 20230321 | 2331 | 2059861 | 309 | Distribution Circuit | Equipment Failure/Involved | Underground | 168 | 34039 | 36.6091 | -121.852 | Yes | Clear;32-90 F | Elbow | Failed/Faulted | 23-0050099 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828770 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | FUSE | 8117 | 20230321 | 1836 | 20230321 | 2040 | 2059973 | 124 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 3348 | 36.4704 | -121.7334 | Yes | Clear;32-90 F |  |  | 23-0050131 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828798 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | OTHER | MIDDLE PHASE OPEN | 20230321 | 1840 | 20230323 | 2007 | 2059991 | 2967 | Distribution Circuit | Equipment Failure/Involved | Overhead | 93 | 227039 | 37.053 | -122.0625 | Yes | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0050029 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | Yes | No | 1828711 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | TRANSFORMER | 315503417488 | 20230321 | 1840 | 20230322 | 1952 | 2060003 | 1512 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 21168 | 36.9694 | -122.0393 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0051002 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829386 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 5269 | 20230321 | 1849 | 20230322 | 1240 | 2060250 | 1071 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 8916 | 36.9894 | -122.0312 | Yes | Overcast-Heavy Rain;32-90 F |  |  | 23-0050696 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829178 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 11663 | 20230321 | 1902 | 20230324 | 1650 | 2063455 | 4188 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 12564 | 36.9616 | -122.0894 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050931 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829332 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6647 | 20230321 | 1926 | 20230323 | 1858 | 2061560 | 2852 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 59892 | 37.0266 | -121.7801 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050313 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828975 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | RECLOSER | 10442 | 20230321 | 1948 | 20230321 | 2002 | 2060487 | 14 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 740 | 10360 | 37.061 | -122.0028 | Yes | Overcast-Rain;32-90 F | Pole-Wood | Burned/flashed | 23-0050113 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1828781 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 3261 | 20230321 | 1948 | 20230323 | 1035 | 2059767 | 2327 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 60502 | 37.0431 | -121.9979 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Burned/flashed | 23-0050113 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1828783 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 9963 | 20230321 | 2003 | 20230322 | 1819 | 2061597 | 1336 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 24048 | 36.9736 | -121.8067 | Yes | Partly Cloudy-Fog-Rain;32-90 F |  |  | 23-0050946 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1829344 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 2241 | 20230321 | 2005 | 20230321 | 2245 | 2056624 | 160 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 5120 | 36.5246 | -121.834 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0050026 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1828708 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | FUSE | 5073 | 20230321 | 2012 | 20230321 | 2222 | 2060582 | 128 | Distribution Circuit | Equipment Failure/Involved | Overhead | 51 | 6528 | 36.9628 | -121.9874 | Yes | Overcast-Rain-Strong Winds;32-90 F | Jumper | Burned Open | 23-0050179 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1828841 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 8643 | 20230321 | 2150 | 20230322 | 1044 | 2061127 | 774 | Distribution Circuit | Vegetation | Tree - branch fell on line | 45 | 34830 | 37.01 | -121.8859 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 23-0050316 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828978 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 5741 | 20230321 | 2202 | 20230322 | 1508 | 2061172 | 1026 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 27702 | 36.9993 | -122.0372 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050720 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829196 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6515 | 20230321 | 2238 | 20230323 | 1000 | 2061279 | 2122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 49 | 104581 | 36.8604 | -121.7075 | Yes | Clear;32-90 F |  |  | 23-0051261 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829573 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | RECLOSER | 2144 | 20230321 | 2246 | 20230322 | 1754 | 2061263 | 1148 | Distribution Circuit | Vegetation | Tree - fell into line | 665 | 763420 | 36.5941 | -121.8893 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050245 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1828905 | 0 | EPSS Ckt | N | 2023 | ABC
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | RECLOSER | 11046 | 20230322 | 19 | 20230323 | 1454 | 2061386 | 2315 | Distribution Circuit | Vegetation | Tree - fell into line | 605 | 1375150 | 36.9995 | -122.0078 | No | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050278 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828939 | 0 | EPSS Ckt | N | 2023 | C-GRD
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 5090 | 20230322 | 215 | 20230323 | 1325 | 2061061 | 2110 | Distribution Circuit | Vegetation | Tree - fell into line | 192 | 169773 | 36.9804 | -121.892 | No | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050302 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828964 | 0 | EPSS Ckt | N | 2023 | B GRD
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 12065 | 20230322 | 247 | 20230324 | 1010 | 2061513 | 3323 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 19938 | 36.9184 | -121.8343 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051202 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829539 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 2465 | 20230322 | 319 | 20230323 | 1120 | 2061526 | 1921 | Distribution Circuit | Vegetation | Tree - branch fell on line | 72 | 138312 | 36.9382 | -121.8619 | No | Overcast-Fog-Heavy Rain;32-90 F | Connector or Splice (OH) | Broken | 23-0050685 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829171 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET 2105 | 83252105 | FUSE | 1661 | 20230322 | 602 | 20230322 | 908 | 2061658 | 186 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 3162 | 36.9853 | -122.0302 | No | Overcast-Fog-Rain;32-90 F |  |  | 23-0050404 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1829020 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 4231 | 20230322 | 719 | 20230323 | 1535 | 2061854 | 1936 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1936 | 36.9885 | -121.8386 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050386 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829012 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 11028 | 20230322 | 730 | 20230322 | 1746 | 2061554 | 616 | Distribution Circuit | Vegetation | Tree - fell into line | 1237 | 232065 | 36.9714 | -121.8908 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050343 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828992 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | JUMPER | 3415 HS OJ | 20230322 | 843 | 20230322 | 1433 | 2063018 | 350 | Distribution Circuit | Equipment Failure/Involved | Overhead | 563 | 197050 | 36.9605 | -121.8864 | No | Overcast-Fog-Rain;32-90 F | Jumper | Burned Open | 23-0050772 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1829233 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 6087 | 20230322 | 845 | 20230322 | 1356 | 2062121 | 311 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 28612 | 37.0665 | -122.0336 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0050558 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829104 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 3621 | 20230322 | 907 | 20230322 | 1319 | 2062027 | 252 | Distribution Circuit | Equipment Failure/Involved | Overhead | 122 | 30744 | 36.7789 | -121.6493 | No | Overcast-Fog-Rain;32-90 F | Pole-Wood | Deteriorated | 23-0050340 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1829023 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412206855548 | 20230322 | 920 | 20230322 | 1705 | 2061912 | 465 | Transformer only | Vegetation | Tree - fell into line | 2 | 930 | 36.8302 | -121.6646 | No | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0050445 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829051 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 12887 | 20230322 | 946 | 20230322 | 1737 | 2062154 | 471 | Distribution Circuit | Vegetation | Tree - branch fell on line | 48 | 22742 | 37.0385 | -122.0681 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0050922 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829323 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | TRANSFORMER | 315534319956 | 20230322 | 956 | 20230323 | 1033 | 2062215 | 1477 | Transformer only | Company Initiated | Construction Activity/equip- company | 6 | 8862 | 37.038 | -122.0311 | No | Overcast-Fog-Drizzle;32-90 F | Secondary | On Ground | 23-0050924 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829325 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | FUSE | 8267 | 20230322 | 959 | 20230322 | 1415 | 2062187 | 256 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 512 | 36.6166 | -121.936 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050452 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1829056 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 83815 | 20230322 | 1005 | 20230324 | 1244 | 2062237 | 3039 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 33429 | 36.9946 | -122.0283 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050479 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829072 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 11331 | 20230322 | 1058 | 20230322 | 1924 | 2062352 | 506 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 4048 | 36.9866 | -121.8871 | No | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 23-0050967 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829359 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | JUMPER | OJ AT 3450 GROSS RD (1/3 #3) | 20230322 | 1132 | 20230323 | 1048 | 2062939 | 1396 | Distribution Circuit | Equipment Failure/Involved | Overhead | 122 | 170312 | 36.9811 | -121.9693 | No | Overcast-Drizzle;32-90 F | Jumper | Burned Open | 23-0050746 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1829217 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 7243 | 20230322 | 1143 | 20230322 | 1644 | 2062476 | 301 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 3612 | 37.0737 | -122.0847 | No | Clear;32-90 F |  |  | 23-0050896 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829309 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRANSFORMER | 315383221287 | 20230322 | 1146 | 20230322 | 1559 | 2062487 | 253 | Transformer only | Unknown Cause | Patrol - found nothing | 8 | 2024 | 37.0739 | -122.0832 | No | Clear;32-90 F |  |  | 23-0050856 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829277 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 8125 | 20230322 | 1237 | 20230323 | 1604 | 2062266 | 1647 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 31293 | 37.099 | -122.1424 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0050630 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1829142 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 11943 | 20230322 | 1257 | 20230322 | 1427 | 2062136 | 90 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 7110 | 37.0112 | -122.0442 | No | Overcast-Fog-Drizzle;32-90 F | Service conductor | Broken | 23-0050681 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1829168 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 4345 | 20230322 | 1303 | 20230322 | 1710 | 2062762 | 247 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 1729 | 36.8303 | -121.6669 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0050690 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1829174 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1103 | 182031103 | SWITCH | 7164 | 20230322 | 1321 | 20230322 | 1329 | 2062819 | 8 | Distribution Circuit | Company Initiated | Return Circuit Normal | 42 | 336 | 36.185 | -121.1463 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0049651 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1829235 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2102 | 182222102 | SWITCH | 2666 | 20230322 | 1348 | 20230322 | 1411 | 2062991 | 23 | Distribution Circuit | Company Initiated | Return Circuit Normal | 23 | 493 | 36.616 | -121.8419 | No | Partly Cloudy;32-90 F | Elbow | Failed/Faulted | 23-0050099 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1829229 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | FUSE | 4447 | 20230322 | 1453 | 20230322 | 1549 | 2063068 | 56 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 1680 | 36.7894 | -121.36 | No | Clear;32-90 F |  |  | 23-0050851 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829274 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | SWITCH | 40029 | 20230322 | 1524 | 20230322 | 1605 | 2063101 | 41 | Distribution Circuit | Equipment Failure/Involved | Overhead | 460 | 18860 | 36.6183 | -121.9342 | No | Partly Cloudy;32-90 F | Switch (OH) | Arcing | 23-0050829 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1829264 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | TRANSFORMER | 315919218320 | 20230322 | 1628 | 20230322 | 1823 | 2063317 | 115 | Transformer only | Unknown Cause | Patrol - found nothing | 6 | 690 | 36.9944 | -121.896 | No | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0050988 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1829376 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 2241 | 20230322 | 1636 | 20230322 | 1647 | 2063340 | 11 | Distribution Circuit | Company Initiated | Coordination failure | 32 | 352 | 36.5246 | -121.834 | No | Overcast;32-90 F | Fuse | Normal | 23-0050892 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1829307 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | TRANSFORMER | 316224212310 | 20230322 | 1651 | 20230323 | 1412 | 2063383 | 1281 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 1281 | 36.8307 | -121.7912 | No | Clear;32-90 F |  |  | 23-0051107 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1829490 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8355 | 20230322 | 1702 | 20230325 | 1913 | 2063410 | 4451 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 480708 | 37.0457 | -122.1099 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051003 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829387 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 2487 | 20230322 | 1719 | 20230325 | 1837 | 2063444 | 4398 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 83562 | 37.0454 | -122.1097 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051004 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829388 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | JUMPER | VERT JPRS 1 SS OF 2064 | 20230322 | 1745 | 20230322 | 2003 | 2063516 | 138 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 2070 | 36.582 | -121.9203 | No | Clear;32-90 F | Recloser | Malfunctioning | 23-0050858 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1829349 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 3647 | 20230322 | 1830 | 20230323 | 840 | 2064215 | 850 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 850 | 36.8942 | -121.7469 | No | Overcast-Rain;32-90 F |  |  | 23-0051209 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1829543 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 18441 | 20230322 | 1839 | 20230323 | 857 | 2063641 | 858 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 4290 | 37.1289 | -121.9772 | No | Overcast-Drizzle;32-90 F |  |  | 23-0051226 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829553 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | TRANSFORMER | 316205416035 | 20230322 | 1957 | 20230323 | 1810 | 2063754 | 1333 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3999 | 36.9331 | -121.7994 | No | Overcast;32-90 F | Transformer | Broken- wire on object | 23-0051247 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829570 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 9431 | 20230322 | 1958 | 20230323 | 2300 | 2063759 | 1622 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 10934 | 37.0743 | -122.0816 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051189 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829532 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | JUMPER | OJ 2 LD SIDE OF CGC ENDING IN 20735 | 20230322 | 2120 | 20230326 | 1206 | 2063841 | 5206 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 10412 | 37.0585 | -122.1262 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken | 23-0051036 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1829418 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | FUSE | 6079 | 20230322 | 2331 | 20230323 | 1402 | 2063957 | 871 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 6968 | 36.2659 | -121.8033 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051129 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829506 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 3921 | 20230323 | 18 | 20230323 | 1153 | 2063981 | 694 | Distribution Circuit | Vegetation | Tree - fell into line | 333 | 57900 | 36.8382 | -121.6835 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051135 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1829512 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 7807 | 20230323 | 549 | 20230324 | 1800 | 2064043 | 2171 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 36907 | 36.9884 | -121.7391 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051231 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829562 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | JUMPER | OJ 1 LD OF 11849 | 20230323 | 902 | 20230325 | 1558 | 2064261 | 3296 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 29664 | 37.0395 | -122.0788 | No | Partly Cloudy;32-90 F | Secondary | Broken- wire on ground | 23-0051613 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1829770 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | JUMPER | BURNT OPEN JUMPER 1 N/O 4375 | 20230323 | 919 | 20230323 | 1310 | 2064294 | 231 | Distribution Circuit | Equipment Failure/Involved | Overhead | 110 | 3261 | 36.8629 | -121.7402 | No | Clear;32-90 F | Jumper | Burned Open | 23-0051337 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1829615 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | TRANSFORMER | 412176339895 | 20230323 | 937 | 20230323 | 1746 | 2064327 | 489 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 489 | 36.3978 | -121.6609 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0051388 | OH | Sus | 35431808 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829641 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRANSFORMER | T1124 | 20230323 | 1050 | 20230324 | 1836 | 2064484 | 1906 | Transformer only | Vegetation | Tree - fell into line | 18 | 34308 | 37.1251 | -122.1239 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052030 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829994 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | TRANSFORMER | 315703617799 | 20230323 | 1127 | 20230325 | 1649 | 2064560 | 3202 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 28818 | 36.9793 | -121.9709 | No | Overcast-Rain-Strong Winds;32-90 F | Transformer (OH) | Failed/Faulted | 23-0051414 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829659 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1101 | 182131101 | TRANSFORMER | 412811443808 | 20230323 | 1131 | 20230323 | 1528 | 2064371 | 237 | Transformer only | Equipment Failure/Involved | Overhead | 23 | 5451 | 36.5115 | -121.4476 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0051340 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829616 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | SWITCH | 10513 | 20230323 | 1318 | 20230323 | 1334 | 2064652 | 16 | Distribution Circuit | Equipment Failure/Involved | Underground | 154 | 2464 | 36.5402 | -121.871 | No | Overcast;32-90 F | Elbow | Failed/Faulted | 23-0046184 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1829639 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | OCB | 2201/2 | 20230323 | 1330 | 20230324 | 1418 | 2064771 | 1488 | Distribution Circuit | Vegetation | Tree - fell into line | 515 | 89633 | 36.5786 | -121.9085 | No | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051416 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | Yes | No | 1829661 | 0 | EPSS Ckt | N | 2023 | ABC GRD
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8427 | 20230323 | 1519 | 20230323 | 1942 | 2064973 | 263 | Distribution Circuit | Vegetation | Tree - branch fell on line | 49 | 12887 | 37.077 | -121.981 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0051601 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829762 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 9271 | 20230323 | 1554 | 20230324 | 1239 | 2065046 | 1245 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 16185 | 37.036 | -121.86 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051583 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829748 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 8331 | 20230323 | 1722 | 20230325 | 1152 | 2066858 | 2550 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 12750 | 37.0579 | -121.9734 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052463 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1830423 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRIP-SAVER | 5401 | 20230323 | 1812 | 20230326 | 1306 | 2065226 | 4014 | Distribution Circuit | Equipment Failure/Involved | Overhead | 69 | 276966 | 37.0647 | -122.1232 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0051572 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1829741 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | RECLOSER | 11036 | 20230323 | 1902 | 20230323 | 1909 | 2065208 | 7 | Distribution Circuit | Equipment Failure/Involved | Underground | 151 | 1057 | 36.8573 | -121.7994 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0051549 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1829757 | 0 | Non-EPSS | N | 2023 | NONE
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8361 | 20230323 | 1913 | 20230325 | 1447 | 2065303 | 2609 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 33917 | 37.0763 | -122.1318 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051612 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1829769 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | JUMPER | BURNT OJ 2 E/OF 974130 | 20230323 | 1922 | 20230324 | 109 | 2065316 | 347 | Distribution Circuit | Equipment Failure/Involved | Overhead | 267 | 32129 | 37.0444 | -121.937 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 23-0051661 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1829812 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 3533 | 20230323 | 2020 | 20230324 | 913 | 2065380 | 773 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 28601 | 37.0016 | -122.0274 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0051710 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1829835 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRANSFORMER | 315397621577 | 20230323 | 2222 | 20230326 | 1039 | 2065436 | 3617 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 36170 | 37.0819 | -122.0789 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051657 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829808 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 346475 | 20230324 | 457 | 20230325 | 1902 | 2065558 | 2285 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 18280 | 37.058 | -121.9416 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0051741 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829852 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1103 | 182201103 | TRANSFORMER | 412511748418 | 20230324 | 1114 | 20230324 | 1509 | 2065936 | 235 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 235 | 36.6359 | -121.5534 | No | Overcast-Heavy Rain;32-90 F |  |  | 23-0051967 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1829949 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1109 | 182011109 | TRANSFORMER | 412444649950 | 20230324 | 1116 | 20230324 | 1254 | 2065941 | 98 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 98 | 36.6776 | -121.5786 | No | Clear;32-90 F |  |  | 23-0051892 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1829917 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | TRANSFORMER | 412134949172 | 20230324 | 1143 | 20230324 | 1445 | 2065989 | 182 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 182 | 36.6539 | -121.6826 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0051879 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829909 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | TRANSFORMER | 315794318860 | 20230324 | 1144 | 20230324 | 1513 | 2065992 | 209 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 209 | 37.0089 | -121.9412 | No | Overcast-Heavy Rain;32-90 F | Fuse | Failed/Faulted | 23-0051986 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829961 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 5805 | 20230324 | 1144 | 20230324 | 1945 | 2065993 | 481 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 36556 | 36.9734 | -121.8805 | No | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051869 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829904 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | OCB | 2202/2 | 20230324 | 1233 | 20230324 | 1601 | 2066068 | 208 | Distribution Circuit | Vegetation | Tree - branch fell on line | 191 | 39728 | 36.5786 | -121.9085 | No | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 23-0051887 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829914 | 0 | EPSS Ckt | N | 2023 | A GRD
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6785 | 20230324 | 1346 | 20230324 | 1708 | 2066163 | 202 | Distribution Circuit | 3rd Party | Other | 17 | 3434 | 36.9175 | -121.6845 | No | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 23-0051975 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1829954 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 2689 | 20230324 | 1423 | 20230325 | 1222 | 2066210 | 1319 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 42208 | 37.1274 | -122.0181 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0052471 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1830433 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 6161 | 20230324 | 1426 | 20230324 | 1746 | 2066215 | 200 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 4600 | 37.1187 | -122.0198 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052007 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829976 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316533013356 | 20230324 | 1713 | 20230324 | 1959 | 2066463 | 166 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 166 | 36.8606 | -121.6862 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0052046 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1830008 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRANSFORMER | 315271323296 | 20230324 | 2233 | 20230325 | 1547 | 2066648 | 1034 | Transformer only | Vegetation | Tree - branch fell on line | 7 | 7238 | 37.1281 | -122.1229 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0052525 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1830476 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | FUSE | 2949 | 20230325 | 642 | 20230325 | 1006 | 2066747 | 204 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 62 | 12648 | 36.4449 | -121.6734 | No | Clear;32-90 F |  |  | 23-0052462 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1830421 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | SWITCH | 9033 | 20230325 | 851 | 20230325 | 1855 | 2066832 | 604 | Distribution Circuit | Vegetation | Tree - grew into line | 27 | 16308 | 37.0722 | -122.0754 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0052454 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1830413 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 585 | 20230325 | 1012 | 20230325 | 1130 | 2066904 | 78 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 156 | 36.9521 | -121.7946 | No | Clear;32-90 F |  |  | 23-0052477 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1830437 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1105 | 182011105 | TRANSFORMER | T1278 | 20230325 | 1018 | 20230325 | 1633 | 2066972 | 375 | Transformer only | Company Initiated | Personnel- company | 20 | 7500 | 36.7038 | -121.6196 | No | Clear;32-90 F | Other | Normal | 23-0052480 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1830440 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 10139 | 20230325 | 1108 | 20230325 | 1622 | 2067031 | 314 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1256 | 37.0439 | -122.1552 | No | Overcast-Rain-Strong Winds;32-90 F | Jumper | Broken | 23-0052505 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1830461 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRANSFORMER | 315398220835 | 20230325 | 1203 | 20230325 | 1416 | 2066983 | 133 | Transformer only | Unknown Cause | Patrol - not conducted | 9 | 1197 | 37.0614 | -122.0781 | No | Clear;32-90 F |  |  | 23-0052506 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1830462 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8333 | 20230325 | 1203 | 20230327 | 1314 | s1830581 | 2951 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2951 | 37.0583 | -121.971 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052638 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1830581 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 6083 | 20230325 | 1216 | 20230327 | 1732 | 2066994 | 3196 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 252484 | 37.0585 | -122.0334 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0052493 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1830452 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1104 | 182201104 | TRANSFORMER | 412534047546 | 20230325 | 1221 | 20230325 | 1742 | 2066999 | 321 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 321 | 36.6123 | -121.5447 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0052488 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1830448 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | TRANSFORMER | 315758720170 | 20230325 | 1235 | 20230328 | 951 | 2066508 | 4156 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 12468 | 37.0446 | -121.9519 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0052489 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1830449 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2103 | 83252103 | RECLOSER | 98594 | 20230325 | 1341 | 20230325 | 1440 | 2067062 | 59 | Distribution Circuit | Vegetation | Tree - branch fell on line | 660 | 38940 | 36.9816 | -122.0252 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0052500 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1830458 | 0 | EPSS Ckt | N | 2023 | A & C
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 4439 | 20230325 | 1406 | 20230325 | 1910 | 2067084 | 304 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 912 | 36.7754 | -121.6769 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052513 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1830466 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 8577 | 20230325 | 1550 | 20230325 | 1810 | 2067166 | 140 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 140 | 37.0465 | -122.152 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0052539 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1830488 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRANSFORMER | 315308423419 | 20230325 | 1709 | 20230327 | 1046 | 2067206 | 2497 | Transformer only | Environmental/External | Water | 4 | 9988 | 37.1325 | -122.1084 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0052544 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1830493 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 9005 | 20230325 | 1712 | 20230325 | 1950 | 2067211 | 158 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 3476 | 37.0318 | -122.1369 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0052552 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1830499 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | FUSE | 5181 | 20230325 | 1849 | 20230325 | 1905 | 2067304 | 16 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 144 | 37.1079 | -122.1082 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0052546 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1830495 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | TRANSFORMER | 315377821485 | 20230325 | 1932 | 20230326 | 1001 | 2067324 | 869 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 869 | 37.0793 | -122.085 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0052646 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1830588 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 5133 | 20230325 | 1950 | 20230326 | 625 | 2067344 | 635 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 4445 | 37.0921 | -122.0917 | No | Clear;32-90 F |  |  | 23-0052624 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1830567 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | TRANSFORMER | 315317122542 | 20230325 | 2003 | 20230326 | 956 | 2067353 | 833 | Transformer only | Vegetation | Tree - fell into line | 2 | 1666 | 37.1087 | -122.1053 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0052652 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1830596 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRIP-SAVER | 9031 | 20230325 | 2006 | 20230325 | 2208 | 2067355 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 48 | 5856 | 37.0726 | -122.0742 | No | Clear;32-90 F |  |  | 23-0052565 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1830509 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 2283 | 20230325 | 2219 | 20230326 | 1140 | 2067411 | 801 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 12135 | 36.5564 | -121.9087 | No | Clear;32-90 F | Conductor- Overhead | Burned/flashed | 23-0052596 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1830540 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | TRANSFORMER | 315318022395 | 20230326 | 335 | 20230327 | 1632 | 2067617 | 2217 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 11085 | 37.1048 | -122.1051 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0052651 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1830594 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 3921 | 20230326 | 636 | 20230326 | 810 | 2067475 | 94 | Distribution Circuit | Animal | Bird found | 203 | 19082 | 36.8382 | -121.6835 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0052632 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1830575 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 6491 | 20230326 | 637 | 20230326 | 846 | 2067476 | 129 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 2838 | 36.9325 | -121.7435 | No | Clear;32-90 F |  |  | 23-0052637 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1830579 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 6033 | 20230326 | 648 | 20230326 | 1425 | 2067493 | 457 | Distribution Circuit | Animal | Bird found | 82 | 37474 | 37.081 | -122.0049 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0052678 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1830619 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | JUMPER | JUMPERS 1 W/OF CGC# 516533013356 | 20230326 | 912 | 20230326 | 1418 | 2067558 | 306 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 612 | 36.8603 | -121.6868 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0052639 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1830582 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 195 | 20230326 | 1113 | 20230326 | 1651 | 2067643 | 338 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 5408 | 37.083 | -122.0809 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0052660 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1830602 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | LOS GATOS-1106 | 82021106 | TRANSFORMER | 315563024196 | 20230326 | 1421 | 20230327 | 1425 | 2067768 | 1444 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 4332 | 37.1561 | -122.0233 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0052711 | OH | Sus | 35434044 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1830646 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 9049 | 20230326 | 1442 | 20230326 | 1600 | 2067782 | 78 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 936 | 36.9963 | -121.8965 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0052701 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1830634 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2102 | 182222102 | RECLOSER | 9060 | 20230326 | 2130 | 20230327 | 206 | 2068079 | 276 | Distribution Circuit | Equipment Failure/Involved | Overhead | 896 | 46037 | 36.608 | -121.8536 | No | Clear;32-90 F | Conductor- Overhead | Arcing | 23-0052724 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1830692 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRANSFORMER | 315227224378 | 20230327 | 812 | 20230327 | 1540 | 2068272 | 448 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 3584 | 37.1584 | -122.136 | No | Clear;32-90 F | Transformer | Broken | 23-0052818 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1830732 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1102 | 182201102 | FUSE | 25111 | 20230327 | 930 | 20230327 | 1118 | 2068448 | 108 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 432 | 36.5889 | -121.5019 | No | Clear;32-90 F |  |  | 23-0052918 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1830801 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | TRANSFORMER | 412036852675 | 20230327 | 1007 | 20230327 | 1421 | 2068229 | 254 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 508 | 36.749 | -121.7194 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0052867 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1830776 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 11909 | 20230327 | 1024 | 20230327 | 1315 | 2068525 | 171 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 171 | 37.0125 | -122.1944 | No | Clear;32-90 F |  |  | 23-0052951 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1830812 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | JUMPER | OPEN JUMPER 1P N/OF 943 | 20230327 | 1105 | 20230327 | 1207 | 2068645 | 62 | Distribution Circuit | Equipment Failure/Involved | Overhead | 419 | 25978 | 36.8819 | -121.6619 | No | Clear;32-90 F | Jumper | Burned Open | 23-0052910 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1830798 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | JUMPER | WIRE DOWN | 20230327 | 1123 | 20230328 | 912 | 2068780 | 1309 | Distribution Circuit | Equipment Failure/Involved | Overhead | 43 | 7668 | 36.5394 | -121.449 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0052974 | OH | Sus | 35431808 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | Yes | Yes | 1830820 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 12443 | 20230327 | 1127 | 20230327 | 1332 | 2068663 | 125 | Distribution Circuit | 3rd Party | Metallic Balloon | 28 | 3500 | 36.9111 | -121.7481 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0053001 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1830831 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | RECLOSER | 7022 | 20230327 | 1150 | 20230327 | 1201 | 2068355 | 11 | Distribution Circuit | Equipment Failure/Involved | Overhead | 45 | 495 | 36.179 | -121.1342 | No | Clear;32-90 F | Regulator | Malfunctioning | 23-0052932 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1830808 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | TRANSFORMER | 316355314296 | 20230327 | 1429 | 20230328 | 1406 | 2068938 | 1417 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1417 | 36.8858 | -121.7473 | No | Clear;32-90 F | Transformer | Burned/flashed | 23-0053111 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1830878 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | JUMPER | JUMPERS 3P N/OF CGC# 315484823113 | 20230327 | 1535 | 20230327 | 1942 | 2069019 | 247 | Distribution Circuit | Vegetation | Tree - grew into line | 4 | 988 | 37.1253 | -122.0497 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0053073 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1830859 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1103 | 182131103 | JUMPER | OJ @ 25213 | 20230327 | 1634 | 20230328 | 5 | 2069274 | 451 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 2255 | 36.4992 | -121.4373 | No | Clear;32-90 F | Jumper | Burned Open | 23-0053148 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1830907 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 4689 | 20230327 | 1659 | 20230327 | 1728 | 2069165 | 29 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 232 | 36.9742 | -121.9857 | No | Clear;32-90 F |  |  | 23-0053134 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1830893 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRANSFORMER | 315170024606 | 20230327 | 2019 | 20230328 | 137 | 2069362 | 318 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 954 | 37.1641 | -122.1586 | No | Clear;32-90 F |  |  | 23-0053197 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1830951 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRANSFORMER | 315222824377 | 20230327 | 2141 | 20230328 | 407 | 2069411 | 386 | Transformer only | Environmental/External | Water | 2 | 772 | 37.1584 | -122.1376 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0053207 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1830960 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | TRANSFORMER | T39166 | 20230328 | 614 | 20230328 | 923 | 2069504 | 189 | Transformer only | Equipment Failure/Involved | Underground | 16 | 3024 | 36.5427 | -121.9263 | No | Partly Cloudy;32-90 F | Connector or Splice (UG) | Broken | 23-0053224 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1830978 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SOLEDAD-2104 | 182052104 | FUSE | 2017 | 20230328 | 1002 | 20230328 | 1319 | 2070090 | 197 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 1970 | 36.4396 | -121.3505 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0053450 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1831111 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | TRANSFORMER | 412933554910 | 20230328 | 1010 | 20230328 | 1212 | 2069740 | 122 | Transformer only | Environmental/External | Water | 3 | 366 | 36.8153 | -121.4175 | No | Overcast;32-90 F | Transformer | Failed/Faulted | 23-0053395 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831085 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | FUSE | 3577 | 20230328 | 1025 | 20230328 | 1600 | 2070166 | 335 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1675 | 36.7251 | -121.7485 | No | Clear;32-90 F | Jumper | Burned Open | 23-0053503 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1831151 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 10977 | 20230328 | 1027 | 20230328 | 1649 | 2070176 | 382 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 5730 | 37.0958 | -122.277 | No | Overcast-Rain;32-90 F | Connector or Splice (OH) | Arcing | 23-0053417 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1831095 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 3567 | 20230328 | 1130 | 20230328 | 1316 | 2070370 | 106 | Distribution Circuit | Vegetation | Tree - branch fell on line | 180 | 19080 | 36.8799 | -121.6939 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0053583 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1831195 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 697 | 20230328 | 1217 | 20230328 | 1320 | 2070524 | 63 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 1197 | 37.0658 | -122.1424 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0053612 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1831212 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0421 | 182440421 | JUMPER | VERT JUMPER | 20230328 | 1240 | 20230328 | 1634 | 2070565 | 234 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 8926 | 36.6174 | -121.9101 | No | Overcast-Rain-Strong Winds;32-90 F | Jumper | Burned Open | 23-0053676 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1831248 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | JUMPER | JUMPERS @ CGC# 411354346781 | 20230328 | 1434 | 20230328 | 1652 | 2070836 | 138 | Distribution Circuit | Vegetation | Tree - grew into line | 4 | 552 | 36.5816 | -121.9465 | No | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0053700 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1831266 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | OTHER | 7233 | 20230328 | 1541 | 20230329 | 727 | 2070972 | 946 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1892 | 37.0859 | -122.0897 | No | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0053808 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | Yes | 1831319 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2102 | 182222102 | FUSE | 8935 | 20230328 | 1629 | 20230329 | 1557 | 2071057 | 1408 | Distribution Circuit | Equipment Failure/Involved | Underground | 168 | 34472 | 36.6091 | -121.852 | No | Overcast-Rain;32-90 F | Elbow | Burned/flashed | 23-0053809 | UG | Sus | 35431811 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831320 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | RECLOSER | 826224 | 20230328 | 1718 | 20230328 | 1736 | 2071074 | 12 | Distribution Circuit | Vegetation | Tree - fell into line | 358 | 4296 | 36.7924 | -121.663 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0053826 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1831333 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | OCB | 1101/2 | 20230328 | 1724 | 20230328 | 1938 | 2071252 | 134 | Distribution Circuit | Vegetation | Tree - fell into line | 2224 | 227220 | 36.8001 | -121.769 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 23-0053839 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | No | No | 1831342 | 0 | EPSS Ckt | N | 2023 | A-C-GRD
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 9511 | 20230328 | 1809 | 20230329 | 1149 | 2071360 | 1060 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 19900 | 36.5229 | -121.8059 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0053889 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1831372 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | OCB | 2105/2 | 20230328 | 1838 | 20230329 | 118 | 2072012 | 400 | Distribution Circuit | Equipment Failure/Involved | Underground | 12720 | 3312639 | 36.5991 | -121.8541 | No | Overcast-Rain;32-90 F | Elbow | Failed/Faulted | 23-0053917 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | No | No | 1831398 | 0 | EPSS Ckt | N | 2023 | BC GRD
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 412001750163 | 20230328 | 2027 | 20230328 | 2225 | 2072032 | 118 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 118 | 36.6798 | -121.7296 | No | Clear;32-90 F | Fuse | Broken | 23-0053962 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831443 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | JUMPER | 4712 | 20230329 | 627 | 20230329 | 927 | 2072315 | 180 | Distribution Circuit | Equipment Failure/Involved | Overhead | 658 | 31426 | 36.8565 | -121.5126 | No | Clear;32-90 F | Jumper | Burned Open | 23-0054007 | OH | Sus | 45698559 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1831476 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 9631 | 20230329 | 724 | 20230329 | 1344 | 2072373 | 380 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 35340 | 36.5854 | -121.9048 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0054063 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1831499 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412236454341 | 20230329 | 730 | 20230329 | 1509 | 2072375 | 459 | Transformer only | Vegetation | Tree - fell into line | 5 | 2295 | 36.7968 | -121.6533 | No | Overcast;32-90 F | Transformer (OH) | Broken- wire on ground | 23-0054111 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1831530 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | RECLOSER | BL 1101 | 20230329 | 820 | 20230329 | 827 | 2072486 | 7 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 742 | 5194 | 37.0926 | -122.0966 | No | Partly Cloudy-Rain;32-90 F |  |  | 23-0054071 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1831503 | 0 | EPSS Ckt | N | 2023 | AC
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | SWITCH | 209531 | 20230329 | 1000 | 20230329 | 1453 | 2072702 | 293 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2344 | 37.0206 | -122.1296 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 23-0054193 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1831557 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 9091 | 20230329 | 1028 | 20230329 | 1400 | 2072754 | 212 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 424 | 36.9091 | -121.2265 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0054457 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831668 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | FUSE | 6713 | 20230329 | 1109 | 20230329 | 1942 | 2072832 | 513 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 26157 | 36.4702 | -121.7242 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0054388 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1831638 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | SWITCH | 35388 | 20230329 | 1208 | 20230329 | 1246 | 2073008 | 38 | Distribution Circuit | Company Initiated | Return Circuit Normal | 1215 | 17379 | 36.6025 | -121.9344 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0054073 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1831612 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9775 | 20230329 | 1209 | 20230329 | 1836 | 2073007 | 387 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 14706 | 37.141 | -122.0902 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0054393 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1831641 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 5151 | 20230329 | 1317 | 20230330 | 1802 | 2073104 | 1725 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 8625 | 37.111 | -122.0899 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0054510 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1831678 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 307348 | 20230329 | 1351 | 20230329 | 1413 | 2073208 | 22 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 34 | 748 | 37.2109 | -122.1505 | No | Clear;32-90 F |  |  | 23-0054446 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1831662 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6521 | 20230329 | 1354 | 20230329 | 1902 | 2073200 | 308 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 3080 | 36.9224 | -121.8401 | No | Partly Cloudy-Drizzle;32-90 F |  |  | 23-0054631 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831732 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 11837 | 20230329 | 1355 | 20230329 | 1610 | 2073188 | 135 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 2113 | 36.9273 | -121.8149 | No | Partly Cloudy-Drizzle;32-90 F |  |  | 23-0054571 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831698 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 7825 | 20230329 | 1400 | 20230329 | 1642 | 2073213 | 162 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 3402 | 36.9677 | -121.794 | No | Partly Cloudy-Drizzle;32-90 F |  |  | 23-0054584 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831702 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 11169 | 20230329 | 1400 | 20230329 | 1738 | 2073198 | 218 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1307 | 36.9307 | -121.8385 | No | Partly Cloudy-Drizzle;32-90 F |  |  | 23-0054594 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831703 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 422016 | 20230329 | 1402 | 20230329 | 2044 | 2073204 | 402 | Distribution Circuit | Environmental/External | Lightning | 1068 | 80329 | 36.964 | -121.8086 | No | Overcast-Rain;32-90 F | Transformer (OH) | Burned/flashed | 23-0054439 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831660 | 0 | EPSS Ckt | N | 2023 | C GRD
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 9613 | 20230329 | 1404 | 20230329 | 1741 | 2073215 | 217 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 795 | 36.9726 | -121.76 | No | Partly Cloudy-Drizzle;32-90 F |  |  | 23-0054613 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831717 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316287817774 | 20230329 | 1409 | 20230329 | 2319 | 2073230 | 550 | Transformer only | Environmental/External | Lightning | 4 | 2200 | 36.9812 | -121.772 | No | Partly Cloudy-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 23-0054626 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831728 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411929953372 | 20230329 | 1500 | 20230329 | 1710 | 2073328 | 130 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 1950 | 36.7675 | -121.7567 | No | Clear;32-90 F | Fuse | Burned Open | 23-0054605 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831709 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316293917669 | 20230329 | 1525 | 20230330 | 1517 | 2073389 | 1432 | Transformer only | Vegetation | Tree - fell into line | 2 | 2864 | 36.9784 | -121.7704 | No | Partly Cloudy-Drizzle;32-90 F | Transformer | Failed/Faulted | 23-0054652 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831751 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | JUMPER | OJ 1 W/OF 1653 | 20230329 | 1550 | 20230330 | 1743 | 2073450 | 1553 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 29507 | 37.1577 | -122.1396 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0054550 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1831691 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | FUSE | 3575 | 20230329 | 1551 | 20230331 | 315 | 2073452 | 2124 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 19116 | 36.7297 | -121.7326 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0054661 | OH | Sus | 31641033 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1831757 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 3379 | 20230329 | 1556 | 20230329 | 2032 | 2073675 | 276 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 276 | 36.9821 | -121.7682 | No | Partly Cloudy;32-90 F |  |  | 23-0054663 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831758 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | TRANSFORMER | 316215517295 | 20230329 | 1704 | 20230330 | 1225 | 2073521 | 1161 | Transformer only | Environmental/External | Lightning | 10 | 11610 | 36.9677 | -121.7964 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0054659 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831755 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 316196617968 | 20230329 | 1818 | 20230330 | 302 | 2073585 | 524 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 524 | 36.9862 | -121.8031 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0054674 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831764 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 937291 | 20230329 | 2012 | 20230330 | 1412 | 2073700 | 1080 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 14040 | 37.1186 | -121.964 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0054675 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1831765 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | FUSE | 7107 | 20230329 | 2039 | 20230330 | 1058 | 2073716 | 859 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 9740 | 36.1984 | -120.7147 | No | Clear;32-90 F |  |  | 23-0054960 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831948 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | OTHER | 5159 | 20230329 | 2241 | 20230330 | 1406 | 2073791 | 925 | Distribution Circuit | Vegetation | Tree - fell into line | 102 | 19704 | 37.0814 | -122.0846 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0054718 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | Yes | 1831807 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 307348 | 20230330 | 103 | 20230330 | 1117 | 2073820 | 614 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 20876 | 37.2109 | -122.1505 | No | Overcast-Drizzle;32-90 F | Recloser | Malfunctioning | 23-0054719 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1831808 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 1539 | 20230330 | 845 | 20230330 | 1122 | 2074022 | 157 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 471 | 36.9762 | -121.811 | No | Clear;32-90 F |  |  | 23-0054950 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831946 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316321517288 | 20230330 | 1013 | 20230330 | 2213 | 2073919 | 720 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 720 | 36.9679 | -121.7602 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 23-0054908 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831927 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1106 | 182011106 | SWITCH | 3985 | 20230330 | 1120 | 20230330 | 1126 | 2074334 | 6 | Distribution Circuit | Equipment Failure/Involved | Overhead | 234 | 1404 | 36.6746 | -121.6532 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Burned/flashed | 23-0054953 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1831947 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 9091 | 20230330 | 1400 | 20230330 | 1410 | 2074606 | 10 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 20 | 36.9091 | -121.2265 | No | Partly Cloudy;32-90 F |  |  | 23-0055146 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831998 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1101 | 182011101 | TRANSFORMER | 412235849439 | 20230330 | 1400 | 20230330 | 1514 | 2074537 | 74 | Transformer only | Vegetation | Tree - grew into line | 19 | 1406 | 36.6619 | -121.6488 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0055144 | OH | Sus | 45711970 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831997 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1107 | 182011107 | TRANSFORMER | 412243649748 | 20230330 | 1531 | 20230330 | 2205 | 2074623 | 394 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 2364 | 36.6705 | -121.6462 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 23-0055159 | OH | Sus | 35435419 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1832002 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | TRANSFORMER | 316311915114 | 20230331 | 501 | 20230331 | 1539 | 2075062 | 638 | Transformer only | 3rd Party | Vehicle | 1 | 638 | 36.9082 | -121.7626 | No | Fog;32-90 F | Transformer | Broken- wire on ground | 23-0055357 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1832121 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 2275 | 20230331 | 723 | 20230331 | 1048 | 2075107 | 205 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 205 | 36.9967 | -121.8312 | No | Fog;32-90 F |  |  | 23-0055480 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1832195 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | OTHER | 1273 | 20230331 | 954 | 20230331 | 1851 | 2075318 | 537 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 5907 | 37.1217 | -121.9784 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0055560 | OH | Sus | 31641135 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1832218 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | FUSE | 6713 | 20230331 | 1037 | 20230331 | 1215 | 2075353 | 98 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 95 | 9310 | 36.4702 | -121.7242 | No | Clear;32-90 F |  |  | 23-0055545 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1832211 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6541 | 20230331 | 1135 | 20230331 | 2221 | 2075439 | 646 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1938 | 36.9117 | -121.8303 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0055553 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | Yes | 1832214 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | TRANSFORMER | 315149720656 | 20230331 | 1400 | 20230331 | 1628 | 2075542 | 148 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 148 | 37.0555 | -122.1634 | No | Clear;32-90 F |  |  | 23-0055658 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1832259 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 316203517556 | 20230331 | 1458 | 20230401 | 2124 | 2075608 | 1826 | Transformer only | Environmental/External | Lightning | 1 | 1826 | 36.9755 | -121.8011 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0055665 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1832262 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | INDUSTRIAL ACRES-0412 | 182300412 | TRANSFORMER | 412350150297 | 20230331 | 1538 | 20230401 | 1121 | 2075641 | 1183 | Transformer only | Unknown Cause | Patrol - found nothing | 25 | 29575 | 36.6863 | -121.6106 | No | Clear;32-90 F |  |  | 23-0055666 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1832263 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | TRANSFORMER | 411460247093 | 20230331 | 1543 | 20230331 | 1641 | 2075639 | 58 | Transformer only | Vegetation | Tree - fell into line | 9 | 522 | 36.5911 | -121.9111 | No | Clear;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0055657 | OH | Sus | 45713542 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1832258 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 445933 | 20230331 | 1620 | 20230331 | 1643 | 2075341 | 23 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 1288 | 37.1372 | -122.1004 | No | Clear;32-90 F |  |  | 23-0055656 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1832257 | 0 | EPSS Ckt | N | 2023 | A-C
CENTRAL COAST | MONTEREY | DEL MONTE-1101 | 182221101 | TRANSFORMER | 411699547824 | 20230331 | 1912 | 20230401 | 1212 | 2075789 | 1020 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 13974 | 36.6128 | -121.83 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 23-0055676 | OH | Sus | 31641114 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1832273 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | JUMPER | UN-NUMBERED SBCO | 20230331 | 1954 | 20230331 | 2044 | 2075790 | 50 | Distribution Circuit | Vegetation | Tree - grew into line | 17 | 850 | 36.9666 | -121.8932 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0055674 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1832271 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 7725 | 20230401 | 712 | 20230401 | 840 | 2076473 | 88 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 88 | 36.6202 | -121.9359 | No | Clear;32-90 F | Fuse | Broken | 23-0055828 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1832423 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 316042815970 | 20230401 | 814 | 20230402 | 1812 | 2076512 | 2038 | Transformer only | Environmental/External | Lightning | 1 | 2038 | 36.9304 | -121.855 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0055842 | OH | Sus | 31641092 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1832452 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | TRANSFORMER | 412219152619 | 20230401 | 938 | 20230401 | 1554 | 2076597 | 376 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 376 | 36.749 | -121.6574 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0055844 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1832456 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | TRANSFORMER | 411592047342 | 20230401 | 1223 | 20230401 | 1242 | 2076697 | 19 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 304 | 36.6 | -121.8656 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0055863 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1832468 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 8983 | 20230401 | 1955 | 20230401 | 2105 | 2076996 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 2288 | 37.0307 | -122.1429 | No | Partly Cloudy;32-90 F |  |  | 23-0055902 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1832498 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 8985 | 20230401 | 2222 | 20230402 | 1210 | 2077083 | 828 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 19044 | 37.0288 | -122.1405 | No | Clear;32-90 F |  |  | 23-0056026 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1832620 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | TRANSFORMER | 316211613577 | 20230402 | 954 | 20230402 | 1640 | 2077368 | 406 | Transformer only | Vegetation | Tree - fell into line | 2 | 812 | 36.8657 | -121.796 | No | Clear;32-90 F | Bushing | Broken | 23-0056016 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1832611 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | TRANSFORMER | 411429146176 | 20230402 | 1443 | 20230402 | 2317 | 2077525 | 514 | Transformer only | Vegetation | Tree - fell into line | 17 | 8738 | 36.5663 | -121.9197 | No | Partly Cloudy;32-90 F | Transformer | Bent or Twisted | 23-0056043 | OH | Sus | 45713946 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1832636 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 6975 | 20230402 | 1900 | 20230402 | 2052 | 2077616 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 50 | 5600 | 36.5797 | -121.9204 | No | Overcast;32-90 F |  |  | 23-0056063 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1832656 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | TRANSFORMER | 411450246183 | 20230403 | 429 | 20230403 | 656 | 2077798 | 147 | Transformer only | Vegetation | Tree - fell into line | 3 | 441 | 36.5662 | -121.9133 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Arcing | 23-0056143 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1832706 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 6659 | 20230403 | 620 | 20230403 | 820 | 2077832 | 120 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 839 | 36.959 | -121.786 | No | Clear;32-90 F |  |  | 23-0056220 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1832806 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 942593 | 20230403 | 646 | 20230403 | 757 | 2077846 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 568 | 36.8837 | -121.6588 | No | Clear;32-90 F |  |  | 23-0056177 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1832730 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 4155 | 20230403 | 945 | 20230403 | 1123 | 2077904 | 98 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 1078 | 36.9115 | -121.2375 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0056224 | OH | Sus | 45713924 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1832811 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1105 | 182201105 | TRANSFORMER | 412432948124 | 20230403 | 1025 | 20230403 | 1408 | 2077940 | 223 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 223 | 36.627 | -121.5797 | No | Clear;32-90 F | Transformer | Deteriorated | 23-0056255 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1832828 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRIP-SAVER | 6577 | 20230403 | 1416 | 20230403 | 1822 | 2078467 | 246 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 49 | 12054 | 37.0487 | -121.8085 | No | Clear;32-90 F |  |  | 23-0056583 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1832980 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 11054 | 20230403 | 1424 | 20230404 | 128 | 2078489 | 664 | Distribution Circuit | Vegetation | Tree - fell into line | 307 | 61196 | 36.9775 | -121.7415 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0056417 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Multi-Fault | 0 | No | Yes | No | 1832886 | 0 | EPSS Ckt | N | 2023 | BC GRD TIME
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | OCB | 96246 | 20230403 | 1424 | 20230403 | 2342 | 2078497 | 558 | Distribution Circuit | Vegetation | Tree - fell into line | 11722 | 503359 | 36.6121 | -121.8991 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0056425 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1832889 | 0 | EPSS Ckt | N | 2023 | B GRD
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 3921 | 20230403 | 1451 | 20230404 | 543 | 2078558 | 892 | Distribution Circuit | Vegetation | Tree - fell into line | 203 | 45842 | 36.8382 | -121.6835 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0056533 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1832945 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | FUSE | 9465 | 20230403 | 1458 | 20230403 | 1705 | 2078565 | 127 | Distribution Circuit | Vegetation | Tree - grew into line | 29 | 3683 | 36.9769 | -121.9453 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0056440 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1832894 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | FUSE | 50953 | 20230403 | 1523 | 20230403 | 1720 | 2078658 | 117 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 702 | 36.96 | -121.4309 | No | Clear;32-90 F |  |  | 23-0056557 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1832962 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRIP-SAVER | 9031 | 20230403 | 1533 | 20230403 | 1740 | 2078692 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 48 | 6096 | 37.0726 | -122.0742 | No | Clear;32-90 F |  |  | 23-0056560 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1832963 | 0 | EPSS Ckt | N | 2023 | A PHASE
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | OCB | 2202/2 | 20230403 | 1548 | 20230403 | 2330 | 2078528 | 462 | Distribution Circuit | Vegetation | Tree - fell into line | 3070 | 294562 | 36.5786 | -121.9085 | No | Clear-Strong Winds;32-90 F | Anchor or Guy | Broken- wire on ground | 23-0056486 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1832920 | 0 | EPSS Ckt | N | 2023 | A GRD
CENTRAL COAST | MONTEREY | LAURELES-1112 | 182371112 | TRANSFORMER | 411920443494 | 20230403 | 1625 | 20230404 | 439 | 2078918 | 734 | Transformer only | Unknown Cause | Patrol - found nothing | 5 | 3670 | 36.4966 | -121.7501 | No | Clear;32-90 F |  |  | 23-0056699 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | None | 0 | No | No | No | 1833063 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | RECLOSER | 617344 | 20230403 | 1647 | 20230404 | 1308 | 2078964 | 1221 | Distribution Circuit | Vegetation | Tree - fell into line | 152 | 185592 | 36.5933 | -121.8713 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0056528 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Multi-Fault | 0 | No | No | No | 1832943 | 0 | EPSS Ckt | N | 2023 | ABC GRD
CENTRAL COAST | SALINAS | SALINAS-1109 | 182011109 | JUMPER | OJ SS/OF 61413 | 20230403 | 1706 | 20230403 | 1906 | 2079221 | 120 | Distribution Circuit | Equipment Failure/Involved | Overhead | 254 | 18256 | 36.6779 | -121.6352 | No | Partly Cloudy-Strong Winds;32-90 F | Connector or Splice (OH) | Burned Open | 23-0056582 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Open Circuit | 0 | No | No | No | 1832979 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 9443 | 20230403 | 1820 | 20230403 | 1942 | 2079225 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 99 | 8118 | 37.0818 | -122.0734 | No | Clear;32-90 F |  |  | 23-0056614 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1832998 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 6855 | 20230403 | 1832 | 20230403 | 1956 | 2079270 | 84 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 430 | 34671 | 36.5958 | -121.9421 | No | Clear-Strong Winds;32-90 F |  |  | 23-0056625 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1833009 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 10996 | 20230403 | 2007 | 20230403 | 2132 | 2079357 | 85 | Distribution Circuit | Vegetation | Tree - branch fell on line | 257 | 21845 | 37.0748 | -122.0845 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0056643 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1833019 | 0 | EPSS Ckt | N | 2023 | A-C
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | SWITCH | 10645 | 20230403 | 2136 | 20230403 | 2240 | 2079406 | 64 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 257 | 16448 | 37.0831 | -122.0878 | No | Clear;32-90 F |  |  | 23-0056698 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | None | 0 | No | No | No | 1833062 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 3909 | 20230403 | 2142 | 20230404 | 1440 | 2079413 | 1018 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 62098 | 36.8018 | -121.7009 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0056686 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1833049 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 3257 | 20230403 | 2220 | 20230404 | 308 | 2079426 | 288 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 2304 | 36.7804 | -121.7774 | No | Strong Winds-Clear;32-90 F | Pole-Wood | Deteriorated | 23-0056668 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1833031 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | OCB | 2202/2 | 20230404 | 104 | 20230404 | 259 | 2079471 | 115 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1215 | 139725 | 36.5786 | -121.9085 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0056705 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1833069 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 5043 | 20230404 | 643 | 20230404 | 1833 | 2079542 | 710 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2840 | 37.061 | -122.2262 | No | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0056827 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | Yes | 1833176 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | TRANSFORMER | 411396847666 | 20230404 | 653 | 20230404 | 900 | 2079547 | 127 | Transformer only | Vegetation | Tree - fell into line | 2 | 254 | 36.6064 | -121.9332 | No | Clear;32-90 F | Fuse | Normal | 23-0056847 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1833198 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | TRANSFORMER | 411335447200 | 20230404 | 715 | 20230404 | 1230 | 2079556 | 315 | Transformer only | Vegetation | Tree - branch fell on line | 3 | 945 | 36.5929 | -121.9535 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0056803 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1833147 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412172156218 | 20230404 | 824 | 20230404 | 1509 | 2079630 | 405 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 810 | 36.8476 | -121.6766 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0056828 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1833178 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | RECLOSER | 3032 | 20230404 | 947 | 20230414 | 1145 | 2079778 | 14518 | Distribution Circuit | Environmental/External | Flood/Erosion | 109 | 22762 | 36.634 | -121.6988 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0056846 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1833197 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | SALINAS | DOLAN ROAD-1103 | 182381103 | FUSE | 23721 | 20230404 | 1106 | 20230404 | 1258 | 2079903 | 112 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 149 | 36.7874 | -121.7817 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0057021 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1833240 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | OTHER | WIRE DWN HOT CGC 411398846319 | 20230404 | 1311 | 20230405 | 336 | 2080014 | 865 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4279 | 36.5691 | -121.931 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0057070 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1833250 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | BUENA VISTA-1106 | 182261106 | FUSE | 20193 | 20230404 | 1513 | 20230404 | 1700 | 2080128 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 107 | 36.6394 | -121.6022 | No | Partly Cloudy;32-90 F |  |  | 23-0057195 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1833284 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1103 | 182381103 | TRANSFORMER | 411882254137 | 20230404 | 1540 | 20230405 | 319 | 2080092 | 699 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 699 | 36.7891 | -121.7733 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0057152 | OH | Sus | 35436349 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1833271 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | DEL MONTE-2104 | 182222104 | TRANSFORMER | 412098943952 | 20230404 | 1558 | 20230405 | 1512 | 2080051 | 1394 | Transformer only | Vegetation | Tree - fell into line | 1 | 1394 | 36.5129 | -121.69 | No | Clear;32-90 F | Conductor- Overhead | On Ground | 23-0057167 | OH | Sus | 45715662 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1833278 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 23325 | 20230404 | 1806 | 20230405 | 445 | 2080262 | 639 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 852 | 36.7889 | -121.7023 | No | Clear;32-90 F |  |  | 23-0057247 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1833332 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | TRANSFORMER | 411808550615 | 20230405 | 36 | 20230405 | 1106 | 2080329 | 630 | Distribution Circuit | Equipment Failure/Involved | Overhead | 57 | 9543 | 36.691 | -121.7957 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0057241 | OH | Sus | 35436383 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1833325 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | TRANSFORMER | 411499147377 | 20230405 | 155 | 20230405 | 339 | 2080343 | 104 | Transformer only | Equipment Failure/Involved | Underground | 17 | 1768 | 36.5993 | -121.8979 | No | Overcast;32-90 F | Connector or Splice (UG) | Deteriorated | 23-0057243 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1833328 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6655 | 20230405 | 707 | 20230405 | 1039 | 2080454 | 212 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1696 | 36.9875 | -121.801 | No | Fog;32-90 F |  |  | 23-0057439 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1833484 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 8701 | 20230405 | 825 | 20230405 | 1437 | 2080498 | 372 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 10788 | 36.8375 | -121.7316 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0057400 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1833472 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | BUENA VISTA-1103 | 182261103 | TRANSFORMER | 412248549305 | 20230405 | 1108 | 20230406 | 339 | 2080473 | 991 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 13874 | 36.6581 | -121.6445 | No | Partly Cloudy;32-90 F | Transformer | Burned/flashed | 23-0057462 | OH | Sus | 45716147 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1833492 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | SOLEDAD-2102 | 182052102 | TRANSFORMER | 413124739870 | 20230405 | 1200 | 20230405 | 1819 | 2080655 | 379 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 379 | 36.4056 | -121.3373 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken | 23-0057496 | OH | Sus | 45716261 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1833505 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | JUMPER | BURNT OPEN JUMPER | 20230405 | 1314 | 20230405 | 2225 | 2080885 | 551 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1102 | 36.7889 | -121.7018 | No | Clear;32-90 F | Jumper | Burned Open | 23-0057668 | OH | Sus | 45716743 | SOUTH BAY AND CENTRAL COAST | APR | Open Circuit | 0 | No | No | No | 1833555 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | TRANSFORMER | 412220452409 | 20230405 | 1327 | 20230406 | 119 | 2080898 | 712 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 712 | 36.7433 | -121.6566 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0057684 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1833557 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411933853234 | 20230405 | 1442 | 20230405 | 1449 | 2080995 | 7 | Transformer only | Equipment Failure/Involved | Overhead | 29 | 203 | 36.7645 | -121.7547 | No | Partly Cloudy;32-90 F | Transformer | Normal | 23-0057640 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1833545 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 316224717640 | 20230405 | 1613 | 20230405 | 1834 | 2081060 | 141 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 141 | 36.9773 | -121.7934 | No | Clear;32-90 F |  |  | 23-0057697 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | None | 0 | No | No | No | 1833562 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412191155215 | 20230405 | 1639 | 20230405 | 2342 | 2081082 | 423 | Distribution Circuit | Equipment Failure/Involved | Overhead | 848 | 9719 | 36.8202 | -121.6693 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0057685 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1833558 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2102 | 182222102 | TRANSFORMER | 411685347644 | 20230405 | 2012 | 20230406 | 250 | 2081171 | 398 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 6368 | 36.6079 | -121.8346 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0057734 | OH | Sus | 45716749 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1833596 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 2199 | 20230405 | 2053 | 20230405 | 2138 | 2081187 | 45 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 1260 | 36.9517 | -121.834 | No | Clear;32-90 F |  |  | 23-0057715 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1833576 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | FUSE | 7065 | 20230406 | 1040 | 20230406 | 1127 | 2081693 | 47 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 2 | 94 | 37.0321 | -121.9732 | No | Partly Cloudy;32-90 F | Elbow | Normal | 23-0057910 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1833800 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | TRANSFORMER | 411660847351 | 20230406 | 1249 | 20230406 | 1339 | 2081592 | 50 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 550 | 36.5998 | -121.8429 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0058033 | OH | Sus | 31641356 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1833825 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 12697 | 20230406 | 1636 | 20230407 | 140 | 2082045 | 544 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1088 | 37.1108 | -122.1478 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0058177 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1833865 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 764889 | 20230406 | 1704 | 20230406 | 2108 | 2082150 | 244 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 343 | 83692 | 37.0019 | -122.0376 | No | Overcast;32-90 F |  |  | 23-0058195 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1833884 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 65444 | 20230407 | 302 | 20230407 | 507 | 2082292 | 125 | Distribution Circuit | Vegetation | Tree - branch fell on line | 802 | 100250 | 37.1278 | -122.1229 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0058283 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1833972 | 0 | EPSS Ckt | N | 2023 | B & C
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | JUMPER | OJ E/OF CGC 413585334293 | 20230407 | 754 | 20230407 | 1618 | 2082394 | 504 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1008 | 36.2555 | -121.177 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0058323 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1833989 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | FUSE | 9879 | 20230407 | 825 | 20230407 | 1226 | 2082436 | 241 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 241 | 36.3185 | -121.2117 | No | Overcast;32-90 F |  |  | 23-0058530 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1834087 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | SWITCH | 835 | 20230407 | 835 | 20230407 | 1425 | 2082442 | 317 | Distribution Circuit | Wildfire Mitigation | CWSP - Vegetation Removal | 186 | 24047 | 37.0937 | -122.0052 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0058019 | OH | Sus | 45714851 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1834013 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 9091 | 20230407 | 840 | 20230407 | 846 | 2082455 | 6 | Distribution Circuit | 3rd Party | Customer Equipment | 2 | 12 | 36.9091 | -121.2265 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0058591 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | None | 0 | No | No | No | 1834097 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | TRANSFORMER | 412855241921 | 20230407 | 1110 | 20230407 | 1127 | 2082430 | 17 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 17 | 36.4603 | -121.4304 | No | Overcast;32-90 F | Fuse | Broken | 23-0058492 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1834080 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | TRANSFORMER | 411435846070 | 20230407 | 1111 | 20230407 | 1601 | 2082606 | 290 | Transformer only | Unknown Cause | Patrol - found nothing | 24 | 6960 | 36.5628 | -121.9181 | No | Overcast;32-90 F |  |  | 23-0058518 | OH | Sus | 31641660 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1834085 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 5411 | 20230407 | 1154 | 20230407 | 1426 | 2082668 | 152 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 2584 | 37.0548 | -122.161 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 23-0058630 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1834101 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | RECLOSER | 88772 | 20230407 | 1210 | 20230408 | 1941 | 2082654 | 1891 | Distribution Circuit | Vegetation | Tree - fell into line | 1255 | 134738 | 36.904 | -121.6085 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0058516 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1834084 | 0 | EPSS Ckt | N | 2023 | C GRD
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 5397 | 20230407 | 1349 | 20230407 | 1656 | 2082729 | 187 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 2869 | 37.076 | -122.1429 | No | Clear;32-90 F |  |  | 23-0058678 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1834120 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | TRANSFORMER | 315476217074 | 20230407 | 1456 | 20230407 | 1948 | 2082759 | 292 | Transformer only | Equipment Failure/Involved | Overhead | 19 | 5548 | 36.9577 | -122.048 | No | Overcast;32-90 F | Secondary | Broken- wire on ground | 23-0058655 | OH | Sus | 31641623 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1834110 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | TRANSFORMER | 411448347798 | 20230407 | 1543 | 20230407 | 1850 | 2082650 | 187 | Transformer only | Equipment Failure/Involved | Overhead | 49 | 9163 | 36.6105 | -121.9158 | No | Overcast;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0058647 | OH | Sus | 45719243 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1834107 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 426822 | 20230407 | 1557 | 20230408 | 1130 | 2082807 | 1173 | Distribution Circuit | Vegetation | Tree - fell into line | 101 | 118473 | 37.1016 | -122.0324 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0058657 | OH | Sus | 45719264 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1834111 | 0 | EPSS Ckt | N | 2023 | B/GRD I
CENTRAL COAST | MONTEREY | DEL MONTE-2102 | 182222102 | FUSE | 7479 | 20230407 | 1742 | 20230407 | 1829 | 2082882 | 47 | Distribution Circuit | Animal | Bird found | 70 | 3290 | 36.6071 | -121.852 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0058685 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1834123 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1105 | 182201105 | OCB | 1105/2 | 20230407 | 1809 | 20230407 | 1816 | 2082837 | 7 | Distribution Circuit | 3rd Party | Other | 67 | 469 | 36.6139 | -121.5666 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0058683 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | None | 0 | No | No | No | 1834121 | 0 | Non-EPSS | N | 2023 | NONE
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 8985 | 20230407 | 1954 | 20230408 | 958 | 2082913 | 844 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 9317 | 37.0288 | -122.1405 | No | Clear;32-90 F |  |  | 23-0058715 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1834154 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | FUSE | 7971 | 20230408 | 955 | 20230408 | 1738 | 2083212 | 463 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 463 | 36.9612 | -121.9766 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0058770 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | Yes | No | 1834228 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316476015805 | 20230408 | 1512 | 20230408 | 2355 | 2083321 | 523 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 1569 | 36.9279 | -121.7066 | No | Clear;32-90 F |  |  | 23-0058836 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | None | 0 | No | No | No | 1834285 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 412009054450 | 20230408 | 1637 | 20230409 | 522 | 2083355 | 765 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 2295 | 36.7976 | -121.73 | No | Clear;32-90 F | Transformer | Deteriorated | 23-0058804 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1834256 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 2009 | 20230408 | 2230 | 20230409 | 149 | 2083488 | 199 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 40 | 7960 | 36.9903 | -121.753 | No | Clear;32-90 F |  |  | 23-0058839 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1834288 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | OTHER | 11521 | 20230409 | 0 | 20230409 | 1359 | 2083507 | 839 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 5034 | 36.8869 | -121.7238 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0058860 | OH | Sus | 45719800 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1834309 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 9907 | 20230409 | 1403 | 20230409 | 1853 | 2083712 | 290 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 4350 | 36.8664 | -121.6683 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0058888 | OH | Sus | 45719849 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1834337 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 5825 | 20230409 | 2027 | 20230409 | 2049 | 2083922 | 22 | Distribution Circuit | Vegetation | Tree - branch fell on line | 72 | 1584 | 37.0127 | -121.7935 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0058906 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1834356 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | TRANSFORMER | 411428245533 | 20230410 | 426 | 20230410 | 656 | 2084007 | 150 | Transformer only | Equipment Failure/Involved | Underground | 2 | 300 | 36.5484 | -121.9193 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0058946 | UG | Sus | 45719851 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1834393 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 316276312712 | 20230410 | 743 | 20230410 | 1018 | 2084080 | 155 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 155 | 36.842 | -121.7735 | No | Clear;32-90 F |  |  | 23-0059066 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | None | 0 | No | No | No | 1834528 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | TRANSFORMER | 411983642546 | 20230410 | 800 | 20230410 | 1334 | 2084102 | 334 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 668 | 36.4716 | -121.7276 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0059162 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1834589 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316395017339 | 20230410 | 1509 | 20230410 | 1526 | 2084594 | 17 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 17 | 36.9701 | -121.7351 | No | Clear;32-90 F | Connector or Splice (OH) | Burned/flashed | 23-0059228 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1834610 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6933 | 20230410 | 1643 | 20230410 | 1803 | 2084767 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 400 | 36.9296 | -121.7331 | No | Partly Cloudy;32-90 F |  |  | 23-0059267 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1834629 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO-1101 | 182191101 | FUSE | 9057 | 20230410 | 1833 | 20230410 | 1930 | 2084842 | 57 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 266 | 36.1506 | -121.0667 | No | Clear;32-90 F |  |  | 23-0059282 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1834639 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 6459 | 20230411 | 1200 | 20230411 | 1223 | 2085612 | 23 | Distribution Circuit | Vegetation | Tree - grew into line | 159 | 3657 | 36.8856 | -121.6406 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0059608 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1834906 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | TRANSFORMER | 411463348186 | 20230411 | 1249 | 20230411 | 1957 | 2085347 | 428 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 4708 | 36.6211 | -121.9112 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0059624 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1834910 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | TRANSFORMER | 412299351670 | 20230411 | 1451 | 20230411 | 1533 | 2085736 | 42 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 42 | 36.7235 | -121.6289 | No | Partly Cloudy;32-90 F |  |  | 23-0059739 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | None | 0 | No | No | No | 1834930 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | OCB | 2101/2 | 20230412 | 500 | 20230412 | 1456 | 2086144 | 596 | Distribution Circuit | Vegetation | Tree - fell into line | 2325 | 145750 | 37.0953 | -122.1437 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0059854 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Multi-Fault | 0 | No | Yes | No | 1835018 | 0 | EPSS Ckt | N | 2023 | ABC GRD TIME OC
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 5215 | 20230412 | 1659 | 20230412 | 2019 | 2086978 | 200 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 60 | 11681 | 37.0325 | -122.0765 | No | Clear;32-90 F |  |  | 23-0060384 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1835301 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SOLEDAD-2101 | 182052101 | FUSE | 7474 | 20230412 | 1944 | 20230413 | 1631 | 2087099 | 1247 | Distribution Circuit | Equipment Failure/Involved | Underground | 286 | 71864 | 36.4374 | -121.3163 | No | Clear;32-90 F | Switch (UG) | Leaking | 23-0060394 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1835309 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 422016 | 20230413 | 615 | 20230413 | 1536 | 2087237 | 561 | Distribution Circuit | Equipment Failure/Involved | Overhead | 969 | 157099 | 36.964 | -121.8086 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0060458 | OH | Sus | 45729042 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1835366 | 0 | EPSS Ckt | N | 2023 | A & GRD
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | FUSE | 7671 | 20230413 | 700 | 20230418 | 1835 | 2087634 | 7895 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 7895 | 36.1987 | -121.2808 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0060628 | UG | Sus | 45729151 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1835553 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | SWITCH | 2459 | 20230413 | 1138 | 20230413 | 1415 | 2087650 | 157 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 471 | 36.9302 | -121.8573 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0060517 | OH | Sus | 35435965 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1835557 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | JUMPER | JPRS 1 N/E OF CGC 315925017251 | 20230413 | 1432 | 20230413 | 2017 | 2087801 | 345 | Distribution Circuit | Vegetation | Tree - grew into line | 8 | 2760 | 36.9653 | -121.8946 | No | Clear;32-90 F | Conductor- Overhead | Burned/flashed | 23-0060749 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1835582 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6649 | 20230413 | 1552 | 20230413 | 1601 | 2087879 | 9 | Distribution Circuit | Company Initiated | Return Circuit Normal | 72 | 648 | 37.0261 | -121.7758 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0060458 | OH | Sus | 45729042 | SOUTH BAY AND CENTRAL COAST | APR | None | 0 | No | No | No | 1835597 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SOLEDAD-2101 | 182052101 | TRANSFORMER | T1191 | 20230413 | 1731 | 20230414 | 402 | 2087943 | 631 | Distribution Circuit | Equipment Failure/Involved | Underground | 20 | 12620 | 36.4369 | -121.3173 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0060879 | UG | Sus | 31641959 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1835624 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 6033 | 20230413 | 1933 | 20230413 | 2130 | 2088103 | 117 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 82 | 9594 | 37.081 | -122.0049 | No | Clear;32-90 F |  |  | 23-0060903 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1835642 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6971 | 20230413 | 2326 | 20230414 | 537 | 2088131 | 371 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 2968 | 36.973 | -121.7552 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0060934 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1835677 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 2495 | 20230414 | 617 | 20230414 | 710 | 2088230 | 53 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 954 | 36.5836 | -121.8521 | No | Partly Cloudy;32-90 F |  |  | 23-0060964 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1835713 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SOLEDAD-2101 | 182052101 | INTERRUPTER | 179334 | 20230414 | 1040 | 20230414 | 1127 | 2088496 | 47 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 129 | 6063 | 36.4283 | -121.3157 | No | Clear;32-90 F |  |  | 23-0061106 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1835870 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | BORONDA-1101 | 182461101 | TRANSFORMER | 412176251491 | 20230414 | 1144 | 20230414 | 2022 | 2088637 | 518 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 518 | 36.7176 | -121.6711 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0061144 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1835880 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | FUSE | 3575 | 20230414 | 1308 | 20230414 | 2145 | 2088717 | 517 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 4653 | 36.7297 | -121.7326 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0061207 | OH | Sus | 31642380 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1835905 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | RECLOSER | 3030 | 20230414 | 2135 | 20230415 | 1708 | 2088988 | 1173 | Distribution Circuit | 3rd Party | Vehicle | 133 | 98585 | 36.5854 | -121.6002 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0061275 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1835931 | 0 | EPSS Ckt | N | 2023 | A-GRD
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 2035 | 20230415 | 416 | 20230415 | 1110 | 2089037 | 414 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 828 | 36.9831 | -122.1473 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0061311 | OH | Sus | 45730923 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1835970 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRANSFORMER | 315209023720 | 20230415 | 1408 | 20230415 | 1810 | 2089293 | 242 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 242 | 37.1396 | -122.1445 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0061374 | OH | Sus | 35438027 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1836058 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412167855559 | 20230415 | 1605 | 20230416 | 1115 | 2089303 | 1150 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 3450 | 36.831 | -121.6777 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 23-0061381 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1836065 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | SWITCH | 21039 | 20230415 | 1728 | 20230415 | 1741 | 2089367 | 13 | Distribution Circuit | Company Initiated | Return Circuit Normal | 53 | 689 | 36.498 | -121.501 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0061275 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | Yes | No | 1836071 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 8429 | 20230415 | 1914 | 20230416 | 1710 | 2089444 | 1316 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 5133 | 37.1092 | -122.0598 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0061396 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1836082 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 5967 | 20230416 | 404 | 20230416 | 1038 | 2089511 | 394 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 9062 | 37.0034 | -121.9547 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0061448 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1836152 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | TRANSFORMER | 411428840648 | 20230416 | 831 | 20230416 | 1925 | 2089588 | 654 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 654 | 36.4147 | -121.9145 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0061454 | OH | Sus | 31642460 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1836159 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | FUSE | 50781 | 20230416 | 1903 | 20230416 | 1950 | 2089801 | 47 | Distribution Circuit | Animal | Bird found | 2 | 94 | 36.7888 | -121.3435 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0061500 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1836188 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | TRANSFORMER | 411598647319 | 20230416 | 2310 | 20230417 | 355 | 2089853 | 285 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 3420 | 36.5987 | -121.8639 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0061522 | OH | Sus | 35438222 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1836213 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2102 | 182222102 | TRANSFORMER | 411612947541 | 20230417 | 1020 | 20230417 | 1158 | 2090051 | 98 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 1176 | 36.6048 | -121.8592 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0061650 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1836406 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1103 | 182011103 | TRANSFORMER | 412201350879 | 20230417 | 1042 | 20230417 | 1314 | 2090335 | 152 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 2432 | 36.7011 | -121.6619 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0061626 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1836400 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1104 | 182201104 | TRANSFORMER | 412768346641 | 20230417 | 1120 | 20230417 | 2308 | 2090412 | 708 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 3540 | 36.5891 | -121.4646 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0061692 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1836430 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | FUSE | 9015 | 20230417 | 1438 | 20230417 | 2130 | 2090646 | 412 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 412 | 36.307 | -121.8841 | No | Clear;32-90 F | Jumper | Burned Open | 23-0061799 | OH | Sus | 45733305 | SOUTH BAY AND CENTRAL COAST | APR | Open Circuit | 0 | No | No | No | 1836486 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2102 | 182222102 | FUSE | 40605 | 20230418 | 330 | 20230418 | 532 | 2090992 | 122 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 3819 | 36.6107 | -121.852 | No | Overcast-Rain;32-90 F | Insulator | Broken | 23-0061864 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1836545 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | TRANSFORMER | 412242547466 | 20230418 | 844 | 20230418 | 938 | 2091204 | 54 | Transformer only | Environmental/External | Flood/Erosion | 1 | 54 | 36.6076 | -121.6442 | No | Partly Cloudy;32-90 F | Fuse | Normal | 23-0061953 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1836695 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DEL MONTE-2104 | 182222104 | TRANSFORMER | 411931246165 | 20230418 | 1117 | 20230418 | 1719 | 2091482 | 362 | Transformer only | 3rd Party | Tree - cutting- 3rd party | 1 | 362 | 36.57 | -121.7494 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0062076 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1836746 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1101 | 182011101 | FUSE | 4767 | 20230418 | 1705 | 20230418 | 1746 | 2091771 | 41 | Distribution Circuit | Equipment Failure/Involved | Overhead | 52 | 2133 | 36.6756 | -121.6378 | No | Clear;32-90 F | Fuse | Broken | 23-0062245 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1836801 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 23299 | 20230418 | 1839 | 20230419 | 1245 | 2091847 | 1086 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 227 | 23774 | 36.7693 | -121.7545 | No | Clear;32-90 F |  |  | 23-0062247 | OH | Sus | 31642663 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1836803 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | SEACLIFF 0402 | 83500402 | OTHER | 12946 | 20230418 | 2222 | 20230419 | 303 | 2091920 | 281 | Distribution Circuit | Equipment Failure/Involved | Overhead | 213 | 59853 | 36.9875 | -121.9186 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0062269 | OH | Sus | 31642701 | SOUTH BAY AND CENTRAL COAST | APR | Open Circuit | 0 | No | Yes | No | 1836823 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 12785 | 20230419 | 815 | 20230419 | 1012 | 2092070 | 117 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 117 | 36.9552 | -121.7496 | No | Clear;32-90 F |  |  | 23-0062425 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1837016 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | TRANSFORMER | 412308052422 | 20230419 | 851 | 20230419 | 1647 | 2092312 | 476 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 476 | 36.7445 | -121.6278 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0062403 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1837010 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | CASTROVILLE-2104 | 182352104 | TRANSFORMER | T34545 | 20230419 | 905 | 20230419 | 1357 | 2092393 | 292 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 292 | 36.6925 | -121.7718 | No | Clear;32-90 F | Crossarm- Wood | Burned/flashed | 23-0056788 | OH | Sus | 45496386 | SOUTH BAY AND CENTRAL COAST | APR | None | 0 | No | No | No | 1836987 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | TRANSFORMER | 316349315753 | 20230419 | 1004 | 20230419 | 1406 | 2092467 | 242 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 3630 | 36.9259 | -121.7499 | No | Clear;32-90 F | Transformer | Broken | 23-0062405 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1837013 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 8879 | 20230419 | 1134 | 20230419 | 1319 | 2092553 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 769 | 36.9554 | -122.0514 | No | Clear;32-90 F |  |  | 23-0062522 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1837052 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | TRANSFORMER | 412192552658 | 20230419 | 1253 | 20230419 | 2325 | 2092603 | 632 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 2528 | 36.7504 | -121.6681 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0062593 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1837069 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1102 | 182011102 | TRANSFORMER | 412266250863 | 20230420 | 120 | 20230420 | 310 | 2092859 | 110 | Transformer only | Vegetation | Tree - grew into line | 12 | 1320 | 36.7011 | -121.6397 | No | Clear;32-90 F | Secondary | Normal | 23-0062769 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1837129 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | RECLOSER | 7022 | 20230420 | 859 | 20230420 | 1421 | 2093016 | 322 | Distribution Circuit | Environmental/External | Flood/Erosion | 45 | 14490 | 36.179 | -121.1342 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0048320 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | Yes | No | 1837196 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 9241 | 20230420 | 937 | 20230420 | 1053 | 2093047 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 456 | 37.0832 | -122.0509 | No | Clear;32-90 F |  |  | 23-0062917 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1837235 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316495013075 | 20230420 | 1249 | 20230421 | 123 | 2093317 | 754 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 754 | 36.8531 | -121.6989 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0063216 | OH | Sus | 45737390 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1837305 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | RECLOSER | 7092 | 20230420 | 1449 | 20230420 | 1510 | 2093267 | 21 | Distribution Circuit | Company Initiated | Return Circuit Normal | 57 | 1185 | 36.2036 | -121.1157 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0048320 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | Yes | No | 1837284 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | FUSE | 9557 | 20230420 | 1615 | 20230420 | 1657 | s1837299 | 42 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 1134 | 36.6159 | -121.8999 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0063196 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1837299 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2103 | 83252103 | FUSE | 8251 | 20230421 | 610 | 20230421 | 720 | 2093483 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 423 | 29610 | 36.975 | -122.0183 | No | Clear;32-90 F |  |  | 23-0063285 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1837362 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2101 | 182492101 | TRANSFORMER | 412959456258 | 20230421 | 828 | 20230421 | 1202 | 2093574 | 214 | Transformer only | Equipment Failure/Involved | Overhead | 35 | 7490 | 36.8539 | -121.4076 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0063338 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1837418 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS COCHES-1102 | 182151102 | FUSE | 8513 | 20230421 | 842 | 20230421 | 958 | 2093631 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 101 | 36.3603 | -121.253 | No | Clear;32-90 F |  |  | 23-0063417 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1837518 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1109 | 182011109 | FUSE | 5255 | 20230421 | 1128 | 20230422 | 411 | 2093878 | 1003 | Distribution Circuit | Equipment Failure/Involved | Underground | 70 | 70210 | 36.6795 | -121.6403 | No | Clear;32-90 F | Connector or Splice (UG) | Burned/flashed | 23-0063538 | UG | Sus | 31642863 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1837562 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | SOLEDAD-2102 | 182052102 | TRANSFORMER | 413052539249 | 20230421 | 1241 | 20230421 | 1325 | 2093933 | 44 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 132 | 36.3881 | -121.3615 | No | Clear;32-90 F | Secondary | Normal | 23-0063522 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1837556 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | RECLOSER | 36982 | 20230421 | 1808 | 20230421 | 1833 | 2094220 | 25 | Distribution Circuit | Equipment Failure/Involved | Overhead | 99 | 2475 | 36.5301 | -121.4747 | No | Clear;32-90 F | Anchor or Guy | Broken | 23-0063642 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1837610 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | FUSE | 4201 | 20230421 | 1957 | 20230421 | 2300 | 2094310 | 183 | Distribution Circuit | 3rd Party | Vehicle | 23 | 4209 | 36.9076 | -121.4397 | No | Clear;32-90 F | Anchor or Guy | Broken- wire on ground | 23-0063656 | OH | Sus | 31642878 | SOUTH BAY AND CENTRAL COAST | APR | Three Phase Fault | 0 | No | Yes | No | 1837626 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1103 | 182011103 | FUSE | 43145 | 20230421 | 2147 | 20230422 | 1246 | 2094350 | 899 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 26071 | 36.6985 | -121.661 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0063697 | OH | Sus | 31642920 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1837667 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | TRANSFORMER | 411419946031 | 20230422 | 112 | 20230422 | 324 | 2094386 | 132 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 528 | 36.5616 | -121.9235 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0063703 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | None | 0 | No | No | No | 1837674 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2108 | 83252108 | TRANSFORMER | 315540317317 | 20230422 | 831 | 20230422 | 1005 | 2094495 | 94 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 846 | 36.965 | -122.0263 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0063747 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1837767 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | FUSE | 24187 | 20230422 | 1136 | 20230422 | 1339 | 2094620 | 123 | Distribution Circuit | Equipment Failure/Involved | Overhead | 217 | 26691 | 36.6755 | -121.665 | No | Clear;32-90 F | Fuse | Broken | 23-0063766 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1837785 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 51741 | 20230422 | 1739 | 20230422 | 1855 | 2094774 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 304 | 37.1746 | -122.1636 | No | Partly Cloudy;32-90 F |  |  | 23-0063792 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1837805 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 5997 | 20230422 | 2127 | 20230422 | 2327 | 2094837 | 120 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 1920 | 36.7882 | -121.6799 | No | Partly Cloudy;32-90 F |  |  | 23-0063802 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1837820 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SOLEDAD-2105 | 182052105 | FUSE | 9571 | 20230423 | 629 | 20230423 | 1245 | 2094945 | 376 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 3109 | 36.5021 | -121.3957 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0063818 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1837846 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 9481 | 20230423 | 1009 | 20230423 | 1059 | 2094990 | 50 | Distribution Circuit | 3rd Party | Vehicle | 10 | 500 | 37.016 | -122.0281 | No | Overcast;32-90 F | Conductor- Overhead | Together | 23-0063844 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1837871 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 11103 | 20230423 | 1245 | 20230423 | 1353 | 2095051 | 68 | Distribution Circuit | 3rd Party | Vehicle | 43 | 2924 | 36.9935 | -122.0701 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0063854 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1837880 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | OILFIELDS-1102 | 182391102 | FUSE | 9207 | 20230423 | 1317 | 20230423 | 1500 | 2095090 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 206 | 35.9614 | -120.8376 | No | Clear;32-90 F |  |  | 23-0063862 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1837887 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | SWITCH | 2319 | 20230423 | 1518 | 20230423 | 1822 | 2095093 | 184 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 2576 | 36.5862 | -121.9075 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0063863 | OH | Sus | 35439340 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1837889 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | RECLOSER | 4068 | 20230423 | 2044 | 20230424 | 839 | 2095192 | 715 | Distribution Circuit | 3rd Party | Vehicle | 1195 | 145406 | 36.8693 | -121.4001 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on object | 23-0063882 | OH | Sus | 31643084 | SOUTH BAY AND CENTRAL COAST | APR | Multi-Fault | 0 | No | Yes | No | 1837903 | 0 | EPSS Ckt | N | 2023 | ABC TIME
CENTRAL COAST | KING CITY | SOLEDAD-2102 | 182052102 | JUMPER | OJ AT CGC 413081038471 | 20230423 | 2147 | 20230424 | 15 | 2095208 | 148 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 1332 | 36.3666 | -121.3506 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Deteriorated | 23-0063887 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1837910 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | TRANSFORMER | 412723245335 | 20230424 | 831 | 20230424 | 1948 | 2095390 | 677 | Transformer only | Equipment Failure/Involved | Underground | 2 | 1354 | 36.5531 | -121.4779 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0064181 | UG | Sus | 45739389 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1838167 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 11539 | 20230424 | 921 | 20230424 | 1132 | 2095520 | 131 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 262 | 36.865 | -121.6887 | No | Clear;32-90 F |  |  | 23-0064077 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1838126 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 411866955542 | 20230424 | 937 | 20230424 | 1653 | 2095352 | 436 | Transformer only | Equipment Failure/Involved | Underground | 1 | 436 | 36.827 | -121.78 | No | Partly Cloudy;32-90 F | Transformer | Burned/flashed | 23-0064008 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1838090 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | SWITCH | 4187 | 20230424 | 1320 | 20230424 | 1332 | 2095793 | 12 | Distribution Circuit | Company Initiated | Return Circuit Normal | 29 | 348 | 36.6728 | -121.6643 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0063766 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1838160 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 2347 | 20230425 | 347 | 20230425 | 522 | 2096173 | 95 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 252 | 23940 | 36.9852 | -121.9573 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0064304 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1838238 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2103 | 182492103 | FUSE | 9389 | 20230425 | 1004 | 20230425 | 1050 | 2096519 | 46 | Distribution Circuit | Animal | Squirrel | 54 | 2484 | 36.8443 | -121.3805 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0064443 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1838404 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | TRANSFORMER | 412114648991 | 20230425 | 1215 | 20230425 | 1934 | 2096583 | 439 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 439 | 36.6487 | -121.6892 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0064516 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1838434 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | FORT ORD-2106 | 182402106 | TRANSFORMER | 411775148815 | 20230426 | 402 | 20230426 | 1355 | 2097132 | 593 | Transformer only | Company Initiated | Construction Activity/equip- company | 12 | 7116 | 36.6414 | -121.8046 | No | Partly Cloudy-Fog;32-90 F | Transformer | Failed/Faulted | 23-0064765 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1838560 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 593991 | 20230426 | 1543 | 20230427 | 410 | 2097380 | 747 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 747 | 36.8487 | -121.6901 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0065143 | OH | Sus | 45741573 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1838791 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | SWITCH | 3794 | 20230426 | 2230 | 20230427 | 125 | 2098008 | 175 | Distribution Circuit | Equipment Failure/Involved | Underground | 9 | 609 | 36.5437 | -121.6692 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0065219 | UG | Sus | 35440011 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1838840 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | TRANSFORMER | T1226 | 20230427 | 434 | 20230427 | 1325 | 2098039 | 531 | Transformer only | Equipment Failure/Involved | Underground | 3 | 1593 | 36.546 | -121.6694 | No | Clear;32-90 F | Transformer | Burned/flashed | 23-0065461 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1839020 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 9495 | 20230427 | 605 | 20230427 | 720 | 2098052 | 75 | Distribution Circuit | Animal | Bird found | 7 | 525 | 37.0301 | -122.0227 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0065301 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1838855 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | FUSE | 9609 | 20230427 | 738 | 20230427 | 1310 | 2098084 | 332 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 2985 | 36.2802 | -121.4545 | No | Clear;32-90 F |  |  | 23-0065596 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1839046 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | FUSE | 7671 | 20230427 | 819 | 20230427 | 1259 | s1838901 | 280 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 280 | 0 | 0 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0065359 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | None | 0 | No | No | No | 1838901 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | RECLOSER | 2166 | 20230427 | 923 | 20230427 | 1140 | 2098261 | 137 | Distribution Circuit | Vegetation | Tree - fell into line | 476 | 27265 | 36.2769 | -121.8264 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 23-0065402 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1838968 | 0 | EPSS Ckt | N | 2023 | A/C
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | RECLOSER | 7062 | 20230427 | 1155 | 20230427 | 1347 | 2098424 | 112 | Distribution Circuit | Equipment Failure/Involved | Underground | 49 | 5488 | 36.2789 | -121.3033 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0065497 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1839031 | 0 | Non-EPSS | N | 2023 | C/GRD
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | FUSE | 43809 | 20230427 | 1211 | 20230427 | 1405 | 2098442 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 46 | 5244 | 36.8073 | -121.4119 | No | Clear;32-90 F |  |  | 23-0065626 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1839056 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 6775 | 20230427 | 1308 | 20230428 | 38 | 2098498 | 690 | Distribution Circuit | Equipment Failure/Involved | Overhead | 74 | 5143 | 36.8813 | -121.6414 | No | Clear;32-90 F | Insulator | Broken | 23-0065604 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1839049 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | OILFIELDS-1103 | 182391103 | FUSE | 9219 | 20230427 | 2026 | 20230428 | 1310 | 2098857 | 1004 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 3012 | 35.8705 | -120.8652 | No | Clear;32-90 F |  |  | 23-0065796 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1839150 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1102 | 182011102 | FUSE | 24271 | 20230428 | 105 | 20230428 | 355 | 2098818 | 170 | Distribution Circuit | Equipment Failure/Involved | Overhead | 52 | 8840 | 36.6967 | -121.6391 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0065800 | OH | Sus | 31643450 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1839152 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | TRANSFORMER | 412022452682 | 20230428 | 627 | 20230428 | 916 | 2099017 | 169 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 169 | 36.7492 | -121.7242 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0065937 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1839281 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | TRANSFORMER | 316252013108 | 20230428 | 940 | 20230428 | 1126 | 2099236 | 106 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 106 | 36.8529 | -121.7822 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0066026 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1839320 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | BORONDA-1101 | 182461101 | TRANSFORMER | 412188451629 | 20230428 | 1003 | 20230428 | 1205 | 2099252 | 122 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 122 | 36.7217 | -121.6672 | No | Clear;32-90 F | Fuse | Broken | 23-0066068 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1839334 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | RECLOSER | 7066 | 20230428 | 1518 | 20230428 | 2115 | 2099530 | 357 | Distribution Circuit | Equipment Failure/Involved | Overhead | 292 | 35338 | 36.0489 | -120.9121 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0066136 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1839355 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 2187 | 20230428 | 1718 | 20230428 | 1900 | 2099632 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 905 | 90350 | 36.5944 | -121.8808 | No | Partly Cloudy;32-90 F |  |  | 23-0066159 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1839368 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1101 | 182131101 | FUSE | 25497 | 20230429 | 818 | 20230429 | 1637 | 2099983 | 499 | Distribution Circuit | 3rd Party | Aircraft | 2 | 998 | 36.5332 | -121.4588 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0066285 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1839514 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 7309 | 20230430 | 416 | 20230430 | 1100 | 2100370 | 404 | Distribution Circuit | Equipment Failure/Involved | Underground | 91 | 35996 | 36.5817 | -121.8617 | No | Overcast;32-90 F | Conductor- Underground | Broken | 23-0066376 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1839596 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 2705 | 20230430 | 735 | 20230430 | 1005 | 2100395 | 150 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 4050 | 37.0005 | -121.7403 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0066398 | OH | Sus | 45745387 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1839625 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 5605 | 20230430 | 902 | 20230430 | 1537 | 2100413 | 395 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 4740 | 37.0874 | -122.0467 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Arcing | 23-0066392 | OH | Sus | 45745384 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1839614 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 764889 | 20230430 | 1657 | 20230430 | 1756 | 2100861 | 57 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 343 | 19551 | 37.0019 | -122.0376 | No | Clear;32-90 F |  |  | 23-0066465 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1839681 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | 83500402 | 83500402 | FUSE | 6005 | 20230430 | 1728 | 20230430 | 1828 | 2100882 | 60 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 1200 | 36.9959 | -121.9233 | No | Partly Cloudy;32-90 F |  |  | 23-0066471 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1839687 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1103 | 182381103 | TRANSFORMER | 411856954093 | 20230430 | 1807 | 20230430 | 1912 | 2100902 | 65 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 130 | 36.788 | -121.7825 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0066481 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1839693 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | TRANSFORMER | 316608514130 | 20230501 | 610 | 20230501 | 812 | 2101097 | 122 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 488 | 36.8823 | -121.6607 | No | Clear;32-90 F |  |  | 23-0066559 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | None | 0 | No | No | No | 1839772 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | TRANSFORMER | 413553533535 | 20230501 | 916 | 20230501 | 2233 | 2101231 | 797 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 797 | 36.2344 | -121.1878 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0066590 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1839841 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO-1101 | 182191101 | JUMPER | FB 1/2 SPAN S/OF CGC#414161028060 | 20230501 | 1053 | 20230501 | 1500 | 2101422 | 247 | Distribution Circuit | Environmental/External | Flood/Erosion | 2 | 494 | 36.087 | -120.9776 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0066614 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1839868 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | SWITCH | 7086 | 20230501 | 1117 | 20230501 | 1131 | 2101482 | 14 | Distribution Circuit | Company Initiated | Return Circuit Normal | 91 | 1010 | 36.5766 | -121.8623 | No | Overcast;32-90 F | Conductor- Underground | Normal | 23-0066376 | UG | Sus | 31643701 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1839881 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 7389 | 20230501 | 1137 | 20230501 | 1235 | 2101526 | 58 | Distribution Circuit | 3rd Party | Customer Equipment | 3 | 193 | 36.5858 | -121.7567 | No | Partly Cloudy;32-90 F | Metering Equipment | Failed/Faulted | 23-0066681 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1839906 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | FUSE | 6713 | 20230501 | 1215 | 20230501 | 1314 | 2101571 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 95 | 5605 | 36.4702 | -121.7242 | No | Clear;32-90 F |  |  | 23-0066707 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1839913 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | RECLOSER | 3032 | 20230501 | 1314 | 20230501 | 1434 | 2101636 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 109 | 8720 | 36.634 | -121.6988 | No | Clear;32-90 F |  |  | 23-0066705 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1839912 | 0 | EPSS Ckt | N | 2023 | SGF
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | TRANSFORMER | 315658017626 | 20230501 | 1348 | 20230501 | 1718 | 2101677 | 210 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 1680 | 36.9744 | -121.9864 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0066767 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1839940 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 12820 | 20230501 | 1654 | 20230502 | 225 | 2101895 | 571 | Distribution Circuit | 3rd Party | Vehicle | 1299 | 40764 | 36.897 | -121.6784 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0066824 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1839958 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | TRANSFORMER | 411433645539 | 20230502 | 15 | 20230502 | 1805 | 2102053 | 1070 | Transformer only | Vegetation | Tree - fell into line | 3 | 3210 | 36.5483 | -121.9182 | No | Overcast-Rain;32-90 F | Service conductor | Broken- wire on ground | 23-0066882 | OH | Sus | 31643733 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1840015 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | FUSE | 50657 | 20230502 | 210 | 20230502 | 1025 | 2102071 | 495 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 2970 | 36.9501 | -121.4891 | No | Overcast-Rain;32-90 F |  |  | 23-0067056 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1840178 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRIP-SAVER | 5479 | 20230502 | 523 | 20230502 | 1005 | 2102107 | 282 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 3948 | 37.1292 | -122.1131 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0067031 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1840165 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6711 | 20230502 | 533 | 20230502 | 1326 | 2102113 | 473 | Distribution Circuit | Vegetation | Tree - branch fell on line | 49 | 12650 | 36.9982 | -121.8687 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0066941 | OH | Sus | 45746381 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1840056 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRIP-SAVER | 9817 | 20230502 | 808 | 20230502 | 1754 | 2102209 | 586 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 5602 | 36.8708 | -121.6902 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0066996 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1840137 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | HOLLISTER | HOLLISTER-2101 | 182492101 | FUSE | 9081 | 20230502 | 810 | 20230502 | 1409 | 2102204 | 359 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 2758 | 36.8272 | -121.4179 | No | Overcast;32-90 F | Transformer (OH) | Broken | 23-0067019 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1840154 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | RECLOSER | 885736 | 20230502 | 939 | 20230502 | 2147 | 2102624 | 728 | Distribution Circuit | Equipment Failure/Involved | Overhead | 438 | 177382 | 36.9937 | -121.9776 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0067017 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Multi-Fault | 0 | No | Yes | No | 1840153 | 0 | EPSS Ckt | N | 2023 | A-C GRD
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 3375 | 20230502 | 948 | 20230502 | 1119 | 2102638 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 546 | 36.9062 | -121.6132 | No | Overcast-Drizzle;32-90 F |  |  | 23-0067100 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1840195 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2102 | 182222102 | TRANSFORMER | 411689647595 | 20230502 | 1155 | 20230502 | 1523 | 2102743 | 208 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 2288 | 36.6075 | -121.8326 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0067153 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1840214 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | RECLOSER | 4018 | 20230502 | 1228 | 20230502 | 1304 | 2102787 | 36 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 236 | 8496 | 36.6885 | -121.2715 | No | Clear;32-90 F | Jumper | Broken | 23-0063065 | OH | Sus | 35361893 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1840211 | 0 | EPSS Ckt | N | 2023 | B-GRD
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 50841 | 20230502 | 1239 | 20230502 | 1357 | 2102807 | 78 | Distribution Circuit | Animal | Bird found | 8 | 624 | 36.9242 | -121.3593 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0067203 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1840231 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 50899 | 20230502 | 1843 | 20230503 | 852 | 2103211 | 849 | Distribution Circuit | Animal | Bird found | 3 | 2262 | 36.8323 | -121.3483 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0067379 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1840283 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | RECLOSER | 66936 | 20230502 | 1919 | 20230503 | 1205 | 2103220 | 1006 | Distribution Circuit | 3rd Party | Vehicle | 57 | 57342 | 36.3067 | -121.3117 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0067378 | OH | Sus | 35441091 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | Yes | No | 1840282 | 0 | EPSS Ckt | N | 2023 | A-B
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | JUMPER | FB 2 S/OF 7877 | 20230502 | 2252 | 20230503 | 228 | 2102880 | 216 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 4968 | 36.926 | -121.7582 | No | Overcast-Rain;32-90 F | Crossarm- Wood | Broken | 23-0067422 | OH | Sus | 35441085 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1840309 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 8419 | 20230503 | 45 | 20230503 | 439 | 2103278 | 234 | Distribution Circuit | Vegetation | Tree - grew into line | 33 | 7722 | 36.5693 | -121.7917 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0067438 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1840319 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 2957 | 20230503 | 521 | 20230503 | 1228 | 2103319 | 427 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 10675 | 37.0536 | -122.0766 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0067480 | OH | Sus | 45746724 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1840337 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | TRANSFORMER | 315285020650 | 20230503 | 633 | 20230503 | 1500 | 2103330 | 507 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1014 | 37.0559 | -122.1168 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0067534 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1840404 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | FUSE | 7057 | 20230503 | 821 | 20230503 | 1047 | 2103425 | 146 | Distribution Circuit | Vegetation | Tree - bark fell into line | 2 | 292 | 36.2673 | -121.2012 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 23-0067623 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1840497 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | SWITCH | 846214 | 20230503 | 851 | 20230503 | 1041 | 2103485 | 110 | Distribution Circuit | Equipment Failure/Involved | Underground | 12 | 1320 | 36.8439 | -121.3605 | No | Overcast;32-90 F | Conductor- Underground | Normal | 23-0067494 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1840418 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | TRIP-SAVER | 3959 | 20230503 | 947 | 20230503 | 1229 | 2103583 | 162 | Distribution Circuit | Equipment Failure/Involved | Overhead | 375 | 60750 | 36.959 | -122.0316 | No | Overcast-Drizzle;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0067617 | OH | Sus | 45748024 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1840494 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | SWITCH | 8805 | 20230503 | 948 | 20230503 | 1054 | 2103572 | 50 | Distribution Circuit | Vegetation | Tree - fell into line | 166 | 5376 | 37.0527 | -122.0758 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0067562 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1840466 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | SWITCH | 1559 | 20230503 | 1102 | 20230503 | 1109 | 2103698 | 7 | Distribution Circuit | Company Initiated | Return Circuit Normal | 68 | 476 | 37.0529 | -122.0753 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0067562 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | None | 0 | No | No | No | 1840505 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | TRANSFORMER | 413602332838 | 20230503 | 1118 | 20230503 | 1630 | 2103432 | 312 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 312 | 36.216 | -121.1698 | No | Overcast-Drizzle;32-90 F | Cutout- fuse holder | Broken | 23-0067645 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1840507 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | FUSE | 711393 | 20230503 | 1321 | 20230503 | 1452 | 2103843 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 364 | 36.6804 | -121.5569 | No | Overcast;32-90 F |  |  | 23-0067784 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1840558 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 7757 | 20230504 | 624 | 20230504 | 1438 | 2104366 | 494 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2470 | 37.0132 | -121.9372 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0068032 | OH | Sus | 45749126 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1840747 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-1101 | 182221101 | JUMPER | C PHASE OJ AT CGC# 411717847884 | 20230504 | 1159 | 20230504 | 1631 | 2104780 | 272 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 8432 | 36.6144 | -121.8237 | No | Overcast;32-90 F | Jumper | Burned Open | 23-0068206 | OH | Sus | 45749462 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1840857 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315561020257 | 20230504 | 2342 | 20230505 | 948 | 2105159 | 606 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 4848 | 37.0464 | -122.022 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0068535 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1840992 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 56257 | 20230505 | 752 | 20230505 | 845 | 2105329 | 53 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 689 | 36.5984 | -121.893 | No | Overcast;32-90 F |  |  | 23-0068628 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1841075 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | TRANSFORMER | 411647447374 | 20230505 | 949 | 20230505 | 1051 | 2105408 | 62 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 62 | 36.6004 | -121.8475 | No | Partly Cloudy-Drizzle;32-90 F | Fuse | Failed/Faulted | 23-0068709 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1841146 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 456903 | 20230505 | 1127 | 20230505 | 2145 | 2105441 | 618 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 4326 | 37.1179 | -121.9643 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0068711 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1841147 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 12731 | 20230505 | 1440 | 20230506 | 1128 | 2105681 | 1248 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1248 | 36.8825 | -121.6974 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0068960 | OH | Sus | 45750829 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1841206 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRANSFORMER | 315412821528 | 20230506 | 207 | 20230506 | 1426 | 2105931 | 739 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 5173 | 37.0806 | -122.0731 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0069107 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1841288 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | FUSE | 25633 | 20230506 | 727 | 20230506 | 1013 | 2105986 | 166 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 5644 | 36.6556 | -121.686 | No | Overcast;32-90 F |  |  | 23-0069143 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1841344 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | TRANSFORMER | 315677717640 | 20230506 | 953 | 20230506 | 1715 | 2106074 | 442 | Transformer only | Equipment Failure/Involved | Overhead | 27 | 11934 | 36.9749 | -121.9796 | No | Overcast;32-90 F | Transformer (OH) | Broken | 23-0069157 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1841358 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | RECLOSER | 22426 | 20230506 | 1037 | 20230506 | 1750 | 2106110 | 430 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2268 | 223619 | 36.7339 | -121.6791 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 23-0069146 | OH | Sus | 31644453 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1841347 | 0 | EPSS Ckt | N | 2023 | C-GRD
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | OCB | 1101/2 | 20230506 | 1643 | 20230507 | 735 | 2106356 | 892 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2224 | 149624 | 36.8001 | -121.769 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0069207 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1841399 | 0 | EPSS Ckt | N | 2023 | C-GRD
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | FUSE | 72277 | 20230506 | 2312 | 20230507 | 634 | 2106482 | 442 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 1768 | 36.6934 | -121.5699 | No | Overcast;32-90 F |  |  | 23-0069265 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1841454 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1105 | 182031105 | OCB | 1105/2 | 20230507 | 507 | 20230507 | 554 | 2106510 | 47 | Distribution Circuit | Company Initiated | Coordination failure | 2892 | 64403 | 36.217 | -121.1269 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Normal | 23-0069263 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | None | 0 | No | No | No | 1841451 | 0 | Non-EPSS | N | 2023 | UNKWN
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 76091 | 20230507 | 750 | 20230507 | 826 | 2106632 | 36 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 468 | 36.7774 | -121.6582 | No | Clear;32-90 F |  |  | 23-0069278 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1841476 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | OCB | 2104/2 | 20230507 | 1528 | 20230507 | 1730 | 2106829 | 122 | Distribution Circuit | 3rd Party | Vehicle | 6469 | 560698 | 36.9926 | -121.9822 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0069304 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1841500 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 1907 | 20230507 | 1902 | 20230507 | 2032 | 2106929 | 90 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1080 | 37.0973 | -121.9748 | No | Clear;32-90 F |  |  | 23-0069332 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1841525 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315708622060 | 20230508 | 521 | 20230508 | 1153 | 2107037 | 392 | Transformer only | Animal | Squirrel | 1 | 392 | 37.0965 | -121.9724 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0069529 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1841718 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | RECLOSER | 3032 | 20230508 | 1238 | 20230508 | 1352 | 2107564 | 74 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 109 | 8066 | 36.634 | -121.6988 | No | Clear;32-90 F |  |  | 23-0069558 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1841731 | 0 | EPSS Ckt | N | 2023 | SGF
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0424 | 182440424 | TRANSFORMER | 411425648572 | 20230508 | 1252 | 20230508 | 1348 | 2107578 | 56 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 560 | 36.6315 | -121.9243 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0069609 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1841747 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1103 | 182201103 | OCB | 1103/2 | 20230508 | 1301 | 20230508 | 1347 | 2107585 | 46 | Distribution Circuit | Equipment Failure/Involved | Overhead | 128 | 5888 | 36.6139 | -121.5667 | No | Clear;32-90 F | Regulator | Failed/Faulted | 23-0069575 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1841739 | 0 | Non-EPSS | N | 2023 | C-GRD
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 6033 | 20230509 | 757 | 20230509 | 1700 | 2108297 | 543 | Distribution Circuit | Equipment Failure/Involved | Overhead | 82 | 17472 | 37.081 | -122.0049 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0069904 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1841985 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | SWITCH | 2459 | 20230509 | 945 | 20230510 | 251 | 2108433 | 1026 | Distribution Circuit | 3rd Party | Vehicle | 459 | 39503 | 36.9302 | -121.8573 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0069892 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1841971 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | TRANSFORMER | 413342637475 | 20230509 | 1001 | 20230509 | 1014 | 2108256 | 13 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 13 | 36.3411 | -121.2613 | No | Overcast;32-90 F | Connector or Splice (OH) | Burned/flashed | 23-0069917 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1841990 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | TRANSFORMER | 411476146743 | 20230509 | 1009 | 20230509 | 1306 | 2108537 | 177 | Transformer only | Vegetation | Tree - branch fell on line | 5 | 885 | 36.5816 | -121.9051 | No | Partly Cloudy;32-90 F | Secondary | Bent or Twisted | 23-0069928 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1841996 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 5090 | 20230509 | 1216 | 20230509 | 1238 | 2108477 | 22 | Distribution Circuit | Equipment Failure/Involved | Overhead | 434 | 9548 | 36.9804 | -121.892 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0069993 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1842024 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | KING CITY | SAN ARDO-1101 | 182191101 | FUSE | 9073 | 20230509 | 1301 | 20230509 | 1358 | 2108691 | 57 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 627 | 36.0841 | -120.9783 | No | Overcast;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0070015 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1842030 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRANSFORMER | 315398020527 | 20230509 | 1435 | 20230509 | 1848 | 2108775 | 253 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 2783 | 37.0529 | -122.0779 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0070110 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1842053 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 8073 | 20230509 | 1723 | 20230509 | 2247 | 2109028 | 324 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 8424 | 36.934 | -121.8613 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0070192 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | None | 0 | No | No | No | 1842087 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 67520 | 20230509 | 2046 | 20230510 | 1210 | 2109005 | 924 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3731 | 60135 | 36.9577 | -121.8525 | No | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0070189 | OH | Sus | 31644578 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1842084 | 0 | EPSS Ckt | N | 2023 | C GRD
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | JUMPER | OJ 1 W/OF 5597 | 20230509 | 2109 | 20230510 | 428 | 2109008 | 439 | Distribution Circuit | Equipment Failure/Involved | Overhead | 104 | 45656 | 36.7817 | -121.7207 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 23-0070236 | OH | Sus | 45753952 | SOUTH BAY AND CENTRAL COAST | MAY | Open Circuit | 0 | No | No | No | 1842126 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | TRANSFORMER | 412741044488 | 20230510 | 1217 | 20230510 | 1852 | 2109475 | 395 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 395 | 36.5312 | -121.472 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0070466 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1842336 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | TRANSFORMER | 412273047073 | 20230510 | 1340 | 20230510 | 2246 | 2109624 | 546 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 3822 | 36.5973 | -121.6336 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0070528 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1842343 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 412086351773 | 20230511 | 854 | 20230511 | 1049 | 2110131 | 115 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 345 | 36.7251 | -121.7023 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0070877 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1842568 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 1665 | 20230511 | 940 | 20230511 | 1145 | 2110244 | 125 | Distribution Circuit | 3rd Party | Vehicle | 2 | 250 | 36.903 | -121.7707 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 23-0070903 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1842578 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0423 | 182440423 | TRANSFORMER | 411436848186 | 20230511 | 1555 | 20230511 | 1709 | 2110556 | 74 | Transformer only | Equipment Failure/Involved | Overhead | 34 | 2516 | 36.6209 | -121.9202 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0071097 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1842637 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 2635 | 20230511 | 1912 | 20230511 | 2331 | 2110673 | 259 | Distribution Circuit | Equipment Failure/Involved | Underground | 206 | 53084 | 36.5863 | -121.8303 | No | Overcast;32-90 F | Conductor- Underground | Broken | 23-0071136 | UG | Sus | 31645140 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1842668 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1102 | 182031102 | TRANSFORMER | 413778533655 | 20230512 | 658 | 20230512 | 905 | 2110869 | 127 | Transformer only | 3rd Party | Other | 3 | 381 | 36.2383 | -121.1106 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0071277 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1842827 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | TRANSFORMER | 413270036650 | 20230512 | 725 | 20230512 | 1001 | 2110880 | 156 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 312 | 36.3171 | -121.2854 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0071316 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1842869 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | TRANSFORMER | 412775743770 | 20230512 | 849 | 20230512 | 1012 | 2111038 | 83 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 83 | 36.5102 | -121.4585 | No | Overcast;32-90 F | Fuse | Broken | 23-0071339 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1842877 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | TRANSFORMER | 412814734071 | 20230512 | 1003 | 20230512 | 1449 | 2111152 | 286 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 286 | 36.2434 | -121.4382 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0071355 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1842881 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | TRANSFORMER | 413766522570 | 20230512 | 1011 | 20230512 | 1251 | 2111170 | 160 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 160 | 35.9344 | -121.1065 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0071388 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1842898 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | TRANSFORMER | 412133053570 | 20230512 | 1338 | 20230512 | 1715 | 2111277 | 217 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 434 | 36.7749 | -121.6876 | No | Clear;32-90 F | Transformer (OH) |  | 23-0071410 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1842904 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | TRANSFORMER | 411927343579 | 20230512 | 1638 | 20230513 | 1100 | 2111306 | 1102 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 3306 | 36.499 | -121.7478 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0071482 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1842925 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 59429 | 20230512 | 2146 | 20230512 | 2239 | 2111556 | 53 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 159 | 36.5928 | -121.8772 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0071525 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1842964 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 11087 | 20230512 | 2203 | 20230513 | 730 | 2111553 | 567 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 11235 | 37.0885 | -122.0847 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0071527 | OH | Sus | 35445033 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1842967 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 8429 | 20230513 | 623 | 20230513 | 1010 | 2111612 | 227 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 908 | 37.1092 | -122.0598 | No | Clear;32-90 F | Conductor- Overhead | On Ground | 23-0071537 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Three Phase Fault | 0 | No | Yes | No | 1842979 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | TRANSFORMER | 413326836430 | 20230514 | 145 | 20230514 | 1249 | 2112024 | 664 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 3984 | 36.3129 | -121.2655 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0071624 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1843078 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 9035 | 20230514 | 833 | 20230514 | 1806 | 2112091 | 573 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 8595 | 37.0715 | -122.0745 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0071643 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1843099 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 12731 | 20230514 | 1331 | 20230514 | 2010 | 2112176 | 399 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 399 | 36.8825 | -121.6974 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0071676 | OH | Sus | 45761706 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1843119 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 36988 | 20230514 | 2026 | 20230515 | 25 | 2112366 | 239 | Distribution Circuit | Equipment Failure/Involved | Underground | 113 | 17128 | 36.6084 | -121.9227 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0071698 | UG | Sus | 31645481 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1843147 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | TRANSFORMER | 23707 | 20230514 | 2140 | 20230515 | 903 | 2112360 | 803 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 2953 | 36.702 | -121.6753 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0071700 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1843150 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | BORONDA-1101 | 182461101 | TRANSFORMER | 412162850924 | 20230514 | 2317 | 20230515 | 636 | 2112408 | 439 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 878 | 36.702 | -121.6751 | No | Overcast;32-90 F | Transformer | Failed/Faulted | 23-0071730 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1843181 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | FUSE | 6615 | 20230515 | 930 | 20230515 | 1300 | 2112602 | 210 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 420 | 36.4472 | -121.7146 | No | Clear;32-90 F |  |  | 23-0071875 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1843312 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | TRANSFORMER | 413036255087 | 20230515 | 938 | 20230515 | 1108 | 2112610 | 90 | Transformer only | Animal | Squirrel | 1 | 90 | 36.8228 | -121.3805 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0071856 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1843301 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | TRANSFORMER | 411366347366 | 20230515 | 1013 | 20230515 | 1516 | 2112566 | 303 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 1818 | 36.5978 | -121.9431 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0071819 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1843276 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | FUSE | 9427 | 20230515 | 1015 | 20230515 | 1034 | 2112866 | 19 | Distribution Circuit | 3rd Party | Vehicle | 1 | 19 | 36.3288 | -121.221 | No | Partly Cloudy;32-90 F | Anchor or Guy | Broken | 23-0071818 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1843275 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | TRANSFORMER | 412823359346 | 20230515 | 1537 | 20230515 | 1612 | 2113284 | 35 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 70 | 36.9385 | -121.4569 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0072060 | OH | Sus | 45763312 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1843399 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1104 | 182201104 | TRANSFORMER | 412716346741 | 20230515 | 1636 | 20230515 | 2331 | 2113408 | 415 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 415 | 36.5915 | -121.4819 | No | Clear;32-90 F | Transformer | Leaking | 23-0072068 | OH | Sus | 35447143 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1843404 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 3811 | 20230516 | 1236 | 20230516 | 1714 | 2114178 | 278 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 555 | 36.9047 | -121.6453 | No | Clear;32-90 F |  |  | 23-0072454 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1843677 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | TRANSFORMER | 412823359346 | 20230516 | 1600 | 20230516 | 1635 | 2114336 | 35 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 70 | 36.9386 | -121.4569 | No | Clear;32-90 F |  |  | 23-0072449 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1843675 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | FUSE | 11589 | 20230516 | 1703 | 20230516 | 1804 | 2114367 | 61 | Distribution Circuit | 3rd Party | Metallic Balloon | 182 | 11102 | 36.9637 | -121.9706 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0072463 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1843679 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 9609 | 20230516 | 1834 | 20230516 | 1940 | 2114426 | 66 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 2178 | 36.8938 | -121.3538 | No | Clear;32-90 F |  |  | 23-0072476 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1843696 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316420315727 | 20230516 | 1929 | 20230517 | 228 | 2114273 | 419 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 419 | 36.9251 | -121.7249 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0072475 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1843695 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 6897 | 20230517 | 138 | 20230517 | 319 | 2114580 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 65 | 6565 | 36.8561 | -121.7958 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0072522 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1843748 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | RECLOSER | 855412 | 20230517 | 939 | 20230517 | 1040 | 2114869 | 61 | Distribution Circuit | Animal | Other | 103 | 5144 | 36.9523 | -121.4743 | No | Clear;32-90 F | Jumper | Burned Open | 23-0072632 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1843912 | 0 | EPSS Ckt | N | 2023 | AB GRD
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 10157 | 20230517 | 1146 | 20230517 | 1341 | 2115015 | 115 | Distribution Circuit | Animal | Bird found | 5 | 575 | 36.9832 | -121.947 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 23-0072759 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1843974 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | SWITCH | 6527 | 20230517 | 1153 | 20230517 | 1200 | 2115017 | 7 | Distribution Circuit | Company Initiated | Return Circuit Normal | 27 | 189 | 37.0045 | -121.7688 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0066398 | OH | Sus | 45745387 | SOUTH BAY AND CENTRAL COAST | MAY | None | 0 | No | No | No | 1843951 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | RECLOSER | 2020 | 20230517 | 1506 | 20230518 | 352 | 2115166 | 766 | Distribution Circuit | Equipment Failure/Involved | Overhead | 834 | 152350 | 36.4632 | -121.7119 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0072802 | OH | Sus | 31645754 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1843988 | 0 | EPSS Ckt | N | 2023 | SGF
CENTRAL COAST | SALINAS | DOLAN ROAD-1104 | 182381104 | OCB | 1104/2 | 20230518 | 10 | 20230518 | 1403 | 2115499 | 791 | Distribution Circuit | Equipment Failure/Involved | Overhead | 260 | 58895 | 36.8001 | -121.7691 | No | Overcast-Fog;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0072929 | OH | Sus | 31645903 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1844058 | 0 | Non-EPSS | N | 2023 | B-GRD
CENTRAL COAST | COAST | PAUL SWEET-2108 | 83252108 | TRANSFORMER | 315596017677 | 20230518 | 104 | 20230518 | 922 | 2115502 | 498 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 3984 | 36.9757 | -122.0088 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0072938 | OH | Sus | 35447762 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1844066 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 2355 | 20230518 | 347 | 20230518 | 1534 | 2115516 | 707 | Distribution Circuit | Equipment Failure/Involved | Underground | 23 | 5681 | 36.5906 | -121.9471 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0072950 | UG | Sus | 45766683 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1844073 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1109 | 182011109 | FUSE | 23277 | 20230518 | 721 | 20230518 | 1600 | 2115552 | 519 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 2076 | 36.6613 | -121.5911 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0073038 | OH | Sus | 45767608 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1844165 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 58573 | 20230518 | 900 | 20230518 | 1405 | 2115665 | 305 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 3458 | 36.8133 | -121.6882 | No | Clear;32-90 F |  |  | 23-0073184 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1844238 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 10205 | 20230518 | 907 | 20230518 | 958 | 2115672 | 51 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 255 | 36.5246 | -121.8127 | No | Partly Cloudy;32-90 F |  |  | 23-0073045 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1844169 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | OILFIELDS-1103 | 182391103 | FUSE | 9827 | 20230518 | 1345 | 20230518 | 1831 | 2116091 | 286 | Distribution Circuit | 3rd Party | Customer Equipment | 3 | 858 | 35.8843 | -120.9556 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0073158 | OH | Sus | 31645945 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1844229 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 12549 | 20230518 | 1359 | 20230518 | 1457 | 2116226 | 58 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 290 | 36.938 | -121.7522 | No | Clear;32-90 F |  |  | 23-0073191 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1844242 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | TRANSFORMER | 412993456797 | 20230518 | 1808 | 20230518 | 2308 | 2116393 | 300 | Transformer only | 3rd Party | Vehicle | 2 | 600 | 36.8691 | -121.3961 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0073256 | OH | Sus | 31645799 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1844272 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 5188 | 20230519 | 1955 | 20230520 | 802 | 2117332 | 708 | Distribution Circuit | 3rd Party | Vehicle | 20 | 14160 | 37.0757 | -122.0568 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0073734 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | Yes | 1844559 | 0 | EPSS Ckt | N | 2023 | C-GRD
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 9659 | 20230520 | 809 | 20230520 | 902 | 2117493 | 53 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 43 | 2279 | 36.9746 | -122.0591 | No | Partly Cloudy;32-90 F |  |  | 23-0073811 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1844649 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 71630 | 20230520 | 1058 | 20230521 | 118 | 2117582 | 860 | Distribution Circuit | Vegetation | Tree - fell into line | 619 | 41368 | 36.9761 | -121.8948 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0073824 | OH | Sus | 31646140 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1844674 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | TRIP-SAVER | 5401 | 20230520 | 1306 | 20230521 | 1420 | 2117653 | 1514 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 40836 | 37.0647 | -122.1232 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0073859 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1844706 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 4459 | 20230520 | 1416 | 20230520 | 1553 | 2117694 | 97 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 8 | 776 | 36.8107 | -121.6565 | No | Clear;32-90 F |  |  | 23-0073871 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1844711 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | SWITCH | 6054 | 20230520 | 2003 | 20230520 | 2227 | 2117803 | 144 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 1 | 144 | 36.5859 | -121.8299 | No | Overcast;32-90 F | Conductor- Underground | Broken | 23-0073892 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1844724 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | BORONDA-1102 | 182461102 | TRANSFORMER | 412100750738 | 20230520 | 2045 | 20230521 | 1220 | 2117805 | 935 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 935 | 36.6966 | -121.6961 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0073910 | OH | Sus | 35448285 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1844728 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | FUSE | 4207 | 20230521 | 654 | 20230521 | 833 | 2117905 | 99 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 693 | 36.4669 | -121.4287 | No | Overcast;32-90 F |  |  | 23-0073956 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1844782 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | LAURELES-1111 | 182371111 | TRANSFORMER | 411975045397 | 20230521 | 2018 | 20230522 | 51 | 2118169 | 273 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 273 | 36.5486 | -121.7333 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0074016 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1844844 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 2651 | 20230522 | 717 | 20230523 | 1425 | 2118308 | 1868 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3736 | 37.0145 | -121.8146 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0074184 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1845049 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1102 | 182201102 | TRANSFORMER | 412594748449 | 20230522 | 956 | 20230522 | 1715 | 2118628 | 439 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 439 | 36.637 | -121.5257 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 23-0074155 | OH | Sus | 31646204 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1845038 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRANSFORMER | 315256823140 | 20230522 | 1439 | 20230522 | 1935 | 2118905 | 296 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 2960 | 37.1248 | -122.126 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0074327 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1845099 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 12401 | 20230522 | 1923 | 20230522 | 2109 | 2119108 | 106 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 107 | 11342 | 36.9726 | -121.765 | No | Overcast;32-90 F |  |  | 23-0074417 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1845140 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | FUSE | 5557 | 20230523 | 609 | 20230523 | 725 | 2119334 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 37 | 2812 | 36.7876 | -121.5893 | No | Clear;32-90 F |  |  | 23-0074486 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1845184 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | TRANSFORMER | 315739817578 | 20230523 | 1114 | 20230523 | 1501 | 2119553 | 227 | Transformer only | Animal | Squirrel | 8 | 1816 | 36.9732 | -121.9586 | No | Overcast;32-90 F | Transformer | Broken- wire on object | 23-0074660 | OH | Sus | 45771681 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1845356 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 6875 | 20230523 | 1235 | 20230523 | 1402 | 2119804 | 87 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 102 | 8874 | 36.8864 | -121.6325 | No | Overcast;32-90 F |  |  | 23-0074752 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1845390 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 9647 | 20230524 | 1235 | 20230524 | 1250 | 2120610 | 15 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 30 | 36.8762 | -121.756 | No | Overcast;32-90 F |  |  | 23-0075158 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1845668 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 6891 | 20230524 | 1415 | 20230524 | 1505 | 2120676 | 50 | Distribution Circuit | Animal | Other | 4 | 200 | 36.8847 | -121.7956 | No | Overcast;32-90 F | Crossarm- Wood | Normal | 23-0075196 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1845680 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | SOQUEL-0402 | 83300402 | TRANSFORMER | 315760517884 | 20230524 | 1642 | 20230524 | 1802 | 2120764 | 80 | Transformer only | Equipment Failure/Involved | Overhead | 26 | 2080 | 36.9819 | -121.9524 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0075270 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1845698 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | RECLOSER | 88772 | 20230525 | 6 | 20230525 | 1025 | 2120924 | 619 | Distribution Circuit | 3rd Party | Vehicle | 1255 | 146577 | 36.904 | -121.6085 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0075344 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Three Phase Fault | 0 | No | No | No | 1845733 | 0 | EPSS Ckt | N | 2023 | A-B-C
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411875151854 | 20230525 | 1421 | 20230526 | 1147 | 2121293 | 1286 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 1286 | 36.7263 | -121.7734 | No | Overcast;32-90 F | Transformer | Failed/Faulted | 23-0075651 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1845939 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | FUSE | 23365 | 20230525 | 1930 | 20230525 | 2153 | 2121589 | 143 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 715 | 36.5575 | -121.7337 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0075741 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1845971 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 9927 | 20230526 | 552 | 20230526 | 1024 | 2121852 | 272 | Distribution Circuit | Equipment Failure/Involved | Overhead | 341 | 92752 | 36.8692 | -121.8163 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0075833 | OH | Sus | 45777142 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | Yes | No | 1846054 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 412019049896 | 20230526 | 937 | 20230526 | 1003 | 2121970 | 26 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 26 | 36.6724 | -121.7231 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0075958 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846152 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 24721 | 20230526 | 1538 | 20230526 | 2155 | 2122300 | 377 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 7917 | 36.8075 | -121.6624 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0076196 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | Yes | No | 1846230 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 6085 | 20230526 | 1657 | 20230526 | 1808 | 2122352 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 781 | 37.0636 | -122.0348 | No | Clear;32-90 F |  |  | 23-0076221 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1846240 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 6343 | 20230527 | 41 | 20230527 | 1249 | 2122446 | 728 | Distribution Circuit | 3rd Party | Vehicle | 18 | 13104 | 37.2222 | -122.1451 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0076257 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | Yes | No | 1846276 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-1101 | 182221101 | FUSE | 8655 | 20230527 | 209 | 20230527 | 1227 | 2122454 | 618 | Distribution Circuit | Equipment Failure/Involved | Underground | 786 | 36414 | 36.6091 | -121.8307 | No | Overcast;32-90 F | Conductor- Underground | Broken | 23-0076276 | UG | Sus | 45785687 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846292 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2102 | 182222102 | FUSE | 10755 | 20230527 | 306 | 20230527 | 643 | 2122460 | 217 | Distribution Circuit | 3rd Party | Metallic Balloon | 41 | 8897 | 36.6131 | -121.8383 | No | Overcast;32-90 F | Transformer (OH) | Normal | 23-0076268 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846287 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | RECLOSER | 2014 | 20230527 | 336 | 20230527 | 532 | 2122465 | 116 | Distribution Circuit | 3rd Party | Vehicle | 123 | 14268 | 36.5776 | -121.9523 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0076260 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1846280 | 0 | EPSS Ckt | N | 2023 | BC
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 10726 | 20230527 | 1607 | 20230528 | 5 | 2122768 | 478 | Distribution Circuit | 3rd Party | Vehicle | 234 | 9890 | 37.061 | -122.1493 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0076293 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1846350 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | OTHER | WIRE BROKEN | 20230527 | 1706 | 20230527 | 2114 | 2122790 | 248 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1488 | 36.9996 | -121.8637 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0076355 | OH | Sus | 45789702 | SOUTH BAY AND CENTRAL COAST | MAY | Open Circuit | 0 | No | Yes | No | 1846358 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | RECLOSER | 3277 | 20230528 | 133 | 20230528 | 1410 | 2122890 | 733 | Distribution Circuit | 3rd Party | Vehicle | 99 | 20409 | 36.6751 | -121.7023 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 23-0076395 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1846391 | 0 | EPSS Ckt | N | 2023 | A PH
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | RECLOSER | 10788 | 20230528 | 411 | 20230528 | 841 | 2122900 | 270 | Distribution Circuit | Equipment Failure/Involved | Overhead | 886 | 96977 | 36.9044 | -121.7438 | No | Overcast-Fog;32-90 F | Woodpin | Broken | 23-0076399 | OH | Sus | 45791462 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1846393 | 0 | EPSS Ckt | N | 2023 | B & C PH
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | RECLOSER | 7082 | 20230528 | 702 | 20230528 | 713 | 2122919 | 11 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 676 | 7436 | 36.2872 | -121.2483 | No | Partly Cloudy;32-90 F |  |  | 23-0076405 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1846398 | 0 | EPSS Ckt | N | 2023 | A & C PHASE
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 6469 | 20230528 | 735 | 20230528 | 957 | 2122929 | 142 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 994 | 36.5315 | -121.8354 | No | Overcast;32-90 F |  |  | 23-0076427 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846413 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 670217 | 20230528 | 828 | 20230528 | 1013 | 2122953 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 5880 | 37.1578 | -122.166 | No | Clear;32-90 F |  |  | 23-0076430 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846417 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | FUSE | 4211 | 20230528 | 932 | 20230528 | 1150 | 2122975 | 138 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 4278 | 36.9688 | -121.4325 | No | Overcast;32-90 F |  |  | 23-0076441 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1846424 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411932853409 | 20230528 | 1044 | 20230528 | 1425 | 2123003 | 221 | Transformer only | Unknown Cause | Patrol - found nothing | 12 | 2652 | 36.7691 | -121.7555 | No | Overcast;32-90 F |  |  | 23-0076445 | OH | Sus | 45791465 | SOUTH BAY AND CENTRAL COAST | MAY | None | 0 | No | No | No | 1846426 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2103 | 83252103 | FUSE | 8067 | 20230528 | 1231 | 20230528 | 1348 | 2123032 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 162 | 12474 | 36.9814 | -122.0135 | No | Overcast;32-90 F |  |  | 23-0076452 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846432 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | RECLOSER | 2026 | 20230528 | 1411 | 20230529 | 608 | 2123072 | 957 | Distribution Circuit | 3rd Party | Vehicle | 1290 | 36558 | 36.5315 | -121.8375 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 23-0076459 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1846437 | 0 | EPSS Ckt | N | 2023 | SGF
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 7371 | 20230528 | 1613 | 20230528 | 1828 | 2123128 | 135 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 810 | 37.0585 | -122.142 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0076483 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1846452 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | JUMPER | BURNED OPEN JPR | 20230528 | 1915 | 20230528 | 2037 | 2123196 | 82 | Distribution Circuit | Equipment Failure/Involved | Overhead | 239 | 9009 | 36.9593 | -121.4304 | No | Clear;32-90 F | Jumper | Burned Open | 23-0076486 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Open Circuit | 0 | No | No | No | 1846458 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | FUSE | 865 | 20230529 | 538 | 20230529 | 655 | 2123327 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 308 | 36.9841 | -121.9658 | No | Overcast;32-90 F |  |  | 23-0076523 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846491 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 11465 | 20230529 | 748 | 20230529 | 933 | 2123350 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 840 | 36.8621 | -121.7526 | No | Clear;32-90 F |  |  | 23-0076549 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1846511 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 5749 | 20230529 | 1110 | 20230529 | 1303 | 2123421 | 113 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 6 | 678 | 37.0001 | -122.0375 | No | Partly Cloudy;32-90 F |  |  | 23-0076581 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846533 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411918853583 | 20230529 | 1124 | 20230530 | 206 | 2123431 | 882 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 882 | 36.7733 | -121.7606 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0076586 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846537 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 79469 | 20230529 | 1316 | 20230529 | 1457 | 2123489 | 101 | Distribution Circuit | 3rd Party | Metallic Balloon | 232 | 19832 | 36.7675 | -121.7532 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0076590 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846539 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | TRANSFORMER | 412892560200 | 20230530 | 927 | 20230530 | 1846 | 2123889 | 559 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 559 | 36.9623 | -121.4339 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0076780 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846743 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 316090815347 | 20230530 | 953 | 20230531 | 219 | 2124422 | 986 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 5916 | 36.9138 | -121.8382 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0077053 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846861 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | FUSE | 4507 | 20230530 | 1029 | 20230530 | 1856 | 2123718 | 507 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1521 | 36.7423 | -121.7394 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 23-0076765 | OH | Sus | 31650402 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1846742 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | JUMPER | 9049 HIGH SIDE OPEN JPR | 20230530 | 1044 | 20230530 | 1354 | 2123967 | 190 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 190 | 36.2997 | -121.3021 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 23-0076790 | OH | Sus | 45804960 | SOUTH BAY AND CENTRAL COAST | MAY | Open Circuit | 0 | No | No | No | 1846745 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | TRANSFORMER | 411527147111 | 20230530 | 1302 | 20230531 | 221 | 2124096 | 799 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 3196 | 36.5922 | -121.8882 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0076876 | OH | Sus | 31650467 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846787 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SOLEDAD-2102 | 182052102 | TRANSFORMER | 413007839036 | 20230530 | 1638 | 20230530 | 1839 | 2124231 | 121 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 121 | 36.3811 | -121.3757 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0076974 | OH | Sus | 45804992 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846819 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | TRANSFORMER | 412392652013 | 20230530 | 1715 | 20230531 | 355 | 2124293 | 640 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 2560 | 36.7344 | -121.5983 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0077009 | OH | Sus | 35450063 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846828 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SOLEDAD-2102 | 182052102 | TRANSFORMER | 413007839036 | 20230531 | 1057 | 20230531 | 1247 | 2124765 | 110 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 110 | 36.3811 | -121.3757 | No | Partly Cloudy;32-90 F |  |  | 23-0077292 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | None | 0 | No | No | No | 1847051 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 762931 | 20230531 | 1445 | 20230531 | 1526 | 2124919 | 41 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 123 | 36.9689 | -121.3747 | No | Clear;32-90 F |  |  | 23-0077388 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1847072 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | FUSE | 9921 | 20230531 | 1647 | 20230531 | 1728 | 2125005 | 41 | Distribution Circuit | 3rd Party | Metallic Balloon | 51 | 2091 | 36.3155 | -121.2449 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 23-0077444 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1847090 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | SWITCH | 8681BP | 20230531 | 1807 | 20230531 | 1949 | 2125090 | 102 | Distribution Circuit | Vegetation | Tree - fell into line | 211 | 21522 | 37.019 | -121.9932 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0077490 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1847101 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | JUMPER | FB 1 P/LD OF CGC 315438920007 | 20230531 | 1951 | 20230601 | 1055 | 2125101 | 904 | Distribution Circuit | Vegetation | Tree - grew into line | 6 | 5424 | 37.039 | -122.0638 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Annealed | 23-0077493 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1847102 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8345 | 20230531 | 2239 | 20230601 | 33 | 2125146 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1368 | 37.0568 | -121.9682 | No | Clear;32-90 F |  |  | 23-0077570 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1847138 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8345 | 20230601 | 226 | 20230601 | 1420 | 2125185 | 714 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 8568 | 37.0568 | -121.9682 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0077580 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | No | 1847146 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 5337 | 20230601 | 1131 | 20230601 | 1204 | 2126636 | 33 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 99 | 37.0341 | -121.9867 | No | Overcast;32-90 F | Other | Broken | 23-0077736 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1847288 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2102 | 182222102 | TRANSFORMER | T1896 | 20230601 | 2132 | 20230602 | 241 | 2126956 | 309 | Distribution Circuit | Equipment Failure/Involved | Underground | 21 | 489 | 36.6169 | -121.8423 | No | Overcast;32-90 F | Transformer (UG) | Failed/Faulted | 23-0078031 | UG | Sus | 35450614 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1847388 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2102 | 182222102 | TRANSFORMER | 411643247920 | 20230602 | 32 | 20230602 | 346 | 2127005 | 194 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 1552 | 36.6153 | -121.8491 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0078059 | OH | Sus | 35451349 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1847410 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2102 | 182222102 | FUSE | 9064 | 20230602 | 507 | 20230602 | 901 | 2127043 | 234 | Distribution Circuit | Equipment Failure/Involved | Overhead | 552 | 129168 | 36.6043 | -121.8624 | No | Overcast;32-90 F | Insulator | Broken | 23-0078085 | OH | Sus | 31650799 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1847430 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | TRANSFORMER | 414008343185 | 20230602 | 857 | 20230602 | 903 | 2127193 | 6 | Transformer only | Animal | Bird found | 2 | 12 | 36.501 | -121.0394 | No | Partly Cloudy;32-90 F | Transformer | Burned Open | 23-0078154 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1847517 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 237 | 20230602 | 1254 | 20230602 | 1411 | 2127436 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 1256 | 36.944 | -121.7945 | No | Clear;32-90 F |  |  | 23-0078382 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1847594 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 316164718221 | 20230602 | 1259 | 20230602 | 1916 | 2127389 | 377 | Transformer only | Equipment Failure/Involved | Electrical Overload | 6 | 2262 | 36.9931 | -121.8142 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0078334 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1847584 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 4717 | 20230602 | 1710 | 20230602 | 1850 | 2127572 | 100 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 148 | 14800 | 36.9206 | -121.3709 | No | Clear;32-90 F |  |  | 23-0078462 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1847613 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 6975 | 20230602 | 1914 | 20230602 | 2045 | 2127625 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 50 | 4550 | 36.5797 | -121.9204 | No | Partly Cloudy;32-90 F |  |  | 23-0078470 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1847617 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO SUB | 18285 | OCB | 2100/2 | 20230602 | 2149 | 20230603 | 1521 | 2127671 | 1052 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5271 | 674002 | 36.5786 | -121.9085 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0078505 | OH | Sus | 31650918 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | No | 1847639 | 0 | Non-EPSS | N | 2023 | B GRD
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 1089 | 20230603 | 758 | 20230603 | 1623 | 2127786 | 505 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1010 | 36.9691 | -122.1169 | No | Overcast;32-90 F | Transformer (OH) | Deteriorated | 23-0078564 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1847704 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 2979 | 20230603 | 1203 | 20230603 | 1219 | 2127920 | 16 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 16 | 37.0366 | -122.1466 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0078587 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1847714 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 40579 | 20230603 | 1623 | 20230603 | 1746 | 2128016 | 83 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 144 | 11940 | 36.5627 | -121.9194 | No | Partly Cloudy;32-90 F |  |  | 23-0078619 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1847737 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 6559 | 20230603 | 1654 | 20230603 | 1808 | 2128049 | 74 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 2294 | 36.9267 | -121.7459 | No | Clear;32-90 F |  |  | 23-0078623 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1847739 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 9875 | 20230603 | 2228 | 20230604 | 810 | 2128185 | 582 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 6984 | 36.8601 | -121.7708 | No | Clear;32-90 F |  |  | 23-0078665 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1847773 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 897 | 20230604 | 549 | 20230604 | 1345 | 2128209 | 476 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 4760 | 36.8706 | -121.6202 | No | Overcast-Fog;32-90 F |  |  | 23-0078717 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1847820 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | TRANSFORMER | T1705 | 20230604 | 703 | 20230604 | 1655 | 2128309 | 592 | Distribution Circuit | Equipment Failure/Involved | Underground | 589 | 26305 | 36.5846 | -121.9035 | No | Overcast-Fog;32-90 F | Transformer (UG) | Failed/Faulted | 23-0078688 | UG | Sus | 35452843 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1847798 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | FUSE | 3699 | 20230604 | 742 | 20230604 | 923 | 2128322 | 101 | Distribution Circuit | Animal | Squirrel | 106 | 10706 | 36.9968 | -121.9371 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0078685 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1847791 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | TRANSFORMER | 411419545908 | 20230604 | 956 | 20230604 | 2312 | 2128381 | 796 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 6368 | 36.5582 | -121.9235 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0078700 | OH | Sus | 35452846 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1847809 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | TRANSFORMER | 411555447213 | 20230604 | 1701 | 20230605 | 331 | 2128484 | 630 | Transformer only | Equipment Failure/Involved | Overhead | 24 | 15120 | 36.5953 | -121.8785 | No | Partly Cloudy;32-90 F | Transformer | Burned/flashed | 23-0078734 | OH | Sus | 35452827 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1847832 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1109 | 182011109 | TRANSFORMER | 412321649847 | 20230605 | 1629 | 20230605 | 2135 | 2129474 | 306 | Transformer only | Equipment Failure/Involved | Overhead | 22 | 6732 | 36.6738 | -121.62 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0079079 | OH | Sus | 35454362 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848103 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6433 | 20230605 | 1817 | 20230605 | 1946 | 2129606 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 267 | 36.9662 | -121.7315 | No | Overcast;32-90 F |  |  | 23-0079110 | OH | Sus | 35454363 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848122 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | FUSE | 2325 | 20230605 | 1933 | 20230605 | 2015 | 2129667 | 42 | Distribution Circuit | Vegetation | Tree - branch fell on line | 157 | 6594 | 36.9663 | -121.9797 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0079121 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1848130 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | DEL MONTE-2104 | 182222104 | FUSE | 20461 | 20230606 | 550 | 20230606 | 717 | 2130173 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 935 | 36.5384 | -121.7252 | No | Clear;32-90 F |  |  | 23-0079218 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848211 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | TRANSFORMER | 412633544559 | 20230606 | 836 | 20230607 | 318 | 2131108 | 1122 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1122 | 36.5315 | -121.5084 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0079540 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | No | 1848461 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | TRANSFORMER | 413013154442 | 20230606 | 836 | 20230606 | 2007 | 2130304 | 691 | Transformer only | Animal | Other | 2 | 1382 | 36.8046 | -121.3874 | No | Overcast;32-90 F | Transformer (OH) | Burned/flashed | 23-0079287 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848335 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | FUSE | 23129 | 20230606 | 905 | 20230606 | 1005 | 2130324 | 60 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 280 | 36.5439 | -121.5146 | No | Clear;32-90 F |  |  | 23-0079309 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848359 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 50899 | 20230606 | 930 | 20230606 | 1207 | 2130459 | 157 | Distribution Circuit | Animal | Other | 8 | 1207 | 36.8323 | -121.3483 | No | Overcast;32-90 F | Fuse | Normal | 23-0079362 | OH | Sus | 45825306 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1848392 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | TRANSFORMER | 412503157742 | 20230606 | 1002 | 20230606 | 2248 | 2130491 | 766 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 766 | 36.8918 | -121.5649 | No | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0079403 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848413 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 23325 | 20230606 | 1006 | 20230606 | 1435 | 2130500 | 269 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 538 | 36.7889 | -121.7023 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0079343 | OH | Sus | 45825152 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | Yes | No | 1848384 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | RECLOSER | 10260 | 20230606 | 1019 | 20230606 | 1124 | 2130517 | 65 | Distribution Circuit | Vegetation | Tree - branch fell on line | 678 | 43629 | 36.9154 | -121.7787 | No | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0079313 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848367 | 0 | Non-EPSS | N | 2023 | C GRD TIME
CENTRAL COAST | KING CITY | LOS COCHES-1102 | 182151102 | FUSE | 2119 | 20230606 | 1052 | 20230606 | 1455 | 2130550 | 243 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 3645 | 36.3519 | -121.269 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0079357 | OH | Sus | 31651410 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1848389 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | FUSE | 9625 | 20230606 | 1214 | 20230606 | 1237 | 2130608 | 23 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 75 | 1725 | 36.8465 | -121.4036 | No | Overcast;32-90 F |  |  | 23-0079384 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848401 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SOLEDAD-2104 | 182052104 | FUSE | 1925 | 20230606 | 1225 | 20230606 | 2358 | 2130622 | 693 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 8316 | 36.4502 | -121.3712 | No | Overcast;32-90 F | Pole-Wood | Burned/flashed | 23-0079410 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1848417 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | TRANSFORMER | 412475354234 | 20230606 | 1419 | 20230606 | 1904 | 2130654 | 285 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 570 | 36.796 | -121.5736 | No | Clear;32-90 F | Customer Equipment | Failed/Faulted | 23-0079465 | OH | Sus | 45825273 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848434 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | RECLOSER | 2028 | 20230606 | 1434 | 20230606 | 1440 | 2131033 | 6 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 431 | 2586 | 36.4728 | -121.7175 | No | Clear;32-90 F |  |  | 23-0079467 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1848436 | 0 | EPSS Ckt | N | 2023 | AC-
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0424 | 182440424 | TRANSFORMER | 411424048670 | 20230606 | 1721 | 20230606 | 2050 | 2131076 | 209 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 627 | 36.6342 | -121.9249 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 23-0079546 | OH | Sus | 35454701 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848464 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | FUSE | 4617 | 20230607 | 723 | 20230607 | 849 | 2131570 | 86 | Distribution Circuit | Equipment Failure/Involved | Underground | 49 | 4214 | 36.831 | -121.3795 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0079705 | UG | Sus | 45828455 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848608 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412196754658 | 20230607 | 949 | 20230607 | 1645 | 2131756 | 416 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1248 | 36.8055 | -121.6672 | No | Partly Cloudy;32-90 F | Transformer (OH) | Deteriorated | 23-0079770 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848716 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1104 | 182201104 | TRANSFORMER | 412518546763 | 20230607 | 1042 | 20230607 | 1636 | 2131879 | 354 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 354 | 36.5909 | -121.5493 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0079822 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848745 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 7805 | 20230607 | 1120 | 20230607 | 1300 | 2131587 | 100 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 200 | 37.2144 | -122.1493 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0079690 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1848592 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | PANOCHE-1103 | 253671103 | TRANSFORMER | 414548346893 | 20230607 | 1343 | 20230607 | 1519 | 2132106 | 96 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 192 | 36.6078 | -120.8589 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 23-0080033 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1848819 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | OCB | 1110/2 | 20230607 | 1650 | 20230607 | 2029 | 2132110 | 219 | Distribution Circuit | 3rd Party | Metallic Balloon | 3743 | 158766 | 36.7848 | -121.671 | No | Clear;32-90 F | Bushing | Burned/flashed | 23-0080038 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Three Phase Fault | 0 | No | No | No | 1848820 | 0 | EPSS Ckt | N | 2023 | ABC
CENTRAL COAST | COAST | CASSERLY-0401 | 83110401 | FUSE | 5729 | 20230607 | 1957 | 20230607 | 2140 | 2132204 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 40 | 4150 | 36.9685 | -121.765 | No | Clear;32-90 F |  |  | 23-0080090 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848848 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 11837 | 20230608 | 459 | 20230608 | 723 | 2132292 | 144 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 47 | 6768 | 36.9273 | -121.8149 | No | Clear;32-90 F |  |  | 23-0080147 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1848893 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | FUSE | 4481 | 20230608 | 556 | 20230608 | 825 | 2132307 | 149 | Distribution Circuit | Animal | Bird found | 92 | 13708 | 36.9904 | -121.9319 | No | Partly Cloudy;32-90 F | Fuse | Normal | 23-0080186 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN |  | 0 | No | No | No | 1848945 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 3823 | 20230608 | 557 | 20230608 | 814 | 2132309 | 137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 73 | 10001 | 36.9736 | -121.727 | No | Clear;32-90 F |  |  | 23-0080159 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848899 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | TRANSFORMER | 412317551240 | 20230608 | 1004 | 20230608 | 1906 | 2132560 | 542 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 7201 | 36.7117 | -121.6227 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0080252 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1849036 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | TRANSFORMER | 412503157742 | 20230608 | 1141 | 20230608 | 1215 | 2132687 | 34 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 34 | 36.8918 | -121.5649 | No | Clear;32-90 F |  |  | 23-0080355 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1849083 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 11331 | 20230608 | 1222 | 20230608 | 1308 | 2132739 | 46 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 368 | 36.9866 | -121.8871 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0080386 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1849091 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SOLEDAD-2105 | 182052105 | TRANSFORMER | 413029642065 | 20230608 | 1232 | 20230608 | 1456 | 2132747 | 144 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 144 | 36.4664 | -121.3696 | No | Clear;32-90 F |  |  | 23-0080456 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1849106 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | FUSE | 5111 | 20230608 | 1633 | 20230609 | 412 | 2132976 | 699 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 6291 | 36.6754 | -121.678 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0080532 | OH | Sus | 45834293 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | No | 1849131 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | TRANSFORMER | 412140649799 | 20230608 | 2005 | 20230608 | 2108 | 2133092 | 63 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 189 | 36.671 | -121.6816 | No | Partly Cloudy;32-90 F | Insulator | Broken | 23-0080543 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1849145 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | RECLOSER | 989608 | 20230609 | 1116 | 20230609 | 2316 | 2133581 | 720 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 5760 | 36.6615 | -121.5473 | No | Overcast;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0080805 | OH | Sus | 31651694 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | Yes | Yes | 1849386 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | SALINAS | SALINAS-1108 | 182011108 | TRANSFORMER | 412243750102 | 20230609 | 1210 | 20230609 | 1437 | 2133624 | 147 | Transformer only | Equipment Failure/Involved | Overhead | 22 | 3234 | 36.6802 | -121.6467 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 23-0080849 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1849406 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 4915 | 20230609 | 1317 | 20230610 | 100 | 2133669 | 703 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 9487 | 37.1032 | -122.0458 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0080993 | OH | Sus | 31651819 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | No | 1849441 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | TRANSFORMER | 411815245721 | 20230609 | 1414 | 20230609 | 1730 | 2133718 | 196 | Transformer only | Animal | Squirrel | 8 | 1568 | 36.5562 | -121.7883 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 23-0081035 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1849454 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 3187 | 20230609 | 2129 | 20230609 | 2212 | 2134011 | 43 | Distribution Circuit | Animal | Bird found | 94 | 4042 | 36.967 | -122.0058 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0081061 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1849479 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | FUSE | 509805 | 20230610 | 819 | 20230610 | 1602 | 2134098 | 463 | Distribution Circuit | Vegetation | Tree - grew into line | 39 | 18057 | 37.107 | -122.1096 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0081104 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1849537 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | JUMPER | JMPRS 7 SOURCE SIDE OF CGC 315726323036 | 20230610 | 911 | 20230610 | 1144 | 2134170 | 153 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 306 | 37.1219 | -121.9649 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0081113 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1849573 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 9261 | 20230610 | 934 | 20230610 | 1107 | 2134180 | 93 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 13 | 1209 | 36.5579 | -121.8961 | No | Overcast-Drizzle;32-90 F |  |  | 23-0081124 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1849587 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 316034215862 | 20230610 | 1128 | 20230610 | 1243 | 2134104 | 72 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 216 | 36.9275 | -121.8578 | No | Overcast;32-90 F | Transformer (OH) | Deteriorated | 23-0081106 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1849545 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | RECLOSER | 944178 | 20230610 | 1601 | 20230610 | 1653 | 2134343 | 52 | Distribution Circuit | Vegetation | Tree - branch fell on line | 886 | 46072 | 37.0926 | -122.0964 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0081158 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Multi-Fault | 0 | No | No | No | 1849607 | 0 | EPSS Ckt | N | 2023 | BCGRD & TIME
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | TRANSFORMER | 316274916725 | 20230610 | 1900 | 20230611 | 934 | 2134391 | 874 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 4370 | 36.9523 | -121.7758 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0081181 | OH | Sus | 35457022 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1849626 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 593 | 20230610 | 2352 | 20230611 | 155 | 2134504 | 123 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 87 | 10701 | 36.8071 | -121.7199 | No | Clear;32-90 F |  |  | 23-0081237 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1849682 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | TRANSFORMER | 315756919247 | 20230611 | 1028 | 20230611 | 1056 | 2134603 | 28 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 28 | 37.0201 | -121.9546 | No | Overcast;32-90 F | Transformer (OH) | Leaking | 23-0081267 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1849712 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1107 | 182011107 | TRANSFORMER | 412231450103 | 20230611 | 1354 | 20230612 | 47 | 2134654 | 653 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1306 | 36.6802 | -121.6509 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0081317 | OH | Sus | 35457027 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1849735 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1102 | 182011102 | FUSE | 25655 | 20230611 | 1432 | 20230611 | 1536 | 2134666 | 64 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 118 | 7556 | 36.6859 | -121.6079 | No | Overcast;32-90 F |  |  | 23-0081313 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1849732 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | FUSE | 7671 | 20230612 | 811 | 20230612 | 2145 | 2135013 | 814 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 814 | 36.1987 | -121.2808 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0081581 | UG | Sus | 45844558 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1850027 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | FUSE | 9891 | 20230612 | 819 | 20230612 | 1044 | 2135032 | 145 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 2998 | 35.9295 | -121.082 | No | Clear;32-90 F |  |  | 23-0081497 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1849972 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | TRANSFORMER | 411476146743 | 20230612 | 1139 | 20230612 | 1424 | 2135307 | 165 | Transformer only | Vegetation | Tree - fell into line | 5 | 825 | 36.5816 | -121.9051 | No | Overcast;32-90 F | Secondary | Bent or Twisted | 23-0081586 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1850032 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 347 | 20230612 | 1150 | 20230612 | 1250 | 2135316 | 60 | Distribution Circuit | Animal | Squirrel | 30 | 1798 | 36.988 | -121.9426 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0081574 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1850022 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | TRANSFORMER | 315245424277 | 20230612 | 1615 | 20230612 | 1711 | 2135563 | 56 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 616 | 37.1556 | -122.13 | No | Partly Cloudy;32-90 F | Anchor or Guy | Broken | 23-0081663 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1850060 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | TRANSFORMER | 411397048007 | 20230612 | 1957 | 20230612 | 2028 | 2135655 | 31 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 62 | 36.6157 | -121.9336 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Arcing | 23-0081695 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1850078 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | TRANSFORMER | 412941060046 | 20230613 | 624 | 20230613 | 759 | 2135749 | 95 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 285 | 36.9579 | -121.4173 | No | Overcast;32-90 F |  |  | 23-0081774 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1850146 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS COCHES-1102 | 182151102 | FUSE | 8505 | 20230613 | 911 | 20230613 | 2321 | 2135984 | 850 | Distribution Circuit | 3rd Party | Vehicle | 16 | 13600 | 36.3756 | -121.2578 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0081826 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Multi-Fault | 0 | No | Yes | No | 1850273 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | FUSE | 7445 | 20230613 | 912 | 20230613 | 1012 | 2135954 | 60 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 45 | 2721 | 35.9657 | -121.0819 | No | Clear;32-90 F |  |  | 23-0081834 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1850280 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | FUSE | 12377 | 20230613 | 1107 | 20230613 | 1131 | 2136027 | 24 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 432 | 37.1052 | -122.1064 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0081870 | OH | Sus | 45846037 | SOUTH BAY AND CENTRAL COAST | JUN | Three Phase Fault | 0 | No | No | No | 1850301 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | TRANSFORMER | 411371643519 | 20230613 | 1115 | 20230613 | 1130 | 2136074 | 15 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 30 | 36.4922 | -121.9363 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0081862 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1850297 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | TRANSFORMER | 411472539165 | 20230614 | 1205 | 20230614 | 1827 | 2136961 | 382 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 382 | 36.3735 | -121.8975 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0082480 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1850691 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | RECLOSER | 3032 | 20230614 | 1448 | 20230614 | 1541 | 2137072 | 53 | Distribution Circuit | Company Initiated | Return Circuit Normal | 6 | 318 | 36.634 | -121.6988 | No | Clear;32-90 F | Switch (OH) | Broken | 23-0066832 | OH | Sus | 31517601 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1850649 | 0 | EPSS Ckt | N | 2023 | NA
CENTRAL COAST | SALINAS | SPENCE-1104 | 182201104 | FUSE | 4489 | 20230614 | 1454 | 20230614 | 2036 | 2137079 | 342 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1825 | 36.5827 | -121.4788 | No | Partly Cloudy;32-90 F | Anchor or Guy | Broken | 23-0082487 | OH | Sus | 45848001 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1850696 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 3477 | 20230615 | 902 | 20230616 | 230 | 2137554 | 1048 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 2096 | 36.9641 | -121.7651 | No | Overcast;32-90 F | Conductor- Underground | Broken | 23-0082691 | UG | Sus | 45849113 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1850837 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | FUSE | 8965 | 20230615 | 1108 | 20230615 | 1230 | 2137652 | 82 | Distribution Circuit | 3rd Party | Metallic Balloon | 72 | 5904 | 36.3175 | -121.2414 | No | Overcast;32-90 F | Fuse | Broken | 23-0082735 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1850852 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | JUMPER | JMPRS 1 SPAN N/O 7095 | 20230615 | 1250 | 20230615 | 1748 | 2137731 | 298 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 596 | 36.121 | -120.6692 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0082761 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1850863 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 2191 | 20230615 | 1454 | 20230615 | 1556 | 2137820 | 62 | Distribution Circuit | Animal | Squirrel | 56 | 3472 | 37.0515 | -122.0216 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0082866 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1850889 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | TRANSFORMER | 412911757262 | 20230615 | 1505 | 20230616 | 1041 | 2137841 | 1176 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1176 | 36.8818 | -121.4248 | No | Clear;32-90 F | Transformer | Broken | 23-0082860 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1850886 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2103 | 182492103 | FUSE | 4623 | 20230615 | 1913 | 20230616 | 147 | 2137988 | 394 | Distribution Circuit | Equipment Failure/Involved | Underground | 12 | 4728 | 36.8374 | -121.3826 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0082929 | UG | Sus | 31652432 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1850919 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | OTHER | J92980 TWD T0495 | 20230615 | 2201 | 20230616 | 229 | 2138076 | 268 | Distribution Circuit | Equipment Failure/Involved | Underground | 12 | 3216 | 36.5897 | -121.948 | No | Partly Cloudy;32-90 F | Conductor- Underground | Deteriorated | 23-0072950 | UG | Sus | 45766683 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1850930 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 287578 | 20230615 | 2357 | 20230616 | 1233 | 2138103 | 756 | Distribution Circuit | Vegetation | Tree - fell into line | 213 | 29169 | 37.0438 | -122.0755 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0082963 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | No | 1850954 | 0 | EPSS Ckt | N | 2023 | A/T
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 11054 | 20230616 | 34 | 20230616 | 1406 | 2138116 | 812 | Distribution Circuit | Vegetation | Tree - fell into line | 307 | 152957 | 36.9775 | -121.7415 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 23-0082966 | OH | Sus | 31652503 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | Yes | No | 1850958 | 0 | EPSS Ckt | N | 2023 | B/C T
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 10195 | 20230616 | 152 | 20230616 | 1510 | 2138126 | 798 | Distribution Circuit | 3rd Party | Vehicle | 4 | 3192 | 36.5293 | -121.8261 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0083096 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1851105 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 27481 | 20230616 | 624 | 20230616 | 1008 | 2138177 | 224 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 6 | 1344 | 36.6017 | -121.897 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0083103 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1851112 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | TRANSFORMER | 412828257793 | 20230616 | 916 | 20230616 | 1044 | 2138380 | 88 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 176 | 36.8955 | -121.4538 | No | Overcast;32-90 F |  |  | 23-0083132 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1851127 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 426822 | 20230616 | 1353 | 20230616 | 1531 | 2138660 | 98 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 101 | 9898 | 37.1016 | -122.0324 | No | Clear;32-90 F |  |  | 23-0083220 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1851167 | 0 | EPSS Ckt | N | 2023 | A&GRD
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 2901 | 20230616 | 1413 | 20230616 | 1458 | 2138684 | 45 | Distribution Circuit | Animal | Bird found | 146 | 6570 | 36.9671 | -122.0079 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 23-0083248 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1851176 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | FUSE | 11589 | 20230616 | 1825 | 20230616 | 1926 | 2138858 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 61 | 3697 | 36.9637 | -121.9706 | No | Clear;32-90 F |  |  | 23-0083293 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1851202 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | TRANSFORMER | 316644013675 | 20230616 | 1920 | 20230616 | 1938 | 2138960 | 18 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 54 | 36.8701 | -121.6482 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0083291 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1851200 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 96986 | 20230616 | 2037 | 20230616 | 2230 | 2139050 | 113 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 827 | 87366 | 37.1719 | -122.1648 | No | Clear;32-90 F |  |  | 23-0083302 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1851216 | 0 | EPSS Ckt | N | 2023 | A/C
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | FUSE | 10387 | 20230617 | 808 | 20230617 | 931 | 2139183 | 83 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 98 | 8154 | 36.9738 | -121.9623 | No | Overcast;32-90 F |  |  | 23-0083341 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1851277 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1104 | 182201104 | TRANSFORMER | 412453046670 | 20230617 | 823 | 20230617 | 1546 | 2139195 | 443 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 443 | 36.5873 | -121.5727 | No | Clear;32-90 F |  |  | 23-0083362 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1851316 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 316210912433 | 20230617 | 1325 | 20230617 | 1548 | 2139291 | 143 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 286 | 36.834 | -121.7959 | No | Partly Cloudy;32-90 F | Jumper | Deteriorated | 23-0083382 | OH | Sus | 45851630 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1851336 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | BORONDA-1101 | 182461101 | FUSE | 23707 | 20230617 | 1638 | 20230617 | 1740 | 2139473 | 62 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 21 | 1323 | 36.702 | -121.6753 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0083421 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1851364 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 4471 | 20230617 | 1918 | 20230617 | 2057 | 2139542 | 97 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 201 | 19497 | 37.0009 | -122.0142 | No | Partly Cloudy;32-90 F |  |  | 23-0083438 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1851381 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | RECLOSER | 607060 | 20230618 | 233 | 20230618 | 1839 | 2139656 | 966 | Distribution Circuit | 3rd Party | Vehicle | 848 | 134446 | 36.8188 | -121.6731 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 23-0083472 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | Yes | No | 1851416 | 0 | EPSS Ckt | N | 2023 | A/B GRD
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 4219 | 20230618 | 337 | 20230618 | 454 | 2139672 | 77 | Distribution Circuit | 3rd Party | Vehicle | 395 | 30415 | 36.9353 | -121.7736 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0083473 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1851417 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 9873 | 20230618 | 1026 | 20230618 | 1200 | 2139763 | 94 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 94 | 36.929 | -121.3754 | No | Clear;32-90 F |  |  | 23-0083498 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1851445 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 10027 | 20230618 | 1352 | 20230618 | 2118 | 2139815 | 446 | Distribution Circuit | 3rd Party | Vehicle | 12 | 5352 | 36.8867 | -121.6279 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0083506 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1851451 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 2191 | 20230618 | 1622 | 20230618 | 1836 | 2139889 | 134 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 7504 | 37.0515 | -122.0216 | No | Clear;32-90 F |  |  | 23-0083538 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1851482 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 8643 | 20230618 | 1930 | 20230619 | 1031 | 2140045 | 901 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 40545 | 37.01 | -121.8859 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0083550 | OH | Sus | 45851787 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | No | 1851494 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | RECLOSER | 5018 | 20230618 | 2052 | 20230618 | 2240 | 2140085 | 108 | Distribution Circuit | Equipment Failure/Involved | Underground | 503 | 54324 | 36.7629 | -121.7347 | No | Clear;32-90 F | Other | Burned/flashed | 23-0083553 | UG | Sus | 45851893 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1851497 | 0 | Non-EPSS | N | 2023 | B GRD
CENTRAL COAST | KING CITY | KING CITY-1101 | 182031101 | FUSE | 8935 | 20230618 | 2107 | 20230618 | 2155 | 2140093 | 48 | Distribution Circuit | 3rd Party | Metallic Balloon | 34 | 1632 | 36.2097 | -121.1218 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0083557 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1851501 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1103 | 182031103 | RECLOSER | 7038 | 20230619 | 543 | 20230619 | 722 | 2140165 | 99 | Distribution Circuit | Animal | Bird found | 794 | 45762 | 36.1935 | -121.1442 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0083585 | OH | Sus | 45851763 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1851526 | 0 | EPSS Ckt | Y | 2023 | AC
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | TRANSFORMER | 413331563225 | 20230619 | 820 | 20230619 | 1031 | 2140278 | 131 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 131 | 37.0491 | -121.2868 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0083625 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1851618 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | TRANSFORMER | 412328352606 | 20230619 | 840 | 20230619 | 1611 | 2140609 | 451 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 4059 | 36.7495 | -121.6212 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0083693 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1851664 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 6689 | 20230619 | 1146 | 20230619 | 1932 | 2140482 | 466 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 5126 | 36.8881 | -121.8071 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0083658 | OH | Sus | 45852644 | SOUTH BAY AND CENTRAL COAST | JUN | Three Phase Fault | 0 | No | Yes | No | 1851642 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 47335 | 20230619 | 1200 | 20230619 | 1926 | 2140583 | 446 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1784 | 36.7786 | -121.6476 | No | Clear-Strong Winds;32-90 F | Transformer (OH) | Deteriorated | 23-0083668 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1851654 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS COCHES-1102 | 182151102 | RECLOSER | 75272 | 20230619 | 1238 | 20230620 | 55 | 2140525 | 737 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 17887 | 36.3671 | -121.2776 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0083654 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Multi-Fault | 0 | No | No | No | 1851637 | 0 | EPSS Ckt | N | 2023 | ABC 50 / 51
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 2209 | 20230619 | 1552 | 20230619 | 1744 | 2140637 | 112 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 224 | 37.0455 | -121.9398 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0083710 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1851676 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | TRANSFORMER | 412188348678 | 20230620 | 858 | 20230620 | 1152 | 2141004 | 174 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 174 | 36.6411 | -121.6638 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0083873 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1851900 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | TRANSFORMER | 413947221698 | 20230620 | 1227 | 20230620 | 1649 | 2141002 | 262 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 262 | 35.9116 | -121.0441 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0083937 | OH | Sus | 45854189 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1851930 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | OCB | 2204/2 | 20230620 | 1414 | 20230620 | 1450 | 2141518 | 36 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4920 | 177120 | 36.5786 | -121.9084 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0083946 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1851934 | 0 | EPSS Ckt | N | 2023 | SET A TRIP / TIME OC
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | TRANSFORMER | 412067146067 | 20230620 | 1650 | 20230621 | 531 | 2141647 | 761 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 3805 | 36.568 | -121.7034 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0084044 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1851977 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 2725 | 20230620 | 1926 | 20230621 | 236 | 2141739 | 430 | Distribution Circuit | Vegetation | Tree - branch fell on line | 207 | 89010 | 36.5453 | -121.9281 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0084032 | OH | Sus | 31652925 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | No | 1851963 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | TRANSFORMER | 412708533790 | 20230620 | 2007 | 20230621 | 1001 | 2141762 | 834 | Transformer only | Vegetation | Tree - cutting- PG&E contractor | 5 | 4170 | 36.2358 | -121.4733 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0084068 | OH | Sus | 45854662 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852004 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DEL MONTE-2104 | 182222104 | RECLOSER | 3088 | 20230621 | 409 | 20230621 | 1022 | 2141900 | 373 | Distribution Circuit | Equipment Failure/Involved | Overhead | 337 | 54709 | 36.5493 | -121.7318 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0084080 | OH | Sus | 45854664 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852015 | 0 | EPSS Ckt | N | 2023 | B/GRD
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | TRANSFORMER | 316359014667 | 20230622 | 754 | 20230622 | 1157 | 2142859 | 243 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 972 | 36.896 | -121.7462 | No | Overcast;32-90 F | Service conductor | Broken | 23-0084686 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852453 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | TRANSFORMER | 412932560115 | 20230622 | 815 | 20230622 | 917 | 2143035 | 62 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 310 | 36.9596 | -121.4167 | No | Overcast;32-90 F | Transformer (OH) | Normal | 23-0084594 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1852400 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1101 | 182131101 | TRANSFORMER | 100000005931 | 20230622 | 830 | 20230622 | 1756 | 2142925 | 566 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 566 | 36.54 | -121.4355 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0084602 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852418 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 3075 | 20230622 | 1053 | 20230622 | 1100 | 2143138 | 7 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 75 | 36.9848 | -122.0387 | No | Overcast;32-90 F | Fuse | Broken | 23-0084651 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852439 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ERTA-0404 | 83510404 | TRANSFORMER | 316287616229 | 20230622 | 1413 | 20230622 | 2039 | 2143017 | 386 | Transformer only | Equipment Failure/Involved | Electrical Overload | 13 | 5018 | 36.9387 | -121.7713 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0084757 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852477 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1102 | 182011102 | FUSE | 29693 | 20230622 | 1714 | 20230623 | 135 | 2143412 | 501 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 3909 | 36.7016 | -121.6517 | No | Overcast;32-90 F | Transformer (OH) | Deteriorated | 23-0084851 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1852506 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | SWITCH | 400551 | 20230622 | 1734 | 20230623 | 304 | 2143316 | 570 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 11400 | 37.1289 | -122.1656 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0084808 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1852500 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 370732 | 20230622 | 2021 | 20230622 | 2118 | 2143533 | 57 | Distribution Circuit | Company Initiated | Personnel- company | 5225 | 297825 | 37.0534 | -122.0438 | No | Clear;32-90 F | Recloser | Normal | 23-0084858 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852517 | 0 | EPSS Ckt | N | 2023 | GRD/I
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | OTHER | J9112 TWD 6012 | 20230622 | 2250 | 20230623 | 228 | 2143639 | 218 | Distribution Circuit | Equipment Failure/Involved | Underground | 75 | 16350 | 36.6 | -121.8943 | No | Overcast;32-90 F | Switch (UG) | Broken | 23-0084771 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1852546 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2102 | 182222102 | TRANSFORMER | 411657847760 | 20230622 | 2256 | 20230623 | 1238 | 2143657 | 822 | Transformer only | Company Initiated | Contact with High Voltage- company | 32 | 26304 | 36.6109 | -121.844 | No | Overcast;32-90 F | Transformer | Failed/Faulted | 23-0084887 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852554 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1104 | 182201104 | RECLOSER | 965598 | 20230623 | 247 | 20230623 | 608 | 2143708 | 201 | Distribution Circuit | Equipment Failure/Involved | Overhead | 168 | 33768 | 36.5774 | -121.4917 | No | Overcast;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0084897 | OH | Sus | 45857332 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | No | 1852563 | 0 | EPSS Ckt | N | 2023 | C/GRD
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 9639 | 20230623 | 715 | 20230623 | 1138 | 2143773 | 263 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 526 | 36.8808 | -121.7784 | No | Partly Cloudy-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 23-0085073 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1852720 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | RECLOSER | 3010 | 20230623 | 727 | 20230623 | 1220 | 2143765 | 293 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 427 | 125111 | 36.28 | -121.3077 | No | Partly Cloudy;32-90 F |  |  | 23-0084929 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852586 | 0 | EPSS Ckt | Y | 2023 | B PHASE
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | TRANSFORMER | 412773235032 | 20230623 | 1255 | 20230623 | 1711 | 2144187 | 256 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 256 | 36.2712 | -121.4531 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0085185 | OH | Sus | 31653274 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852748 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SOLEDAD-2102 | 182052102 | TRANSFORMER | 413123038800 | 20230623 | 1359 | 20230623 | 1553 | 2144232 | 114 | Transformer only | 3rd Party | Other | 1 | 114 | 36.3763 | -121.3375 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0085201 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852753 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 5607 | 20230624 | 851 | 20230624 | 1030 | 2144625 | 99 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 99 | 36.6674 | -121.7054 | No | Clear;32-90 F |  |  | 23-0085312 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852867 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | INDUSTRIAL ACRES-0412 | 182300412 | FUSE | 25269 | 20230624 | 1127 | 20230624 | 1715 | 2144767 | 348 | Distribution Circuit | 3rd Party | Vehicle | 1 | 348 | 36.6849 | -121.6177 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0085311 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1852866 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | FUSE | 24557 | 20230624 | 1316 | 20230624 | 2207 | 2144955 | 531 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1417 | 36.4888 | -121.4248 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0085342 | OH | Sus | 45858631 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852890 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS COCHES-1102 | 182151102 | TRANSFORMER | 413307237957 | 20230624 | 1656 | 20230624 | 2025 | 2145005 | 209 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 209 | 36.3538 | -121.274 | No | Clear;32-90 F | Connector or Splice (OH) | Burned/flashed | 23-0085364 | OH | Sus | 45858633 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852907 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 50899 | 20230624 | 1753 | 20230626 | 856 | 2145072 | 2343 | Distribution Circuit | Animal | Bird found | 3 | 6242 | 36.8323 | -121.3483 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0085375 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852915 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | RECLOSER | 7086 | 20230625 | 901 | 20230625 | 2159 | 2145219 | 649 | Distribution Circuit | Equipment Failure/Involved | Overhead | 131 | 44942 | 36.2942 | -121.1997 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0085415 | OH | Sus | 45858924 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | No | 1852966 | 0 | EPSS Ckt | N | 2023 | B-GRD
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | INTERRUPTER | 418606 | 20230625 | 1007 | 20230625 | 1345 | 2145252 | 218 | Distribution Circuit | Equipment Failure/Involved | Underground | 686 | 135668 | 36.8888 | -121.3949 | No | Overcast;32-90 F | Switch (UG) | Broken | 23-0085420 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852970 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 5805 | 20230625 | 1910 | 20230626 | 146 | 2145464 | 396 | Distribution Circuit | Equipment Failure/Involved | Overhead | 76 | 6912 | 36.9734 | -121.8805 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0085448 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853000 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | OILFIELDS-1102 | 182391102 | FUSE | 9593 | 20230626 | 712 | 20230626 | 1045 | 2145939 | 213 | Distribution Circuit | Animal | Bird found | 1 | 213 | 35.9513 | -120.8106 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0085576 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1853187 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | TRANSFORMER | 413420034765 | 20230626 | 752 | 20230626 | 914 | 2145629 | 82 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 82 | 36.2673 | -121.233 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0085525 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853152 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | RECLOSER | 5144 | 20230626 | 853 | 20230627 | 230 | 2145780 | 1057 | Distribution Circuit | Vegetation | Tree - fell into line | 265 | 48224 | 37.0911 | -122.0774 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0085522 | OH | Sus | 45860603 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1853145 | 0 | EPSS Ckt | Y | 2023 | B-C
CENTRAL COAST | KING CITY | LOS COCHES-1102 | 182151102 | JUMPER | BURNT OPEN JUMPER | 20230626 | 1502 | 20230626 | 1849 | 2146275 | 227 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 6356 | 36.3743 | -121.2636 | No | Clear;32-90 F | Jumper | Burned Open | 23-0085766 | OH | Sus | 45860725 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853257 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 5453 | 20230626 | 1952 | 20230626 | 2140 | 2146426 | 108 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 1513 | 37.1361 | -122.1393 | No | Clear;32-90 F | Service conductor | Together | 23-0085848 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853304 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | SWITCH | 40065 | 20230626 | 1953 | 20230627 | 239 | 2146428 | 406 | Distribution Circuit | Equipment Failure/Involved | Overhead | 63 | 25578 | 36.5837 | -121.9123 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 23-0085803 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1853296 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | SWITCH | 2839 | 20230626 | 2230 | 20230627 | 57 | 2146490 | 147 | Distribution Circuit | Equipment Failure/Involved | Overhead | 60 | 8820 | 36.9977 | -122.1304 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0085862 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1853319 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1102 | 182201102 | FUSE | 20161 | 20230627 | 802 | 20230627 | 934 | 2146690 | 92 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 1473 | 36.6064 | -121.5148 | No | Overcast;32-90 F | Fuse | Broken | 23-0085992 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853454 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | TRANSFORMER | 413257935845 | 20230627 | 926 | 20230627 | 1142 | 2146855 | 136 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 136 | 36.2962 | -121.2892 | No | Partly Cloudy;32-90 F |  |  | 23-0086087 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1853487 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 8315 | 20230627 | 934 | 20230627 | 1056 | 2146868 | 82 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 17 | 1394 | 37.0995 | -122.1181 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0086050 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853479 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1106 | 182011106 | TRANSFORMER | 412233448751 | 20230627 | 936 | 20230628 | 212 | 2146671 | 996 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 996 | 36.6435 | -121.6494 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0085999 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853462 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 5769 | 20230627 | 1214 | 20230628 | 221 | 2147057 | 838 | Distribution Circuit | 3rd Party | Vehicle | 14 | 11732 | 36.8919 | -121.6432 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0086160 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Three Phase Fault | 0 | No | Yes | No | 1853509 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | OILFIELDS-1102 | 182391102 | FUSE | 559 | 20230627 | 1504 | 20230627 | 2014 | 2147149 | 310 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 5238 | 35.9793 | -120.8779 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0086221 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1853520 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 8983 | 20230627 | 1550 | 20230627 | 1652 | 2147202 | 62 | Distribution Circuit | Vegetation | Tree - branch fell on line | 49 | 3038 | 37.0307 | -122.1429 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0086294 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1853535 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | JUMPER | WIRE DOWN | 20230627 | 1634 | 20230627 | 2142 | 2147224 | 308 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 2184 | 36.6658 | -121.523 | No | Overcast;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0086276 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | Yes | 1853530 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | TRANSFORMER | 413394836856 | 20230627 | 2102 | 20230627 | 2208 | 2147340 | 66 | Transformer only | Equipment Failure/Involved | Overhead | 21 | 1386 | 36.3242 | -121.2433 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0086343 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853580 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | TRANSFORMER | 413316236840 | 20230627 | 2256 | 20230628 | 13 | 2147377 | 77 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 77 | 36.3236 | -121.2701 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0086342 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1853579 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | BUENA VISTA-1106 | 182261106 | SWITCH | 25305 | 20230628 | 113 | 20230628 | 143 | 2147385 | 30 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 360 | 36.6246 | -121.6301 | No | Overcast;32-90 F | Connector or Splice (OH) | Burned/flashed | 23-0086355 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1853586 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | FUSE | 512621 | 20230628 | 535 | 20230628 | 634 | 2147421 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 61 | 3599 | 36.8416 | -121.4567 | No | Overcast;32-90 F |  |  | 23-0086370 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1853601 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | TRANSFORMER | 7421 | 20230628 | 635 | 20230628 | 2020 | 2147442 | 825 | Distribution Circuit | Equipment Failure/Involved | Underground | 16 | 13200 | 36.5933 | -121.8976 | No | Overcast-Fog;32-90 F | Transformer (UG) | Failed/Faulted | 23-0086454 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853716 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 595388 | 20230628 | 841 | 20230628 | 1953 | 2147561 | 672 | Distribution Circuit | Vegetation | Tree - fell into line | 179 | 120288 | 37.1517 | -122.136 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0083860 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1853686 | 0 | EPSS Ckt | Y | 2023 | N/A
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | TRANSFORMER | 411450247934 | 20230628 | 851 | 20230628 | 949 | 2147608 | 58 | Transformer only | 3rd Party | Other | 11 | 638 | 36.6142 | -121.9153 | No | Overcast-Fog;32-90 F | Secondary | Together | 23-0086494 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853768 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | TRANSFORMER | 413087051378 | 20230628 | 937 | 20230628 | 1151 | 2147714 | 134 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 134 | 36.7214 | -121.3602 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0086578 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853806 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | SWITCH | 3465 | 20230628 | 1034 | 20230628 | 1041 | 2147849 | 7 | Distribution Circuit | Equipment Failure/Involved | Overhead | 178 | 1246 | 36.7097 | -121.7011 | No | Clear;32-90 F | Regulator | Malfunctioning | 23-0086510 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1853776 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 1461 | 20230628 | 1051 | 20230628 | 2002 | 2147979 | 551 | Distribution Circuit | Equipment Failure/Involved | Overhead | 133 | 72280 | 36.557 | -121.9042 | No | Overcast;32-90 F | Lightning Arrestor | Burned/flashed | 23-0086568 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1853799 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 1463 | 20230628 | 1051 | 20230629 | 1554 | s1853838 | 1743 | Distribution Circuit | Equipment Failure/Involved | Underground | 255 | 229098 | 36.5648 | -121.9118 | No | Clear;32-90 F | Elbow | Burned/flashed | 23-0086568 | UG | Sus | 31653854 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853838 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | INTERRUPTER | 9220 | 20230628 | 1100 | 20230628 | 1737 | 2148021 | 397 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 325 | 129025 | 36.5262 | -121.8675 | No | Overcast;32-90 F |  |  | 23-0086834 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853855 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | RECLOSER | 75304 | 20230628 | 1138 | 20230629 | 419 | 2148030 | 1001 | Distribution Circuit | Equipment Failure/Involved | Underground | 922 | 306956 | 36.5245 | -121.8121 | No | Overcast;32-90 F | Conductor- Underground | Broken | 23-0086574 | UG | Sus | 31653819 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853804 | 0 | EPSS Ckt | N | 2023 | C PH & GRD
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | FUSE | 9577 | 20230628 | 1451 | 20230628 | 1634 | 2148207 | 103 | Distribution Circuit | Animal | Bird found | 16 | 1648 | 35.9901 | -121.1344 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0086814 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1853852 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | TRANSFORMER | 315318022395 | 20230628 | 1737 | 20230629 | 130 | 2148315 | 473 | Transformer only | Vegetation | Tree - fell into line | 5 | 2365 | 37.1048 | -122.1051 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0086860 | OH | Sus | 45864270 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853867 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 2283 | 20230629 | 247 | 20230629 | 605 | 2148539 | 198 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 63 | 12546 | 36.5564 | -121.9087 | No | Overcast-Fog;32-90 F |  |  | 23-0086916 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853909 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 11797 | 20230629 | 710 | 20230629 | 2301 | 2148615 | 951 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 14265 | 36.8677 | -121.7087 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0087026 | OH | Sus | 45864493 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | No | 1854033 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS COCHES-1102 | 182151102 | FUSE | 8895 | 20230629 | 851 | 20230629 | 1906 | 2148738 | 615 | Distribution Circuit | Animal | Bird found | 18 | 2942 | 36.3894 | -121.2686 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0087040 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1854056 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 595388 | 20230629 | 901 | 20230629 | 1559 | 2148757 | 418 | Distribution Circuit | Vegetation | Tree - fell into line | 179 | 74822 | 37.1517 | -122.136 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0086871 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1854001 | 0 | EPSS Ckt | N | 2023 | NA
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 412090751210 | 20230629 | 1025 | 20230629 | 2031 | 2148885 | 606 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 606 | 36.7101 | -121.7 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0087189 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1854107 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | BUENA VISTA-1106 | 182261106 | FUSE | 23699 | 20230629 | 1339 | 20230629 | 2145 | 2149027 | 486 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 486 | 36.6421 | -121.6148 | No | Clear;32-90 F | Fuse | Broken | 23-0087286 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1854130 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | SWITCH | 8621 | 20230629 | 1450 | 20230629 | 1600 | 2149067 | 70 | Distribution Circuit | Equipment Failure/Involved | Overhead | 51 | 3570 | 36.3604 | -120.8491 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0087257 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1854118 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | TRANSFORMER | T0813 | 20230629 | 1453 | 20230629 | 1826 | 2149087 | 213 | Transformer only | Equipment Failure/Involved | Underground | 32 | 6816 | 36.9229 | -121.7392 | No | Clear;32-90 F | Secondary | Broken | 23-0087268 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1854123 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1107 | 182011107 | TRANSFORMER | 412244749482 | 20230629 | 1651 | 20230629 | 1948 | 2149215 | 177 | Transformer only | Vegetation | Tree - branch fell on line | 10 | 1770 | 36.6631 | -121.6458 | No | Clear;32-90 F | Secondary | Normal | 23-0087331 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1854144 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1103 | 182011103 | TRANSFORMER | 412210450766 | 20230629 | 2014 | 20230629 | 2320 | 2149343 | 186 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 744 | 36.698 | -121.6588 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 23-0087413 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1854214 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | OTHER | T2423 TWD T2424 | 20230629 | 2150 | 20230629 | 2325 | 2149393 | 95 | Distribution Circuit | Equipment Failure/Involved | Underground | 45 | 4275 | 36.7157 | -121.6423 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0087124 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1854182 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1101 | 182011101 | TRANSFORMER | 412245349557 | 20230629 | 2218 | 20230630 | 38 | 2149419 | 140 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 1960 | 36.6651 | -121.6456 | No | Overcast-Fog;32-90 F | Fuse | Burned Open | 23-0087421 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1854223 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | FUSE | 7107 | 20230629 | 2246 | 20230630 | 309 | 2149429 | 263 | Distribution Circuit | Environmental/External | Flood/Erosion | 17 | 4471 | 36.1979 | -120.714 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0087403 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1854209 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2108 | 83252108 | TRANSFORMER | 315531217453 | 20230630 | 136 | 20230630 | 1705 | 2149481 | 929 | Transformer only | 3rd Party | Vehicle | 8 | 7432 | 36.9688 | -122.0295 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0087426 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1854228 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 595388 | 20230630 | 845 | 20230630 | 1547 | 2149622 | 422 | Distribution Circuit | Vegetation | Tree - fell into line | 179 | 75538 | 37.1517 | -122.136 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0087309 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1854302 | 0 | EPSS Ckt | N | 2023 | NA
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 412080251138 | 20230630 | 921 | 20230630 | 2010 | 2149553 | 649 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 649 | 36.7081 | -121.7039 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0087514 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1854341 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | TRANSFORMER | 412666545295 | 20230630 | 924 | 20230630 | 943 | 2149623 | 19 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 19 | 36.5514 | -121.498 | No | Clear;32-90 F |  |  | 23-0087528 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1854351 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 942143 | 20230630 | 1125 | 20230630 | 1134 | 2149841 | 9 | Distribution Circuit | Company Initiated | Personnel- company | 113 | 1017 | 36.965 | -121.7331 | No | Clear;32-90 F | Fuse | Normal | 23-0087595 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1854374 | 0 | EPSS Ckt | Y | 2023 | B&C
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | FUSE | 4583 | 20230630 | 1425 | 20230630 | 1905 | 2149988 | 280 | Distribution Circuit | Animal | Bird found | 16 | 4480 | 36.9716 | -121.9875 | No | Clear;32-90 F | Fuse | Broken | 23-0087731 | OH | Sus | 31653954 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1854419 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 12868 | 20230630 | 2137 | 20230630 | 2332 | 2150395 | 115 | Distribution Circuit | Vegetation | Tree - branch fell on line | 125 | 14375 | 37.0954 | -122.1442 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0087803 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1854465 | 0 | EPSS Ckt | Y | 2023 | C PHASE & GRD
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 10720 | 20230630 | 2137 | 20230701 | 318 | 2150494 | 341 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 91 | 31031 | 37.1085 | -122.1441 | No | Clear;32-90 F |  |  | 23-0087803 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1854494 | 0 | EPSS Ckt | Y | 2023 | NA
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 688040 | 20230630 | 2137 | 20230701 | 746 | 2150495 | 609 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 609 | 37.1308 | -122.1715 | No | Clear;32-90 F |  |  | 23-0087803 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1854495 | 0 | EPSS Ckt | Y | 2023 | NA
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 10254 | 20230630 | 2137 | 20230701 | 747 | 2150496 | 610 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 7 | 4270 | 37.1392 | -122.1787 | No | Clear;32-90 F |  |  | 23-0087803 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1854496 | 0 | EPSS Ckt | Y | 2023 | NA
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 12758 | 20230630 | 2137 | 20230701 | 1330 | 2150497 | 953 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 283 | 269699 | 37.1486 | -122.1745 | No | Clear;32-90 F |  |  | 23-0087803 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1854497 | 0 | EPSS Ckt | Y | 2023 | NA
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 12124 | 20230630 | 2137 | 20230701 | 1331 | 2150498 | 954 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 289 | 275706 | 37.1677 | -122.1662 | No | Clear;32-90 F |  |  | 23-0087803 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1854498 | 0 | EPSS Ckt | Y | 2023 | NA
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 12992 | 20230630 | 2137 | 20230701 | 1335 | 2150504 | 958 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 697 | 667726 | 37.1991 | -122.1532 | No | Clear;32-90 F |  |  | 23-0087803 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1854500 | 0 | EPSS Ckt | Y | 2023 | NA
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 95690 | 20230630 | 2137 | 20230701 | 319 | 2150514 | 342 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 756 | 258552 | 37.1249 | -122.125 | No | Clear;32-90 F |  |  | 23-0087803 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1854503 | 0 | EPSS Ckt | Y | 2023 | NA
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 12838 | 20230630 | 2137 | 20230701 | 321 | 2150515 | 344 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 248 | 85312 | 37.1272 | -122.1236 | No | Clear;32-90 F |  |  | 23-0087803 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1854504 | 0 | EPSS Ckt | Y | 2023 | NA
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 65444 | 20230630 | 2137 | 20230701 | 324 | 2150516 | 347 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 390 | 135330 | 37.1278 | -122.1229 | No | Clear;32-90 F |  |  | 23-0087803 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1854505 | 0 | EPSS Ckt | Y | 2023 | NA
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | SWITCH | 69550 | 20230630 | 2137 | 20230701 | 322 | 2150517 | 345 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 275 | 94875 | 37.1319 | -122.1095 | No | Clear;32-90 F |  |  | 23-0087803 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1854506 | 0 | EPSS Ckt | Y | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 445933 | 20230630 | 2137 | 20230701 | 331 | 2150518 | 354 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 56 | 19824 | 37.1372 | -122.1004 | No | Clear;32-90 F |  |  | 23-0087803 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1854507 | 0 | EPSS Ckt | Y | 2023 | NA
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 921168 | 20230630 | 2137 | 20230701 | 325 | 2150520 | 348 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 142 | 49416 | 37.1431 | -122.1317 | No | Clear;32-90 F |  |  | 23-0087803 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1854509 | 0 | EPSS Ckt | N | 2023 | NA
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 595388 | 20230630 | 2137 | 20230701 | 327 | 2150521 | 350 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 179 | 62650 | 37.1517 | -122.136 | No | Clear;32-90 F |  |  | 23-0087803 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1854510 | 0 | EPSS Ckt | Y | 2023 | NA
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 136050 | 20230630 | 2137 | 20230701 | 328 | 2150522 | 351 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 91 | 31941 | 37.1525 | -122.134 | No | Clear;32-90 F |  |  | 23-0087803 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1854511 | 0 | EPSS Ckt | Y | 2023 | NA
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | SWITCH | 76752 | 20230630 | 2137 | 20230701 | 1333 | 2150525 | 956 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 190 | 181640 | 37.1535 | -122.1612 | No | Clear;32-90 F |  |  | 23-0087803 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1854512 | 0 | EPSS Ckt | Y | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | SWITCH | 967473 | 20230630 | 2137 | 20230701 | 1324 | 2150623 | 947 | Distribution Circuit | Vegetation | Tree - branch fell on line | 236 | 223492 | 37.1386 | -122.1774 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0087803 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1854541 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 12122 | 20230701 | 49 | 20230701 | 408 | 2150529 | 199 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 63 | 12537 | 37.0666 | -122.2288 | No | Clear;32-90 F |  |  | 23-0087839 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1854516 | 0 | EPSS Ckt | N | 2023 | A&GRD TIME
CENTRAL COAST | SALINAS | SALINAS-1105 | 182011105 | FUSE | 20242 | 20230701 | 218 | 20230701 | 1941 | 2150547 | 1043 | Distribution Circuit | Equipment Failure/Involved | Underground | 171 | 128489 | 36.7097 | -121.6111 | No | Overcast-Fog;32-90 F | Transformer (UG) | Failed/Faulted | 23-0087895 | UG | Sus | 35463979 | SOUTH BAY AND CENTRAL COAST | JUL | Three Phase Fault | 0 | No | No | No | 1854570 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | OCB | 1102/2 | 20230701 | 608 | 20230701 | 1508 | 2150583 | 540 | Distribution Circuit | Equipment Failure/Involved | Overhead | 656 | 212630 | 36.0734 | -120.9364 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0087846 | OH | Sus | 45867209 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | Yes | No | 1854526 | 0 | EPSS Ckt | N | 2023 | BC
CENTRAL COAST | SALINAS | SOLEDAD-2105 | 182052105 | SWITCH | 526864 | 20230701 | 750 | 20230701 | 941 | 2150626 | 111 | Distribution Circuit | Animal | Bird found | 11 | 1221 | 36.5039 | -121.378 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0087857 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1854542 | 0 | EPSS Ckt | Y | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | RECLOSER | 7592 | 20230701 | 1033 | 20230701 | 1644 | 2150735 | 371 | Distribution Circuit | Equipment Failure/Involved | Overhead | 95 | 14445 | 36.2633 | -121.1535 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0087889 | OH | Sus | 45867226 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1854568 | 0 | EPSS Ckt | N | 2023 | A&GRD
CENTRAL COAST | SALINAS | SPENCE-1104 | 182201104 | RECLOSER | 965598 | 20230701 | 1515 | 20230701 | 2136 | 2150905 | 381 | Distribution Circuit | 3rd Party | Vehicle | 168 | 64008 | 36.5774 | -121.4917 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0087947 | OH | Sus | 35464047 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | Yes | No | 1854598 | 0 | EPSS Ckt | Y | 2023 | BC
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | FUSE | 4015 | 20230701 | 2333 | 20230702 | 1248 | 2151698 | 795 | Distribution Circuit | Equipment Failure/Involved | Underground | 10 | 5808 | 36.8902 | -121.4219 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0088081 | UG | Sus | 35464210 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1854720 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | RECLOSER | 88772 | 20230702 | 641 | 20230704 | 743 | 2151848 | 2942 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1255 | 118042 | 36.904 | -121.6085 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 23-0088106 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1854745 | 0 | EPSS Ckt | Y | 2023 | A GRD
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | RECLOSER | 370948 | 20230702 | 715 | 20230702 | 1543 | 2151875 | 508 | Distribution Circuit | Equipment Failure/Involved | Overhead | 718 | 129180 | 36.5785 | -121.7263 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0088112 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1854748 | 0 | EPSS Ckt | Y | 2023 | C&GRD INST
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | RECLOSER | 2624 | 20230702 | 757 | 20230702 | 1636 | 2151904 | 376 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1471 | 362655 | 36.569 | -121.7955 | No | Partly Cloudy;32-90 F |  |  | 23-0088118 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1854751 | 0 | EPSS Ckt | Y | 2023 | C GRD
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | RECLOSER | 7066 | 20230702 | 841 | 20230702 | 1746 | 2151938 | 545 | Distribution Circuit | Equipment Failure/Involved | Overhead | 292 | 159140 | 36.0489 | -120.9121 | No | Partly Cloudy;32-90 F | Insulator | Broken | 23-0088125 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1854759 | 0 | EPSS Ckt | Y | 2023 | A&B
CENTRAL COAST | MONTEREY | FORT ORD-2107 | 182402107 | TRANSFORMER | 411844650197 | 20230702 | 914 | 20230702 | 1752 | 2151957 | 518 | Transformer only | Unknown Cause | Patrol - found nothing | 12 | 6216 | 36.6796 | -121.7831 | No | Clear;32-90 F |  |  | 23-0088210 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1854831 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 4253 | 20230702 | 1030 | 20230703 | 239 | 2152003 | 969 | Distribution Circuit | Equipment Failure/Involved | Underground | 23 | 8217 | 36.8736 | -121.6428 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0088149 | UG | Sus | 45867542 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1854778 | 0 | EPSS Ckt | Y | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | RECLOSER | 88772 | 20230702 | 1034 | 20230702 | 1041 | s1862541 | 7 | Distribution Circuit | Company Initiated | Personnel- company | 1232 | 8624 | 36.904 | -121.6085 | No | Partly Cloudy;32-90 F | Recloser | Normal | 23-0088149 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1862541 | 0 | EPSS Ckt | Y | 2023 | A GRD
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 9629 | 20230702 | 1242 | 20230702 | 1847 | 2152064 | 365 | Distribution Circuit | Vegetation | Tree - branch fell on line | 464 | 169360 | 36.5853 | -121.9054 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0088216 | OH | Sus | 45867515 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1854836 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 6753 | 20230702 | 1418 | 20230702 | 1547 | 2152161 | 89 | Distribution Circuit | Vegetation | Tree - branch fell on line | 38 | 3382 | 36.5659 | -121.8876 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0088187 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1854813 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | SWITCH | 969667 | 20230702 | 1618 | 20230702 | 1650 | 2152204 | 32 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 160 | 37.0515 | -122.0952 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0088195 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1854820 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1109 | 182011109 | TRANSFORMER | T316501 | 20230702 | 1811 | 20230703 | 244 | 2152208 | 513 | Distribution Circuit | Equipment Failure/Involved | Underground | 20 | 10260 | 36.6774 | -121.5971 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0088213 | UG | Sus | 35464142 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1854833 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 12868 | 20230702 | 1905 | 20230703 | 948 | 2152531 | 870 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4054 | 1780241 | 37.0954 | -122.1442 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0088231 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Multi-Fault | 0 | No | No | No | 1854852 | 0 | EPSS Ckt | Y | 2023 | AC GRD
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5587 | 20230703 | 836 | 20230703 | 1025 | 2153093 | 109 | Distribution Circuit | Animal | Squirrel | 8 | 872 | 37.0672 | -122.0586 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0088423 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855007 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 412054849515 | 20230703 | 1025 | 20230703 | 1104 | 2153222 | 39 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 39 | 36.6625 | -121.7111 | No | Clear;32-90 F | Fuse | Broken | 23-0088451 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855018 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | TRANSFORMER | 412213252767 | 20230703 | 1115 | 20230703 | 1815 | 2153117 | 420 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 557 | 36.7527 | -121.6593 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0088478 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855028 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412316955026 | 20230703 | 1603 | 20230703 | 2311 | 2153447 | 428 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 428 | 36.8159 | -121.626 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0088620 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855062 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | FUSE | 4205 | 20230703 | 2104 | 20230704 | 815 | 2153797 | 671 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1343 | 36.4715 | -121.423 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0088731 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855143 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | RECLOSER | 2028 | 20230704 | 259 | 20230704 | 706 | 2153904 | 247 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 489 | 120783 | 36.4728 | -121.7175 | No | Clear;32-90 F |  |  | 23-0088705 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1855125 | 0 | EPSS Ckt | Y | 2023 | A-B
CENTRAL COAST | KING CITY | SOLEDAD-2102 | 182052102 | RECLOSER | 858388 | 20230704 | 550 | 20230704 | 1018 | 2153931 | 268 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 116 | 25559 | 36.4021 | -121.3443 | No | Partly Cloudy;32-90 F |  |  | 23-0088712 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1855131 | 0 | EPSS Ckt | Y | 2023 | B-C
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | RECLOSER | 944178 | 20230704 | 2012 | 20230705 | 246 | 2154233 | 374 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 886 | 253882 | 37.0926 | -122.0964 | No | Clear;32-90 F |  |  | 23-0088776 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855180 | 0 | EPSS Ckt | Y | 2023 | C-GRD
CENTRAL COAST | SALINAS | SALINAS-1109 | 182011109 | TRANSFORMER | 25645 | 20230705 | 53 | 20230705 | 802 | 2154204 | 429 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 8250 | 36.6727 | -121.6242 | No | Overcast;32-90 F | Pole-Wood | Deteriorated | 23-0088777 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855181 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 6559 | 20230705 | 853 | 20230705 | 943 | 2154476 | 50 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 1550 | 36.9267 | -121.7459 | No | Overcast;32-90 F |  |  | 23-0088887 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1855296 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | TRANSFORMER | 315456517260 | 20230705 | 1019 | 20230705 | 1055 | 2154577 | 36 | Transformer only | Equipment Failure/Involved | Overhead | 25 | 900 | 36.9636 | -122.0551 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0088916 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1855314 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | TRANSFORMER | 414147638347 | 20230705 | 1127 | 20230705 | 1912 | 2154372 | 465 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 465 | 36.3705 | -120.9894 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0088956 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855325 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | OTHER | 5741 | 20230705 | 1537 | 20230705 | 2031 | 2154821 | 294 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 7938 | 36.9993 | -122.0372 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0089126 | OH | Sus | 45871161 | SOUTH BAY AND CENTRAL COAST | JUL | Open Circuit | 0 | No | Yes | Yes | 1855358 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 6799 | 20230705 | 1612 | 20230705 | 1739 | 2154865 | 87 | Distribution Circuit | 3rd Party | Vehicle | 2 | 174 | 36.9042 | -121.7191 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0089121 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1855355 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | FUSE | 9809 | 20230706 | 431 | 20230706 | 511 | 2155078 | 40 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 160 | 36.8765 | -121.409 | No | Overcast;32-90 F | Pole-Wood | Normal | 23-0089207 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855416 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | RECLOSER | 7086 | 20230706 | 729 | 20230706 | 1516 | 2155129 | 467 | Distribution Circuit | Equipment Failure/Involved | Overhead | 336 | 59932 | 36.2942 | -121.1997 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0089242 | OH | Sus | 45871177 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1855421 | 0 | EPSS Ckt | N | 2023 | A-GRD
CENTRAL COAST | SALINAS | SPENCE-1104 | 182201104 | FUSE | 680957 | 20230706 | 801 | 20230707 | 355 | 2155269 | 1194 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 2388 | 36.5767 | -121.5098 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0089303 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | Yes | No | 1855493 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1104 | 182201104 | FUSE | 24797 | 20230706 | 806 | 20230706 | 1024 | 2155150 | 138 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 138 | 36.6007 | -121.5896 | No | Partly Cloudy;32-90 F |  |  | 23-0089347 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855512 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8427 | 20230706 | 1255 | 20230706 | 1955 | 2155383 | 420 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 4894 | 37.077 | -121.981 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0089424 | OH | Sus | 45872553 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1855533 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | RECLOSER | 7596 | 20230706 | 1441 | 20230706 | 1508 | s1868725 | 27 | Distribution Circuit | Company Initiated | Personnel- company | 70 | 1890 | 36.3234 | -121.2307 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0089242 | OH | Sus | 45871177 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1868725 | 0 | Non-EPSS | N | 2023 | N/A
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8383 | 20230706 | 2322 | 20230707 | 1830 | 2155913 | 1148 | Distribution Circuit | Equipment Failure/Involved | Overhead | 163 | 158880 | 37.0396 | -122.0302 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0089737 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1855676 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 7887 | 20230707 | 645 | 20230707 | 751 | 2155996 | 66 | Distribution Circuit | Animal | Bird found | 18 | 1188 | 36.9234 | -121.7507 | No | Overcast-Fog;32-90 F | Transformer (OH) | Normal | 23-0089693 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855642 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | HOLLISTER | PANOCHE-1103 | 253671103 | FUSE | 4153 | 20230707 | 805 | 20230707 | 1337 | 2156048 | 332 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1660 | 36.6386 | -121.0493 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0089697 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1855648 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1101 | 182131101 | FUSE | 25497 | 20230707 | 810 | 20230707 | 1346 | 2156057 | 336 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 448 | 36.5332 | -121.4588 | No | Overcast;32-90 F | Cutout- fuse holder | Broken | 23-0089849 | OH | Sus | 31654564 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855718 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 2199 | 20230707 | 1338 | 20230707 | 1441 | 2156359 | 63 | Distribution Circuit | 3rd Party | Vehicle | 28 | 1764 | 36.9517 | -121.834 | No | Partly Cloudy;32-90 F | Pole-Wood | Normal | 23-0089950 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1855745 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | FUSE | 8551 | 20230707 | 1618 | 20230707 | 1753 | 2156482 | 95 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 95 | 36.3238 | -121.2179 | No | Clear;32-90 F |  |  | 23-0089998 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1855761 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 316071515495 | 20230707 | 1914 | 20230707 | 2010 | 2156569 | 56 | Transformer only | Unknown Cause | Patrol - found nothing | 11 | 616 | 36.9176 | -121.845 | No | Clear;32-90 F |  |  | 23-0090027 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1855770 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | RECLOSER | 91424 | 20230708 | 535 | 20230708 | 642 | 2156903 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 143 | 9581 | 36.9335 | -121.3885 | No | Partly Cloudy;32-90 F |  |  | 23-0090052 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1855806 | 0 | EPSS Ckt | Y | 2023 | B-C
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | FUSE | 23309 | 20230708 | 638 | 20230708 | 740 | 2156916 | 62 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 347 | 36.7584 | -121.7433 | No | Clear;32-90 F |  |  | 23-0090060 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855817 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2103 | 182492103 | FUSE | 55031 | 20230708 | 748 | 20230708 | 1410 | 2156934 | 382 | Distribution Circuit | Equipment Failure/Involved | Underground | 33 | 12606 | 36.8394 | -121.3639 | No | Overcast;32-90 F | Cable Termination(live front | Burned/flashed | 23-0090075 | UG | Sus | 45875382 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855834 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 762931 | 20230708 | 755 | 20230708 | 817 | 2156940 | 22 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 66 | 36.9689 | -121.3747 | No | Partly Cloudy;32-90 F |  |  | 23-0090065 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1855825 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 11461 | 20230708 | 1122 | 20230708 | 1831 | 2157106 | 429 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 1342 | 36.8678 | -121.76 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0090109 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855862 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 36516 | 20230708 | 1353 | 20230708 | 2102 | 2157202 | 429 | Distribution Circuit | Vegetation | Tree - branch fell on line | 396 | 54564 | 37.0787 | -122.1336 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0090120 | OH | Sus | 45875814 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855873 | 0 | EPSS Ckt | Y | 2023 | B PHASE & GRD
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | SWITCH | 3067 | 20230708 | 1443 | 20230708 | 1522 | 2157213 | 39 | Distribution Circuit | Company Initiated | Return Circuit Normal | 28 | 1052 | 36.5638 | -121.5195 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0090064 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1855876 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | TRANSFORMER | 315230624172 | 20230708 | 1616 | 20230708 | 1718 | 2157297 | 62 | Transformer only | Unknown Cause | Patrol - found nothing | 11 | 682 | 37.1528 | -122.1349 | No | Clear;32-90 F |  |  | 23-0090152 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1855895 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1103 | 182011103 | RECLOSER | 282702 | 20230708 | 1829 | 20230709 | 1557 | 2157340 | 1032 | Distribution Circuit | Equipment Failure/Involved | Underground | 2331 | 324231 | 36.7141 | -121.6562 | No | Partly Cloudy;32-90 F | Connector or Splice (UG) | Failed/Faulted | 23-0090156 | UG | Sus | 45875900 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855899 | 0 | Non-EPSS | N | 2023 | C-GRD
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6805 | 20230708 | 2041 | 20230709 | 1022 | 2157397 | 821 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 4105 | 36.9396 | -121.7419 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0090172 | OH | Sus | 45875841 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | Yes | No | 1855915 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | JUMPER | 115450 | 20230709 | 851 | 20230709 | 1313 | 2157600 | 223 | Distribution Circuit | Equipment Failure/Involved | Overhead | 670 | 36343 | 36.3373 | -121.252 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 23-0079382 | OH | Sus | 45875844 | SOUTH BAY AND CENTRAL COAST | JUL | Open Circuit | 0 | No | No | No | 1855943 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | FUSE | 7865 | 20230709 | 1607 | 20230709 | 1702 | 2157755 | 55 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 1705 | 36.3588 | -120.7683 | No | Clear;32-90 F | Lightning Arrestor | Broken | 23-0090247 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1855974 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1103 | 182011103 | OTHER | #1 PHASE COIS @ T931 TWD 3548 | 20230709 | 1617 | 20230709 | 1755 | 2157806 | 98 | Distribution Circuit | Company Initiated | Operating error | 476 | 43048 | 36.7109 | -121.6625 | No | Clear;32-90 F | Cable Termination(live front | Normal | 23-0090253 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Open Circuit | 0 | No | No | No | 1855982 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | TRANSFORMER | 411452040494 | 20230710 | 1643 | 20230711 | 1342 | 2158744 | 1259 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 8813 | 36.4112 | -121.9067 | No | Clear;32-90 F | Cutout- fuse holder | Failed/Faulted | 23-0090606 | OH | Sus | 35466800 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1856240 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 7989 | 20230710 | 1744 | 20230710 | 1920 | 2158904 | 96 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 204 | 19584 | 36.9817 | -121.8645 | No | Clear;32-90 F |  |  | 23-0090626 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1856250 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 2993 | 20230710 | 2209 | 20230710 | 2327 | 2159048 | 78 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 106 | 8286 | 36.9722 | -122.0306 | No | Clear;32-90 F |  |  | 23-0090659 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1856289 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | TRANSFORMER | 413044558540 | 20230711 | 722 | 20230711 | 1328 | 2159340 | 366 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 732 | 36.918 | -121.3794 | No | Clear;32-90 F |  |  | 23-0090705 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1856333 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 12868 | 20230711 | 1008 | 20230711 | 1552 | 2159753 | 344 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4054 | 1260191 | 37.0954 | -122.1442 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0090767 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1856489 | 0 | EPSS Ckt | Y | 2023 | C- GRD
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 412126652012 | 20230711 | 1058 | 20230711 | 1111 | 2159413 | 13 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 13 | 36.7319 | -121.6901 | No | Clear;32-90 F | Fuse | Burned Open | 23-0090806 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1856513 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | FUSE | 4823 | 20230711 | 1331 | 20230711 | 1415 | 2159940 | 44 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 278 | 36.9428 | -121.4451 | No | Clear;32-90 F |  |  | 23-0090922 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1856565 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | RECLOSER | 7086 | 20230711 | 1447 | 20230711 | 1513 | 2159993 | 26 | Distribution Circuit | 3rd Party | Metallic Balloon | 131 | 3406 | 36.2942 | -121.1997 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0090944 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1856571 | 0 | EPSS Ckt | N | 2023 | A- B PHASE
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 12868 | 20230711 | 1559 | 20230712 | 221 | s1856592 | 622 | Distribution Circuit | 3rd Party | Vehicle | 4054 | 431819 | 37.0954 | -122.1442 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0090767 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1856592 | 0 | EPSS Ckt | Y | 2023 | A PHASE
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | T2486 | 20230711 | 1945 | 20230712 | 1915 | 2160231 | 1410 | Distribution Circuit | Equipment Failure/Involved | Underground | 4 | 2934 | 37.0108 | -121.869 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0091072 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1856633 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | RECLOSER | 7002 | 20230711 | 2142 | 20230712 | 446 | 2160267 | 424 | Distribution Circuit | Equipment Failure/Involved | Overhead | 138 | 37660 | 35.9663 | -121.1146 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0091044 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1856611 | 0 | EPSS Ckt | Y | 2023 | B-C-
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | OCB | 1102/2 | 20230712 | 827 | 20230712 | 1342 | 2160514 | 315 | Distribution Circuit | 3rd Party | Other | 606 | 149944 | 36.0134 | -121.1674 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0091158 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1856721 | 0 | EPSS Ckt | Y | 2023 | A & GRD
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | TRANSFORMER | 412154048433 | 20230712 | 1101 | 20230712 | 2135 | 2160733 | 634 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 634 | 36.6351 | -121.6766 | No | Clear;32-90 F | Transformer | Leaking | 23-0091283 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1856840 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | TRANSFORMER | 412525149078 | 20230712 | 1122 | 20230713 | 351 | 2160580 | 989 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 989 | 36.6537 | -121.5499 | No | Overcast;32-90 F | Transformer | Failed/Faulted | 23-0091295 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1856842 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 9317 | 20230712 | 1132 | 20230712 | 1305 | 2160759 | 93 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 1953 | 36.9436 | -121.8607 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0091357 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1856882 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | OCB | 2105/2 | 20230712 | 1157 | 20230712 | 1533 | 2160787 | 216 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 3731 | 573510 | 37.0417 | -122.0255 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0091316 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1856851 | 0 | EPSS Ckt | Y | 2023 | A B & GRD INST
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 11054 | 20230712 | 1429 | 20230712 | 1617 | 2160953 | 108 | Distribution Circuit | Animal | Bird found | 307 | 33156 | 36.9775 | -121.7415 | No | Clear;32-90 F | Crossarm- Steel | Normal | 23-0091398 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1856896 | 0 | EPSS Ckt | Y | 2023 | B & C PHASE
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 6641 | 20230712 | 1553 | 20230712 | 1619 | 2160980 | 26 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 832 | 37.016 | -121.8161 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0091452 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1856905 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 11006 | 20230712 | 1640 | 20230713 | 141 | 2161073 | 541 | Distribution Circuit | Vegetation | Tree - fell into line | 104 | 18650 | 37.05 | -122.0657 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0091479 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1856911 | 0 | EPSS Ckt | Y | 2023 | A & GRD PHASE
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | TRANSFORMER | 315853917743 | 20230712 | 1944 | 20230712 | 2031 | 2161195 | 47 | Transformer only | Vegetation | Tree - grew into line | 4 | 188 | 36.9786 | -121.9204 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0091535 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1856932 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 9609 | 20230712 | 2145 | 20230713 | 204 | 2161241 | 259 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 8547 | 36.8938 | -121.3538 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0091583 | OH | Sus | 31655356 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | Yes | No | 1856964 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | RECLOSER | 7030 | 20230713 | 248 | 20230713 | 1201 | 2161281 | 553 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 106 | 58618 | 36.2025 | -120.8432 | No | Clear;32-90 F |  |  | 23-0091587 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1856968 | 0 | EPSS Ckt | Y | 2023 | AB
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | FUSE | 7865 | 20230713 | 814 | 20230713 | 1028 | 2161315 | 134 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 4154 | 36.3588 | -120.7683 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0091608 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1856981 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | RECLOSER | 258688 | 20230713 | 821 | 20230713 | 909 | 2161394 | 48 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 624 | 36.2774 | -121.2298 | No | Clear;32-90 F |  |  | 23-0091651 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1857023 | 0 | EPSS Ckt | Y | 2023 | A- B- & C PHASE
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | TRANSFORMER | 315271123543 | 20230713 | 859 | 20230713 | 1710 | 2161833 | 491 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 982 | 37.1357 | -122.1211 | No | Clear;32-90 F | Jumper | Burned Open | 23-0091996 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1857227 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 6641 | 20230713 | 928 | 20230713 | 1045 | 2161501 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 41 | 3157 | 36.6023 | -121.8968 | No | Partly Cloudy;32-90 F |  |  | 23-0091768 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1857159 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1101 | 182131101 | FUSE | 7977 | 20230713 | 1244 | 20230713 | 1341 | 2161707 | 57 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 570 | 36.5164 | -121.4325 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0091840 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1857187 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | OTHER | WIRE DOWN 1 SP/N/OF 413118657562 | 20230713 | 1629 | 20230713 | 1947 | 2161903 | 198 | Distribution Circuit | Equipment Failure/Involved | Overhead | 72 | 5381 | 36.8916 | -121.3545 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0092003 | OH | Sus | 31655314 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | Yes | 1857232 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | TRIP-SAVER | 6661 | 20230713 | 2237 | 20230714 | 2000 | 2162060 | 1283 | Distribution Circuit | Vegetation | Tree - grew into line | 19 | 24377 | 36.9247 | -121.8133 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0092089 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1857279 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 7005 | 20230714 | 446 | 20230714 | 833 | 2162105 | 227 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 3024 | 36.9961 | -121.7994 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0092172 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1857383 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 454176 | 20230714 | 512 | 20230714 | 1740 | 2162111 | 748 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 4675 | 36.994 | -121.7761 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Normal | 23-0092127 | OH | Sus | 45886807 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1857298 | 0 | EPSS Ckt | Y | 2023 | B & C PHASE
CENTRAL COAST | HOLLISTER | HOLLISTER-2103 | 182492103 | TRANSFORMER | 413057556226 | 20230714 | 635 | 20230714 | 1423 | 2162135 | 468 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 3744 | 36.854 | -121.3742 | No | Partly Cloudy;32-90 F | Transformer (OH) | Deteriorated | 23-0092142 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1857321 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 737512 | 20230714 | 842 | 20230714 | 1711 | 2162271 | 509 | Distribution Circuit | Vegetation | Tree - fell into line | 918 | 33036 | 37.0467 | -122.074 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0092191 | OH | Sus | 45887550 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1857413 | 0 | EPSS Ckt | Y | 2023 | N/A
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | FUSE | 863 | 20230714 | 1227 | 20230714 | 1338 | 2162593 | 71 | Distribution Circuit | Animal | Bird found | 15 | 1065 | 36.9847 | -121.9657 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0092382 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1857518 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | TRANSFORMER | 315256823140 | 20230714 | 1250 | 20230714 | 1912 | 2162548 | 382 | Transformer only | Equipment Failure/Involved | Electrical Overload | 10 | 3820 | 37.1248 | -122.126 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0092307 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1857497 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SOLEDAD-2101 | 182052101 | RECLOSER | 7048 | 20230714 | 1254 | 20230714 | 2042 | 2162636 | 468 | Distribution Circuit | 3rd Party | Vehicle | 173 | 63588 | 36.4253 | -121.3075 | No | Clear;32-90 F | Pole-Wood | On Ground | 23-0092357 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1857512 | 0 | EPSS Ckt | Y | 2023 | A PH GRD
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | RECLOSER | 3010 | 20230714 | 1304 | 20230714 | 2133 | 2162646 | 509 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 465 | 196081 | 36.28 | -121.3077 | No | Clear;Above 90 |  |  | 23-0092362 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Three Phase Fault | 0 | No | No | No | 1857513 | 0 | EPSS Ckt | Y | 2023 | A- B- & C PHASE
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 96986 | 20230714 | 1600 | 20230715 | 1011 | 2162791 | 1091 | Distribution Circuit | Vegetation | Tree - branch fell on line | 827 | 299498 | 37.1719 | -122.1648 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0092438 | OH | Sus | 31655569 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | Yes | No | 1857534 | 0 | EPSS Ckt | Y | 2023 | A & C PHASE
CENTRAL COAST | SALINAS | BORONDA-1102 | 182461102 | FUSE | 23375 | 20230715 | 226 | 20230715 | 1714 | 2163092 | 886 | Distribution Circuit | 3rd Party | Vehicle | 7 | 6501 | 36.6839 | -121.673 | No | Overcast-Fog;32-90 F | Conductor- Underground | Broken | 23-0092529 | UG | Sus | 31655681 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1857594 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6647 | 20230715 | 1454 | 20230716 | 1333 | 2163525 | 1359 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 10449 | 37.0266 | -121.7801 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0092688 | OH | Sus | 45887917 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1857717 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | JUMPER | OJ NE/OF 3533 | 20230715 | 1858 | 20230715 | 2026 | 2163803 | 88 | Distribution Circuit | Equipment Failure/Involved | Overhead | 141 | 12265 | 36.6922 | -121.7072 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 23-0092708 | OH | Sus | 45888755 | SOUTH BAY AND CENTRAL COAST | JUL | Open Circuit | 0 | No | No | No | 1857728 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 922576 | 20230716 | 113 | 20230716 | 1310 | 2163958 | 717 | Distribution Circuit | Vegetation | Tree - fell into line | 306 | 87727 | 37.0994 | -122.0532 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0092750 | OH | Sus | 31655761 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1857769 | 0 | EPSS Ckt | Y | 2023 | B GRD
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | RECLOSER | 10932 | 20230716 | 320 | 20230716 | 331 | 2163977 | 11 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 362 | 3982 | 36.938 | -121.7772 | No | Overcast-Fog;32-90 F |  |  | 23-0092757 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1857776 | 0 | EPSS Ckt | N | 2023 | C GRD
CENTRAL COAST | COAST | ERTA-0404 | 83510404 | SWITCH | 5797 | 20230716 | 812 | 20230716 | 2324 | 2164063 | 874 | Distribution Circuit | 3rd Party | Vehicle | 1338 | 316664 | 36.9396 | -121.7801 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0092770 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1857798 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 4645 | 20230716 | 1006 | 20230716 | 1437 | 2164134 | 271 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 256 | 69376 | 36.5668 | -121.7548 | No | Clear;32-90 F |  |  | 23-0092802 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1857832 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | JUMPER | WIRE DOWN 2 SP SS OF CGC 315243520835 | 20230716 | 1014 | 20230717 | 325 | 2164196 | 1031 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2062 | 37.0606 | -122.1296 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0092808 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | Yes | 1857837 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1104 | 182201104 | TRANSFORMER | 412602645982 | 20230716 | 1431 | 20230716 | 1700 | 2164317 | 149 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 596 | 36.5698 | -121.5199 | No | Clear;32-90 F |  |  | 23-0092861 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1857890 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRANSFORMER | 315489122363 | 20230716 | 1443 | 20230716 | 1619 | 2164323 | 96 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 384 | 37.1037 | -122.0478 | No | Clear;32-90 F |  |  | 23-0092867 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1857894 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | RECLOSER | 5402 | 20230716 | 1852 | 20230716 | 2017 | 2164597 | 85 | Distribution Circuit | Vegetation | Tree - branch fell on line | 952 | 80920 | 37.0104 | -122.0341 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0092896 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1857917 | 0 | EPSS Ckt | Y | 2023 | A GRD
CENTRAL COAST | KING CITY | OILFIELDS-1102 | 182391102 | RECLOSER | 41992 | 20230716 | 1913 | 20230717 | 957 | 2164613 | 884 | Distribution Circuit | Vegetation | Tree - branch fell on line | 46 | 40664 | 35.9889 | -120.88 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0092902 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1857923 | 0 | EPSS Ckt | Y | 2023 | A & C PHASE
CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | OCB | 1103/2 | 20230717 | 607 | 20230717 | 927 | 2165028 | 200 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 4000 | 36.0134 | -121.1673 | No | Clear;32-90 F |  |  | 23-0092984 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1857997 | 0 | EPSS Ckt | Y | 2023 | A-C
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | JUMPER | OJ 2 SS OUF 9187 | 20230717 | 807 | 20230717 | 1207 | 2165080 | 240 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 1920 | 35.9822 | -121.126 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0093008 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1858017 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | JUMPER | BURNED OJ SS OF 465 | 20230717 | 1101 | 20230717 | 2245 | 2165780 | 704 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1408 | 36.304 | -121.8762 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 23-0093320 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Open Circuit | 0 | No | No | No | 1858230 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411977553210 | 20230717 | 1147 | 20230717 | 1702 | 2165116 | 315 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 315 | 36.7648 | -121.7404 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0093155 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1858179 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | RECLOSER | BL 1101 | 20230717 | 1228 | 20230717 | 1352 | 2165559 | 84 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 744 | 48384 | 37.0926 | -122.0966 | No | Clear;32-90 F |  |  | 23-0093171 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1858184 | 0 | EPSS Ckt | Y | 2023 | A & B PHASE
CENTRAL COAST | COAST | PAUL SWEET-2103 | 83252103 | JUMPER | UN NUMBERED FUCO | 20230717 | 1633 | 20230717 | 1653 | 2165846 | 20 | Distribution Circuit | Company Initiated | Personnel- company | 77 | 1540 | 36.983 | -122.0209 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0091110 | OH | Sus | 35274381 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1858240 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2101 | 182492101 | FUSE | 9349 | 20230717 | 1645 | 20230718 | 1907 | 2165851 | 1582 | Distribution Circuit | Equipment Failure/Involved | Underground | 107 | 96179 | 36.857 | -121.4125 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0093384 | UG | Sus | 31656012 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1858253 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DEL MONTE-2104 | 182222104 | RECLOSER | 2762 | 20230717 | 1727 | 20230717 | 1918 | 2165879 | 111 | Distribution Circuit | Vegetation | Tree - branch fell on line | 420 | 46537 | 36.5581 | -121.7505 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0093386 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1858255 | 0 | EPSS Ckt | Y | 2023 | AB
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 3187 | 20230718 | 18 | 20230718 | 349 | 2166119 | 211 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 94 | 14498 | 36.967 | -122.0058 | No | Partly Cloudy;32-90 F |  |  | 23-0093478 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1858317 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 5232 | 20230718 | 1052 | 20230718 | 1207 | 2166566 | 75 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 788 | 59100 | 37.0752 | -122.054 | No | Clear;32-90 F |  |  | 23-0093623 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1858489 | 0 | EPSS Ckt | Y | 2023 | A GRD
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | TRANSFORMER | 316229316302 | 20230718 | 2005 | 20230719 | 327 | 2167056 | 442 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 5746 | 36.9404 | -121.7913 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0093936 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1858581 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1106 | 182011106 | FUSE | 5097 | 20230719 | 127 | 20230719 | 506 | 2167314 | 219 | Distribution Circuit | Equipment Failure/Involved | Overhead | 104 | 22776 | 36.6553 | -121.6572 | No | Overcast-Fog;32-90 F | Crossarm- Wood | Broken | 23-0093989 | OH | Sus | 31656039 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1858627 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 12124 | 20230719 | 2059 | 20230719 | 2154 | 2168498 | 55 | Distribution Circuit | Vegetation | Tree - branch fell on line | 480 | 26400 | 37.1677 | -122.1662 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0094402 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1858931 | 0 | EPSS Ckt | Y | 2023 | A&B
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | RECLOSER | 7004 | 20230720 | 1049 | 20230720 | 1318 | 2168843 | 149 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 149 | 22201 | 35.9367 | -121.0781 | No | Clear;32-90 F |  |  | 23-0094613 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859085 | 0 | EPSS Ckt | Y | 2023 | B/GRD
CENTRAL COAST | HOLLISTER | SAN BENITO 2102 | 182742102 | TRANSFORMER | 412822056636 | 20230720 | 1622 | 20230720 | 2153 | 2169208 | 331 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 1986 | 36.8632 | -121.4547 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0094904 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859168 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 1661 | 20230720 | 1758 | 20230720 | 1920 | 2169277 | 82 | Distribution Circuit | Animal | Bird found | 17 | 1394 | 36.9853 | -122.0302 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0094910 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1859173 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | FUSE | 5077 | 20230720 | 1945 | 20230721 | 340 | 2169261 | 475 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1425 | 36.6992 | -121.5727 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0094925 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | Yes | 1859180 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 3477 | 20230720 | 2200 | 20230721 | 448 | 2169375 | 408 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 816 | 36.9641 | -121.7651 | No | Partly Cloudy;32-90 F | Conductor- Underground | Burned/flashed | 23-0094951 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1859199 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | TRIP-SAVER | 40461 | 20230721 | 1046 | 20230721 | 1726 | 2169845 | 400 | Distribution Circuit | 3rd Party | Vehicle | 283 | 46592 | 36.5481 | -121.9108 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0095163 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1859416 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | JUMPER | BURNT FB JUMPER | 20230721 | 1201 | 20230721 | 1349 | 2169922 | 108 | Distribution Circuit | Equipment Failure/Involved | Overhead | 510 | 52800 | 36.9598 | -122.0582 | No | Clear;32-90 F | Jumper | Burned Open | 23-0095252 | OH | Sus | 45895639 | SOUTH BAY AND CENTRAL COAST | JUL | Open Circuit | 0 | No | No | No | 1859435 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | RECLOSER | 11056 | 20230721 | 1333 | 20230721 | 1358 | 2170012 | 25 | Distribution Circuit | Company Initiated | Personnel- company | 345 | 8625 | 36.9937 | -122.0299 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0095307 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1859454 | 1 | EPSS Ckt | Y | 2023 | A-GRD
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | RECLOSER | 2642 | 20230721 | 1433 | 20230721 | 1439 | 2170066 | 6 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 285 | 1710 | 36.5933 | -121.8948 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0095349 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859461 | 0 | EPSS Ckt | N | 2023 | C-GRD
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411986750359 | 20230721 | 1519 | 20230722 | 1825 | 2170014 | 1626 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 1626 | 36.685 | -121.7349 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0095368 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859470 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1102 | 182011102 | TRANSFORMER | T0364 | 20230721 | 2142 | 20230721 | 2252 | 2170438 | 70 | Transformer only | Equipment Failure/Involved | Underground | 27 | 1890 | 36.6847 | -121.62 | No | Clear;32-90 F | Connector or Splice (UG) | Failed/Faulted | 23-0095454 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1859514 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 11471 | 20230721 | 2323 | 20230722 | 210 | 2170483 | 167 | Distribution Circuit | 3rd Party | Vehicle | 13 | 2171 | 36.869 | -121.7445 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0095489 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859548 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | TRANSFORMER | 315248320980 | 20230722 | 9 | 20230722 | 541 | 2170500 | 332 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 332 | 37.0648 | -122.1296 | No | Clear;32-90 F |  |  | 23-0095504 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1859566 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | RECLOSER | 7066 | 20230722 | 441 | 20230722 | 837 | 2170535 | 236 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 292 | 68877 | 36.0489 | -120.9121 | No | Partly Cloudy;32-90 F |  |  | 23-0095496 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1859555 | 0 | EPSS Ckt | Y | 2023 | B&C
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | OCB | 1104/2 | 20230722 | 544 | 20230722 | 1227 | 2170544 | 403 | Distribution Circuit | Equipment Failure/Involved | Overhead | 363 | 112543 | 36.5092 | -121.4466 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0095498 | OH | Sus | 31656525 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1859559 | 0 | EPSS Ckt | N | 2023 | B&GRD
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | TRANSFORMER | 412140449740 | 20230722 | 919 | 20230722 | 1029 | 2170731 | 70 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 700 | 36.6693 | -121.6816 | No | Overcast;32-90 F | Fuse | Broken | 23-0095539 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859641 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1102 | 182031102 | RECLOSER | 728782 | 20230722 | 1644 | 20230722 | 1904 | 2171018 | 140 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 62 | 6343 | 36.2711 | -121.0646 | No | Clear;Above 90 |  |  | 23-0095587 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1859679 | 0 | EPSS Ckt | Y | 2023 | A&B INST
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 11054 | 20230723 | 637 | 20230723 | 808 | 2171316 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 307 | 27937 | 36.9775 | -121.7415 | No | Overcast-Fog;32-90 F |  |  | 23-0095655 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1859752 | 0 | EPSS Ckt | Y | 2023 | AB
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 94770 | 20230723 | 1043 | 20230723 | 1514 | 2171414 | 271 | Distribution Circuit | Vegetation | Tree - fell into line | 2360 | 189887 | 37.0632 | -122.0057 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0095677 | OH | Sus | 45897610 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1859779 | 0 | EPSS Ckt | Y | 2023 | C-GRD
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 94770 | 20230723 | 1348 | 20230723 | 1804 | 2171590 | 256 | Distribution Circuit | Equipment Failure/Involved | Underground | 1897 | 142649 | 37.0632 | -122.0057 | No | Partly Cloudy;32-90 F | Conductor- Underground | Burned/flashed | 23-0095694 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859793 | 0 | EPSS Ckt | Y | 2023 | A-GRD
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | FUSE | 7929 | 20230723 | 1405 | 20230723 | 1515 | 2171599 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 420 | 36.4935 | -121.4965 | No | Partly Cloudy;Above 90 |  |  | 23-0095703 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859803 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | RECLOSER | 75304 | 20230723 | 1617 | 20230723 | 1657 | 2171666 | 40 | Distribution Circuit | Animal | Bird found | 923 | 20067 | 36.5245 | -121.8121 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0095707 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1859806 | 0 | EPSS Ckt | Y | 2023 | AB
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | TRANSFORMER | 412627342985 | 20230723 | 1636 | 20230723 | 1906 | 2171794 | 150 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 450 | 36.487 | -121.5077 | No | Clear;32-90 F | Transformer | Broken | 23-0095714 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859814 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1103 | 182011103 | TRANSFORMER | 412205950636 | 20230723 | 1757 | 20230724 | 216 | 2171859 | 499 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 6487 | 36.6945 | -121.6602 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 23-0095723 | OH | Sus | 31656646 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859824 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | RECLOSER | 2624 | 20230723 | 2308 | 20230724 | 109 | 2171964 | 121 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4576 | 553696 | 36.569 | -121.7955 | No | Partly Cloudy;32-90 F |  |  | 23-0095753 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859857 | 0 | EPSS Ckt | Y | 2023 | C&GRD
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | OTHER | 1102/2 | 20230724 | 125 | 20230724 | 1338 | 2172040 | 733 | Distribution Circuit | 3rd Party | Vehicle | 3421 | 642849 | 36.7313 | -121.6135 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0095764 | OH | Sus | 35472083 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1859864 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1109 | 182011109 | FUSE | 64189 | 20230724 | 645 | 20230724 | 811 | 2172115 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 352 | 30272 | 36.6774 | -121.6379 | No | Overcast-Fog;32-90 F |  |  | 23-0095798 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1859888 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | TRANSFORMER | 411982152794 | 20230724 | 947 | 20230724 | 1838 | 2172186 | 531 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 531 | 36.7528 | -121.7376 | No | Partly Cloudy;32-90 F | Transformer | Burned/flashed | 23-0095881 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1860000 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9133 | 20230724 | 1141 | 20230724 | 1547 | 2172133 | 246 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 3198 | 37.1779 | -122.12 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0095928 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1860040 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | TRANSFORMER | 414270827621 | 20230724 | 1216 | 20230724 | 1552 | 2172566 | 216 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 216 | 36.0776 | -120.9403 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0095987 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1860062 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1105 | 182011105 | SWITCH | 3317 | 20230724 | 1350 | 20230724 | 1436 | 2172661 | 46 | Distribution Circuit | Company Initiated | Return Circuit Normal | 2672 | 113894 | 36.733 | -121.6388 | No | Clear;32-90 F | Regulator | Burned/flashed | 23-0095764 | OH | Sus | 35472083 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1860086 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | BUENA VISTA-1104 | 182261104 | SWITCH | 4537 | 20230724 | 1530 | 20230724 | 1730 | 2172739 | 120 | Distribution Circuit | 3rd Party | Customer Equipment | 2 | 240 | 36.6547 | -121.6231 | No | Clear;32-90 F | Metering Equipment | Arcing | 23-0096146 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1860105 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 67520 | 20230725 | 947 | 20230725 | 1412 | 2173378 | 265 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2738 | 168107 | 36.9577 | -121.8525 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0096400 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1860350 | 0 | EPSS Ckt | Y | 2023 | B-GRD
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | RECLOSER | 9500 | 20230725 | 1421 | 20230725 | 1557 | 2173487 | 96 | Distribution Circuit | Vegetation | Tree - fell into line | 3663 | 351648 | 36.5582 | -121.7507 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0096613 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Multi-Fault | 0 | No | Yes | No | 1860417 | 0 | EPSS Ckt | Y | 2023 | AC GRD
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | RECLOSER | 779322 | 20230725 | 1701 | 20230726 | 250 | 2173769 | 589 | Distribution Circuit | Vegetation | Tree - fell into line | 169 | 4117 | 36.4868 | -121.7395 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0096738 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Multi-Fault | 0 | No | Yes | No | 1860432 | 0 | EPSS Ckt | Y | 2023 | BC GRD
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | RECLOSER | 438 | 20230726 | 9 | 20230726 | 1325 | 2173956 | 796 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 245 | 173510 | 36.4967 | -121.7313 | No | Clear;32-90 F |  |  | 23-0096816 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1860488 | 0 | EPSS Ckt | Y | 2023 | B&C
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 4999 | 20230726 | 407 | 20230726 | 558 | 2174013 | 111 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 1766 | 36.9914 | -121.9845 | No | Partly Cloudy;32-90 F |  |  | 23-0096827 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1860501 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | FUSE | 24972 | 20230726 | 754 | 20230726 | 910 | 2174235 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 47 | 3572 | 36.6772 | -121.673 | No | Overcast-Fog;32-90 F |  |  | 23-0096938 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1860633 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 7347 | 20230726 | 1400 | 20230727 | 352 | 2174538 | 832 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 9152 | 37.0409 | -121.9423 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0097193 | OH | Sus | 45902792 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1860737 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 4303 | 20230726 | 1429 | 20230726 | 2340 | 2174561 | 551 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 896 | 36.7265 | -121.7874 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0097178 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Multi-Fault | 0 | No | No | No | 1860736 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | JUMPER | 96738 | 20230726 | 1713 | 20230726 | 1834 | 2174723 | 81 | Distribution Circuit | Vegetation | Tree - branch fell on line | 284 | 22531 | 37.1111 | -122.1142 | No | Clear;32-90 F | Jumper | Burned Open | 23-0097233 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Open Circuit | 0 | No | No | No | 1860743 | 1 | EPSS Ckt | Y | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | RECLOSER | 80794 | 20230726 | 1930 | 20230726 | 2020 | 2174820 | 50 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 68 | 3400 | 36.7423 | -121.7676 | No | Overcast-Fog;32-90 F |  |  | 23-0097263 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Three Phase Fault | 0 | No | No | No | 1860756 | 0 | Non-EPSS | N | 2023 | A- B- C- INST
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | OTHER | WIRE DOWN 1 SPAN LD SIDE OF 8315 | 20230727 | 227 | 20230727 | 1300 | 2174947 | 633 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 13926 | 37.0996 | -122.1182 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0097347 | OH | Sus | 31657096 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | Yes | 1860786 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | RECLOSER | 7086 | 20230727 | 618 | 20230727 | 1121 | 2174982 | 303 | Distribution Circuit | Equipment Failure/Involved | Overhead | 131 | 18592 | 36.2942 | -121.1997 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0097365 | OH | Sus | 31657170 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1860797 | 0 | EPSS Ckt | N | 2023 | A B & GRD
CENTRAL COAST | KING CITY | LOS COCHES-1102 | 182151102 | FUSE | 99177 | 20230727 | 2031 | 20230728 | 14 | 2175811 | 223 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1115 | 36.3625 | -121.2766 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0097821 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1861054 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 94770 | 20230728 | 509 | 20230728 | 724 | 2175924 | 135 | Distribution Circuit | 3rd Party | Vehicle | 1904 | 79161 | 37.0632 | -122.0057 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0097887 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1861102 | 0 | EPSS Ckt | Y | 2023 | B- GRD
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 88094 | 20230728 | 614 | 20230728 | 755 | 2175938 | 101 | Distribution Circuit | Vegetation | Tree - fell into line | 247 | 21542 | 36.5966 | -121.9409 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0097916 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1861122 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | TRANSFORMER | 315917217321 | 20230728 | 951 | 20230728 | 1522 | 2176192 | 331 | Transformer only | Vegetation | Tree - grew into line | 11 | 3641 | 36.9671 | -121.8975 | No | Clear;32-90 F | Transformer | Arcing | 23-0098151 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1861311 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | TRANSFORMER | 411934243534 | 20230728 | 1018 | 20230728 | 1053 | 2176244 | 35 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 280 | 36.4977 | -121.7453 | No | Clear;32-90 F | Secondary | Normal | 23-0098021 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1861257 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | TRANSFORMER | 412507248953 | 20230728 | 1059 | 20230728 | 1526 | 2176285 | 267 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 267 | 36.6509 | -121.5556 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0098073 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1861283 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 6087 | 20230728 | 1228 | 20230728 | 1823 | 2176370 | 339 | Distribution Circuit | Vegetation | Tree - fell into line | 186 | 30623 | 37.0665 | -122.0336 | No | Clear;32-90 F | Anchor or Guy | Normal | 23-0098069 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1861293 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | SWITCH | 10657 | 20230728 | 1310 | 20230728 | 1425 | 2176530 | 75 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 2100 | 37.0467 | -122.02 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0098113 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1861300 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411986750359 | 20230728 | 1624 | 20230729 | 103 | 2176646 | 519 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 519 | 36.685 | -121.7349 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0098209 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1861331 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8137 | 20230728 | 1632 | 20230728 | 1831 | 2176618 | 119 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 1666 | 37.0581 | -121.9802 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0098217 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1861335 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SOLEDAD-2105 | 182052105 | RECLOSER | 3076 | 20230728 | 2209 | 20230730 | 1559 | 2176830 | 2510 | Distribution Circuit | 3rd Party | Customer Equipment | 182 | 30100 | 36.4974 | -121.4319 | No | Partly Cloudy;32-90 F | Conductor- Underground | Contaminated | 23-0098245 | UG | Sus | 45905870 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1861366 | 0 | EPSS Ckt | N | 2023 | B- GRD
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 8009 | 20230729 | 456 | 20230729 | 636 | 2176893 | 100 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 3900 | 36.6314 | -121.9328 | No | Partly Cloudy;32-90 F |  |  | 23-0098271 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1861387 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2103 | 83252103 | FUSE | 3103 | 20230729 | 614 | 20230729 | 908 | 2176910 | 174 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 6090 | 36.9811 | -122.0225 | No | Partly Cloudy;32-90 F |  |  | 23-0098286 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1861433 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | RECLOSER | 383718 | 20230729 | 705 | 20230729 | 1111 | 2176925 | 246 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 710 | 174660 | 36.5788 | -121.7198 | No | Clear;32-90 F |  |  | 23-0098276 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1861393 | 0 | EPSS Ckt | Y | 2023 | AB 50 INST
CENTRAL COAST | KING CITY | SOLEDAD-2104 | 182052104 | RECLOSER | 858388 | 20230729 | 1026 | 20230729 | 1228 | 2177074 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 116 | 14152 | 36.4021 | -121.3443 | No | Clear;32-90 F |  |  | 23-0098300 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1861457 | 0 | EPSS Ckt | Y | 2023 | BC
CENTRAL COAST | COAST | PAUL SWEET-2103 | 83252103 | RECLOSER | 98594 | 20230729 | 1744 | 20230729 | 1752 | 2177298 | 8 | Distribution Circuit | Company Initiated | Personnel- company | 648 | 5184 | 36.9816 | -122.0252 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0098363 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1861497 | 0 | EPSS Ckt | N | 2023 | A-GRD
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 9609 | 20230729 | 2013 | 20230729 | 2042 | 2177357 | 29 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 957 | 36.8938 | -121.3538 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0098381 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1861517 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | RECLOSER | 944178 | 20230729 | 2318 | 20230730 | 840 | 2177466 | 508 | Distribution Circuit | Vegetation | Tree - branch fell on line | 886 | 450088 | 37.0926 | -122.0964 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0098408 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1861544 | 0 | EPSS Ckt | Y | 2023 | A GRD
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 9665 | 20230730 | 438 | 20230730 | 932 | 2177521 | 294 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 2058 | 36.8549 | -121.7925 | No | Partly Cloudy;32-90 F |  |  | 23-0098441 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1861584 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | RECLOSER | 777828 | 20230730 | 834 | 20230730 | 948 | 2177581 | 74 | Distribution Circuit | 3rd Party | Customer Equipment | 1659 | 122766 | 36.9871 | -122.0358 | No | Partly Cloudy;32-90 F | Connector or Splice (UG) | Failed/Faulted | 23-0098434 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1861571 | 0 | EPSS Ckt | Y | 2023 | AB INST
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | TRANSFORMER | MTR#1008828327 | 20230730 | 1201 | 20230730 | 1930 | 2177668 | 449 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 449 | 36.9676 | -121.8802 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0098451 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1861599 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SOLEDAD-2105 | 182052105 | RECLOSER | 3076 | 20230730 | 1703 | 20230730 | 1709 | 2177895 | 6 | Distribution Circuit | 3rd Party | Customer Equipment | 182 | 1092 | 36.4974 | -121.4319 | No | Partly Cloudy;32-90 F | Circuit Breaker | Failed/Faulted | 23-0098465 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1861611 | 0 | EPSS Ckt | N | 2023 | B GRD
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | OCB | 1102/2 | 20230730 | 1938 | 20230730 | 2232 | 2177965 | 174 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2134 | 358206 | 36.6242 | -121.6886 | No | Clear;32-90 F |  |  | 23-0098485 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1861624 | 0 | EPSS Ckt | Y | 2023 | GRD
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 2819 | 20230731 | 545 | 20230731 | 1927 | 2178116 | 822 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 20808 | 37.0521 | -121.9787 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0098576 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1861726 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | RECLOSER | 7592 | 20230731 | 725 | 20230731 | 938 | 2178153 | 133 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 95 | 12635 | 36.2633 | -121.1535 | No | Partly Cloudy;32-90 F |  |  | 23-0098556 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1861690 | 0 | EPSS Ckt | Y | 2023 | A & C PHASE
CENTRAL COAST | MONTEREY | FORT ORD-2106 | 182402106 | OTHER | J408 TWD T1997 | 20230731 | 1412 | 20230801 | 222 | 2178715 | 730 | Distribution Circuit | 3rd Party | Vehicle | 34 | 24820 | 36.6587 | -121.7636 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0098762 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1861878 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | RECLOSER | BL 1101 | 20230731 | 1441 | 20230801 | 343 | 2178709 | 782 | Distribution Circuit | Vegetation | Tree - fell into line | 744 | 93490 | 37.0926 | -122.0966 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0098778 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | Yes | No | 1861876 | 0 | EPSS Ckt | Y | 2023 | B & C PH
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | TRANSFORMER | 412485245839 | 20230731 | 1519 | 20230801 | 1145 | 2178759 | 1226 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1226 | 36.5651 | -121.5601 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0098839 | OH | Sus | 35473598 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1861889 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 942143 | 20230801 | 646 | 20230801 | 855 | 2179121 | 129 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 148 | 19092 | 36.965 | -121.7331 | No | Overcast-Fog;32-90 F |  |  | 23-0098953 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1861965 | 0 | EPSS Ckt | Y | 2023 | B&C
CENTRAL COAST | KING CITY | KING CITY-1105 | 182031105 | OCB | 1105/2 | 20230801 | 651 | 20230801 | 747 | 2179122 | 56 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 966 | 54096 | 36.217 | -121.1269 | No | Partly Cloudy;32-90 F |  |  | 23-0098943 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1861957 | 0 | Non-EPSS | N | 2023 | B C PH
CENTRAL COAST | KING CITY | KING CITY-1106 | 182031106 | RECLOSER | 944510 | 20230801 | 651 | 20230801 | 915 | 2179135 | 144 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 124 | 17856 | 36.2071 | -121.1151 | No | Partly Cloudy;32-90 F |  |  | 23-0098945 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1861959 | 0 | EPSS Ckt | Y | 2023 | A & B
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | RECLOSER | 117328 | 20230801 | 656 | 20230801 | 1107 | 2179130 | 251 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 9036 | 36.8827 | -121.3274 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0098946 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1861960 | 0 | EPSS Ckt | Y | 2023 | A & C INST
CENTRAL COAST | SALINAS | DOLAN ROAD-1104 | 182381104 | TRANSFORMER | 411940754378 | 20230801 | 836 | 20230802 | 315 | 2179263 | 1119 | Transformer only | Equipment Failure/Involved | Electrical Overload | 7 | 7833 | 36.796 | -121.7539 | No | Clear;32-90 F | Transformer | Deteriorated | 23-0099031 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1862116 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 412068650284 | 20230801 | 1330 | 20230801 | 2155 | 2179524 | 505 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 505 | 36.6839 | -121.7061 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0099174 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1862172 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | TRANSFORMER | 413218757321 | 20230801 | 1334 | 20230801 | 1742 | 2179608 | 248 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 496 | 36.885 | -121.3199 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0099219 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1862184 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 12760 | 20230801 | 1810 | 20230801 | 1822 | 2179835 | 12 | Distribution Circuit | Company Initiated | Personnel- company | 549 | 6588 | 37.0674 | -121.9966 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0099322 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1862212 | 0 | EPSS Ckt | Y | 2023 | C-GRD
CENTRAL COAST | SALINAS | SALINAS-1106 | 182011106 | TRANSFORMER | 412216849611 | 20230801 | 2018 | 20230802 | 112 | 2179919 | 294 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 3528 | 36.6664 | -121.6547 | No | Overcast;32-90 F | Cutout- fuse holder | Broken | 23-0099351 | OH | Sus | 31657829 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1862237 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 12124 | 20230801 | 2037 | 20230802 | 2200 | 2179929 | 1523 | Distribution Circuit | Equipment Failure/Involved | Overhead | 480 | 32661 | 37.1677 | -122.1662 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0099343 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1862231 | 0 | EPSS Ckt | Y | 2023 | A B
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 12760 | 20230801 | 2044 | 20230801 | 2111 | 2179933 | 27 | Distribution Circuit | Equipment Failure/Involved | Overhead | 549 | 14823 | 37.0674 | -121.9966 | No | Clear;32-90 F | PT/CCVT | Failed/Faulted | 23-0099344 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Multi-Fault | 0 | No | No | No | 1862232 | 0 | EPSS Ckt | Y | 2023 | A-C-GRD
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 6409 | 20230802 | 321 | 20230802 | 2130 | 2180074 | 1089 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 106 | 49814 | 36.59 | -121.9115 | No | Overcast-Fog;32-90 F | Crossarm- Wood | Burned/flashed | 23-0099390 | OH | Sus | 31657885 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1862266 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | TRANSFORMER | 413698135647 | 20230802 | 851 | 20230802 | 1431 | 2180301 | 340 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 340 | 36.2934 | -121.1387 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0099461 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1862390 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | TRANSFORMER | T0127 | 20230802 | 945 | 20230802 | 1039 | 2180392 | 54 | Transformer only | Animal | Other | 5 | 270 | 36.4701 | -121.698 | No | Clear;32-90 F | Other | Normal | 23-0099534 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1862456 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6851 | 20230802 | 1052 | 20230803 | 28 | 2180364 | 816 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 13056 | 37.0421 | -121.8171 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0099541 | OH | Sus | 45908161 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1862459 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1101 | 182131101 | TRANSFORMER | 412998045775 | 20230802 | 1130 | 20230802 | 1710 | 2180504 | 340 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 340 | 36.5669 | -121.3853 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0099571 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1862475 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 7553 | 20230802 | 1218 | 20230802 | 1401 | 2180662 | 103 | Distribution Circuit | Animal | Squirrel | 28 | 2884 | 36.9803 | -121.9002 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 23-0099665 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1862512 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2101 | 182492101 | FUSE | 50501 | 20230802 | 1219 | 20230802 | 1348 | 2180649 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 158 | 14062 | 36.8354 | -121.4205 | No | Clear;32-90 F |  |  | 23-0099622 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1862497 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 6897 | 20230802 | 1259 | 20230803 | 120 | 2180697 | 741 | Distribution Circuit | Equipment Failure/Involved | Overhead | 65 | 6459 | 36.8561 | -121.7958 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0099672 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1862514 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | FUSE | 7546 | 20230802 | 1631 | 20230802 | 1741 | 2180858 | 70 | Distribution Circuit | 3rd Party | Metallic Balloon | 79 | 5267 | 36.3202 | -121.2365 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0099767 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1862539 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 2303 | 20230802 | 1758 | 20230803 | 309 | 2180904 | 551 | Distribution Circuit | Vegetation | Tree - branch fell on line | 112 | 52186 | 36.5894 | -121.8975 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0099788 | OH | Sus | 31659022 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1862551 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS COCHES-1101 | 182151101 | SWITCH | 3001 | 20230803 | 644 | 20230803 | 1527 | 2181125 | 523 | Distribution Circuit | 3rd Party | Vehicle | 100 | 18804 | 36.3658 | -121.281 | No | Fog;32-90 F | Pole-Wood | Broken | 23-0099892 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1862603 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | TRANSFORMER | 315808719740 | 20230803 | 705 | 20230803 | 1321 | 2181139 | 376 | Transformer only | Equipment Failure/Involved | Electrical Overload | 3 | 1128 | 37.0325 | -121.9349 | No | Partly Cloudy;32-90 F | Transformer | Deteriorated | 23-0099918 | OH | Sus | 45908585 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1862613 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | FUSE | 25449 | 20230803 | 709 | 20230803 | 925 | 2181141 | 136 | Distribution Circuit | 3rd Party | Vehicle | 12 | 1632 | 36.5571 | -121.4467 | No | Overcast;32-90 F | Pole-Wood | Normal | 23-0099996 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1862722 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 737512 | 20230803 | 814 | 20230803 | 1132 | 2181223 | 198 | Distribution Circuit | Vegetation | Tree - branch fell on line | 918 | 75840 | 37.0467 | -122.074 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0099960 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1862673 | 0 | EPSS Ckt | Y | 2023 | AC
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | TRANSFORMER | 412479445560 | 20230803 | 816 | 20230804 | 10 | 2181203 | 954 | Transformer only | Animal | Bird found | 4 | 3816 | 36.5574 | -121.5614 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0100065 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1862784 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 2451 | 20230803 | 853 | 20230803 | 1045 | 2181286 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 896 | 36.5723 | -121.9406 | No | Overcast-Fog;32-90 F |  |  | 23-0100039 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1862767 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CASSERLY-0401 | 83110401 | JUMPER | 12106 | 20230803 | 1126 | 20230804 | 842 | 2181563 | 1265 | Distribution Circuit | 3rd Party | Vehicle | 219 | 133098 | 36.9718 | -121.7649 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0100110 | OH | Sus | 35474649 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | Yes | 1862806 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412230054901 | 20230803 | 1147 | 20230803 | 1730 | 2181319 | 343 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 686 | 36.8118 | -121.6557 | No | Partly Cloudy;32-90 F | Transformer (OH) | Deteriorated | 23-0100105 | OH | Sus | 45910002 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1862802 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 2615 | 20230803 | 1413 | 20230804 | 340 | 2181704 | 807 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2421 | 37.0346 | -121.9969 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0100279 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | Yes | Yes | 1862870 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | RECLOSER | 12990 | 20230803 | 1941 | 20230804 | 1501 | 2181945 | 1160 | Distribution Circuit | Vegetation | Tree - fell into line | 788 | 76850 | 37.039 | -122.0214 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0100308 | OH | Sus | 31661486 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1862886 | 0 | EPSS Ckt | Y | 2023 | A&GRD
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | RECLOSER | 196060 | 20230803 | 2303 | 20230804 | 1546 | 2182006 | 1003 | Distribution Circuit | 3rd Party | Vehicle | 175 | 34565 | 36.7702 | -121.7645 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0100356 | OH | Sus | 31659006 | SOUTH BAY AND CENTRAL COAST | AUG | Three Phase Fault | 0 | No | Yes | No | 1862918 | 0 | Non-EPSS | N | 2023 | ABC
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | RECLOSER | 432 | 20230804 | 1 | 20230804 | 1442 | 2182019 | 881 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 323 | 277339 | 36.398 | -121.6493 | No | Clear;32-90 F |  |  | 23-0100360 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1862922 | 0 | EPSS Ckt | Y | 2023 | A-C
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 9089 | 20230804 | 140 | 20230804 | 814 | 2182027 | 394 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 2758 | 36.7764 | -121.3109 | No | Clear;32-90 F |  |  | 23-0100370 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1862929 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 942143 | 20230804 | 655 | 20230804 | 1043 | 2182074 | 228 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 148 | 33066 | 36.965 | -121.7331 | No | Overcast-Fog;32-90 F |  |  | 23-0100413 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1862944 | 0 | EPSS Ckt | Y | 2023 | B AND C PH
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | TRANSFORMER | 411283846710 | 20230804 | 1026 | 20230804 | 1411 | 2182343 | 225 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 900 | 36.579 | -121.9704 | No | Overcast-Fog;32-90 F |  |  | 23-0100606 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863111 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5629 | 20230804 | 1330 | 20230804 | 1455 | 2182414 | 85 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 1700 | 37.1128 | -122.048 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0100670 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1863138 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS COCHES-1102 | 182151102 | TRANSFORMER | 413196739614 | 20230804 | 1807 | 20230804 | 1922 | 2182394 | 75 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 75 | 36.3986 | -121.3129 | No | Strong Winds-Clear;32-90 F | Cutout- fuse holder | Broken | 23-0100792 | OH | Sus | 31661961 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863172 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | RECLOSER | 80794 | 20230805 | 247 | 20230805 | 254 | 2182818 | 7 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 69 | 483 | 36.7423 | -121.7676 | No | Overcast-Fog;32-90 F |  |  | 23-0100832 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1863215 | 0 | Non-EPSS | N | 2023 | A-C
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 4303 | 20230805 | 315 | 20230805 | 1002 | 2182824 | 407 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 813 | 36.7265 | -121.7874 | No | Clear;32-90 F | Jumper | Broken | 23-0100838 | OH | Sus | 45912114 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863221 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1105 | 182011105 | FUSE | 20419 | 20230805 | 702 | 20230805 | 840 | 2182946 | 98 | Distribution Circuit | Animal | Bird found | 23 | 2254 | 36.7041 | -121.6323 | No | Overcast-Fog;32-90 F | Fuse | Burned Open | 23-0100856 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863268 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | RECLOSER | BL 1101 | 20230805 | 811 | 20230805 | 956 | 2182899 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 744 | 48300 | 37.0926 | -122.0966 | No | Partly Cloudy;32-90 F |  |  | 23-0100852 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1863243 | 0 | EPSS Ckt | Y | 2023 | B & C PHASE
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | FUSE | 53217 | 20230805 | 845 | 20230805 | 1020 | 2182941 | 95 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 3195 | 36.9693 | -121.9812 | No | Partly Cloudy;32-90 F |  |  | 23-0100867 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863298 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1109 | 182011109 | FUSE | 3173 | 20230805 | 932 | 20230805 | 1110 | 2182992 | 98 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 915 | 36.6609 | -121.5904 | No | Overcast;32-90 F |  |  | 23-0100881 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863307 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 9381 | 20230805 | 1105 | 20230805 | 1620 | 2183049 | 315 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 315 | 37.0891 | -122.2717 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0100878 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1863305 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | SWITCH | 97574 | 20230805 | 1319 | 20230805 | 1328 | 2183150 | 9 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 55 | 495 | 36.9865 | -121.752 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0100908 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863319 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | JUMPER | OJ @ CGC # 315353821141 | 20230805 | 1415 | 20230805 | 2353 | 2183164 | 578 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2890 | 37.0699 | -122.0932 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0100918 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | Yes | No | 1863326 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | RECLOSER | 370948 | 20230805 | 2040 | 20230806 | 1100 | 2183374 | 860 | Distribution Circuit | Vegetation | Tree - branch fell on line | 718 | 101981 | 36.5785 | -121.7263 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0100950 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1863350 | 0 | EPSS Ckt | Y | 2023 | A & B PH
CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | OCB | 1103/2 | 20230805 | 2200 | 20230806 | 139 | 2183434 | 219 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 4380 | 36.0134 | -121.1673 | No | Clear;32-90 F |  |  | 23-0100958 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863358 | 0 | EPSS Ckt | Y | 2023 | B PHSE & GRD
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | RECLOSER | 2144 | 20230806 | 8 | 20230806 | 1539 | 2183473 | 931 | Distribution Circuit | Vegetation | Tree - grew into line | 665 | 619115 | 36.5941 | -121.8893 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0100976 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1863378 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0421 | 182440421 | TRANSFORMER | 411440748066 | 20230806 | 853 | 20230806 | 1105 | 2183547 | 132 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 1584 | 36.6178 | -121.9186 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0101007 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863419 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | HOLLISTER | TRES PINOS-1111 | 183221111 | RECLOSER | 203126 | 20230806 | 1401 | 20230806 | 1635 | 2183660 | 154 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 46 | 7084 | 36.787 | -121.3587 | No | Clear;Above 90 |  |  | 23-0101015 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1863427 | 0 | EPSS Ckt | Y | 2023 | B & C PHASE
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | JUMPER | WIRE DOWN SS OF CGC #315680920572 | 20230806 | 1417 | 20230806 | 2205 | 2183707 | 468 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 2524 | 37.0553 | -121.9817 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0101032 | OH | Sus | 31662122 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1863432 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1109 | 182011109 | TRANSFORMER | 412355549907 | 20230806 | 1946 | 20230807 | 446 | 2183827 | 540 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 6480 | 36.6758 | -121.6084 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0101057 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863455 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRANSFORMER | 315413021641 | 20230806 | 2036 | 20230807 | 131 | 2183840 | 295 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1180 | 37.0836 | -122.0731 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 23-0101072 | OH | Sus | 45914309 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863471 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 7771 | 20230807 | 27 | 20230808 | 256 | 2183917 | 1584 | Distribution Circuit | Equipment Failure/Involved | Underground | 5 | 7920 | 36.9842 | -121.8981 | No | Partly Cloudy;32-90 F | Conductor- Underground | Deteriorated | 23-0101089 | UG | Sus | 35475448 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863487 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 9629 | 20230807 | 414 | 20230807 | 548 | 2183972 | 94 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 464 | 43616 | 36.5853 | -121.9054 | No | Partly Cloudy;32-90 F |  |  | 23-0101095 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1863498 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1104 | 182201104 | OCB | 1104/2 | 20230807 | 448 | 20230807 | 1243 | 2183986 | 475 | Distribution Circuit | 3rd Party | Vehicle | 682 | 91617 | 36.6139 | -121.5666 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0101097 | OH | Sus | 35475466 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | Yes | No | 1863497 | 0 | EPSS Ckt | N | 2023 | A B TIME
CENTRAL COAST | KING CITY | KING CITY-1101 | 182031101 | TRANSFORMER | 413726032750 | 20230807 | 834 | 20230807 | 1009 | 2184199 | 95 | Transformer only | Unknown Cause | Patrol - found nothing | 19 | 1805 | 36.2134 | -121.1279 | No | Clear;32-90 F |  |  | 23-0101200 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863659 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 46449 | 20230807 | 1106 | 20230807 | 1736 | 2184458 | 390 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 390 | 37.0276 | -121.9487 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0101256 | OH | Sus | 45915834 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | Yes | No | 1863700 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | TRANSFORMER | 414228540760 | 20230807 | 1148 | 20230807 | 1804 | 2184564 | 376 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 376 | 36.4362 | -120.9671 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0101308 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863737 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6853 | 20230807 | 1150 | 20230807 | 1255 | 2184581 | 65 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 59 | 3835 | 36.9342 | -121.7302 | No | Clear;32-90 F |  |  | 23-0101271 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1863709 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 7977 | 20230807 | 1303 | 20230807 | 1557 | 2184658 | 174 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2598 | 27663 | 36.9374 | -121.7267 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0101289 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1863718 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1109 | 182011109 | FUSE | 3173 | 20230807 | 1547 | 20230807 | 2306 | 2184859 | 439 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 6146 | 36.6609 | -121.5904 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0101435 | OH | Sus | 31662217 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1863774 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRANSFORMER | 315413021641 | 20230807 | 1700 | 20230807 | 1726 | 2184941 | 26 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 104 | 37.0836 | -122.0731 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0101421 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1863769 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 1217 | 20230807 | 2023 | 20230808 | 1158 | 2185093 | 935 | Distribution Circuit | Equipment Failure/Involved | Underground | 4 | 3740 | 36.4164 | -121.9139 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0101497 | UG | Sus | 31662076 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863827 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | TRIP-SAVER | 25695 | 20230808 | 30 | 20230808 | 1427 | 2185142 | 837 | Distribution Circuit | 3rd Party | Vehicle | 157 | 131409 | 36.7493 | -121.6573 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0101500 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | Yes | Yes | 1863830 | 0 | EPSS Ckt | N | 2023 | NA
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 12122 | 20230808 | 520 | 20230808 | 727 | 2185182 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 63 | 8001 | 37.0666 | -122.2288 | No | Partly Cloudy;32-90 F |  |  | 23-0101506 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863839 | 0 | EPSS Ckt | Y | 2023 | C&GRD
CENTRAL COAST | COAST | PAUL SWEET-2103 | 83252103 | FUSE | 8067 | 20230808 | 653 | 20230808 | 1238 | 2185199 | 345 | Distribution Circuit | Equipment Failure/Involved | Underground | 162 | 46391 | 36.9814 | -122.0135 | No | Overcast-Fog;32-90 F | Conductor- Underground | Deteriorated | 23-0101581 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863907 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | RECLOSER | 22412 | 20230808 | 916 | 20230809 | 352 | 2185455 | 1116 | Distribution Circuit | 3rd Party | Vehicle | 127 | 107936 | 36.4699 | -121.4635 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0101621 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | Yes | No | 1863995 | 0 | EPSS Ckt | N | 2023 | B/C GRD
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | JUMPER | JMPRS 1 N/O CGC 412877534455 | 20230808 | 958 | 20230808 | 1340 | 2185425 | 222 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 222 | 36.2559 | -121.4173 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0101613 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1863973 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | RECLOSER | 1132 | 20230808 | 1306 | 20230809 | 1418 | 2185829 | 1512 | Distribution Circuit | Animal | Bird found | 162 | 49168 | 36.3584 | -121.2034 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0101778 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1864058 | 0 | Non-EPSS | Y | 2023 | B & C PH
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 9651 | 20230808 | 1616 | 20230809 | 220 | 2185932 | 604 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1535 | 36.8577 | -121.7717 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0101913 | OH | Sus | 31662545 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1864099 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 6307 | 20230808 | 1655 | 20230808 | 1804 | 2186018 | 69 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 759 | 36.5407 | -121.8806 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0101917 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1864103 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | RECLOSER | 77978 | 20230808 | 2121 | 20230808 | 2244 | s1869965 | 83 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 155 | 12865 | 36.4795 | -121.4142 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0101621 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1869965 | 1 | EPSS Ckt | N | 2023 | B/C GRD
CENTRAL COAST | COAST | PAUL SWEET-2103 | 83252103 | OTHER | T0120 TWD T1130 | 20230808 | 2143 | 20230809 | 201 | 2186157 | 258 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 258 | 36.98 | -122.0195 | No | Partly Cloudy;32-90 F | Conductor- Underground | Deteriorated | 23-0101922 | UG | Sus | 31661922 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1864114 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 1735 | 20230808 | 2343 | 20230809 | 1024 | 2186197 | 641 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 51 | 13327 | 36.9987 | -121.8318 | No | Overcast;32-90 F |  |  | 23-0101975 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1864133 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 4645 | 20230809 | 243 | 20230809 | 1802 | 2186212 | 919 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 256 | 77029 | 36.5668 | -121.7548 | No | Clear;32-90 F |  |  | 23-0101979 | UG | Sus | 31662536 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1864139 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | RECLOSER | 399900 | 20230809 | 644 | 20230809 | 850 | 2186258 | 126 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 340 | 24979 | 36.5403 | -121.8762 | No | Overcast;32-90 F |  |  | 23-0101995 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1864151 | 0 | EPSS Ckt | Y | 2023 | B-C- INST
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 2987 | 20230809 | 742 | 20230809 | 921 | 2186287 | 99 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 9858 | 36.9761 | -121.7506 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 23-0102022 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1864164 | 0 | EPSS Ckt | Y | 2023 | C-GRD
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 3835 | 20230809 | 826 | 20230809 | 1119 | 2186631 | 173 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 173 | 36.9082 | -121.7892 | No | Overcast;32-90 F |  |  | 23-0102132 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1864351 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9771 | 20230809 | 829 | 20230809 | 1012 | 2186377 | 103 | Distribution Circuit | Animal | Bird found | 38 | 3914 | 37.1313 | -122.1209 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0102089 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1864329 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5427 | 20230809 | 1051 | 20230809 | 1438 | 2186607 | 227 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 9080 | 37.1235 | -122.1213 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0102082 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1864344 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | FUSE | 9245 | 20230809 | 1357 | 20230809 | 1448 | 2186800 | 51 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 153 | 36.132 | -121.0243 | No | Clear;32-90 F |  |  | 23-0102303 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1864392 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | RECLOSER | 11056 | 20230809 | 1439 | 20230809 | 1617 | 2186834 | 98 | Distribution Circuit | Vegetation | Tree - branch fell on line | 952 | 60074 | 36.9937 | -122.0299 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0102293 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1864391 | 0 | EPSS Ckt | Y | 2023 | A GRD
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | RECLOSER | 2142 | 20230810 | 21 | 20230810 | 118 | 2187206 | 57 | Distribution Circuit | Animal | Bird found | 752 | 42864 | 36.4806 | -121.7292 | No | Clear;32-90 F | Bushing | Normal | 23-0102470 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1864453 | 0 | EPSS Ckt | Y | 2023 | C-GRD
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | FUSE | 10259 | 20230810 | 237 | 20230810 | 1222 | 2187231 | 585 | Distribution Circuit | Equipment Failure/Involved | Underground | 193 | 41584 | 36.4825 | -121.7327 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0102480 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1864463 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS COCHES-1102 | 182151102 | TRANSFORMER | 413270738509 | 20230810 | 1027 | 20230810 | 1210 | 2187365 | 103 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 103 | 36.3685 | -121.2866 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Burned/flashed | 23-0102634 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1864653 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | JUMPER | OJ 1 S OF 9093 | 20230810 | 1528 | 20230811 | 158 | 2187948 | 630 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 2784 | 36.9796 | -122.0413 | No | Partly Cloudy;32-90 F | Secondary | Broken- wire on ground | 23-0102854 | OH | Sus | 31662778 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1864727 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | OCB | 1101/2 | 20230810 | 1831 | 20230810 | 1840 | 2188160 | 9 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 3539 | 31851 | 36.5569 | -121.8976 | No | Overcast;32-90 F | Other | Normal | 23-0102977 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1864757 | 0 | EPSS Ckt | N | 2023 | A GRD 50
CENTRAL COAST | KING CITY | SOLEDAD-2105 | 182052105 | FUSE | 30067 | 20230810 | 2156 | 20230811 | 1040 | 2188250 | 764 | Distribution Circuit | 3rd Party | Vehicle | 253 | 193292 | 36.4313 | -121.3336 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 23-0103053 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | Yes | No | 1864816 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | FUSE | 50715 | 20230811 | 259 | 20230811 | 1049 | 2188314 | 470 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 470 | 36.9447 | -121.464 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0103106 | OH | Sus | 31662951 | SOUTH BAY AND CENTRAL COAST | AUG | Three Phase Fault | 0 | No | Yes | No | 1864841 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412170756282 | 20230811 | 924 | 20230812 | 541 | 2188480 | 1217 | Transformer only | Equipment Failure/Involved | Underground | 1 | 1217 | 36.8493 | -121.677 | No | Clear;32-90 F | Service conductor | Broken | 23-0103217 | UG | Sus | 45924306 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1864962 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | JUMPER | WIRE DOWN 5 SP LD SIDE OF 3575 | 20230811 | 957 | 20230811 | 1906 | 2188673 | 549 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 4071 | 36.7317 | -121.7301 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0103323 | OH | Sus | 31662956 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | Yes | 1865010 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 36516 | 20230811 | 1150 | 20230811 | 1336 | 2188629 | 106 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 396 | 41959 | 37.0787 | -122.1336 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0103287 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1864983 | 0 | EPSS Ckt | Y | 2023 | B GRD
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | TRANSFORMER | 411827849923 | 20230811 | 1305 | 20230811 | 1539 | 2188682 | 154 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 1386 | 36.6721 | -121.7884 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0103370 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1865027 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | INDUSTRIAL ACRES-0415 | 182300415 | TRANSFORMER | 412287649452 | 20230811 | 1352 | 20230812 | 542 | 2188625 | 950 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 7600 | 36.6626 | -121.6311 | No | Clear;32-90 F | Transformer | Burned/flashed | 23-0103367 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1865025 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 412028253045 | 20230811 | 1425 | 20230812 | 1746 | 2188733 | 1641 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1641 | 36.7593 | -121.7227 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0103398 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1865037 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 7765 | 20230811 | 1537 | 20230811 | 2300 | 2188797 | 443 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 2 | 886 | 37.0278 | -121.9313 | No | Clear;32-90 F | Pole-Wood | Normal | 23-0103445 | OH | Sus | 31663052 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1865049 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1103 | 182131103 | RECLOSER | 727404 | 20230811 | 1820 | 20230812 | 1507 | 2188895 | 1247 | Distribution Circuit | 3rd Party | Vehicle | 15 | 3625 | 36.4982 | -121.4501 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0103495 | OH | Sus | 35480212 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1865069 | 0 | Non-EPSS | N | 2023 | NONE
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | JUMPER | OJ 1SP W/OF CGC #315274425400 | 20230811 | 1849 | 20230811 | 2103 | 2188896 | 134 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 134 | 37.1862 | -122.1239 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0103496 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1865070 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 7421 | 20230811 | 1856 | 20230811 | 1955 | 2188889 | 59 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 944 | 36.5933 | -121.8976 | No | Overcast;32-90 F | Fuse | Broken | 23-0103509 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1865078 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 412120754649 | 20230812 | 802 | 20230812 | 2012 | 2189002 | 730 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 2190 | 36.8051 | -121.6929 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 23-0103566 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1865141 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 27481 | 20230812 | 852 | 20230813 | 1102 | 2189078 | 1570 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 9420 | 36.6017 | -121.897 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 23-0103604 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1865210 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411954452971 | 20230812 | 1306 | 20230813 | 528 | 2189208 | 982 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 7856 | 36.7573 | -121.7476 | No | Partly Cloudy;32-90 F | Transformer | Deteriorated | 23-0103619 | OH | Sus | 45924766 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1865220 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | TRANSFORMER | T65724 | 20230812 | 1744 | 20230813 | 529 | 2189348 | 705 | Transformer only | Equipment Failure/Involved | Underground | 13 | 9165 | 36.6755 | -121.656 | No | Partly Cloudy;32-90 F | Transformer | Normal | 23-0103662 | UG | Sus | 45924691 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1865249 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 5071 | 20230814 | 626 | 20230814 | 815 | 2190039 | 109 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 10 | 1090 | 36.9718 | -121.7895 | No | Overcast-Fog;32-90 F |  |  | 23-0103874 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1865457 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 181 | 20230814 | 1114 | 20230814 | 1127 | 2190465 | 13 | Distribution Circuit | Vegetation | Tree - branch fell on line | 57 | 741 | 37.0628 | -122.0336 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0104005 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1865606 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 1007 | 20230814 | 1658 | 20230814 | 1857 | 2190760 | 119 | Distribution Circuit | Animal | Bird found | 2 | 238 | 36.9936 | -121.8644 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0104264 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1865672 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | RECLOSER | 3018 | 20230814 | 2155 | 20230815 | 1527 | 2191069 | 1052 | Distribution Circuit | 3rd Party | Vehicle | 55 | 57860 | 36.6662 | -121.6858 | No | Partly Cloudy;32-90 F | Pole-Wood | On Ground | 23-0104295 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1865702 | 0 | EPSS Ckt | N | 2023 | A & B PH
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 12081 | 20230815 | 637 | 20230815 | 846 | 2191249 | 129 | Distribution Circuit | Animal | Squirrel | 19 | 2451 | 36.9318 | -121.8071 | No | Overcast-Fog;32-90 F | Transformer (OH) | Normal | 23-0104397 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1865795 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRANSFORMER | 315451921035 | 20230815 | 656 | 20230815 | 1110 | 2191255 | 254 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 934 | 37.0672 | -122.0595 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0104409 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1865812 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | TRANSFORMER | 315414916816 | 20230815 | 1006 | 20230815 | 1427 | 2191523 | 261 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 261 | 36.9513 | -122.0701 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken | 23-0104650 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1865940 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | TRANSFORMER | 411954643354 | 20230815 | 1033 | 20230816 | 200 | 2191761 | 927 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 2781 | 36.493 | -121.7381 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0104729 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1865965 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1105 | 182011105 | SWITCH | 24483 | 20230815 | 1848 | 20230815 | 1900 | 2192145 | 12 | Distribution Circuit | 3rd Party | Metallic Balloon | 1865 | 22380 | 36.7032 | -121.6321 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0104801 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1865994 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | JUMPER | VERT JPRS 1 S/OF 50837 | 20230815 | 2158 | 20230816 | 304 | 2192268 | 306 | Distribution Circuit | 3rd Party | Vehicle | 15 | 4590 | 36.9217 | -121.3674 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0104830 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1866018 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 8075 | 20230816 | 1050 | 20230817 | 341 | 2192777 | 1011 | Distribution Circuit | Equipment Failure/Involved | Underground | 104 | 22934 | 36.5702 | -121.8015 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0105040 | UG | Sus | 31663696 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1866248 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2108 | 83252108 | FUSE | 9019 | 20230816 | 1105 | 20230817 | 48 | 2192740 | 823 | Distribution Circuit | 3rd Party | Vehicle | 179 | 44941 | 36.9884 | -121.9929 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0105020 | OH | Sus | 35481371 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1866232 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LOS OSITOS-2103 | 182082103 | SWITCH | 2237 | 20230816 | 1107 | 20230816 | 1130 | 2192826 | 23 | Distribution Circuit | Company Initiated | Return Circuit Normal | 38 | 874 | 36.3339 | -121.499 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0104947 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1866247 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | RECLOSER | 7030 | 20230816 | 1506 | 20230817 | 46 | 2193039 | 580 | Distribution Circuit | Equipment Failure/Involved | Overhead | 106 | 24514 | 36.2025 | -120.8432 | No | Clear;Above 90 | Crossarm- Wood | Broken | 23-0105179 | OH | Sus | 31663697 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1866294 | 0 | EPSS Ckt | Y | 2023 | AC
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 643 | 20230817 | 131 | 20230818 | 145 | 2193409 | 1454 | Distribution Circuit | Vegetation | Other ground vegetation | 4 | 4556 | 36.1985 | -121.7129 | No | Partly Cloudy-Fog;32-90 F | Fuse | Burned Open | 23-0105414 | OH | Sus | 45929997 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1866428 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 10613 | 20230817 | 216 | 20230817 | 1340 | 2193415 | 684 | Distribution Circuit | 3rd Party | Vehicle | 35 | 23940 | 36.9873 | -122.0256 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Broken | 23-0105365 | OH | Sus | 31663749 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1866405 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | RECLOSER | 4002 | 20230817 | 606 | 20230817 | 757 | 2193464 | 111 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 170 | 13920 | 36.8322 | -121.5312 | No | Clear;32-90 F |  |  | 23-0105378 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1866416 | 0 | EPSS Ckt | Y | 2023 | AC
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | TRANSFORMER | 413385536785 | 20230817 | 650 | 20230817 | 902 | 2193474 | 132 | Transformer only | Unknown Cause | Patrol - found nothing | 18 | 2376 | 36.3227 | -121.2466 | No | Partly Cloudy;32-90 F |  |  | 23-0105466 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1866501 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | OTHER | T1011 TWD T1012 | 20230817 | 743 | 20230817 | 1113 | 2193507 | 210 | Distribution Circuit | Equipment Failure/Involved | Underground | 26 | 5460 | 36.837 | -121.3921 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0105454 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1866480 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | TRANSFORMER | 412281851943 | 20230817 | 952 | 20230817 | 2157 | 2193514 | 725 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 11600 | 36.7311 | -121.6356 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0105518 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1866523 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1102 | 182031102 | FUSE | 9713 | 20230817 | 1006 | 20230817 | 1106 | 2193647 | 60 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 60 | 36.2175 | -121.1264 | No | Partly Cloudy;32-90 F | Secondary | Burned Open | 23-0105500 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1866518 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | RECLOSER | 549180 | 20230817 | 1022 | 20230817 | 1211 | 2193671 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 981 | 36.0057 | -121.2422 | No | Clear;32-90 F |  |  | 23-0105520 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1866525 | 0 | EPSS Ckt | Y | 2023 | A 50 INST
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 2021 | 20230817 | 1053 | 20230818 | 230 | 2193690 | 937 | Distribution Circuit | Equipment Failure/Involved | Underground | 5 | 4680 | 36.577 | -121.9383 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0105575 | UG | Sus | 45930758 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1866536 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | TRANSFORMER | 315676522766 | 20230817 | 1104 | 20230817 | 1819 | 2193701 | 435 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 435 | 37.1157 | -121.9837 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0105557 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1866531 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | BUENA VISTA-1102 | 182261102 | TRANSFORMER | 412234847989 | 20230817 | 1110 | 20230817 | 2054 | 2193709 | 584 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1752 | 36.6223 | -121.6472 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0105610 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1866561 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | RECLOSER | 460414 | 20230817 | 1353 | 20230817 | 1839 | 2193858 | 286 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 3640 | 36.7777 | -121.5971 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0105633 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1866570 | 0 | EPSS Ckt | Y | 2023 | B&C
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | FUSE | 9441 | 20230817 | 1532 | 20230817 | 1621 | 2193934 | 49 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 360 | 36.5466 | -121.7527 | No | Clear;32-90 F |  |  | 23-0105724 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1866582 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | TRANSFORMER | 412084047336 | 20230817 | 1733 | 20230818 | 407 | 2194061 | 634 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 4438 | 36.6025 | -121.6986 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0105768 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1866596 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | JUMPER | OPEN PRIMARY NEUTRAL | 20230817 | 1938 | 20230818 | 31 | 2194191 | 293 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 10468 | 37.0725 | -122.0843 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0105794 | OH | Sus | 31663885 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1866617 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | RECLOSER | 7070 | 20230817 | 2003 | 20230818 | 927 | 2194167 | 804 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 259 | 56646 | 35.9644 | -121.1175 | No | Clear;32-90 F |  |  | 23-0105787 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1866608 | 0 | EPSS Ckt | Y | 2023 | C PH & GRD
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 6559 | 20230817 | 2048 | 20230818 | 0 | 2194190 | 192 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 5952 | 36.9267 | -121.7459 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Together | 23-0105791 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1866616 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 11006 | 20230817 | 2107 | 20230817 | 2239 | 2194203 | 92 | Distribution Circuit | Animal | Bird found | 1965 | 161130 | 37.05 | -122.0657 | No | Clear;32-90 F | Fuse | Normal | 23-0105798 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1866620 | 0 | EPSS Ckt | Y | 2023 | C PH GRD
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 10718 | 20230817 | 2107 | 20230817 | 2217 | 2194210 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 926 | 64820 | 37.036 | -122.1068 | No | Partly Cloudy;32-90 F |  |  | 23-0105799 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1866621 | 0 | EPSS Ckt | N | 2023 | GR INST
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 11959 | 20230817 | 2217 | 20230818 | 1256 | 2194271 | 879 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 17580 | 36.9826 | -121.7685 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0105836 | OH | Sus | 45931270 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1866652 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | BUENA VISTA-1106 | 182261106 | FUSE | 24439 | 20230818 | 1128 | 20230818 | 1321 | 2194860 | 113 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1243 | 36.6272 | -121.5876 | No | Overcast;32-90 F |  |  | 23-0106141 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1866881 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 9463 | 20230818 | 1308 | 20230818 | 1511 | 2194944 | 123 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 60 | 7380 | 37.0697 | -122.0714 | No | Clear;32-90 F |  |  | 23-0106210 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1866900 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 12868 | 20230818 | 1542 | 20230818 | 1618 | 2195160 | 36 | Distribution Circuit | Company Initiated | Personnel- company | 4028 | 131582 | 37.0954 | -122.1442 | No | Clear;32-90 F | Conductor- Underground | Normal | 23-0106231 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1866908 | 0 | EPSS Ckt | Y | 2023 | A GRD
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRANSFORMER | 315241023220 | 20230818 | 1649 | 20230818 | 1908 | 2195269 | 139 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 417 | 37.127 | -122.1314 | No | Clear;32-90 F |  |  | 23-0106266 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1866918 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | TRANSFORMER | 411424545568 | 20230818 | 1846 | 20230818 | 2242 | 2195300 | 236 | Transformer only | 3rd Party | Vehicle | 12 | 2832 | 36.5489 | -121.9213 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0106270 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1866922 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | JUMPER | FB 1 SPAN LD SIDE OF CGC# 315575520514 | 20230819 | 140 | 20230819 | 444 | s1866972 | 184 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 6992 | 0 | 0 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0106258 | OH | Sus | 45933564 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1866972 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | OCB | 2101/2 | 20230819 | 201 | 20230819 | 1107 | 2195404 | 440 | Distribution Circuit | Equipment Failure/Involved | Underground | 7013 | 1807910 | 36.9926 | -121.9822 | No | Partly Cloudy;32-90 F | Interrupter | Failed/Faulted | 23-0106318 | UG | Sus | 31664008 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1866966 | 0 | Non-EPSS | N | 2023 | A & GRD
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | FUSE | 9875 | 20230819 | 605 | 20230819 | 822 | 2195429 | 137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1644 | 36.3081 | -121.2308 | No | Partly Cloudy;32-90 F |  |  | 23-0106331 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1866989 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 5090 | 20230819 | 722 | 20230819 | 751 | 2195451 | 29 | Distribution Circuit | Vegetation | Tree - branch fell on line | 434 | 12586 | 36.9804 | -121.892 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Normal | 23-0106329 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1866984 | 0 | EPSS Ckt | Y | 2023 | NA
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 2469 | 20230819 | 935 | 20230819 | 1123 | 2195563 | 108 | Distribution Circuit | Vegetation | Tree - branch fell on line | 32 | 3456 | 36.8825 | -121.7078 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0106349 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1867047 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | RECLOSER | 974130 | 20230819 | 1249 | 20230819 | 2204 | 2195658 | 555 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 11805 | 37.0448 | -121.9382 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0106364 | OH | Sus | 45934025 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1867053 | 0 | EPSS Ckt | Y | 2023 | C& GRD INST
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 411975054455 | 20230819 | 1503 | 20230819 | 2144 | 2195679 | 401 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 2807 | 36.7986 | -121.7441 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0106396 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1867071 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-1101 | 182221101 | TRANSFORMER | 411704448135 | 20230819 | 1520 | 20230819 | 1917 | 2195677 | 237 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 1422 | 36.6214 | -121.8284 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0106407 | OH | Sus | 31664101 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1867079 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | TRANSFORMER | T0134 | 20230819 | 1534 | 20230820 | 1430 | 2195771 | 1376 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 1376 | 36.1906 | -121.7085 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0106457 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1867123 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | PANOCHE-1103 | 253671103 | RECLOSER | 90540 | 20230819 | 1843 | 20230820 | 1335 | 2196868 | 1132 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 210 | 237720 | 36.6332 | -120.6422 | No | Clear;32-90 F |  |  | 23-0106654 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1867316 | 0 | EPSS Ckt | N | 2023 | A&C
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 1403 | 20230819 | 2159 | 20230820 | 1654 | 2196546 | 1135 | Distribution Circuit | Equipment Failure/Involved | Underground | 106 | 48766 | 36.5521 | -121.9031 | No | Overcast;32-90 F | Conductor- Underground | Burned/flashed | 23-0106544 | UG | Sus | 45934029 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1867216 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | TRANSFORMER | 315668917194 | 20230820 | 900 | 20230820 | 2055 | 2196819 | 715 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 7865 | 36.9625 | -121.9826 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0106629 | OH | Sus | 35482512 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1867298 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 68191 | 20230820 | 1319 | 20230820 | 1519 | 2196997 | 120 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 2280 | 36.9816 | -121.9026 | No | Clear;32-90 F |  |  | 23-0106680 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1867334 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 4269 | 20230820 | 1412 | 20230820 | 2253 | 2197020 | 521 | Distribution Circuit | Equipment Failure/Involved | Overhead | 54 | 5618 | 36.7712 | -121.6672 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0106695 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1867345 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | JUMPER | COIS @ J267 TWD 6177 | 20230820 | 1521 | 20230821 | 204 | 2197114 | 643 | Distribution Circuit | Equipment Failure/Involved | Overhead | 62 | 39866 | 36.9806 | -121.9087 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0106611 | OH | Sus | 35482096 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1867340 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 5131 | 20230820 | 1849 | 20230820 | 1906 | 2197213 | 17 | Distribution Circuit | Vegetation | Tree - branch fell on line | 113 | 1921 | 37.0902 | -122.0899 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0106737 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1867385 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 4295 | 20230820 | 2110 | 20230821 | 1048 | 2197365 | 818 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 20450 | 37.033 | -122.0105 | No | Overcast;32-90 F |  |  | 23-0106965 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1867617 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | RECLOSER | 9096 | 20230821 | 58 | 20230821 | 242 | 2197445 | 104 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2672 | 157590 | 36.5951 | -121.8454 | No | Partly Cloudy;32-90 F |  |  | 23-0106783 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1867433 | 0 | EPSS Ckt | Y | 2023 | A & GRD
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 5735 | 20230821 | 329 | 20230821 | 440 | 2197491 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 781 | 36.9481 | -121.7351 | No | Overcast;32-90 F |  |  | 23-0106799 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1867451 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 12868 | 20230821 | 955 | 20230821 | 1200 | 2197865 | 125 | Distribution Circuit | 3rd Party | Customer Equipment | 4033 | 403948 | 37.0954 | -122.1442 | No | Partly Cloudy;32-90 F | Circuit Breaker | Failed/Faulted | 23-0106949 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1867604 | 0 | EPSS Ckt | N | 2023 | A
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | JUMPER | NG POTHEAD CABLE | 20230821 | 1149 | 20230822 | 329 | 2198062 | 940 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 940 | 36.7251 | -121.7848 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0107115 | OH | Sus | 31664251 | SOUTH BAY AND CENTRAL COAST | AUG | Open Circuit | 0 | No | No | No | 1867688 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 688040 | 20230821 | 1239 | 20230821 | 1301 | 2198134 | 22 | Distribution Circuit | 3rd Party | Customer Equipment | 1701 | 37422 | 37.1308 | -122.1715 | No | Partly Cloudy;32-90 F | Circuit Breaker | Normal | 23-0107055 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1867664 | 0 | EPSS Ckt | N | 2023 | AB
CENTRAL COAST | COAST | PAUL SWEET-2108 | 83252108 | FUSE | 3855 | 20230821 | 1340 | 20230821 | 1546 | 2198272 | 126 | Distribution Circuit | Equipment Failure/Involved | Overhead | 230 | 28980 | 36.9684 | -122.0349 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken | 23-0107105 | OH | Sus | 45935663 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1867684 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 3277 | 20230821 | 1927 | 20230821 | 2110 | 2198675 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 686 | 36.6751 | -121.7023 | No | Clear;32-90 F |  |  | 23-0107287 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1867786 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | RECLOSER | 432 | 20230822 | 137 | 20230823 | 150 | 2198811 | 1453 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 324 | 233033 | 36.398 | -121.6493 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Deteriorated | 23-0107330 | OH | Sus | 31664475 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1867819 | 0 | EPSS Ckt | Y | 2023 | A & C PHASE
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | RECLOSER | 10260 | 20230822 | 625 | 20230822 | 1248 | 2198860 | 383 | Distribution Circuit | Equipment Failure/Involved | Overhead | 678 | 46368 | 36.9154 | -121.7787 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0107351 | OH | Sus | 31664292 | SOUTH BAY AND CENTRAL COAST | AUG | Multi-Fault | 0 | No | Yes | No | 1867834 | 0 | Non-EPSS | N | 2023 | ABC TIME
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | TRANSFORMER | 411777934457 | 20230822 | 822 | 20230822 | 2217 | 2198978 | 835 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 835 | 36.2458 | -121.791 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0107443 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1867925 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 100000024804 | 20230822 | 843 | 20230822 | 1853 | 2199018 | 610 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1220 | 36.6653 | -121.7015 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0107525 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1868002 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 11054 | 20230822 | 845 | 20230822 | 1011 | 2199022 | 86 | Distribution Circuit | Animal | Squirrel | 308 | 26488 | 36.9775 | -121.7415 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0107431 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1867914 | 0 | EPSS Ckt | Y | 2023 | A GRD INST
CENTRAL COAST | SALINAS | SALINAS-1109 | 182011109 | TRANSFORMER | 412339549864 | 20230822 | 957 | 20230822 | 1718 | 2198960 | 441 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 4410 | 36.6744 | -121.6138 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0107482 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1867988 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | TRANSFORMER | 412818742935 | 20230822 | 1238 | 20230823 | 1419 | 2199279 | 1541 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 1541 | 36.4875 | -121.4445 | No | Clear;32-90 F |  |  | 23-0107613 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1868051 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | TRANSFORMER | 315759418396 | 20230822 | 1421 | 20230822 | 1717 | 2199451 | 176 | Transformer only | Vegetation | Tree - grew into line | 8 | 1408 | 36.9961 | -121.953 | No | Clear;32-90 F | Secondary | Arcing | 23-0107724 | OH | Sus | 45937265 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1868067 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412178455989 | 20230822 | 1454 | 20230822 | 1618 | 2199468 | 84 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 168 | 36.8414 | -121.6742 | No | Clear;32-90 F | Fuse | Burned Open | 23-0107740 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1868072 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | RECLOSER | 12656 | 20230822 | 1542 | 20230823 | 418 | 2199158 | 756 | Distribution Circuit | Vegetation | Tree - fell into line | 896 | 135519 | 36.9118 | -121.7973 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0107717 | OH | Sus | 45937347 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1868065 | 0 | EPSS Ckt | N | 2023 | A GRD TIME
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | TRANSFORMER | 412877041202 | 20230822 | 1743 | 20230823 | 1414 | 2199452 | 1231 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 1231 | 36.4412 | -121.4216 | No | Clear;32-90 F |  |  | 23-0107772 | OH | Sus | 35483192 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1868083 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0424 | 182440424 | RECLOSER | 2610 | 20230822 | 1939 | 20230823 | 929 | 2199623 | 830 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1173 | 49290 | 36.6225 | -121.9268 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0107779 | OH | Sus | 31664370 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1868094 | 0 | Non-EPSS | N | 2023 | C PH GRD
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316373418537 | 20230822 | 2014 | 20230823 | 1225 | 2199636 | 971 | Transformer only | Animal | Squirrel | 2 | 1942 | 37.0026 | -121.7433 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0107809 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1868123 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | FUSE | 11597 | 20230823 | 915 | 20230823 | 1008 | 2200025 | 53 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 125 | 6618 | 36.9644 | -121.9674 | No | Partly Cloudy;32-90 F |  |  | 23-0107962 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1868308 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | TRANSFORMER | 315759418396 | 20230823 | 928 | 20230823 | 1124 | 2199941 | 116 | Transformer only | Vegetation | Tree - grew into line | 8 | 928 | 36.9961 | -121.953 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0107912 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1868263 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | RECLOSER | 16010 | 20230823 | 1846 | 20230824 | 1601 | 2200627 | 1275 | Distribution Circuit | Equipment Failure/Involved | Overhead | 265 | 187459 | 37.0886 | -122.0874 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0108309 | OH | Sus | 45940018 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1868410 | 0 | EPSS Ckt | Y | 2023 | B/C
CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | OCB | 1103/2 | 20230823 | 2123 | 20230824 | 51 | 2200716 | 208 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 3467 | 36.0134 | -121.1673 | No | Clear;32-90 F |  |  | 23-0108344 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1868432 | 0 | EPSS Ckt | Y | 2023 | A/GRD I
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | RECLOSER | 283170 | 20230824 | 522 | 20230825 | 226 | 2200834 | 1250 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2203 | 196055 | 36.8829 | -121.7979 | No | Overcast-Fog;32-90 F | Pothead(Riser Termination) | Failed/Faulted | 23-0108406 | OH | Sus | 45938035 | SOUTH BAY AND CENTRAL COAST | AUG | Multi-Fault | 0 | No | No | No | 1868494 | 0 | EPSS Ckt | N | 2023 | ABC GRD
CENTRAL COAST | KING CITY | LOS COCHES-1102 | 182151102 | TRANSFORMER | 413369938134 | 20230824 | 744 | 20230824 | 1237 | 2200886 | 293 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 586 | 36.3593 | -121.2526 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0108509 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1868634 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 7771 | 20230824 | 1028 | 20230824 | 1703 | 2201196 | 395 | Distribution Circuit | Equipment Failure/Involved | Underground | 5 | 1975 | 36.9842 | -121.8981 | No | Overcast;32-90 F | Conductor- Underground | Broken | 23-0108539 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1868656 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS COCHES-1101 | 182151101 | TRANSFORMER | 413169437960 | 20230824 | 1448 | 20230824 | 1500 | 2201439 | 12 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 12 | 36.3537 | -121.321 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 23-0108741 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1868743 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 11010 | 20230824 | 1602 | 20230824 | 1609 | 2201514 | 7 | Distribution Circuit | Company Initiated | Return Circuit Normal | 100 | 700 | 37.1053 | -122.0517 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0108309 | OH | Sus | 45940018 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1868752 | 0 | EPSS Ckt | N | 2023 | NA
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 3427 | 20230824 | 1911 | 20230825 | 225 | 2201636 | 434 | Distribution Circuit | Equipment Failure/Involved | Overhead | 85 | 2870 | 36.853 | -121.7084 | No | Overcast;32-90 F | Conductor- Overhead | Arcing | 23-0108808 | OH | Sus | 31664688 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1868777 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | TRANSFORMER | 412159449698 | 20230824 | 2130 | 20230825 | 2 | 2201705 | 152 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 5776 | 36.6685 | -121.6755 | No | Overcast;32-90 F | Transformer (OH) | Deteriorated | 23-0108821 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1868791 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 135762 | 20230825 | 227 | 20230825 | 1706 | 2201758 | 879 | Distribution Circuit | Equipment Failure/Involved | Underground | 36 | 8732 | 36.9567 | -121.7269 | No | Overcast-Fog;32-90 F | Conductor- Underground | Deteriorated | 23-0108887 | UG | Sus | 45940394 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1868851 | 0 | EPSS Ckt | Y | 2023 | C/GRD
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | SWITCH | 12513 | 20230825 | 851 | 20230825 | 905 | 2201944 | 14 | Distribution Circuit | 3rd Party | Vehicle | 1849 | 25886 | 36.9038 | -121.7549 | No | Overcast;32-90 F | Anchor or Guy | Broken | 23-0108978 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1868957 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | DOLAN ROAD-1101 | 182381101 | FUSE | 2223 | 20230825 | 948 | 20230825 | 1142 | 2202079 | 114 | Distribution Circuit | 3rd Party | Other | 8 | 912 | 36.8319 | -121.7798 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0109127 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1869029 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 50107 | 20230825 | 1008 | 20230825 | 1130 | 2202107 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 82 | 36.8961 | -121.4016 | No | Partly Cloudy;32-90 F |  |  | 23-0109113 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1869025 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | FUSE | 3725 | 20230825 | 1027 | 20230825 | 1448 | 2202133 | 261 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1290 | 36.5547 | -121.5365 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0109146 | OH | Sus | 31664785 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1869036 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | TRANSFORMER | 315489517350 | 20230825 | 1420 | 20230825 | 1700 | 2202294 | 160 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 1920 | 36.9656 | -122.0442 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0109231 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1869072 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2103 | 182492103 | FUSE | 4065 | 20230825 | 1526 | 20230825 | 1612 | 2202353 | 44 | Distribution Circuit | 3rd Party | Metallic Balloon | 316 | 13904 | 36.8388 | -121.3812 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0109280 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1869087 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 12824 | 20230825 | 1726 | 20230826 | 1003 | 2202466 | 997 | Distribution Circuit | 3rd Party | Vehicle | 601 | 23797 | 36.9284 | -121.7063 | No | Clear;32-90 F | Transformer (OH) | On Ground | 23-0109297 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1869099 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1105 | 182031105 | FUSE | 9905 | 20230825 | 1953 | 20230826 | 315 | 2202520 | 442 | Distribution Circuit | Equipment Failure/Involved | Underground | 130 | 11678 | 36.2165 | -121.1331 | No | Clear;32-90 F | Elbow | Deteriorated | 23-0109060 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1869105 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | HOLLISTER | SAN BENITO-2104 | 182742104 | SWITCH | 785888 | 20230826 | 326 | 20230826 | 548 | 2202619 | 142 | Distribution Circuit | Animal | Bird found | 1293 | 175545 | 36.8765 | -121.5546 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0109349 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1869149 | 0 | EPSS Ckt | Y | 2023
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | FUSE | 53217 | 20230826 | 632 | 20230826 | 813 | 2202636 | 101 | Distribution Circuit | Animal | Squirrel | 101 | 10201 | 36.9693 | -121.9812 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Normal | 23-0109367 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1869183 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SOLEDAD-2104 | 182052104 | FUSE | 1929 | 20230827 | 401 | 20230827 | 902 | 2203100 | 299 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 996 | 36.466 | -121.3906 | No | Overcast-Fog;32-90 F |  |  | 23-0109496 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1869319 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 1699 | 20230827 | 501 | 20230827 | 643 | 2203120 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 918 | 36.9707 | -121.797 | No | Overcast-Fog;32-90 F |  |  | 23-0109488 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1869303 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 95394 | 20230827 | 747 | 20230827 | 1142 | 2203182 | 235 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6813 | 1524789 | 37.0895 | -122.0928 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0109489 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1869304 | 0 | EPSS Ckt | Y | 2023 | AB GRD
CENTRAL COAST | COAST | POINT MORETTI SUB | 8293 | OCB | POINT MORETTI | 20230827 | 747 | 20230827 | 1209 | 2203288 | 262 | Distribution Circuit | Vegetation | Tree - branch fell on line | 382 | 100084 | 0 | 0 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0109489 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1869324 | 0 | Non-EPSS | N | 2023 | N/A
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 12381 | 20230827 | 749 | 20230827 | 1234 | 2203205 | 285 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 155 | 44175 | 37.0383 | -122.0411 | No | Partly Cloudy;32-90 F |  |  | 23-0109512 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1869331 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 130936 | 20230827 | 843 | 20230827 | 1025 | s1869336 | 81 | Distribution Circuit | Company Initiated | Personnel- company | 6 | 486 | 37.0354 | -122.0867 | No | Clear;32-90 F | Recloser | Normal | 23-0109489 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1869336 | 0 | EPSS Ckt | Y | 2023 | STALE
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 13001 | 20230827 | 1648 | 20230827 | 1926 | 2203406 | 158 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 8848 | 36.9781 | -122.0455 | No | Clear;32-90 F |  |  | 23-0109560 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1869352 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | OTHER | WIRE DOWN | 20230827 | 1724 | 20230828 | 134 | 2203430 | 490 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 8216 | 37.0093 | -121.9361 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0109557 | OH | Sus | 45942071 | SOUTH BAY AND CENTRAL COAST | AUG | Open Circuit | 0 | No | Yes | Yes | 1869349 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | JUMPER | WIRE DOWN | 20230828 | 134 | 20230828 | 1003 | 2203589 | 509 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 9140 | 37.021 | -121.9848 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0109594 | OH | Sus | 31665602 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | Yes | 1869385 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 2181 | 20230828 | 356 | 20230828 | 717 | 2203578 | 201 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 85 | 17085 | 36.4895 | -121.9363 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0109613 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1869402 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 9065 | 20230828 | 545 | 20230828 | 759 | 2203614 | 134 | Distribution Circuit | Animal | Bird found | 102 | 13668 | 36.6226 | -121.9183 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0109630 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1869417 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | RECLOSER | 7086 | 20230828 | 730 | 20230828 | 1236 | 2203663 | 306 | Distribution Circuit | Equipment Failure/Involved | Overhead | 132 | 25154 | 36.2942 | -121.1997 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0109624 | OH | Sus | 31665604 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1869408 | 0 | EPSS Ckt | N | 2023 | A GRD
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | OTHER | WIRE DOWN 4 LD SIDE OF 9693 | 20230828 | 958 | 20230828 | 1323 | 2203920 | 205 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 205 | 36.4398 | -121.423 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0109763 | OH | Sus | 31665610 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | Yes | 1869584 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 12760 | 20230828 | 1100 | 20230828 | 1111 | 2204015 | 11 | Distribution Circuit | Company Initiated | Personnel- company | 412 | 4532 | 37.0674 | -121.9966 | No | Clear;32-90 F | Recloser | Normal | 23-0109741 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1869568 | 0 | EPSS Ckt | Y | 2023 | A PH & GRD
CENTRAL COAST | SALINAS | DEL MONTE-2104 | 182222104 | RECLOSER | 2762 | 20230828 | 1719 | 20230828 | 1838 | 2204375 | 79 | Distribution Circuit | Animal | Bird found | 420 | 33180 | 36.5581 | -121.7505 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 23-0109935 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1869646 | 0 | EPSS Ckt | Y | 2023 | B/GRD
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | RECLOSER | 3032 | 20230829 | 851 | 20230829 | 1151 | 2204776 | 180 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 109 | 19620 | 36.634 | -121.6988 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0110093 | OH | Sus | 31665885 | SOUTH BAY AND CENTRAL COAST | AUG | Multi-Fault | 0 | No | Yes | No | 1869822 | 0 | EPSS Ckt | Y | 2023 | BC GRD
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | RECLOSER | 741002 | 20230829 | 851 | 20230829 | 1710 | s1869910 | 499 | Distribution Circuit | Equipment Failure/Involved | Overhead | 523 | 71416 | 36.597 | -121.6247 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0110093 | OH | Sus | 31665885 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1869910 | 0 | EPSS Ckt | Y | 2023 | AC GRD INST
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316418514180 | 20230829 | 1012 | 20230829 | 1443 | 2204910 | 271 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 1355 | 36.8832 | -121.7256 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0110222 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1869914 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 50885 | 20230829 | 1342 | 20230829 | 1749 | 2205116 | 247 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 329 | 36.8797 | -121.3591 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0110380 | OH | Sus | 31665942 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1869970 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | SWITCH | 3067 | 20230829 | 1748 | 20230829 | 1811 | 2205359 | 23 | Distribution Circuit | Company Initiated | Personnel- company | 509 | 11707 | 36.597 | -121.6247 | No | Clear;32-90 F | Recloser | Normal | 23-0110455 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1869990 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | OCB | 2104/2 | 20230830 | 702 | 20230830 | 1732 | 2205589 | 454 | Distribution Circuit | 3rd Party | Vehicle | 8029 | 637109 | 36.9522 | -121.76 | No | Partly Cloudy;32-90 F | Anchor or Guy | Broken | 23-0110573 | OH | Sus | 45946309 | SOUTH BAY AND CENTRAL COAST | AUG | Three Phase Fault | 0 | No | No | No | 1870072 | 0 | Non-EPSS | N | 2023 | ABC
CENTRAL COAST | SALINAS | BUENA VISTA-1106 | 182261106 | TRANSFORMER | 412366648202 | 20230830 | 1118 | 20230830 | 1235 | 2205946 | 77 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 77 | 36.6294 | -121.6033 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0110785 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1870234 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | FUSE | 4817 | 20230830 | 1121 | 20230830 | 1341 | 2205951 | 140 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 793 | 36.9193 | -121.4497 | No | Clear;32-90 F |  |  | 23-0110820 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1870244 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1108 | 182011108 | TRANSFORMER | 412257349952 | 20230830 | 1228 | 20230830 | 1256 | 2206022 | 28 | Transformer only | Unknown Cause | Patrol - not conducted | 9 | 252 | 36.6762 | -121.6416 | No | Clear;32-90 F |  |  | 23-0110827 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1870250 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 2423 | 20230830 | 1343 | 20230901 | 1402 | 2206090 | 2899 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 569 | 58941 | 36.8878 | -121.7225 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0110845 | OH | Sus | 31666234 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1870254 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | TRANSFORMER | 412810042950 | 20230830 | 1446 | 20230831 | 349 | 2206153 | 783 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 783 | 36.4879 | -121.4472 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0110946 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1870275 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | OTHER | HOT WIRE DOWN 2 E/OF 5219 | 20230830 | 1602 | 20230830 | 2349 | 2206243 | 467 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1668 | 288147 | 36.7219 | -121.6613 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0110963 | OH | Sus | 45946598 | SOUTH BAY AND CENTRAL COAST | AUG | Open Circuit | 0 | No | Yes | Yes | 1870284 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | OTHER | HOT WIRE DOWN 1 SSD OF CGC# 316680014148 | 20230830 | 1610 | 20230831 | 259 | 2206272 | 649 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1119 | 91207 | 36.8821 | -121.636 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0110969 | OH | Sus | 31666235 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | Yes | 1870286 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | TRANSFORMER | 411405945621 | 20230830 | 1851 | 20230830 | 2252 | 2206019 | 241 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 2651 | 36.5502 | -121.9277 | No | Clear;32-90 F | Conductor- Overhead | Burned/flashed | 23-0110997 | OH | Sus | 31666010 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1870298 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1104 | 182031104 | FUSE | 9989 | 20230830 | 1902 | 20230830 | 2024 | 2206456 | 82 | Distribution Circuit | Animal | Bird found | 5 | 410 | 36.2066 | -121.1173 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0111009 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1870308 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1104 | 182031104 | FUSE | 7260 | 20230830 | 2104 | 20230830 | 2219 | 2206471 | 75 | Distribution Circuit | Animal | Bird found | 7 | 500 | 36.2077 | -121.1178 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0111024 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1870321 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 6409 | 20230830 | 2107 | 20230831 | 218 | 2206466 | 311 | Distribution Circuit | Equipment Failure/Involved | Overhead | 106 | 32966 | 36.59 | -121.9115 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0111012 | OH | Sus | 31665952 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1870310 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | OCB | 1102/2 | 20230831 | 14 | 20230831 | 1339 | 2206515 | 805 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2146 | 480784 | 36.5569 | -121.8976 | No | Partly Cloudy;32-90 F |  |  | 23-0111041 | OH | Sus | 31666620 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1870333 | 0 | EPSS Ckt | Y | 2023 | SET A RLY TRIP
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | JUMPER | JMPRS 1 E/O CGC 315705417053 | 20230831 | 824 | 20230831 | 1048 | 2206736 | 144 | Distribution Circuit | Vegetation | Tree - grew into line | 26 | 3744 | 36.9586 | -121.9696 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0111107 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1870414 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | RECLOSER | 549180 | 20230831 | 941 | 20230831 | 1113 | 2206895 | 92 | Distribution Circuit | 3rd Party | Customer Equipment | 9 | 828 | 36.0057 | -121.2422 | No | Clear;32-90 F | Switch (OH) | Normal | 23-0111173 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1870506 | 0 | EPSS Ckt | Y | 2023 | NA
CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | OCB | 1103/2 | 20230831 | 1123 | 20230831 | 1140 | 2206971 | 17 | Distribution Circuit | 3rd Party | Customer Equipment | 20 | 329 | 36.0134 | -121.1673 | No | Clear;32-90 F | Switch (OH) | Normal | 23-0111261 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Three Phase Fault | 0 | No | No | No | 1870562 | 0 | EPSS Ckt | Y | 2023 | ABC
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | RECLOSER | 2002 | 20230831 | 2014 | 20230901 | 234 | 2207401 | 380 | Distribution Circuit | Equipment Failure/Involved | Overhead | 120 | 45600 | 36.2248 | -121.7587 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0111527 | OH | Sus | 35485631 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1870632 | 0 | EPSS Ckt | N | 2023 | NA
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 8917 | 20230901 | 930 | 20230901 | 1307 | 2207700 | 217 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 3255 | 36.5771 | -121.9274 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0111694 | OH | Sus | 31666986 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | No | 1870764 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 5691 | 20230901 | 931 | 20230901 | 2359 | 2207676 | 868 | Distribution Circuit | Equipment Failure/Involved | Underground | 143 | 124124 | 36.772 | -121.7904 | No | Overcast-Fog;32-90 F | Transformer (UG) | Deteriorated | 23-0111674 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1870743 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 4899 | 20230901 | 1310 | 20230901 | 1719 | 2207924 | 249 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 996 | 36.7226 | -121.7881 | No | Clear;32-90 F |  |  | 23-0111909 | OH | Sus | 31667303 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1870833 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 925620 | 20230901 | 1345 | 20230901 | 1720 | 2207934 | 215 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 3870 | 37.1594 | -122.1269 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0111869 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1870823 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | TRANSFORMER | 411562946863 | 20230901 | 1531 | 20230901 | 2322 | 2208007 | 471 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1413 | 36.5859 | -121.8752 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0111971 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1870841 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412175655293 | 20230901 | 1554 | 20230902 | 20 | 2207975 | 506 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1012 | 36.8223 | -121.6747 | No | Partly Cloudy;32-90 F | Transformer | Burned/flashed | 23-0111949 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1870838 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 12596 | 20230902 | 412 | 20230902 | 611 | 2208308 | 119 | Distribution Circuit | Vegetation | Tree - branch fell on line | 406 | 48314 | 36.987 | -121.8327 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 23-0112041 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1870899 | 0 | EPSS Ckt | Y | 2023 | A.B
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 12596 | 20230902 | 658 | 20230902 | 815 | 2208327 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 406 | 27332 | 36.987 | -121.8327 | No | Overcast-Fog;32-90 F |  |  | 23-0112047 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1870904 | 0 | EPSS Ckt | Y | 2023 | A-B
CENTRAL COAST | SALINAS | SPENCE-1105 | 182201105 | FUSE | 5065 | 20230902 | 1319 | 20230902 | 2335 | 2208716 | 616 | Distribution Circuit | 3rd Party | Vehicle | 5 | 3287 | 36.6225 | -121.5825 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0112173 | OH | Sus | 45951665 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1870979 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | OILFIELDS-1103 | 182391103 | RECLOSER | 83158 | 20230902 | 1522 | 20230902 | 1807 | 2208769 | 165 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 196 | 32340 | 35.8992 | -120.9421 | No | Partly Cloudy;32-90 F |  |  | 23-0112144 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1870962 | 0 | EPSS Ckt | Y | 2023 | A-C
CENTRAL COAST | SALINAS | DEL MONTE-2104 | 182222104 | RECLOSER | 2762 | 20230902 | 1532 | 20230902 | 1743 | 2208775 | 131 | Distribution Circuit | Animal | Bird found | 420 | 38892 | 36.5581 | -121.7505 | No | Clear;32-90 F | Fuse | Normal | 23-0112146 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1870964 | 0 | EPSS Ckt | Y | 2023 | B-GRD
CENTRAL COAST | KING CITY | KING CITY-1103 | 182031103 | FUSE | 320211 | 20230902 | 2102 | 20230903 | 1538 | 2208925 | 1116 | Distribution Circuit | 3rd Party | Vehicle | 11 | 12276 | 36.2058 | -121.1346 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 23-0112193 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Multi-Fault | 0 | No | Yes | No | 1871004 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 5691 | 20230902 | 2141 | 20230902 | 2349 | 2208929 | 128 | Distribution Circuit | Equipment Failure/Involved | Underground | 143 | 18304 | 36.772 | -121.7904 | No | Overcast;32-90 F | Conductor- Underground | Broken | 23-0112178 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1870988 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 10901 | 20230903 | 907 | 20230903 | 1042 | 2209043 | 95 | Distribution Circuit | Vegetation | Tree - bark fell into line | 12 | 1140 | 37.0948 | -121.9732 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0112231 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1871044 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | SWITCH | 2735 | 20230904 | 806 | 20230904 | 1741 | 2209274 | 575 | Distribution Circuit | 3rd Party | Vehicle | 663 | 83186 | 36.9743 | -122.0584 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken | 23-0112295 | OH | Sus | 35486403 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1871098 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412249654400 | 20230904 | 922 | 20230904 | 1539 | 2209328 | 377 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 2262 | 36.7984 | -121.6487 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0112330 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1871119 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | RECLOSER | 11046 | 20230904 | 1333 | 20230904 | 1429 | 2209445 | 56 | Distribution Circuit | Vegetation | Tree - fell into line | 351 | 19656 | 36.9995 | -122.0078 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0112345 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1871127 | 0 | EPSS Ckt | Y | 2023 | B GRD
CENTRAL COAST | SALINAS | DEL MONTE-2104 | 182222104 | RECLOSER | 2762 | 20230904 | 1624 | 20230904 | 1716 | 2209506 | 52 | Distribution Circuit | Animal | Bird found | 420 | 14928 | 36.5581 | -121.7505 | No | Clear;32-90 F | Fuse | Normal | 23-0112366 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1871142 | 0 | EPSS Ckt | Y | 2023 | B GRD
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | RECLOSER | 10986 | 20230904 | 1926 | 20230904 | 2207 | 2209556 | 161 | Distribution Circuit | Equipment Failure/Involved | Overhead | 185 | 29785 | 36.9615 | -122.0627 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0112379 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1871149 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 10449 | 20230904 | 2028 | 20230904 | 2330 | 2209581 | 182 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1274 | 37.1105 | -122.047 | No | Clear;32-90 F |  |  | 23-0112414 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1871170 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | FUSE | 20075 | 20230904 | 2351 | 20230905 | 100 | 2209620 | 69 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 138 | 36.6305 | -121.668 | No | Clear;32-90 F |  |  | 23-0112417 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1871174 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 67520 | 20230905 | 55 | 20230905 | 558 | 2209622 | 303 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2737 | 391545 | 36.9577 | -121.8525 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0112415 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | Yes | No | 1871172 | 0 | EPSS Ckt | Y | 2023 | B&C
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 6795 | 20230905 | 134 | 20230905 | 353 | 2209631 | 139 | Distribution Circuit | 3rd Party | Vehicle | 19 | 2303 | 36.9041 | -121.7102 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0112413 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1871176 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 659 | 20230905 | 453 | 20230905 | 840 | 2209650 | 227 | Distribution Circuit | Vegetation | Tree - branch fell on line | 67 | 15209 | 36.9182 | -121.8348 | No | Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0112492 | OH | Sus | 45953437 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | Yes | No | 1871255 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 12122 | 20230905 | 521 | 20230905 | 534 | 2209653 | 13 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 63 | 819 | 37.0666 | -122.2288 | No | Partly Cloudy;32-90 F |  |  | 23-0112424 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Multi-Fault | 0 | No | No | No | 1871181 | 0 | EPSS Ckt | N | 2023 | AB & GRD TIME
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | FUSE | 24803 | 20230905 | 627 | 20230905 | 854 | 2209765 | 147 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1029 | 36.6313 | -121.6693 | No | Overcast-Fog;32-90 F |  |  | 23-0112499 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1871264 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | TRIP-SAVER | 3571 | 20230905 | 823 | 20230905 | 1029 | 2209781 | 126 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 756 | 36.723 | -121.7268 | No | Partly Cloudy;32-90 F |  |  | 23-0112550 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1871333 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | SALINAS | SPENCE-1104 | 182201104 | FUSE | 454817 | 20230905 | 1101 | 20230905 | 1824 | 2209993 | 443 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 2544 | 36.5962 | -121.5387 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0112650 | OH | Sus | 31667478 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1871365 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | RECLOSER | 549180 | 20230905 | 1539 | 20230905 | 1641 | 2210273 | 62 | Distribution Circuit | 3rd Party | Customer Equipment | 9 | 558 | 36.0057 | -121.2422 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0112756 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1871379 | 0 | EPSS Ckt | Y | 2023 | AC
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | TRANSFORMER | 413329436293 | 20230905 | 1539 | 20230905 | 2225 | 2210253 | 406 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 812 | 36.3086 | -121.2654 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 23-0112759 | OH | Sus | 45953825 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1871382 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | TRANSFORMER | 315483817368 | 20230905 | 2040 | 20230906 | 1336 | 2210428 | 1016 | Transformer only | Vegetation | Tree - fell into line | 9 | 9144 | 36.9659 | -122.0459 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0112845 | OH | Sus | 45954095 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1871413 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | OTHER | WIRE DOWN 3 SS OF 156775 | 20230906 | 242 | 20230906 | 1125 | 2210557 | 523 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 2564 | 36.6637 | -121.7208 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0112893 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Open Circuit | 0 | No | Yes | Yes | 1871439 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | RECLOSER | 974130 | 20230906 | 725 | 20230906 | 926 | 2210577 | 121 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 91 | 8221 | 37.0448 | -121.9382 | No | Overcast;32-90 F |  |  | 23-0112925 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1871447 | 0 | EPSS Ckt | Y | 2023 | C-GRD-INST
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 7643 | 20230906 | 730 | 20230906 | 1450 | 2210583 | 440 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 3552 | 37.0204 | -121.9515 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0113034 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1871586 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 50107 | 20230906 | 1329 | 20230906 | 1417 | 2211007 | 48 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 48 | 36.8961 | -121.4016 | No | Clear;32-90 F |  |  | 23-0113249 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1871653 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 7691 | 20230906 | 1434 | 20230906 | 1501 | 2211051 | 27 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 162 | 36.9865 | -121.8088 | No | Clear;32-90 F | Secondary | Broken | 23-0113251 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1871654 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | TRANSFORMER | 412176048560 | 20230906 | 1550 | 20230907 | 1105 | 2211104 | 1155 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 3465 | 36.6374 | -121.6689 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0113371 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1871691 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 4709 | 20230906 | 1625 | 20230906 | 1835 | 2211095 | 130 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 910 | 36.6877 | -121.3445 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0113296 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1871663 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | RECLOSER | 491190 | 20230906 | 2338 | 20230907 | 214 | 2211336 | 156 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 807 | 103597 | 36.8007 | -121.7217 | No | Overcast;32-90 F |  |  | 23-0113417 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1871719 | 0 | EPSS Ckt | Y | 2023 | AB INST
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 5635 | 20230907 | 644 | 20230907 | 1028 | 2211397 | 224 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 7616 | 36.7889 | -121.6838 | No | Clear;32-90 F |  |  | 23-0113579 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1871882 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | RECLOSER | 36922 | 20230907 | 940 | 20230907 | 2104 | 2211593 | 684 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 13680 | 36.6956 | -121.7354 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0113545 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1871861 | 0 | EPSS Ckt | N | 2023 | A- B
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411902252789 | 20230907 | 1115 | 20230908 | 246 | 2211758 | 931 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 931 | 36.7513 | -121.7656 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0113857 | OH | Sus | 35487254 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1871965 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 2751 | 20230907 | 1115 | 20230908 | 453 | 2211759 | 1058 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 88624 | 36.9693 | -121.8319 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0113658 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1871912 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2103 | 83252103 | OTHER | T0120 TWD T1130 | 20230907 | 1721 | 20230907 | 1902 | 2212100 | 78 | Distribution Circuit | Equipment Failure/Involved | Underground | 162 | 12659 | 36.98 | -122.0195 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0101922 | UG | Sus | 31661922 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1871969 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 2639 | 20230907 | 2316 | 20230908 | 202 | 2212258 | 166 | Distribution Circuit | Vegetation | Tree - grew into line | 1 | 166 | 37.0483 | -121.9822 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0113886 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1871979 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SOLEDAD-2104 | 182052104 | RECLOSER | 7008 | 20230908 | 513 | 20230908 | 823 | 2212342 | 190 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 95 | 18050 | 36.4058 | -121.3538 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0113935 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1872003 | 0 | EPSS Ckt | Y | 2023 | B
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 71630 | 20230908 | 625 | 20230908 | 839 | 2212373 | 134 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 619 | 41006 | 36.9761 | -121.8948 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0113946 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1872009 | 0 | EPSS Ckt | Y | 2023 | A-B
CENTRAL COAST | SALINAS | SALINAS-1101 | 182011101 | TRANSFORMER | T271 | 20230908 | 627 | 20230908 | 1822 | 2212375 | 715 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 715 | 36.671 | -121.6436 | No | Partly Cloudy-Fog;32-90 F | Transformer (UG) | Failed/Faulted | 23-0113975 | UG | Sus | 35486992 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1872027 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | TRANSFORMER | 411409748369 | 20230908 | 813 | 20230908 | 820 | 2212376 | 7 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 21 | 36.6262 | -121.9294 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0113998 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1872055 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | TRANSFORMER | 411820649974 | 20230908 | 821 | 20230908 | 1243 | 2212461 | 262 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 2358 | 36.6734 | -121.791 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0114205 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1872195 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | RECLOSER | 22418 | 20230908 | 829 | 20230909 | 243 | 2212481 | 1094 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 94 | 102836 | 36.538 | -121.4635 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0114017 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1872078 | 0 | EPSS Ckt | Y | 2023 | AB
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 1555 | 20230908 | 847 | 20230908 | 2344 | 2212536 | 897 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 4641 | 37.0512 | -122.0751 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0114054 | OH | Sus | 35487404 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | Yes | 1872123 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1106 | 182031106 | RECLOSER | 500 | 20230908 | 1118 | 20230908 | 2227 | 2212726 | 669 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 24549 | 36.2185 | -121.0846 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0114135 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | No | 1872165 | 0 | EPSS Ckt | N | 2023 | SGF
CENTRAL COAST | SALINAS | BUENA VISTA-1106 | 182261106 | TRANSFORMER | 412398448224 | 20230908 | 1517 | 20230908 | 2135 | 2212958 | 378 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 378 | 36.63 | -121.5915 | No | Clear;32-90 F | Transformer | Broken | 23-0114275 | OH | Sus | 45967264 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1872211 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 370732 | 20230908 | 1636 | 20230908 | 1643 | 2213138 | 7 | Distribution Circuit | Company Initiated | Personnel- company | 430 | 3010 | 37.0534 | -122.0438 | No | Clear;32-90 F | Fuse | Normal | 23-0114304 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1872224 | 0 | EPSS Ckt | Y | 2023 | GRD-INST
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315424919753 | 20230908 | 1730 | 20230909 | 1012 | 2213112 | 1002 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 6012 | 37.0318 | -122.0685 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114318 | OH | Sus | 45967530 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1872233 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | SAN BENITO-2104 | 182742104 | RECLOSER | 785888 | 20230908 | 1857 | 20230909 | 1517 | 2213212 | 1220 | Distribution Circuit | Vegetation | Tree - fell into line | 1293 | 157590 | 36.8765 | -121.5546 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0114332 | OH | Sus | 31668321 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | No | 1872240 | 0 | EPSS Ckt | Y | 2023 | C GRD
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | FUSE | 4297 | 20230909 | 102 | 20230909 | 1012 | 2213281 | 550 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 2200 | 36.7428 | -121.6868 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0114370 | OH | Sus | 45968166 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | Yes | Yes | 1872270 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | TRANSFORMER | 413346036565 | 20230909 | 353 | 20230910 | 242 | 2213330 | 1369 | Transformer only | Environmental/External | Lightning | 13 | 17797 | 36.3162 | -121.2598 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114445 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1872395 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | CAMPHORA-0401 | 182070401 | RECLOSER | 401/2 | 20230909 | 458 | 20230909 | 515 | 2213338 | 17 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1 | 17 | 36.468 | -121.3901 | Yes | Partly Cloudy;32-90 F |  |  | 23-0114373 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | None | 0 | No | No | No | 1872274 | 0 | Non-EPSS | N | 2023 | N/A
CENTRAL COAST | KING CITY | SOLEDAD-2104 | 182052104 | RECLOSER | 413916 | 20230909 | 459 | 20230909 | 905 | 2213337 | 246 | Distribution Circuit | Environmental/External | Lightning | 33 | 8118 | 36.4469 | -121.3318 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0114374 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1872276 | 0 | EPSS Ckt | Y | 2023 | A GRD INST
CENTRAL COAST | KING CITY | SOLEDAD-2104 | 182052104 | RECLOSER | 7008 | 20230909 | 557 | 20230909 | 815 | 2213355 | 138 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 95 | 13110 | 36.4058 | -121.3538 | Yes | Partly Cloudy;32-90 F |  |  | 23-0114380 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1872282 | 0 | EPSS Ckt | Y | 2023 | A GRD
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | FUSE | 7967 | 20230909 | 655 | 20230909 | 902 | 2213371 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 170 | 14624 | 36.5431 | -121.4676 | Yes | Partly Cloudy;32-90 F |  |  | 23-0114384 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1872290 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SOLEDAD-2104 | 182052104 | RECLOSER | 7646 | 20230909 | 752 | 20230909 | 1645 | 2213435 | 533 | Distribution Circuit | Environmental/External | Lightning | 20 | 2632 | 36.4251 | -121.3307 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0114393 | OH | Sus | 35487519 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | No | 1872305 | 0 | EPSS Ckt | N | 2023 | C GRD
CENTRAL COAST | KING CITY | LOS COCHES-1101 | 182151101 | RECLOSER | 625902 | 20230909 | 755 | 20230911 | 202 | 2213437 | 2527 | Distribution Circuit | Environmental/External | Lightning | 18 | 10553 | 36.3482 | -121.3219 | Yes | Partly Cloudy;32-90 F | Transformer (OH) | Burned/flashed | 23-0114421 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1872371 | 0 | EPSS Ckt | Y | 2023 | AB
CENTRAL COAST | KING CITY | LOS COCHES-1102 | 182151102 | TRANSFORMER | 413287939204 | 20230909 | 800 | 20230910 | 2132 | 2214993 | 2252 | Transformer only | Environmental/External | Lightning | 2 | 4504 | 36.3888 | -121.2807 | Yes | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114738 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1872705 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS COCHES-1102 | 182151102 | TRANSFORMER | 413304939418 | 20230909 | 847 | 20230909 | 2335 | 2214994 | 888 | Transformer only | Environmental/External | Lightning | 5 | 4440 | 36.3946 | -121.2757 | Yes | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114739 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1872706 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1101 | 182201101 | FUSE | 1633 | 20230909 | 901 | 20230910 | 2143 | 2213515 | 2202 | Distribution Circuit | Environmental/External | Lightning | 11 | 9592 | 36.5975 | -121.6052 | Yes | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0114430 | OH | Sus | 35487582 | SOUTH BAY AND CENTRAL COAST | SEP | Three Phase Fault | 0 | No | No | No | 1872379 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1105 | 182201105 | OCB | 1105/2 | 20230909 | 915 | 20230909 | 1133 | 2213537 | 138 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 67 | 9246 | 36.6139 | -121.5666 | Yes | Clear;32-90 F |  |  | 23-0114412 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | None | 0 | No | No | No | 1872354 | 0 | Non-EPSS | N | 2023 | NONE
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | RECLOSER | 4002 | 20230909 | 917 | 20230909 | 1626 | 2213548 | 429 | Distribution Circuit | Equipment Failure/Involved | Overhead | 170 | 23018 | 36.8322 | -121.5312 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114413 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1872355 | 0 | EPSS Ckt | Y | 2023 | A
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | RECLOSER | 4004 | 20230909 | 923 | 20230909 | 1112 | 2213553 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 5995 | 36.8169 | -121.3906 | Yes | Clear;32-90 F |  |  | 23-0114414 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1872356 | 0 | EPSS Ckt | Y | 2023 | AC
CENTRAL COAST | SALINAS | BUENA VISTA-1104 | 182261104 | FUSE | 63907 | 20230909 | 1001 | 20230909 | 2007 | 2213590 | 606 | Distribution Circuit | Environmental/External | Lightning | 6 | 3636 | 36.6671 | -121.6135 | Yes | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0114420 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1872370 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | RECLOSER | 36982 | 20230909 | 1004 | 20230909 | 2022 | 2213595 | 618 | Distribution Circuit | Equipment Failure/Involved | Overhead | 170 | 74128 | 36.5301 | -121.4747 | Yes | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0114422 | OH | Sus | 31668308 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | Yes | No | 1872372 | 0 | EPSS Ckt | Y | 2023 | AC
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6761 | 20230909 | 1232 | 20230909 | 1648 | 2213810 | 256 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 512 | 36.8841 | -121.6816 | Yes | Clear;32-90 F |  |  | 23-0114506 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1872442 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | TRANSFORMER | 413423637545 | 20230909 | 1406 | 20230910 | 1315 | 2213787 | 1389 | Transformer only | Environmental/External | Lightning | 3 | 4167 | 36.3438 | -121.2339 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114481 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1872419 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | FUSE | 79717 | 20230909 | 1452 | 20230910 | 1629 | 2214627 | 1537 | Distribution Circuit | Environmental/External | Lightning | 1 | 1537 | 36.337 | -121.211 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114641 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1872590 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | JUMPER | 5 NE/OF CGC 414307026850 | 20230909 | 1628 | 20230910 | 34 | 2213911 | 486 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 972 | 36.0577 | -120.931 | Yes | Clear;Above 90 | Crossarm- Wood | Broken | 23-0114502 | OH | Sus | 31668325 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1872440 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SOLEDAD-2104 | 182052104 | FUSE | 2017 | 20230909 | 1904 | 20230910 | 1955 | 2214062 | 1491 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 2395 | 36.4396 | -121.3505 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114575 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Three Phase Fault | 0 | No | No | No | 1872509 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | RECLOSER | 36982 | 20230909 | 2114 | 20230910 | 1558 | 2214309 | 1124 | Distribution Circuit | Equipment Failure/Involved | Overhead | 170 | 145672 | 36.5301 | -121.4747 | Yes | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0114582 | OH | Sus | 45968463 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | No | 1872518 | 0 | EPSS Ckt | Y | 2023 | SGF INST
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | RECLOSER | 7030 | 20230910 | 1926 | 20230911 | 1143 | 2214939 | 977 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 106 | 103562 | 36.2025 | -120.8432 | No | Clear;32-90 F |  |  | 23-0114728 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1872695 | 0 | EPSS Ckt | Y | 2023 | BC
CENTRAL COAST | KING CITY | SOLEDAD-2104 | 182052104 | RECLOSER | 7248 | 20230911 | 232 | 20230911 | 240 | 2215061 | 8 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 72 | 576 | 36.4351 | -121.3426 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 23-0114761 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1872734 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | MONTEREY | FORT ORD-2106 | 182402106 | RECLOSER | 95186 | 20230911 | 607 | 20230911 | 1043 | 2215081 | 276 | Distribution Circuit | Equipment Failure/Involved | Overhead | 264 | 22599 | 36.6604 | -121.7936 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0114777 | OH | Sus | 45973563 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | No | 1872748 | 0 | EPSS Ckt | N | 2023 | SGF
CENTRAL COAST | SALINAS | SOLEDAD-2105 | 182052105 | TRANSFORMER | T172592 | 20230911 | 1157 | 20230912 | 420 | 2215283 | 983 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 983 | 36.5061 | -121.4001 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0114967 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1872973 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 316157717426 | 20230911 | 1227 | 20230911 | 1422 | 2215570 | 115 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 345 | 36.971 | -121.8165 | No | Clear;32-90 F |  |  | 23-0115098 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1873025 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1104 | 182201104 | JUMPER | OJ 8 E/OF 5767 | 20230911 | 1228 | 20230911 | 2119 | 2215572 | 531 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 2954 | 36.5856 | -121.5668 | No | Clear;32-90 F | Jumper | Broken | 23-0115113 | OH | Sus | 45974973 | SOUTH BAY AND CENTRAL COAST | SEP | Open Circuit | 0 | No | No | No | 1873031 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 67520 | 20230912 | 552 | 20230914 | 222 | 2216092 | 2670 | Distribution Circuit | Equipment Failure/Involved | Underground | 2737 | 191320 | 36.9577 | -121.8525 | No | Partly Cloudy-Fog;32-90 F | Conductor- Underground | Broken | 23-0115295 | UG | Sus | 31668654 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1873139 | 0 | EPSS Ckt | Y | 2023 | C GRD
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | RECLOSER | 4002 | 20230912 | 633 | 20230912 | 750 | 2216103 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 170 | 10450 | 36.8322 | -121.5312 | No | Clear;32-90 F |  |  | 23-0115299 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1873144 | 0 | EPSS Ckt | Y | 2023 | B-C
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | TRANSFORMER | 315575018089 | 20230912 | 646 | 20230912 | 810 | 2216112 | 84 | Transformer only | Vegetation | Tree - branch fell on line | 6 | 504 | 36.9866 | -122.0152 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0115344 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | No | 1873211 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | RECLOSER | 3034 | 20230912 | 657 | 20230912 | 725 | 2216114 | 28 | Distribution Circuit | Animal | Bird found | 544 | 15232 | 36.7317 | -121.6129 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0115302 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1873149 | 0 | EPSS Ckt | Y | 2023 | B-C
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | FUSE | 9787 | 20230912 | 801 | 20230912 | 1110 | 2216242 | 189 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1134 | 36.3052 | -121.236 | No | Clear;32-90 F |  |  | 23-0115439 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Multi-Fault | 0 | No | No | No | 1873335 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | OTHER | WIRE DOWN | 20230912 | 827 | 20230912 | 1306 | 2216476 | 279 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 3921 | 37.0398 | -122.0644 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0115397 | OH | Sus | 31668468 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | Yes | 1873307 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | RECLOSER | 7066 | 20230912 | 841 | 20230912 | 1708 | 2216244 | 507 | Distribution Circuit | Equipment Failure/Involved | Overhead | 292 | 141494 | 36.0489 | -120.9121 | No | Clear;32-90 F | Regulator | Burned/flashed | 23-0115361 | OH | Sus | 35488284 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1873238 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRANSFORMER | 315261824077 | 20230912 | 947 | 20230912 | 2150 | 2216474 | 723 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1446 | 37.1503 | -122.1243 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0115470 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1873351 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 412034854872 | 20230912 | 1046 | 20230912 | 1509 | 2216574 | 263 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 263 | 36.8106 | -121.7224 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0115452 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1873342 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6867 | 20230912 | 1158 | 20230912 | 2149 | 2216572 | 591 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 8865 | 37.025 | -121.8275 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0115463 | OH | Sus | 45977136 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1873348 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 4119 | 20230912 | 1510 | 20230913 | 243 | 2216824 | 693 | Distribution Circuit | 3rd Party | Vehicle | 4 | 2772 | 36.8045 | -121.762 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0115675 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1873413 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS COCHES-1102 | 182151102 | TRANSFORMER | 413317039052 | 20230912 | 1538 | 20230914 | 2035 | 2216798 | 3177 | Transformer only | Environmental/External | Lightning | 1 | 3177 | 36.3848 | -121.2698 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0115653 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1873410 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | RECLOSER | 549180 | 20230912 | 2146 | 20230913 | 540 | 2217112 | 474 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 4266 | 36.0057 | -121.2422 | No | Clear;32-90 F |  |  | 23-0115747 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1873452 | 0 | EPSS Ckt | Y | 2023 | A GRD INST
CENTRAL COAST | KING CITY | SOLEDAD-2104 | 182052104 | FUSE | 2017 | 20230913 | 904 | 20230913 | 1525 | 2217543 | 381 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 3429 | 36.4396 | -121.3505 | No | Partly Cloudy-Fog;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0115973 | OH | Sus | 31668478 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | Yes | 1873698 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 7755 | 20230913 | 1008 | 20230913 | 1525 | 2217677 | 317 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 66 | 20922 | 36.9106 | -121.7654 | No | Overcast-Fog;32-90 F |  |  | 23-0116235 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1873763 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | TRANSFORMER | 412738052439 | 20230913 | 1147 | 20230913 | 1742 | 2217775 | 355 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 355 | 36.7469 | -121.4806 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0116126 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1873745 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5489 | 20230913 | 1342 | 20230913 | 1621 | 2217999 | 159 | Distribution Circuit | Vegetation | Tree - grew into line | 19 | 3021 | 37.1354 | -122.1407 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0116136 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1873749 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2103 | 182492103 | TRANSFORMER | 413050756277 | 20230913 | 1643 | 20230913 | 1859 | 2218186 | 136 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 136 | 36.8556 | -121.3765 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 23-0116297 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1873782 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | HOLLISTER | TRES PINOS-1111 | 183221111 | RECLOSER | 4064 | 20230913 | 1955 | 20230914 | 1352 | 2218280 | 1077 | Distribution Circuit | Equipment Failure/Involved | Overhead | 106 | 13737 | 36.788 | -121.3161 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0116315 | OH | Sus | 45978921 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | No | 1873796 | 0 | EPSS Ckt | N | 2023 | B-GRD
CENTRAL COAST | KING CITY | SAN ARDO-1101 | 182191101 | OCB | 1101/2 | 20230913 | 2140 | 20230913 | 2155 | 2218305 | 15 | Distribution Circuit | Equipment Failure/Involved | Overhead | 149 | 2235 | 36.0734 | -120.9364 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0116327 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1873800 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | OCB | 2104/2 | 20230914 | 755 | 20230914 | 900 | 2218488 | 65 | Distribution Circuit | Animal | Squirrel | 3064 | 116728 | 37.0417 | -122.0256 | No | Overcast-Fog;32-90 F | Cutout- fuse holder | Normal | 23-0116434 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1873885 | 0 | EPSS Ckt | Y | 2023 | PHASE OC/ GRD OC I
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 67520 | 20230914 | 844 | 20230914 | 1155 | 2218596 | 191 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2736 | 481911 | 36.9577 | -121.8525 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 23-0116468 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1873949 | 0 | EPSS Ckt | Y | 2023 | B/C
CENTRAL COAST | KING CITY | SAN ARDO-1101 | 182191101 | FUSE | 7789 | 20230914 | 1229 | 20230914 | 1351 | 2218922 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 2296 | 36.1112 | -121.0874 | No | Clear;32-90 F |  |  | 23-0116683 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1874067 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 86397 | 20230914 | 1500 | 20230914 | 1519 | 2218979 | 19 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 76 | 37.0322 | -122.0148 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken | 23-0116746 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | None | 0 | No | No | No | 1874078 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | JUMPER | JUMPERS @ CGC# 411750043895 | 20230914 | 1655 | 20230914 | 2204 | 2219091 | 309 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 3708 | 36.5062 | -121.809 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0116835 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | None | 0 | No | No | No | 1874095 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | TRANSFORMER | 316703014575 | 20230914 | 1709 | 20230915 | 111 | 2218724 | 482 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 482 | 36.8949 | -121.6284 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0116848 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1874099 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6809 | 20230914 | 1714 | 20230914 | 1958 | 2219107 | 164 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 3444 | 36.8451 | -121.6349 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0116871 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1874109 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 7631 | 20230915 | 831 | 20230916 | 255 | 2219464 | 1104 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 2208 | 36.9503 | -121.8637 | No | Overcast-Fog;32-90 F | Conductor- Underground | Broken | 23-0117103 | UG | Sus | 45980608 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1874334 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SOLEDAD-2104 | 182052104 | TRANSFORMER | 413136742272 | 20230915 | 938 | 20230915 | 1115 | 2219678 | 97 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 97 | 36.4702 | -121.3377 | No | Clear;32-90 F |  |  | 23-0117153 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | None | 0 | No | No | No | 1874356 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 11243 | 20230915 | 1001 | 20230916 | 600 | 2219708 | 1199 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1597 | 36.8749 | -121.7775 | No | Overcast;32-90 F | Connector or Splice (OH) | Broken | 23-0117120 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1874347 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | RECLOSER | 944178 | 20230915 | 1016 | 20230915 | 1838 | 2219756 | 502 | Distribution Circuit | Vegetation | Tree - fell into line | 885 | 81048 | 37.0926 | -122.0964 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0117109 | OH | Sus | 31669267 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | No | 1874342 | 0 | EPSS Ckt | Y | 2023 | C-GRD
CENTRAL COAST | KING CITY | LOS COCHES-1102 | 182151102 | TRANSFORMER | 413279339016 | 20230915 | 1139 | 20230916 | 156 | 2219807 | 857 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 857 | 36.383 | -121.2832 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0117177 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1874360 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | TRANSFORMER | 413420737612 | 20230915 | 1235 | 20230915 | 2007 | 2219895 | 452 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 452 | 36.3458 | -121.2351 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0117240 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1874385 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | RECLOSER | 549180 | 20230915 | 1510 | 20230915 | 1635 | 2219996 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 765 | 36.0057 | -121.2422 | No | Clear;32-90 F |  |  | 23-0117310 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1874408 | 0 | EPSS Ckt | Y | 2023 | C-GRD
CENTRAL COAST | SALINAS | SOLEDAD-2105 | 182052105 | TRANSFORMER | 413068041898 | 20230915 | 1828 | 20230915 | 2209 | 2219953 | 221 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 221 | 36.4609 | -121.3584 | No | Clear;32-90 F | Jumper | Burned Open | 23-0117360 | OH | Sus | 45981245 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1874421 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | TRANSFORMER | 411820649974 | 20230916 | 721 | 20230916 | 821 | 2220366 | 60 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 540 | 36.6734 | -121.791 | No | Overcast;32-90 F | Cutout- fuse holder | Broken | 23-0117402 | OH | Sus | 31668991 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1874488 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | RECLOSER | 113634 | 20230917 | 606 | 20230917 | 1121 | 2220873 | 315 | Distribution Circuit | 3rd Party | Vehicle | 91 | 14565 | 36.961 | -121.4309 | No | Overcast;32-90 F | Pole-Wood | On Ground | 23-0117517 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1874598 | 0 | EPSS Ckt | Y | 2023 | A & B PHASE
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | RECLOSER | 37088 | 20230917 | 634 | 20230917 | 828 | 2220906 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3037 | 338869 | 36.5465 | -121.8985 | No | Overcast;32-90 F |  |  | 23-0117520 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1874601 | 0 | EPSS Ckt | Y | 2023 | DCD
CENTRAL COAST | KING CITY | KING CITY-1101 | 182031101 | FUSE | 9897 | 20230917 | 1228 | 20230917 | 1315 | 2221024 | 47 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 47 | 36.2024 | -121.1292 | No | Partly Cloudy;32-90 F |  |  | 23-0117551 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1874631 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1101 | 182031101 | FUSE | 9897 | 20230917 | 1425 | 20230917 | 1528 | 2221040 | 63 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 63 | 36.2024 | -121.1292 | No | Partly Cloudy;32-90 F |  |  | 23-0117558 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1874639 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | TRANSFORMER | 412165749804 | 20230917 | 2031 | 20230918 | 305 | 2221129 | 394 | Transformer only | Equipment Failure/Involved | Overhead | 23 | 9062 | 36.6714 | -121.673 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0117582 | OH | Sus | 31669381 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1874663 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 3301 | 20230918 | 305 | 20230918 | 538 | 2221162 | 153 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 255 | 36.9712 | -121.7758 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0117598 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1874680 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | JUMPER | OJ 3 E/OF CGC#411813150751 | 20230918 | 1128 | 20230918 | 1139 | 2221599 | 11 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 209 | 36.6941 | -121.7931 | No | Clear;32-90 F | Anchor or Guy | Broken | 23-0117764 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1874887 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | RECLOSER | 491190 | 20230918 | 1248 | 20230918 | 1355 | 2221667 | 67 | Distribution Circuit | Company Initiated | Personnel- company | 807 | 54069 | 36.8007 | -121.7217 | No | Clear;32-90 F | Recloser | Malfunctioning | 23-0117817 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | None | 0 | No | No | No | 1874908 | 0 | EPSS Ckt | Y | 2023 | DCD/SGF
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | TRANSFORMER | 100000025998 | 20230919 | 709 | 20230919 | 738 | 2222095 | 29 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 29 | 36.433 | -121.4182 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0118054 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1875016 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | SWITCH | 84623 | 20230919 | 735 | 20230919 | 1820 | 2222116 | 645 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 6450 | 37.0551 | -122.0501 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0074754 | OH | Sus | 35356707 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1875014 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1101 | 182201101 | TRANSFORMER | 100000036895 | 20230919 | 1103 | 20230920 | 233 | 2222447 | 930 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 930 | 36.6055 | -121.6003 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0118227 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1875230 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1103 | 182131103 | TRANSFORMER | 412783043171 | 20230919 | 1104 | 20230920 | 527 | 2222450 | 1103 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1103 | 36.4939 | -121.4567 | No | Clear;32-90 F | Transformer | Leaking | 23-0118175 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1875210 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | TRANSFORMER | 316215013350 | 20230919 | 1105 | 20230919 | 1445 | 2222231 | 220 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 220 | 36.8597 | -121.7944 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0118176 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1875211 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | SWITCH | 8451 | 20230919 | 1313 | 20230919 | 2319 | 2222553 | 606 | Distribution Circuit | Vegetation | Tree - branch fell on line | 396 | 59576 | 37.1463 | -122.1334 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0118256 | OH | Sus | 31669597 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1875239 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 4309 | 20230919 | 1539 | 20230919 | 2010 | 2222646 | 271 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 3252 | 36.81 | -121.7218 | No | Partly Cloudy;32-90 F |  |  | 23-0118443 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1875299 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 5709 | 20230919 | 1610 | 20230919 | 2035 | 2222676 | 265 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 795 | 36.7984 | -121.7452 | No | Partly Cloudy;32-90 F |  |  | 23-0118445 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1875300 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1106 | 182031106 | OTHER | 99446 | 20230920 | 459 | 20230920 | 1136 | 2222853 | 397 | Distribution Circuit | Equipment Failure/Involved | Overhead | 305 | 68182 | 36.2129 | -121.1203 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0118509 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | Yes | 1875337 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | FORT ORD-2107 | 182402107 | TRANSFORMER | 411818750137 | 20230920 | 927 | 20230920 | 935 | 2222954 | 8 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 72 | 36.678 | -121.7919 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0118660 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1875535 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 2751 | 20230920 | 927 | 20230920 | 1421 | 2223208 | 294 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 5292 | 36.9693 | -121.8319 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0118646 | OH | Sus | 45985533 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1875518 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | RECLOSER | 2028 | 20230920 | 1018 | 20230920 | 1028 | 2223287 | 10 | Distribution Circuit | Company Initiated | Personnel- company | 395 | 3950 | 36.4728 | -121.7175 | No | Clear;32-90 F | Fuse | Normal | 23-0118688 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1875550 | 0 | EPSS Ckt | Y | 2023 | A- C
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 136050 | 20230920 | 1026 | 20230920 | 1105 | 2223302 | 39 | Distribution Circuit | Equipment Failure/Involved | Overhead | 230 | 8970 | 37.1525 | -122.134 | No | Clear;32-90 F | Recloser | Malfunctioning | 23-0089227 | OH | Sus | 35316415 | SOUTH BAY AND CENTRAL COAST | SEP | Three Phase Fault | 0 | No | No | No | 1875561 | 0 | EPSS Ckt | Y | 2023 | NONE
CENTRAL COAST | KING CITY | KING CITY-1105 | 182031105 | SWITCH | 124937 | 20230920 | 1315 | 20230920 | 1659 | 2223428 | 224 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 224 | 36.2257 | -121.1335 | No | Clear;32-90 F | Switch (OH) | Broken | 23-0118419 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1875595 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1105 | 182201105 | TRANSFORMER | 412418947652 | 20230920 | 1549 | 20230921 | 2300 | 2223427 | 1871 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1871 | 36.6146 | -121.584 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0118919 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1875634 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | RECLOSER | 432 | 20230920 | 2151 | 20230921 | 1123 | 2223742 | 812 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 323 | 201216 | 36.398 | -121.6493 | No | Partly Cloudy;32-90 F |  |  | 23-0118983 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1875662 | 0 | EPSS Ckt | Y | 2023 | AC
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412275755159 | 20230922 | 921 | 20230922 | 1619 | 2224600 | 418 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1254 | 36.8196 | -121.6402 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0119634 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1876008 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | BUENA VISTA-1102 | 182261102 | FUSE | 696907 | 20230922 | 1042 | 20230922 | 1220 | 2224792 | 98 | Distribution Circuit | 3rd Party | Vehicle | 11 | 1046 | 36.6498 | -121.6313 | No | Overcast;32-90 F | Anchor or Guy | Normal | 23-0119797 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1876077 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0424 | 182440424 | TRANSFORMER | 411418148678 | 20230922 | 1603 | 20230922 | 1840 | 2225005 | 157 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 1413 | 36.6342 | -121.9264 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken | 23-0119930 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1876117 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | RECLOSER | 549180 | 20230922 | 2055 | 20230922 | 2213 | 2225127 | 78 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 702 | 36.0057 | -121.2422 | No | Partly Cloudy;32-90 F |  |  | 23-0119968 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1876128 | 0 | EPSS Ckt | Y | 2023 | A GRD
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | RECLOSER | 4002 | 20230923 | 651 | 20230923 | 747 | 2225192 | 56 | Distribution Circuit | Animal | Bird found | 170 | 5890 | 36.8322 | -121.5312 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0119993 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1876153 | 0 | EPSS Ckt | Y | 2023 | A- C
CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | RECLOSER | 549180 | 20230923 | 735 | 20230923 | 919 | 2225219 | 104 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 936 | 36.0057 | -121.2422 | No | Fog;32-90 F |  |  | 23-0120001 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1876157 | 0 | EPSS Ckt | Y | 2023 | A- C
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 10473 | 20230924 | 655 | 20230924 | 1139 | 2225766 | 284 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 1136 | 36.9742 | -122.0626 | No | Partly Cloudy;32-90 F |  |  | 23-0120139 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1876314 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | RECLOSER | 428102 | 20230924 | 659 | 20230924 | 1014 | 2225767 | 195 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 346 | 67470 | 36.9976 | -121.9515 | No | Partly Cloudy;32-90 F |  |  | 23-0120130 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1876285 | 0 | EPSS Ckt | Y | 2023 | B- GRD
CENTRAL COAST | COAST | PAUL SWEET-2103 | 83252103 | FUSE | 3103 | 20230925 | 833 | 20230925 | 1005 | 2226254 | 92 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 3220 | 36.9811 | -122.0225 | No | Overcast-Drizzle;32-90 F |  |  | 23-0120296 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1876539 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SOLEDAD-2104 | 182052104 | TRANSFORMER | 413098039626 | 20230925 | 836 | 20230925 | 1412 | 2226155 | 336 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1344 | 36.3988 | -121.3464 | No | Partly Cloudy-Fog;32-90 F | Transformer | Arcing | 23-0120268 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1876470 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 67520 | 20230925 | 1307 | 20230925 | 2158 | 2226675 | 531 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 2736 | 296226 | 36.9577 | -121.8525 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0120453 | OH | Sus | 31670303 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | No | 1876624 | 0 | EPSS Ckt | Y | 2023 | C-GRD
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 10960 | 20230926 | 34 | 20230926 | 157 | 2227058 | 75 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2393 | 84540 | 36.9866 | -121.8582 | No | Fog;32-90 F |  |  | 23-0120685 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1876727 | 0 | EPSS Ckt | Y | 2023 | AC
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 11829 | 20230926 | 431 | 20230926 | 930 | 2227159 | 299 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1495 | 37.009 | -122.0756 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0120711 | OH | Sus | 45990019 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1876743 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | OCB | 1102/2 | 20230926 | 644 | 20230926 | 849 | 2227196 | 125 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2147 | 221407 | 36.5569 | -121.8976 | No | Partly Cloudy;32-90 F |  |  | 23-0120723 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Multi-Fault | 0 | No | No | No | 1876747 | 0 | EPSS Ckt | N | 2023 | B-C-GRD
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | RECLOSER | 88772 | 20230926 | 1414 | 20230926 | 1627 | 2227771 | 133 | Distribution Circuit | Vegetation | Tree - bark fell into line | 1255 | 157465 | 36.904 | -121.6085 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0121054 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1877000 | 0 | EPSS Ckt | Y | 2023 | C/GRD
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | FUSE | 53607 | 20230926 | 2008 | 20230927 | 623 | 2228035 | 615 | Distribution Circuit | 3rd Party | Vehicle | 38 | 23370 | 36.9819 | -121.9792 | No | Clear;32-90 F | Anchor or Guy | Broken | 23-0121202 | OH | Sus | 31670397 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1877063 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316467014940 | 20230926 | 2329 | 20230927 | 432 | 2228060 | 303 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 303 | 36.9041 | -121.7096 | No | Clear;32-90 F |  |  | 23-0121227 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1877084 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 316181118292 | 20230927 | 37 | 20230927 | 1145 | 2228117 | 668 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 2004 | 36.9951 | -121.8084 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0121255 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1877099 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | FUSE | 9079 | 20230927 | 53 | 20230927 | 1427 | 2228120 | 814 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 1628 | 36.8376 | -121.4551 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0121253 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Three Phase Fault | 0 | No | Yes | No | 1877095 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | RECLOSER | 741002 | 20230927 | 1027 | 20230927 | 1034 | 2228498 | 7 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 523 | 3661 | 36.597 | -121.6247 | No | Clear;32-90 F |  |  | 23-0121430 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1877290 | 0 | EPSS Ckt | N | 2023 | AB/I
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | TRANSFORMER | 412423946111 | 20230927 | 1151 | 20230927 | 1745 | 2228584 | 354 | Transformer only | Animal | Bird found | 5 | 1770 | 36.5723 | -121.5804 | No | Clear;32-90 F | Fuse | Normal | 23-0121598 | OH | Sus | 31670621 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1877342 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | FUSE | 411947349938 | 20230927 | 1229 | 20230927 | 2222 | 2228624 | 593 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 5113 | 36.6731 | -121.7472 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0121589 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1877341 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | FUSE | 663423 | 20230927 | 1946 | 20230928 | 204 | 2228955 | 378 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 378 | 36.2949 | -121.2034 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0121770 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1877378 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1109 | 182011109 | OTHER | WIRE DOWN | 20230927 | 2128 | 20230928 | 606 | 2229000 | 518 | Distribution Circuit | 3rd Party | Metallic Balloon | 3995 | 232786 | 36.6789 | -121.6085 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0121796 | OH | Sus | 31670510 | SOUTH BAY AND CENTRAL COAST | SEP | Open Circuit | 0 | No | Yes | Yes | 1877396 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411960450493 | 20230928 | 913 | 20230928 | 1700 | 2229150 | 467 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 934 | 36.6888 | -121.7444 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0121930 | OH | Sus | 35492391 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1877539 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 7757 | 20230928 | 1208 | 20230928 | 1356 | 2229544 | 108 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 540 | 37.0132 | -121.9372 | No | Clear;32-90 F |  |  | 23-0122151 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1877651 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO-1101 | 182191101 | RECLOSER | 7054 | 20230928 | 1334 | 20230929 | 27 | 2229557 | 653 | Distribution Circuit | 3rd Party | Vehicle | 20 | 9558 | 36.1127 | -121.0362 | No | Clear;32-90 F | Pole-Wood | Broken- wire on object | 23-0122157 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | Yes | No | 1877654 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | RECLOSER | 11046 | 20230928 | 1750 | 20230928 | 1809 | 2229816 | 19 | Distribution Circuit | Company Initiated | Personnel- company | 683 | 12977 | 36.9995 | -122.0078 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0122287 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1877704 | 0 | EPSS Ckt | Y | 2023 | B/GRD
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | TRANSFORMER | 315958317553 | 20230928 | 2013 | 20230928 | 2030 | 2229849 | 17 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 51 | 36.9738 | -121.8846 | No | Clear;32-90 F | Connector or Splice (OH) | Arcing | 23-0122308 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1877715 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316675813162 | 20230929 | 105 | 20230929 | 307 | 2229964 | 122 | Transformer only | Equipment Failure/Involved | Underground | 3 | 366 | 36.8562 | -121.637 | No | Clear;32-90 F | Connector or Splice (UG) | Broken | 23-0122350 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1877747 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | TRANSFORMER | 412314351365 | 20230929 | 817 | 20230929 | 1149 | 2230117 | 212 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 848 | 36.7151 | -121.6235 | No | Clear;32-90 F |  |  | 23-0122574 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | None | 0 | No | No | No | 1877930 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | TRANSFORMER | 100000084756 | 20230929 | 2002 | 20230930 | 950 | 2230750 | 828 | Transformer only | Vegetation | Tree - fell into line | 1 | 828 | 37.0367 | -121.9848 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0122773 | OH | Sus | 35492784 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1878002 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2101 | 182492101 | FUSE | 44963 | 20230930 | 135 | 20230930 | 247 | 2231180 | 72 | Distribution Circuit | 3rd Party | Metallic Balloon | 13 | 936 | 36.84 | -121.4059 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0122815 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1878050 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2101 | 182492101 | FUSE | 9951 | 20230930 | 301 | 20230930 | 328 | 2231191 | 27 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 675 | 36.8361 | -121.4191 | No | Partly Cloudy;32-90 F |  |  | 23-0122824 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1878060 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1105 | 182201105 | OCB | 1105/2 | 20230930 | 332 | 20230930 | 530 | 2231249 | 118 | Distribution Circuit | Equipment Failure/Involved | Overhead | 67 | 7906 | 36.6139 | -121.5666 | No | Overcast-Rain;32-90 F | Regulator | Failed/Faulted | 23-0122823 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1878059 | 0 | Non-EPSS | N | 2023 | SET A RLY
CENTRAL COAST | MONTEREY | FORT ORD-2106 | 182402106 | FUSE | 40725 | 20230930 | 803 | 20230930 | 1705 | 2231371 | 542 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 41 | 22222 | 36.671 | -121.7932 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Burned/flashed | 23-0122881 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1878142 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2103 | 83252103 | TRANSFORMER | T1130 | 20230930 | 837 | 20230930 | 857 | 2231414 | 20 | Transformer only | Equipment Failure/Involved | Underground | 1 | 20 | 36.98 | -122.0209 | No | Overcast;32-90 F | Transformer (UG) | Deteriorated | 23-0122876 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1878136 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 10788 | 20230930 | 1114 | 20230930 | 1502 | 2231544 | 228 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 887 | 21047 | 36.9044 | -121.7438 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0122929 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1878181 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | RECLOSER | 11046 | 20230930 | 1341 | 20230930 | 1622 | 2231658 | 161 | Distribution Circuit | Vegetation | Tree - branch fell on line | 351 | 56511 | 36.9995 | -122.0078 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0122972 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1878213 | 0 | EPSS Ckt | Y | 2023 | B & GRD
CENTRAL COAST | KING CITY | SOLEDAD-2105 | 182052105 | RECLOSER | 823854 | 20230930 | 1426 | 20230930 | 2010 | 2231710 | 344 | Distribution Circuit | Equipment Failure/Involved | Overhead | 217 | 18488 | 36.4271 | -121.313 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0122979 | OH | Sus | 45995125 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1878216 | 0 | EPSS Ckt | Y | 2023 | B-GRD
CENTRAL COAST | KING CITY | SOLEDAD-2105 | 182052105 | RECLOSER | 823854 | 20230930 | 1619 | 20230930 | 1835 | 2231773 | 136 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 216 | 29376 | 36.4271 | -121.313 | No | Partly Cloudy;32-90 F |  |  | 23-0123006 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1878233 | 0 | EPSS Ckt | Y | 2023 | B & C
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 4569 | 20230930 | 1645 | 20230930 | 1844 | 2231786 | 119 | Distribution Circuit | Animal | Bird found | 4 | 476 | 37.0333 | -121.987 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0123030 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1878256 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | RECLOSER | 3034 | 20230930 | 2137 | 20230930 | 2243 | 2231963 | 66 | Distribution Circuit | 3rd Party | Vehicle | 544 | 35904 | 36.7317 | -121.6129 | No | Overcast;32-90 F | Pole-Wood | Normal | 23-0123044 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1878272 | 0 | EPSS Ckt | Y | 2023 | A & B
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | RECLOSER | 1132 | 20231001 | 640 | 20231001 | 1137 | 2232031 | 297 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 163 | 32679 | 36.3584 | -121.2034 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0123071 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1878301 | 0 | Non-EPSS | Y | 2023 | AB
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 310750 | 20231001 | 1922 | 20231002 | 613 | 2232283 | 651 | Distribution Circuit | 3rd Party | Vehicle | 1503 | 176843 | 36.916 | -121.7339 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0123141 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Multi-Fault | 0 | No | Yes | No | 1878374 | 0 | EPSS Ckt | N | 2023 | A B C GRD 51
CENTRAL COAST | SALINAS | BUENA VISTA-1106 | 182261106 | RECLOSER | 3714 | 20231002 | 529 | 20231002 | 1830 | 2232397 | 781 | Distribution Circuit | 3rd Party | Vehicle | 31 | 24211 | 36.6414 | -121.6072 | No | Overcast;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0123179 | OH | Sus | 31671102 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1878408 | 0 | Non-EPSS | N | 2023 | B&GRD
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | RECLOSER | 7062 | 20231002 | 640 | 20231002 | 824 | 2232408 | 104 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 50 | 5200 | 36.2789 | -121.3033 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0123185 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1878413 | 0 | EPSS Ckt | Y | 2023 | B-C
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | TRANSFORMER | 315842520800 | 20231002 | 1213 | 20231003 | 523 | 2232774 | 1030 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 2953 | 37.062 | -121.9264 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0123392 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1878613 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 41677 | 20231002 | 1742 | 20231003 | 30 | 2233186 | 408 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 1766 | 36.711 | -121.6997 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0123600 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1878724 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | FORT ORD-2105 | 182402105 | TRANSFORMER | 411736048851 | 20231002 | 1810 | 20231002 | 1825 | 2233196 | 15 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 90 | 36.6422 | -121.8179 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0123538 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1878664 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | BUENA VISTA-1106 | 182261106 | OCB | 1106/2 | 20231002 | 1830 | 20231003 | 945 | 2233210 | 889 | Distribution Circuit | 3rd Party | Vehicle | 31 | 8240 | 36.6539 | -121.6292 | No | Partly Cloudy;32-90 F | Capacitor | Burned/flashed | 23-0123179 | OH | Sus | 31671102 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1878666 | 0 | Non-EPSS | N | 2023 | A PH & GRD
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 5923 | 20231002 | 2136 | 20231002 | 2308 | 2233112 | 92 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 92 | 36.971 | -122.1244 | No | Partly Cloudy;32-90 F | Transformer (OH) | Burned/flashed | 23-0123558 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1878683 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 41677 | 20231003 | 506 | 20231003 | 1052 | 2233356 | 346 | Distribution Circuit | 3rd Party | Vehicle | 13 | 4498 | 36.711 | -121.6997 | No | Clear;32-90 F | Anchor or Guy | Broken | 23-0123760 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1878933 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 9442 | 20231003 | 927 | 20231003 | 1010 | 2233585 | 43 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 124 | 5332 | 36.6222 | -121.9167 | No | Partly Cloudy;32-90 F |  |  | 23-0123721 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1878922 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | TRANSFORMER | 9442 | 20231003 | 1055 | 20231004 | 29 | 2233684 | 176 | Distribution Circuit | Equipment Failure/Involved | Underground | 110 | 19560 | 36.6222 | -121.9167 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0123828 | UG | Sus | 35493562 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1878948 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | TRANSFORMER | 316261113364 | 20231003 | 1344 | 20231003 | 1521 | 2233932 | 97 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 194 | 36.8601 | -121.7793 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0123990 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1878991 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 412054949985 | 20231003 | 1421 | 20231003 | 2324 | 2233712 | 543 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 543 | 36.6755 | -121.71 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0123915 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1878978 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | JUMPER | JMPRS 2 POLES SOURCE SIDE OF CGC 316257417120 | 20231003 | 1810 | 20231003 | 2207 | 2234040 | 237 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 474 | 36.9627 | -121.7814 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0124048 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1879009 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SOLEDAD-2105 | 182052105 | SWITCH | 227086 | 20231003 | 2001 | 20231003 | 2117 | 2234097 | 76 | Distribution Circuit | Equipment Failure/Involved | Underground | 101 | 3776 | 36.4299 | -121.3148 | No | Clear;32-90 F | Switch (UG) | Broken | 23-0123897 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1879025 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 8033 | 20231003 | 2138 | 20231004 | 515 | 2234128 | 457 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3656 | 37.1035 | -122.2771 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0124081 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1879033 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | RECLOSER | 974130 | 20231004 | 715 | 20231004 | 845 | 2234199 | 90 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 91 | 8190 | 37.0448 | -121.9382 | No | Clear;32-90 F |  |  | 23-0124166 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1879089 | 0 | EPSS Ckt | Y | 2023 | GRD
CENTRAL COAST | SALINAS | SPENCE-1103 | 182201103 | JUMPER | WIRE DWN JSO CGC 412548448217 | 20231004 | 851 | 20231004 | 2005 | 2234341 | 674 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 674 | 36.6306 | -121.5408 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0124319 | OH | Sus | 31671401 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1879294 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | FUSE | 4447 | 20231004 | 932 | 20231004 | 1002 | 2234444 | 30 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 900 | 36.7894 | -121.36 | No | Clear;32-90 F |  |  | 23-0124292 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1879272 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 50107 | 20231004 | 1127 | 20231004 | 1204 | 2234659 | 37 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 37 | 36.8961 | -121.4016 | No | Clear;32-90 F |  |  | 23-0124374 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1879318 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 11451 | 20231004 | 1326 | 20231004 | 1438 | 2234759 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 48 | 36.8556 | -121.7946 | No | Clear;32-90 F |  |  | 23-0124505 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1879356 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | RECLOSER | 68346 | 20231004 | 1850 | 20231005 | 349 | 2234996 | 539 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1668 | 185756 | 36.7226 | -121.6635 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0124636 | OH | Sus | 46000324 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1879389 | 0 | EPSS Ckt | N | 2023 | B- GRD- 50- 51
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | RECLOSER | 36982 | 20231005 | 614 | 20231005 | 1839 | 2235239 | 745 | Distribution Circuit | 3rd Party | Vehicle | 171 | 78087 | 36.5301 | -121.4747 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0124707 | OH | Sus | 31671413 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1879443 | 0 | EPSS Ckt | Y | 2023 | A-B
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6805 | 20231005 | 950 | 20231005 | 1210 | 2235565 | 140 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 233 | 36.9396 | -121.7419 | No | Clear;32-90 F |  |  | 23-0124892 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1879644 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | TRANSFORMER | T0832 | 20231005 | 1117 | 20231006 | 650 | 2235899 | 1173 | Distribution Circuit | Equipment Failure/Involved | Underground | 23 | 2717 | 36.9772 | -121.9675 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0125045 | UG | Sus | 35494222 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1879701 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 135762 | 20231005 | 1221 | 20231005 | 1257 | 2235712 | 36 | Distribution Circuit | Animal | Bird found | 37 | 1332 | 36.9567 | -121.7269 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0124906 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1879653 | 0 | EPSS Ckt | Y | 2023 | A GRD
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 5597 | 20231005 | 1317 | 20231005 | 1429 | 2235771 | 72 | Distribution Circuit | Equipment Failure/Involved | Overhead | 259 | 8263 | 36.7816 | -121.7203 | No | Clear;Above 90 | Cutout- fuse holder | Broken | 23-0124982 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Open Circuit | 0 | No | No | No | 1879683 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | HOLLISTER | SAN BENITO-2102 | 182742102 | TRANSFORMER | 412717056371 | 20231005 | 1321 | 20231005 | 1710 | 2235775 | 229 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 458 | 36.8555 | -121.4907 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0124975 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1879682 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 7987 | 20231005 | 1737 | 20231006 | 56 | 2235985 | 439 | Distribution Circuit | Equipment Failure/Involved | Overhead | 44 | 2675 | 36.8458 | -121.6363 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0125096 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1879716 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6805 | 20231005 | 1744 | 20231005 | 2044 | 2235988 | 180 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 300 | 36.9396 | -121.7419 | No | Clear;32-90 F |  |  | 23-0125107 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1879726 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412148754142 | 20231005 | 1853 | 20231006 | 255 | 2236031 | 482 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1446 | 36.7903 | -121.683 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0125109 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1879728 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1101 | 182011101 | TRANSFORMER | 412236349695 | 20231005 | 1924 | 20231006 | 12 | 2236046 | 288 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 4320 | 36.6689 | -121.649 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0125102 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1879722 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | SWITCH | 6393 | 20231005 | 2239 | 20231006 | 133 | 2236130 | 174 | Distribution Circuit | Equipment Failure/Involved | Overhead | 45 | 7830 | 36.8914 | -121.6904 | No | Clear;32-90 F | Insulator | Broken | 23-0125103 | OH | Sus | 31671592 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1879759 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | RECLOSER | 4002 | 20231006 | 657 | 20231006 | 808 | 2236278 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 170 | 12070 | 36.8322 | -121.5312 | No | Clear;32-90 F |  |  | 23-0125174 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Three Phase Fault | 0 | No | No | No | 1879799 | 0 | EPSS Ckt | Y | 2023 | A-B-C
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | TRANSFORMER | 411824633943 | 20231006 | 708 | 20231006 | 1510 | 2236283 | 482 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 482 | 36.232 | -121.7752 | No | Clear;32-90 F | Anchor or Guy | Burned/flashed | 23-0125497 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1880004 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SOLEDAD-2104 | 182052104 | FUSE | 7721 | 20231006 | 1014 | 20231006 | 1504 | 2236541 | 290 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 7540 | 36.3794 | -121.3399 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0125444 | OH | Sus | 31671507 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | Yes | No | 1879984 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | RECLOSER | 5404 | 20231006 | 1135 | 20231006 | 1316 | 2236635 | 101 | Distribution Circuit | Vegetation | Tree - branch fell on line | 740 | 63435 | 37.0157 | -122.0254 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0125417 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1879975 | 0 | EPSS Ckt | Y | 2023 | A GRD
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | SWITCH | 777828 | 20231006 | 1136 | 20231006 | 1234 | 2236632 | 58 | Distribution Circuit | Vegetation | Tree - fell into line | 1659 | 96222 | 36.9871 | -122.0358 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0125413 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Open Circuit | 0 | No | No | No | 1879974 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | JUMPER | BURNT OJ SS OF 4793 | 20231006 | 1458 | 20231006 | 2045 | 2236862 | 347 | Distribution Circuit | Equipment Failure/Involved | Overhead | 171 | 59337 | 36.7982 | -121.6457 | No | Clear;32-90 F | Jumper | Burned Open | 23-0125621 | OH | Sus | 31671789 | SOUTH BAY AND CENTRAL COAST | OCT | Open Circuit | 0 | No | No | No | 1880068 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1104 | 182031104 | RECLOSER | 7092 | 20231006 | 1745 | 20231006 | 1753 | 2236979 | 8 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 58 | 464 | 36.2036 | -121.1157 | No | Clear;Above 90 |  |  | 23-0125622 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1880069 | 0 | EPSS Ckt | N | 2023 | C-GRD
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | RECLOSER | 22104 | 20231006 | 2138 | 20231006 | 2146 | 2237194 | 8 | Distribution Circuit | Vegetation | Tree - branch fell on line | 990 | 7920 | 36.7957 | -121.6669 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0125649 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1880093 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | SALINAS | SOLEDAD-2105 | 182052105 | FUSE | 7021 | 20231006 | 2159 | 20231007 | 1615 | 2237237 | 1096 | Distribution Circuit | 3rd Party | Vehicle | 8 | 8768 | 36.4581 | -121.3788 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0125660 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Three Phase Fault | 0 | No | Yes | No | 1880106 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 316095615372 | 20231006 | 2200 | 20231007 | 1040 | 2237204 | 760 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1520 | 36.9144 | -121.8365 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0125658 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1880104 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | OCB | 1102/2 | 20231007 | 151 | 20231007 | 316 | 2237281 | 85 | Distribution Circuit | Animal | Bird found | 606 | 51510 | 36.0134 | -121.1674 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0125664 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1880109 | 0 | EPSS Ckt | Y | 2023 | B- C- 50
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | JUMPER | OJ 1 S/OF 11497 | 20231007 | 908 | 20231007 | 1637 | 2237458 | 442 | Distribution Circuit | 3rd Party | Vehicle | 8 | 3536 | 36.9043 | -121.7367 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0125698 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1880178 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | TRANSFORMER | 316466713111 | 20231007 | 1457 | 20231007 | 2310 | 2237707 | 493 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 986 | 36.8539 | -121.7085 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 23-0125765 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1880236 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | TRANSFORMER | 411796050694 | 20231007 | 1655 | 20231007 | 2202 | 2237844 | 307 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 307 | 36.6929 | -121.7996 | No | Clear;32-90 F | Other | Broken | 23-0125774 | OH | Sus | 46003056 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1880241 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | FUSE | 1443 | 20231007 | 1732 | 20231008 | 2107 | 2237872 | 1655 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 3310 | 36.9879 | -121.9244 | No | Clear;32-90 F | Connector or Splice (UG) | Failed/Faulted | 23-0125779 | UG | Sus | 46003300 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1880246 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | RECLOSER | 4002 | 20231008 | 653 | 20231008 | 812 | 2238121 | 79 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 170 | 13430 | 36.8322 | -121.5312 | No | Clear;32-90 F |  |  | 23-0125837 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1880298 | 0 | EPSS Ckt | Y | 2023 | BC
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6487 | 20231008 | 746 | 20231008 | 935 | 2238149 | 109 | Distribution Circuit | 3rd Party | Metallic Balloon | 15 | 1635 | 36.8972 | -121.6758 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0125852 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1880318 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1106 | 182011106 | TRANSFORMER | 412220649709 | 20231008 | 1832 | 20231008 | 1943 | 2238368 | 71 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 994 | 36.6691 | -121.6543 | No | Overcast;32-90 F | Fuse | Broken | 23-0125881 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1880360 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1104 | 182031104 | RECLOSER | 7092 | 20231009 | 408 | 20231009 | 906 | 2238515 | 298 | Distribution Circuit | 3rd Party | Other | 58 | 17284 | 36.2036 | -121.1157 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0125907 | OH | Sus | 46003748 | SOUTH BAY AND CENTRAL COAST | OCT | Three Phase Fault | 0 | No | No | No | 1880395 | 0 | EPSS Ckt | N | 2023 | A- B- C
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 33542 | 20231009 | 656 | 20231009 | 952 | 2238529 | 176 | Distribution Circuit | Vegetation | Tree - branch fell on line | 400 | 60436 | 37.0906 | -122.0456 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0125918 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1880415 | 0 | EPSS Ckt | Y | 2023 | B & INST
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 10960 | 20231009 | 720 | 20231009 | 953 | 2238569 | 153 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2393 | 366129 | 36.9866 | -121.8582 | No | Overcast-Fog;32-90 F |  |  | 23-0125931 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1880428 | 0 | EPSS Ckt | Y | 2023 | A & GRD TGTS
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 700187 | 20231009 | 1038 | 20231009 | 1140 | 2238895 | 62 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 310 | 36.8949 | -121.7773 | No | Overcast;32-90 F |  |  | 23-0126047 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1880610 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-1101 | 182221101 | RECLOSER | 38582 | 20231009 | 1335 | 20231009 | 1344 | 2239048 | 9 | Distribution Circuit | 3rd Party | Other | 746 | 6714 | 36.6191 | -121.8249 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0126121 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1880659 | 0 | EPSS Ckt | N | 2023 | NONE
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | RECLOSER | 11048 | 20231009 | 1739 | 20231010 | 726 | 2239281 | 827 | Distribution Circuit | Vegetation | Tree - fell into line | 748 | 139119 | 37.0482 | -122.0339 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0126242 | OH | Sus | 46004200 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1880697 | 0 | EPSS Ckt | Y | 2023 | A- GRD
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 5061 | 20231009 | 1858 | 20231009 | 2002 | 2239360 | 64 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 85 | 36.7591 | -121.7642 | No | Clear;32-90 F |  |  | 23-0126276 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1880714 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 12009 | 20231010 | 643 | 20231010 | 845 | 2239536 | 122 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 610 | 36.8535 | -121.6486 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0126404 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1880862 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | TRANSFORMER | 411699644200 | 20231010 | 846 | 20231010 | 1046 | 2239727 | 120 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 120 | 36.5137 | -121.8283 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0126476 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1880950 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 2615 | 20231010 | 1606 | 20231010 | 2118 | 2240147 | 312 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 936 | 37.0346 | -121.9969 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0126712 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1881021 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | TRANSFORMER | 316720013995 | 20231010 | 2118 | 20231011 | 244 | 2240304 | 326 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 326 | 36.8792 | -121.6225 | No | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0126801 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1881068 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | RECLOSER | 25695 | 20231010 | 2139 | 20231010 | 2310 | 2240311 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 157 | 14287 | 36.7493 | -121.6573 | No | Clear;32-90 F |  |  | 23-0126799 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1881067 | 1 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | RECLOSER | 440 | 20231011 | 726 | 20231011 | 902 | 2240428 | 96 | Distribution Circuit | Vegetation | Tree - branch fell on line | 378 | 28390 | 36.4389 | -121.9203 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0126854 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1881096 | 0 | EPSS Ckt | Y | 2023 | BC
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | FUSE | 24581 | 20231011 | 924 | 20231012 | 343 | 2240630 | 1099 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 2198 | 36.602 | -121.6756 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0127164 | OH | Sus | 46009960 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1881378 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 5921 | 20231011 | 1244 | 20231011 | 1451 | 2240928 | 127 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 254 | 36.961 | -122.0935 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0127045 | OH | Sus | 46009981 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1881339 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | TRANSFORMER | 412392751990 | 20231011 | 1327 | 20231011 | 1334 | 2240479 | 7 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 21 | 36.733 | -121.5975 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0127080 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1881353 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | 83500401 | 83500401 | RECLOSER | 12946 | 20231011 | 1413 | 20231011 | 1535 | 2241074 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 213 | 17466 | 36.9875 | -121.9186 | No | Clear;32-90 F |  |  | 23-0127109 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1881363 | 0 | EPSS Ckt | Y | 2023 | BC
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | RECLOSER | 11048 | 20231011 | 1429 | 20231011 | 2024 | 2241098 | 355 | Distribution Circuit | Equipment Failure/Involved | Overhead | 748 | 74959 | 37.0482 | -122.0339 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0127123 | OH | Sus | 46010375 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1881368 | 0 | EPSS Ckt | Y | 2023 | C GRD
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | RECLOSER | 557716 | 20231011 | 1509 | 20231012 | 308 | 2241140 | 719 | Distribution Circuit | Vegetation | Tree - bark fell into line | 333 | 61134 | 36.831 | -121.6794 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0127156 | OH | Sus | 31672018 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1881375 | 0 | EPSS Ckt | Y | 2023 | C SGF INST
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 1803 | 20231011 | 1515 | 20231011 | 2349 | 2241151 | 514 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 16 | 8224 | 36.9958 | -121.8303 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0127218 | OH | Sus | 46010407 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1881390 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 12124 | 20231011 | 1840 | 20231011 | 1947 | 2241275 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 480 | 14531 | 37.1677 | -122.1662 | No | Clear;32-90 F |  |  | 23-0127239 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1881400 | 0 | EPSS Ckt | Y | 2023 | A-B
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 9613 | 20231011 | 1922 | 20231012 | 802 | 2241305 | 758 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 2777 | 36.9726 | -121.76 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0127290 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1881429 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | SWITCH | 9427 | 20231012 | 1015 | 20231012 | 1521 | 2241425 | 306 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 1 | 306 | 36.5445 | -121.7981 | No | Partly Cloudy;32-90 F | Conductor- Underground | Normal | 23-0127328 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1881451 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2103 | 83252103 | OTHER | T0120 TWD T1130 | 20231012 | 1827 | 20231013 | 348 | 2242131 | 561 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 561 | 36.98 | -122.0195 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0127367 | UG | Sus | 35492812 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1881705 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | RECLOSER | 855412 | 20231013 | 722 | 20231013 | 1142 | 2242323 | 260 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 103 | 18626 | 36.9523 | -121.4743 | No | Partly Cloudy;32-90 F |  |  | 23-0127833 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1881770 | 0 | EPSS Ckt | Y | 2023 | BC
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 412054849515 | 20231013 | 1029 | 20231013 | 1234 | 2242594 | 125 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 125 | 36.6625 | -121.7111 | No | Clear;32-90 F |  |  | 23-0128052 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1881966 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | FUSE | 9111 | 20231013 | 1050 | 20231013 | 1140 | 2242607 | 50 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 1668 | 36.0178 | -120.9067 | No | Clear;32-90 F |  |  | 23-0128019 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1881955 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | FUSE | 9039 | 20231013 | 1307 | 20231013 | 1426 | 2242731 | 79 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 158 | 36.9624 | -121.4314 | No | Clear;32-90 F |  |  | 23-0128117 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1881990 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 9211 | 20231013 | 1623 | 20231013 | 1844 | 2242882 | 141 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 704 | 36.5718 | -121.8051 | No | Partly Cloudy;32-90 F | Jumper | Broken | 23-0128202 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1882013 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | RECLOSER | 12828 | 20231013 | 2155 | 20231013 | 2340 | 2243032 | 105 | Distribution Circuit | Vegetation | Tree - branch fell on line | 639 | 67095 | 36.9874 | -121.949 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0128238 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1882046 | 0 | EPSS Ckt | Y | 2023 | A & B PHSE
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 10960 | 20231014 | 300 | 20231014 | 815 | 2243094 | 315 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2391 | 335265 | 36.9866 | -121.8582 | No | Partly Cloudy;32-90 F |  |  | 23-0128245 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1882057 | 0 | EPSS Ckt | Y | 2023 | B
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | TRANSFORMER | 100000025998 | 20231014 | 618 | 20231014 | 1617 | 2243271 | 599 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 599 | 36.433 | -121.4182 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0128305 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1882173 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | RECLOSER | 4048 | 20231014 | 914 | 20231014 | 1007 | 2243259 | 53 | Distribution Circuit | Animal | Bird found | 127 | 6731 | 36.719 | -121.2811 | No | Clear;32-90 F | Recloser | Normal | 23-0128272 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1882160 | 0 | EPSS Ckt | Y | 2023 | SGF
CENTRAL COAST | MONTEREY | DEL MONTE-2102 | 182222102 | TRANSFORMER | 411629547724 | 20231015 | 105 | 20231015 | 1323 | 2243615 | 738 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 5904 | 36.6099 | -121.8536 | No | Overcast-Fog;32-90 F | Transformer | Failed/Faulted | 23-0128382 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1882238 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | FUSE | 4463 | 20231015 | 658 | 20231015 | 850 | 2243639 | 112 | Distribution Circuit | Animal | Bird found | 21 | 2352 | 36.5772 | -121.6292 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0128405 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1882255 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 5277 | 20231015 | 1239 | 20231015 | 1435 | 2243751 | 116 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 4640 | 36.7758 | -121.6878 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0128425 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1882274 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2101 | 182492101 | FUSE | 9953 | 20231015 | 1333 | 20231015 | 1404 | 2243764 | 31 | Distribution Circuit | Animal | Bird found | 84 | 2604 | 36.8443 | -121.4077 | No | Clear;32-90 F | Jumper | Normal | 23-0128420 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1882268 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0421 | 182440421 | TRANSFORMER | 411452148123 | 20231015 | 1435 | 20231015 | 1536 | 2243819 | 61 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 305 | 36.6193 | -121.9149 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 23-0128424 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1882273 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1106 | 182031106 | OCB | 1106/2 | 20231015 | 1841 | 20231016 | 425 | 2243921 | 584 | Distribution Circuit | Equipment Failure/Involved | Overhead | 339 | 76497 | 36.217 | -121.1269 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0128455 | OH | Sus | 31672824 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1882290 | 0 | EPSS Ckt | N | 2023 | B PHSE & GRD TIME
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 412004256017 | 20231015 | 1957 | 20231016 | 702 | 2243963 | 665 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 2660 | 36.8405 | -121.7335 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0128515 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1882344 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | RECLOSER | 2026 | 20231016 | 203 | 20231016 | 1858 | 2244047 | 1015 | Distribution Circuit | Equipment Failure/Involved | Underground | 3036 | 390499 | 36.5315 | -121.8375 | No | Overcast;32-90 F | Conductor- Underground | Deteriorated | 23-0128496 | UG | Sus | 46018012 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1882328 | 0 | EPSS Ckt | Y | 2023 | C-GRD
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | TRANSFORMER | 315816719648 | 20231016 | 711 | 20231016 | 1120 | 2244092 | 249 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 249 | 37.0307 | -121.9339 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 23-0128554 | OH | Sus | 46016450 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1882417 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1102 | 182201102 | FUSE | 25111 | 20231016 | 1015 | 20231016 | 1210 | 2244377 | 115 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 460 | 36.5889 | -121.5019 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 23-0128602 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1882488 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | RECLOSER | 36982 | 20231016 | 1323 | 20231016 | 1858 | 2244590 | 335 | Distribution Circuit | Equipment Failure/Involved | Overhead | 171 | 11421 | 36.5301 | -121.4747 | No | Overcast;32-90 F | Connector or Splice (OH) | Broken- wire on object | 23-0128740 | OH | Sus | 46018014 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1882546 | 0 | EPSS Ckt | Y | 2023 | SGF/INST/DCD
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | TRANSFORMER | 412158549562 | 20231016 | 1515 | 20231017 | 225 | 2244685 | 670 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 28618 | 36.6646 | -121.6751 | No | Overcast;32-90 F | Secondary | Burned Open | 23-0128863 | OH | Sus | 31672908 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1882575 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 10728 | 20231016 | 1533 | 20231016 | 1753 | 2244711 | 140 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1323 | 185220 | 37.0665 | -122.0797 | No | Overcast;32-90 F | Transformer (OH) | Normal | 23-0128858 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1882573 | 0 | EPSS Ckt | Y | 2023 | B/GRD
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 9463 | 20231016 | 1815 | 20231016 | 2105 | 2244837 | 170 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 60 | 10200 | 37.0697 | -122.0714 | No | Clear;32-90 F |  |  | 23-0128898 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1882591 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | JUMPER | OJ 1 POLE S/OF CGC 316251517775 | 20231016 | 2110 | 20231017 | 241 | 2244867 | 331 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1655 | 36.9804 | -121.7839 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0128897 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1882590 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | SWITCH | 557716 | 20231017 | 819 | 20231017 | 1515 | 2245029 | 416 | Distribution Circuit | Animal | Bird found | 333 | 45568 | 36.831 | -121.6794 | No | Fog;32-90 F | Transformer (OH) | Burned/flashed | 23-0129004 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1882680 | 0 | EPSS Ckt | Y | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | TRANSFORMER | 412968049292 | 20231017 | 930 | 20231017 | 1414 | 2245204 | 284 | Transformer only | Company Initiated | Personnel- company | 1 | 284 | 36.6636 | -121.3975 | No | Partly Cloudy;32-90 F | Transformer | Deteriorated | 23-0117645 | OH | Sus | 35425137 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1882806 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 107579 | 20231017 | 936 | 20231017 | 1204 | 2245171 | 148 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 1480 | 36.988 | -122.1579 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0129020 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1882786 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | TRANSFORMER | 412838240661 | 20231017 | 1120 | 20231018 | 21 | 2245176 | 781 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 781 | 36.4253 | -121.4353 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0129145 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1882857 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | TRANSFORMER | 412161349626 | 20231017 | 1456 | 20231018 | 323 | 2245559 | 747 | Transformer only | Equipment Failure/Involved | Overhead | 26 | 19422 | 36.6664 | -121.6743 | No | Clear;32-90 F | Secondary | Deteriorated | 23-0129313 | OH | Sus | 31672839 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1882926 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1112 | 182371112 | OCB | 1112/2 | 20231017 | 2025 | 20231017 | 2129 | 2245706 | 64 | Distribution Circuit | Company Initiated | Operating error | 2443 | 156352 | 36.4778 | -121.7271 | No | Clear;32-90 F | Circuit Breaker | Normal | 23-0110859 | OH | Sus | 31652875 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1882936 | 0 | EPSS Ckt | Y | 2023 | PH OC INST SGF
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | TRANSFORMER | 412479545770 | 20231018 | 650 | 20231018 | 2132 | 2245814 | 882 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 3528 | 36.5633 | -121.5617 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0129596 | OH | Sus | 31673372 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1883167 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2108 | 83252108 | JUMPER | OJ 1/2 SPAN W/OF 9019 | 20231018 | 2222 | 20231019 | 411 | 2246570 | 349 | Distribution Circuit | Vegetation | Tree - grew into line | 16 | 5584 | 36.9883 | -121.993 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0129787 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1883276 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | TRANSFORMER | 412291651809 | 20231019 | 1012 | 20231019 | 2140 | 2246711 | 688 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 688 | 36.7255 | -121.6325 | No | Clear;32-90 F | Fuse | Burned Open | 23-0130090 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1883351 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 6699 | 20231019 | 1136 | 20231019 | 1352 | 2246865 | 136 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 4 | 544 | 36.8672 | -121.7955 | No | Clear;32-90 F |  |  | 23-0130254 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1883397 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | RECLOSER | 566352 | 20231019 | 1227 | 20231019 | 1333 | 2246915 | 66 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 330 | 36.7687 | -121.6076 | No | Clear;32-90 F |  |  | 23-0130190 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1883378 | 0 | EPSS Ckt | Y | 2023 | A INST OC
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | RECLOSER | 7002 | 20231019 | 1536 | 20231019 | 1704 | 2247070 | 88 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 138 | 12144 | 35.9663 | -121.1146 | No | Clear;32-90 F |  |  | 23-0130340 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1883424 | 0 | EPSS Ckt | Y | 2023 | A-C
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | TRANSFORMER | 412291651809 | 20231019 | 1635 | 20231020 | 513 | 2247232 | 758 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 758 | 36.7255 | -121.6325 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0130411 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1883468 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | BUENA VISTA-1102 | 182261102 | TRANSFORMER | 412200948168 | 20231019 | 2231 | 20231020 | 1145 | 2247222 | 794 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1588 | 36.6266 | -121.659 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0130402 | OH | Sus | 31673521 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1883466 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1101 | 182201101 | RECLOSER | 965598 | 20231020 | 130 | 20231020 | 527 | 2247266 | 237 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 168 | 39816 | 36.5774 | -121.4917 | No | Partly Cloudy;32-90 F |  |  | 23-0130423 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1883473 | 0 | Non-EPSS | Y | 2023 | A & B
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 412077354161 | 20231020 | 941 | 20231020 | 1915 | 2247526 | 574 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 2296 | 36.7912 | -121.7075 | No | Clear;32-90 F |  | Failed/Faulted | 23-0130689 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1883692 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 6891 | 20231020 | 1343 | 20231020 | 1739 | 2247381 | 236 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 944 | 36.8847 | -121.7956 | No | Overcast-Fog;32-90 F | Crossarm- Wood | Burned/flashed | 23-0130677 | OH | Sus | 31673259 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1883690 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2102 | 182222102 | FUSE | 10453 | 20231020 | 1523 | 20231020 | 1609 | 2247802 | 46 | Distribution Circuit | Animal | Bird found | 2 | 92 | 36.6097 | -121.854 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Normal | 23-0130779 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1883711 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | TRANSFORMER | 411971943505 | 20231020 | 2113 | 20231021 | 858 | 2247920 | 705 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 705 | 36.4972 | -121.7322 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0130818 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1883728 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1103 | 182011103 | TRANSFORMER | 412200651025 | 20231020 | 2215 | 20231021 | 1432 | 2247931 | 977 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 15632 | 36.7051 | -121.6623 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0130841 | OH | Sus | 46027985 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1883747 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | RECLOSER | 2020 | 20231021 | 1102 | 20231021 | 1202 | 2248231 | 60 | Distribution Circuit | Company Initiated | Operating error | 838 | 50280 | 36.4632 | -121.7119 | No | Clear;32-90 F | Other | Normal | 23-0130904 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1883867 | 0 | EPSS Ckt | Y | 2023 | GRD
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | RECLOSER | 69608 | 20231021 | 2210 | 20231021 | 2317 | 2248557 | 67 | Distribution Circuit | Company Initiated | Operating error | 3529 | 163786 | 36.5203 | -121.7901 | No | Clear;32-90 F | Recloser | Normal | 23-0107512 | OH | Sus | 31653931 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1883926 | 0 | EPSS Ckt | N | 2023 | ABC
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | OCB | 1104/2 | 20231022 | 306 | 20231022 | 1506 | 2248694 | 720 | Distribution Circuit | 3rd Party | Vehicle | 364 | 47404 | 36.5092 | -121.4466 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0130983 | OH | Sus | 35506300 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1883946 | 0 | EPSS Ckt | N | 2023 | FORCE OUT
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 9645 | 20231022 | 809 | 20231022 | 855 | 2248791 | 46 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 138 | 36.9272 | -121.3798 | No | Overcast;32-90 F |  |  | 23-0131010 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1883979 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 67520 | 20231022 | 1158 | 20231023 | 48 | 2248897 | 770 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2735 | 250231 | 36.9577 | -121.8525 | No | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Burned/flashed | 23-0131028 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1883999 | 0 | EPSS Ckt | Y | 2023 | B/GRD
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 974520 | 20231022 | 1226 | 20231023 | 428 | 2248924 | 899 | Distribution Circuit | Vegetation | Tree - fell into line | 330 | 17385 | 36.9908 | -121.8063 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 23-0131031 | OH | Sus | 46028247 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1884001 | 0 | EPSS Ckt | Y | 2023 | B/GRD
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | RECLOSER | 83518 | 20231022 | 1600 | 20231023 | 247 | 2249062 | 647 | Distribution Circuit | 3rd Party | Vehicle | 304 | 106660 | 36.8183 | -121.3881 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0131061 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Multi-Fault | 0 | No | Yes | No | 1884028 | 0 | EPSS Ckt | N | 2023 | ABC GRD
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 5090 | 20231022 | 1813 | 20231022 | 2030 | 2249112 | 137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 435 | 36449 | 36.9804 | -121.892 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 23-0131070 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1884039 | 0 | EPSS Ckt | Y | 2023 | A PHASE AND GRD
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 12235 | 20231022 | 1921 | 20231023 | 214 | 2249228 | 413 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 1652 | 36.9243 | -121.8127 | No | Overcast;32-90 F |  |  | 23-0131131 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1884091 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 2287 | 20231022 | 2048 | 20231022 | 2156 | 2249269 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 1360 | 36.9502 | -121.829 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 23-0131109 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1884070 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | RECLOSER | 432 | 20231023 | 314 | 20231023 | 1434 | 2249421 | 680 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 323 | 168642 | 36.398 | -121.6493 | No | Overcast;32-90 F |  |  | 23-0131132 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1884093 | 0 | EPSS Ckt | Y | 2023 | A & C
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | RECLOSER | 974130 | 20231023 | 711 | 20231023 | 836 | 2249488 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 91 | 7735 | 37.0448 | -121.9382 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0131161 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1884121 | 0 | EPSS Ckt | Y | 2023 | GRD INST
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | OTHER | 9093 | 20231023 | 859 | 20231023 | 2252 | 2249637 | 833 | Distribution Circuit | Animal | Bird found | 2 | 1665 | 36.1019 | -120.9803 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0131246 | OH | Sus | 31673871 | SOUTH BAY AND CENTRAL COAST | OCT | Open Circuit | 0 | No | Yes | Yes | 1884282 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | RECLOSER | 7002 | 20231023 | 1100 | 20231023 | 1241 | 2249843 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 138 | 13938 | 35.9663 | -121.1146 | No | Clear;32-90 F |  |  | 23-0131345 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1884328 | 0 | EPSS Ckt | Y | 2023 | AB
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | RECLOSER | 12990 | 20231023 | 1706 | 20231024 | 410 | 2250147 | 664 | Distribution Circuit | Vegetation | Tree - fell into line | 791 | 59216 | 37.039 | -122.0214 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0131554 | OH | Sus | 46029157 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1884379 | 0 | EPSS Ckt | Y | 2023 | A/GRD
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 40709 | 20231024 | 41 | 20231024 | 201 | 2250249 | 80 | Distribution Circuit | Equipment Failure/Involved | Overhead | 163 | 13040 | 36.5932 | -121.8935 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Arcing | 23-0131603 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1884412 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1106 | 182011106 | TRANSFORMER | 412197049629 | 20231024 | 805 | 20231024 | 959 | 2250398 | 114 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 1140 | 36.6666 | -121.6623 | No | Overcast;32-90 F | Fuse | Broken | 23-0131767 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1884618 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | HOLLISTER | PANOCHE-1103 | 253671103 | RECLOSER | 4010 | 20231024 | 814 | 20231024 | 1825 | 2250419 | 611 | Distribution Circuit | Equipment Failure/Involved | Overhead | 207 | 32006 | 36.5951 | -120.7911 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0131774 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1884622 | 0 | EPSS Ckt | N | 2023 | GRD
CENTRAL COAST | SALINAS | SALINAS-1105 | 182011105 | FUSE | 23011 | 20231024 | 1015 | 20231024 | 1104 | 2250667 | 49 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 98 | 36.687 | -121.6467 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0131807 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1884638 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1101 | 182201101 | TRANSFORMER | 412717646607 | 20231024 | 1136 | 20231024 | 2110 | 2250682 | 574 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 574 | 36.5881 | -121.4811 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0131831 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1884644 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | TRANSFORMER | 412151649937 | 20231024 | 1223 | 20231024 | 2332 | 2250775 | 669 | Transformer only | 3rd Party | Vehicle | 10 | 6690 | 36.6749 | -121.678 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0131859 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1884656 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | RECLOSER | 4002 | 20231024 | 1227 | 20231024 | 1236 | 2250771 | 9 | Distribution Circuit | Company Initiated | Coordination failure | 170 | 1530 | 36.8322 | -121.5312 | No | Clear;32-90 F | Recloser | Normal | 23-0131851 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1884654 | 0 | EPSS Ckt | Y | 2023 | DCD
CENTRAL COAST | SALINAS | SALINAS-1103 | 182011103 | TRANSFORMER | 412217051061 | 20231024 | 2053 | 20231025 | 2031 | 2250641 | 1418 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 22688 | 36.7062 | -121.6568 | No | Partly Cloudy;32-90 F | Transformer | Leaking | 23-0131771 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1884621 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | BUENA VISTA-1104 | 182261104 | FUSE | 23263 | 20231025 | 531 | 20231025 | 815 | 2251217 | 164 | Distribution Circuit | 3rd Party | Metallic Balloon | 5 | 820 | 36.6664 | -121.6139 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0132181 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1884788 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 9497 | 20231025 | 724 | 20231025 | 819 | 2251151 | 55 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 880 | 37.0296 | -122.0228 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0132178 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1884785 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | RECLOSER | 2026 | 20231025 | 948 | 20231025 | 1030 | 2251448 | 42 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1292 | 45290 | 36.5315 | -121.8375 | No | Partly Cloudy;32-90 F |  |  | 23-0132269 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1884920 | 0 | EPSS Ckt | Y | 2023 | AC
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 183 | 20231025 | 1054 | 20231026 | 320 | 2251535 | 986 | Distribution Circuit | Equipment Failure/Involved | Overhead | 55 | 20217 | 36.9293 | -121.8586 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0132419 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1884993 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 67520 | 20231025 | 1303 | 20231025 | 1316 | 2251439 | 8 | Distribution Circuit | Company Initiated | Personnel- company | 2680 | 27780 | 36.9577 | -121.8525 | No | Overcast;32-90 F | Transformer (OH) | Broken | 23-0132417 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1884990 | 0 | EPSS Ckt | Y | 2023 | B GRD
CENTRAL COAST | KING CITY | LOS COCHES-1102 | 182151102 | FUSE | 8891 | 20231025 | 1520 | 20231025 | 1603 | 2251766 | 43 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 57 | 36.375 | -121.2914 | No | Partly Cloudy;32-90 F | Fuse | Normal | 23-0132560 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1885029 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1112 | 182371112 | RECLOSER | 2142 | 20231026 | 220 | 20231026 | 632 | 2251988 | 252 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 751 | 97265 | 36.4806 | -121.7292 | No | Clear;32-90 F |  |  | 23-0132673 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1885084 | 0 | EPSS Ckt | Y | 2023 | A- C- & INST
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | RECLOSER | 975548 | 20231026 | 508 | 20231026 | 717 | 2252011 | 129 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2255 | 290895 | 36.6214 | -121.6846 | No | Clear;32-90 F |  |  | 23-0132675 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1885087 | 0 | EPSS Ckt | Y | 2023 | SGF & DCD
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | FUSE | 4245 | 20231026 | 750 | 20231026 | 1012 | 2252100 | 142 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 28 | 3976 | 36.8938 | -121.5972 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0132718 | OH | Sus | 31674088 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1885118 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | TRANSFORMER | 411965053028 | 20231026 | 815 | 20231026 | 1910 | 2252195 | 655 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1310 | 36.7589 | -121.7438 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 23-0132807 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1885303 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 9641 | 20231026 | 1236 | 20231026 | 1355 | 2252533 | 79 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 79 | 36.8761 | -121.7727 | No | Clear;32-90 F | Fuse | Broken | 23-0132927 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1885359 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | TRANSFORMER | 316272014025 | 20231026 | 1325 | 20231027 | 118 | 2252644 | 713 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 713 | 36.8781 | -121.7756 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0132948 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1885370 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | OTHER | WIRE DOWN 1 SPAN SS OF CGC 316086318167 | 20231026 | 2248 | 20231027 | 1211 | 2252889 | 803 | Distribution Circuit | Vegetation | Tree - bark fell into line | 500 | 69316 | 36.9915 | -121.8411 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0133052 | OH | Sus | 46032474 | SOUTH BAY AND CENTRAL COAST | OCT | Open Circuit | 0 | No | Yes | Yes | 1885433 | 1 | EPSS Ckt | Y | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 3347 | 20231027 | 1128 | 20231027 | 1330 | 2253320 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 4148 | 36.8707 | -121.6898 | No | Partly Cloudy;32-90 F |  |  | 23-0133299 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1885671 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | RECLOSER | 16010 | 20231027 | 1451 | 20231027 | 1620 | 2253510 | 89 | Distribution Circuit | Vegetation | Tree - branch fell on line | 265 | 23585 | 37.0886 | -122.0874 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0133361 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1885690 | 0 | EPSS Ckt | Y | 2023 | C GRD
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 597 | 20231027 | 1941 | 20231027 | 2100 | 2253692 | 79 | Distribution Circuit | Animal | Bird found | 6 | 474 | 36.9525 | -121.782 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0133436 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1885718 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 4135 | 20231028 | 157 | 20231028 | 1455 | 2253836 | 778 | Distribution Circuit | Vegetation | Tree - bark fell into line | 4 | 3112 | 36.7879 | -121.7197 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0133469 | OH | Sus | 46033119 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | Yes | No | 1885747 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | FUSE | 12261 | 20231028 | 1304 | 20231028 | 1356 | 2254266 | 52 | Distribution Circuit | Equipment Failure/Involved | Overhead | 69 | 3588 | 36.9611 | -121.9779 | No | Clear;32-90 F | Insulator | Arcing | 23-0133554 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1885860 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | RECLOSER | 5144 | 20231028 | 1410 | 20231028 | 1800 | 2254334 | 230 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 149 | 34270 | 37.0911 | -122.0774 | No | Clear;32-90 F |  |  | 23-0133567 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1885873 | 0 | EPSS Ckt | Y | 2023 | DCD SGF
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | RECLOSER | 2020 | 20231028 | 1547 | 20231029 | 1112 | 2254386 | 1165 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 838 | 976270 | 36.4632 | -121.7119 | No | Clear;32-90 F |  |  | 23-0133582 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1885882 | 0 | EPSS Ckt | Y | 2023 | GRD INST
CENTRAL COAST | HOLLISTER | SAN BENITO-2104 | 182742104 | RECLOSER | 785888 | 20231028 | 2227 | 20231029 | 1234 | 2254522 | 847 | Distribution Circuit | 3rd Party | Vehicle | 1293 | 150909 | 36.8765 | -121.5546 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0133637 | OH | Sus | 35508280 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1885919 | 0 | EPSS Ckt | Y | 2023 | B & C PHASE
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316351817568 | 20231029 | 44 | 20231029 | 58 | 2254552 | 14 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 14 | 36.9756 | -121.7499 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0133643 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1885927 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316351817568 | 20231029 | 1032 | 20231029 | 1055 | 2254785 | 23 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 23 | 36.9756 | -121.7499 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 23-0133677 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1885971 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | PANOCHE-1103 | 253671103 | RECLOSER | 107270 | 20231029 | 1422 | 20231029 | 2044 | 2254954 | 382 | Distribution Circuit | Equipment Failure/Involved | Overhead | 152 | 58064 | 36.6026 | -120.8391 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0133715 | OH | Sus | 46033694 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1886003 | 0 | EPSS Ckt | Y | 2023 | SGF & DCD
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | FUSE | 9791 | 20231029 | 1605 | 20231029 | 2107 | 2254998 | 302 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 5738 | 36.3162 | -121.2519 | No | Clear;32-90 F | Fuse | Broken | 23-0133749 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1886038 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 6477 | 20231029 | 1931 | 20231030 | 227 | 2255128 | 416 | Distribution Circuit | Equipment Failure/Involved | Overhead | 427 | 177632 | 36.8655 | -121.7346 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0133748 | OH | Sus | 31674442 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1886036 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | RECLOSER | 7002 | 20231029 | 2333 | 20231030 | 309 | 2255173 | 216 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 138 | 29808 | 35.9663 | -121.1146 | No | Clear;32-90 F |  |  | 23-0133772 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1886054 | 0 | EPSS Ckt | Y | 2023 | A & B PHASE INST
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412240752255 | 20231030 | 857 | 20231030 | 2009 | 2255361 | 672 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1344 | 36.7391 | -121.65 | No | Clear;32-90 F | Transformer | Deteriorated | 23-0133944 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1886242 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS COCHES-1102 | 182151102 | FUSE | 8891 | 20231030 | 1420 | 20231030 | 1635 | 2255943 | 135 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 180 | 36.375 | -121.2914 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0134104 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1886316 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | TRANSFORMER | 411756844408 | 20231030 | 1551 | 20231030 | 2110 | 2256019 | 319 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 638 | 36.5196 | -121.8071 | No | Partly Cloudy;32-90 F | Transformer | Arcing | 23-0134118 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1886322 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1105 | 182011105 | TRANSFORMER | 412311351032 | 20231030 | 1828 | 20231031 | 230 | 2256097 | 482 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 5302 | 36.706 | -121.6247 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0134156 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1886340 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | HOLLISTER | SAN BENITO-2104 | 182742104 | RECLOSER | 785888 | 20231031 | 438 | 20231101 | 1315 | 2256261 | 1957 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 1293 | 283843 | 36.8765 | -121.5546 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0134199 | OH | Sus | 35508665 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1886372 | 0 | EPSS Ckt | Y | 2023 | A & GRD
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | FUSE | 72277 | 20231031 | 1014 | 20231031 | 1545 | 2256850 | 331 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 1324 | 36.6934 | -121.5699 | No | Partly Cloudy;32-90 F |  |  | 23-0134407 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1886642 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2103 | 182492103 | FUSE | 50489 | 20231031 | 1047 | 20231031 | 2240 | 2256663 | 713 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 1426 | 36.8509 | -121.4 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0134368 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1886633 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 5071 | 20231031 | 1108 | 20231031 | 1215 | 2256604 | 67 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 670 | 36.9718 | -121.7895 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0134286 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1886565 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1103 | 182201103 | TRANSFORMER | 412458048545 | 20231031 | 1129 | 20231031 | 1257 | 2256543 | 88 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 88 | 36.6383 | -121.57 | No | Clear;32-90 F |  |  | 23-0134318 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1886606 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | RECLOSER | 2010 | 20231031 | 1205 | 20231031 | 1422 | 2256687 | 137 | Distribution Circuit | Vegetation | Tree - branch fell on line | 122 | 16714 | 36.5058 | -121.936 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0134307 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1886587 | 0 | EPSS Ckt | N | 2023 | B- C
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | FUSE | 23161 | 20231031 | 1552 | 20231031 | 1625 | 2256849 | 33 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 88 | 36.4984 | -121.5015 | No | Partly Cloudy;32-90 F |  |  | 23-0134420 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1886649 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | RECLOSER | 7062 | 20231101 | 721 | 20231101 | 915 | 2257043 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 50 | 5700 | 36.2789 | -121.3033 | No | Clear;32-90 F |  |  | 23-0134520 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1886703 | 0 | EPSS Ckt | Y | 2023 | A&B
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316493516075 | 20231101 | 1535 | 20231101 | 1641 | 2257721 | 66 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 66 | 36.935 | -121.7009 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0134837 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1886957 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6433 | 20231101 | 1625 | 20231101 | 1645 | 2257742 | 20 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3 | 60 | 36.9662 | -121.7316 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0134885 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1886962 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | RECLOSER | 4002 | 20231101 | 1832 | 20231102 | 949 | 2257835 | 917 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 170 | 91499 | 36.8322 | -121.5312 | No | Clear;32-90 F |  |  | 23-0134915 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1886968 | 0 | EPSS Ckt | Y | 2023 | SGF/DCD
CENTRAL COAST | SALINAS | SALINAS-1101 | 182011101 | TRANSFORMER | 412230049958 | 20231101 | 2334 | 20231102 | 227 | 2257891 | 173 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 1730 | 36.6761 | -121.6513 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0134922 | OH | Sus | 31674997 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1887002 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | SWITCH | 2600 | 20231102 | 556 | 20231102 | 745 | 2257983 | 80 | Distribution Circuit | Company Initiated | Improper Construction | 161 | 4102 | 36.5858 | -121.8888 | No | Clear;32-90 F | Switch (UG) | Normal | 23-0113585 | UG | Sus | 35396128 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1887032 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | OTHER | 12897 | 20231102 | 847 | 20231102 | 2303 | 2258094 | 856 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1937 | 36.9723 | -121.7403 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0135088 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1887177 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRANSFORMER | 315253023525 | 20231102 | 852 | 20231102 | 1358 | 2258109 | 306 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1224 | 37.1353 | -122.1273 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0135104 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1887192 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | RECLOSER | 4002 | 20231102 | 1108 | 20231102 | 1344 | 2258345 | 156 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 148 | 23088 | 36.8322 | -121.5312 | No | Clear;32-90 F |  |  | 23-0135178 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1887227 | 0 | EPSS Ckt | Y | 2023 | SGF DCD
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 5061 | 20231102 | 1240 | 20231102 | 1415 | 2258425 | 95 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 127 | 36.7591 | -121.7642 | No | Clear;32-90 F | Fuse | Broken | 23-0135297 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1887275 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 9031 | 20231102 | 1730 | 20231102 | 2300 | 2258483 | 330 | Distribution Circuit | 3rd Party | Vehicle | 1 | 330 | 36.9401 | -121.4182 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0135354 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1887283 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | RECLOSER | 2002 | 20231103 | 713 | 20231103 | 1446 | 2258784 | 453 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 54360 | 36.2248 | -121.7587 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0135446 | OH | Sus | 46047359 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1887348 | 0 | EPSS Ckt | N | 2023 | A & GRD
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | TRANSFORMER | 316298516162 | 20231103 | 950 | 20231103 | 1104 | 2258995 | 74 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 592 | 36.9369 | -121.7676 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0135529 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1887499 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | RECLOSER | 77978 | 20231103 | 1352 | 20231103 | 1418 | 2259277 | 26 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 265 | 6890 | 36.4795 | -121.4142 | No | Clear;32-90 F |  |  | 23-0135684 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Three Phase Fault | 0 | No | No | No | 1887600 | 0 | EPSS Ckt | N | 2023 | ABC
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | TRANSFORMER | 411357747512 | 20231103 | 1530 | 20231104 | 542 | 2259276 | 852 | Transformer only | Equipment Failure/Involved | Electrical Overload | 9 | 7668 | 36.6018 | -121.9461 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0135729 | OH | Sus | 35509439 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1887613 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | TRANSFORMER | 411801450306 | 20231104 | 855 | 20231104 | 911 | 2259841 | 16 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 288 | 36.6822 | -121.798 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 23-0135870 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1887749 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SOLEDAD-2104 | 182052104 | RECLOSER | 7008 | 20231104 | 1012 | 20231104 | 1230 | 2259916 | 138 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 80 | 11040 | 36.4058 | -121.3538 | No | Partly Cloudy;32-90 F |  |  | 23-0135877 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1887762 | 0 | EPSS Ckt | Y | 2023 | A- B
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 51025 | 20231104 | 1059 | 20231104 | 1205 | 2259937 | 66 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 198 | 36.7522 | -121.2882 | No | Clear;32-90 F |  |  | 23-0135891 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1887774 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 95050 | 20231104 | 1211 | 20231104 | 1226 | 2259983 | 15 | Distribution Circuit | Company Initiated | Personnel- company | 37 | 555 | 37.0888 | -122.0877 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0135897 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1887780 | 0 | EPSS Ckt | Y | 2023 | A GRD
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | TRANSFORMER | T0200 | 20231104 | 1448 | 20231105 | 1017 | s1889339 | 1169 | Transformer only | Equipment Failure/Involved | Underground | 2 | 1274 | 36.8924 | -121.3969 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0116085 | UG | Sus | 35426356 | SOUTH BAY AND CENTRAL COAST | NOV | Open Circuit | 0 | No | No | No | 1889339 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | SWITCH | 10175 | 20231104 | 1548 | 20231104 | 1557 | 2260105 | 9 | Distribution Circuit | Company Initiated | Operating error | 433 | 3897 | 37.0439 | -122.1539 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0110244 | OH | Sus | 31611514 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1887803 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | JUMPER | OJ @ FUCO 44451 | 20231105 | 354 | 20231105 | 1622 | s1887902 | 748 | Distribution Circuit | 3rd Party | Vehicle | 2 | 1496 | 0 | 0 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0135979 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1887902 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | RECLOSER | 5144 | 20231105 | 1022 | 20231105 | 1315 | 2260450 | 173 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 149 | 25777 | 37.0911 | -122.0774 | No | Partly Cloudy;32-90 F |  |  | 23-0135999 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1887897 | 0 | EPSS Ckt | Y | 2023 | DCD SGF
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | TRANSFORMER | T1869 | 20231105 | 1315 | 20231106 | 421 | 2260467 | 906 | Distribution Circuit | Equipment Failure/Involved | Underground | 47 | 9219 | 36.6705 | -121.5452 | No | Overcast;32-90 F | Transformer (UG) | Failed/Faulted | 23-0136006 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1887908 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 9647 | 20231105 | 1418 | 20231105 | 1540 | 2260505 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 246 | 36.9275 | -121.3811 | No | Clear;32-90 F |  |  | 23-0136017 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1887915 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | RECLOSER | 741002 | 20231105 | 1810 | 20231105 | 1837 | 2260635 | 27 | Distribution Circuit | Company Initiated | Operating error | 305 | 8235 | 36.5971 | -121.6247 | No | Partly Cloudy;32-90 F | Recloser | Normal | 23-0136031 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1887928 | 0 | EPSS Ckt | N | 2023 | A/C I
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 10214 | 20231105 | 2305 | 20231106 | 103 | 2260806 | 118 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1971 | 135108 | 37.0909 | -122.0439 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0136078 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1887961 | 0 | EPSS Ckt | Y | 2023 | A/B
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | RECLOSER | 36982 | 20231105 | 2305 | 20231106 | 1528 | 2260775 | 983 | Distribution Circuit | 3rd Party | Vehicle | 171 | 25629 | 36.5301 | -121.4747 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 23-0136077 | OH | Sus | 35509783 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | Yes | No | 1887960 | 0 | EPSS Ckt | Y | 2023 | A/B INST
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 10718 | 20231106 | 10 | 20231106 | 249 | 2260892 | 159 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 927 | 140173 | 37.036 | -122.1068 | No | Overcast;32-90 F |  |  | 23-0136084 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1887965 | 0 | EPSS Ckt | N | 2023 | INST OC
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316412014575 | 20231106 | 50 | 20231106 | 538 | 2260922 | 288 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 576 | 36.8937 | -121.728 | No | Overcast-Fog-Rain;32-90 F | Fuse | Broken | 23-0136106 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1887985 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SOLEDAD-2105 | 182052105 | RECLOSER | 107872 | 20231106 | 321 | 20231106 | 1252 | 2260981 | 571 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 17223 | 36.4233 | -121.2905 | No | Overcast-Fog;32-90 F |  |  | 23-0136098 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1887977 | 0 | EPSS Ckt | Y | 2023 | B/C INST
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | FUSE | 9029 | 20231106 | 547 | 20231106 | 1430 | 2261013 | 523 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1538 | 36.9416 | -121.432 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 23-0136120 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1888007 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | RECLOSER | 586340 | 20231106 | 616 | 20231106 | 805 | 2261038 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 710 | 61550 | 36.5537 | -121.694 | No | Clear;32-90 F |  |  | 23-0136110 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1887990 | 0 | EPSS Ckt | Y | 2023 | B-C-
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 9325 | 20231106 | 714 | 20231106 | 933 | 2261081 | 139 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 278 | 36.5998 | -121.8977 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0136179 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1888126 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-1101 | 182221101 | TRANSFORMER | 411716148079 | 20231106 | 731 | 20231106 | 852 | 2261099 | 81 | Transformer only | Unknown Cause | Patrol - not conducted | 12 | 972 | 36.6199 | -121.8243 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0136166 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1888080 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | OCB | 2102/2 | 20231106 | 738 | 20231106 | 926 | 2261103 | 108 | Distribution Circuit | Equipment Failure/Involved | Overhead | 202 | 21816 | 36.2938 | -121.1999 | No | Partly Cloudy-Fog;32-90 F | Bushing | Burned/flashed | 23-0136130 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1888018 | 0 | EPSS Ckt | N | 2023 | SET A- MAINT TARGET- TIME OC
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | FUSE | 4327 | 20231106 | 740 | 20231106 | 1209 | 2261110 | 269 | Distribution Circuit | 3rd Party | Vehicle | 2 | 538 | 36.8414 | -121.4798 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken | 23-0136134 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1888022 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | RECLOSER | 113634 | 20231106 | 907 | 20231106 | 1048 | 2261250 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 90 | 4450 | 36.961 | -121.4309 | No | Overcast;32-90 F |  |  | 23-0136172 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1888101 | 0 | EPSS Ckt | Y | 2023 | B-C
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | OCB | 2102/2 | 20231106 | 927 | 20231106 | 1020 | 2261302 | 53 | Distribution Circuit | Equipment Failure/Involved | Overhead | 202 | 10706 | 36.2938 | -121.1999 | No | Partly Cloudy;32-90 F | Recloser | Burned/flashed | 23-0136130 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1888133 | 0 | EPSS Ckt | N | 2023 | SET A TRIP- TIME OC
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | FUSE | 7951 | 20231106 | 1023 | 20231106 | 1144 | 2261455 | 81 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 162 | 36.2756 | -121.1611 | No | Partly Cloudy;32-90 F | Lightning Arrestor | Failed/Faulted | 23-0136261 | OH | Sus | 31675436 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1888186 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | FUSE | 12265 | 20231106 | 1121 | 20231106 | 1739 | 2261539 | 378 | Distribution Circuit | Equipment Failure/Involved | Overhead | 72 | 15804 | 36.9588 | -121.9805 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0136370 | OH | Sus | 46049074 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1888239 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 12235 | 20231106 | 1411 | 20231107 | 235 | 2261787 | 744 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 2976 | 36.9243 | -121.8127 | No | Overcast;32-90 F | Transformer (OH) | Deteriorated | 23-0136433 | OH | Sus | 35510013 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1888256 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | FUSE | 4447 | 20231106 | 1605 | 20231106 | 1704 | 2261900 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 1770 | 36.7894 | -121.36 | No | Partly Cloudy;32-90 F |  |  | 23-0136448 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1888262 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1103 | 182011103 | OTHER | 1103/2 | 20231106 | 1802 | 20231106 | 2020 | 2262029 | 138 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6269 | 663621 | 36.6828 | -121.6513 | No | Overcast;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0136461 | OH | Sus | 46049078 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1888269 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | TRANSFORMER | 413559533274 | 20231106 | 1825 | 20231107 | 532 | 2262046 | 667 | Transformer only | Animal | Bird found | 2 | 1334 | 36.2271 | -121.1852 | No | Partly Cloudy;32-90 F | Transformer | Burned/flashed | 23-0136493 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1888305 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SOLEDAD-2101 | 182052101 | FUSE | 9843 | 20231107 | 610 | 20231107 | 2231 | 2262264 | 981 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 8820 | 36.4388 | -121.2917 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0136681 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1888539 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 10718 | 20231107 | 920 | 20231107 | 1537 | 2262520 | 377 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 927 | 349479 | 37.036 | -122.1068 | No | Clear;32-90 F |  |  | 23-0136626 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1888495 | 0 | EPSS Ckt | N | 2023 | GRD
CENTRAL COAST | COAST | POINT MORETTI SUB | 8293 | OCB | POINT MORETTI | 20231107 | 920 | 20231107 | 1322 | 2262686 | 242 | Distribution Circuit | Vegetation | Tree - branch fell on line | 380 | 90464 | 0 | 0 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0136638 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1888509 | 0 | Non-EPSS | N | 2023 | NA
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | SWITCH | 257600 | 20231107 | 921 | 20231108 | 300 | 2262577 | 1059 | Distribution Circuit | Equipment Failure/Involved | Underground | 2422 | 812895 | 37.0504 | -122.0246 | No | Clear;32-90 F | Elbow | Failed/Faulted | 23-0136628 | UG | Sus | 46049847 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1888498 | 0 | EPSS Ckt | Y | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | SWITCH | 95394 | 20231107 | 921 | 20231107 | 1441 | 2262679 | 320 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5864 | 1701971 | 37.0895 | -122.0928 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0136631 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1888502 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | RECLOSER | 77978 | 20231107 | 1054 | 20231107 | 1102 | 2262806 | 8 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 265 | 2120 | 36.4795 | -121.4142 | No | Clear;32-90 F |  |  | 23-0136688 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1888544 | 0 | EPSS Ckt | N | 2023 | B&C
CENTRAL COAST | SALINAS | INDUSTRIAL ACRES-0412 | 182300412 | TRANSFORMER | 412337750285 | 20231107 | 1156 | 20231107 | 1622 | 2262875 | 266 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 2128 | 36.6859 | -121.6148 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0136760 | OH | Sus | 31675664 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1888593 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0422 | 182440422 | TRANSFORMER | 411341547212 | 20231107 | 1212 | 20231107 | 1624 | 2262860 | 252 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 1512 | 36.5936 | -121.9511 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0136744 | OH | Sus | 31675473 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1888581 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SOLEDAD-2104 | 182052104 | TRANSFORMER | 413063341410 | 20231107 | 1237 | 20231108 | 229 | 2262920 | 832 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 832 | 36.4468 | -121.3597 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0136749 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1888587 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | TRANSFORMER | 315161720459 | 20231107 | 1329 | 20231107 | 1729 | 2262965 | 240 | Transformer only | Vegetation | Tree - branch fell on line | 7 | 1680 | 37.0501 | -122.1591 | No | Clear;32-90 F | Service conductor | Broken | 23-0136875 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1888647 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 5585 | 20231107 | 1629 | 20231107 | 1946 | 2263066 | 197 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 12214 | 37.0555 | -122.0609 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0136852 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1888632 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 11829 | 20231107 | 1934 | 20231107 | 2100 | 2263201 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 430 | 37.009 | -122.0756 | No | Clear;32-90 F |  |  | 23-0136889 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1888658 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SOLEDAD-2105 | 182052105 | RECLOSER | 107872 | 20231107 | 2239 | 20231107 | 2306 | 2263253 | 27 | Distribution Circuit | Company Initiated | Personnel- company | 33 | 891 | 36.4233 | -121.2905 | No | Fog;32-90 F | Fuse | Normal | 23-0136908 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1888682 | 0 | EPSS Ckt | Y | 2023 | B& C PHASE
CENTRAL COAST | HOLLISTER | HOLLISTER-2103 | 182492103 | FUSE | 50652 | 20231108 | 230 | 20231108 | 314 | 2263293 | 40 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 280 | 36.8562 | -121.3899 | No | Clear;32-90 F |  |  | 23-0136914 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Three Phase Fault | 0 | No | No | No | 1888690 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | RECLOSER | 3032 | 20231108 | 659 | 20231108 | 822 | 2263334 | 83 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 109 | 9047 | 36.634 | -121.6988 | No | Clear;32-90 F |  |  | 23-0136934 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1888704 | 0 | EPSS Ckt | N | 2023 | SGF
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412246054855 | 20231108 | 1037 | 20231109 | 203 | 2263803 | 926 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 6482 | 36.8107 | -121.65 | No | Clear;32-90 F | Transformer | Leaking | 23-0137045 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1888892 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412248154794 | 20231108 | 1055 | 20231108 | 2123 | 2263805 | 628 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1256 | 36.8095 | -121.6497 | No | Clear;32-90 F | Transformer | Deteriorated | 23-0137065 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1888904 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1108 | 182011108 | FUSE | 4197 | 20231108 | 1102 | 20231109 | 335 | 2263843 | 993 | Distribution Circuit | 3rd Party | Vandalism | 1 | 993 | 36.6807 | -121.6467 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0137072 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1888911 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1101 | 182201101 | JUMPER | OJS 3P N/O 24353 | 20231108 | 1132 | 20231108 | 1815 | 2263830 | 403 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 403 | 36.5971 | -121.4383 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0137060 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1888900 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | HOLLISTER | TRES PINOS-1111 | 183221111 | FUSE | 4441 | 20231108 | 1451 | 20231108 | 1715 | 2264409 | 144 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 432 | 36.8014 | -121.2715 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0137212 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1888986 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1103 | 182011103 | TRANSFORMER | T1711 | 20231108 | 1505 | 20231108 | 1629 | 2264126 | 84 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 168 | 36.6882 | -121.6659 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0137220 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1888991 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | RECLOSER | 37088 | 20231108 | 1744 | 20231109 | 406 | 2264559 | 622 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3037 | 520625 | 36.5465 | -121.8985 | No | Clear;32-90 F |  |  | 23-0137260 | OH | Sus | 46051313 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1889004 | 0 | EPSS Ckt | Y | 2023 | SGF-DCD
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | TRANSFORMER | 411504047740 | 20231109 | 28 | 20231109 | 120 | 2264661 | 52 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 52 | 36.6093 | -121.8967 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0137309 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1889051 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | RECLOSER | 370948 | 20231109 | 611 | 20231109 | 803 | 2264754 | 112 | Distribution Circuit | Vegetation | Tree - branch fell on line | 718 | 80416 | 36.5785 | -121.7263 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0137328 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1889072 | 0 | EPSS Ckt | Y | 2023 | AC
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | TRANSFORMER | 315944118006 | 20231109 | 922 | 20231109 | 1840 | 2264979 | 558 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 2232 | 36.986 | -121.8878 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0137545 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1889302 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | OTHER | J800 TWD T0976 | 20231109 | 1938 | 20231110 | 216 | 2265514 | 398 | Distribution Circuit | Equipment Failure/Involved | Underground | 31 | 12338 | 36.3268 | -121.2365 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0137607 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1889346 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 6515 | 20231109 | 2301 | 20231110 | 204 | 2265677 | 183 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 49 | 9019 | 36.8604 | -121.7075 | No | Clear;32-90 F |  |  | 23-0137694 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1889393 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 11913 | 20231109 | 2350 | 20231110 | 320 | 2265741 | 210 | Distribution Circuit | 3rd Party | Vehicle | 1 | 210 | 36.9403 | -121.7667 | No | Clear;32-90 F | Pole-Wood | Normal | 23-0137702 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1889401 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | RECLOSER | 7070 | 20231110 | 205 | 20231110 | 726 | 2265698 | 321 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 260 | 83130 | 35.9644 | -121.1175 | No | Clear;32-90 F |  |  | 23-0137697 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1889396 | 0 | EPSS Ckt | Y | 2023 | SGF
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 5304 | 20231110 | 630 | 20231110 | 1529 | 2265859 | 539 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1078 | 63938 | 36.9731 | -121.8204 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0137716 | OH | Sus | 31675936 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | Yes | No | 1889416 | 0 | EPSS Ckt | N | 2023 | AB
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | TRANSFORMER | 412554356078 | 20231110 | 835 | 20231110 | 853 | 2265946 | 18 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 36 | 36.8465 | -121.5461 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0137770 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1889455 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1102 | 182201102 | RECLOSER | 276712 | 20231110 | 1153 | 20231110 | 1202 | 2266133 | 9 | Distribution Circuit | Equipment Failure/Involved | Overhead | 197 | 1773 | 36.6279 | -121.5432 | No | Clear;32-90 F | Insulator | Broken | 23-0137882 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1889586 | 0 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | JUMPER | 841 | 20231110 | 1229 | 20231110 | 2200 | 2266346 | 571 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 2855 | 36.7594 | -121.7869 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0137956 | OH | Sus | 31676120 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | Yes | 1889625 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | TRANSFORMER | 414393024820 | 20231110 | 1543 | 20231110 | 1642 | 2266405 | 59 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 59 | 36 | -120.896 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0137976 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1889635 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411914053465 | 20231110 | 1551 | 20231110 | 2028 | 2266410 | 277 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1108 | 36.77 | -121.7622 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0137983 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1889637 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 10599 | 20231111 | 1437 | 20231111 | 1533 | 2266835 | 56 | Distribution Circuit | Animal | Bird found | 1 | 56 | 36.9386 | -121.7424 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0138118 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1889772 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | TRANSFORMER | 414226140431 | 20231111 | 1501 | 20231112 | 1119 | 2266824 | 1218 | Transformer only | Vegetation | Tree - fell into line | 1 | 1218 | 36.4274 | -120.9653 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0138132 | OH | Sus | 35511348 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1889784 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 8397 | 20231111 | 1731 | 20231112 | 1230 | 2266913 | 1139 | Distribution Circuit | 3rd Party | Vehicle | 10 | 11390 | 37.0795 | -122.1393 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0138157 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1889814 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | OCB | 2201/2 | 20231111 | 1802 | 20231111 | 2342 | 2266887 | 340 | Distribution Circuit | 3rd Party | Metallic Balloon | 1485 | 131349 | 36.5786 | -121.9085 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0138131 | OH | Sus | 31675891 | SOUTH BAY AND CENTRAL COAST | NOV | Three Phase Fault | 0 | No | Yes | No | 1889783 | 0 | EPSS Ckt | N | 2023 | ABC- SET A- TIME
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 9823 | 20231111 | 1905 | 20231112 | 110 | 2266904 | 365 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 41 | 14965 | 36.9781 | -121.8802 | No | Clear;32-90 F |  |  | 23-0138160 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1889819 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | RECLOSER | 3716 | 20231112 | 318 | 20231112 | 1217 | 2266974 | 539 | Distribution Circuit | 3rd Party | Vehicle | 448 | 106940 | 36.8245 | -121.6753 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0138164 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1889824 | 0 | EPSS Ckt | N | 2023 | FORCE OUT
CENTRAL COAST | COAST | PAUL SWEET-2108 | 83252108 | FUSE | 80061 | 20231112 | 518 | 20231112 | 714 | 2266989 | 116 | Distribution Circuit | Animal | Bird found | 17 | 1972 | 36.9867 | -121.9963 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0138173 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1889835 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | SAN BENITO-2104 | 182742104 | RECLOSER | 785888 | 20231112 | 629 | 20231112 | 814 | 2267012 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1292 | 132910 | 36.8765 | -121.5546 | No | Clear;32-90 F |  |  | 23-0138170 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1889832 | 0 | EPSS Ckt | Y | 2023 | A&C PHASE
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | FUSE | 4679 | 20231112 | 1346 | 20231112 | 1606 | 2267240 | 140 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 36 | 4560 | 36.8334 | -121.5213 | No | Clear;32-90 F |  |  | 23-0138214 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1889886 | 0 | EPSS Ckt | Y | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2102 | 182222102 | TRANSFORMER | 411614347340 | 20231112 | 1614 | 20231112 | 2336 | 2267280 | 442 | Transformer only | Equipment Failure/Involved | Electrical Overload | 27 | 11934 | 36.6001 | -121.8586 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0138226 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1889898 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | FUSE | 65633 | 20231112 | 1641 | 20231112 | 2050 | 2267297 | 249 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1743 | 36.0937 | -120.9635 | No | Partly Cloudy;32-90 F |  |  | 23-0138245 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1889915 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 36516 | 20231112 | 1719 | 20231112 | 2137 | 2267314 | 258 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 396 | 99368 | 37.0787 | -122.1336 | No | Overcast;32-90 F |  |  | 23-0138230 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1889902 | 0 | EPSS Ckt | Y | 2023 | A&B PHASE
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | RECLOSER | 2020 | 20231113 | 703 | 20231113 | 718 | 2267442 | 15 | Distribution Circuit | Company Initiated | Coordination failure | 839 | 12585 | 36.4632 | -121.7119 | No | Clear;32-90 F | Recloser | Normal | 23-0138286 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1889965 | 0 | EPSS Ckt | Y | 2023 | SGF
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | TRANSFORMER | 411355247558 | 20231113 | 810 | 20231113 | 1104 | 2267518 | 174 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 1218 | 36.6031 | -121.9471 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 23-0138411 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1890155 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | TRANSFORMER | 412307253278 | 20231113 | 1556 | 20231114 | 159 | 2267976 | 603 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 603 | 36.7657 | -121.6288 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0138548 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1890218 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | TRANSFORMER | 411382543477 | 20231113 | 1623 | 20231113 | 2224 | 2268098 | 361 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1444 | 36.4907 | -121.9323 | No | Partly Cloudy;32-90 F | Other | Failed/Faulted | 23-0138561 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1890224 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS COCHES-1102 | 182151102 | OTHER | 1 PH WIRE DWN @ CGC 413321038010 | 20231113 | 1757 | 20231114 | 411 | 2268171 | 614 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3575 | 2144313 | 36.3581 | -121.2724 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0138577 | OH | Sus | 35511728 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | Yes | 1890239 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | TRANSFORMER | 413288056056 | 20231114 | 818 | 20231114 | 837 | 2268681 | 19 | Transformer only | Animal | Bird found | 1 | 19 | 36.8505 | -121.296 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0138729 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1890359 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | RECLOSER | 7070 | 20231114 | 949 | 20231114 | 1246 | 2268942 | 177 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 260 | 46020 | 35.9644 | -121.1175 | No | Clear;32-90 F |  |  | 23-0138879 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1890502 | 0 | EPSS Ckt | Y | 2023 | AB
CENTRAL COAST | SALINAS | SALINAS-1101 | 182011101 | TRANSFORMER | 412232049502 | 20231114 | 1407 | 20231115 | 719 | 2269154 | 1032 | Transformer only | Vegetation | Tree - fell into line | 11 | 11352 | 36.6636 | -121.6499 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0138973 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1890527 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 95050 | 20231114 | 1437 | 20231114 | 1650 | 2269171 | 133 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2367 | 107802 | 37.0888 | -122.0877 | No | Partly Cloudy;32-90 F |  |  | 23-0138975 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Multi-Fault | 0 | No | No | No | 1890528 | 0 | EPSS Ckt | Y | 2023 | AB GRD
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5239 | 20231114 | 1440 | 20231115 | 205 | 2269174 | 685 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 28085 | 37.0682 | -122.0827 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0139055 | OH | Sus | 31676296 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1890546 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 101 | 20231114 | 2003 | 20231115 | 942 | 2269315 | 819 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 819 | 36.9066 | -121.758 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0139079 | UG | Sus | 31676366 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1890567 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | TRANSFORMER | 412307253278 | 20231115 | 739 | 20231115 | 1125 | 2269454 | 226 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 226 | 36.7657 | -121.6288 | No | Clear;32-90 F |  |  | 23-0139279 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1890784 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316557514875 | 20231115 | 914 | 20231115 | 1053 | 2269623 | 99 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 99 | 36.9024 | -121.6782 | No | Clear;32-90 F |  |  | 23-0139255 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1890769 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1106 | 182031106 | FUSE | 7103 | 20231115 | 1004 | 20231115 | 1033 | 2269741 | 26 | Distribution Circuit | 3rd Party | Vehicle | 13 | 338 | 36.3107 | -120.9185 | No | Overcast;32-90 F | Anchor or Guy | Broken | 23-0139260 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1890771 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 11313 | 20231115 | 1310 | 20231115 | 1821 | 2269810 | 311 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 622 | 37.0035 | -121.8847 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0139568 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1890875 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412219054609 | 20231115 | 1313 | 20231115 | 1812 | 2269953 | 299 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 1794 | 36.8038 | -121.6593 | No | Clear;32-90 F | Capacitor | Broken- wire on ground | 23-0139437 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1890842 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | TRANSFORMER | 413045155488 | 20231115 | 1317 | 20231115 | 1636 | 2269882 | 199 | Transformer only | Vegetation | Tree - branch fell on line | 6 | 1194 | 36.8337 | -121.3775 | No | Overcast;32-90 F | Transformer | Broken | 23-0139564 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1890874 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 11533 | 20231115 | 1331 | 20231115 | 1418 | 2269970 | 47 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 705 | 36.8749 | -121.6884 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0139426 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1890840 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1105 | 182011105 | FUSE | 25051 | 20231115 | 1349 | 20231115 | 2330 | 2269999 | 581 | Distribution Circuit | Equipment Failure/Involved | Overhead | 232 | 134792 | 36.7066 | -121.6399 | No | Overcast-Strong Winds;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0139467 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Three Phase Fault | 0 | No | Yes | No | 1890847 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | JUMPER | 4611 | 20231115 | 1408 | 20231115 | 1920 | 2270018 | 293 | Distribution Circuit | Equipment Failure/Involved | Overhead | 59 | 17287 | 36.7611 | -121.7388 | No | Clear;32-90 F | Jumper | Burned Open | 23-0139598 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Open Circuit | 0 | No | No | No | 1890887 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS COCHES-1101 | 182151101 | FUSE | 94893 | 20231115 | 1519 | 20231115 | 1943 | 2270148 | 264 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 264 | 36.3683 | -121.3243 | No | Overcast-Drizzle;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0139569 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1890876 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2103 | 83252103 | RECLOSER | 49370 | 20231115 | 1633 | 20231116 | 518 | 2270216 | 765 | Distribution Circuit | Vegetation | Tree - branch fell on line | 664 | 147104 | 36.9816 | -122.0251 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0139585 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1890883 | 0 | EPSS Ckt | N | 2023 | B-GRD
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 4459 | 20231115 | 1719 | 20231115 | 1940 | 2270277 | 141 | Distribution Circuit | Vegetation | Tree - bark fell into line | 8 | 1128 | 36.8107 | -121.6565 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0139651 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1890918 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9771 | 20231115 | 1724 | 20231115 | 1910 | 2270273 | 103 | Distribution Circuit | Vegetation | Tree - branch fell on line | 38 | 3914 | 37.1313 | -122.1209 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0139637 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1890910 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | JUMPER | OJ AT CGC 413092357425 | 20231115 | 1724 | 20231115 | 1924 | 2270304 | 120 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 1196 | 139226 | 36.8693 | -121.4001 | No | Overcast-Drizzle;32-90 F | Jumper | Burned Open | 23-0139606 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Open Circuit | 0 | No | No | No | 1890889 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | RECLOSER | 10986 | 20231115 | 1735 | 20231115 | 1932 | 2270354 | 117 | Distribution Circuit | Vegetation | Tree - bark fell into line | 512 | 47151 | 36.9615 | -122.0627 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0139610 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1890893 | 0 | EPSS Ckt | N | 2023 | A- C
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | OCB | 2106/2 | 20231115 | 1746 | 20231115 | 1753 | 2270375 | 7 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 5494 | 38458 | 37.0417 | -122.0255 | No | Overcast-Drizzle;32-90 F |  |  | 23-0139613 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1890895 | 0 | EPSS Ckt | N | 2023 | A-GRD
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 2061 | 20231115 | 1811 | 20231115 | 2154 | 2270405 | 223 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 71 | 15833 | 37.071 | -121.9642 | No | Clear;32-90 F |  |  | 23-0139643 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1890913 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | JUMPER | JMPRS 1 W/O CGC 315898717427 | 20231115 | 1925 | 20231115 | 2015 | 2270423 | 50 | Distribution Circuit | Equipment Failure/Involved | Overhead | 58 | 2900 | 36.9702 | -121.9039 | No | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken | 23-0139628 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1890904 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | FUSE | 9235 | 20231115 | 2134 | 20231116 | 2046 | 2270474 | 1392 | Distribution Circuit | Equipment Failure/Involved | Overhead | 44 | 21008 | 35.9072 | -121.0291 | No | Clear;32-90 F | Jumper | Burned/flashed | 23-0139735 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1890962 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 5587 | 20231115 | 2257 | 20231116 | 1402 | 2270499 | 905 | Distribution Circuit | Equipment Failure/Involved | Overhead | 82 | 16780 | 36.6785 | -121.7147 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0139714 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1890957 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1105 | 182031105 | SWITCH | 81553 | 20231116 | 9 | 20231116 | 38 | 2270509 | 29 | Distribution Circuit | Equipment Failure/Involved | Overhead | 568 | 16472 | 36.2186 | -121.1308 | No | Overcast-Fog-Drizzle;32-90 F | Switch (OH) | Arcing | 23-0139685 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1890955 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1103 | 182031103 | TRANSFORMER | 413661131593 | 20231116 | 111 | 20231116 | 649 | 2270539 | 338 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1352 | 36.1814 | -121.1489 | No | Overcast-Fog-Drizzle;32-90 F | Fuse | Failed/Faulted | 23-0139753 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1890978 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | RECLOSER | 826224 | 20231116 | 629 | 20231116 | 802 | 2270580 | 93 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 358 | 33294 | 36.7924 | -121.663 | No | Overcast-Fog;32-90 F |  |  | 23-0139746 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1890973 | 0 | EPSS Ckt | Y | 2023 | A-B
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | JUMPER | FB @ MESA DR & CLEARVIEW DR | 20231116 | 1216 | 20231116 | 2149 | 2270871 | 550 | Distribution Circuit | Equipment Failure/Involved | Overhead | 274 | 109500 | 36.8327 | -121.3775 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0139921 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1891072 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 6957 | 20231116 | 1342 | 20231116 | 1425 | s1891095 | 43 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 1247 | 36.5963 | -121.8513 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0140069 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1891095 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 8949 | 20231116 | 1824 | 20231116 | 1920 | s1891117 | 56 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 616 | 36.5007 | -121.9336 | No | Clear;32-90 F |  |  | 23-0140196 |  | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1891117 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | PANOCHE-1103 | 253671103 | RECLOSER | 4010 | 20231117 | 1213 | 20231117 | 1238 | 2271587 | 25 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 184 | 3921 | 36.5951 | -120.7911 | No | Overcast-Drizzle;32-90 F |  |  | 23-0140473 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1891352 | 0 | EPSS Ckt | N | 2023 | AB
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | TRANSFORMER | 100000056222 | 20231117 | 1216 | 20231117 | 1657 | 2271500 | 281 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 562 | 36.5515 | -121.6762 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0140479 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891355 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316664513120 | 20231117 | 1307 | 20231117 | 1357 | 2271614 | 50 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 50 | 36.8548 | -121.641 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 23-0140511 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1891363 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | OTHER | 11549 | 20231117 | 1319 | 20231117 | 2102 | 2271627 | 463 | Distribution Circuit | 3rd Party | Vehicle | 3 | 1389 | 36.8641 | -121.7123 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0140569 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Open Circuit | 0 | No | Yes | Yes | 1891381 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | FUSE | 11199 | 20231117 | 1351 | 20231117 | 1651 | 2271625 | 180 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 360 | 36.9668 | -121.9858 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0140520 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1891367 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316351317021 | 20231117 | 1517 | 20231117 | 1740 | 2271725 | 143 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 143 | 36.9606 | -121.7498 | No | Overcast-Rain;32-90 F | Fuse | Failed/Faulted | 23-0140688 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891417 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1106 | 182031106 | OCB | 1106/2 | 20231117 | 1602 | 20231117 | 2327 | 2271769 | 445 | Distribution Circuit | Equipment Failure/Involved | Overhead | 339 | 17883 | 36.217 | -121.1269 | No | Overcast-Drizzle;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0140643 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1891397 | 0 | EPSS Ckt | N | 2023 | PHASE OC-GRD
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 393582 | 20231117 | 1644 | 20231118 | 29 | 2271820 | 465 | Distribution Circuit | Vegetation | Tree - fell into line | 636 | 79360 | 37.1284 | -122.1222 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0140667 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1891406 | 1 | EPSS Ckt | N | 2023 | C-GRD
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 40389 | 20231118 | 508 | 20231118 | 1730 | 2272030 | 742 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 7872 | 36.6079 | -121.9235 | No | Overcast-Heavy Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0140782 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Three Phase Fault | 0 | No | No | No | 1891492 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 3089 | 20231118 | 619 | 20231118 | 2353 | 2272056 | 1054 | Distribution Circuit | Equipment Failure/Involved | Underground | 49 | 31430 | 36.9635 | -122.0244 | No | Overcast-Fog-Rain;32-90 F | Transformer (UG) | Failed/Faulted | 23-0140802 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891517 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2101 | 182492101 | FUSE | 9951 | 20231118 | 712 | 20231118 | 725 | 2272076 | 13 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 325 | 36.8361 | -121.4191 | No | Overcast-Drizzle;32-90 F |  |  | 23-0140771 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891482 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 2885 | 20231118 | 732 | 20231118 | 752 | 2272091 | 20 | Distribution Circuit | Vegetation | Tree - branch fell on line | 79 | 1580 | 36.5423 | -121.93 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 23-0140773 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1891483 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 3301 | 20231118 | 756 | 20231118 | 2020 | 2272252 | 744 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 2876 | 36.9712 | -121.7758 | No | Overcast-Fog-Heavy Rain;32-90 F | Insulator | Broken | 23-0140784 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891495 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | TRANSFORMER | 411401245355 | 20231118 | 1111 | 20231118 | 1358 | 2272470 | 167 | Transformer only | Vegetation | Tree - branch fell on line | 7 | 1169 | 36.5425 | -121.9291 | No | Overcast;32-90 F | Transformer | Failed/Faulted | 23-0140865 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891568 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | OTHER | WIRE DOWN AT R28 | 20231118 | 1141 | 20231118 | 2045 | 2272519 | 544 | Distribution Circuit | 3rd Party | Vehicle | 3422 | 961987 | 36.7278 | -121.6433 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0140864 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | Yes | 1891569 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | TRANSFORMER | T2563 | 20231118 | 1222 | 20231118 | 2153 | 2272599 | 571 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 571 | 36.6925 | -121.8019 | No | Overcast-Drizzle;32-90 F | Transformer (UG) | Failed/Faulted | 23-0140904 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891592 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1101 | 182011101 | RECLOSER | 22052 | 20231118 | 1232 | 20231118 | 1315 | 2272592 | 43 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 1017 | 43731 | 36.6807 | -121.6511 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0140879 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891577 | 0 | Non-EPSS | N | 2023 | C GRD
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 7241 | 20231118 | 1320 | 20231118 | 1359 | 2272664 | 39 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 35 | 1365 | 36.619 | -121.9338 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0140905 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891593 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 6421 | 20231118 | 1725 | 20231119 | 825 | 2272985 | 900 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4500 | 36.9634 | -122.0252 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0140965 | OH | Sus | 31676708 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1891635 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | FUSE | 7443 | 20231118 | 1801 | 20231118 | 1900 | 2273035 | 59 | Distribution Circuit | Animal | Bird found | 5 | 275 | 36.0294 | -120.9113 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0140971 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891641 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 5215 | 20231118 | 2202 | 20231119 | 1157 | 2273341 | 833 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 49980 | 37.0325 | -122.0765 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0141029 | OH | Sus | 46061761 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | Yes | No | 1891700 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | FUSE | 2467 | 20231118 | 2207 | 20231119 | 1806 | 2273343 | 1199 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 33572 | 36.3936 | -121.6141 | No | Clear;32-90 F |  |  | 23-0141044 | OH | Sus | 46061751 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1891713 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 412090751185 | 20231118 | 2259 | 20231119 | 1300 | 2273367 | 841 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 2523 | 36.7094 | -121.7002 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0141043 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891712 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 3277 | 20231119 | 30 | 20231119 | 924 | 2273382 | 534 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 10680 | 36.6751 | -121.7023 | No | Clear;32-90 F | Other | Broken | 23-0141051 | OH | Sus | 46061752 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1891721 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | JUMPER | 1 SPAN WIRE DOWN LS OF 315976019180 | 20231119 | 208 | 20231119 | 1548 | 2273403 | 820 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 8678 | 37.0186 | -121.879 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0141065 | OH | Sus | 46061782 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | Yes | 1891739 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | TRANSFORMER | 315653217302 | 20231119 | 726 | 20231119 | 957 | 2273467 | 151 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 453 | 36.9654 | -121.9879 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0141082 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891755 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 9827 | 20231119 | 2020 | 20231120 | 1536 | 2273719 | 1156 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 39304 | 37.0797 | -122.1385 | No | Clear;32-90 F |  |  | 23-0141165 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1891825 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | OTHER | WIRE DOWN 2 LD SIDE OF 391980 | 20231120 | 2 | 20231121 | 1742 | 2274704 | 2500 | Distribution Circuit | 3rd Party | Vehicle | 49 | 121045 | 37.1482 | -122.0877 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0141626 | OH | Sus | 31676817 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | Yes | 1892049 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 6283 | 20231120 | 225 | 20231120 | 1405 | 2273849 | 700 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 5600 | 37.0683 | -121.9858 | No | Clear;32-90 F |  |  | 23-0141277 | OH | Sus | 31676789 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891946 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6851 | 20231120 | 317 | 20231120 | 1010 | 2273866 | 413 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 6608 | 37.0421 | -121.8171 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0141288 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891951 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 6343 | 20231120 | 706 | 20231120 | 1550 | 2273946 | 524 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 9432 | 37.2222 | -122.1451 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0141513 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1892003 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | TRANSFORMER | 412261951874 | 20231120 | 1248 | 20231120 | 2255 | 2274354 | 607 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 3642 | 36.729 | -121.6422 | No | Clear;32-90 F | Transformer | Burned/flashed | 23-0141409 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891975 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | LAURELES-1112 | 182371112 | TRANSFORMER | 411963545108 | 20231120 | 1358 | 20231121 | 502 | 2274417 | 904 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 4520 | 36.5408 | -121.7362 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0141555 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1892017 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 6343 | 20231120 | 1559 | 20231121 | 17 | 2274515 | 496 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 8928 | 37.2222 | -122.1451 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0141627 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1892050 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2103 | 83252103 | JUMPER | WIRE DOWN 1 SOURCE SIDE OF 11973 TWD 11973 | 20231120 | 1606 | 20231120 | 2147 | 2274518 | 341 | Distribution Circuit | Animal | Bird found | 20 | 6820 | 36.9841 | -121.9895 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0141552 | OH | Sus | 31676776 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | Yes | No | 1892015 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | JUMPER | JPRS LD SIDE OF CGC 412168754632 | 20231120 | 2304 | 20231121 | 424 | 2274693 | 320 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1600 | 36.8043 | -121.6762 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0141622 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1892045 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 412052454952 | 20231121 | 637 | 20231121 | 1228 | 2274741 | 351 | Transformer only | Vegetation | Tree - branch fell on line | 3 | 1053 | 36.8129 | -121.7166 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0141855 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1892189 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | RECLOSER | 4048 | 20231121 | 809 | 20231121 | 939 | 2274798 | 90 | Distribution Circuit | Vegetation | Tree - branch fell on line | 126 | 6348 | 36.719 | -121.2811 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0141690 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1892086 | 0 | EPSS Ckt | Y | 2023 | A GRD INST 50
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6541 | 20231121 | 921 | 20231121 | 1544 | 2274938 | 383 | Distribution Circuit | 3rd Party | Customer Equipment | 3 | 1149 | 36.9117 | -121.8303 | No | Partly Cloudy;32-90 F | Customer Equipment | Normal | 23-0141724 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1892138 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | SWITCH | 10513 | 20231122 | 20 | 20231122 | 404 | 2275430 | 224 | Distribution Circuit | Equipment Failure/Involved | Underground | 154 | 10440 | 36.5402 | -121.871 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0142007 | UG | Sus | 35513216 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1892280 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 3301 | 20231122 | 828 | 20231122 | 1210 | 2275517 | 222 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 5 | 1110 | 36.9712 | -121.7758 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0142169 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1892304 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | JUMPER | OJ @ CGC 316234515960 | 20231122 | 953 | 20231122 | 1740 | 2275609 | 467 | Distribution Circuit | 3rd Party | Vehicle | 2 | 925 | 36.9311 | -121.7892 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0142252 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1892338 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 9653 | 20231122 | 1057 | 20231122 | 1115 | 2275691 | 18 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 18 | 36.8644 | -121.7708 | No | Partly Cloudy;32-90 F |  |  | 23-0142310 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1892355 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | JUMPER | BURNT OJ 1 POLE S/OF 50905 | 20231122 | 1501 | 20231122 | 1818 | 2275838 | 197 | Distribution Circuit | Equipment Failure/Involved | Overhead | 227 | 42517 | 36.8686 | -121.5543 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 23-0142419 | OH | Sus | 46064331 | SOUTH BAY AND CENTRAL COAST | NOV | Open Circuit | 0 | No | No | No | 1892382 | 0 | EPSS Ckt | Y | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 2809 | 20231122 | 1644 | 20231122 | 1821 | 2275905 | 97 | Distribution Circuit | Animal | Bird found | 38 | 3686 | 36.5196 | -121.8082 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0142454 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1892398 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 11054 | 20231122 | 1720 | 20231123 | 1225 | 2275924 | 1050 | Distribution Circuit | Vegetation | Tree - fell into line | 309 | 107893 | 36.9775 | -121.7415 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 23-0142445 | OH | Sus | 46064559 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1892393 | 0 | EPSS Ckt | Y | 2023 | C & GRD INST
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 12775 | 20231122 | 2133 | 20231123 | 1242 | 2275992 | 559 | Distribution Circuit | Equipment Failure/Involved | Overhead | 110 | 80192 | 36.9691 | -121.9048 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0142486 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1892425 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 12247 | 20231123 | 207 | 20231124 | 1249 | 2276024 | 1517 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 2682 | 36.8995 | -121.7479 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0142513 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1892451 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 6165 | 20231123 | 923 | 20231123 | 1029 | 2276077 | 66 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 660 | 36.528 | -121.8179 | No | Overcast;32-90 F |  |  | 23-0142506 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1892445 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 35874 | 20231123 | 1128 | 20231123 | 1955 | 2276116 | 502 | Distribution Circuit | Equipment Failure/Involved | Overhead | 815 | 149969 | 37.0312 | -122.1882 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0142516 | OH | Sus | 46064884 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | Yes | No | 1892453 | 0 | EPSS Ckt | N | 2023 | B&C PHASE TIME
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | FUSE | 512621 | 20231123 | 2005 | 20231123 | 2149 | 2276254 | 104 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 61 | 6344 | 36.8416 | -121.4567 | No | Clear;32-90 F |  |  | 23-0142553 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1892485 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 40457 | 20231124 | 735 | 20231124 | 928 | 2276401 | 113 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 3503 | 36.5513 | -121.9086 | No | Clear;32-90 F |  |  | 23-0142618 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1892549 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | JUMPER | OJ 3 POLES S/W OF CGC 315722021902 | 20231124 | 844 | 20231124 | 920 | 2276422 | 36 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 108 | 37.0924 | -121.9699 | No | Clear;32-90 F | Conductor- Overhead | Annealed | 23-0142605 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1892537 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | RECLOSER | 975548 | 20231124 | 1017 | 20231124 | 1322 | 2276523 | 185 | Distribution Circuit | Equipment Failure/Involved | Underground | 2256 | 171705 | 36.6214 | -121.6846 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0142624 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1892551 | 0 | EPSS Ckt | Y | 2023 | SGF- DCD
CENTRAL COAST | HOLLISTER | TRES PINOS-1111 | 183221111 | FUSE | 50791 | 20231124 | 1053 | 20231124 | 1320 | 2276580 | 147 | Distribution Circuit | Animal | Other | 2 | 294 | 36.8047 | -121.3668 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0142655 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1892571 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | TRANSFORMER | 413417236871 | 20231124 | 1226 | 20231124 | 1237 | 2276566 | 11 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 110 | 36.325 | -121.2359 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0142648 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1892564 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | FUSE | 5721 | 20231124 | 1354 | 20231125 | 1436 | 2276642 | 1352 | Distribution Circuit | Equipment Failure/Involved | Underground | 91 | 16863 | 36.5674 | -121.7023 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0142668 | UG | Sus | 35513556 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1892580 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | RECLOSER | 1132 | 20231124 | 1524 | 20231125 | 1107 | 2276666 | 1183 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 163 | 126766 | 36.3584 | -121.2034 | No | Clear;32-90 F |  |  | 23-0142673 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1892584 | 0 | Non-EPSS | Y | 2023 | B & C PHASE
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 1721 | 20231125 | 430 | 20231125 | 1437 | 2276803 | 607 | Distribution Circuit | Equipment Failure/Involved | Underground | 39 | 12914 | 37.056 | -121.9972 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0142737 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1892642 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | FUSE | 4679 | 20231125 | 630 | 20231125 | 854 | 2276850 | 144 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 36 | 5184 | 36.8334 | -121.5213 | No | Clear;32-90 F |  |  | 23-0142740 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1892646 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | FUSE | 24972 | 20231125 | 847 | 20231125 | 1207 | 2276914 | 200 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 47 | 9400 | 36.6772 | -121.673 | No | Clear;32-90 F |  |  | 23-0142777 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1892671 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | FUSE | 4679 | 20231125 | 857 | 20231125 | 920 | 2276925 | 23 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 12 | 276 | 36.8334 | -121.5213 | No | Clear;32-90 F |  |  | 23-0142749 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1892653 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 8643 | 20231125 | 1150 | 20231125 | 1527 | 2277012 | 217 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 45 | 9765 | 37.01 | -121.8859 | No | Clear;32-90 F |  |  | 23-0142787 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1892674 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | TRANSFORMER | 412358652314 | 20231125 | 1457 | 20231125 | 1805 | 2277068 | 188 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 188 | 36.7415 | -121.6095 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0142807 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1892678 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | RECLOSER | 22158 | 20231125 | 1513 | 20231125 | 1614 | 2277072 | 61 | Distribution Circuit | Vegetation | Tree - bark fell into line | 466 | 28426 | 36.7999 | -121.6992 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0142812 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1892683 | 0 | EPSS Ckt | Y | 2023 | A & C PHASE
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 7105 | 20231126 | 709 | 20231126 | 922 | 2277299 | 133 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 5187 | 36.6101 | -121.9165 | No | Partly Cloudy;32-90 F |  |  | 23-0142898 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1892742 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 6895 | 20231126 | 816 | 20231126 | 1105 | 2277315 | 169 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 113 | 36.8382 | -121.7668 | No | Clear;32-90 F |  |  | 23-0142905 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1892748 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1105 | 182011105 | FUSE | 64039 | 20231126 | 1136 | 20231126 | 1305 | 2277409 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 3471 | 36.7056 | -121.6372 | No | Partly Cloudy;32-90 F |  |  | 23-0142929 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1892761 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | HOLLISTER | TRES PINOS-1111 | 183221111 | FUSE | 4441 | 20231126 | 1240 | 20231126 | 1715 | 2277430 | 275 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 825 | 36.8014 | -121.2715 | No | Clear;32-90 F | Insulator | Broken | 23-0142931 | OH | Sus | 31677260 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1892762 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 6137 | 20231126 | 1438 | 20231126 | 1513 | 2277461 | 35 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 40 | 1399 | 36.5945 | -121.8932 | No | Partly Cloudy;32-90 F |  |  | 23-0142935 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1892765 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | FUSE | 885 | 20231126 | 1726 | 20231126 | 2004 | 2277528 | 158 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 335 | 50257 | 36.9639 | -121.9916 | No | Overcast;32-90 F |  |  | 23-0142954 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1892784 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | DEL MONTE-2104 | 182222104 | FUSE | 20461 | 20231126 | 1913 | 20231126 | 1955 | 2277552 | 42 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 11 | 462 | 36.5384 | -121.7252 | No | Clear;32-90 F |  |  | 23-0142955 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1892785 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 8643 | 20231127 | 1 | 20231127 | 221 | 2277584 | 140 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 2098 | 37.01 | -121.8859 | No | Partly Cloudy;32-90 F |  |  | 23-0142975 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1892805 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 52559 | 20231127 | 641 | 20231127 | 835 | 2277655 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 1140 | 36.8343 | -121.6603 | No | Clear;32-90 F |  |  | 23-0143020 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1892867 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | PANOCHE-1103 | 253671103 | RECLOSER | 4010 | 20231127 | 811 | 20231127 | 1504 | 2277728 | 413 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 152 | 51193 | 36.5951 | -120.7911 | No | Partly Cloudy;32-90 F |  |  | 23-0143008 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1892849 | 0 | EPSS Ckt | N | 2023 | A- B
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | TRANSFORMER | T1679 | 20231127 | 900 | 20231127 | 1737 | 2277810 | 517 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1551 | 36.5932 | -121.8514 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0143079 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1893004 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | CASTROVILLE-2103 | 182352103 | OTHER | HOT WIRE DOWN 1 E/OF 9097 | 20231127 | 934 | 20231127 | 1124 | s1893002 | 110 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 522 | 53794 | 36.6979 | -121.798 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0143059 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Open Circuit | 0 | No | Yes | Yes | 1893002 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 316380117429 | 20231127 | 951 | 20231127 | 1833 | 2277944 | 522 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 5 | 1626 | 36.9724 | -121.7401 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0143167 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1893054 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SOLEDAD-2105 | 182052105 | FUSE | 768837 | 20231127 | 958 | 20231127 | 1115 | 2277957 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 51 | 36.4156 | -121.2963 | No | Partly Cloudy;32-90 F |  |  | 23-0143110 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1893015 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | CASTROVILLE-2103 | 182352103 | FUSE | 8413 | 20231127 | 1207 | 20231127 | 1622 | 2278167 | 255 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 89 | 22695 | 36.6992 | -121.8026 | No | Partly Cloudy;32-90 F |  |  | 23-0143247 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1893074 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | BORONDA-1102 | 182461102 | TRANSFORMER | 412148050200 | 20231127 | 1218 | 20231127 | 1719 | 2278081 | 301 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 301 | 36.6818 | -121.6793 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0143145 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1893038 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | BORONDA-1101 | 182461101 | FUSE | 4743 | 20231127 | 1316 | 20231127 | 1328 | 2278236 | 12 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 36 | 36.6937 | -121.6756 | No | Partly Cloudy;32-90 F |  |  | 23-0143175 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1893057 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | CASTROVILLE-2103 | 182352103 | FUSE | 9615 | 20231127 | 1452 | 20231127 | 1910 | 2278291 | 258 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1290 | 36.6921 | -121.7999 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0143262 | OH | Sus | 46069498 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1893079 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | JUMPER | OJ 2 S/OF C923 | 20231127 | 1651 | 20231127 | 1910 | 2278375 | 139 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2402 | 326321 | 36.7256 | -121.7876 | No | Clear;32-90 F | Jumper | Burned Open | 23-0143263 | OH | Sus | 46069643 | SOUTH BAY AND CENTRAL COAST | NOV | Open Circuit | 0 | No | No | No | 1893080 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | SOLEDAD-2104 | 182052104 | FUSE | 2061 | 20231127 | 1653 | 20231127 | 1839 | 2278368 | 106 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1272 | 36.4056 | -121.3498 | No | Partly Cloudy;32-90 F |  |  | 23-0143275 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1893090 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 11054 | 20231127 | 2021 | 20231128 | 418 | 2278465 | 477 | Distribution Circuit | 3rd Party | Vehicle | 309 | 147393 | 36.9775 | -121.7415 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0143279 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1893094 | 0 | EPSS Ckt | Y | 2023 | B 50 INST
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 11525 | 20231128 | 636 | 20231128 | 1105 | 2278947 | 269 | Distribution Circuit | Animal | Bird found | 3 | 807 | 36.885 | -121.7271 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0143446 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1893344 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 4915 | 20231128 | 1117 | 20231128 | 1127 | 2278843 | 10 | Distribution Circuit | Vegetation | Tree - branch fell on line | 35 | 350 | 37.1032 | -122.0458 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0143439 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1893341 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | SWITCH | 2257 | 20231128 | 1335 | 20231128 | 1345 | 2279052 | 10 | Distribution Circuit | Company Initiated | Return Circuit Normal | 13 | 130 | 37.0233 | -122.031 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0129613 | OH | Sus | 46000788 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1893371 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | TRES PINOS-1111 | 183221111 | RECLOSER | 4032 | 20231128 | 1511 | 20231128 | 1611 | 2279122 | 60 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 170 | 10200 | 36.7834 | -121.3204 | No | Clear;32-90 F |  |  | 23-0143566 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1893387 | 0 | EPSS Ckt | N | 2023 | B GRD
CENTRAL COAST | KING CITY | KING CITY-1106 | 182031106 | OCB | 1106/2 | 20231128 | 1550 | 20231129 | 9 | 2279153 | 499 | Distribution Circuit | Equipment Failure/Involved | Overhead | 339 | 56714 | 36.217 | -121.1269 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0143585 | OH | Sus | 31677173 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1893389 | 0 | EPSS Ckt | N | 2023 | B GRD OC
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | RECLOSER | 198478 | 20231129 | 356 | 20231129 | 1143 | 2279355 | 467 | Distribution Circuit | Equipment Failure/Involved | Overhead | 238 | 111146 | 36.3913 | -121.6195 | No | Partly Cloudy;32-90 F | Transformer (OH) | Burned/flashed | 23-0143671 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Three Phase Fault | 0 | No | No | No | 1893467 | 0 | EPSS Ckt | Y | 2023 | A-B-C
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | OTHER | WIRE DOWN LD SIDE OF CGC 100000021176 | 20231129 | 723 | 20231129 | 1415 | 2279788 | 410 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1660 | 36.6313 | -121.7047 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0143762 | OH | Sus | 46072079 | SOUTH BAY AND CENTRAL COAST | NOV | Open Circuit | 0 | No | Yes | Yes | 1893648 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | BUENA VISTA-1106 | 182261106 | TRANSFORMER | 412418947652 | 20231129 | 850 | 20231129 | 1528 | 2279672 | 398 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 398 | 36.6146 | -121.584 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0143945 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1893749 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | RECLOSER | 7002 | 20231129 | 1049 | 20231129 | 1102 | 2279870 | 13 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 138 | 1794 | 35.9663 | -121.1146 | No | Clear;32-90 F |  |  | 23-0143787 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1893679 | 0 | EPSS Ckt | Y | 2023 | A & B PHASE
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | RECLOSER | 432 | 20231129 | 1204 | 20231129 | 1327 | 2279951 | 83 | Distribution Circuit | Equipment Failure/Involved | Overhead | 324 | 26892 | 36.398 | -121.6493 | No | Partly Cloudy;32-90 F | Transformer (OH) | Burned/flashed | 23-0143821 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1893702 | 0 | EPSS Ckt | Y | 2023 | A & C PHASES
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | RECLOSER | 69466 | 20231129 | 1259 | 20231129 | 1515 | 2280000 | 136 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 241 | 32776 | 36.8266 | -121.7254 | No | Clear;32-90 F |  |  | 23-0143853 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1893719 | 0 | EPSS Ckt | N | 2023 | A PH & GRD
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | FUSE | 2467 | 20231129 | 1500 | 20231129 | 1720 | 2280096 | 140 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 3920 | 36.3936 | -121.6141 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0144005 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1893765 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 12301 | 20231129 | 1554 | 20231129 | 1658 | 2280154 | 64 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 64 | 36.9736 | -122.1295 | No | Overcast;32-90 F |  |  | 23-0143998 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1893760 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | RECLOSER | 198478 | 20231130 | 707 | 20231130 | 1220 | 2280363 | 313 | Distribution Circuit | Equipment Failure/Involved | Overhead | 238 | 74494 | 36.3913 | -121.6195 | No | Overcast;32-90 F | Transformer (OH) | Burned/flashed | 23-0144098 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1893818 | 0 | EPSS Ckt | Y | 2023 | A & C PH
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | FUSE | 9837 | 20231130 | 1022 | 20231130 | 1155 | 2280796 | 93 | Distribution Circuit | Animal | Bird found | 74 | 6906 | 36.9879 | -121.9735 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Normal | 23-0144268 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1894033 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | FUSE | 2467 | 20231130 | 1220 | 20231130 | 1657 | 2280841 | 277 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 7756 | 36.3936 | -121.6141 | No | Partly Cloudy;32-90 F | Lightning Arrestor | Burned/flashed | 23-0144290 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1894047 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | RECLOSER | 1111/2 | 20231130 | 1558 | 20231130 | 2154 | 2280980 | 356 | Distribution Circuit | Equipment Failure/Involved | Overhead | 533 | 25804 | 36.7844 | -121.3196 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0144396 | OH | Sus | 31677657 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1894077 | 0 | EPSS Ckt | N | 2023 | B & GRD
CENTRAL COAST | SALINAS | SOLEDAD-2105 | 182052105 | FUSE | 9573 | 20231130 | 1647 | 20231130 | 2017 | 2281036 | 210 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1260 | 36.5168 | -121.4119 | No | Partly Cloudy;32-90 F |  |  | 23-0144438 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1894098 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | TRANSFORMER | 412312039900 | 20231130 | 2022 | 20231201 | 1211 | 2281096 | 949 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 949 | 36.4006 | -121.6129 | No | Overcast;32-90 F | Transformer | Burned Open | 23-0144482 | OH | Sus | 31677860 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1894137 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | INTERRUPTER | 9220 | 20231201 | 650 | 20231202 | 1735 | 2281177 | 807 | Distribution Circuit | Equipment Failure/Involved | Underground | 328 | 366156 | 36.5262 | -121.8675 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0144541 | UG | Sus | 31677786 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1894177 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | INDUSTRIAL ACRES-0412 | 182300412 | TRANSFORMER | 412324350216 | 20231201 | 750 | 20231201 | 1443 | 2281234 | 413 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 4130 | 36.6839 | -121.6194 | No | Clear;32-90 F | Insulator | Deteriorated | 23-0144574 | OH | Sus | 31677766 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1894239 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | TRANSFORMER | 411509536727 | 20231201 | 958 | 20231201 | 1544 | 2281459 | 346 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 346 | 36.3072 | -121.8837 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0144701 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1894361 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | BUENA VISTA-1106 | 182261106 | TRANSFORMER | 412357048780 | 20231201 | 1145 | 20231201 | 1300 | 2281591 | 75 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 75 | 36.645 | -121.6064 | No | Partly Cloudy;32-90 F |  |  | 23-0144737 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1894383 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1102 | 182201102 | TRANSFORMER | 412533048054 | 20231201 | 1403 | 20231201 | 2258 | 2281646 | 535 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 535 | 36.6264 | -121.5455 | No | Clear;32-90 F | Transformer | Deteriorated | 23-0144771 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1894404 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 393582 | 20231202 | 204 | 20231202 | 1554 | 2281952 | 830 | Distribution Circuit | 3rd Party | Vehicle | 636 | 282952 | 37.1284 | -122.1222 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0144877 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1894462 | 0 | EPSS Ckt | N | 2023 | C GRD
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 4135 | 20231202 | 655 | 20231202 | 955 | 2281986 | 180 | Distribution Circuit | Animal | Bird found | 4 | 720 | 36.7879 | -121.7197 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0144908 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1894552 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | SOLEDAD-2105 | 182052105 | FUSE | 9571 | 20231202 | 702 | 20231202 | 1315 | 2281989 | 372 | Distribution Circuit | Equipment Failure/Involved | Overhead | 297 | 7919 | 36.5021 | -121.3957 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0144896 | OH | Sus | 46077605 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | Yes | 1894523 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 615 | 20231202 | 737 | 20231202 | 826 | 2282005 | 49 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 441 | 36.9393 | -121.8056 | No | Overcast-Fog;32-90 F |  |  | 23-0144892 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1894501 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | OCB | 2107/2 | 20231202 | 1124 | 20231202 | 2258 | 2282204 | 538 | Distribution Circuit | 3rd Party | Vehicle | 11655 | 675600 | 36.9926 | -121.9821 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 23-0144924 | OH | Sus | 35514695 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | No | 1894566 | 0 | EPSS Ckt | N | 2023 | A-B INST
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 6357 | 20231203 | 313 | 20231203 | 645 | 2282584 | 212 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 102 | 21624 | 36.9018 | -121.8246 | No | Clear;32-90 F |  |  | 23-0145006 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1894640 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SOLEDAD-2105 | 182052105 | FUSE | 9573 | 20231204 | 612 | 20231204 | 836 | 2283054 | 144 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 864 | 36.5168 | -121.4119 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0145131 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1894808 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | TRANSFORMER | T0906 | 20231204 | 827 | 20231206 | 1340 | 2283203 | 3193 | Transformer only | Wildfire Mitigation | CWSP - Vegetation Removal | 10 | 31930 | 36.9646 | -122.0234 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Normal | 23-0136776 | OH | Sus | 47024460 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1894811 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1112 | 182371112 | TRANSFORMER | 411958943015 | 20231204 | 1356 | 20231204 | 1815 | 2283659 | 259 | Transformer only | 3rd Party | Tree - cutting- 3rd party | 5 | 1295 | 36.4837 | -121.7365 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0145324 | OH | Sus | 31677777 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1895034 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | FUSE | 2751 | 20231204 | 1712 | 20231205 | 1215 | 2283860 | 1143 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 25877 | 36.3856 | -121.5538 | No | Clear;32-90 F |  |  | 23-0145408 | OH | Sus | 46078760 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1895074 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | INTERRUPTER | 977600 | 20231205 | 35 | 20231205 | 146 | 2283903 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 254 | 18034 | 36.9801 | -121.9084 | No | Clear;32-90 F |  |  | 23-0145415 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1895087 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SOLEDAD-2105 | 182052105 | FUSE | 9573 | 20231205 | 1220 | 20231205 | 1258 | 2284383 | 38 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 228 | 36.5168 | -121.4119 | No | Clear;32-90 F |  |  | 23-0145565 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1895349 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | RECLOSER | 9094 | 20231205 | 1229 | 20231205 | 1316 | 2284387 | 47 | Distribution Circuit | Vegetation | Tree - branch fell on line | 374 | 17578 | 36.5607 | -121.915 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0145557 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1895342 | 0 | EPSS Ckt | N | 2023 | A C
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 374675 | 20231205 | 1411 | 20231205 | 1439 | 2284498 | 28 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 336 | 37.0953 | -122.0854 | No | Partly Cloudy;32-90 F | Anchor or Guy | Broken | 23-0145601 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1895363 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 3017 | 20231205 | 1429 | 20231205 | 1722 | 2284501 | 173 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 173 | 37.1423 | -122.1536 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0145602 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1895364 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 1427 | 20231205 | 1516 | 20231205 | 1630 | 2284543 | 74 | Distribution Circuit | Animal | Squirrel | 55 | 4070 | 37.0823 | -122.0914 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0145667 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1895379 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1103 | 182201103 | FUSE | 24441 | 20231205 | 1546 | 20231206 | 215 | 2284570 | 629 | Distribution Circuit | 3rd Party | Vehicle | 4 | 2516 | 36.6346 | -121.5533 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0145676 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Three Phase Fault | 0 | No | Yes | No | 1895383 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | TRANSFORMER | 411805050075 | 20231205 | 1610 | 20231205 | 2033 | 2284571 | 263 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 3419 | 36.676 | -121.7957 | No | Partly Cloudy;32-90 F | Transformer | Deteriorated | 23-0145671 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1895381 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | TRANSFORMER | 316466512820 | 20231205 | 2320 | 20231206 | 121 | 2284691 | 121 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 484 | 36.8451 | -121.7088 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0145697 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1895401 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | FUSE | 44583 | 20231206 | 916 | 20231206 | 1342 | 2284991 | 266 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 532 | 36.3484 | -121.2631 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0145838 | OH | Sus | 31678501 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | Yes | 1895588 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | TRANSFORMER | 412322052615 | 20231206 | 1206 | 20231207 | 20 | 2285195 | 734 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 3670 | 36.7498 | -121.6221 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0145884 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1895625 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 491331 | 20231206 | 1309 | 20231206 | 1704 | 2285419 | 235 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 1 | 235 | 36.5828 | -121.9497 | No | Overcast-Drizzle;32-90 F | Fuse | Burned Open | 23-0146008 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1895686 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 5721 | 20231206 | 1511 | 20231206 | 1722 | 2285347 | 131 | Distribution Circuit | 3rd Party | Vehicle | 1 | 131 | 36.8974 | -121.7478 | No | Partly Cloudy-Fog-Rain;32-90 F | Pole-Wood | Normal | 23-0146017 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1895692 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | SWITCH | 10795 | 20231206 | 1745 | 20231207 | 2327 | 2285519 | 1782 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2204 | 739135 | 36.9346 | -121.774 | No | Overcast-Fog-Drizzle;32-90 F | Jumper | Burned Open | 23-0146028 | OH | Sus | 46080167 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1895698 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1101 | 182011101 | OTHER | WIRE DOWN | 20231206 | 1756 | 20231207 | 753 | 2285524 | 837 | Distribution Circuit | 3rd Party | Vehicle | 1737 | 109114 | 36.6818 | -121.6502 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on object | 23-0146034 | OH | Sus | 35515733 | SOUTH BAY AND CENTRAL COAST | DEC | Three Phase Fault | 0 | No | Yes | Yes | 1895703 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | RECLOSER | 1132 | 20231206 | 2238 | 20231207 | 1455 | 2285682 | 977 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 163 | 159251 | 36.3584 | -121.2034 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0146063 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1895730 | 0 | Non-EPSS | Y | 2023 | A C
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 9567 | 20231207 | 111 | 20231207 | 1539 | 2285707 | 868 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 12152 | 36.9497 | -121.8033 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0146082 | OH | Sus | 46080117 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1895742 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 921146 | 20231207 | 516 | 20231207 | 534 | 2285738 | 18 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 988 | 17784 | 37.0577 | -122.0595 | No | Clear;32-90 F |  |  | 23-0146085 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1895743 | 0 | EPSS Ckt | Y | 2023 | A C 50 INST
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 2321 | 20231207 | 653 | 20231207 | 1013 | 2285776 | 200 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 5600 | 37.0048 | -121.8624 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0146121 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1895870 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 4339 | 20231207 | 912 | 20231207 | 1136 | 2285985 | 144 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 2160 | 36.9838 | -121.9822 | No | Partly Cloudy;32-90 F |  |  | 23-0146200 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1895949 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SOLEDAD-2105 | 182052105 | FUSE | 9573 | 20231207 | 1213 | 20231207 | 1234 | 2286217 | 21 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 126 | 36.5168 | -121.4119 | No | Clear;32-90 F |  |  | 23-0146218 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1895959 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | BUENA VISTA-1103 | 182261103 | OCB | 1103/2 | 20231207 | 1648 | 20231209 | 10 | 2286442 | 1882 | Distribution Circuit | Equipment Failure/Involved | Overhead | 674 | 20166 | 36.654 | -121.6294 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0146300 | OH | Sus | 31678583 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1896003 | 0 | Non-EPSS | N | 2023 | INST
CENTRAL COAST | KING CITY | LOS COCHES-1102 | 182151102 | OTHER | J13021 TWD T27246 | 20231207 | 2010 | 20231208 | 150 | 2286526 | 340 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 340 | 36.3797 | -121.305 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0146286 | UG | Sus | 35515892 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1896023 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS COCHES-1102 | 182151102 | JUMPER | WIRE DOWN 1P E/OF 712011 | 20231208 | 654 | 20231208 | 1520 | 2286825 | 506 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 506 | 36.3757 | -121.2906 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0146420 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Open Circuit | 0 | No | Yes | Yes | 1896150 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS COCHES-1102 | 182151102 | FUSE | 8877 | 20231208 | 722 | 20231208 | 1621 | 2286667 | 539 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1078 | 36.3917 | -121.3075 | No | Partly Cloudy-Fog;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0146401 | OH | Sus | 31678533 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1896100 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 9919 | 20231208 | 850 | 20231208 | 1428 | 2287065 | 338 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 338 | 36.876 | -121.8066 | No | Clear;32-90 F | Insulator | Broken | 23-0146532 | OH | Sus | 46083129 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1896277 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 491331 | 20231208 | 1135 | 20231208 | 1225 | 2287130 | 50 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 1 | 50 | 36.5828 | -121.9497 | No | Clear;32-90 F | Fuse | Burned Open | 23-0146519 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1896272 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | TRANSFORMER | 411815550644 | 20231208 | 1258 | 20231208 | 1432 | 2287144 | 94 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 94 | 36.6918 | -121.7933 | No | Clear;32-90 F | Connector or Splice (OH) | Arcing | 23-0146568 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1896296 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | TRANSFORMER | 413411837315 | 20231208 | 1308 | 20231208 | 2018 | 2287155 | 430 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 430 | 36.3372 | -121.2379 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0146571 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1896297 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411910754180 | 20231208 | 1328 | 20231211 | 1129 | 2287171 | 4201 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 4201 | 36.7895 | -121.7639 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 23-0146574 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1896300 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 491331 | 20231208 | 1545 | 20231208 | 1559 | 2287282 | 14 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 1 | 14 | 36.5828 | -121.9497 | No | Clear;32-90 F | Fuse | Burned Open | 23-0146582 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1896304 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 9333 | 20231208 | 2057 | 20231209 | 220 | 2287289 | 323 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 6783 | 36.9423 | -121.8574 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0146606 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1896331 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SOLEDAD-2105 | 182052105 | FUSE | 9357 | 20231209 | 1119 | 20231209 | 1340 | 2287912 | 141 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 141 | 36.439 | -121.3336 | No | Clear;32-90 F |  |  | 23-0146662 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1896494 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 737 | 20231211 | 108 | 20231211 | 1630 | 2288548 | 922 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 31023 | 37.0046 | -121.8551 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0146809 | OH | Sus | 46087446 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1896669 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | TRANSFORMER | 412251851968 | 20231211 | 625 | 20231211 | 1619 | 2288581 | 594 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1782 | 36.7314 | -121.6457 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0146851 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1896840 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | FORT ORD-2107 | 182402107 | SWITCH | UN NUMBERED SBCO 1 SE/OF 251883 | 20231211 | 1059 | 20231211 | 1432 | 2289143 | 213 | Distribution Circuit | 3rd Party | Vehicle | 45 | 9585 | 36.6763 | -121.7626 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0146861 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1896854 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | TRANSFORMER | 412904260038 | 20231211 | 1110 | 20231211 | 1359 | 2289172 | 169 | Transformer only | 3rd Party | Gun Shot | 3 | 507 | 36.9577 | -121.4299 | No | Clear;32-90 F | Service conductor | Broken | 23-0146880 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1896886 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | JUMPER | DDE 3 E/OF 25585 | 20231211 | 1121 | 20231211 | 1822 | 2289186 | 421 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1263 | 36.7314 | -121.6458 | No | Clear;32-90 F | Switch (OH) | Broken | 23-0146853 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1896861 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | TRANSFORMER | 411428746156 | 20231211 | 1646 | 20231211 | 1747 | 2289506 | 61 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 732 | 36.5652 | -121.9207 | No | Clear;32-90 F | Transformer | Arcing | 23-0146929 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1896932 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 2953 | 20231211 | 1659 | 20231211 | 1851 | 2289514 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 336 | 37.1622 | -122.0815 | No | Clear;32-90 F |  |  | 23-0146940 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1896944 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | TRANSFORMER | 411815550644 | 20231211 | 1853 | 20231212 | 209 | 2289570 | 436 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 436 | 36.6918 | -121.7933 | No | Clear;32-90 F | Transformer | Leaking | 23-0146939 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1896943 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | TRANSFORMER | 411681944814 | 20231211 | 2256 | 20231211 | 2333 | 2289635 | 37 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 148 | 36.5306 | -121.8329 | No | Partly Cloudy;32-90 F | Secondary | Normal | 23-0146959 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1896967 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 6779 | 20231212 | 921 | 20231212 | 1023 | 2289877 | 62 | Distribution Circuit | Vegetation | Tree - bark fell into line | 2 | 124 | 36.8936 | -121.6442 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0147043 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1897163 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1102 | 182011102 | TRANSFORMER | 412249850454 | 20231212 | 944 | 20231213 | 400 | 2289929 | 1096 | Transformer only | Company Initiated | Improper Construction | 1 | 1096 | 36.6902 | -121.645 | No | Clear;32-90 F | Transformer | Normal | 23-0147068 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1897197 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | FUSE | 4817 | 20231212 | 1026 | 20231212 | 1357 | 2289972 | 211 | Distribution Circuit | 3rd Party | Vehicle | 17 | 963 | 36.9193 | -121.4497 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0147056 | OH | Sus | 31678965 | SOUTH BAY AND CENTRAL COAST | DEC | Three Phase Fault | 0 | No | Yes | No | 1897183 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | TRANSFORMER | 412072746018 | 20231212 | 1544 | 20231213 | 30 | 2290200 | 526 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 526 | 36.5667 | -121.7005 | No | Clear;32-90 F |  |  | 23-0147118 | OH | Sus | 35516878 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1897229 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | TRANSFORMER | 411419147504 | 20231213 | 946 | 20231213 | 1434 | 2290818 | 288 | Transformer only | 3rd Party | Vehicle | 14 | 4032 | 36.6021 | -121.9254 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0147230 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1897500 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | SWITCH | 10315 | 20231213 | 1003 | 20231213 | 1700 | 2290826 | 417 | Distribution Circuit | 3rd Party | Vehicle | 208 | 86736 | 37.0824 | -122.0752 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0147177 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1897475 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 316206416949 | 20231213 | 1011 | 20231213 | 1128 | 2290836 | 77 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 77 | 36.9578 | -121.7998 | No | Clear;32-90 F |  |  | 23-0147240 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1897516 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | BUENA VISTA-1106 | 182261106 | FUSE | 3969 | 20231213 | 1127 | 20231213 | 1736 | 2290979 | 369 | Distribution Circuit | 3rd Party | Vehicle | 7 | 2583 | 36.6253 | -121.6288 | No | Clear;32-90 F | Anchor or Guy | Broken- wire on ground | 23-0147261 | OH | Sus | 46090030 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | Yes | 1897536 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 1651 | 20231213 | 1239 | 20231213 | 2208 | 2291075 | 569 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1030 | 36.9565 | -121.8001 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0147287 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1897567 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | FUSE | 4071 | 20231213 | 1317 | 20231213 | 1420 | 2291127 | 63 | Distribution Circuit | 3rd Party | Vehicle | 34 | 2142 | 36.9641 | -121.9676 | No | Clear;32-90 F | Pole-Wood | Normal | 23-0147281 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1897563 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 9445 | 20231213 | 1804 | 20231213 | 1857 | 2291343 | 53 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 2968 | 37.081 | -122.073 | No | Clear;32-90 F |  |  | 23-0147331 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1897606 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 1071 | 20231213 | 2214 | 20231214 | 1330 | 2291416 | 916 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 7999 | 37.1665 | -122.1353 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0147363 | OH | Sus | 46091227 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | No | 1897638 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | TRANSFORMER | T1237 | 20231213 | 2217 | 20231213 | 2230 | 2291415 | 13 | Transformer only | Equipment Failure/Involved | Underground | 25 | 325 | 36.6676 | -121.6832 | No | Partly Cloudy;32-90 F | Secondary | Deteriorated | 23-0147354 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1897629 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | TRANSFORMER | 315709217263 | 20231213 | 2259 | 20231214 | 432 | 2291402 | 333 | Distribution Circuit | 3rd Party | Vehicle | 19 | 4850 | 36.9641 | -121.9681 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0147352 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1897627 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8343 | 20231214 | 934 | 20231214 | 1320 | 2291746 | 226 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 1 | 226 | 37.0647 | -121.9662 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0147413 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1897802 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SOLEDAD-2105 | 182052105 | TRANSFORMER | 413204541238 | 20231214 | 1404 | 20231214 | 2026 | 2291919 | 382 | Transformer only | 3rd Party | Customer Equipment | 2 | 764 | 36.4434 | -121.3118 | No | Clear;32-90 F | Customer Equipment | Failed/Faulted | 23-0147462 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1897894 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 627797 | 20231214 | 1719 | 20231214 | 1756 | 2292096 | 37 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 444 | 36.5701 | -121.9396 | No | Overcast;32-90 F |  |  | 23-0147491 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1897917 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | RECLOSER | 70782 | 20231214 | 2036 | 20231215 | 841 | 2292145 | 725 | Distribution Circuit | 3rd Party | Vehicle | 175 | 23035 | 36.7798 | -121.7788 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 23-0147498 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Three Phase Fault | 0 | No | Yes | No | 1897926 | 0 | Non-EPSS | N | 2023 | ABC
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 6685 | 20231214 | 2230 | 20231214 | 2255 | 2292165 | 25 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 50 | 36.8842 | -121.7955 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 23-0147513 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1897947 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2108 | 83252108 | FUSE | 80061 | 20231215 | 542 | 20231215 | 732 | 2292190 | 110 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 1870 | 36.9867 | -121.9963 | No | Partly Cloudy;32-90 F |  |  | 23-0147526 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1897975 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 5967 | 20231216 | 1700 | 20231216 | 2335 | 2293356 | 395 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 9085 | 37.0034 | -121.9547 | No | Clear;32-90 F | Jumper | Burned Open | 23-0147686 | OH | Sus | 46093154 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1898410 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 23653 | 20231216 | 1719 | 20231216 | 1826 | 2293352 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 134 | 36.7971 | -121.7481 | No | Clear;32-90 F |  |  | 23-0147682 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1898405 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | TRANSFORMER | 413393736813 | 20231216 | 2224 | 20231217 | 407 | 2293405 | 343 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 6174 | 36.3233 | -121.2438 | No | Clear;32-90 F | Fuse | Burned Open | 23-0147719 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1898446 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | OTHER | WIRE DOWN E PHASE 4S/N/O 10141 | 20231217 | 1009 | 20231218 | 1534 | 2293649 | 1765 | Distribution Circuit | Equipment Failure/Involved | Overhead | 839 | 245445 | 36.4482 | -121.7164 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0147744 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | Yes | 1898493 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 6459 | 20231217 | 1540 | 20231217 | 1647 | 2293792 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 53 | 3525 | 36.8856 | -121.6406 | No | Clear;32-90 F |  |  | 23-0147774 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1898525 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | JUMPER | CENTER PHASE BLOWN JPR AT 8TH & PALM | 20231217 | 1556 | 20231217 | 1647 | 2293816 | 51 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3445 | 29085 | 36.3229 | -121.2436 | No | Overcast;32-90 F | Jumper | Burned Open | 23-0147775 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Open Circuit | 0 | No | No | No | 1898526 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 6459 | 20231217 | 1704 | 20231217 | 2030 | 2293880 | 206 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 53 | 10838 | 36.8856 | -121.6406 | No | Clear;32-90 F |  |  | 23-0147800 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1898557 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | RECLOSER | 774760 | 20231218 | 433 | 20231218 | 801 | 2294053 | 208 | Distribution Circuit | Vegetation | Tree - branch fell on line | 271 | 56368 | 36.9896 | -122.0693 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Together | 23-0147827 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1898588 | 0 | EPSS Ckt | N | 2023 | B C
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | TRANSFORMER | 315593617305 | 20231218 | 513 | 20231218 | 1011 | 2294359 | 298 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 5364 | 36.9654 | -122.0094 | No | Overcast-Fog-Rain;32-90 F | Secondary | Burned Open | 23-0147879 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1898671 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1106 | 182011106 | TRANSFORMER | 412238748720 | 20231218 | 546 | 20231218 | 1453 | 2294074 | 547 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1094 | 36.6425 | -121.6472 | No | Rain-Overcast;32-90 F | Transformer | Failed/Faulted | 23-0147841 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1898606 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | RECLOSER | 7014 | 20231218 | 619 | 20231218 | 1037 | 2294104 | 258 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 106 | 27348 | 36.3875 | -121.0045 | No | Overcast-Rain;32-90 F |  |  | 23-0147838 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1898601 | 0 | Non-EPSS | Y | 2023 | B & C PHASE
CENTRAL COAST | SALINAS | GONZALES-1101 | 182131101 | OTHER | 1 PHASE WIRE DOWN CGC 412956644823 | 20231218 | 725 | 20231218 | 1311 | 2294301 | 346 | Distribution Circuit | Equipment Failure/Involved | Overhead | 68 | 5074 | 36.541 | -121.3987 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0147862 | OH | Sus | 46094562 | SOUTH BAY AND CENTRAL COAST | DEC | Open Circuit | 0 | No | Yes | Yes | 1898646 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 3893 | 20231218 | 820 | 20231218 | 1105 | 2294217 | 165 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 2640 | 36.9688 | -121.8551 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 23-0147898 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1898703 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1106 | 182031106 | FUSE | 338309 | 20231218 | 938 | 20231218 | 1024 | 2294409 | 46 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 61 | 36.2179 | -121.0862 | No | Overcast-Fog-Rain;32-90 F |  |  | 23-0147888 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1898683 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6911 | 20231218 | 1052 | 20231218 | 1355 | 2294446 | 183 | Distribution Circuit | Vegetation | Tree - branch fell on line | 98 | 17934 | 37.0171 | -121.7217 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0147924 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1898733 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | RECLOSER | 7014 | 20231218 | 1226 | 20231219 | 1145 | 2294541 | 1399 | Distribution Circuit | Equipment Failure/Involved | Overhead | 163 | 86587 | 36.3875 | -121.0045 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Annealed | 23-0147910 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1898718 | 0 | Non-EPSS | Y | 2023 | B & C PHASE
CENTRAL COAST | KING CITY | SOLEDAD-2104 | 182052104 | FUSE | 78197 | 20231218 | 1410 | 20231218 | 2234 | 2294783 | 504 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 7056 | 36.4295 | -121.3331 | No | Overcast;32-90 F | Crossarm- Wood | Deteriorated | 23-0147933 | OH | Sus | 46095102 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1898741 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 7371 | 20231218 | 1438 | 20231218 | 1658 | 2294800 | 140 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 840 | 37.0585 | -122.142 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0147966 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1898775 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 11044 | 20231218 | 1625 | 20231218 | 1929 | 2294934 | 184 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2247 | 47510 | 37.0401 | -122.0297 | No | Overcast-Drizzle;32-90 F |  |  | 23-0147954 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Multi-Fault | 0 | No | No | No | 1898762 | 0 | EPSS Ckt | N | 2023 | A- B- C- & GRD
CENTRAL COAST | COAST | PAUL SWEET-2103 | 83252103 | RECLOSER | 12075 | 20231218 | 1657 | 20231219 | 421 | 2294981 | 681 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3659 | 777255 | 36.9736 | -122.0175 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0147958 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Multi-Fault | 0 | No | Yes | No | 1898767 | 0 | EPSS Ckt | N | 2023 | A- C- & GRD
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 5143 | 20231218 | 1812 | 20231219 | 7 | 2295049 | 355 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 9585 | 37.0994 | -122.0868 | No | Clear;32-90 F |  |  | 23-0148022 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1898838 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 11939 | 20231218 | 1812 | 20231218 | 2121 | 2295050 | 189 | Distribution Circuit | Vegetation | Tree - branch fell on line | 71 | 13419 | 37.0106 | -122.0442 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0148009 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1898822 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 10214 | 20231218 | 1946 | 20231218 | 2200 | 2295111 | 134 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 218 | 29212 | 37.0909 | -122.0439 | No | Overcast-Fog-Rain;32-90 F |  |  | 23-0147983 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1898794 | 0 | EPSS Ckt | N | 2023 | A C
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | RECLOSER | 974130 | 20231218 | 1957 | 20231218 | 2123 | 2295116 | 86 | Distribution Circuit | Vegetation | Tree - bark fell into line | 91 | 7826 | 37.0448 | -121.9382 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0147984 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Multi-Fault | 0 | No | No | No | 1898795 | 0 | EPSS Ckt | N | 2023 | B C GRD 51
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 5215 | 20231218 | 2301 | 20231219 | 118 | 2295220 | 137 | Distribution Circuit | Vegetation | Tree - branch fell on line | 60 | 8220 | 37.0325 | -122.0765 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 23-0148027 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1898843 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 2811 | 20231218 | 2314 | 20231219 | 144 | 2294877 | 150 | Distribution Circuit | Equipment Failure/Involved | Overhead | 169 | 8072 | 36.9669 | -121.7651 | No | Overcast-Fog-Rain;32-90 F | Crossarm- Wood | Broken | 23-0148016 | OH | Sus | 31679847 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1898831 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 3041 | 20231219 | 336 | 20231219 | 1005 | 2295269 | 389 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 1167 | 37.0413 | -122.0825 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0148080 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1898937 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9783 | 20231219 | 555 | 20231219 | 1722 | 2295292 | 687 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 14390 | 37.1573 | -122.1336 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0148042 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1898858 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 5149 | 20231219 | 602 | 20231219 | 840 | 2295308 | 158 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 790 | 37.1109 | -122.0899 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0148069 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1898895 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412252354890 | 20231219 | 932 | 20231219 | 2311 | 2295524 | 819 | Transformer only | Vegetation | Tree - grew into line | 6 | 4914 | 36.8125 | -121.6484 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0148084 | OH | Sus | 31679719 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1898947 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | FUSE | 37778 | 20231219 | 1011 | 20231219 | 1206 | 2295567 | 115 | Distribution Circuit | 3rd Party | Vehicle | 9 | 1035 | 36.841 | -121.4949 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0148095 | OH | Sus | 31679852 | SOUTH BAY AND CENTRAL COAST | DEC | Three Phase Fault | 0 | No | No | No | 1898958 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | SWITCH | 620441 | 20231219 | 1057 | 20231219 | 1103 | 2295627 | 6 | Distribution Circuit | Environmental/External | Water | 1 | 6 | 37.1288 | -122.1362 | No | Overcast-Drizzle;32-90 F | Transformer (UG) | Normal | 23-0148087 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1898950 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 12758 | 20231220 | 138 | 20231220 | 1244 | 2296159 | 654 | Distribution Circuit | Vegetation | Tree - fell into line | 284 | 62479 | 37.1486 | -122.1745 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0148198 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Multi-Fault | 0 | No | Yes | No | 1899067 | 0 | EPSS Ckt | N | 2023 | A B C GRD 51
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 7839 | 20231220 | 753 | 20231220 | 1632 | 2296268 | 519 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 5709 | 36.9612 | -121.7897 | No | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0148217 | OH | Sus | 46097301 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1899105 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 11054 | 20231220 | 815 | 20231220 | 1418 | 2296295 | 360 | Distribution Circuit | Vegetation | Tree - fell into line | 309 | 40956 | 36.9775 | -121.7415 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0148215 | OH | Sus | 31679907 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1899102 | 0 | EPSS Ckt | N | 2023 | B GRD 51 TIME
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | TRANSFORMER | 316483014940 | 20231220 | 821 | 20231220 | 1436 | 2296296 | 375 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 375 | 36.9047 | -121.7038 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0148245 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1899174 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | TRANSFORMER | 412041352552 | 20231220 | 848 | 20231220 | 1409 | 2296341 | 321 | Transformer only | Equipment Failure/Involved | Electrical Overload | 3 | 963 | 36.747 | -121.718 | No | Rain-Overcast-Fog;32-90 F | Transformer | Failed/Faulted | 23-0148238 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1899163 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 12009 | 20231220 | 1103 | 20231220 | 1200 | 2296538 | 57 | Distribution Circuit | Vegetation | Tree - bark fell into line | 5 | 285 | 36.8535 | -121.6486 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0148253 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1899185 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5485 | 20231220 | 1105 | 20231221 | 1017 | 2296465 | 1392 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 24249 | 37.1322 | -122.109 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0148247 | OH | Sus | 46096974 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1899178 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | TRANSFORMER | 315327121963 | 20231220 | 1113 | 20231220 | 1700 | 2296491 | 347 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 694 | 37.0922 | -122.1031 | No | Clear;32-90 F |  |  | 23-0148258 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1899190 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 6779 | 20231220 | 1130 | 20231220 | 1355 | 2296548 | 145 | Distribution Circuit | Vegetation | Tree - bark fell into line | 2 | 290 | 36.8936 | -121.6442 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0148276 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1899208 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | FUSE | 24972 | 20231220 | 1133 | 20231220 | 1236 | 2296518 | 63 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 47 | 2961 | 36.6772 | -121.673 | No | Overcast-Drizzle;32-90 F |  |  | 23-0148259 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1899191 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SPENCE-1101 | 182201101 | TRANSFORMER | 412338647166 | 20231220 | 1205 | 20231220 | 1631 | 2296539 | 266 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 266 | 36.6002 | -121.6112 | No | Overcast-Drizzle;32-90 F | Transformer | Broken | 23-0148264 | OH | Sus | 31679972 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1899194 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315659721962 | 20231220 | 1459 | 20231221 | 1010 | 2296696 | 1151 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2302 | 37.0935 | -121.9897 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 23-0148302 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1899239 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | RECLOSER | BL 1101 | 20231220 | 1547 | 20231220 | 1756 | 2296808 | 129 | Distribution Circuit | Vegetation | Tree - fell into line | 744 | 87336 | 37.0926 | -122.0966 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0148297 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Three Phase Fault | 0 | No | No | No | 1899233 | 0 | EPSS Ckt | N | 2023 | A B C
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 12518 | 20231220 | 1735 | 20231221 | 1003 | 2296891 | 988 | Distribution Circuit | Vegetation | Tree - fell into line | 617 | 533589 | 37.0791 | -122.0037 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0148318 | OH | Sus | 46098236 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1899256 | 0 | EPSS Ckt | N | 2023 | C&GRD
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | OTHER | 12990 | 20231220 | 1739 | 20231220 | 2356 | 2296909 | 377 | Distribution Circuit | Vegetation | Tree - fell into line | 791 | 114040 | 37.039 | -122.0214 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0148321 | OH | Sus | 46097999 | SOUTH BAY AND CENTRAL COAST | DEC | Open Circuit | 0 | No | Yes | No | 1899259 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | OCB | 2201/2 | 20231221 | 244 | 20231221 | 726 | 2297295 | 282 | Distribution Circuit | Equipment Failure/Involved | Underground | 1936 | 434256 | 36.5786 | -121.9085 | No | Overcast-Fog;32-90 F | Connector or Splice (UG) | Failed/Faulted | 23-0148415 | UG | Sus | 46097850 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1899373 | 0 | EPSS Ckt | N | 2023 | C-GRD
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 974520 | 20231221 | 403 | 20231221 | 2154 | 2297315 | 1071 | Distribution Circuit | Vegetation | Tree - fell into line | 329 | 139537 | 36.9908 | -121.8063 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0148425 | OH | Sus | 46098293 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1899384 | 0 | EPSS Ckt | N | 2023 | A-GRD
CENTRAL COAST | KING CITY | KING CITY-1106 | 182031106 | RECLOSER | 500 | 20231221 | 804 | 20231221 | 1357 | 2297480 | 353 | Distribution Circuit | Equipment Failure/Involved | Overhead | 81 | 18198 | 36.2185 | -121.0846 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0148458 | OH | Sus | 46098558 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1899441 | 0 | EPSS Ckt | N | 2023 | ABC TIME
CENTRAL COAST | COAST | PAUL SWEET-2108 | 83252108 | TRANSFORMER | T0457 | 20231221 | 900 | 20231221 | 1142 | 2297479 | 162 | Distribution Circuit | Equipment Failure/Involved | Underground | 365 | 12791 | 36.9661 | -122.032 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0148468 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1899455 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | JUMPER | BURNED OPEN JMPR HIGH SIDE OF 6045 | 20231221 | 938 | 20231221 | 2241 | 2297515 | 783 | Distribution Circuit | Equipment Failure/Involved | Overhead | 45 | 35235 | 37.0969 | -121.9747 | No | Clear;32-90 F | Jumper | Burned Open | 23-0148469 | OH | Sus | 46097858 | SOUTH BAY AND CENTRAL COAST | DEC | Open Circuit | 0 | No | No | No | 1899456 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315646021536 | 20231221 | 1002 | 20231221 | 2241 | 2297536 | 759 | Distribution Circuit | Equipment Failure/Involved | Overhead | 574 | 168075 | 37.0818 | -121.9938 | No | Clear;32-90 F | Jumper | Burned Open | 23-0148489 | OH | Sus | 46098683 | SOUTH BAY AND CENTRAL COAST | DEC | Open Circuit | 0 | No | No | No | 1899485 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | TRANSFORMER | 412856743214 | 20231221 | 1121 | 20231221 | 1145 | s1899458 | 24 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 24 | 36.4956 | -121.4318 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0148471 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1899458 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | TRANSFORMER | T0429 | 20231221 | 1400 | 20231222 | 139 | 2297793 | 699 | Distribution Circuit | Equipment Failure/Involved | Underground | 31 | 11574 | 36.7095 | -121.6261 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0148507 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1899502 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | TRANSFORMER | 316665314049 | 20231221 | 1543 | 20231221 | 2143 | 2297880 | 360 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 720 | 36.8806 | -121.6413 | No | Overcast;32-90 F | Secondary | Arcing | 23-0148503 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1899499 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 316201616575 | 20231221 | 1750 | 20231222 | 130 | 2297972 | 460 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 460 | 36.9477 | -121.8008 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0148524 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1899521 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 2553 | 20231221 | 2259 | 20231222 | 109 | 2298062 | 130 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 4290 | 36.5766 | -121.97 | No | Partly Cloudy;32-90 F |  |  | 23-0148559 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1899562 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 4281 | 20231222 | 151 | 20231222 | 645 | 2298089 | 294 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 2252 | 36.9018 | -121.7809 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0148567 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1899574 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | SWITCH | 9472 | 20231222 | 905 | 20231222 | 1425 | s1899626 | 320 | Distribution Circuit | Company Initiated | Personnel- company | 50 | 16000 | 36.5312 | -121.7775 | No | Partly Cloudy-Fog;32-90 F | Switch (UG) | Normal | 23-0144768 | UG | Sus | 35183970 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1899626 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-0414 | 83330414 | FUSE | 4869 | 20231222 | 1112 | 20231222 | 1155 | 2298374 | 43 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 43 | 36.9127 | -121.7511 | No | Clear;32-90 F |  |  | 23-0148590 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1899645 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | FUSE | 3575 | 20231222 | 2057 | 20231223 | 2030 | 2298621 | 1413 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 12717 | 36.7297 | -121.7326 | No | Clear;32-90 F |  |  | 23-0148635 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1899695 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | T0177 | 20231223 | 1148 | 20231223 | 1636 | 2298798 | 288 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 288 | 37.0414 | -122.0297 | No | Clear;32-90 F |  |  | 23-0148681 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1899747 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | TRANSFORMER | 413061756592 | 20231223 | 1317 | 20231223 | 1427 | 2298845 | 70 | Transformer only | Animal | Bird found | 2 | 140 | 36.8643 | -121.3732 | No | Clear;32-90 F | Transformer | Normal | 23-0148673 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1899738 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 6469 | 20231223 | 1543 | 20231223 | 1802 | 2298890 | 139 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 973 | 36.5315 | -121.8354 | No | Clear;32-90 F |  |  | 23-0148684 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1899751 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | RECLOSER | 9488 | 20231224 | 648 | 20231224 | 1713 | 2299056 | 209 | Distribution Circuit | Equipment Failure/Involved | Underground | 175 | 32790 | 36.5902 | -121.9442 | No | Partly Cloudy;32-90 F | Elbow | Burned/flashed | 23-0148730 | UG | Sus | 46100462 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1899798 | 0 | EPSS Ckt | N | 2023 | C & GRD
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 454081 | 20231224 | 1414 | 20231224 | 1706 | 2299176 | 172 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 516 | 36.5844 | -121.9483 | No | Clear;32-90 F |  |  | 23-0148768 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1899840 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 2249 | 20231224 | 1431 | 20231224 | 1556 | 2299186 | 85 | Distribution Circuit | Animal | Bird found | 177 | 11349 | 36.5968 | -121.8553 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0148761 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1899833 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | TRANSFORMER | 316478013615 | 20231224 | 1817 | 20231225 | 1043 | 2299287 | 986 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 986 | 36.8677 | -121.704 | No | Clear;32-90 F |  |  | 23-0148819 | OH | Sus | 46100430 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1899890 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | FUSE | 6625 | 20231225 | 357 | 20231225 | 1308 | 2299367 | 551 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 12722 | 36.3759 | -121.5909 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0148813 | OH | Sus | 46100386 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | No | 1899884 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | DOLAN ROAD-1103 | 182381103 | INTERRUPTER | 86772 | 20231225 | 958 | 20231226 | 152 | 2299423 | 954 | Distribution Circuit | Equipment Failure/Involved | Underground | 42 | 6264 | 36.7908 | -121.784 | No | Clear;32-90 F | Transformer (UG) | Deteriorated | 23-0148820 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1899891 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 11797 | 20231225 | 1059 | 20231225 | 1141 | 2299442 | 42 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 630 | 36.8677 | -121.7087 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken | 23-0148821 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1899892 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 5269 | 20231225 | 1403 | 20231226 | 907 | 2299492 | 1144 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 26 | 29640 | 36.9894 | -122.0312 | No | Partly Cloudy;32-90 F |  |  | 23-0148839 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1899910 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | TRANSFORMER | 315473622371 | 20231225 | 1525 | 20231226 | 1150 | 2299512 | 1225 | Transformer only | Equipment Failure/Involved | Electrical Overload | 3 | 3675 | 37.1038 | -122.0532 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0148841 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1899912 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | TRANSFORMER | 411417945469 | 20231225 | 1546 | 20231225 | 1658 | 2299515 | 72 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 1080 | 36.5461 | -121.9234 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 23-0148840 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1899911 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2103 | 83252103 | TRANSFORMER | 315580517945 | 20231225 | 1949 | 20231226 | 928 | 2299548 | 819 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 13104 | 36.983 | -122.0143 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0148853 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1899924 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | FUSE | 6623 | 20231225 | 2149 | 20231226 | 1223 | 2299563 | 874 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 40 | 34977 | 36.3779 | -121.5902 | No | Clear;32-90 F |  |  | 23-0148891 | OH | Sus | 46100446 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900008 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | RECLOSER | 502 | 20231226 | 722 | 20231226 | 1805 | 2299626 | 643 | Distribution Circuit | Equipment Failure/Involved | Overhead | 162 | 40566 | 36.1289 | -121.0147 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0148860 | OH | Sus | 31680222 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | No | 1899932 | 0 | EPSS Ckt | N | 2023 | A-B-C
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | TRANSFORMER | 412339452885 | 20231226 | 1553 | 20231226 | 2355 | 2299991 | 482 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 3856 | 36.7573 | -121.6177 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0148906 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900025 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1106 | 182031106 | SWITCH | 7007 | 20231226 | 1856 | 20231226 | 1904 | s1900038 | 8 | Distribution Circuit | Company Initiated | Return Circuit Normal | 137 | 1096 | 36.2043 | -120.8471 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0148860 | OH | Sus | 31680222 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1900038 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1106 | 182031106 | RECLOSER | 500 | 20231227 | 842 | 20231227 | 1524 | 2300487 | 331 | Distribution Circuit | Equipment Failure/Involved | Overhead | 81 | 14211 | 36.2185 | -121.0846 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0148978 | OH | Sus | 46101949 | SOUTH BAY AND CENTRAL COAST | DEC | Three Phase Fault | 0 | No | Yes | No | 1900130 | 0 | EPSS Ckt | N | 2023 | A-B-C
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 412031852085 | 20231227 | 1157 | 20231227 | 1653 | 2300654 | 296 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 888 | 36.7338 | -121.7201 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0149002 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900168 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411957153231 | 20231227 | 1315 | 20231228 | 27 | 2300655 | 672 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 3360 | 36.7639 | -121.7473 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0149007 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900175 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | TRIP-SAVER | 3959 | 20231227 | 1358 | 20231227 | 1504 | 2300785 | 66 | Distribution Circuit | Vegetation | Tree - branch fell on line | 125 | 8264 | 36.959 | -122.0316 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0149030 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900201 | 1 | EPSS Ckt | N | 2023 | N/A
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | TRANSFORMER | 315523216960 | 20231227 | 1555 | 20231228 | 28 | 2300867 | 513 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 6156 | 36.9557 | -122.0331 | No | Rain-Overcast;32-90 F | Transformer | Failed/Faulted | 23-0149051 | OH | Sus | 35519998 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900228 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 8643 | 20231227 | 1732 | 20231227 | 1924 | 2300922 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 45 | 4428 | 37.01 | -121.8859 | No | Overcast-Fog-Rain;32-90 F |  |  | 23-0149045 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900219 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 12525 | 20231227 | 1940 | 20231227 | 2346 | 2300966 | 246 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 527 | 15962 | 37.0938 | -122.0243 | No | Clear;32-90 F |  |  | 23-0149074 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900252 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1106 | 182031106 | JUMPER | JMPRS 1 SPAN SOURCE SIDE CGC 415010331216 | 20231228 | 3 | 20231229 | 306 | 2301635 | 1623 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1623 | 36.1771 | -120.6899 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0149169 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1900428 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 316260712308 | 20231228 | 203 | 20231228 | 1055 | 2301005 | 532 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 5320 | 36.831 | -121.7786 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0149081 | OH | Sus | 46102450 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1900260 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | OCB | 1101/2 | 20231228 | 331 | 20231228 | 1123 | 2301021 | 472 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4454 | 1818458 | 36.6434 | -121.792 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0149078 | OH | Sus | 46102451 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1900257 | 0 | EPSS Ckt | N | 2023 | A- GRD TIME 51
CENTRAL COAST | MONTEREY | FORT ORD-2107 | 182402107 | OCB | 2107/2/NORM | 20231228 | 331 | 20231228 | 1119 | 2301022 | 468 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3994 | 1283454 | 36.6433 | -121.7918 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0149079 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1900258 | 0 | EPSS Ckt | N | 2023 | 8-GRD 51
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | FUSE | 6623 | 20231228 | 654 | 20231228 | 1725 | 2301046 | 631 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 60 | 37860 | 36.3779 | -121.5902 | No | Clear;32-90 F |  |  | 23-0149137 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1900394 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 9629 | 20231228 | 959 | 20231228 | 1043 | 2301217 | 44 | Distribution Circuit | Vegetation | Tree - branch fell on line | 464 | 20416 | 36.5853 | -121.9054 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Normal | 23-0149100 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1900342 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | FUSE | 6045 | 20231228 | 1124 | 20231229 | 544 | 2301278 | 1100 | Distribution Circuit | Equipment Failure/Involved | Underground | 203 | 64520 | 36.6825 | -121.7986 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 23-0149108 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900350 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | JUMPER | OJ 6 SS OF CGC#414075523120 | 20231228 | 1240 | 20231228 | 1519 | 2301344 | 159 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 2385 | 35.9399 | -121.0178 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0149111 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1900359 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | SWITCH | 122 | 20231228 | 1315 | 20231228 | 2300 | 2301180 | 585 | Distribution Circuit | Environmental/External | Flood/Erosion | 136 | 13260 | 36.9729 | -121.9523 | No | Overcast;32-90 F | Secondary | Burned/flashed | 23-0149114 | UG | Sus | 46102781 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1900364 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | KING CITY-1106 | 182031106 | FUSE | 9057 | 20231228 | 1326 | 20231228 | 2119 | 2301381 | 473 | Distribution Circuit | Animal | Bird found | 7 | 3311 | 36.1506 | -121.0667 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0149119 | OH | Sus | 31680472 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | No | 1900375 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | RECLOSER | 3032 | 20231228 | 1601 | 20231228 | 1653 | 2301509 | 52 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 109 | 5668 | 36.634 | -121.6988 | No | Clear;32-90 F |  |  | 23-0149123 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900381 | 0 | EPSS Ckt | N | 2023 | SGF
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 11865 | 20231228 | 1615 | 20231229 | 228 | 2301438 | 613 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 44749 | 37.001 | -121.7398 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0149126 | OH | Sus | 46102787 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1900384 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | TRANSFORMER | 315483817638 | 20231228 | 2104 | 20231229 | 239 | 2301599 | 335 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 5025 | 36.9733 | -122.0462 | No | Partly Cloudy-Fog;32-90 F | Crossarm- Wood | Broken | 23-0149167 | OH | Sus | 31680477 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1900424 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412210154964 | 20231228 | 2220 | 20231229 | 913 | 2301637 | 653 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 2612 | 36.8138 | -121.6627 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0149173 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900433 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315398519887 | 20231229 | 539 | 20231229 | 1328 | 2301668 | 469 | Transformer only | Vegetation | Tree - branch fell on line | 9 | 4221 | 37.0358 | -122.0777 | No | Overcast-Fog;32-90 F | Transformer | Broken- wire on ground | 23-0149182 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1900443 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | OCB | 1102/2 | 20231229 | 545 | 20231229 | 720 | 2301680 | 95 | Distribution Circuit | Vegetation | Tree - branch fell on line | 412 | 21545 | 36.5569 | -121.8976 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 23-0149180 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1900441 | 0 | EPSS Ckt | N | 2023 | B&C
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | OTHER | NG CONNECTION LD SIDE T0586 | 20231229 | 604 | 20231229 | 753 | 2301722 | 109 | Distribution Circuit | Equipment Failure/Involved | Underground | 203 | 17129 | 36.6838 | -121.7976 | No | Overcast-Fog;32-90 F | Elbow | Broken | 23-0149189 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Open Circuit | 0 | No | No | No | 1900453 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | 83500401 | 83500401 | FUSE | 6007 | 20231229 | 716 | 20231229 | 938 | 2301698 | 142 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 2553 | 37.0029 | -121.9273 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 23-0149187 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900451 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 8015 | 20231229 | 936 | 20231229 | 1909 | 2301802 | 573 | Distribution Circuit | Vegetation | Tree - fell into line | 140 | 80220 | 37.1536 | -122.1615 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0149209 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | No | 1900500 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315400519945 | 20231229 | 1151 | 20231229 | 1305 | 2301915 | 74 | Transformer only | Vegetation | Tree - grew into line | 10 | 740 | 37.0369 | -122.077 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Contaminated | 23-0149213 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900507 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 40411 | 20231229 | 1215 | 20231229 | 1330 | 2301931 | 75 | Distribution Circuit | Vegetation | Tree - branch fell on line | 155 | 11625 | 36.4918 | -121.938 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0149225 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1900522 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-0414 | 83330414 | JUMPER | BURNT OJ @ MAPLE & MERCHANT | 20231229 | 1327 | 20231229 | 1556 | 2302013 | 149 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 7450 | 36.9115 | -121.7527 | No | Overcast-Drizzle;32-90 F | Jumper | Burned Open | 23-0149232 | OH | Sus | 46103099 | SOUTH BAY AND CENTRAL COAST | DEC | Open Circuit | 0 | No | No | No | 1900530 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2108 | 83252108 | OCB | 2108/2 | 20231229 | 1539 | 20231229 | 2322 | 2302106 | 463 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5734 | 342449 | 36.9926 | -121.982 | No | Overcast-Rain;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0149247 | OH | Sus | 46106412 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | No | 1900544 | 0 | EPSS Ckt | N | 2023 | A-C
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9761 | 20231229 | 1547 | 20231229 | 1940 | 2302118 | 233 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 699 | 37.1729 | -122.1638 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0149270 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1900568 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | SWITCH | 2677 | 20231229 | 1603 | 20231229 | 2149 | 2302123 | 346 | Distribution Circuit | Vegetation | Tree - fell into line | 783 | 18801 | 37.1312 | -122.1245 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0149246 | OH | Sus | 46106411 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1900549 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-0414 | 83330414 | TRANSFORMER | 316338615210 | 20231229 | 1621 | 20231229 | 2129 | 2302147 | 308 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 4928 | 36.911 | -121.7533 | No | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0149257 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900555 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 5981 | 20231229 | 1632 | 20231230 | 1122 | 2302151 | 1130 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 18080 | 37.0468 | -121.9526 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0149260 | OH | Sus | 46107706 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1900558 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-0414 | 83330414 | TRANSFORMER | 316336415192 | 20231229 | 1637 | 20231229 | 2214 | 2302158 | 337 | Transformer only | Equipment Failure/Involved | Overhead | 22 | 7414 | 36.9104 | -121.7541 | No | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0149262 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900560 | 0 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 5101 | 20231229 | 1812 | 20231229 | 1819 | 2302169 | 7 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 393 | 2751 | 36.9626 | -122.0354 | No | Overcast-Rain;32-90 F | Transformer (OH) | Normal | 23-0149264 | OH | Sus | 46106412 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1900562 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 5151 | 20231229 | 2119 | 20231230 | 545 | 2302283 | 506 | Distribution Circuit | Vegetation | Tree - bark fell into line | 5 | 2530 | 37.111 | -122.0899 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0149314 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1900612 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 7299 | 20231229 | 2140 | 20231230 | 1204 | 2302286 | 864 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 11232 | 37.0308 | -122.0939 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0149298 | OH | Sus | 46106417 | SOUTH BAY AND CENTRAL COAST | DEC | Three Phase Fault | 0 | No | Yes | No | 1900596 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315708222583 | 20231230 | 313 | 20231230 | 1400 | 2302398 | 647 | Transformer only | Vegetation | Tree - fell into line | 2 | 1294 | 37.1108 | -121.9727 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0149332 | OH | Sus | 46118327 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1900640 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 4269 | 20231230 | 315 | 20231230 | 710 | 2302396 | 235 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 7826 | 36.9143 | -121.6626 | No | Clear;32-90 F |  |  | 23-0149318 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900619 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | KING CITY | SOLEDAD-2104 | 182052104 | TRANSFORMER | 413152040721 | 20231230 | 414 | 20231230 | 708 | 2302411 | 174 | Transformer only | Unknown Cause | Patrol - found nothing | 7 | 1218 | 36.4289 | -121.3288 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 23-0149324 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900627 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | FUSE | 50377 | 20231230 | 621 | 20231230 | 1358 | 2302441 | 457 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 457 | 36.8356 | -121.4452 | No | Partly Cloudy-Fog-Drizzle;32-90 F | Lightning Arrestor | Burned/flashed | 23-0149321 | OH | Sus | 46106418 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1900623 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | TRANSFORMER | 412128349646 | 20231230 | 727 | 20231230 | 1547 | 2302465 | 500 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 500 | 36.6666 | -121.6854 | No | Partly Cloudy-Fog-Drizzle;32-90 F | Transformer | Deteriorated | 23-0149340 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900648 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | RECLOSER | 974130 | 20231230 | 744 | 20231230 | 1333 | 2302473 | 349 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 31759 | 37.0448 | -121.9382 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0149319 | OH | Sus | 31680546 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | No | 1900621 | 0 | EPSS Ckt | N | 2023 | AB GRD T
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 9185 | 20231230 | 753 | 20231230 | 845 | 2302477 | 52 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 87 | 37.0568 | -122.0075 | No | Overcast-Fog-Drizzle;32-90 F | Fuse | Broken | 23-0149328 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900635 | 1 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | TRANSFORMER | 316622014923 | 20231230 | 1103 | 20231230 | 2109 | 2302668 | 606 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1212 | 36.9049 | -121.6551 | No | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0149370 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900682 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | JUMPER | JUMPERS 1P N/OF CGC# 316095015460 | 20231230 | 1119 | 20231230 | 1808 | 2302705 | 409 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 5726 | 36.917 | -121.8369 | No | Overcast;32-90 F | Pole-Wood | Deteriorated | 23-0149360 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1900668 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRANSFORMER | 315219025413 | 20231230 | 1144 | 20231230 | 1954 | 2302660 | 490 | Transformer only | Vegetation | Tree - fell into line | 8 | 3920 | 37.1863 | -122.1422 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0149381 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1900693 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRANSFORMER | 315216225488 | 20231230 | 1244 | 20231230 | 1954 | 2302789 | 430 | Transformer only | Unknown Cause | Patrol - not conducted | 8 | 3440 | 37.1883 | -122.1431 | No | Clear;32-90 F |  |  | 23-0149383 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900695 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 1699 | 20231230 | 1405 | 20231230 | 1624 | 2302836 | 135 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1215 | 36.9707 | -121.797 | No | Partly Cloudy;32-90 F |  |  | 23-0149395 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1900707 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | TRANSFORMER | 411976551287 | 20231230 | 1430 | 20231231 | 25 | 2302849 | 595 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1190 | 36.7111 | -121.739 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0149387 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900700 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | RECLOSER | 4060 | 20231230 | 1608 | 20231230 | 1910 | 2302906 | 182 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1004 | 45118 | 36.801 | -121.3379 | No | Partly Cloudy;32-90 F | PT/CCVT | Burned/flashed | 23-0149390 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1900702 | 0 | EPSS Ckt | N | 2023 | A/B
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 3269 | 20231230 | 2232 | 20231231 | 1440 | 2303045 | 968 | Distribution Circuit | 3rd Party | Vehicle | 2394 | 59505 | 36.9877 | -121.8416 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken | 23-0149443 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Three Phase Fault | 0 | No | No | No | 1900758 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | SALINAS | BUENA VISTA-1102 | 182261102 | FUSE | 5993 | 20231231 | 730 | 20240102 | 828 | 2303111 | 2938 | Distribution Circuit | Vegetation | Other ground vegetation | 107 | 25652 | 36.6524 | -121.6297 | No | Overcast;32-90 F | Transformer (UG) | Burned/flashed | 23-0149455 | UG | Sus | 46122447 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900772 | 1 | Non-EPSS | N | 2023
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 11489 | 20231231 | 826 | 20231231 | 913 | 2303120 | 47 | Distribution Circuit | Animal | Squirrel | 54 | 2538 | 36.9045 | -121.7473 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 23-0149456 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900774 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 1699 | 20231231 | 921 | 20231231 | 1400 | 2303154 | 279 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 2511 | 36.9707 | -121.797 | No | Overcast-Fog;32-90 F |  |  | 23-0149484 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1900805 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | JUMPER | UN NUM FUCO 7 S/OF CGC 315508618438 | 20231231 | 940 | 20231231 | 2315 | 2303182 | 815 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 815 | 36.9923 | -122.0348 | No | Overcast;32-90 F | Insulator | Broken- wire on ground | 23-0149468 | OH | Sus | 31680680 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1900787 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | PAUL SWEET-2103 | 83252103 | RECLOSER | 458558 | 20231231 | 1011 | 20231231 | 2027 | 2303165 | 616 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 786 | 80916 | 36.9721 | -122.0176 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0149463 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900782 | 0 | EPSS Ckt | N | 2023 | B GRD
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | TRANSFORMER | 315495917831 | 20231231 | 1047 | 20231231 | 1459 | 2303167 | 252 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 2016 | 36.9787 | -122.0422 | No | Overcast;32-90 F | Transformer | Broken | 23-0149464 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1900783 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | TRANSFORMER | 316205717466 | 20231231 | 1556 | 20240101 | 1128 | 2303282 | 1172 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2344 | 36.9725 | -121.7998 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0149493 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900814 | 0 | EPSS Ckt | N | 2023
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 40349 | 20240101 | 420 | 20240101 | 456 | 2303822 | 36 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 196 | 7056 | 36.5965 | -121.8402 | No | Clear;32-90 F |  |  | 24-0005749 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1900864 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRIP-SAVER | 6577 | 20240101 | 807 | 20240102 | 1221 | 2304145 | 1694 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 83006 | 37.0487 | -121.8085 | No | Fog;32-90 F | Recloser | Failed/Faulted | 24-0005781 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1900886 | 0 | EPSS Ckt | N | 2024 | A PHASE
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | TRANSFORMER | 100000008488 | 20240101 | 1214 | 20240101 | 1257 | 2304245 | 43 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 258 | 36.6719 | -121.788 | No | Clear;32-90 F | Fuse | Broken | 24-0005790 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1900893 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 1513 | 20240101 | 1408 | 20240102 | 154 | 2304307 | 706 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 706 | 36.9919 | -121.7999 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 24-0005818 | OH | Sus | 31680607 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1900919 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 11054 | 20240101 | 1432 | 20240101 | 2217 | 2304268 | 465 | Distribution Circuit | Vegetation | Tree - branch fell on line | 309 | 36305 | 36.9775 | -121.7415 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0005798 | OH | Sus | 46122472 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1900901 | 0 | EPSS Ckt | N | 2024 | NONE
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 3263 | 20240102 | 258 | 20240102 | 511 | 2304464 | 133 | Distribution Circuit | Equipment Failure/Involved | Underground | 6 | 798 | 37.0324 | -122.0365 | No | Partly Cloudy-Fog;32-90 F | Service conductor | Burned Open | 24-0005851 | UG | Sus | 31680693 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1900950 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | FUSE | 4497 | 20240102 | 659 | 20240102 | 800 | 2304492 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 570 | 36.8725 | -121.5547 | No | Overcast-Fog;32-90 F |  |  | 24-0005883 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1900960 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | INDUSTRIAL ACRES-0415 | 182300415 | TRANSFORMER | 412301849473 | 20240102 | 859 | 20240102 | 1507 | 2304617 | 368 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1472 | 36.6631 | -121.6263 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 24-0005948 | OH | Sus | 46124647 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1901043 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | BUENA VISTA-1103 | 182261103 | FUSE | 5101 | 20240102 | 1335 | 20240102 | 1436 | 2304942 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 126 | 7686 | 36.6533 | -121.6484 | No | Partly Cloudy;32-90 F |  |  | 24-0006129 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1901094 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | BUENA VISTA-1103 | 182261103 | JUMPER | OJ @ CGC 412241149281 | 20240102 | 1442 | 20240102 | 1910 | 2305013 | 268 | Distribution Circuit | Animal | Bird found | 126 | 26687 | 36.6575 | -121.647 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 24-0006174 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1901100 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | OTHER | WIRE DOWN MAINLINE FROM 53217 TWD SOUTH | 20240102 | 1851 | 20240103 | 28 | 2305245 | 337 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2496 | 395178 | 36.9692 | -121.9811 | No | Overcast-Rain;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0006216 | OH | Sus | 46125500 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | Yes | Yes | 1901116 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 5090 | 20240102 | 1912 | 20240103 | 1008 | 2305297 | 896 | Distribution Circuit | Vegetation | Tree - branch fell on line | 435 | 196481 | 36.9804 | -121.892 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 24-0006219 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1901119 | 0 | EPSS Ckt | N | 2024 | A & C PHSE
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | FUSE | 12265 | 20240102 | 1917 | 20240103 | 931 | 2305300 | 854 | Distribution Circuit | Vegetation | Tree - branch fell on line | 72 | 34721 | 36.9588 | -121.9805 | No | Overcast-Rain;32-90 F | Transformer (OH) | Broken | 24-0006301 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1901200 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2102 | 182222102 | RECLOSER | 2650 | 20240102 | 1919 | 20240103 | 1104 | 2305320 | 945 | Distribution Circuit | Equipment Failure/Involved | Overhead | 769 | 98585 | 36.6182 | -121.8424 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Together | 24-0006227 | OH | Sus | 46125267 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1901127 | 0 | EPSS Ckt | N | 2024 | A-B
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6643 | 20240102 | 1921 | 20240103 | 305 | 2305318 | 464 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 14384 | 36.9998 | -121.7972 | No | Partly Cloudy-Fog-Heavy Rain;32-90 F |  |  | 24-0006304 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1901203 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 5529 | 20240102 | 1928 | 20240102 | 2350 | 2305390 | 262 | Distribution Circuit | Vegetation | Tree - bark fell into line | 329 | 86198 | 36.9879 | -121.9467 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0006276 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1901172 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 40321 | 20240102 | 2011 | 20240102 | 2221 | 2305432 | 130 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 3380 | 36.6039 | -121.9501 | No | Overcast-Rain;32-90 F |  |  | 24-0006277 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1901173 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | RECLOSER | 12594 | 20240102 | 2154 | 20240103 | 138 | 2305509 | 224 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4187 | 29743 | 36.9652 | -121.9741 | No | Overcast-Drizzle;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0006271 | OH | Sus | 31680777 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1901166 | 0 | Non-EPSS | N | 2024 | N/A
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 12565 | 20240102 | 2231 | 20240103 | 651 | 2305537 | 500 | Distribution Circuit | Vegetation | Tree - bark fell into line | 8 | 4000 | 36.9909 | -122.0176 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0006283 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1901180 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SOLEDAD-2105 | 182052105 | JUMPER | 7913 C PHASE OPEN BURNT OPEN JPR | 20240102 | 2237 | 20240103 | 250 | 2305591 | 253 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1012 | 36.4893 | -121.4205 | No | Partly Cloudy-Fog-Heavy Rain;32-90 F | Jumper | Burned Open | 24-0006290 | OH | Sus | 46125269 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1901187 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2102 | 182222102 | TRANSFORMER | 411671148143 | 20240102 | 2303 | 20240103 | 235 | 2305498 | 212 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 848 | 36.6215 | -121.8397 | No | Overcast-Heavy Rain;32-90 F | Cutout- fuse holder | Broken | 24-0006284 | OH | Sus | 31680655 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1901181 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | JUMPER | 5529 HIGH SIDE CNTR PHASE OPEN JMPR | 20240103 | 14 | 20240103 | 710 | 2305608 | 416 | Distribution Circuit | Equipment Failure/Involved | Overhead | 329 | 136864 | 36.9879 | -121.9466 | No | Overcast-Drizzle;32-90 F | Jumper | Burned Open | 24-0006298 | OH | Sus | 46125423 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1901197 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 24399 | 20240103 | 706 | 20240103 | 906 | 2305740 | 120 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 1800 | 36.8231 | -121.6696 | No | Clear;32-90 F |  |  | 24-0006377 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1901289 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1107 | 182011107 | TRANSFORMER | T1444 | 20240103 | 913 | 20240103 | 1916 | 2306173 | 591 | Distribution Circuit | Equipment Failure/Involved | Underground | 12 | 7092 | 36.6651 | -121.6412 | No | Overcast-Drizzle;32-90 F | Transformer (UG) | Broken | 24-0006419 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1901329 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | TRANSFORMER | 316355814984 | 20240103 | 915 | 20240103 | 1045 | 2306151 | 90 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 990 | 36.9048 | -121.7473 | No | Partly Cloudy-Drizzle;32-90 F | Crossarm- Wood | Broken | 24-0006373 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1901283 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | BORONDA-1101 | 182461101 | TRANSFORMER | 412148050590 | 20240103 | 923 | 20240103 | 1624 | 2306184 | 421 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1263 | 36.6927 | -121.6797 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0006450 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1901340 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | BORONDA-1101 | 182461101 | TRANSFORMER | 412148250609 | 20240103 | 1013 | 20240103 | 1637 | 2306257 | 384 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 384 | 36.6932 | -121.6797 | No | Overcast-Drizzle;32-90 F | Transformer | Failed/Faulted | 24-0006456 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1901345 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 370732 | 20240103 | 1050 | 20240103 | 2148 | 2306296 | 658 | Distribution Circuit | Vegetation | Tree - fell into line | 430 | 120611 | 37.0534 | -122.0438 | No | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0006443 | OH | Sus | 46127742 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1901338 | 0 | EPSS Ckt | N | 2024 | AB
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | JUMPER | OJ 2685 | 20240103 | 1055 | 20240103 | 1540 | 2306299 | 285 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 10545 | 37.0285 | -121.8626 | No | Partly Cloudy-Drizzle;32-90 F | Jumper | Burned Open | 24-0006550 | OH | Sus | 46128223 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1901378 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | BUENA VISTA-1106 | 182261106 | TRANSFORMER | 412431048320 | 20240103 | 1242 | 20240103 | 1920 | 2306412 | 398 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 796 | 36.633 | -121.5805 | No | Partly Cloudy-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 24-0006538 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1901376 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411943353360 | 20240103 | 1320 | 20240103 | 1640 | 2306383 | 200 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 2000 | 36.7678 | -121.7519 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0006518 | OH | Sus | 46127598 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1901363 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | TRANSFORMER | 412323351621 | 20240103 | 1337 | 20240103 | 2318 | 2306460 | 581 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1743 | 36.7229 | -121.621 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0006597 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1901390 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | TRANSFORMER | 411764744614 | 20240103 | 1433 | 20240104 | 52 | 2306510 | 619 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1238 | 36.5252 | -121.8045 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0006606 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1901393 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | TRANSFORMER | 412218550112 | 20240103 | 1617 | 20240104 | 138 | 2306746 | 561 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 2244 | 36.6802 | -121.6552 | No | Overcast;32-90 F | Service conductor | Broken | 24-0006677 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1901437 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 6999 | 20240103 | 2127 | 20240104 | 301 | 2306715 | 334 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 4715 | 36.4908 | -121.9382 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0006674 | OH | Sus | 31680993 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1901433 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 1699 | 20240104 | 550 | 20240104 | 1206 | 2306770 | 376 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 3384 | 36.9707 | -121.797 | No | Fog;32-90 F | Conductor- Overhead | Together | 24-0006792 | OH | Sus | 46129363 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1901568 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 79469 | 20240104 | 1800 | 20240105 | 623 | 2307423 | 743 | Distribution Circuit | 3rd Party | Vehicle | 233 | 25467 | 36.7675 | -121.7532 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0007099 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1901658 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 4809 | 20240104 | 2150 | 20240105 | 805 | 2307474 | 605 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 17951 | 36.9782 | -121.9891 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Deteriorated | 24-0007111 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1901666 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 12549 | 20240104 | 2304 | 20240105 | 645 | 2307533 | 461 | Distribution Circuit | 3rd Party | Vehicle | 5 | 2305 | 36.938 | -121.7522 | No | Fog;32-90 F | Pole-Wood | Broken- wire on ground | 24-0007147 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1901700 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 8983 | 20240105 | 927 | 20240105 | 1908 | 2307767 | 581 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 19208 | 37.0307 | -122.1429 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0007359 | OH | Sus | 31681066 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1901857 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | TRANSFORMER | 412826255973 | 20240105 | 1706 | 20240106 | 958 | 2308146 | 1012 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2024 | 36.8451 | -121.4532 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0007537 | OH | Sus | 35521644 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1901924 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRANSFORMER | 315316024209 | 20240105 | 2102 | 20240106 | 1057 | 2308235 | 835 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 835 | 37.1531 | -122.1082 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0007547 | OH | Sus | 35521645 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1901931 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 1109 | 20240105 | 2326 | 20240106 | 1250 | 2308329 | 804 | Distribution Circuit | Equipment Failure/Involved | Underground | 8 | 6432 | 37.0103 | -121.9903 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0007555 | UG | Sus | 46131895 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1901938 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | TRANSFORMER | 411385746160 | 20240106 | 602 | 20240106 | 1324 | 2308383 | 442 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 884 | 36.5649 | -121.9353 | No | Partly Cloudy;32-90 F |  |  | 24-0007583 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1901976 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | JUMPER | 3048 | 20240106 | 1526 | 20240106 | 1942 | 2308840 | 256 | Distribution Circuit | Equipment Failure/Involved | Overhead | 183 | 46604 | 36.8037 | -121.7623 | No | Overcast;32-90 F | Jumper | Burned Open | 24-0007657 | OH | Sus | 46131919 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1902029 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | RECLOSER | 88772 | 20240106 | 1616 | 20240107 | 537 | 2308888 | 801 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1255 | 134269 | 36.904 | -121.6085 | No | Overcast-Heavy Rain;32-90 F | Crossarm- Wood | Broken | 24-0007663 | OH | Sus | 31681094 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | No | No | 1902034 | 0 | EPSS Ckt | N | 2024 | ABC PHASE
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 681 | 20240106 | 1621 | 20240107 | 39 | 2308892 | 498 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3984 | 36.8616 | -121.6581 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0007668 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1902039 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 2765 | 20240106 | 1740 | 20240106 | 1918 | 2308945 | 98 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 24 | 2352 | 36.5574 | -121.9253 | No | Overcast-Rain;32-90 F | Fuse | Burned Open | 24-0007679 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1902050 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | TRANSFORMER | 411405247575 | 20240106 | 2010 | 20240107 | 1215 | 2309003 | 965 | Transformer only | Vegetation | Tree - fell into line | 8 | 7720 | 36.604 | -121.9303 | No | Partly Cloudy;32-90 F | Secondary | On Ground | 24-0007684 | OH | Sus | 31681120 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1902055 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | SWITCH | 12543 | 20240106 | 2140 | 20240106 | 2242 | 2309018 | 62 | Distribution Circuit | Equipment Failure/Involved | Overhead | 428 | 26536 | 36.9652 | -122.0159 | No | Partly Cloudy;32-90 F | Switch (OH) | Burned/flashed | 24-0007675 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1902080 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 9357 | 20240107 | 858 | 20240107 | 1147 | 2309122 | 169 | Distribution Circuit | 3rd Party | Vehicle | 1 | 169 | 36.9185 | -121.4055 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0007737 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1902111 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1103 | 182381103 | TRANSFORMER | T74702 | 20240107 | 1027 | 20240107 | 1844 | 2309149 | 497 | Transformer only | Equipment Failure/Involved | Underground | 7 | 3479 | 36.7981 | -121.7859 | No | Clear;32-90 F | Splice box | Deteriorated | 24-0007743 | UG | Sus | 46132101 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1902118 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 7893 | 20240107 | 1030 | 20240107 | 1401 | 2309171 | 211 | Distribution Circuit | Equipment Failure/Involved | Overhead | 93 | 5403 | 36.9152 | -121.7493 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0007742 | OH | Sus | 31681181 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | Yes | Yes | 1902117 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | TRANSFORMER | T0315 | 20240107 | 1800 | 20240108 | 1818 | 2309313 | 1458 | Distribution Circuit | Equipment Failure/Involved | Underground | 166 | 38709 | 36.563 | -121.7372 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0007795 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1902157 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2103 | 83252103 | FUSE | 11763 | 20240107 | 1856 | 20240107 | 2050 | 2309340 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 88 | 10060 | 36.9769 | -122.016 | No | Clear;32-90 F |  |  | 24-0007787 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1902149 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 3889 | 20240108 | 843 | 20240108 | 1220 | 2309541 | 217 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 15190 | 36.9487 | -121.8523 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0007859 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1902219 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411905152896 | 20240108 | 928 | 20240108 | 2015 | 2309673 | 647 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 647 | 36.7541 | -121.7647 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0007929 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1902345 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | TRANSFORMER | 411785750174 | 20240108 | 1112 | 20240108 | 1433 | 2309719 | 201 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 2211 | 36.6786 | -121.8031 | No | Partly Cloudy;32-90 F | Transformer | Deteriorated | 24-0007951 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1902357 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | FUSE | 5913 | 20240108 | 1118 | 20240109 | 132 | 2309805 | 854 | Distribution Circuit | Equipment Failure/Involved | Overhead | 88 | 53228 | 36.7303 | -121.6406 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 24-0007991 | OH | Sus | 46133115 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1902372 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2107 | 182402107 | TRANSFORMER | 411827050478 | 20240108 | 1614 | 20240108 | 1625 | 2310059 | 11 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 132 | 36.6872 | -121.7894 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0008184 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1902420 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1105 | 182011105 | TRANSFORMER | T0864 | 20240108 | 1935 | 20240109 | 1755 | 2310193 | 1340 | Distribution Circuit | Equipment Failure/Involved | Underground | 160 | 6587 | 36.7066 | -121.652 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0008242 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1902455 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1112 | 182371112 | JUMPER | OJS @ 7041 | 20240108 | 2353 | 20240109 | 518 | 2310222 | 325 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 975 | 36.5086 | -121.7655 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0008244 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1902460 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | TRANSFORMER | 412424756998 | 20240109 | 32 | 20240109 | 839 | 2310223 | 487 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 974 | 36.8712 | -121.5913 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0008247 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1902463 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 6137 | 20240109 | 48 | 20240109 | 417 | 2310226 | 209 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 120 | 24440 | 36.5945 | -121.8932 | No | Partly Cloudy;32-90 F |  |  | 24-0008248 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1902464 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | TRANSFORMER | 315220521539 | 20240109 | 1031 | 20240109 | 1817 | 2310560 | 466 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 2724 | 37.08 | -122.1396 | No | Overcast;32-90 F | Transformer (OH) | Deteriorated | 24-0008378 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1902652 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | TRANSFORMER | 412516155313 | 20240109 | 1359 | 20240109 | 1700 | 2310937 | 181 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 362 | 36.826 | -121.5581 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0008556 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1902698 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | FUSE | 5111 | 20240109 | 1438 | 20240109 | 1652 | 2310296 | 134 | Distribution Circuit | 3rd Party | Vehicle | 9 | 1206 | 36.6754 | -121.678 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0008562 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1902699 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | RECLOSER | 3034 | 20240109 | 1617 | 20240109 | 1724 | 2311035 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 40 | 2680 | 36.7317 | -121.6129 | No | Overcast-Rain;32-90 F |  |  | 24-0008651 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1902710 | 0 | EPSS Ckt | N | 2024 | AB
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 7723 | 20240109 | 1639 | 20240109 | 1900 | 2311073 | 141 | Distribution Circuit | Animal | Other | 1 | 94 | 36.5852 | -121.7531 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 24-0008697 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1902722 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1101 | 182131101 | RECLOSER | 65704 | 20240109 | 1654 | 20240110 | 350 | 2311061 | 656 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 7695 | 36.5271 | -121.4178 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0008682 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1902715 | 0 | EPSS Ckt | N | 2024 | A GRD
CENTRAL COAST | KING CITY | LOS COCHES-1102 | 182151102 | TRANSFORMER | 413310838465 | 20240110 | 818 | 20240110 | 1654 | 2311390 | 516 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1032 | 36.3681 | -121.2728 | No | Partly Cloudy-Fog-Drizzle;32-90 F | Transformer | Failed/Faulted | 24-0008853 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1902899 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 11797 | 20240110 | 1030 | 20240110 | 1243 | 2311086 | 133 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 1995 | 36.8677 | -121.7087 | No | Clear;32-90 F | Service conductor | Deteriorated | 24-0008863 | OH | Sus | 46134918 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1902922 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | TRANSFORMER | 412660543243 | 20240110 | 1603 | 20240110 | 1617 | 2311950 | 14 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 42 | 36.4945 | -121.4973 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 24-0009246 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1903050 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 2549 | 20240110 | 2137 | 20240110 | 2242 | 2312405 | 65 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 975 | 36.6017 | -121.9537 | No | Overcast;32-90 F |  |  | 24-0009359 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1903122 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1112 | 182371112 | FUSE | 78521 | 20240110 | 2210 | 20240111 | 1315 | 2312444 | 905 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 17195 | 36.5075 | -121.7536 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0009380 | OH | Sus | 46140996 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1903132 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2107 | 182402107 | TRANSFORMER | T0957 | 20240110 | 2316 | 20240111 | 257 | 2312448 | 221 | Transformer only | Equipment Failure/Involved | Overhead | 46 | 10166 | 36.6867 | -121.7961 | No | Clear;32-90 F | Connector or Splice (OH) | Arcing | 24-0009364 | OH | Sus | 46141096 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1903123 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ERTA SUB | 8351 | OCB | 404/2 | 20240111 | 313 | 20240111 | 1029 | 2312601 | 436 | Distribution Circuit | Equipment Failure/Involved | Overhead | 779 | 103460 | 36.9307 | -121.7642 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0009405 | OH | Sus | 31681562 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1903157 | 0 | Non-EPSS | N | 2024 | GRD
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | SWITCH | 2600 | 20240111 | 327 | 20240111 | 503 | 2312604 | 95 | Distribution Circuit | Equipment Failure/Involved | Underground | 299 | 17997 | 36.5858 | -121.8888 | No | Partly Cloudy;32-90 F | Elbow | Burned/flashed | 24-0000635 | UG | Sus | 35396128 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | No | No | 1903147 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 9659 | 20240111 | 606 | 20240111 | 757 | 2312629 | 111 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 43 | 4773 | 36.9746 | -122.0591 | No | Clear;32-90 F |  |  | 24-0009451 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1903191 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | JUMPER | OJ 1 W/OF CGC# 316312019090 | 20240111 | 1421 | 20240111 | 2140 | 2313155 | 439 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1317 | 37.0183 | -121.7654 | No | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0009773 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1903402 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1108 | 182011108 | TRANSFORMER | 412249650013 | 20240112 | 953 | 20240112 | 1126 | 2313776 | 93 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 930 | 36.6778 | -121.6442 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0010179 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1903651 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | FUSE | 7445 | 20240113 | 815 | 20240113 | 935 | 2314493 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 45 | 3628 | 35.9657 | -121.0819 | No | Clear;32-90 F |  |  | 24-0010432 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1903773 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | TRANSFORMER | T0717 | 20240113 | 2210 | 20240114 | 1252 | 2315110 | 882 | Distribution Circuit | Equipment Failure/Involved | Underground | 49 | 3336 | 36.569 | -121.7455 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0010631 | UG | Sus | 35523800 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1903922 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | FUSE | 3591 | 20240114 | 1050 | 20240114 | 1213 | 2315321 | 83 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 109 | 9024 | 36.5626 | -121.7327 | No | Clear;32-90 F |  |  | 24-0010687 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1903972 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | TRANSFORMER | T0717 | 20240114 | 1336 | 20240114 | 1342 | 2315451 | 6 | Transformer only | Equipment Failure/Involved | Underground | 3 | 18 | 36.569 | -121.7455 | No | Clear;32-90 F | Secondary | Broken | 24-0010631 | UG | Sus | 35523800 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1903977 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 3945 | 20240114 | 1541 | 20240114 | 1718 | 2315481 | 97 | Distribution Circuit | Vegetation | Tree - branch fell on line | 52 | 5044 | 36.8172 | -121.636 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0010723 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1903993 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | KING CITY-1104 | 182031104 | RECLOSER | 549180 | 20240114 | 1733 | 20240114 | 1809 | 2315508 | 36 | Distribution Circuit | Equipment Failure/Involved | Overhead | 525 | 18900 | 36.0057 | -121.2422 | No | Partly Cloudy;32-90 F | Regulator | Malfunctioning | 24-0010724 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1903994 | 0 | EPSS Ckt | N | 2024 | SGF/I
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 3621 | 20240115 | 703 | 20240115 | 920 | 2315650 | 137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 343 | 46991 | 36.7789 | -121.6493 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0010757 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1904022 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 985275 | 20240115 | 735 | 20240115 | 956 | 2315665 | 141 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1269 | 36.8629 | -121.6657 | No | Clear;32-90 F |  |  | 24-0010770 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1904041 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 985275 | 20240115 | 1112 | 20240115 | 1725 | 2315780 | 373 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 3357 | 36.8629 | -121.6657 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0010793 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1904059 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2106 | 182402106 | TRANSFORMER | 411773648688 | 20240115 | 1458 | 20240115 | 1546 | 2315875 | 48 | Transformer only | Unknown Cause | Patrol - found nothing | 6 | 288 | 36.6379 | -121.805 | No | Partly Cloudy;32-90 F |  |  | 24-0010819 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1904074 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 23225 | 20240115 | 1504 | 20240116 | 1432 | 2315874 | 1408 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 1408 | 36.725 | -121.7849 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 24-0010816 | UG | Sus | 35523902 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1904070 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRANSFORMER | 315226324463 | 20240115 | 1557 | 20240115 | 1846 | 2315898 | 169 | Transformer only | Vegetation | Tree - bark fell into line | 5 | 845 | 37.1608 | -122.1365 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0010832 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1904081 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | TRANSFORMER | 315532317535 | 20240115 | 1915 | 20240116 | 222 | 2316009 | 427 | Transformer only | Equipment Failure/Involved | Electrical Overload | 3 | 1281 | 36.9715 | -122.0304 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0010854 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1904102 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | SWITCH | 8451 | 20240116 | 958 | 20240116 | 2136 | 2316378 | 698 | Distribution Circuit | 3rd Party | Vehicle | 396 | 141444 | 37.1463 | -122.1334 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0010950 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1904271 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1101 | 182011101 | TRANSFORMER | 412225049505 | 20240116 | 1524 | 20240116 | 2341 | 2316607 | 497 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 497 | 36.6636 | -121.6523 | No | Overcast;32-90 F | Transformer | Deteriorated | 24-0011232 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1904342 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | KING CITY-1104 | 182031104 | RECLOSER | 549180 | 20240116 | 1612 | 20240116 | 2018 | 2316655 | 246 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 686 | 130438 | 36.0057 | -121.2422 | No | Partly Cloudy;32-90 F |  |  | 24-0011263 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1904349 | 0 | EPSS Ckt | N | 2024 | SGF/INST
CENTRAL COAST | SALINAS | SALINAS-1101 | 182011101 | TRANSFORMER | 412230849539 | 20240116 | 1710 | 20240117 | 222 | 2316779 | 552 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 6072 | 36.6645 | -121.6507 | No | Overcast;32-90 F | Transformer | Broken | 24-0011299 | OH | Sus | 31681923 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1904362 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | SOLEDAD-2105 | 182052105 | TRANSFORMER | 413176740663 | 20240116 | 1958 | 20240116 | 2353 | 2316820 | 235 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 1175 | 36.4276 | -121.3204 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0011318 | OH | Sus | 35524133 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1904380 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 655 | 20240117 | 24 | 20240117 | 145 | 2317202 | 81 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 1782 | 36.8785 | -121.6416 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0011413 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1904436 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | BUENA VISTA-1106 | 182261106 | TRANSFORMER | 412293048164 | 20240117 | 926 | 20240117 | 1351 | 2317533 | 265 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 265 | 36.6276 | -121.6274 | No | Overcast;32-90 F | Transformer | Failed/Faulted | 24-0011552 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1904613 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | OCB | 2102/2 | 20240117 | 927 | 20240117 | 1802 | 2317466 | 515 | Distribution Circuit | Equipment Failure/Involved | Overhead | 233 | 35461 | 36.2938 | -121.1999 | No | Partly Cloudy-Fog;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0011521 | OH | Sus | 31681963 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1904583 | 0 | EPSS Ckt | N | 2024 | A- C- & GRD
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 9601 | 20240117 | 1002 | 20240117 | 1042 | 2317526 | 40 | Distribution Circuit | Animal | Bird found | 25 | 1000 | 36.9112 | -121.3527 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Normal | 24-0011576 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1904621 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 3287 | 20240117 | 1521 | 20240117 | 1624 | 2317882 | 63 | Distribution Circuit | Animal | Bird found | 12 | 756 | 37.001 | -121.9453 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0011831 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1904674 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | FUSE | 4483 | 20240117 | 2119 | 20240118 | 1037 | 2318073 | 798 | Distribution Circuit | Equipment Failure/Involved | Underground | 23 | 18354 | 36.8369 | -121.3824 | No | Fog;32-90 F | Conductor- Underground | Broken | 24-0011925 | UG | Sus | 46164161 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1904714 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | JUMPER | OJ N/OF 8835 | 20240117 | 2151 | 20240118 | 415 | 2318047 | 384 | Distribution Circuit | Animal | Other | 15 | 5760 | 36.4705 | -121.7231 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0011896 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1904693 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 4915 | 20240117 | 2211 | 20240118 | 233 | 2318084 | 262 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 9170 | 37.1032 | -122.0458 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0011918 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1904711 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 40251 | 20240118 | 237 | 20240118 | 558 | 2318154 | 201 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 7910 | 36.2415 | -121.7971 | No | Clear;32-90 F |  |  | 24-0011952 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1904723 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 8097 | 20240118 | 745 | 20240118 | 931 | 2318219 | 106 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 1802 | 37.0785 | -122.139 | No | Clear;32-90 F |  |  | 24-0012050 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1904793 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | TRANSFORMER | 411387948335 | 20240118 | 1218 | 20240118 | 1933 | 2318479 | 435 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1740 | 36.625 | -121.9367 | No | Overcast;32-90 F | Transformer | Failed/Faulted | 24-0012243 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1904841 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | TRANSFORMER | 412314252616 | 20240118 | 1320 | 20240118 | 1830 | 2318506 | 310 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 310 | 36.7499 | -121.6263 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0012203 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1904834 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | RECLOSER | 3018 | 20240118 | 1951 | 20240119 | 136 | 2318746 | 345 | Distribution Circuit | Equipment Failure/Involved | Overhead | 55 | 18975 | 36.6662 | -121.6858 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0012403 | OH | Sus | 31682048 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1904881 | 0 | EPSS Ckt | N | 2024 | B-GRD
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412220655605 | 20240119 | 719 | 20240119 | 1059 | 2318851 | 220 | Transformer only | Equipment Failure/Involved | Electrical Overload | 3 | 660 | 36.8323 | -121.66 | No | Partly Cloudy;32-90 F | Transformer | Normal | 24-0012569 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1905066 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412226055667 | 20240119 | 915 | 20240119 | 1205 | 2318997 | 170 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 170 | 36.8329 | -121.6579 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 24-0012626 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1905085 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 412064850539 | 20240119 | 1131 | 20240119 | 1508 | 2319139 | 217 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 217 | 36.6908 | -121.7078 | No | Clear;32-90 F | Transformer | Broken | 24-0012651 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1905094 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | RECLOSER | 187705 | 20240119 | 1219 | 20240119 | 1313 | 2319189 | 54 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 2 | 108 | 36.3958 | -121.8796 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0006959 | OH | Sus | 31568902 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1905096 | 0 | EPSS Ckt | N | 2024 | A & B
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 3567 | 20240119 | 1910 | 20240120 | 1424 | 2319436 | 1154 | Distribution Circuit | 3rd Party | Vehicle | 181 | 79501 | 36.8799 | -121.6939 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0012805 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | No | No | 1905142 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | TRANSFORMER | 411665044858 | 20240119 | 2206 | 20240120 | 942 | 2319491 | 696 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 2088 | 36.5317 | -121.839 | No | Overcast-Drizzle;32-90 F | Transformer | Deteriorated | 24-0012845 | OH | Sus | 35525251 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1905181 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 8491 | 20240119 | 2252 | 20240120 | 1406 | 2319497 | 914 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 75862 | 37.056 | -121.9974 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0012883 | OH | Sus | 31682038 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1905211 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 3583 | 20240120 | 739 | 20240120 | 1422 | 2319674 | 403 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 5642 | 37.1389 | -122.1011 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0012906 | OH | Sus | 31682039 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1905244 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | TRANSFORMER | 411837449917 | 20240120 | 1113 | 20240120 | 1206 | 2319872 | 53 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 954 | 36.672 | -121.7852 | No | Overcast-Drizzle;32-90 F | Fuse | Broken | 24-0012952 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1905262 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2103 | 83252103 | TRANSFORMER | 315595017909 | 20240120 | 1250 | 20240120 | 2142 | 2319925 | 532 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 5320 | 36.9818 | -122.0082 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 24-0012980 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1905271 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 3677 | 20240120 | 1318 | 20240120 | 1602 | 2319946 | 164 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 656 | 37.0644 | -121.9846 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0012989 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1905275 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 6081 | 20240120 | 1406 | 20240121 | 144 | 2319980 | 698 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 3849 | 37.0577 | -122.0333 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0012988 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1905274 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | TRES PINOS-1111 | 183221111 | TRANSFORMER | 413172054380 | 20240120 | 1559 | 20240120 | 2344 | 2320033 | 465 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 930 | 36.8047 | -121.3344 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0012993 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1905278 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 5215 | 20240120 | 1627 | 20240121 | 145 | 2320055 | 558 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 33480 | 37.0325 | -122.0765 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0012999 | OH | Sus | 46166313 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1905281 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | RECLOSER | 5470 | 20240121 | 18 | 20240121 | 1211 | 2320243 | 713 | Distribution Circuit | Vegetation | Tree - fell into line | 1259 | 354867 | 36.878 | -121.7472 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 24-0013039 | OH | Sus | 46166382 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1905312 | 0 | EPSS Ckt | N | 2024 | B-C
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | RECLOSER | 974130 | 20240121 | 320 | 20240121 | 1400 | 2320260 | 640 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 57408 | 37.0448 | -121.9382 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0013048 | OH | Sus | 46166443 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1905318 | 0 | EPSS Ckt | N | 2024 | A PHASE & GRD INST
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 5213 | 20240121 | 515 | 20240121 | 1708 | 2320273 | 713 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 36363 | 37.0324 | -122.0768 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken | 24-0013064 | OH | Sus | 46168854 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1905333 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | RECLOSER | 57184 | 20240121 | 616 | 20240121 | 1145 | 2320274 | 329 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 2632 | 36.7916 | -121.722 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0013054 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1905324 | 0 | EPSS Ckt | N | 2024 | N/A
CENTRAL COAST | MONTEREY | FORT ORD-2105 | 182402105 | TRANSFORMER | 411762249583 | 20240121 | 722 | 20240121 | 1230 | 2320296 | 308 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 616 | 36.6623 | -121.8097 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Broken | 24-0013088 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1905352 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | TRANSFORMER | 315503617112 | 20240121 | 748 | 20240121 | 1642 | 2320346 | 534 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 4806 | 36.9591 | -122.0387 | No | Overcast-Fog-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0013070 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1905340 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRANSFORMER | 315151925569 | 20240121 | 1041 | 20240121 | 1428 | 2320395 | 227 | Transformer only | Equipment Failure/Involved | Electrical Overload | 4 | 908 | 37.1895 | -122.1656 | No | Clear;32-90 F | Secondary | Broken | 24-0013102 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1905364 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 4251 | 20240121 | 1115 | 20240121 | 1513 | 2320393 | 238 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 952 | 36.9945 | -121.8533 | No | Partly Cloudy-Fog;32-90 F | Insulator | Broken | 24-0013086 | OH | Sus | 46166422 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1905350 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | BORONDA-1102 | 182461102 | TRANSFORMER | 412126050416 | 20240121 | 1400 | 20240121 | 2102 | 2320406 | 422 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1266 | 36.6874 | -121.6876 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0013104 | OH | Sus | 35525345 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1905365 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | TRANSFORMER | 315515720677 | 20240121 | 1624 | 20240121 | 1934 | 2320546 | 190 | Transformer only | Vegetation | Tree - fell into line | 1 | 190 | 37.0579 | -122.0374 | No | Clear;32-90 F | Transformer | Broken | 24-0013122 | OH | Sus | 46169808 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1905376 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 3233 | 20240121 | 2039 | 20240122 | 1027 | 2320692 | 828 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 32292 | 37.0325 | -122.0628 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0013170 | OH | Sus | 46166397 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1905418 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 1429 | 20240121 | 2144 | 20240122 | 445 | 2320730 | 421 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 42 | 17682 | 37.0831 | -122.0942 | No | Clear;32-90 F |  |  | 24-0013189 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1905438 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 287578 | 20240122 | 6 | 20240122 | 1044 | 2320804 | 638 | Distribution Circuit | Vegetation | Tree - branch fell on line | 213 | 6726 | 37.0438 | -122.0755 | No | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0013168 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | No | No | 1905416 | 0 | EPSS Ckt | N | 2024 | ABC TIME
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | TRANSFORMER | 315626218214 | 20240122 | 129 | 20240122 | 446 | 2320833 | 197 | Transformer only | Vegetation | Tree - fell into line | 8 | 1576 | 36.9905 | -121.9978 | No | Overcast-Heavy Rain-Fog;32-90 F | Secondary | Broken- wire on ground | 24-0013177 | OH | Sus | 31682304 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1905425 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5225 | 20240122 | 144 | 20240122 | 1441 | 2320839 | 777 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 6993 | 37.0496 | -122.0856 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0013186 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1905435 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 5459 | 20240122 | 222 | 20240122 | 1350 | 2320861 | 688 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 15232 | 37.1385 | -122.1432 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0013285 | OH | Sus | 31682208 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1905493 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 75993 | 20240122 | 222 | 20240122 | 422 | 2320866 | 118 | Distribution Circuit | Vegetation | Tree - bark fell into line | 92 | 10856 | 36.9799 | -122.0316 | No | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0013181 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1905430 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 11943 | 20240122 | 239 | 20240122 | 1237 | 2320875 | 598 | Distribution Circuit | Vegetation | Tree - branch fell on line | 79 | 47242 | 37.0112 | -122.0442 | No | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0013217 | OH | Sus | 31682206 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1905457 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 10457 | 20240122 | 451 | 20240122 | 1940 | 2320912 | 889 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 9769 | 37.1086 | -122.0459 | No | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0013451 | OH | Sus | 46170437 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1905591 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 52559 | 20240122 | 742 | 20240122 | 905 | 2321023 | 83 | Distribution Circuit | Animal | Bird found | 10 | 830 | 36.8343 | -121.6603 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 24-0013295 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1905508 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2107 | 182402107 | FUSE | 6423 | 20240122 | 846 | 20240122 | 1225 | 2321095 | 219 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 3285 | 36.6874 | -121.7961 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0013337 | OH | Sus | 46170232 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1905541 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1102 | 182011102 | TRANSFORMER | T1113 | 20240122 | 923 | 20240122 | 1710 | 2321178 | 467 | Distribution Circuit | Equipment Failure/Involved | Underground | 26 | 12142 | 36.6871 | -121.611 | No | Overcast-Rain;32-90 F | Transformer (UG) | Failed/Faulted | 24-0013353 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1905545 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | JUMPER | WIRE DOWN | 20240122 | 926 | 20240122 | 2240 | 2321596 | 794 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 9051 | 37.0407 | -122.0655 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0013537 | OH | Sus | 46170543 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | Yes | Yes | 1905618 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | JUMPER | OJ AT CGC 315820018680 | 20240122 | 1155 | 20240122 | 1606 | 2321373 | 251 | Distribution Circuit | Vegetation | Tree - grew into line | 9 | 2259 | 37.004 | -121.9325 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0013415 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1905573 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2101 | 182492101 | FUSE | 266281 | 20240122 | 1305 | 20240122 | 1358 | 2321443 | 53 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 424 | 36.8312 | -121.4353 | No | Partly Cloudy;32-90 F |  |  | 24-0013490 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1905602 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | TRANSFORMER | 413571035130 | 20240122 | 1747 | 20240123 | 546 | 2321730 | 719 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 1438 | 36.2773 | -121.1831 | No | Partly Cloudy;32-90 F | Transformer | Leaking | 24-0013607 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1905638 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2107 | 182402107 | TRANSFORMER | 411850250112 | 20240122 | 1826 | 20240123 | 135 | 2321788 | 429 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 6864 | 36.677 | -121.7812 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0013617 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1905645 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1102 | 182201102 | TRANSFORMER | 412596948452 | 20240122 | 1957 | 20240123 | 254 | 2321844 | 417 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 417 | 36.6372 | -121.5246 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0013644 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1905669 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412268055525 | 20240122 | 2041 | 20240123 | 308 | 2321854 | 387 | Transformer only | Equipment Failure/Involved | Electrical Overload | 6 | 2322 | 36.8297 | -121.6435 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0013642 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1905665 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | OTHER | WIRE DOWN 1 LD SIDE OF CGC 316084518041 | 20240122 | 2234 | 20240123 | 1411 | 2321882 | 937 | Distribution Circuit | Vegetation | Tree - fell into line | 2394 | 248442 | 36.9877 | -121.841 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0013646 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1905671 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 8021 | 20240123 | 133 | 20240123 | 401 | 2321910 | 148 | Distribution Circuit | Vegetation | Tree - branch fell on line | 85 | 12580 | 36.5868 | -121.9097 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 24-0013674 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1905680 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | TRANSFORMER | 413070551833 | 20240123 | 614 | 20240123 | 1034 | 2321967 | 260 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 260 | 36.7347 | -121.3679 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0013723 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1905711 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | RECLOSER | 281712 | 20240123 | 1143 | 20240123 | 1153 | 2322227 | 10 | Distribution Circuit | Equipment Failure/Involved | Overhead | 57 | 570 | 36.8038 | -121.4072 | No | Partly Cloudy;32-90 F | Regulator | Malfunctioning | 24-0013878 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1905858 | 0 | EPSS Ckt | N | 2024 | N/A
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | JUMPER | FB 2 S/OF CGC315684018185 | 20240123 | 1348 | 20240123 | 1933 | 2322460 | 345 | Distribution Circuit | 3rd Party | Vehicle | 82 | 28290 | 36.9908 | -121.9785 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0013780 | OH | Sus | 35525665 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1905881 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315637421066 | 20240123 | 2336 | 20240124 | 1450 | 2322690 | 914 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 10968 | 37.069 | -121.9964 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0014153 | OH | Sus | 35525779 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1905947 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2108 | 83252108 | FUSE | 80061 | 20240124 | 154 | 20240124 | 738 | 2322714 | 344 | Distribution Circuit | Animal | Bird found | 17 | 5848 | 36.9867 | -121.9963 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 24-0014154 | OH | Sus | 35525941 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1905948 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8541 | 20240124 | 321 | 20240124 | 1447 | 2322737 | 686 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 59682 | 37.0684 | -121.9969 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0014158 | OH | Sus | 31682278 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1905952 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 4563 | 20240124 | 953 | 20240124 | 1105 | 2323002 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 1656 | 36.7259 | -121.6536 | No | Partly Cloudy-Fog-Rain;32-90 F |  |  | 24-0014370 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1906061 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 316188216799 | 20240124 | 1329 | 20240125 | 212 | 2323205 | 763 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 763 | 36.9535 | -121.8053 | No | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0014617 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1906109 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 411986554465 | 20240124 | 1420 | 20240124 | 2214 | 2323247 | 474 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 474 | 36.7978 | -121.7386 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0014585 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1906104 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8961 | 20240124 | 1526 | 20240125 | 1230 | 2323306 | 1264 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 2518 | 37.0432 | -122.0518 | No | Overcast;32-90 F |  |  | 24-0014671 | OH | Sus | 46171542 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1906111 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | TRIP-SAVER | 3959 | 20240124 | 1608 | 20240124 | 1749 | 2323339 | 101 | Distribution Circuit | Vegetation | Tree - bark fell into line | 375 | 32175 | 36.959 | -122.0316 | No | Overcast;32-90 F | Cutout- fuse holder | Normal | 24-0014680 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1906115 | 0 | EPSS Ckt | N | 2024 | A-B
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 4213 | 20240124 | 1703 | 20240124 | 2113 | 2323364 | 250 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 9250 | 36.9756 | -121.884 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 24-0014674 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1906112 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | TRANSFORMER | 315859517673 | 20240124 | 2217 | 20240125 | 1200 | 2323512 | 823 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 8230 | 36.9766 | -121.9185 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0014756 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1906157 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | SWITCH | 2683 | 20240124 | 2337 | 20240125 | 230 | 2323523 | 173 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 19722 | 37.001 | -121.8996 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 24-0014755 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1906156 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 7007 | 20240124 | 2349 | 20240125 | 1057 | 2323540 | 668 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 9601 | 36.6019 | -121.9341 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0014795 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1906166 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | TRANSFORMER | MTR#1008267195 | 20240125 | 703 | 20240125 | 1332 | 2323608 | 389 | Transformer only | Vegetation | Tree - fell into line | 2 | 778 | 36.8932 | -121.5912 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0014889 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1906224 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | TRANSFORMER | 315592220038 | 20240125 | 725 | 20240125 | 901 | 2323647 | 96 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 288 | 37.04 | -122.0111 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0014911 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1906257 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | KING CITY-1106 | 182031106 | RECLOSER | 666728 | 20240125 | 809 | 20240125 | 1032 | 2323733 | 143 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 143 | 36.1764 | -121.0321 | No | Partly Cloudy-Fog-Drizzle;32-90 F | Recloser | Malfunctioning | 24-0014886 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1906216 | 0 | EPSS Ckt | N | 2024 | NONE
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0424 | 182440424 | JUMPER | OJ @ 10335 | 20240125 | 947 | 20240125 | 1606 | 2323876 | 379 | Distribution Circuit | Equipment Failure/Involved | Overhead | 106 | 40174 | 36.6248 | -121.9193 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0014934 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1906308 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 4503 | 20240125 | 1057 | 20240125 | 1345 | 2324005 | 168 | Distribution Circuit | Animal | Bird found | 84 | 14119 | 36.7321 | -121.6559 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 24-0015182 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1906420 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2101 | 182492101 | FUSE | 266281 | 20240125 | 1206 | 20240125 | 1338 | 2324080 | 92 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 736 | 36.8312 | -121.4353 | No | Partly Cloudy;32-90 F |  |  | 24-0015172 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1906415 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315667122569 | 20240125 | 1532 | 20240126 | 318 | 2324183 | 706 | Transformer only | Vegetation | Tree - fell into line | 1 | 706 | 37.1103 | -121.987 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0015274 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1906436 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 6083 | 20240125 | 1749 | 20240126 | 416 | 2324311 | 627 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 39013 | 37.0585 | -122.0334 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0015329 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1906449 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2106 | 182402106 | RECLOSER | 9138 | 20240126 | 948 | 20240126 | 1025 | 2324740 | 37 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 460 | 17020 | 36.6413 | -121.8077 | No | Partly Cloudy;32-90 F | Recloser | Normal | 24-0008401 | OH | Sus | 35466089 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1906660 | 0 | EPSS Ckt | N | 2024 | SGF
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRANSFORMER | 315151925569 | 20240126 | 1322 | 20240126 | 1523 | 2325060 | 121 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 484 | 37.1895 | -122.1656 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0015652 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1906703 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | TRANSFORMER | 315937017450 | 20240126 | 1348 | 20240126 | 2125 | 2325083 | 457 | Distribution Circuit | Vegetation | Tree - branch fell on line | 49 | 9373 | 36.9707 | -121.8905 | No | Overcast;32-90 F | Secondary | Normal | 24-0015741 | OH | Sus | 46173432 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1906726 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1105 | 182011105 | OTHER | J385 TWD T2118 | 20240126 | 1409 | 20240126 | 2350 | 2325098 | 581 | Distribution Circuit | Equipment Failure/Involved | Underground | 65 | 32683 | 36.7109 | -121.6445 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0015685 | UG | Sus | 35526579 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1906711 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1105 | 182011105 | TRANSFORMER | T0366 | 20240126 | 1607 | 20240127 | 1608 | 2325179 | 1441 | Distribution Circuit | Equipment Failure/Involved | Underground | 72 | 40212 | 36.7066 | -121.6292 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0015762 | UG | Sus | 35526664 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1906740 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 11555 | 20240127 | 654 | 20240127 | 1309 | 2325386 | 375 | Distribution Circuit | Equipment Failure/Involved | Overhead | 81 | 10235 | 36.865 | -121.7224 | No | Overcast;32-90 F | Transformer (OH) | Burned/flashed | 24-0015819 | OH | Sus | 31682474 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1906801 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6655 | 20240127 | 709 | 20240127 | 946 | 2325390 | 157 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1256 | 36.9875 | -121.801 | No | Clear;32-90 F |  |  | 24-0015831 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1906831 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2102 | 182222102 | FUSE | 6101 | 20240127 | 840 | 20240127 | 918 | 2325446 | 38 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 3253 | 52814 | 36.6076 | -121.852 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 24-0015823 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1906814 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 6895 | 20240127 | 1139 | 20240127 | 1548 | 2325582 | 249 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 166 | 36.8382 | -121.7668 | No | Clear;32-90 F |  |  | 24-0015885 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1906864 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 65444 | 20240127 | 1258 | 20240128 | 36 | 2325627 | 698 | Distribution Circuit | Vegetation | Tree - branch fell on line | 143 | 8470 | 37.1278 | -122.1229 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 24-0015861 | OH | Sus | 35526418 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1906853 | 0 | EPSS Ckt | N | 2024 | AC GRD
CENTRAL COAST | COAST | PAUL SWEET-2108 | 83252108 | FUSE | 4469 | 20240127 | 1349 | 20240127 | 1754 | 2325643 | 245 | Distribution Circuit | Animal | Bird found | 32 | 7832 | 36.9788 | -122.0097 | No | Overcast;32-90 F | Transformer (OH) | Normal | 24-0015897 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1906867 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | TRANSFORMER | 316322315546 | 20240127 | 1834 | 20240127 | 1948 | 2325731 | 74 | Transformer only | Unknown Cause | Patrol - found nothing | 10 | 740 | 36.9201 | -121.7591 | No | Clear;32-90 F |  |  | 24-0015904 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1906868 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | JUMPER | OJ CGC 316253215660 | 20240128 | 1347 | 20240128 | 2017 | 2326399 | 390 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 8190 | 36.9228 | -121.7829 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0015966 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1906930 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | TRANSFORMER | 411814050632 | 20240128 | 1510 | 20240129 | 5 | 2326446 | 535 | Transformer only | Equipment Failure/Involved | Overhead | 19 | 10165 | 36.6915 | -121.7939 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0015995 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1906939 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316404517060 | 20240128 | 1658 | 20240129 | 1125 | 2326631 | 1107 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2214 | 36.962 | -121.7318 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0016014 | OH | Sus | 35526787 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1906956 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | RECLOSER | 4060 | 20240128 | 1739 | 20240128 | 1841 | s1906947 | 62 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1004 | 62248 | 36.801 | -121.3379 | No | Clear;32-90 F |  |  | 24-0016001 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1906947 | 0 | EPSS Ckt | N | 2024 | GRD
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 281488 | 20240128 | 1915 | 20240128 | 2002 | 2326619 | 45 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 90 | 36.8612 | -121.4349 | No | Clear;32-90 F |  |  | 24-0016009 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1906951 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | TRANSFORMER | 411760043922 | 20240128 | 2034 | 20240129 | 1304 | 2326638 | 990 | Transformer only | Equipment Failure/Involved | Electrical Overload | 4 | 3960 | 36.5072 | -121.8056 | No | Clear;32-90 F | Transformer | Broken | 24-0016027 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1906970 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | BUENA VISTA-1106 | 182261106 | TRANSFORMER | 412294848377 | 20240129 | 709 | 20240129 | 1346 | 2326857 | 397 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 397 | 36.6342 | -121.6273 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0016088 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1907079 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-0414 | 83330414 | FUSE | 4869 | 20240129 | 753 | 20240129 | 2000 | 2326938 | 727 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 727 | 36.9127 | -121.7511 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0016144 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1907183 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | TRANSFORMER | 315299522940 | 20240129 | 907 | 20240129 | 1059 | 2327094 | 112 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 224 | 37.1184 | -122.1131 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0016169 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1907190 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | TRANSFORMER | 412876142295 | 20240129 | 1050 | 20240129 | 1347 | 2327153 | 177 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 177 | 36.47 | -121.4246 | No | Clear;32-90 F | Transformer | Broken | 24-0016179 | OH | Sus | 46174031 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1907193 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 11415 | 20240129 | 1220 | 20240129 | 1705 | 2327219 | 285 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1710 | 37.0626 | -122.0132 | No | Clear;32-90 F | Secondary | Broken | 24-0016229 | OH | Sus | 46174200 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1907215 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 411965056525 | 20240129 | 1244 | 20240130 | 1157 | 2327363 | 1393 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1393 | 36.8545 | -121.7474 | No | Clear;32-90 F | Transformer | Contaminated | 24-0016350 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1907264 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | RECLOSER | 4018 | 20240129 | 1442 | 20240129 | 1456 | 2327467 | 14 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 239 | 3346 | 36.6885 | -121.2715 | No | Clear;32-90 F |  |  | 24-0016330 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1907254 | 0 | EPSS Ckt | N | 2024 | C & 51 TIME
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | TRANSFORMER | 411760043922 | 20240129 | 2330 | 20240130 | 201 | 2327738 | 151 | Transformer only | Equipment Failure/Involved | Underground | 4 | 604 | 36.5072 | -121.8056 | No | Clear;32-90 F | Secondary | Broken | 24-0016449 | UG | Sus | 46174403 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1907316 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 3311 | 20240130 | 840 | 20240130 | 1046 | 2328187 | 126 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 1 | 126 | 37.0116 | -121.7084 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0016612 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1907517 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411823852021 | 20240130 | 944 | 20240130 | 1515 | 2328128 | 331 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 331 | 36.7298 | -121.7916 | No | Clear;32-90 F |  |  | 24-0016604 | OH | Sus | 31682840 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1907514 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 1617 | 20240130 | 1053 | 20240130 | 1918 | 2328197 | 505 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 5160 | 37.0334 | -122.0091 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0016717 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1907543 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1102 | 182011102 | FUSE | 25683 | 20240130 | 1423 | 20240130 | 1500 | 2328405 | 37 | Distribution Circuit | 3rd Party | Metallic Balloon | 298 | 11026 | 36.6882 | -121.6118 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0016817 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1907567 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | TRANSFORMER | 412024542279 | 20240130 | 2105 | 20240130 | 2112 | s1907618 | 7 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 14 | 36.4645 | -121.7133 | No | Clear;32-90 F | Pole-Wood | Normal | 24-0001600 | OH | Sus | 35487993 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1907618 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | TRANSFORMER | 412026342278 | 20240130 | 2126 | 20240130 | 2132 | s1907619 | 6 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 6 | 36.4639 | -121.7129 | No | Clear;32-90 F | Pole-Wood | Normal | 24-0001600 | OH | Sus | 35487993 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1907619 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0421 | 182440421 | TRANSFORMER | 411474048039 | 20240130 | 2242 | 20240130 | 2311 | 2328670 | 29 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 435 | 36.6171 | -121.9072 | No | Partly Cloudy;32-90 F | Transformer (OH) | Deteriorated | 24-0016949 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1907627 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 412084949439 | 20240131 | 737 | 20240131 | 1708 | 2328935 | 571 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 571 | 36.6605 | -121.6998 | No | Clear;32-90 F |  |  | 24-0017183 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1907842 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 11943 | 20240131 | 758 | 20240131 | 812 | 2328928 | 14 | Distribution Circuit | Vegetation | Tree - branch fell on line | 79 | 1106 | 37.0112 | -122.0442 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0017075 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1907731 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1101 | 182131101 | TRANSFORMER | 412813043832 | 20240131 | 928 | 20240131 | 1624 | 2328973 | 416 | Transformer only | Equipment Failure/Involved | Electrical Overload | 14 | 5824 | 36.5122 | -121.4468 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0017145 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1907816 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 181 | 20240131 | 1034 | 20240131 | 1210 | 2329376 | 96 | Distribution Circuit | Animal | Bird found | 56 | 5376 | 37.0628 | -122.0336 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0017270 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1907874 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2101 | 182492101 | FUSE | 266281 | 20240131 | 1039 | 20240131 | 1143 | 2329382 | 64 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 512 | 36.8312 | -121.4353 | No | Clear;32-90 F |  |  | 24-0017249 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1907865 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | JUMPER | OJ @ 8455 | 20240131 | 1045 | 20240131 | 1340 | 2329671 | 175 | Distribution Circuit | Equipment Failure/Involved | Overhead | 164 | 28700 | 36.6001 | -121.8456 | No | Overcast;32-90 F | Jumper | Burned Open | 24-0017298 | OH | Sus | 46175710 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1907884 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 5143 | 20240131 | 1159 | 20240131 | 1315 | 2329573 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 2052 | 37.0994 | -122.0868 | No | Clear-Strong Winds;32-90 F |  |  | 24-0017345 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1907897 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | TRANSFORMER | 412141649142 | 20240131 | 1606 | 20240201 | 1009 | 2330439 | 1083 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1083 | 36.6529 | -121.6801 | No | Strong Winds-Overcast-Heavy Rain;32-90 F | Transformer | Arcing | 24-0017752 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1908150 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 3347 | 20240131 | 1742 | 20240131 | 1827 | 2330143 | 45 | Distribution Circuit | Vegetation | Tree - bark fell into line | 11 | 509 | 36.8707 | -121.6898 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0017584 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1908002 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1101 | 182201101 | FUSE | 5319 | 20240131 | 1747 | 20240131 | 2125 | 2330051 | 218 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 1962 | 36.5823 | -121.4982 | No | Overcast-Heavy Rain-Strong Winds;32-90 F | Insulator | Broken | 24-0017580 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1907998 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 10726 | 20240131 | 1751 | 20240131 | 1926 | 2330160 | 95 | Distribution Circuit | Vegetation | Tree - bark fell into line | 235 | 22325 | 37.061 | -122.1493 | No | Overcast-Heavy Rain;32-90 F | Pothead(Riser Termination) | Normal | 24-0017571 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1907988 | 0 | EPSS Ckt | N | 2024 | B & GRD
CENTRAL COAST | KING CITY | KING CITY-1101 | 182031101 | JUMPER | BURNT OJ | 20240131 | 1802 | 20240131 | 1937 | 2330190 | 95 | Distribution Circuit | Equipment Failure/Involved | Overhead | 49 | 4655 | 36.211 | -121.1249 | No | Overcast-Rain-Strong Winds;32-90 F | Jumper | Burned Open | 24-0017591 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1908006 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 6689 | 20240131 | 1822 | 20240131 | 1932 | 2330217 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 770 | 36.8881 | -121.8071 | No | Overcast-Rain;32-90 F |  |  | 24-0017626 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1908034 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | RECLOSER | 63868 | 20240131 | 1833 | 20240131 | 1845 | 2330240 | 12 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 418 | 5016 | 36.264 | -121.7952 | No | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0017592 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1908008 | 0 | EPSS Ckt | N | 2024 | A & C
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 6689 | 20240131 | 1938 | 20240131 | 2236 | 2330375 | 178 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 1958 | 36.8881 | -121.8071 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Together | 24-0017630 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1908037 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | SWITCH | 11223 | 20240131 | 1947 | 20240131 | 2041 | 2330376 | 54 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1348 | 40804 | 36.9485 | -121.8633 | No | Overcast-Rain;32-90 F |  |  | 24-0017632 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1908038 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SOLEDAD-2105 | 182052105 | RECLOSER | 315500 | 20240131 | 2024 | 20240131 | 2318 | 2330428 | 174 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 2958 | 36.4743 | -121.3523 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0017648 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1908050 | 0 | EPSS Ckt | N | 2024 | A & B
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 3917 | 20240131 | 2031 | 20240131 | 2120 | 2330473 | 49 | Distribution Circuit | Vegetation | Tree - bark fell into line | 16 | 784 | 36.9516 | -121.8502 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0017668 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1908065 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | RECLOSER | 3090 | 20240131 | 2055 | 20240201 | 1655 | 2330464 | 1200 | Distribution Circuit | 3rd Party | Vehicle | 1772 | 187452 | 36.7322 | -121.61 | No | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0017657 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1908055 | 0 | EPSS Ckt | N | 2024 | C & GRD
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 1051 | 20240131 | 2125 | 20240201 | 58 | 2330491 | 213 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 38 | 8015 | 36.9541 | -121.847 | No | Overcast-Fog-Heavy Rain;32-90 F |  |  | 24-0017739 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1908136 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 24715 | 20240131 | 2128 | 20240201 | 113 | 2330492 | 225 | Distribution Circuit | Vegetation | Tree - bark fell into line | 15 | 3375 | 36.8074 | -121.6701 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0017736 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1908133 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 9875 | 20240131 | 2128 | 20240201 | 1015 | 2330499 | 767 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 12 | 9204 | 36.8601 | -121.7708 | No | Clear;32-90 F |  |  | 24-0017701 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1908095 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 5945 | 20240131 | 2142 | 20240201 | 132 | 2330510 | 230 | Distribution Circuit | Vegetation | Tree - bark fell into line | 223 | 51392 | 36.7919 | -121.7232 | No | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0017741 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1908138 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | RECLOSER | 63868 | 20240131 | 2146 | 20240131 | 2329 | 2330480 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 418 | 43054 | 36.264 | -121.7952 | No | Overcast-Heavy Rain;32-90 F |  |  | 24-0017690 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1908084 | 0 | EPSS Ckt | N | 2024 | A-GRD
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | FUSE | 5561 | 20240131 | 2147 | 20240201 | 855 | 2330514 | 668 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 8911 | 36.7763 | -121.5987 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0017743 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1908140 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6545 | 20240131 | 2205 | 20240201 | 935 | 2330525 | 690 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 17250 | 36.9404 | -121.8542 | No | Overcast-Fog-Heavy Rain;32-90 F |  |  | 24-0017855 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1908213 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 9125 | 20240201 | 305 | 20240201 | 1023 | 2330818 | 438 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 18834 | 37.1004 | -122.086 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0017778 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1908174 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 7191 | 20240201 | 533 | 20240201 | 1718 | 2330815 | 705 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 9870 | 36.2368 | -121.7875 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0017874 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1908229 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | TRANSFORMER | 412218551660 | 20240201 | 620 | 20240201 | 1212 | 2330834 | 352 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 4928 | 36.7228 | -121.6562 | No | Overcast;32-90 F | Connector or Splice (OH) | Broken | 24-0017829 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1908191 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 4133 | 20240201 | 738 | 20240201 | 830 | 2330920 | 52 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 1248 | 36.9249 | -121.3784 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 24-0017852 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1908211 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | JUMPER | 647 #1 JUMPER OPEN | 20240201 | 842 | 20240201 | 1338 | 2331021 | 296 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1184 | 36.1794 | -121.6952 | No | Clear;32-90 F | Jumper | Burned Open | 24-0017964 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1908286 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | RECLOSER | 4780 | 20240201 | 1001 | 20240201 | 1706 | 2331161 | 425 | Distribution Circuit | 3rd Party | Vehicle | 241 | 18293 | 36.9425 | -121.4435 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 24-0017933 | OH | Sus | 35528522 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1908276 | 0 | EPSS Ckt | N | 2024 | ABC- GRD
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | JUMPER | 99672 | 20240201 | 1045 | 20240201 | 1611 | 2331210 | 326 | Distribution Circuit | Equipment Failure/Involved | Overhead | 98 | 30610 | 36.7642 | -121.7605 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 24-0017970 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1908288 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | FUSE | 5561 | 20240201 | 1048 | 20240201 | 1210 | 2331217 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1094 | 36.7763 | -121.5987 | No | Clear;32-90 F |  |  | 24-0018057 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1908320 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | RECLOSER | 4712 | 20240201 | 1438 | 20240202 | 304 | 2331537 | 746 | Distribution Circuit | 3rd Party | Vehicle | 716 | 86927 | 36.8565 | -121.5126 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0018177 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1908349 | 0 | EPSS Ckt | N | 2024 | A-GRD-MTT
CENTRAL COAST | SALINAS | INDUSTRIAL ACRES-0412 | 182300412 | TRANSFORMER | 412347050162 | 20240201 | 1450 | 20240201 | 1643 | 2331456 | 113 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 904 | 36.6826 | -121.6116 | No | Overcast;32-90 F | Transformer | Broken- wire on ground | 24-0018205 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1908359 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411942053064 | 20240201 | 1601 | 20240201 | 2347 | 2331962 | 466 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 2796 | 36.7597 | -121.7523 | No | Clear;32-90 F | Secondary | Broken | 24-0018353 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1908418 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 8045 | 20240201 | 1615 | 20240201 | 1722 | 2331689 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 67 | 36.5039 | -121.9353 | No | Overcast;32-90 F |  |  | 24-0018298 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1908380 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | TRANSFORMER | 412259753579 | 20240201 | 1716 | 20240202 | 1210 | 2331720 | 1134 | Transformer only | Equipment Failure/Involved | Underground | 1 | 1134 | 36.776 | -121.6454 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0018305 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1908382 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 4393 | 20240201 | 1742 | 20240201 | 2047 | 2331858 | 185 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 95 | 17575 | 37.1199 | -122.1209 | No | Clear;32-90 F |  |  | 24-0018335 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1908402 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1109 | 182011109 | SWITCH | 21130 | 20240201 | 1756 | 20240201 | 1849 | s1908514 | 53 | Distribution Circuit | Company Initiated | Return Circuit Normal | 1418 | 5868 | 36.6859 | -121.5967 | No | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Normal | 24-0017657 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1908514 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1106 | 182011106 | FUSE | 24291 | 20240202 | 4 | 20240202 | 427 | 2332011 | 263 | Distribution Circuit | Equipment Failure/Involved | Overhead | 111 | 11529 | 36.6614 | -121.661 | No | Partly Cloudy-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0018383 | OH | Sus | 46176757 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1908445 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | RECLOSER | 563516 | 20240202 | 200 | 20240202 | 436 | 2332040 | 155 | Distribution Circuit | Vegetation | Tree - fell into line | 1021 | 155993 | 36.5785 | -121.9279 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0018390 | OH | Sus | 46176758 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1908452 | 0 | EPSS Ckt | N | 2024 | A-B-C GRD
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 40321 | 20240202 | 417 | 20240202 | 517 | 2332108 | 60 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 1560 | 36.6039 | -121.9501 | No | Overcast;32-90 F |  |  | 24-0018403 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1908461 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | TRANSFORMER | 412611849615 | 20240202 | 620 | 20240202 | 954 | 2332132 | 214 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 428 | 36.6682 | -121.5204 | No | Overcast-Drizzle;32-90 F | Fuse | Burned Open | 24-0018523 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1908585 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 393582 | 20240202 | 824 | 20240202 | 2028 | 2332230 | 701 | Distribution Circuit | Vegetation | Tree - fell into line | 636 | 116982 | 37.1284 | -122.1222 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 24-0018463 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1908512 | 0 | EPSS Ckt | N | 2024 | B GRD TIME
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | JUMPER | WIRE DOWN 1 W & 1 S/OF CGC 315330019750 | 20240202 | 1036 | 20240202 | 2037 | 2332437 | 601 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 6625 | 37.0281 | -122.1001 | No | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0018664 | OH | Sus | 46178119 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1908618 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 5271 | 20240202 | 1633 | 20240202 | 1720 | 2333147 | 47 | Distribution Circuit | 3rd Party | Vehicle | 5 | 235 | 36.8383 | -121.6715 | No | Clear;32-90 F | Fuse | Normal | 24-0018836 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | No | No | 1908697 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1109 | 182011109 | TRANSFORMER | 412350249989 | 20240202 | 1906 | 20240202 | 1957 | 2333250 | 51 | Transformer only | Equipment Failure/Involved | Overhead | 65 | 3315 | 36.6779 | -121.6102 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0018853 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1908712 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | TRANSFORMER | T262 | 20240202 | 2216 | 20240204 | 100 | 2333337 | 1604 | Distribution Circuit | Equipment Failure/Involved | Underground | 16 | 25664 | 36.5634 | -121.731 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0018887 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1908747 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 7867 | 20240202 | 2246 | 20240203 | 146 | 2333345 | 180 | Distribution Circuit | 3rd Party | Vehicle | 1121 | 36921 | 36.9224 | -121.7669 | No | Overcast;32-90 F | Anchor or Guy | Normal | 24-0018888 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1908748 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 5289 | 20240203 | 58 | 20240203 | 1114 | 2333365 | 616 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 10683 | 36.7755 | -121.678 | No | Clear;32-90 F |  |  | 24-0018894 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1908754 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9771 | 20240203 | 929 | 20240203 | 1020 | 2333541 | 51 | Distribution Circuit | Animal | Bird found | 38 | 1938 | 37.1313 | -122.1209 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0018920 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1908827 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | FUSE | 7877 | 20240203 | 1042 | 20240203 | 1415 | 2333616 | 213 | Distribution Circuit | Animal | Bird found | 11 | 2273 | 35.9639 | -121.0998 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0018938 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1908838 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | RECLOSER | 3712 | 20240203 | 1423 | 20240203 | 1935 | 2333643 | 312 | Distribution Circuit | 3rd Party | Vehicle | 655 | 204360 | 36.7758 | -121.6691 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0018914 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1908851 | 0 | EPSS Ckt | N | 2024 | N/A
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 412056354596 | 20240203 | 1521 | 20240204 | 1917 | 2333761 | 1676 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 5028 | 36.8022 | -121.7147 | No | Overcast;32-90 F | Transformer | Failed/Faulted | 24-0018957 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1908860 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 316056415389 | 20240203 | 1851 | 20240204 | 104 | 2333887 | 373 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 373 | 36.9144 | -121.8501 | No | Rain-Overcast-Fog;32-90 F | Transformer | Broken- wire on ground | 24-0018978 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1908871 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2107 | 182402107 | OTHER | WIRE DOWN | 20240203 | 2210 | 20240204 | 1358 | 2333976 | 948 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2856 | 276477 | 36.6777 | -121.7946 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019068 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1908961 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 6779 | 20240203 | 2247 | 20240204 | 1620 | 2333985 | 1053 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 2106 | 36.8936 | -121.6442 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0020387 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1910215 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | RECLOSER | 974130 | 20240203 | 2255 | 20240204 | 332 | 2333982 | 277 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 15059 | 37.0448 | -121.9382 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 24-0019070 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1908962 | 0 | EPSS Ckt | N | 2024 | B GRD 51
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 1939 | 20240203 | 2339 | 20240204 | 827 | 2334006 | 528 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 3168 | 36.9839 | -121.8312 | No | Overcast-Fog-Rain;32-90 F |  |  | 24-0019231 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909123 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 3945 | 20240204 | 13 | 20240204 | 210 | 2334074 | 117 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 52 | 6084 | 36.8172 | -121.636 | Yes | Clear;32-90 F |  |  | 24-0019102 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1908988 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2107 | 182402107 | FUSE | 6051 | 20240204 | 17 | 20240204 | 49 | 2334176 | 32 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 640 | 36.6805 | -121.7948 | Yes | Overcast;32-90 F |  |  | 24-0019089 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1908974 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | RECLOSER | 187705 | 20240204 | 105 | 20240204 | 239 | 2334181 | 94 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 3196 | 36.3958 | -121.8796 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0019092 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1908977 | 0 | EPSS Ckt | N | 2024 | B GRD
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 2181 | 20240204 | 136 | 20240209 | 1913 | 2334200 | 8257 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 429364 | 36.4895 | -121.9363 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019115 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1909002 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | JUMPER | OJ CGC 411373943352 | 20240204 | 142 | 20240210 | 1059 | 2372304 | 9197 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 294304 | 36.4872 | -121.9352 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0027181 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1915695 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | FUSE | 10387 | 20240204 | 149 | 20240204 | 1051 | 2334203 | 542 | Distribution Circuit | Equipment Failure/Involved | Underground | 285 | 121122 | 36.9738 | -121.9623 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0019116 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909003 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 5901 | 20240204 | 216 | 20240204 | 839 | 2334288 | 383 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 6128 | 37.0944 | -121.9716 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0019218 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909109 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 4277 | 20240204 | 232 | 20240204 | 826 | 2334270 | 354 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 5310 | 36.9387 | -121.7255 | Yes | Overcast-Fog-Rain;32-90 F |  |  | 24-0019254 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909145 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 2687 | 20240204 | 348 | 20240205 | 1057 | 2334721 | 1869 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 24297 | 37.0224 | -121.8276 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019387 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1909272 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | JUMPER | OJS 2 N/OF 411449045593 | 20240204 | 434 | 20240209 | 1310 | 2353916 | 7716 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 38580 | 36.5505 | -121.9138 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020994 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1910816 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 40251 | 20240204 | 439 | 20240208 | 1340 | 2334364 | 6301 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 371759 | 36.2415 | -121.7971 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022158 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1911837 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2108 | 83252108 | OCB | 2108/2 | 20240204 | 450 | 20240204 | 640 | 2334380 | 110 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 6272 | 318959 | 36.9926 | -121.982 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0019134 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909021 | 0 | EPSS Ckt | N | 2024 | BC
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 11967 | 20240204 | 502 | 20240205 | 1511 | 2334404 | 2049 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 63519 | 37.029 | -122.0723 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019339 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1909222 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | RECLOSER | 42086 | 20240204 | 509 | 20240204 | 1759 | 2334427 | 734 | Distribution Circuit | Vegetation | Tree - fell into line | 178 | 130652 | 36.9036 | -121.7361 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019136 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1909023 | 0 | EPSS Ckt | N | 2024 | ABC GRD
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 12106 | 20240204 | 526 | 20240204 | 731 | 2334465 | 125 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1012 | 126500 | 36.9718 | -121.7649 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 24-0019148 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909035 | 0 | EPSS Ckt | N | 2024 | A-B
CENTRAL COAST | COAST | PAUL SWEET-2108 | 83252108 | FUSE | 5111 | 20240204 | 531 | 20240206 | 820 | 2334469 | 3049 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 112 | 341488 | 36.9716 | -122.008 | Yes | Overcast-Fog-Heavy Rain;32-90 F |  |  | 24-0023001 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912585 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 4951 | 20240204 | 538 | 20240206 | 2118 | 2334483 | 3820 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 8029 | 36.8201 | -121.3455 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019179 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1909068 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1112 | 182371112 | FUSE | 9441 | 20240204 | 551 | 20240206 | 2358 | 2334511 | 3967 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 29106 | 36.5466 | -121.7527 | Yes | Clear;32-90 F |  |  | 24-0023914 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913278 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6557 | 20240204 | 600 | 20240204 | 856 | 2334544 | 176 | Distribution Circuit | Vegetation | Tree - bark fell into line | 54 | 9504 | 36.916 | -121.832 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0019367 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909250 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | SWITCH | 4735 | 20240204 | 601 | 20240207 | 1520 | 2364847 | 4879 | Distribution Circuit | Vegetation | Tree - fell into line | 157 | 766003 | 37.0512 | -122.1155 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021577 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1912947 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | RECLOSER | 63868 | 20240204 | 606 | 20240210 | 1526 | 2334575 | 9200 | Distribution Circuit | Vegetation | Tree - grew into line | 29 | 266800 | 36.264 | -121.7952 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Service conductor | Broken | 24-0019162 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909051 | 0 | EPSS Ckt | N | 2024 | A & C PH
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 40411 | 20240204 | 606 | 20240209 | 1913 | 2356014 | 7987 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 415324 | 36.4918 | -121.938 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021348 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1911182 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 457 | 20240204 | 606 | 20240210 | 1139 | 2372307 | 8973 | Distribution Circuit | Vegetation | Tree - grew into line | 19 | 170487 | 36.4927 | -121.9335 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0027182 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1915696 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | SWITCH | 6731 | 20240204 | 606 | 20240211 | 1335 | 2360501 | 10529 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 947610 | 36.2086 | -121.7384 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0022241 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1911905 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | FUSE | 485 | 20240204 | 606 | 20240209 | 1156 | 2361243 | 7550 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 45300 | 36.2254 | -121.7618 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022464 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1912103 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | TRIP-SAVER | 5401 | 20240204 | 607 | 20240209 | 1600 | 2334867 | 7793 | Distribution Circuit | Equipment Failure/Involved | Overhead | 69 | 448117 | 37.0647 | -122.1232 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0024640 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1913701 | 0 | EPSS Ckt | N | 2024 | NA
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 4873 | 20240204 | 615 | 20240204 | 755 | 2334596 | 100 | Distribution Circuit | Vegetation | Tree - bark fell into line | 45 | 4500 | 36.8538 | -121.3637 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0019252 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909143 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 6895 | 20240204 | 631 | 20240206 | 1732 | 2365386 | 3541 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 2358 | 36.8382 | -121.7668 | Yes | Clear;32-90 F |  |  | 24-0023669 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913070 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 465 | 20240204 | 633 | 20240208 | 1218 | 2336330 | 6105 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 12210 | 36.304 | -121.8762 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019390 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1909275 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | FUSE | 40555 | 20240204 | 633 | 20240209 | 1736 | 2369290 | 7863 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 7863 | 36.3078 | -121.8819 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023871 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1914983 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 3965 | 20240204 | 633 | 20240204 | 748 | 2334626 | 75 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 165 | 12375 | 36.9606 | -122.0275 | Yes | Overcast-Fog-Heavy Rain;32-90 F |  |  | 24-0019225 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909116 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | RECLOSER | 440 | 20240204 | 634 | 20240208 | 1218 | 2334645 | 6104 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 54936 | 36.4389 | -121.9203 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019175 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1909064 | 0 | EPSS Ckt | N | 2024 | A/GRD
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | RECLOSER | 2052 | 20240204 | 634 | 20240209 | 1830 | 2369379 | 7916 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 245396 | 36.4 | -121.9022 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026021 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | Yes | No | 1915004 | 0 | EPSS Ckt | N | 2024 | NONE
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | SWITCH | 6369 | 20240204 | 634 | 20240208 | 1218 | 2364388 | 6104 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 219744 | 36.3692 | -121.8924 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0023360 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1912831 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | FUSE | 9015 | 20240204 | 634 | 20240209 | 1736 | 2365871 | 7862 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 7862 | 36.307 | -121.8841 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023871 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1913243 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | FUSE | 6191 | 20240204 | 634 | 20240209 | 1608 | 2369829 | 7774 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 23322 | 36.3753 | -121.8967 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026180 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1915083 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | FUSE | 23113 | 20240204 | 638 | 20240204 | 850 | 2334684 | 132 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1188 | 36.5963 | -121.621 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0019331 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909214 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | OTHER | WIRE DOWN 4P LOAD SIDE OF 894556 | 20240204 | 658 | 20240209 | 1216 | 2334798 | 7518 | Distribution Circuit | Vegetation | Tree - bark fell into line | 8 | 60144 | 37.0599 | -121.9411 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019317 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1909202 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 4303 | 20240204 | 703 | 20240207 | 1100 | 2361395 | 4557 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 19550 | 36.7265 | -121.7874 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022517 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1912149 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | RECLOSER | 99672 | 20240204 | 704 | 20240205 | 1918 | 2334824 | 2174 | Distribution Circuit | Equipment Failure/Involved | Overhead | 89 | 125235 | 36.7642 | -121.7605 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0019194 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | Yes | No | 1909085 | 0 | Non-EPSS | N | 2024 | B C GRD
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 4307 | 20240204 | 704 | 20240207 | 1249 | 2361446 | 4665 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 9330 | 36.7145 | -121.7926 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022533 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | Yes | No | 1912162 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 11941 | 20240204 | 706 | 20240205 | 2125 | 2334822 | 2299 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 66671 | 37.0087 | -122.0453 | Yes | Overcast-Fog-Heavy Rain;32-90 F |  |  | 24-0022818 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1912454 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | TRANSFORMER | MTR#1009052704 | 20240204 | 706 | 20240204 | 1211 | 2334552 | 305 | Transformer only | Equipment Failure/Involved | Electrical Overload | 13 | 3965 | 36.711 | -121.6229 | Yes | Strong Winds-Overcast-Drizzle;32-90 F | Transformer | Together | 24-0019217 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909108 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 12129 | 20240204 | 706 | 20240209 | 1723 | 2340167 | 7817 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 7817 | 37.0851 | -122.1416 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019851 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1909689 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 10720 | 20240204 | 707 | 20240207 | 1557 | 2359148 | 4850 | Distribution Circuit | Vegetation | Tree - fell into line | 1701 | 8110422 | 37.1085 | -122.1441 | Yes | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021615 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1911605 | 0 | EPSS Ckt | N | 2024 | NA
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 5078 | 20240204 | 711 | 20240209 | 1723 | 2334849 | 7812 | Distribution Circuit | Vegetation | Tree - fell into line | 528 | 3151431 | 37.0314 | -122.1879 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019201 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | Yes | No | 1909092 | 0 | EPSS Ckt | N | 2024 | ABC/GRD T
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | JUMPER | JPRS 5 E/OF 1219 | 20240204 | 711 | 20240209 | 1723 | 2361083 | 7812 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 78120 | 37.0852 | -122.139 | Yes | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0019851 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1912060 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 563 | 20240204 | 711 | 20240210 | 1711 | 2371210 | 9240 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 101640 | 37.0587 | -122.1418 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026821 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1915502 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 8985 | 20240204 | 711 | 20240210 | 1235 | 2371217 | 8964 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 206172 | 37.0288 | -122.1405 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026826 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1915505 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1104 | 182381104 | OTHER | WIRE DOWN | 20240204 | 712 | 20240205 | 1108 | 2337276 | 1676 | Distribution Circuit | Vegetation | Tree - fell into line | 260 | 431188 | 36.771 | -121.735 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019509 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | Yes | Yes | 1909383 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | RECLOSER | 5144 | 20240204 | 713 | 20240206 | 1736 | 2334854 | 3503 | Distribution Circuit | Vegetation | Tree - fell into line | 125 | 53775 | 37.0911 | -122.0774 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019206 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1909097 | 0 | EPSS Ckt | N | 2024 | ABC
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRIP-SAVER | 1831 | 20240204 | 720 | 20240204 | 1946 | 2335012 | 746 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 32078 | 36.8143 | -121.7007 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019698 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1909552 | 0 | EPSS Ckt | N | 2024 | ABC
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 796388 | 20240204 | 724 | 20240207 | 1625 | 2356339 | 4861 | Distribution Circuit | Vegetation | Tree - fell into line | 269 | 757934 | 36.9818 | -121.901 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Insulator | Broken | 24-0021426 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911261 | 0 | EPSS Ckt | N | 2024 | B GRD
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | FUSE | 50229 | 20240204 | 733 | 20240206 | 1350 | 2336663 | 3257 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 22491 | 36.8508 | -121.502 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019436 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1909314 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 9901 | 20240204 | 733 | 20240206 | 22 | 2362607 | 2449 | Distribution Circuit | Vegetation | Tree - branch fell on line | 570 | 248287 | 36.8772 | -121.688 | Yes | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Normal | 24-0022839 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912473 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 3889 | 20240204 | 740 | 20240204 | 1705 | 2334985 | 565 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 39550 | 36.9487 | -121.8523 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019291 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1909178 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | FUSE | 7249 | 20240204 | 741 | 20240204 | 1540 | 2335004 | 479 | Distribution Circuit | Vegetation | Tree - branch fell on line | 248 | 6454 | 36.4553 | -121.445 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0019980 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909814 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2107 | 182402107 | OTHER | WIRE DOWN @ CGC# 411814550196 | 20240204 | 742 | 20240204 | 1358 | -2335000 | 376 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2732 | 228008 | 36.6792 | -121.7921 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019296 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | Yes | Yes | 1909183 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2107 | 182402107 | TRANSFORMER | 411833050433 | 20240204 | 743 | 20240204 | 1404 | 2334591 | 381 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 4572 | 36.686 | -121.7874 | Yes | Clear;32-90 F | Anchor or Guy | Broken- wire on ground | 24-0019202 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1909093 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | RECLOSER | 3034 | 20240204 | 743 | 20240204 | 1513 | 2335016 | 450 | Distribution Circuit | Equipment Failure/Involved | Overhead | 542 | 44718 | 36.7317 | -121.6129 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Jumper | Bent or Twisted | 24-0019237 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909128 | 0 | EPSS Ckt | N | 2024 | A B
CENTRAL COAST | SALINAS | SPENCE-1101 | 182201101 | FUSE | 5319 | 20240204 | 743 | 20240204 | 1547 | 2335011 | 484 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 4356 | 36.5823 | -121.4982 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Together | 24-0019513 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909387 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 129651 | 20240204 | 744 | 20240204 | 1041 | 2335015 | 177 | Distribution Circuit | Vegetation | Tree - bark fell into line | 18 | 3186 | 36.8107 | -121.6346 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0019516 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909390 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | RECLOSER | 4002 | 20240204 | 746 | 20240204 | 925 | 2335053 | 99 | Distribution Circuit | Vegetation | Tree - branch fell on line | 170 | 16830 | 36.8322 | -121.5312 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0019377 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | No | No | 1909262 | 0 | EPSS Ckt | N | 2024 | ABC
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | OCB | 2202/2 | 20240204 | 746 | 20240207 | 1518 | 2337926 | 4772 | Distribution Circuit | Vegetation | Tree - fell into line | 729 | 2624194 | 36.5786 | -121.9085 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken | 24-0019877 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | No | No | 1909714 | 0 | EPSS Ckt | N | 2024 | ABC
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | RECLOSER | 9104 | 20240204 | 746 | 20240207 | 1518 | 2358710 | 4772 | Distribution Circuit | Vegetation | Tree - fell into line | 490 | 2313528 | 36.5869 | -121.9142 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019877 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1911517 | 0 | EPSS Ckt | N | 2024 | NONE
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | RECLOSER | 92792 | 20240204 | 746 | 20240206 | 1430 | 2364055 | 3284 | Distribution Circuit | Vegetation | Tree - fell into line | 126 | 413784 | 36.5898 | -121.9457 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 24-0019877 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1912745 | 0 | EPSS Ckt | N | 2024 | NONE
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 6855 | 20240204 | 746 | 20240208 | 1443 | 2364107 | 6177 | Distribution Circuit | Vegetation | Tree - fell into line | 268 | 1075286 | 36.5958 | -121.9421 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019877 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1912756 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | SWITCH | 6023 | 20240204 | 746 | 20240207 | 1054 | 2364191 | 4508 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 230 | 1036840 | 36.597 | -121.942 | Yes | Overcast-Rain;32-90 F |  |  | 24-0019877 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1912784 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | RECLOSER | 9120 | 20240204 | 746 | 20240209 | 1633 | 2364194 | 3139 | Distribution Circuit | Vegetation | Tree - fell into line | 454 | 1092372 | 36.6022 | -121.9359 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken | 24-0019877 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1912785 | 0 | EPSS Ckt | N | 2024 | NA
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | RECLOSER | 9100 | 20240204 | 746 | 20240207 | 1519 | 2364962 | 4773 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1520 | 7254960 | 36.6163 | -121.9248 | Yes | Overcast-Rain;32-90 F | Service conductor | Bent or Twisted | 24-0019877 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1912982 | 0 | EPSS Ckt | N | 2024 | N/A
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 9047 | 20240204 | 746 | 20240209 | 1248 | 2366822 | 7502 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 255222 | 36.6212 | -121.9135 | Yes | Overcast-Rain;32-90 F | Crossarm- Wood | Broken | 24-0019877 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913388 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 412033954745 | 20240204 | 747 | 20240208 | 632 | 2335040 | 5685 | Transformer only | Vegetation | Tree - fell into line | 2 | 11370 | 36.807 | -121.7227 | Yes | Strong Winds-Clear;32-90 F | Transformer | Broken | 24-0020761 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1910580 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 3533 | 20240204 | 748 | 20240204 | 1519 | 2335046 | 451 | Distribution Circuit | Vegetation | Tree - bark fell into line | 37 | 16687 | 37.0016 | -122.0274 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0020080 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909908 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | RECLOSER | 144394 | 20240204 | 749 | 20240206 | 350 | 2335088 | 2641 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2339 | 546696 | 36.7259 | -121.6447 | Yes | Clear;32-90 F | Pole-Wood | Broken | 24-0019249 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | No | No | 1909140 | 0 | Non-EPSS | N | 2024 | ABC TIME
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 5607 | 20240204 | 751 | 20240204 | 1545 | 2338814 | 474 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 474 | 36.6674 | -121.7054 | Yes | Clear;32-90 F | Fuse | Failed/Faulted | 24-0020280 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1910109 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 5277 | 20240204 | 752 | 20240204 | 1522 | 2335075 | 450 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 18000 | 36.7758 | -121.6878 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019399 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | Yes | No | 1909284 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5157 | 20240204 | 754 | 20240208 | 1651 | 2335127 | 6297 | Distribution Circuit | Vegetation | Tree - fell into line | 168 | 1057896 | 37.0839 | -122.089 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024608 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1913675 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 8047 | 20240204 | 755 | 20240205 | 1612 | 2335796 | 1937 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 46488 | 36.5029 | -121.9336 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021356 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1911190 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 23437 | 20240204 | 756 | 20240204 | 1245 | 2335130 | 289 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 5870 | 36.7709 | -121.7541 | Yes | Clear-Strong Winds;32-90 F | Fuse | Broken | 24-0019753 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909601 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2106 | 182402106 | OTHER | 9961 | 20240204 | 756 | 20240207 | 1818 | 2335133 | 4942 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 24710 | 36.6362 | -121.8186 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020546 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1910368 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 11851 | 20240204 | 801 | 20240204 | 1759 | 2335189 | 598 | Distribution Circuit | Vegetation | Tree - bark fell into line | 6 | 3588 | 36.8781 | -121.6687 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0020214 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1910040 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 2469 | 20240204 | 801 | 20240205 | 1028 | 2335157 | 1587 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 50784 | 36.8825 | -121.7078 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0021681 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911461 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 4473 | 20240204 | 802 | 20240204 | 1727 | 2335304 | 565 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 9605 | 37.003 | -122.0141 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0019594 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909464 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 2993 | 20240204 | 802 | 20240204 | 1727 | 2335196 | 565 | Distribution Circuit | Vegetation | Tree - branch fell on line | 319 | 180235 | 36.9722 | -122.0306 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0019911 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909745 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | OCB | 2105/2 | 20240204 | 802 | 20240204 | 1727 | 2341298 | 565 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5891 | 3328415 | 36.9926 | -121.9821 | Yes | Overcast-Fog-Heavy Rain;32-90 F |  |  | 24-0020070 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909898 | 0 | EPSS Ckt | N | 2024 | GRD
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 5269 | 20240204 | 802 | 20240206 | 1657 | 2350568 | 3415 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 79862 | 36.9894 | -122.0312 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020884 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1910703 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 7653 | 20240204 | 802 | 20240205 | 1921 | s1912283 | 2119 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 19071 | 36.9739 | -122.0381 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0022650 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1912283 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | RECLOSER | 2103/2 | 20240204 | 804 | 20240205 | 1724 | 2335192 | 2000 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2201 | 1977963 | 36.952 | -121.7601 | Yes | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0019262 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | Yes | No | 1909155 | 0 | EPSS Ckt | N | 2024 | A B C GRD
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | RECLOSER | 10268 | 20240204 | 805 | 20240205 | 44 | 2335287 | 999 | Distribution Circuit | Equipment Failure/Involved | Overhead | 292 | 186796 | 36.9065 | -121.7678 | Yes | Overcast-Fog-Rain;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0019282 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1909171 | 0 | Non-EPSS | N | 2024 | A & B
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 5945 | 20240204 | 808 | 20240204 | 1342 | 2335341 | 334 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 335 | 111890 | 36.7919 | -121.7232 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0019907 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909741 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | JUMPER | 3883 HS JMPR BLOWN | 20240204 | 808 | 20240206 | 1304 | 2337560 | 3176 | Distribution Circuit | Equipment Failure/Involved | Overhead | 208 | 460828 | 36.9141 | -121.7738 | Yes | Overcast-Rain;32-90 F | Jumper | Burned Open | 24-0021915 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1911645 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | OCB | 2104/2 | 20240204 | 810 | 20240204 | 1040 | 2335254 | 150 | Distribution Circuit | Vegetation | Tree - fell into line | 6356 | 952005 | 36.9522 | -121.76 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019267 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1909160 | 0 | Non-EPSS | N | 2024 | GRD
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 5335 | 20240204 | 811 | 20240205 | 2003 | 2360438 | 2152 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 154944 | 37.028 | -121.9873 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0022222 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1911891 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 471 | 20240204 | 811 | 20240207 | 1743 | 2364354 | 4892 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 92948 | 36.4954 | -121.9372 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023350 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1912825 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 8157 | 20240204 | 811 | 20240206 | 821 | 2335256 | 673 | Distribution Circuit | Vegetation | Tree - fell into line | 132 | 62648 | 36.98 | -122.0308 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020354 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1910182 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 9337 | 20240204 | 811 | 20240204 | 1139 | 2335268 | 208 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 46 | 9568 | 36.9399 | -121.8573 | Yes | Overcast-Rain;32-90 F |  |  | 24-0019610 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909477 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 24923 | 20240204 | 812 | 20240205 | 1157 | 2335291 | 1665 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 6660 | 36.7891 | -121.698 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020687 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1910507 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-0414 | 83330414 | TRANSFORMER | 316353015183 | 20240204 | 815 | 20240205 | 309 | 2335286 | 1134 | Transformer only | Unknown Cause | Patrol - found nothing | 19 | 21546 | 36.9103 | -121.7484 | Yes | Overcast-Rain;32-90 F |  |  | 24-0021440 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1911275 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 8193 | 20240204 | 816 | 20240205 | 1021 | 2335307 | 1565 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 62600 | 36.9817 | -121.8969 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Together | 24-0020445 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1910271 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 9629 | 20240204 | 817 | 20240209 | 250 | 2360474 | 6873 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 75034 | 36.9849 | -121.8845 | Yes | Overcast-Fog-Heavy Rain;32-90 F |  |  | 24-0022232 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911902 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | RECLOSER | 12990 | 20240204 | 818 | 20240205 | 1522 | 2335321 | 1864 | Distribution Circuit | Vegetation | Tree - fell into line | 719 | 722563 | 37.039 | -122.0214 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019283 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1909172 | 0 | EPSS Ckt | N | 2024 | A&GRD
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | JUMPER | WIRE DOWN | 20240204 | 820 | 20240205 | 1058 | 2336343 | 1598 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 14062 | 37.0513 | -122.0945 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019392 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | Yes | No | 1909277 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 921 | 20240204 | 821 | 20240207 | 1752 | 2335563 | 4891 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 9782 | 36.8838 | -121.6206 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024201 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1913438 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 39126 | 20240204 | 823 | 20240207 | 1916 | 2338873 | 4973 | Distribution Circuit | Vegetation | Tree - fell into line | 138 | 686274 | 37.0778 | -122.1322 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020395 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1910222 | 0 | EPSS Ckt | N | 2024 | AB
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 415734 | 20240204 | 823 | 20240208 | 1638 | 2335342 | 6255 | Distribution Circuit | Equipment Failure/Involved | Overhead | 76 | 439782 | 37.0316 | -122.1893 | Yes | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0019464 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1909339 | 0 | EPSS Ckt | N | 2024 | FORCE OUT
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 1227 | 20240204 | 823 | 20240209 | 1455 | 2370362 | 7592 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 22776 | 37.0711 | -122.2325 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026376 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1915183 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | SWITCH | 77303 | 20240204 | 823 | 20240209 | 1603 | 2370626 | 7660 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 137880 | 37.0865 | -122.2603 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0019464 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915230 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 6851 | 20240204 | 825 | 20240205 | 1118 | 2335434 | 1613 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 30647 | 36.5569 | -121.9156 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0021844 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911586 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | FUSE | 12261 | 20240204 | 828 | 20240204 | 1015 | 2335384 | 107 | Distribution Circuit | Equipment Failure/Involved | Overhead | 69 | 7383 | 36.9611 | -121.9779 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Secondary | Broken | 24-0019489 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909362 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 655 | 20240204 | 833 | 20240205 | 827 | 2335442 | 1434 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 31548 | 36.8785 | -121.6416 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0021571 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911387 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | TRANSFORMER | 316265916103 | 20240204 | 834 | 20240204 | 1927 | 2335449 | 653 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 5877 | 36.9351 | -121.7787 | Yes | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0019567 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909436 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | SWITCH | 9143 | 20240204 | 837 | 20240209 | 1724 | 2364462 | 7727 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 517709 | 37.1269 | -122.0181 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022587 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1912856 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 7199 | 20240204 | 837 | 20240207 | 1623 | 2365315 | 4786 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 23930 | 37.1116 | -122.0477 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022587 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1913047 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 11829 | 20240204 | 843 | 20240205 | 1130 | 2335665 | 1607 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 8035 | 37.009 | -122.0756 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0019720 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1909569 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 5365 | 20240204 | 848 | 20240208 | 1133 | 2335728 | 5925 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 109236 | 36.9946 | -122.0283 | Yes | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020400 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1910227 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 428972 | 20240204 | 849 | 20240206 | 1839 | 2335745 | 3470 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 274130 | 37.1056 | -121.9724 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022580 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1912208 | 0 | EPSS Ckt | N | 2024 | N/A
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 456903 | 20240204 | 849 | 20240208 | 1630 | 2364658 | 6221 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 43547 | 37.1179 | -121.9643 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023466 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1912904 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | RECLOSER | 9096 | 20240204 | 850 | 20240206 | 1050 | 2335707 | 3000 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3601 | 5834983 | 36.5951 | -121.8454 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0019327 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909211 | 0 | EPSS Ckt | N | 2024 | AB
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 5529 | 20240204 | 850 | 20240204 | 1626 | 2335711 | 456 | Distribution Circuit | Vegetation | Tree - branch fell on line | 329 | 150024 | 36.9879 | -121.9467 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019375 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1909260 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | SOQUEL-0402 | 83300402 | FUSE | 6339 | 20240204 | 851 | 20240205 | 1315 | 2335710 | 1704 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 80068 | 36.9751 | -121.9496 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020716 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1910536 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | SWITCH | 12131 | 20240204 | 855 | 20240204 | 1053 | 2336075 | 118 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1228 | 144904 | 36.9033 | -121.7549 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0019368 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909252 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | RECLOSER | 399900 | 20240204 | 858 | 20240205 | 2021 | 2335787 | 2123 | Distribution Circuit | Vegetation | Tree - fell into line | 340 | 721820 | 36.5403 | -121.8762 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0020052 | OH | Sus | 35528881 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909880 | 0 | EPSS Ckt | N | 2024 | A & B PHSE
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 93223 | 20240204 | 901 | 20240207 | 1047 | 2336336 | 4426 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 331950 | 36.9559 | -122.0462 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0023999 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1913325 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | OCB | 2201/2 | 20240204 | 902 | 20240209 | 1329 | 2337248 | 7467 | Distribution Circuit | Vegetation | Tree - fell into line | 1616 | 5375599 | 36.5786 | -121.9085 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020459 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1910285 | 0 | EPSS Ckt | N | 2024 | A-GRD
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 2323 | 20240204 | 902 | 20240207 | 1639 | 2360874 | 4777 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 234073 | 36.5822 | -121.9214 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken | 24-0022360 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1912012 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 6973 | 20240204 | 902 | 20240207 | 2047 | 2360900 | 5025 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 180900 | 36.5816 | -121.9216 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0022363 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1912015 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 2145 | 20240204 | 902 | 20240207 | 1823 | 2363529 | 4881 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 24405 | 36.5682 | -121.9289 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken | 24-0020459 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1912614 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 7259 | 20240204 | 902 | 20240207 | 1912 | 2364170 | 4930 | Distribution Circuit | Vegetation | Tree - branch fell on line | 46 | 226780 | 36.5752 | -121.9365 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020459 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1912775 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 7257 | 20240204 | 902 | 20240207 | 1822 | 2364176 | 4880 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 190320 | 36.5768 | -121.9393 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020459 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1912777 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 2799 | 20240204 | 902 | 20240207 | 1703 | 2365311 | 4801 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 28806 | 36.5731 | -121.9443 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020459 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1913044 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 7879 | 20240204 | 902 | 20240208 | 1659 | 2368556 | 6237 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 99792 | 36.5783 | -121.9441 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020459 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1913713 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 7873 | 20240204 | 902 | 20240208 | 1635 | 2368558 | 6213 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 186390 | 36.5773 | -121.9451 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020459 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1913715 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 16000 | 20240204 | 903 | 20240208 | 1145 | 2335931 | 5922 | Distribution Circuit | Vegetation | Tree - fell into line | 2174 | 3861247 | 37.0464 | -122.0243 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019351 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1909233 | 0 | EPSS Ckt | N | 2024 | B & C PHASE
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | SWITCH | 6037 | 20240204 | 903 | 20240206 | 1502 | 2359711 | 3239 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 80975 | 37.073 | -122.0159 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022004 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1911722 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 279434 | 20240204 | 903 | 20240207 | 1834 | 2359950 | 4891 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 87 | 425517 | 37.0695 | -121.995 | Yes | Clear;32-90 F |  |  | 24-0022058 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911764 | 0 | EPSS Ckt | N | 2024 | N/A
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 7357 | 20240204 | 903 | 20240208 | 135 | 2361602 | 5312 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 53120 | 37.0682 | -121.9831 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022573 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1912201 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | SWITCH | 6041 | 20240204 | 903 | 20240208 | 1157 | 2361640 | 5934 | Distribution Circuit | Vegetation | Tree - fell into line | 390 | 2295554 | 37.0679 | -121.994 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 24-0022586 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1912214 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 12065 | 20240204 | 903 | 20240205 | 1101 | 2336626 | 1558 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 9348 | 36.9184 | -121.8343 | Yes | Overcast-Rain;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0019433 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1909312 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 1617 | 20240204 | 913 | 20240204 | 1455 | 2336032 | 342 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 5130 | 37.0334 | -122.0091 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0020046 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909875 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | TRANSFORMER | 411400645315 | 20240204 | 916 | 20240207 | 1034 | 2365308 | 4398 | Transformer only | Vegetation | Tree - fell into line | 16 | 70368 | 36.5417 | -121.9291 | Yes | Clear;32-90 F | Pole-Wood | Broken | 24-0023636 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1913039 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | RECLOSER | 1101/2 | 20240204 | 917 | 20240211 | 1335 | 2335252 | 3106 | Distribution Circuit | Equipment Failure/Involved | Overhead | 573 | 1779738 | 36.3803 | -121.8988 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019373 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1909258 | 0 | EPSS Ckt | N | 2024 | C & GRD
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | SWITCH | 8343 | 20240204 | 917 | 20240206 | 1303 | 2337961 | 3106 | Distribution Circuit | Equipment Failure/Involved | Overhead | 102 | 316812 | 36.4816 | -121.9373 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019373 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1909448 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 1491 | 20240204 | 918 | 20240209 | 1615 | 2370974 | 7617 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 312297 | 36.5057 | -121.9352 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 24-0026577 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1915296 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 9811 | 20240204 | 919 | 20240205 | 1438 | 2336208 | 1759 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 238472 | 36.8591 | -121.6955 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Together | 24-0020605 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | No | No | 1910425 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | OCB | 1102/2 | 20240204 | 920 | 20240210 | 1845 | 2336293 | 9205 | Distribution Circuit | Vegetation | Tree - branch fell on line | 929 | 1714142 | 36.5569 | -121.8976 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019564 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1909433 | 0 | EPSS Ckt | N | 2024 | B & C PHSE
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | FUSE | 4759 | 20240204 | 920 | 20240204 | 1228 | 2336335 | 188 | Distribution Circuit | Vegetation | Tree - branch fell on line | 71 | 13348 | 36.981 | -121.9168 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 24-0019669 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909528 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 2725 | 20240204 | 922 | 20240206 | 1939 | 2336412 | 3497 | Distribution Circuit | Equipment Failure/Involved | Overhead | 194 | 678418 | 36.5453 | -121.9281 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020946 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1910766 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | TRIP-SAVER | 40465 | 20240204 | 924 | 20240205 | 1618 | 2353937 | 1854 | Distribution Circuit | Vegetation | Tree - fell into line | 346 | 641484 | 36.5371 | -121.9127 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020999 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1910821 | 0 | EPSS Ckt | N | 2024 | N/A
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 8625 | 20240204 | 925 | 20240205 | 1240 | 2340001 | 1635 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3270 | 36.5405 | -121.902 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019821 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1909662 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 40747 | 20240204 | 927 | 20240205 | 1848 | 2341456 | 2001 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 16008 | 36.5329 | -121.8494 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019979 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1909813 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 12665 | 20240204 | 927 | 20240205 | 1459 | 2342051 | 1772 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 49616 | 36.8621 | -121.6879 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020044 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1909873 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 670217 | 20240204 | 928 | 20240208 | 1753 | 2336299 | 6265 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 344575 | 37.1578 | -122.166 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023832 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1913207 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | RECLOSER | 9488 | 20240204 | 931 | 20240208 | 1958 | 2335375 | 6387 | Distribution Circuit | Vegetation | Tree - fell into line | 160 | 1011159 | 36.5902 | -121.9442 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken | 24-0019406 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909289 | 0 | EPSS Ckt | N | 2024 | A C
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | OTHER | J94066 TWD 491331 | 20240204 | 931 | 20240208 | 1627 | 2364294 | 6176 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6176 | 36.5818 | -121.9503 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019877 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1912810 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 102695 | 20240204 | 931 | 20240208 | 1750 | 2370013 | 6259 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 100144 | 36.5801 | -121.9516 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019877 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1915120 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 11797 | 20240204 | 931 | 20240209 | 1122 | 2336350 | 7311 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 109665 | 36.8677 | -121.7087 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024046 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1913347 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 6161 | 20240204 | 934 | 20240204 | 1728 | 2336408 | 474 | Distribution Circuit | Vegetation | Tree - branch fell on line | 46 | 21804 | 36.5318 | -121.8412 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0021353 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911187 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | JUMPER | OJ CGC 315230624378 | 20240204 | 935 | 20240208 | 1649 | 2368973 | 6194 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 43358 | 37.1582 | -122.1346 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0025009 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1914038 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 555 | 20240204 | 936 | 20240205 | 2247 | 2335522 | 2231 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 70810 | 36.9641 | -121.9987 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0019411 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1909292 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | SWITCH | 817855 | 20240204 | 937 | 20240208 | 1542 | 2365090 | 6125 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 637 | 3901625 | 37.1971 | -122.1543 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0021622 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1913004 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | SWITCH | 46429 | 20240204 | 937 | 20240208 | 136 | 2365331 | 5279 | Distribution Circuit | Vegetation | Tree - fell into line | 119 | 621025 | 37.167 | -122.1668 | Yes | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021622 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1913054 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 12124 | 20240204 | 937 | 20240208 | 43 | 2365336 | 5226 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 403 | 2106078 | 37.1677 | -122.1662 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0021622 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1913058 | 0 | EPSS Ckt | N | 2024 | NA
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 8915 | 20240204 | 937 | 20240208 | 1434 | 2365848 | 6057 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 72684 | 37.1665 | -122.1671 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023856 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1913231 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 2251 | 20240204 | 937 | 20240208 | 1810 | 2368710 | 6273 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 125460 | 37.1702 | -122.1646 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024697 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1913749 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 5066 | 20240204 | 937 | 20240209 | 1853 | 2368714 | 7756 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 286972 | 37.1706 | -122.1655 | Yes | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021622 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1913750 | 0 | EPSS Ckt | N | 2024 | NA
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRIP-SAVER | 6219 | 20240204 | 937 | 20240208 | 1755 | 2368915 | 6258 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 137676 | 37.1841 | -122.1409 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024811 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1913842 | 0 | EPSS Ckt | N | 2024 | NONE
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 2913 | 20240204 | 937 | 20240208 | 1542 | 2368928 | 6125 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 42875 | 37.1752 | -122.1446 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024844 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1913875 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9133 | 20240204 | 937 | 20240208 | 1908 | 2368935 | 6331 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 88634 | 37.1779 | -122.12 | Yes | Clear-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0024882 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1913911 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9753 | 20240204 | 937 | 20240209 | 1024 | 2368980 | 7247 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 152187 | 37.1656 | -122.1639 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0025053 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1914083 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 2923 | 20240204 | 937 | 20240208 | 1611 | 2369008 | 6154 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 289238 | 37.1737 | -122.1456 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0025148 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1914177 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 871 | 20240204 | 938 | 20240204 | 1755 | 2336432 | 497 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 2982 | 36.8187 | -121.6857 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0020609 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1910429 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1101 | 182201101 | RECLOSER | 965598 | 20240204 | 938 | 20240204 | 2030 | 2336444 | 652 | Distribution Circuit | Equipment Failure/Involved | Overhead | 167 | 108884 | 36.5774 | -121.4917 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0019408 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1909290 | 0 | Non-EPSS | N | 2024 | NONE
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | RECLOSER | 131442 | 20240204 | 947 | 20240204 | 1709 | 2335647 | 442 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3882 | 401305 | 36.6744 | -121.79 | Yes | Overcast-Rain;32-90 F | Pole-Wood | Broken | 24-0019424 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1909303 | 0 | EPSS Ckt | N | 2024 | NONE
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | SWITCH | 400551 | 20240204 | 949 | 20240207 | 1123 | 2359145 | 4414 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 322222 | 37.1289 | -122.1656 | Yes | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021615 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1911603 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 643012 | 20240204 | 949 | 20240207 | 1145 | 2359151 | 4436 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 79848 | 37.1026 | -122.1415 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0021615 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1911606 | 0 | EPSS Ckt | N | 2024 | NA
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 3583 | 20240204 | 949 | 20240208 | 1948 | 2361336 | 6359 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 89026 | 37.1389 | -122.1011 | Yes | Clear-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0022485 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1912122 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 8125 | 20240204 | 949 | 20240207 | 1146 | 2365032 | 4437 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 93177 | 37.099 | -122.1424 | Yes | Clear-Strong Winds;32-90 F | Crossarm- Wood | Broken | 24-0023581 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1912989 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 2887 | 20240204 | 949 | 20240207 | 1822 | 2365307 | 4833 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 9666 | 37.1394 | -122.0948 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021615 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1913041 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 12838 | 20240204 | 949 | 20240208 | 1746 | 2365522 | 6237 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 492723 | 37.1272 | -122.1236 | Yes | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021615 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1913107 | 0 | EPSS Ckt | N | 2024 | NA
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | SWITCH | 8621 | 20240204 | 949 | 20240208 | 1746 | 2365524 | 6237 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 170 | 1060290 | 37.1337 | -122.1381 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0021615 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1913108 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9597 | 20240204 | 949 | 20240207 | 1455 | 2365581 | 4626 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 23130 | 37.1442 | -122.0895 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023732 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1913122 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5477 | 20240204 | 949 | 20240207 | 1445 | 2365865 | 4616 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 230800 | 37.1292 | -122.1143 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023864 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1913239 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRANSFORMER | 315252523770 | 20240204 | 949 | 20240208 | 347 | 2367927 | 5398 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 59378 | 37.1419 | -122.1274 | Yes | Clear-Strong Winds;32-90 F | Transformer (OH) | Failed/Faulted | 24-0024471 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1913588 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRANSFORMER | 315226324463 | 20240204 | 949 | 20240208 | 310 | 2367986 | 5361 | Transformer only | Vegetation | Tree - fell into line | 5 | 26805 | 37.1608 | -122.1365 | Yes | Clear-Strong Winds;32-90 F | Secondary | Broken- wire on ground | 24-0024489 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1913598 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | JUMPER | #2 JUMPER BLOWN | 20240204 | 949 | 20240204 | 1543 | 2342757 | 354 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 2832 | 36.4725 | -121.4023 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Jumper | Burned Open | 24-0020121 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1909950 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | RECLOSER | 2628 | 20240204 | 950 | 20240207 | 1558 | 2336647 | 4688 | Distribution Circuit | Vegetation | Tree - fell into line | 1618 | 2881732 | 36.5603 | -121.919 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken | 24-0021521 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911359 | 0 | EPSS Ckt | N | 2024 | A & B
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | RECLOSER | 86496 | 20240204 | 954 | 20240209 | 1554 | 2338167 | 7560 | Distribution Circuit | Vegetation | Tree - bark fell into line | 2547 | 5227126 | 36.5937 | -121.873 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021068 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1910891 | 0 | EPSS Ckt | N | 2024 | B/GRD
CENTRAL COAST | SALINAS | GONZALES-1103 | 182131103 | JUMPER | OPEN JUMPER 2 SPANS LD SIDE OF 25749 | 20240204 | 954 | 20240204 | 1811 | 2338235 | 497 | Distribution Circuit | Equipment Failure/Involved | Overhead | 60 | 28764 | 36.5073 | -121.4423 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Jumper | Burned Open | 24-0019607 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1909474 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 1527 | 20240204 | 954 | 20240206 | 2208 | 2336689 | 3614 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 14456 | 37.0303 | -121.9339 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0023883 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913254 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | OCB | 2109/2 | 20240204 | 1000 | 20240204 | 2054 | 2344972 | 654 | Distribution Circuit | Vegetation | Tree - bark fell into line | 5574 | 3645396 | 36.9926 | -121.982 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0020760 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1910579 | 0 | EPSS Ckt | N | 2024 | B-C
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | TRANSFORMER | 411435245911 | 20240204 | 1002 | 20240206 | 1533 | 2336845 | 3211 | Transformer only | Vegetation | Tree - branch fell on line | 18 | 57798 | 36.5581 | -121.9181 | Yes | Rain-Overcast;32-90 F | Service conductor | Broken | 24-0023464 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912902 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 6921 | 20240204 | 1006 | 20240207 | 1221 | 2359045 | 4455 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 218295 | 36.5546 | -121.9156 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021838 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1911583 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | RECLOSER | 9106 | 20240204 | 1007 | 20240206 | 1327 | 2337526 | 3080 | Distribution Circuit | Vegetation | Tree - fell into line | 821 | 863724 | 36.5917 | -121.8675 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021188 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1911014 | 0 | EPSS Ckt | N | 2024 | B-C-GRD
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | FUSE | 98783 | 20240204 | 1013 | 20240204 | 2025 | 2351898 | 612 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 612 | 36.6908 | -121.7575 | Yes | Clear;32-90 F | Other | Normal | 24-0020802 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1910621 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | RECLOSER | 36922 | 20240204 | 1019 | 20240205 | 1417 | 2337072 | 1678 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 30155 | 36.6956 | -121.7354 | Yes | Clear;32-90 F | Pole-Wood | Broken | 24-0019483 | OH | Sus | 35528881 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1909356 | 0 | EPSS Ckt | N | 2024 | N/A
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 67520 | 20240204 | 1019 | 20240204 | 1139 | 2337056 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2683 | 214640 | 36.9577 | -121.8525 | Yes | Clear;32-90 F |  |  | 24-0019609 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909476 | 0 | EPSS Ckt | N | 2024 | C GRD
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 2761 | 20240204 | 1019 | 20240205 | 1920 | 2361799 | 1981 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 98616 | 36.5514 | -121.9242 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Transformer (OH) | Broken | 24-0022624 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1912252 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | FUSE | 78633 | 20240204 | 1020 | 20240206 | 1918 | 2337177 | 3418 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 140138 | 36.9636 | -121.9752 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0021567 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911385 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 7299 | 20240204 | 1021 | 20240208 | 1426 | 2337104 | 6005 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 78065 | 37.0308 | -122.0939 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026080 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1915043 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | JUMPER | OJ AT CGC 315028519310 | 20240204 | 1024 | 20240206 | 2321 | 2343030 | 3657 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 3657 | 37.0177 | -122.2037 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020151 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1909979 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 8915 | 20240204 | 1025 | 20240206 | 1836 | 2349643 | 3371 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 74162 | 36.5781 | -121.928 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Together | 24-0020602 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1910422 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 1445 | 20240204 | 1025 | 20240208 | 1638 | 2337184 | 6133 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 59838 | 36.5735 | -121.9108 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021700 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1911472 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | TRANSFORMER | 316260016107 | 20240204 | 1033 | 20240204 | 1932 | 2337285 | 539 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 2156 | 36.9352 | -121.7802 | Yes | Overcast-Fog-Drizzle-Strong Winds;32-90 F | Transformer (OH) | Failed/Faulted | 24-0019581 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909452 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0424 | 182440424 | RECLOSER | 2610 | 20240204 | 1035 | 20240208 | 1509 | 2339486 | 6034 | Distribution Circuit | Vegetation | Tree - fell into line | 1178 | 2060049 | 36.6225 | -121.9268 | Yes | Overcast-Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0021557 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | Yes | No | 1911380 | 0 | Non-EPSS | N | 2024 | A C GRD
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 6799 | 20240204 | 1035 | 20240207 | 1820 | 2364678 | 4785 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 186615 | 36.5903 | -121.9583 | Yes | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0023475 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1912908 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 6753 | 20240204 | 1036 | 20240210 | 1818 | 2347445 | 9102 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 345876 | 36.5659 | -121.8876 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0020422 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1910249 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-1101 | 182221101 | FUSE | 9333 | 20240204 | 1037 | 20240205 | 1556 | 2339245 | 1759 | Distribution Circuit | Equipment Failure/Involved | Overhead | 115 | 202973 | 36.6161 | -121.8249 | Yes | Overcast-Rain-Strong Winds;32-90 F | Jumper | Burned Open | 24-0021591 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1911400 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 8427 | 20240204 | 1037 | 20240205 | 1249 | 2359181 | 1572 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 25127 | 36.5921 | -121.8464 | Yes | Overcast-Rain;32-90 F |  |  | 24-0021874 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911610 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 10205 | 20240204 | 1037 | 20240205 | 1314 | 2342018 | 1597 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 9582 | 36.5246 | -121.8127 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020041 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1909871 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 9629 | 20240204 | 1037 | 20240206 | 135 | 2337383 | 2338 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 467 | 1091846 | 36.5853 | -121.9054 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0022852 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | No | No | 1912487 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 2249 | 20240204 | 1038 | 20240205 | 1227 | 2337415 | 1549 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 59 | 90784 | 36.5968 | -121.8553 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0021964 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911691 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 1263 | 20240204 | 1039 | 20240205 | 1210 | 2337551 | 1531 | Distribution Circuit | Equipment Failure/Involved | Overhead | 216 | 331385 | 36.5981 | -121.8534 | Yes | Overcast-Rain-Strong Winds;32-90 F | Cutout- fuse holder | Broken | 24-0021942 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911670 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0422 | 182440422 | FUSE | 2581 | 20240204 | 1040 | 20240207 | 1842 | 2337429 | 4802 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 460992 | 36.5918 | -121.9454 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023277 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1912768 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | FUSE | 4353 | 20240204 | 1042 | 20240204 | 1245 | 2337442 | 123 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 8 | 984 | 36.7688 | -121.4125 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0021610 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911415 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | OTHER | 2636 | 20240204 | 1044 | 20240205 | 1849 | 2337080 | 1925 | Distribution Circuit | Vegetation | Tree - fell into line | 109 | 209825 | 36.5516 | -121.9243 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022559 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1912185 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | SWITCH | UN-NUMMBERED SBCO 1 LD SIDE OF 3965 | 20240204 | 1045 | 20240204 | 2045 | 2335774 | 600 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 9600 | 36.9605 | -122.0274 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken | 24-0019578 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1909449 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 597 | 20240204 | 1046 | 20240207 | 1709 | 2339277 | 4703 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 28218 | 36.9525 | -121.782 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022629 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1912259 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | RECLOSER | 7004 | 20240204 | 1052 | 20240205 | 1153 | 2337692 | 1501 | Distribution Circuit | Vegetation | Tree - fell into line | 150 | 225150 | 35.9367 | -121.0781 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021683 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1911462 | 0 | EPSS Ckt | N | 2024 | C/GRD
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | RECLOSER | 2101/2 | 20240204 | 1055 | 20240204 | 1151 | 2337715 | 56 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2883 | 80353 | 36.9032 | -121.7565 | Yes | Overcast-Rain;32-90 F |  |  | 24-0019559 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | No | No | 1909427 | 0 | EPSS Ckt | N | 2024 | BC GRD
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | FUSE | 10435 | 20240204 | 1056 | 20240205 | 1726 | 2337668 | 1830 | Distribution Circuit | Vegetation | Tree - branch fell on line | 260 | 475800 | 36.6935 | -121.7969 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0019868 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909706 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 1113 | 20240204 | 1103 | 20240204 | 1602 | 2337755 | 299 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 95 | 28405 | 36.926 | -121.7457 | Yes | Overcast;32-90 F |  |  | 24-0020359 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1910187 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | FUSE | 10449 | 20240204 | 1108 | 20240205 | 1649 | 2338046 | 1781 | Distribution Circuit | Equipment Failure/Involved | Overhead | 121 | 215501 | 36.6871 | -121.801 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Connector or Splice (OH) | Broken | 24-0021727 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911491 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | INTERRUPTER | 594940 | 20240204 | 1115 | 20240205 | 1757 | 2336852 | 1842 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1005 | 1851210 | 36.5609 | -121.9198 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0022536 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912165 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SAN ARDO-1101 | 182191101 | FUSE | 7099 | 20240204 | 1117 | 20240204 | 1805 | 2338052 | 408 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 4488 | 36.0566 | -121.0005 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0019826 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909667 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0421 | 182440421 | TRANSFORMER | 411475048082 | 20240204 | 1119 | 20240205 | 1841 | 2338016 | 1882 | Transformer only | Unknown Cause | Patrol - not conducted | 20 | 37640 | 36.6185 | -121.9073 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0022620 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1912247 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 2529 | 20240204 | 1120 | 20240204 | 1508 | 2339522 | 228 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 119 | 27132 | 36.6028 | -121.9308 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0020050 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909878 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 2303 | 20240204 | 1121 | 20240206 | 1829 | 2356688 | 3308 | Distribution Circuit | Vegetation | Tree - fell into line | 113 | 348932 | 36.5894 | -121.8975 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021464 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1911299 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 10769 | 20240204 | 1121 | 20240205 | 1804 | s1912044 | 1843 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 611 | 1126073 | 36.6099 | -121.9114 | Yes | Clear;32-90 F |  |  | 24-0020437 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1912044 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 7103 | 20240204 | 1121 | 20240207 | 1908 | 2361610 | 4787 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 373386 | 36.6106 | -121.9169 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022579 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1912207 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | RECLOSER | 9094 | 20240204 | 1122 | 20240206 | 1634 | 2337178 | 3192 | Distribution Circuit | Vegetation | Tree - branch fell on line | 324 | 679666 | 36.5607 | -121.915 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021777 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1911530 | 0 | EPSS Ckt | N | 2024 | A & GRD
CENTRAL COAST | SALINAS | SALINAS-1102 | 182011102 | JUMPER | BURN OJ | 20240204 | 1124 | 20240204 | 2030 | 2338056 | 546 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2460 | 192375 | 36.6887 | -121.6109 | Yes | Overcast-Rain-Strong Winds;32-90 F | Jumper | Burned Open | 24-0019917 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1909751 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 861255 | 20240204 | 1127 | 20240205 | 1606 | 2338120 | 1719 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 27504 | 36.5604 | -121.9199 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0022333 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911986 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | OCB | 1101/2 | 20240204 | 1128 | 20240205 | 1109 | 2338866 | 1421 | Distribution Circuit | Vegetation | Tree - fell into line | 2951 | 793002 | 36.5569 | -121.8976 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Together | 24-0019727 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909576 | 0 | EPSS Ckt | N | 2024 | B & C PHASE
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 495039 | 20240204 | 1130 | 20240205 | 1354 | 2338155 | 1584 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 40 | 63360 | 36.5692 | -121.9118 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0022073 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911778 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | FUSE | 2445 | 20240204 | 1139 | 20240206 | 930 | 2338409 | 2751 | Distribution Circuit | Equipment Failure/Involved | Overhead | 395 | 1086645 | 36.6151 | -121.9078 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022838 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1912472 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 8947 | 20240204 | 1140 | 20240209 | 950 | 2367128 | 7090 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 163070 | 36.4994 | -121.9336 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Insulator | Broken | 24-0024218 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1913448 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 4439 | 20240204 | 1141 | 20240204 | 1720 | 2338418 | 339 | Distribution Circuit | Vegetation | Tree - bark fell into line | 3 | 1017 | 36.7754 | -121.6769 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0020542 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1910364 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 67520 | 20240204 | 1142 | 20240204 | 1515 | 2338681 | 213 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1342 | 285846 | 36.9577 | -121.8525 | Yes | Overcast-Rain;32-90 F |  |  | 24-0019682 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1909538 | 0 | EPSS Ckt | N | 2024 | NA
CENTRAL COAST | MONTEREY | LAURELES-1112 | 182371112 | RECLOSER | 438 | 20240204 | 1146 | 20240205 | 1554 | 2338646 | 1688 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 236 | 398368 | 36.4967 | -121.7313 | Yes | Clear;32-90 F |  |  | 24-0022288 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911943 | 0 | EPSS Ckt | N | 2024 | A C
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 9231 | 20240204 | 1148 | 20240205 | 1237 | 2359326 | 1489 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 1489 | 36.5924 | -121.852 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0021921 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911651 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 2487 | 20240204 | 1200 | 20240207 | 1520 | 2338712 | 4520 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 85880 | 37.0454 | -122.1097 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0019643 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1909506 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 7799 | 20240204 | 1207 | 20240208 | 1327 | 2338828 | 5840 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 325582 | 37.091 | -122.1396 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019975 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1909809 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | TRIP-SAVER | 4929 | 20240204 | 1211 | 20240204 | 1817 | 2338803 | 366 | Distribution Circuit | Vegetation | Tree - fell into line | 133 | 48678 | 36.9129 | -121.8055 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019830 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1909671 | 0 | EPSS Ckt | N | 2024 | BC
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0422 | 182440422 | RECLOSER | 2614 | 20240204 | 1214 | 20240207 | 1840 | 2339689 | 4706 | Distribution Circuit | Vegetation | Tree - fell into line | 416 | 1767178 | 36.6076 | -121.9243 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023160 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1912692 | 0 | EPSS Ckt | N | 2024 | C & GRD
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0422 | 182440422 | TRANSFORMER | 411330947464 | 20240204 | 1214 | 20240207 | 1937 | 2364018 | 4706 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 23530 | 36.6002 | -121.9553 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Jumper | Burned Open | 24-0023160 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1912736 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | FUSE | 8629 | 20240204 | 1216 | 20240206 | 1555 | 2339169 | 3099 | Distribution Circuit | Vegetation | Tree - branch fell on line | 72 | 223240 | 36.4489 | -121.7158 | Yes | Clear;32-90 F | Fuse | Normal | 24-0023600 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913003 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | FUSE | 1259 | 20240204 | 1223 | 20240205 | 1800 | 2339109 | 1777 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 58641 | 36.3983 | -121.6482 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0022596 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1912225 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | RECLOSER | 2101/2 | 20240204 | 1224 | 20240204 | 1759 | 2339107 | 335 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2883 | 502405 | 36.9032 | -121.7565 | Yes | Overcast-Rain-Strong Winds;32-90 F | Switch (OH) | Burned/flashed | 24-0019690 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | No | No | 1909545 | 0 | EPSS Ckt | N | 2024 | BC GRD
CENTRAL COAST | KING CITY | LOS COCHES-1101 | 182151101 | FUSE | 9031 | 20240204 | 1232 | 20240207 | 2036 | 2339224 | 4804 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 33628 | 36.328 | -121.315 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020537 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1910359 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | PACIFIC GROVE SUB | 18244 | OCB | 423/2 | 20240204 | 1238 | 20240205 | 915 | 2342145 | 1237 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 536 | 663032 | 36.6171 | -121.9192 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0021657 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911443 | 0 | Non-EPSS | N | 2024 | INST
CENTRAL COAST | SALINAS | SALINAS-1102 | 182011102 | FUSE | 4993 | 20240204 | 1238 | 20240204 | 1508 | s1909983 | 150 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 57 | 8550 | 36.6904 | -121.616 | Yes | Clear;32-90 F |  |  | 24-0020155 |  | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909983 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 1391 | 20240204 | 1244 | 20240208 | 1653 | 2370139 | 6009 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 24036 | 36.5761 | -121.8998 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026295 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1915136 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2105 | 182402105 | JUMPER | JUMPER 5P E/OF CGC# 411768448909 | 20240204 | 1250 | 20240204 | 1841 | 2346538 | 351 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1901 | 667251 | 36.6439 | -121.8054 | Yes | Overcast-Rain-Strong Winds;32-90 F | Jumper | Burned Open | 24-0020373 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1910201 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 1859 | 20240204 | 1252 | 20240209 | 1205 | 2364295 | 7153 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 35765 | 37.0939 | -122.1443 | Yes | Clear-Strong Winds;32-90 F | Crossarm- Wood | Broken | 24-0019975 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1912811 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | JUMPER | JPRS 2 SS OF CGC 315229021430 | 20240204 | 1256 | 20240208 | 1935 | 2369643 | 6159 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 30795 | 37.0772 | -122.1354 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026137 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1915070 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SOLEDAD-2105 | 182052105 | FUSE | 9903 | 20240204 | 1303 | 20240209 | 938 | 2357285 | 6995 | Distribution Circuit | 3rd Party | Customer Equipment | 2 | 13990 | 36.3733 | -121.2392 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0021748 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911504 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0422 | 182440422 | TRANSFORMER | 411416747667 | 20240204 | 1305 | 20240208 | 1834 | 2364385 | 6089 | Transformer only | Vegetation | Tree - branch fell on line | 20 | 121780 | 36.6066 | -121.9263 | Yes | Strong Winds-Rain-Overcast;32-90 F | Secondary | Broken- wire on ground | 24-0023357 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912830 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 8315 | 20240204 | 1316 | 20240208 | 1113 | 2368302 | 5637 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 101466 | 37.0995 | -122.1181 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021577 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1913663 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 2283 | 20240204 | 1316 | 20240208 | 1357 | 2368543 | 5801 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 23204 | 37.1011 | -122.1128 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021577 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1913709 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 11103 | 20240204 | 1326 | 20240206 | 1353 | 2340126 | 2907 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 22051 | 36.9935 | -122.0701 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020031 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | Yes | No | 1909862 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 9423 | 20240204 | 1355 | 20240204 | 1520 | 2340631 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 2295 | 37.077 | -122.0862 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0020131 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909960 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 2191 | 20240204 | 1359 | 20240206 | 410 | 2340812 | 2291 | Distribution Circuit | Vegetation | Tree - branch fell on line | 56 | 128296 | 37.0515 | -122.0216 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0022905 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1912541 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 8929 | 20240204 | 1359 | 20240208 | 58 | 2340907 | 4979 | Distribution Circuit | Vegetation | Tree - branch fell on line | 57 | 283803 | 37.0661 | -122.0844 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0025348 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1914370 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | SWITCH | 11010 | 20240204 | 1400 | 20240209 | 847 | 2368296 | 6829 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 138 | 89191 | 37.1053 | -122.0517 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0021577 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1913659 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | SWITCH | 89251 | 20240204 | 1400 | 20240208 | 1808 | 2368243 | 6008 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 90120 | 37.1183 | -122.1137 | Yes | Clear-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0024569 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1913645 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 10719 | 20240204 | 1400 | 20240209 | 1128 | 2368227 | 7048 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 56384 | 37.0863 | -122.1043 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024563 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1913640 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 10717 | 20240204 | 1400 | 20240209 | 1128 | 2368306 | 7048 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 126864 | 37.0913 | -122.1045 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021577 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1913666 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 9691 | 20240204 | 1400 | 20240208 | 1234 | 2368549 | 5674 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 113480 | 37.095 | -122.1387 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021577 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1913710 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 538096 | 20240204 | 1400 | 20240209 | 1316 | 2344273 | 7156 | Distribution Circuit | Vegetation | Tree - branch fell on line | 915 | 4035233 | 37.0578 | -122.0595 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022587 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1912215 | 0 | EPSS Ckt | N | 2024 | C 51 TIME
CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | FUSE | 8997 | 20240204 | 1401 | 20240208 | 1715 | 2341039 | 5954 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 17862 | 36.0219 | -121.2481 | Yes | Clear-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0021354 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | Yes | No | 1911188 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 11943 | 20240204 | 1402 | 20240205 | 2205 | 2362545 | 1923 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 79 | 151917 | 37.0112 | -122.0442 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0022823 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1912459 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 7243 | 20240204 | 1410 | 20240206 | 41 | 2341073 | 2071 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 24852 | 37.0737 | -122.0847 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0022858 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912493 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 3233 | 20240204 | 1414 | 20240205 | 2001 | 2358206 | 1787 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 69693 | 37.0325 | -122.0628 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021644 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1911435 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2107 | 182402107 | FUSE | 6051 | 20240204 | 1434 | 20240205 | 1116 | 2341740 | 1242 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 24840 | 36.6805 | -121.7948 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0021801 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911549 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 11939 | 20240204 | 1440 | 20240206 | 939 | 2362546 | 2579 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 71 | 183109 | 37.0106 | -122.0442 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0022821 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1912457 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 195 | 20240204 | 1445 | 20240206 | 248 | 2342063 | 2163 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 32445 | 37.0831 | -122.081 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0022887 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1912521 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | FUSE | 4971 | 20240204 | 1448 | 20240204 | 2146 | 2342153 | 418 | Distribution Circuit | Vegetation | Tree - branch fell on line | 134 | 55956 | 36.9738 | -121.9509 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0020932 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1910752 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | FUSE | 9731 | 20240204 | 1449 | 20240207 | 1533 | 2342266 | 4364 | Distribution Circuit | Equipment Failure/Involved | Overhead | 58 | 238640 | 36.3064 | -121.2637 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020431 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1910258 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | JUMPER | OJ'S 1 WEST OF CGC# 411410547541 | 20240204 | 1457 | 20240206 | 1746 | 2345081 | 3049 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 64029 | 36.603 | -121.9288 | Yes | Clear;32-90 F | Insulator | Broken- wire on ground | 24-0020282 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | Yes | 1910111 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 6087 | 20240204 | 1504 | 20240206 | 230 | 2342684 | 2126 | Distribution Circuit | Vegetation | Tree - fell into line | 186 | 395436 | 37.0665 | -122.0336 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0022875 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1912510 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 9591 | 20240204 | 1506 | 20240204 | 1600 | 2342652 | 54 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 1187 | 36.9161 | -121.3532 | Yes | Clear;32-90 F |  |  | 24-0020292 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1910121 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | SWITCH | 8729 | 20240204 | 1507 | 20240207 | 1833 | 2359430 | 4526 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 391188 | 37.0882 | -122.0884 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021918 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1911665 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 6085 | 20240204 | 1509 | 20240208 | 29 | 2342749 | 4880 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 53680 | 37.0636 | -122.0348 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0023979 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1913315 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | FUSE | 12265 | 20240204 | 1511 | 20240205 | 844 | 2342813 | 1053 | Distribution Circuit | Vegetation | Tree - bark fell into line | 72 | 75816 | 36.9588 | -121.9805 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0021602 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911408 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 9659 | 20240204 | 1515 | 20240205 | 1805 | 2356882 | 1610 | Distribution Circuit | Equipment Failure/Involved | Overhead | 43 | 69230 | 36.9746 | -122.0591 | Yes | Overcast-Rain-Strong Winds;32-90 F | Fuse | Broken | 24-0021637 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911431 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | SWITCH | 794081 | 20240204 | 1515 | 20240207 | 1322 | 2361321 | 4207 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 155879 | 37.0344 | -121.8205 | Yes | Clear;32-90 F | Conductor- Overhead | On Ground | 24-0022483 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | Yes | 1912121 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | RECLOSER | 9118 | 20240204 | 1515 | 20240207 | 2200 | 2364848 | 4725 | Distribution Circuit | Vegetation | Tree - fell into line | 455 | 2062296 | 36.6037 | -121.9359 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019877 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1912948 | 0 | EPSS Ckt | N | 2024 | NA
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 5819 | 20240204 | 1529 | 20240207 | 1406 | 2361363 | 4237 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 254220 | 37.0449 | -121.8139 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022496 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1912134 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 422016 | 20240204 | 1530 | 20240206 | 1414 | 2353526 | 2804 | Distribution Circuit | Vegetation | Tree - fell into line | 837 | 1436085 | 36.964 | -121.8086 | Yes | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Normal | 24-0022009 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911727 | 0 | EPSS Ckt | N | 2024 | C/GRD T
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | SWITCH | 10745 | 20240204 | 1531 | 20240205 | 1655 | 2351166 | 1524 | Distribution Circuit | Vegetation | Tree - branch fell on line | 721 | 217981 | 36.9366 | -121.8624 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020734 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1910554 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | FUSE | 7227 | 20240204 | 1535 | 20240205 | 1230 | 2343950 | 1255 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 4 | 5020 | 35.9778 | -121.2147 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0021437 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911272 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 181 | 20240204 | 1543 | 20240206 | 102 | 2345445 | 1999 | Distribution Circuit | Vegetation | Tree - branch fell on line | 56 | 111944 | 37.0628 | -122.0336 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0022857 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1912492 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 1847 | 20240204 | 1544 | 20240208 | 1115 | s1913442 | 5491 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 5491 | 37.0635 | -122.0696 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024205 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1913442 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5239 | 20240204 | 1546 | 20240206 | 1740 | 2344410 | 2994 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 122754 | 37.0682 | -122.0827 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022534 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1912163 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 5319 | 20240204 | 1605 | 20240210 | 30 | 2345994 | 7705 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 192432 | 37.0019 | -122.0318 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0023926 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913289 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 91034 | 20240204 | 1606 | 20240208 | 1236 | 2346612 | 5550 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 174930 | 37.0944 | -122.1411 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020378 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1910206 | 0 | EPSS Ckt | N | 2024 | AB T
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 9569 | 20240204 | 1609 | 20240207 | 1024 | 2349996 | 3975 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 41 | 162975 | 36.9783 | -121.8269 | Yes | Partly Cloudy-Rain;32-90 F |  |  | 24-0022876 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1912511 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 5957 | 20240204 | 1611 | 20240205 | 1855 | 2345564 | 1604 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 32080 | 37.0051 | -121.9393 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0022565 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912192 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 7637 | 20240204 | 1618 | 20240206 | 1901 | 2346067 | 3043 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 82161 | 37.0078 | -121.9385 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0022659 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912294 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 2199 | 20240204 | 1619 | 20240207 | 1408 | 2347435 | 4189 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 121481 | 36.9517 | -121.834 | Yes | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022895 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1912531 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 100000003290 | 20240204 | 1620 | 20240204 | 1636 | 2346012 | 16 | Transformer only | Unknown Cause | Patrol - found nothing | 9 | 144 | 36.8261 | -121.7256 | Yes | Clear;32-90 F |  |  | 24-0020660 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1910481 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | SWITCH | 3611 | 20240204 | 1621 | 20240204 | 1632 | 2345500 | 11 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 66 | 36.9143 | -121.8078 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0020313 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1910142 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 370732 | 20240204 | 1628 | 20240208 | 1715 | 2346545 | 5807 | Distribution Circuit | Vegetation | Tree - fell into line | 431 | 801635 | 37.0534 | -122.0438 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0022424 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | No | No | 1912072 | 0 | EPSS Ckt | N | 2024 | ABC
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 153 | 20240204 | 1628 | 20240206 | 1237 | 2361742 | 2649 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 31788 | 37.0523 | -122.0525 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022424 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1912235 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | JUMPER | OJ 1 P SS OF CGC# 315471420334 | 20240204 | 1628 | 20240206 | 1530 | 2361910 | 2822 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 11288 | 37.0479 | -122.0535 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022424 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1912275 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 9517 | 20240204 | 1630 | 20240207 | 1152 | 2346493 | 4042 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 76798 | 37.0204 | -122.02 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0024229 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913452 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 9443 | 20240204 | 1631 | 20240207 | 1419 | 2346551 | 4188 | Distribution Circuit | Vegetation | Tree - fell into line | 99 | 403613 | 37.0818 | -122.0734 | Yes | Clear-Strong Winds;32-90 F | Crossarm- Wood | Broken | 24-0023934 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913295 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | OTHER | 12899 | 20240204 | 1631 | 20240208 | 1806 | 2365038 | 5855 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 368865 | 37.0536 | -121.9394 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023584 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1912992 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | RECLOSER | 607772 | 20240204 | 1631 | 20240206 | 2108 | s1924706 | 3157 | Distribution Circuit | Vegetation | Tree - fell into line | 346 | 926643 | 37.0124 | -121.9527 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019317 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1924706 | 0 | EPSS Ckt | N | 2024 | B GRD
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 5967 | 20240204 | 1632 | 20240205 | 1745 | 2346553 | 1513 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 11588 | 37.0034 | -121.9547 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0022504 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1912141 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | FUSE | 8643 | 20240204 | 1637 | 20240205 | 2155 | 2346833 | 1758 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 22854 | 36.4802 | -121.713 | Yes | Clear;32-90 F |  |  | 24-0022815 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1912451 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 7763 | 20240204 | 1639 | 20240206 | 1845 | 2346935 | 3006 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 12024 | 37.0216 | -121.9331 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0023730 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1913120 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 5149 | 20240204 | 1650 | 20240209 | 1722 | 2368213 | 7232 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 36160 | 37.1109 | -122.0899 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024561 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1913638 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | OCB | 2204/2 | 20240204 | 1651 | 20240208 | 1551 | 2347659 | 5700 | Distribution Circuit | Vegetation | Tree - bark fell into line | 3631 | 5263589 | 36.5786 | -121.9084 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020437 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1910263 | 0 | EPSS Ckt | N | 2024 | ABC
CENTRAL COAST | COAST | ERTA SUB | 8351 | OCB | 403/2 | 20240204 | 1653 | 20240205 | 2113 | 2347740 | 1700 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1257 | 849310 | 36.9307 | -121.7642 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Together | 24-0021646 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911436 | 0 | Non-EPSS | N | 2024 | B GRD
CENTRAL COAST | COAST | PAUL SWEET-2103 | 83252103 | FUSE | 5395 | 20240204 | 1655 | 20240206 | 1605 | 2347698 | 2830 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 283000 | 36.9737 | -122.0156 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021764 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1911519 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 8247 | 20240204 | 1658 | 20240206 | 1547 | 2342852 | 2809 | Distribution Circuit | 3rd Party | Other | 14 | 39326 | 36.5606 | -121.9155 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0020454 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1910280 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRIP-SAVER | 9031 | 20240204 | 1706 | 20240206 | 1753 | 2348153 | 2927 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 47 | 137569 | 37.0726 | -122.0742 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0023689 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913086 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 3029 | 20240204 | 1707 | 20240205 | 2028 | 2348154 | 1641 | Distribution Circuit | Vegetation | Tree - bark fell into line | 47 | 77127 | 36.9641 | -121.8172 | Yes | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0022726 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912361 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | OTHER | WIRE DOWN E/O 8823 TWD 5095 | 20240204 | 1715 | 20240205 | 1918 | 2354750 | 1527 | Distribution Circuit | Vegetation | Tree - fell into line | 240 | 162209 | 36.9546 | -122.0277 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021104 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1910927 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | TRIP-SAVER | 3959 | 20240204 | 1715 | 20240205 | 1032 | 2348530 | 1037 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 300 | 311100 | 36.959 | -122.0316 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0021786 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911539 | 0 | EPSS Ckt | N | 2024 | AB
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | JUMPER | OPEN JUMPERS 1 SS OF 841 | 20240204 | 1717 | 20240209 | 831 | 2368358 | 6674 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6674 | 37.0339 | -121.9674 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024611 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1913677 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | FUSE | 5185 | 20240204 | 1722 | 20240208 | 830 | 2361440 | 5228 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 120244 | 37.1074 | -122.1096 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022532 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1912161 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 11044 | 20240204 | 1726 | 20240205 | 1814 | 2349043 | 1488 | Distribution Circuit | Vegetation | Tree - fell into line | 1928 | 1671592 | 37.0401 | -122.0297 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020786 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1910605 | 0 | EPSS Ckt | N | 2024 | C-GRD
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 5205 | 20240204 | 1726 | 20240205 | 1427 | 2352264 | 1280 | Distribution Circuit | Vegetation | Tree - fell into line | 237 | 303360 | 37.0417 | -122.0728 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020835 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1910653 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 1775 | 20240204 | 1726 | 20240206 | 2201 | s1913252 | 3155 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 3155 | 36.9837 | -121.8654 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0023881 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913252 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | OTHER | 10645 | 20240204 | 1730 | 20240207 | 1748 | 2349015 | 4338 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 321012 | 37.0831 | -122.0878 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021918 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1911648 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 4999 | 20240204 | 1731 | 20240206 | 1044 | 2353126 | 2473 | Distribution Circuit | Vegetation | Tree - bark fell into line | 16 | 39165 | 36.9914 | -121.9845 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0023149 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912682 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | TRANSFORMER | 315477917219 | 20240204 | 1733 | 20240206 | 1638 | 2354857 | 2825 | Transformer only | Vegetation | Tree - branch fell on line | 16 | 45200 | 36.9617 | -122.0476 | Yes | Rain-Overcast-Fog;32-90 F | Transformer | Broken | 24-0023540 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912958 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 7675 | 20240204 | 1733 | 20240207 | 1330 | 2349168 | 4077 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 65232 | 36.9692 | -122.0502 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024184 | OH | Sus | 31683440 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1913430 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 6095 | 20240204 | 1740 | 20240208 | 1306 | 2349420 | 5486 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 104234 | 37.0209 | -122.0264 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024056 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1913354 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 2321 | 20240204 | 1740 | 20240206 | 1948 | 2363328 | 3005 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 28019 | 37.0048 | -121.8624 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0023800 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913175 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 6081 | 20240204 | 1741 | 20240205 | 2253 | 2349473 | 1752 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 28032 | 37.0577 | -122.0333 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0022831 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1912466 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | RECLOSER | 955754 | 20240204 | 1748 | 20240205 | 1810 | 2349440 | 1462 | Distribution Circuit | Vegetation | Tree - branch fell on line | 567 | 223384 | 36.9648 | -121.9738 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020604 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | Yes | 1910424 | 0 | Non-EPSS | N | 2024 | NONE
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | RECLOSER | 36982 | 20240204 | 1810 | 20240205 | 1650 | 2350464 | 1360 | Distribution Circuit | Equipment Failure/Involved | Overhead | 172 | 69811 | 36.5301 | -121.4747 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020666 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | Yes | No | 1910487 | 0 | EPSS Ckt | N | 2024 | AB GRD
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 2455 | 20240204 | 1811 | 20240208 | 2012 | 2350491 | 5881 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 46784 | 37.0111 | -121.9871 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022045 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1911757 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 6477 | 20240204 | 1816 | 20240204 | 1841 | 2350526 | 25 | Distribution Circuit | Vegetation | Tree - bark fell into line | 427 | 10675 | 36.8655 | -121.7346 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0020825 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1910644 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 8951 | 20240204 | 1819 | 20240205 | 1851 | 2338861 | 1631 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 79919 | 36.5674 | -121.9158 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022055 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1911763 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 6371 | 20240204 | 1829 | 20240207 | 1338 | 2355042 | 4029 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 44319 | 36.8639 | -121.7228 | Yes | Clear;32-90 F |  |  | 24-0021458 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911293 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 3899 | 20240204 | 1833 | 20240208 | 1105 | 2350949 | 5312 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 58432 | 36.948 | -121.8501 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022844 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1912478 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 4677 | 20240204 | 1836 | 20240205 | 2347 | 2351180 | 1751 | Distribution Circuit | Vegetation | Tree - bark fell into line | 88 | 154088 | 36.9713 | -121.8229 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0022793 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1912428 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 1943 | 20240204 | 1845 | 20240207 | 1815 | 2351328 | 4290 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 24590 | 36.9865 | -121.8527 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023040 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1912608 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2105 | 182402105 | RECLOSER | 66836 | 20240204 | 1850 | 20240205 | 1230 | 2352090 | 1060 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 954 | 1011240 | 36.6436 | -121.81 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F |  |  | 24-0021955 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | No | No | 1911682 | 0 | EPSS Ckt | N | 2024 | AC&GRD
CENTRAL COAST | MONTEREY | DEL MONTE-1101 | 182221101 | TRANSFORMER | 411665047502 | 20240204 | 1854 | 20240205 | 1205 | 2351517 | 1031 | Transformer only | Equipment Failure/Involved | Overhead | 23 | 23713 | 36.6039 | -121.8414 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Connector or Splice (OH) | Broken | 24-0021726 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911490 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 921168 | 20240204 | 1855 | 20240209 | 1254 | 2365586 | 6839 | Distribution Circuit | Vegetation | Tree - fell into line | 143 | 977977 | 37.1431 | -122.1317 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021615 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1913124 | 0 | EPSS Ckt | N | 2024 | NA
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6545 | 20240204 | 1856 | 20240206 | 1311 | 2360958 | 2535 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 63375 | 36.9404 | -121.8542 | Yes | Overcast-Rain;32-90 F |  |  | 24-0023290 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912779 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 11523 | 20240204 | 1921 | 20240205 | 1224 | 2358862 | 1023 | Distribution Circuit | Vegetation | Tree - bark fell into line | 15 | 15345 | 36.8839 | -121.7257 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0021992 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911711 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | SWITCH | 653707 | 20240204 | 1938 | 20240209 | 831 | 2365058 | 6533 | Distribution Circuit | Vegetation | Tree - fell into line | 237 | 1053299 | 37.0099 | -121.9648 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0023744 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1913131 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 4933 | 20240204 | 2029 | 20240206 | 1515 | 2353854 | 2566 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 48754 | 36.9265 | -121.816 | Yes | Partly Cloudy-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0023523 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1912943 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 931192 | 20240204 | 2042 | 20240206 | 1605 | 2354170 | 2603 | Distribution Circuit | Vegetation | Tree - fell into line | 711 | 1314825 | 36.9754 | -121.8942 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Together | 24-0021214 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911042 | 0 | EPSS Ckt | N | 2024 | AC
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 8219 | 20240204 | 2044 | 20240206 | 909 | 2354917 | 2185 | Distribution Circuit | Vegetation | Tree - fell into line | 343 | 749455 | 36.9707 | -121.8976 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021139 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1910962 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | SWITCH | 467 | 20240204 | 2048 | 20240208 | 1258 | 2354138 | 5290 | Distribution Circuit | Equipment Failure/Involved | Overhead | 59 | 312110 | 36.2958 | -121.863 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021016 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1910838 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 4217 | 20240204 | 2049 | 20240206 | 1323 | 2354151 | 2434 | Distribution Circuit | Vegetation | Tree - fell into line | 117 | 23094 | 36.9762 | -121.8816 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021028 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1910851 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 374097 | 20240204 | 2049 | 20240205 | 1919 | 2355860 | 1350 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 45536 | 36.9777 | -121.9026 | Yes | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021320 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1911153 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6911 | 20240204 | 2054 | 20240207 | 1551 | 2367518 | 4017 | Distribution Circuit | Vegetation | Tree - branch fell on line | 98 | 393666 | 37.0171 | -121.7217 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0024333 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1913520 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 3895 | 20240204 | 2054 | 20240207 | 1238 | 2354223 | 3824 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 19120 | 36.9475 | -121.853 | Yes | Partly Cloudy-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022878 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1912512 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 8187 | 20240204 | 2055 | 20240206 | 1957 | 2354231 | 2822 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 256734 | 36.9701 | -121.8856 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022518 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1912150 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | FUSE | 861 | 20240204 | 2102 | 20240205 | 2029 | 2354328 | 1407 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 43617 | 36.9875 | -121.9653 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 24-0022686 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1912322 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | SWITCH | 64964SW | 20240204 | 2114 | 20240206 | 1352 | 2363673 | 2438 | Distribution Circuit | Equipment Failure/Involved | Overhead | 336 | 816816 | 36.9806 | -121.9088 | Yes | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0023095 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912651 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | RECLOSER | 42086 | 20240204 | 2152 | 20240205 | 2102 | 2356848 | 1390 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 178 | 247420 | 36.9036 | -121.7361 | Yes | Overcast-Fog-Rain;32-90 F |  |  | 24-0021488 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | No | No | 1911327 | 0 | EPSS Ckt | N | 2024 | AB GRD
CENTRAL COAST | KING CITY | OILFIELDS-1102 | 182391102 | TRANSFORMER | 414534424247 | 20240204 | 2159 | 20240208 | 1516 | 2355126 | 5357 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 10714 | 35.9849 | -120.8494 | Yes | Overcast;32-90 F | Service conductor | Broken- wire on ground | 24-0021193 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911020 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | FUSE | 4971 | 20240204 | 2215 | 20240205 | 26 | 2355730 | 131 | Distribution Circuit | Equipment Failure/Involved | Overhead | 402 | 52662 | 36.9738 | -121.9509 | Yes | Overcast-Fog-Rain;32-90 F | Fuse | Failed/Faulted | 24-0021357 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911191 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 6759 | 20240204 | 2253 | 20240205 | 1405 | 2355513 | 912 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 10326 | 36.8777 | -121.6876 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0021739 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911495 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 1009 | 20240204 | 2310 | 20240206 | 2324 | 2363498 | 2894 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 2894 | 36.9892 | -121.8643 | Yes | Overcast-Rain;32-90 F |  |  | 24-0023910 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1913274 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 6627 | 20240205 | 17 | 20240205 | 1020 | 2355957 | 603 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 107 | 64521 | 36.5949 | -121.8792 | No | Overcast-Rain;32-90 F |  |  | 24-0021759 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911515 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | FUSE | 10331 | 20240205 | 20 | 20240206 | 1110 | 2355958 | 2090 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 87780 | 36.9735 | -121.9552 | No | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0021904 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911636 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 2277 | 20240205 | 110 | 20240205 | 1336 | 2356097 | 746 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 18650 | 36.5429 | -121.9135 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0022038 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911751 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 2579 | 20240205 | 215 | 20240206 | 1726 | 2356313 | 2351 | Distribution Circuit | Vegetation | Tree - branch fell on line | 300 | 705300 | 36.9762 | -121.9052 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022888 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1912522 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 1153 | 20240205 | 236 | 20240206 | 1243 | 2356369 | 2047 | Distribution Circuit | Vegetation | Tree - fell into line | 146 | 169226 | 36.9786 | -121.8924 | No | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken | 24-0021550 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911377 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 6121 | 20240205 | 310 | 20240206 | 1414 | 2360470 | 2104 | Distribution Circuit | Vegetation | Tree - branch fell on line | 109 | 229336 | 36.9835 | -121.8848 | No | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022230 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1911900 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | FUSE | 8417 | 20240205 | 552 | 20240206 | 354 | 2359550 | 1322 | Distribution Circuit | Vegetation | Tree - bark fell into line | 27 | 35218 | 36.9638 | -121.9778 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0022893 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912528 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 7457 | 20240205 | 600 | 20240205 | 1025 | 2357069 | 265 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 111 | 29297 | 37.0369 | -122.0421 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 24-0021769 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911523 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | OTHER | WIRE DOWN AT CGC 315934917227 | 20240205 | 624 | 20240206 | 1658 | 2362806 | 2074 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 26962 | 36.964 | -121.8913 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022896 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1912532 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | JUMPER | BURNT OPEN JPR 2 W/OF 4617 | 20240205 | 631 | 20240206 | 1246 | 2363833 | 1815 | Distribution Circuit | Equipment Failure/Involved | Overhead | 291 | 10313 | 36.8859 | -121.7859 | No | Overcast-Rain;32-90 F | Jumper | Burned Open | 24-0023234 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1912737 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | TRANSFORMER | 411728844609 | 20240205 | 716 | 20240206 | 1834 | 2360603 | 2118 | Transformer only | Vegetation | Tree - grew into line | 4 | 8472 | 36.5249 | -121.8165 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022791 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1912426 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | JUMPER | OJ AT 23301 | 20240205 | 742 | 20240205 | 2125 | 2357579 | 823 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 29628 | 36.767 | -121.758 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0021751 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1911507 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | RECLOSER | 781810 | 20240205 | 751 | 20240206 | 1359 | 2357826 | 1808 | Distribution Circuit | Equipment Failure/Involved | Overhead | 511 | 768890 | 36.9615 | -122.0627 | No | Overcast-Heavy Rain-Strong Winds;32-90 F | Recloser | Burned/flashed | 24-0022139 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | No | No | 1911820 | 0 | EPSS Ckt | N | 2024 | ABC
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | TRANSFORMER | 412348646129 | 20240205 | 751 | 20240209 | 1753 | 2357667 | 6362 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 6362 | 36.5719 | -121.6081 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0022129 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911814 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1101 | 182201101 | JUMPER | WIRE DOWN 13 SPANS LD SIDE OF 20005 | 20240205 | 809 | 20240207 | 2132 | 2358373 | 3683 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 90549 | 36.5893 | -121.5593 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021772 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | Yes | No | 1911525 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | SWITCH | 2979 | 20240205 | 812 | 20240206 | 1632 | 2336795 | 1940 | Distribution Circuit | Equipment Failure/Involved | Overhead | 272 | 524026 | 36.5484 | -121.9243 | No | Overcast-Heavy Rain-Strong Winds;32-90 F | Other | Broken- wire on ground | 24-0021574 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1911389 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | TRANSFORMER | 315745617613 | 20240205 | 818 | 20240206 | 1209 | 2357888 | 1671 | Transformer only | Equipment Failure/Involved | Electrical Overload | 8 | 13368 | 36.9742 | -121.9565 | No | Overcast-Fog-Drizzle;32-90 F | Transformer | Failed/Faulted | 24-0021962 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911689 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2101 | 182492101 | TRANSFORMER | 412968456140 | 20240205 | 829 | 20240206 | 1204 | 2357980 | 1655 | Transformer only | Equipment Failure/Involved | Electrical Overload | 20 | 33100 | 36.851 | -121.4044 | No | Overcast-Fog;32-90 F | Transformer | Deteriorated | 24-0021691 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911466 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | OTHER | WIRE DWN W/OF 332507 | 20240205 | 831 | 20240208 | 1701 | 2368159 | 4830 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 23376 | 37.0415 | -122.0908 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024535 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | Yes | Yes | 1913624 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | SWITCH | 7931 | 20240205 | 833 | 20240205 | 1530 | s1912669 | 417 | Distribution Circuit | Equipment Failure/Involved | Overhead | 408 | 170136 | 36.6811 | -121.8018 | No | Overcast-Rain;32-90 F | Pole-Wood | Broken | 24-0019424 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1912669 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 11185 | 20240205 | 840 | 20240205 | 1101 | 2358923 | 141 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 564 | 36.8829 | -121.7017 | No | Overcast;32-90 F |  |  | 24-0021810 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911557 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 5090 | 20240205 | 914 | 20240207 | 2118 | 2356773 | 3604 | Distribution Circuit | Vegetation | Tree - fell into line | 308 | 323642 | 36.9804 | -121.892 | No | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken | 24-0021675 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911455 | 0 | EPSS Ckt | N | 2024 | B GRD
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 10763 | 20240205 | 915 | 20240205 | 1454 | 2358690 | 339 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 4068 | 36.5856 | -121.8485 | No | Overcast-Rain;32-90 F |  |  | 24-0022215 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1911883 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1102 | 182201102 | TRANSFORMER | 412489247735 | 20240205 | 930 | 20240208 | 1612 | 2358449 | 4722 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 4722 | 36.6172 | -121.5602 | No | Overcast-Heavy Rain;32-90 F | Jumper | Burned Open | 24-0021973 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911699 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1112 | 182371112 | TRANSFORMER | 411929843413 | 20240205 | 941 | 20240208 | 1839 | 2361371 | 4858 | Transformer only | Environmental/External | Water | 6 | 29148 | 36.4945 | -121.7468 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0023328 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912805 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 3987 | 20240205 | 944 | 20240207 | 1837 | 2368568 | 3413 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 4546 | 37.0425 | -122.0498 | No | Overcast-Fog-Rain;32-90 F |  |  | 24-0024661 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913720 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | TRANSFORMER | 411620647234 | 20240205 | 1007 | 20240205 | 2031 | 2358658 | 624 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 3120 | 36.5965 | -121.8563 | No | Overcast-Rain;32-90 F | Transformer (OH) | Broken | 24-0022259 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911913 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 48597 | 20240205 | 1021 | 20240207 | 945 | 2358786 | 2844 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 11376 | 36.967 | -121.8915 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023507 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1912932 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315444819854 | 20240205 | 1044 | 20240208 | 1813 | 2358931 | 4769 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 19076 | 37.0344 | -122.0618 | No | Rain-Overcast;32-90 F | Transformer | Failed/Faulted | 24-0024451 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913580 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 10003 | 20240205 | 1053 | 20240205 | 1922 | 2358997 | 509 | Distribution Circuit | Equipment Failure/Involved | Underground | 23 | 11707 | 36.5962 | -121.8796 | No | Overcast-Rain;32-90 F | Transformer (UG) | Failed/Faulted | 24-0022566 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912193 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 3147 | 20240205 | 1127 | 20240209 | 1723 | 2359222 | 6116 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 48928 | 37.0583 | -122.1598 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0021891 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911626 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | TRANSFORMER | 413129859312 | 20240205 | 1151 | 20240206 | 1801 | 2359392 | 1810 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 1810 | 36.9397 | -121.3525 | No | Overcast-Heavy Rain-Fog;32-90 F |  |  | 24-0022109 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1911800 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | RECLOSER | 2628 | 20240205 | 1201 | 20240205 | 1319 | 2359632 | 78 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 1507 | 117546 | 36.5603 | -121.919 | No | Overcast;32-90 F | Jumper | Bent or Twisted | 24-0022011 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1911729 | 0 | EPSS Ckt | N | 2024 | N/A
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 6701 | 20240205 | 1211 | 20240207 | 1553 | 2362810 | 3102 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 9306 | 36.8754 | -121.7577 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022899 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1912535 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | TRANSFORMER | T1269 | 20240205 | 1221 | 20240205 | 1320 | 2359570 | 59 | Transformer only | Unknown Cause | Patrol - found nothing | 79 | 4661 | 36.5951 | -121.8508 | No | Overcast-Drizzle;32-90 F |  |  | 24-0022052 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1911761 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 8143 | 20240205 | 1240 | 20240207 | 1100 | 2359682 | 2780 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 50040 | 36.5314 | -121.8506 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 24-0022336 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1911989 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6521 | 20240205 | 1257 | 20240208 | 1727 | 2359782 | 4590 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 45900 | 36.9224 | -121.8401 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023151 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1912684 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | JUMPER | OJ 2 NW 40581 | 20240205 | 1324 | 20240205 | 2131 | 2359962 | 487 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 4870 | 36.5676 | -121.9138 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0022062 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1911768 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | TRANSFORMER | T1269 | 20240205 | 1327 | 20240205 | 1341 | 2359975 | 14 | Transformer only | Unknown Cause | Patrol - found nothing | 79 | 1106 | 36.5951 | -121.8508 | No | Overcast;32-90 F |  |  | 24-0022118 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1911808 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | SWITCH | 122 | 20240205 | 1405 | 20240207 | 1517 | 2360224 | 2952 | Distribution Circuit | Equipment Failure/Involved | Underground | 136 | 170568 | 36.9729 | -121.9523 | No | Overcast-Drizzle;32-90 F | Transformer (UG) | Broken | 24-0022152 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1911832 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | TRANSFORMER | T1269 | 20240205 | 1406 | 20240208 | 1708 | 2360195 | 4502 | Distribution Circuit | Equipment Failure/Involved | Underground | 79 | 355658 | 36.5951 | -121.8508 | No | Overcast-Drizzle;32-90 F | Transformer (UG) | Failed/Faulted | 24-0022170 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911848 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1104 | 182381104 | TRANSFORMER | 412002553483 | 20240205 | 1406 | 20240208 | 1450 | 2360193 | 4364 | Transformer only | Environmental/External | Water | 7 | 30548 | 36.7719 | -121.7317 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0022404 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912054 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2102 | 182222102 | TRANSFORMER | T1502 | 20240205 | 1413 | 20240205 | 1548 | 2360236 | 95 | Transformer only | Vegetation | Other ground vegetation | 43 | 4085 | 36.6225 | -121.8237 | No | Overcast;32-90 F | Transformer (UG) | Normal | 24-0022332 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911985 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | TRANSFORMER | 412064245975 | 20240205 | 1648 | 20240208 | 1834 | 2361130 | 4426 | Transformer only | Environmental/External | Water | 1 | 4426 | 36.5654 | -121.7039 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0022991 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912579 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | TRANSFORMER | 315944817519 | 20240205 | 1700 | 20240205 | 1930 | 2360688 | 150 | Transformer only | Vegetation | Tree - fell into line | 5 | 750 | 36.9726 | -121.8879 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Bent or Twisted | 24-0022660 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912295 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 6689 | 20240205 | 1720 | 20240207 | 1038 | 2361276 | 2478 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 27258 | 36.8881 | -121.8071 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023065 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1912631 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | TRANSFORMER | T1488 | 20240205 | 1724 | 20240207 | 1614 | 2356816 | 2810 | Transformer only | Equipment Failure/Involved | Underground | 30 | 84300 | 36.973 | -121.9513 | No | Partly Cloudy-Drizzle;32-90 F | Transformer | Failed/Faulted | 24-0022482 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912120 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 10591 | 20240205 | 1731 | 20240205 | 1902 | 2361348 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 274 | 24934 | 36.8679 | -121.8177 | No | Clear;32-90 F |  |  | 24-0022628 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912258 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 6137 | 20240205 | 1754 | 20240206 | 1050 | 2361468 | 1016 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 40 | 40599 | 36.5945 | -121.8932 | No | Partly Cloudy;32-90 F |  |  | 24-0023136 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912672 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | RECLOSER | 2016 | 20240205 | 1800 | 20240205 | 2026 | 2361517 | 146 | Distribution Circuit | Vegetation | Tree - branch fell on line | 398 | 58108 | 36.5515 | -121.9268 | No | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0022613 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912242 | 0 | EPSS Ckt | N | 2024 | A & C PHSE
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | TRANSFORMER | 411432845946 | 20240205 | 1811 | 20240208 | 1708 | 2361568 | 4257 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 63855 | 36.5597 | -121.919 | No | Overcast;32-90 F | Transformer | Broken | 24-0022977 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912571 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | TRANSFORMER | 315436717698 | 20240205 | 1821 | 20240207 | 1020 | 2361615 | 2399 | Transformer only | Vegetation | Tree - branch fell on line | 5 | 11995 | 36.9757 | -122.0631 | No | Partly Cloudy-Drizzle;32-90 F | Transformer | Malfunctioning | 24-0024048 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913348 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 445933 | 20240205 | 1822 | 20240208 | 1948 | 2361617 | 4406 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 185052 | 37.1372 | -122.1004 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022582 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1912211 | 0 | EPSS Ckt | N | 2024 | NA
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 4645 | 20240205 | 1826 | 20240208 | 1132 | 2361732 | 3906 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 182 | 545741 | 36.5668 | -121.7548 | No | Clear;32-90 F |  |  | 24-0022707 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1912341 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 8419 | 20240205 | 1835 | 20240205 | 2144 | 2361791 | 189 | Distribution Circuit | Vegetation | Tree - branch fell on line | 107 | 20223 | 36.5693 | -121.7917 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0022732 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1912367 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | SWITCH | 5873 | 20240205 | 1840 | 20240206 | 1006 | 2363433 | 926 | Distribution Circuit | Equipment Failure/Involved | Overhead | 137 | 126862 | 36.9569 | -121.9745 | No | Partly Cloudy-Fog;32-90 F | Jumper | Burned Open | 24-0023018 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1912600 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | OTHER | WIRE DOWN 1 SPAN SS OF CGC 315689116980 | 20240205 | 1840 | 20240208 | 1210 | 2364468 | 3845 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 30844 | 36.957 | -121.9754 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023018 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | Yes | No | 1912855 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 974520 | 20240205 | 1843 | 20240206 | 1355 | 2361836 | 1152 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 232 | 267264 | 36.9908 | -121.8063 | No | Overcast-Fog;32-90 F |  |  | 24-0023238 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912740 | 0 | EPSS Ckt | N | 2024 | A/GRD T
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | TRANSFORMER | 411447446224 | 20240205 | 2154 | 20240206 | 1310 | 2363022 | 916 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 10992 | 36.5672 | -121.9143 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0023244 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912744 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | TRANSFORMER | 315490119039 | 20240205 | 2232 | 20240206 | 1736 | 2365727 | 1144 | Transformer only | Vegetation | Tree - fell into line | 7 | 8008 | 37.0119 | -122.045 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 24-0023803 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1913178 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | TRANSFORMER | 315475217209 | 20240205 | 2325 | 20240206 | 1517 | 2362058 | 952 | Transformer only | Unknown Cause | Patrol - found nothing | 5 | 4760 | 36.9614 | -122.0484 | No | Partly Cloudy-Fog-Drizzle;32-90 F |  |  | 24-0023534 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1912952 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 8649 | 20240206 | 457 | 20240207 | 1114 | 2362983 | 1817 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 16353 | 37.0003 | -121.8852 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Normal | 24-0024154 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913409 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 6741 | 20240206 | 559 | 20240206 | 1758 | 2363019 | 719 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 5033 | 36.5716 | -121.8844 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023159 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1912691 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | RECLOSER | 578112 | 20240206 | 746 | 20240207 | 1436 | 2364815 | 1850 | Distribution Circuit | Vegetation | Tree - fell into line | 1497 | 2392023 | 36.6048 | -121.934 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0019877 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1912941 | 0 | EPSS Ckt | N | 2024 | NA
CENTRAL COAST | KING CITY | SOLEDAD-2104 | 182052104 | TRANSFORMER | 413088839477 | 20240206 | 826 | 20240208 | 1142 | 2363360 | 3076 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 3076 | 36.395 | -121.3492 | No | Partly Cloudy-Fog;32-90 F | Transformer | Failed/Faulted | 24-0023879 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913250 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 9605 | 20240206 | 833 | 20240206 | 1721 | 2363400 | 528 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 3168 | 36.9836 | -121.778 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0023624 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1913030 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2105 | 182402105 | TRANSFORMER | 411710448685 | 20240206 | 845 | 20240208 | 1236 | 2363453 | 3111 | Transformer only | Vegetation | Tree - fell into line | 6 | 18666 | 36.6374 | -121.8265 | No | Overcast;32-90 F | Transformer (OH) | Broken | 24-0023094 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912650 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | TRANSFORMER | 413292752637 | 20240206 | 901 | 20240209 | 816 | 2363507 | 4275 | Transformer only | Vegetation | Tree - fell into line | 2 | 8550 | 36.7574 | -121.2909 | No | Partly Cloudy-Fog;32-90 F | Service conductor | Broken- wire on ground | 24-0023150 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912683 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 316125316648 | 20240206 | 917 | 20240208 | 1845 | 2369878 | 3448 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 6896 | 36.9493 | -121.8275 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0026196 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915095 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | TRANSFORMER | 411684847479 | 20240206 | 918 | 20240208 | 659 | 2363583 | 2741 | Transformer only | Equipment Failure/Involved | Overhead | 21 | 57561 | 36.6033 | -121.8348 | No | Partly Cloudy;32-90 F | Transformer | Malfunctioning | 24-0023395 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912859 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | TRANSFORMER | 316442514475 | 20240206 | 933 | 20240207 | 949 | 2363668 | 1456 | Transformer only | Unknown Cause | Patrol - found nothing | 7 | 10192 | 36.8909 | -121.7177 | No | Clear;32-90 F |  |  | 24-0024068 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1913359 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 5219 | 20240206 | 1037 | 20240208 | 1057 | 2363886 | 2900 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 58000 | 37.0371 | -122.066 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023211 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1912720 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ERTA-0403 | 83510403 | TRANSFORMER | 316288215676 | 20240206 | 1037 | 20240206 | 1715 | 2363884 | 398 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 4776 | 36.9236 | -121.7709 | No | Overcast-Fog;32-90 F | Crossarm- Wood | Broken | 24-0023678 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913077 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 40747 | 20240206 | 1102 | 20240207 | 1758 | 2363995 | 1856 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 9904 | 36.5329 | -121.8494 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken | 24-0023453 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912895 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | TRANSFORMER | 412453054110 | 20240206 | 1117 | 20240208 | 1506 | 2364163 | 3109 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 3109 | 36.7938 | -121.5765 | No | Clear;32-90 F | Transformer | On Ground | 24-0023441 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912886 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | FUSE | 5557 | 20240206 | 1145 | 20240206 | 1258 | 2364217 | 73 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 1753 | 36.7876 | -121.5893 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0023446 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912890 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | TRANSFORMER | 412076445762 | 20240206 | 1229 | 20240209 | 1241 | 2363706 | 4332 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 4332 | 36.5602 | -121.6996 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0023342 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912818 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | TRANSFORMER | 411438045968 | 20240206 | 1312 | 20240206 | 1331 | 2364411 | 19 | Transformer only | Vegetation | Tree - fell into line | 13 | 247 | 36.56 | -121.9173 | No | Partly Cloudy;32-90 F | Secondary | Broken- wire on ground | 24-0023367 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1912837 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 633 | 20240206 | 1351 | 20240208 | 1249 | 2365268 | 2818 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 64814 | 36.4177 | -121.9132 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0023629 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1913033 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | SWITCH | 9189 | 20240206 | 1351 | 20240207 | 1743 | 2365324 | 1672 | Distribution Circuit | Vegetation | Tree - fell into line | 253 | 423016 | 36.3801 | -121.8994 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023647 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1913051 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 11295 | 20240206 | 1432 | 20240208 | 1728 | 2367868 | 3056 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 12224 | 37.002 | -121.9004 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0024493 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913600 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 5901 | 20240206 | 1522 | 20240208 | 1659 | 2364885 | 2977 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 47632 | 37.0944 | -121.9716 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024416 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1913561 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 45255 | 20240206 | 1532 | 20240209 | 1441 | 2364901 | 4269 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 166491 | 36.5862 | -121.9149 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 24-0023606 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913010 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | TRANSFORMER | 316295815975 | 20240206 | 1604 | 20240207 | 1819 | 2365035 | 1575 | Transformer only | Environmental/External | Water | 1 | 1575 | 36.9318 | -121.7685 | No | Overcast;32-90 F | Transformer | Failed/Faulted | 24-0023896 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913263 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | TRANSFORMER | 413026355317 | 20240206 | 1645 | 20240206 | 1832 | 2364965 | 107 | Transformer only | Vegetation | Tree - grew into line | 2 | 214 | 36.8279 | -121.3835 | No | Partly Cloudy;32-90 F | Service conductor | Burned Open | 24-0023635 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913038 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 8865 | 20240206 | 1646 | 20240209 | 1733 | 2365332 | 4367 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 240185 | 36.6133 | -121.9272 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019877 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1913055 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 6295 | 20240206 | 1655 | 20240209 | 1535 | 2368237 | 4240 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 131440 | 37.0991 | -122.0866 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024565 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1913642 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 426822 | 20240206 | 1818 | 20240207 | 10 | 2365625 | 352 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 4576 | 37.1016 | -122.0324 | No | Clear;32-90 F |  |  | 24-0023916 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1913280 | 0 | EPSS Ckt | N | 2024 | N/A
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6597 | 20240206 | 2027 | 20240209 | 1537 | 2365764 | 4030 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 24180 | 36.9966 | -121.7163 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026197 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1915096 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | SWITCH | 886203 | 20240206 | 2046 | 20240206 | 2103 | 2365782 | 17 | Distribution Circuit | Vegetation | Tree - branch fell on line | 74 | 1258 | 36.9699 | -121.8864 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0023826 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1913201 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 955435 | 20240206 | 2124 | 20240207 | 511 | 2365959 | 467 | Distribution Circuit | Vegetation | Tree - branch fell on line | 38 | 17746 | 37.0489 | -121.9394 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0023941 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1913300 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | RECLOSER | 9452 | 20240206 | 2203 | 20240207 | 309 | 2365910 | 306 | Distribution Circuit | Vegetation | Tree - branch fell on line | 391 | 119646 | 36.5969 | -121.8855 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0023884 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1913255 | 0 | EPSS Ckt | N | 2024 | BC
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 8489 | 20240206 | 2242 | 20240207 | 1825 | 2365939 | 1183 | Distribution Circuit | Equipment Failure/Involved | Overhead | 103 | 18969 | 37.0579 | -121.9987 | No | Partly Cloudy-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0023911 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | Yes | 1913275 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2106 | 182402106 | RECLOSER | 9138 | 20240206 | 2250 | 20240209 | 1437 | 2365956 | 3827 | Distribution Circuit | Vegetation | Tree - fell into line | 455 | 278892 | 36.6413 | -121.8077 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023938 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1913298 | 0 | EPSS Ckt | N | 2024 | ABC
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | TRANSFORMER | 315976019180 | 20240207 | 201 | 20240208 | 1749 | 2364316 | 2388 | Transformer only | Vegetation | Tree - fell into line | 1 | 2388 | 37.0185 | -121.879 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 24-0024644 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913704 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 7011 | 20240207 | 401 | 20240207 | 734 | 2366072 | 213 | Distribution Circuit | Vegetation | Tree - bark fell into line | 17 | 3546 | 36.9739 | -121.7971 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 24-0023967 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913311 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 6087 | 20240207 | 615 | 20240207 | 1855 | 2366145 | 760 | Distribution Circuit | Vegetation | Tree - fell into line | 186 | 141360 | 37.0665 | -122.0336 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023983 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1913318 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 955435 | 20240207 | 654 | 20240207 | 948 | 2366167 | 174 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 38 | 6612 | 37.0489 | -121.9393 | No | Overcast-Drizzle;32-90 F | Fuse | Failed/Faulted | 24-0024060 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913356 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1109 | 182011109 | FUSE | 948327 | 20240207 | 727 | 20240207 | 1028 | 2366309 | 181 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 966 | 36.6776 | -121.5908 | No | Overcast;32-90 F |  |  | 24-0024122 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913391 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | SWITCH | 151139 | 20240207 | 823 | 20240207 | 1611 | 2366416 | 468 | Distribution Circuit | Vegetation | Tree - fell into line | 248 | 116064 | 37.058 | -122.0333 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0023302 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1913320 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 9665 | 20240207 | 828 | 20240208 | 1118 | 2366450 | 1610 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 11270 | 36.8549 | -121.7925 | No | Clear;32-90 F | Jumper | Burned Open | 24-0024672 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1913729 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | JUMPER | 3315 C/OUT BURNED OPEN | 20240207 | 1006 | 20240207 | 1133 | 2366782 | 87 | Distribution Circuit | Equipment Failure/Involved | Overhead | 542 | 15654 | 36.7614 | -121.6142 | No | Clear;32-90 F | Jumper | Burned Open | 24-0024166 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1913417 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 5159 | 20240207 | 1015 | 20240208 | 1342 | 2366788 | 1647 | Distribution Circuit | Vegetation | Tree - fell into line | 102 | 146737 | 37.0814 | -122.0846 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024107 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1913378 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRANSFORMER | 315394520779 | 20240207 | 1039 | 20240208 | 209 | 2366876 | 930 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 10230 | 37.06 | -122.0794 | No | Overcast-Heavy Rain;32-90 F | Transformer (OH) | Broken | 24-0024700 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913751 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | RECLOSER | 88772 | 20240207 | 1102 | 20240208 | 1557 | 2366990 | 1735 | Distribution Circuit | Vegetation | Tree - fell into line | 1251 | 122427 | 36.904 | -121.6085 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024159 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1913413 | 0 | EPSS Ckt | N | 2024 | B-GRD
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6545 | 20240207 | 1109 | 20240207 | 1603 | 2367020 | 294 | Distribution Circuit | Vegetation | Tree - bark fell into line | 25 | 7350 | 36.9404 | -121.8542 | No | Partly Cloudy-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0024362 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913537 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | TRANSFORMER | 412146949719 | 20240207 | 1110 | 20240207 | 1245 | 2367012 | 95 | Transformer only | Vegetation | Tree - fell into line | 13 | 1235 | 36.6688 | -121.6793 | No | Overcast-Rain;32-90 F | Secondary | Broken- wire on ground | 24-0024178 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1913427 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | 83500401 | 83500401 | JUMPER | DDE JUMPERS @ CGC# 315831818627 | 20240207 | 1120 | 20240208 | 1945 | 2366970 | 1945 | Distribution Circuit | Vegetation | Tree - bark fell into line | 7 | 13615 | 37.0024 | -121.9276 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0024150 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1913407 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | RECLOSER | 37234 | 20240207 | 1228 | 20240207 | 1309 | 2367225 | 41 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 654 | 26814 | 36.9596 | -122.0524 | No | Overcast-Heavy Rain-Lightning;32-90 F |  |  | 24-0024274 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1913480 | 0 | EPSS Ckt | N | 2024 | A AND B PHASE
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | TRANSFORMER | 315972518535 | 20240207 | 1241 | 20240208 | 1725 | 2367251 | 1724 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 3448 | 37.0003 | -121.8797 | No | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0025198 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1914224 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 11103 | 20240207 | 1242 | 20240207 | 1415 | 2367252 | 93 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1332 | 36.9935 | -122.0701 | No | Overcast-Heavy Rain-Lightning;32-90 F |  |  | 24-0024375 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913544 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | TRANSFORMER | 412081552622 | 20240207 | 1247 | 20240208 | 1248 | 2367277 | 1441 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1441 | 36.7478 | -121.704 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0024564 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913641 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1112 | 182371112 | RECLOSER | 438 | 20240207 | 1315 | 20240208 | 1506 | 2367419 | 1551 | Distribution Circuit | Equipment Failure/Involved | Overhead | 247 | 98154 | 36.4967 | -121.7313 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024299 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1913502 | 0 | EPSS Ckt | N | 2024 | B&C PHASE
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 11541 | 20240207 | 1315 | 20240208 | 302 | 2367414 | 827 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 9924 | 36.8612 | -121.686 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0025655 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1914676 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 4797 | 20240207 | 1318 | 20240210 | 1321 | 2367424 | 4323 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 34584 | 36.8004 | -121.6433 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0024410 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1913558 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 2493 | 20240207 | 1321 | 20240208 | 1558 | 2367479 | 1597 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1597 | 36.5833 | -121.8549 | No | Partly Cloudy-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024562 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1913639 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 10720 | 20240207 | 1401 | 20240207 | 1408 | 2367566 | 7 | Distribution Circuit | Vegetation | Tree - branch fell on line | 463 | 3241 | 37.1085 | -122.1441 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0022890 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1913529 | 0 | EPSS Ckt | N | 2024 | A&C T
CENTRAL COAST | KING CITY | SAN ARDO-1101 | 182191101 | RECLOSER | 7632 | 20240207 | 1418 | 20240208 | 1207 | 2367638 | 1309 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 28708 | 36.0712 | -120.9813 | No | Overcast-Rain;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0024368 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1913540 | 0 | EPSS Ckt | N | 2024 | A-GRD
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9709 | 20240207 | 1419 | 20240208 | 252 | 2367626 | 753 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 11295 | 37.1163 | -122.1184 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0025630 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1914651 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316436016285 | 20240207 | 1427 | 20240208 | 1140 | 2367687 | 1273 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 3819 | 36.941 | -121.7205 | No | Overcast-Rain;32-90 F | Transformer (OH) | Deteriorated | 24-0024619 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913684 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-1101 | 182221101 | TRANSFORMER | 411719448024 | 20240207 | 1442 | 20240207 | 1659 | 2367775 | 137 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 1233 | 36.6184 | -121.8232 | No | Overcast-Rain;32-90 F | Crossarm- Wood | Broken | 24-0024399 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1913551 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | RECLOSER | 7594 | 20240207 | 1442 | 20240207 | 1555 | 2367755 | 73 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4951 | 361423 | 36.3148 | -121.237 | No | Overcast-Rain;32-90 F | Recloser | Burned/flashed | 24-0024408 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1913557 | 0 | Non-EPSS | N | 2024 | NONE
CENTRAL COAST | MONTEREY | DEL MONTE-2102 | 182222102 | TRANSFORMER | 411689647595 | 20240207 | 1501 | 20240207 | 1636 | 2367819 | 95 | Transformer only | Vegetation | Tree - branch fell on line | 11 | 1045 | 36.6075 | -121.8327 | No | Overcast-Rain;32-90 F | Secondary | Together | 24-0024433 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1913572 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | JUMPER | JMPRS @ CGC 411400347982 | 20240207 | 1510 | 20240209 | 1902 | 2367824 | 3112 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 18672 | 36.6149 | -121.9325 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0024434 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1913573 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | RECLOSER | LR 9440 | 20240207 | 1511 | 20240207 | 2110 | 2367447 | 359 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2630 | 944170 | 36.6025 | -121.9049 | No | Overcast-Fog;32-90 F |  |  | 24-0024453 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913581 | 0 | EPSS Ckt | N | 2024 | C GRD
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 287578 | 20240207 | 1538 | 20240207 | 1916 | 2367943 | 218 | Distribution Circuit | Vegetation | Tree - fell into line | 345 | 40934 | 37.0438 | -122.0755 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024479 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | Yes | No | 1913593 | 0 | EPSS Ckt | N | 2024 | AC GRD
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9779 | 20240207 | 1602 | 20240208 | 321 | 2368017 | 679 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 4074 | 37.1548 | -122.0829 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0025755 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1914776 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 8243 | 20240207 | 1640 | 20240207 | 2211 | 2368430 | 331 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 64 | 21184 | 36.6075 | -121.9369 | No | Overcast-Drizzle;32-90 F |  |  | 24-0024962 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1913992 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | TRANSFORMER | 411460247093 | 20240207 | 1640 | 20240209 | 1553 | 2368185 | 2833 | Transformer only | Vegetation | Tree - fell into line | 9 | 25497 | 36.5911 | -121.9111 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026420 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1915194 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | RECLOSER | 578112 | 20240207 | 1650 | 20240207 | 1811 | s1960390 | 67 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3017 | 232309 | 36.6048 | -121.934 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0019877 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1960390 | 0 | EPSS Ckt | N | 2024 | A/B
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | TRANSFORMER | 412203051660 | 20240207 | 1719 | 20240208 | 1140 | 2367614 | 1101 | Transformer only | Environmental/External | Water | 5 | 5505 | 36.7225 | -121.6634 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0024646 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913706 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 6995 | 20240207 | 1754 | 20240208 | 1801 | 2368745 | 1447 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 144700 | 36.4883 | -121.9379 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024708 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1913754 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | OTHER | 440 | 20240207 | 1802 | 20240209 | 1850 | 2368528 | 2928 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 64562 | 36.4389 | -121.9203 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024693 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1913745 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | SWITCH | 10645 | 20240207 | 1803 | 20240208 | 1651 | 2368469 | 1368 | Distribution Circuit | Vegetation | Tree - branch fell on line | 87 | 119016 | 37.0831 | -122.0878 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0026428 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1915198 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | TRANSFORMER | 411428548022 | 20240207 | 1828 | 20240209 | 1614 | 2368563 | 2746 | Transformer only | Vegetation | Tree - fell into line | 18 | 49428 | 36.6163 | -121.9228 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 24-0026305 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915142 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | JUMPER | 279434 | 20240207 | 1835 | 20240207 | 2128 | 2368589 | 173 | Distribution Circuit | Equipment Failure/Involved | Overhead | 136 | 23528 | 37.0695 | -121.995 | No | Clear;32-90 F | Jumper | Burned Open | 24-0024800 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1913833 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0422 | 182440422 | RECLOSER | 2608 | 20240207 | 1913 | 20240207 | 1937 | 2368678 | 24 | Distribution Circuit | Equipment Failure/Involved | Overhead | 302 | 7248 | 36.5912 | -121.9465 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0023160 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1913748 | 0 | EPSS Ckt | N | 2024 | NONE
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 10718 | 20240207 | 1918 | 20240208 | 1022 | 2368689 | 904 | Distribution Circuit | Vegetation | Tree - branch fell on line | 296 | 113934 | 37.036 | -122.1068 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0024479 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1913744 | 0 | EPSS Ckt | N | 2024 | BC
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 2335 | 20240207 | 1918 | 20240208 | 1418 | 2369563 | 1140 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2280 | 37.0737 | -122.1297 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026110 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1915054 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8361 | 20240207 | 1918 | 20240208 | 1147 | 2369566 | 989 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 12857 | 37.0763 | -122.1318 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026113 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1915055 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 1995 | 20240207 | 1918 | 20240208 | 1710 | 2369571 | 1312 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 2624 | 37.0556 | -122.1209 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0026116 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915056 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GONZALES SUB | 18213 | OCB | 1103/2 | 20240207 | 1946 | 20240207 | 2004 | 2368727 | 18 | Distribution Circuit | Equipment Failure/Involved | Overhead | 388 | 6984 | 36.5092 | -121.4466 | No | Overcast-Rain;32-90 F | Anchor or Guy | Broken | 24-0024702 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1913753 | 0 | Non-EPSS | N | 2024 | N/A
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | TRANSFORMER | 411360643480 | 20240207 | 2059 | 20240210 | 1353 | 2368879 | 3894 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 15576 | 36.4908 | -121.9401 | No | Overcast-Drizzle;32-90 F | Transformer | Broken- wire on ground | 24-0026027 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1915009 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 471 | 20240207 | 2113 | 20240208 | 1948 | 2368902 | 1355 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 25745 | 36.4954 | -121.9372 | No | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0025056 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1914086 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 2253 | 20240207 | 2128 | 20240208 | 21 | 2368933 | 173 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 2076 | 37.1709 | -122.1652 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0025137 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1914166 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 8605 | 20240207 | 2327 | 20240208 | 1920 | 2369013 | 1193 | Distribution Circuit | Vegetation | Tree - fell into line | 242 | 110366 | 36.9612 | -121.888 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0025530 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1914552 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | TRANSFORMER | 315508820532 | 20240207 | 2332 | 20240208 | 1918 | 2369019 | 1186 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 4744 | 37.0539 | -122.0391 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0026176 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915081 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9749 | 20240208 | 44 | 20240208 | 1500 | 2369058 | 856 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 5992 | 37.1489 | -122.157 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0025541 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1914563 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 2875 | 20240208 | 434 | 20240209 | 1746 | s1915209 | 2232 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 17856 | 36.4995 | -121.9313 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0024218 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915209 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1103 | 182201103 | TRANSFORMER | 412417748819 | 20240208 | 656 | 20240208 | 1143 | 2369111 | 287 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 574 | 36.6466 | -121.5858 | No | Fog;32-90 F | Jumper | Broken | 24-0025964 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1914973 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | JUMPER | OJS 1 P E.OF CGC 411367343329 | 20240208 | 734 | 20240208 | 1626 | 2369194 | 532 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3724 | 36.4865 | -121.9378 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0025983 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1914977 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | RECLOSER | 2052 | 20240208 | 840 | 20240211 | 1535 | s1916039 | 4723 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 306995 | 36.3999 | -121.9022 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026021 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1916039 | 0 | EPSS Ckt | N | 2024 | NA
CENTRAL COAST | MONTEREY | FORT ORD-2107 | 182402107 | FUSE | 40371 | 20240208 | 900 | 20240208 | 1457 | 2369232 | 357 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 714 | 36.6732 | -121.7654 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0025996 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1914981 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | JUMPER | JPRS SS OF CGC 316328715720 | 20240208 | 950 | 20240208 | 1745 | 2369317 | 475 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 3325 | 36.9244 | -121.7588 | No | Partly Cloudy-Fog;32-90 F | Secondary | Normal | 24-0026006 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1914987 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 7683 | 20240208 | 954 | 20240208 | 1120 | 2369478 | 86 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 1806 | 36.9669 | -122.046 | No | Partly Cloudy;32-90 F | Jumper | Bent or Twisted | 24-0026061 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915028 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | TRANSFORMER | 412828542403 | 20240208 | 956 | 20240208 | 1002 | 2366722 | 6 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 6 | 36.4729 | -121.4412 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0026132 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915065 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | JUMPER | JPRS AT MAPLE & SEACLIFF | 20240208 | 1035 | 20240208 | 1441 | 2369485 | 246 | Distribution Circuit | Vegetation | Tree - grew into line | 10 | 2460 | 36.9785 | -121.9212 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0026064 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915031 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | TRANSFORMER | 316726014167 | 20240208 | 1048 | 20240208 | 2329 | 2369820 | 761 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 1522 | 36.8837 | -121.6205 | No | Clear;32-90 F |  |  | 24-0026763 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1915474 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | FUSE | 30075 | 20240208 | 1058 | 20240208 | 1158 | 2369853 | 53 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 53 | 36.2683 | -121.1455 | No | Partly Cloudy;32-90 F |  |  | 24-0026185 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915087 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | TRANSFORMER | 315315022562 | 20240208 | 1059 | 20240208 | 1518 | 2369854 | 259 | Transformer only | Vegetation | Tree - bark fell into line | 5 | 1295 | 37.1093 | -122.106 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0026291 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915135 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8961 | 20240208 | 1103 | 20240208 | 1351 | 2369861 | 168 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 112 | 37.0432 | -122.0518 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0026326 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915156 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | TRANSFORMER | 100000036160 | 20240208 | 1141 | 20240208 | 1525 | 2369940 | 224 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 672 | 37.0987 | -122.086 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0026435 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915200 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 11877 | 20240208 | 1143 | 20240208 | 1752 | 2369946 | 369 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 3831 | 37.0433 | -122.1149 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026331 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1915160 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8223 | 20240208 | 1200 | 20240208 | 1251 | 2370014 | 51 | Distribution Circuit | Vegetation | Tree - branch fell on line | 97 | 4947 | 37.0579 | -121.9689 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0026328 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1915157 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 4693 | 20240208 | 1216 | 20240208 | 1823 | 2370062 | 367 | Distribution Circuit | Equipment Failure/Involved | Overhead | 63 | 23121 | 36.7255 | -121.2676 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0026345 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915169 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | OTHER | 3603 | 20240208 | 1252 | 20240208 | 1946 | 2370067 | 414 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 3726 | 37.115 | -122.1138 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026301 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1915139 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 6987 | 20240208 | 1305 | 20240208 | 1444 | 2370424 | 99 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 297 | 36.9432 | -121.768 | No | Overcast;32-90 F |  |  | 24-0026422 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1915195 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 40349 | 20240208 | 1331 | 20240208 | 1516 | 2370229 | 105 | Distribution Circuit | Equipment Failure/Involved | Overhead | 196 | 20580 | 36.5965 | -121.8402 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0026241 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915151 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | TRANSFORMER | 411857033558 | 20240208 | 1340 | 20240209 | 1326 | 2370283 | 1426 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2852 | 36.2224 | -121.7637 | No | Partly Cloudy;32-90 F | Transformer (OH) | Deteriorated | 24-0026536 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915265 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | JUMPER | OJS 2 SPANS W/O CGC 100000040952 | 20240208 | 1438 | 20240210 | 1223 | 2370655 | 2745 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 2745 | 36.3894 | -121.5857 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0026502 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1915236 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5621 | 20240208 | 1520 | 20240208 | 1635 | 2370450 | 75 | Distribution Circuit | Vegetation | Tree - branch fell on line | 45 | 3375 | 37.1016 | -122.0524 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0026480 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1915223 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2102 | 182222102 | TRANSFORMER | 411640047530 | 20240208 | 1541 | 20240208 | 1616 | 2370519 | 35 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 420 | 36.6046 | -121.85 | No | Overcast;32-90 F | Cutout- fuse holder | Failed/Faulted | 24-0026482 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915224 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 3413 | 20240208 | 1604 | 20240208 | 2208 | 2370530 | 364 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 2184 | 37.0301 | -121.8579 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0026454 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915211 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9181 | 20240208 | 1608 | 20240209 | 1112 | 2370556 | 1144 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 14872 | 37.2288 | -122.148 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0026623 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915341 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 6083 | 20240208 | 1612 | 20240208 | 1830 | 2370569 | 138 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 414 | 36.2624 | -121.7941 | No | Partly Cloudy-Drizzle;32-90 F | Crossarm- Wood | Broken | 24-0026470 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915217 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 8143 | 20240208 | 1643 | 20240208 | 2001 | 2370582 | 198 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 2377 | 36.5314 | -121.8506 | No | Overcast;32-90 F |  |  | 24-0026567 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915286 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 1421 | 20240208 | 1733 | 20240209 | 1818 | 2370728 | 1485 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 23805 | 36.5743 | -121.9483 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0026963 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1915576 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | TRANSFORMER | 411766034570 | 20240208 | 1735 | 20240210 | 1235 | 2370731 | 2580 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 2580 | 36.2505 | -121.7927 | No | Clear;32-90 F | Lightning Arrestor | Broken | 24-0026933 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915567 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | FUSE | 20055 | 20240208 | 1831 | 20240208 | 2012 | 2370829 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 41 | 4177 | 36.5568 | -121.7326 | No | Clear;32-90 F |  |  | 24-0026564 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915283 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | SOQUEL-0402 | 83300402 | TRANSFORMER | 315760017805 | 20240208 | 1942 | 20240209 | 1814 | 2370918 | 1352 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 4056 | 36.9796 | -121.9516 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0026748 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915463 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0422 | 182440422 | TRANSFORMER | 411357347180 | 20240208 | 2022 | 20240208 | 2258 | 2370957 | 156 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 156 | 36.5926 | -121.9458 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0026764 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915475 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | TRANSFORMER | 411793234095 | 20240208 | 2042 | 20240209 | 1605 | 2370981 | 1163 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1163 | 36.2362 | -121.786 | No | Clear;32-90 F | Lightning Arrestor | Broken | 24-0026875 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915533 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 2553 | 20240208 | 2148 | 20240209 | 836 | 2371031 | 648 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 21384 | 36.5766 | -121.97 | No | Partly Cloudy;32-90 F |  |  | 24-0026834 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1915512 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | FUSE | 6001 | 20240208 | 2316 | 20240209 | 51 | 2371079 | 95 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 332 | 31540 | 36.9898 | -121.9328 | No | Clear;32-90 F |  |  | 24-0026768 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1915478 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | TRANSFORMER | T1697 | 20240208 | 2324 | 20240209 | 1338 | 2371088 | 853 | Distribution Circuit | Equipment Failure/Involved | Underground | 36 | 5815 | 36.5563 | -121.7282 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0026779 | UG | Sus | 35528882 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915484 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | FUSE | 5443 | 20240209 | 102 | 20240209 | 851 | 2370976 | 469 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2345 | 37.1105 | -122.1144 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026783 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | Yes | 1915487 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | JUMPER | OJ W/OF CGC 315782120910 | 20240209 | 317 | 20240209 | 1315 | 2371124 | 598 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 598 | 37.0655 | -121.9478 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026791 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1915495 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | TRANSFORMER | 411374044067 | 20240209 | 538 | 20240209 | 1241 | 2371136 | 423 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 423 | 36.507 | -121.9359 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0027033 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1915606 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | TRANSFORMER | 315485116846 | 20240209 | 811 | 20240209 | 1652 | 2371897 | 521 | Transformer only | Vegetation | Tree - fell into line | 12 | 6252 | 36.9515 | -122.0446 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 24-0027060 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB |  | 0 | No | No | No | 1915624 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | OTHER | 9488 | 20240209 | 851 | 20240209 | 1427 | 2371320 | 336 | Distribution Circuit | Vegetation | Tree - branch fell on line | 195 | 13981 | 36.5902 | -121.9442 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026866 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1915527 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | TRANSFORMER | 412064245975 | 20240209 | 859 | 20240209 | 1030 | 2371308 | 91 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 91 | 36.5654 | -121.7039 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0026862 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915522 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6641 | 20240209 | 954 | 20240209 | 1641 | 2371437 | 407 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 31339 | 37.016 | -121.8161 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0026840 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915548 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | TRANSFORMER | 411459536684 | 20240209 | 957 | 20240209 | 1643 | 2371442 | 406 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 812 | 36.3058 | -121.9005 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0026997 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915593 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | JUMPER | 1 SPAN N/OF CGC 315436419791 | 20240209 | 958 | 20240209 | 1320 | 2371212 | 202 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 606 | 37.0336 | -122.0647 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken | 24-0026822 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915503 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | JUMPER | JUMPERS 1P LOAD SIDE OF CGC# 315500522552 | 20240209 | 1035 | 20240209 | 1310 | 2371448 | 155 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 775 | 37.1088 | -122.0443 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0026899 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915550 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | OTHER | WIRE DWN N/OF 10719 | 20240209 | 1144 | 20240209 | 1952 | 2371806 | 488 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 9779 | 37.0875 | -122.1045 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0027110 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1915654 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | FUSE | 885 | 20240209 | 1157 | 20240209 | 1410 | 2371698 | 133 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 112 | 14837 | 36.9639 | -121.9916 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0027062 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915625 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1102 | 182011102 | TRANSFORMER | 412241650956 | 20240209 | 1208 | 20240209 | 1915 | 2371718 | 427 | Transformer only | Equipment Failure/Involved | Overhead | 24 | 10248 | 36.7035 | -121.6483 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0027043 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915612 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | SWITCH | 9465 | 20240209 | 1218 | 20240209 | 1417 | 2371734 | 119 | Distribution Circuit | Equipment Failure/Involved | Overhead | 130 | 15470 | 36.6183 | -121.9309 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0026900 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915595 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1109 | 182011109 | RECLOSER | 97654 | 20240209 | 1230 | 20240209 | 1903 | 2371766 | 393 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 9833 | 36.6699 | -121.5984 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 24-0027010 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915597 | 0 | Non-EPSS | N | 2024 | C GRD
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 1445 | 20240209 | 1234 | 20240209 | 1603 | 2371769 | 209 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 2508 | 36.5735 | -121.9108 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0027013 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915600 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | TRANSFORMER | 412154552160 | 20240209 | 1334 | 20240210 | 1355 | 2371791 | 1461 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1461 | 36.7351 | -121.6795 | No | Clear;32-90 F | Transformer | Broken | 24-0027059 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915623 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 6465 | 20240209 | 1406 | 20240210 | 1013 | 2371908 | 1207 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2414 | 37.0541 | -122.1697 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0027067 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1915627 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | TRANSFORMER | T2436 | 20240209 | 1411 | 20240210 | 1131 | 2371792 | 1280 | Distribution Circuit | Equipment Failure/Involved | Underground | 13 | 2747 | 36.4757 | -121.932 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0027070 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915628 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | OTHER | 6165 | 20240209 | 1426 | 20240210 | 1129 | 2371935 | 1263 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2526 | 37.0822 | -121.9928 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0027168 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1915688 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1109 | 182011109 | TRANSFORMER | 412399849450 | 20240209 | 1542 | 20240210 | 612 | 2372081 | 870 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 870 | 36.6632 | -121.5925 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0027118 | OH | Sus | 35528881 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915657 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | TRANSFORMER | 315207821932 | 20240209 | 1554 | 20240209 | 2029 | 2372096 | 275 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 825 | 37.0908 | -122.1441 | No | Clear;32-90 F |  |  | 24-0027196 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915710 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 1447 | 20240209 | 1610 | 20240209 | 2324 | 2372118 | 434 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 3906 | 36.565 | -121.9568 | No | Clear;32-90 F |  |  | 24-0027273 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1915782 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 1433 | 20240209 | 1619 | 20240209 | 2005 | 2372210 | 226 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 7232 | 36.567 | -121.9568 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0027187 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915701 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRANSFORMER | 315266524287 | 20240209 | 1623 | 20240210 | 936 | 2372133 | 1033 | Transformer only | Vegetation | Tree - fell into line | 4 | 4132 | 37.156 | -122.1227 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0027176 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915692 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | TRANSFORMER | 411381343737 | 20240209 | 1637 | 20240209 | 1837 | 2372148 | 120 | Transformer only | Unknown Cause | Patrol - found nothing | 7 | 840 | 36.498 | -121.933 | No | Partly Cloudy;32-90 F |  |  | 24-0027184 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915698 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 8097 | 20240209 | 1732 | 20240210 | 611 | 2372208 | 759 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 12903 | 37.0785 | -122.139 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0027280 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1915789 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 711 | 20240209 | 1740 | 20240209 | 2010 | 2372215 | 150 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 3300 | 37.0529 | -122.1604 | No | Clear;32-90 F |  |  | 24-0027188 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915702 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | TRANSFORMER | 315214321847 | 20240209 | 1801 | 20240210 | 818 | 2372238 | 857 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 857 | 37.0884 | -122.1419 | No | Clear;32-90 F |  |  | 24-0027298 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1915797 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 4393 | 20240209 | 1805 | 20240209 | 2302 | 2372251 | 297 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 95 | 27555 | 37.1199 | -122.1209 | No | Clear;32-90 F |  |  | 24-0027266 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1915776 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | TRANSFORMER | 315209221420 | 20240209 | 1807 | 20240210 | 1517 | 2372249 | 1270 | Transformer only | Vegetation | Tree - branch fell on line | 4 | 5080 | 37.0767 | -122.1432 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0027295 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915794 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | SWITCH | 5066BP | 20240209 | 1905 | 20240209 | 1931 | 2372316 | 26 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 1014 | 37.1706 | -122.1655 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 24-0021622 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915699 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | TRANSFORMER | 411553140090 | 20240209 | 1905 | 20240210 | 1521 | 2372320 | 1216 | Transformer only | Environmental/External | Water | 1 | 1216 | 36.3999 | -121.872 | No | Clear;32-90 F | Transformer | Normal | 24-0027358 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915831 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | OTHER | WIRE DOWN | 20240209 | 2337 | 20240210 | 1232 | 2372565 | 775 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 4069 | 36.5317 | -121.738 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0027321 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | Yes | Yes | 1915813 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 23299 | 20240210 | 7 | 20240210 | 714 | 2372414 | 427 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 227 | 96929 | 36.7693 | -121.7545 | No | Clear;32-90 F |  |  | 24-0027283 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1915790 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 23589 | 20240210 | 620 | 20240210 | 1330 | 2372461 | 430 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 860 | 36.7183 | -121.7717 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0027332 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1915817 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 1445 | 20240210 | 928 | 20240210 | 1600 | 2372554 | 392 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 4704 | 36.5735 | -121.9108 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0027315 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915812 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 2533 | 20240210 | 1352 | 20240210 | 1622 | 2372793 | 150 | Distribution Circuit | Equipment Failure/Involved | Overhead | 219 | 32850 | 36.5605 | -121.9164 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0027413 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1915866 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | JUMPER | OJ W/OF CGC 411382543477 | 20240210 | 1735 | 20240211 | 1300 | 2372947 | 1165 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 5825 | 36.4908 | -121.9328 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0027446 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1915886 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5239 | 20240210 | 1810 | 20240211 | 1228 | 2372973 | 1098 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 45018 | 37.0682 | -122.0827 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0027457 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1915896 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 8557 | 20240211 | 933 | 20240211 | 1438 | 2373155 | 305 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1830 | 36.5665 | -121.8863 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0027576 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1916010 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | TRANSFORMER | 411378843550 | 20240211 | 1216 | 20240211 | 1424 | 2373300 | 128 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 256 | 36.4928 | -121.9338 | No | Partly Cloudy;32-90 F |  |  | 24-0027613 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1916036 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2107 | 182402107 | TRANSFORMER | 411845650092 | 20240211 | 1613 | 20240211 | 2111 | 2373411 | 298 | Transformer only | Equipment Failure/Involved | Electrical Overload | 10 | 2980 | 36.6768 | -121.7825 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0027642 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1916062 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1109 | 182011109 | OCB | 1109/2 | 20240211 | 1923 | 20240212 | 443 | 2373479 | 546 | Distribution Circuit | 3rd Party | Vehicle | 3997 | 567435 | 36.6828 | -121.6513 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0027652 | OH | Sus | 46178151 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1916069 | 0 | Non-EPSS | N | 2024 | C GRD
CENTRAL COAST | COAST | PAUL SWEET-2108 | 83252108 | TRANSFORMER | 315631218072 | 20240211 | 2359 | 20240212 | 53 | 2373529 | 54 | Transformer only | Unknown Cause | Patrol - found nothing | 16 | 864 | 36.9865 | -121.9957 | No | Partly Cloudy;32-90 F |  |  | 24-0027710 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1916118 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 11461 | 20240212 | 759 | 20240212 | 1140 | 2373631 | 221 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 2652 | 36.8678 | -121.76 | No | Clear;32-90 F |  |  | 24-0027894 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1916252 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS COCHES-1102 | 182151102 | FUSE | 8787 | 20240212 | 837 | 20240212 | 1100 | 2373612 | 143 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 286 | 36.3951 | -121.3103 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0027763 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1916156 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 6987 | 20240212 | 929 | 20240212 | 1413 | 2373788 | 284 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 284 | 36.9432 | -121.768 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0027988 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1916280 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | TRANSFORMER | 24771 | 20240212 | 1141 | 20240212 | 2202 | 2373971 | 621 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1863 | 36.748 | -121.7073 | No | Partly Cloudy;32-90 F | Transformer | Broken | 24-0027997 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1916282 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 83765 | 20240212 | 1143 | 20240212 | 1628 | 2373974 | 285 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1710 | 37.1174 | -121.9748 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0027937 | OH | Sus | 46189631 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1916263 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412182555875 | 20240212 | 1335 | 20240212 | 1424 | 2374096 | 49 | Transformer only | Equipment Failure/Involved | Underground | 4 | 196 | 36.8395 | -121.673 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0027958 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1916270 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS COCHES-1102 | 182151102 | JUMPER | FB 1 SOUTH & 5 W/O CGC 413308739355 | 20240212 | 1352 | 20240212 | 1529 | 2374006 | 97 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 388 | 36.3918 | -121.2756 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken | 24-0027906 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1916256 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | TRANSFORMER | 316507213300 | 20240212 | 1509 | 20240212 | 1840 | 2374225 | 211 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 633 | 36.8591 | -121.6949 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 24-0028019 | OH | Sus | 31684055 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1916288 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | FUSE | 9875 | 20240212 | 1553 | 20240212 | 1700 | 2374267 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 804 | 36.3081 | -121.2308 | No | Partly Cloudy;32-90 F |  |  | 24-0028050 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1916295 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | FUSE | 54180 | 20240212 | 1624 | 20240212 | 1726 | 2374292 | 62 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 141 | 8742 | 36.5987 | -121.8787 | No | Partly Cloudy;32-90 F |  |  | 24-0028074 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1916308 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | TRANSFORMER | 100000009699 | 20240212 | 1723 | 20240213 | 1311 | 2374272 | 1188 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1188 | 36.5386 | -121.4788 | No | Partly Cloudy;32-90 F | Jumper | Broken | 24-0028079 | OH | Sus | 46190114 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1916312 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 8485 | 20240213 | 108 | 20240213 | 159 | 2374486 | 51 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 174 | 8874 | 37.06 | -122.0013 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0028134 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1916359 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 12903 | 20240213 | 653 | 20240213 | 733 | 2374572 | 40 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 320 | 37.0503 | -121.9379 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0028182 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1916377 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 24463 | 20240213 | 730 | 20240213 | 1110 | 2374591 | 220 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 1320 | 36.7977 | -121.6995 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0028317 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1916536 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 11909 | 20240213 | 745 | 20240213 | 1206 | 2374606 | 261 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 261 | 37.0125 | -122.1944 | No | Clear;32-90 F |  |  | 24-0028302 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1916530 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | TRANSFORMER | 412689644593 | 20240213 | 842 | 20240213 | 1155 | 2374685 | 193 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 193 | 36.5323 | -121.4888 | No | Clear;32-90 F |  |  | 24-0028346 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1916552 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 1225 | 20240213 | 1506 | 20240214 | 122 | 2375377 | 616 | Distribution Circuit | Animal | Bird found | 20 | 7183 | 36.9376 | -121.7762 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Burned/flashed | 24-0028566 | OH | Sus | 46190411 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1916612 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | JUMPER | OJ CGC 411354043530 | 20240213 | 1830 | 20240213 | 2218 | 2375560 | 228 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 2052 | 36.4911 | -121.9423 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0028590 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1916623 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 3909 | 20240213 | 1858 | 20240214 | 1536 | 2375610 | 1238 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 61 | 31935 | 36.8018 | -121.7009 | No | Clear;32-90 F |  |  | 24-0028612 | OH | Sus | 46190625 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1916645 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | TRANSFORMER | 412072452745 | 20240214 | 1033 | 20240215 | 1448 | 2376114 | 1695 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1695 | 36.7512 | -121.7073 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0028853 | OH | Sus | 35531690 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1916844 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | TRANSFORMER | 412203051660 | 20240214 | 1142 | 20240214 | 1347 | 2376239 | 125 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 625 | 36.7225 | -121.6634 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0028868 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1916848 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0424 | 182440424 | TRANSFORMER | 411422348611 | 20240214 | 1528 | 20240215 | 336 | 2376467 | 728 | Transformer only | Vegetation | Tree - branch fell on line | 5 | 3640 | 36.6326 | -121.9254 | No | Overcast;32-90 F | Other | Bent or Twisted | 24-0029115 | OH | Sus | 46190838 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1916902 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 7585 | 20240214 | 1832 | 20240214 | 1952 | 2376662 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 1520 | 37.0681 | -122.0054 | No | Clear;32-90 F |  |  | 24-0029201 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1916929 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | RECLOSER | 10946 | 20240214 | 1954 | 20240215 | 1111 | 2376567 | 917 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 10087 | 37.0343 | -122.0227 | No | Overcast-Rain;32-90 F | Crossarm- Wood | Broken- wire on object | 24-0029203 | OH | Sus | 31684017 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1916931 | 0 | EPSS Ckt | N | 2024 | N/A
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 12525 | 20240214 | 2015 | 20240215 | 1428 | 2376718 | 1093 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 28819 | 37.0938 | -122.0243 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0029242 | OH | Sus | 31684259 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1916958 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 9049 | 20240214 | 2015 | 20240215 | 218 | 2376837 | 363 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 4356 | 36.9963 | -121.8965 | No | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Normal | 24-0029267 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1916988 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 5351 | 20240214 | 2018 | 20240215 | 34 | 2376725 | 256 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 5120 | 37.0009 | -122.0209 | No | Overcast-Fog-Rain;32-90 F |  |  | 24-0029260 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1916977 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 5209 | 20240214 | 2100 | 20240215 | 1528 | 2376764 | 1108 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 21052 | 37.0373 | -122.0723 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0029255 | OH | Sus | 31684018 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1916971 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | TRANSFORMER | 412406657081 | 20240214 | 2126 | 20240215 | 953 | 2376806 | 747 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 747 | 36.8732 | -121.5971 | No | Partly Cloudy-Fog-Drizzle;32-90 F | Transformer | Failed/Faulted | 24-0029263 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1916981 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 621 | 20240214 | 2209 | 20240215 | 1212 | 2376793 | 843 | Distribution Circuit | Vegetation | Tree - fell into line | 151 | 104477 | 36.5298 | -121.8305 | No | Partly Cloudy-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0029253 | OH | Sus | 31684218 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1916967 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SOLEDAD-2104 | 182052104 | JUMPER | BLOWN JUMPER | 20240215 | 349 | 20240215 | 922 | 2376851 | 333 | Distribution Circuit | Equipment Failure/Involved | Overhead | 117 | 27391 | 36.4058 | -121.3538 | No | Partly Cloudy-Fog-Drizzle;32-90 F | Jumper | Burned Open | 24-0029271 | OH | Sus | 46190966 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1916992 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 12887 | 20240215 | 516 | 20240215 | 1539 | 2376877 | 623 | Distribution Circuit | 3rd Party | Vehicle | 145 | 90335 | 37.0385 | -122.0681 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken | 24-0029283 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1917001 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | OTHER | WIRE DOWN | 20240215 | 742 | 20240215 | 1143 | 2377000 | 241 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 1736 | 36.8662 | -121.5968 | No | Partly Cloudy-Fog;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0029338 | OH | Sus | 31684580 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1917037 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | TRANSFORMER | 412742644493 | 20240215 | 931 | 20240215 | 1343 | 2376915 | 252 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 252 | 36.5301 | -121.4715 | No | Partly Cloudy-Fog;32-90 F | Transformer | Failed/Faulted | 24-0029384 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917060 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | TRANSFORMER | 411816350867 | 20240215 | 1016 | 20240215 | 1802 | 2377097 | 466 | Transformer only | Equipment Failure/Involved | Overhead | 49 | 22834 | 36.6979 | -121.7935 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0029491 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917079 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0424 | 182440424 | TRANSFORMER | 411422348611 | 20240215 | 1056 | 20240215 | 1136 | 2377160 | 40 | Transformer only | Vegetation | Tree - grew into line | 5 | 200 | 36.6326 | -121.9254 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0029433 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1917071 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | FUSE | 5869 | 20240215 | 1150 | 20240216 | 402 | 2377208 | 972 | Distribution Circuit | Vegetation | Tree - fell into line | 375 | 72075 | 36.9634 | -121.9732 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0029540 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1917092 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 316395216006 | 20240215 | 1300 | 20240215 | 1811 | 2377279 | 311 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 9856 | 36.933 | -121.7345 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0029541 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1917093 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | SWITCH | 11011 | 20240215 | 1353 | 20240215 | 1416 | 2377068 | 23 | Distribution Circuit | Vegetation | Tree - grew into line | 512 | 11776 | 37.022 | -122.0214 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0029581 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1917099 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0423 | 182440423 | TRANSFORMER | 411436848098 | 20240215 | 1532 | 20240216 | 6 | 2377435 | 514 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 6682 | 36.6185 | -121.9201 | No | Partly Cloudy;32-90 F | Transformer (OH) | Deteriorated | 24-0029720 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917163 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1103 | 182011103 | RECLOSER | 93720 | 20240216 | 220 | 20240216 | 1502 | 2377727 | 762 | Distribution Circuit | Equipment Failure/Involved | Underground | 2329 | 360704 | 36.698 | -121.6619 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 24-0029738 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917177 | 0 | Non-EPSS | N | 2024 | C & GRD
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 2695 | 20240216 | 819 | 20240216 | 1318 | 2377848 | 299 | Distribution Circuit | Vegetation | Tree - grew into line | 18 | 5382 | 36.5886 | -121.9082 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0029780 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1917219 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1101 | 182201101 | TRANSFORMER | 412453947844 | 20240216 | 902 | 20240216 | 1928 | 2377788 | 626 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 626 | 36.6199 | -121.5721 | No | Overcast;32-90 F | Transformer | Broken | 24-0029821 | OH | Sus | 46191278 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917275 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 1803 | 20240216 | 1342 | 20240216 | 2252 | 2378293 | 550 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 8800 | 36.9958 | -121.8303 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0030092 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917426 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | TRANSFORMER | 315463617135 | 20240216 | 1503 | 20240217 | 1130 | 2378392 | 1227 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 13497 | 36.9592 | -122.0524 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0030088 | OH | Sus | 35532288 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917420 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | SWITCH | 8733 | 20240216 | 1835 | 20240216 | 2207 | 2378547 | 212 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 2282 | 36.4994 | -121.9364 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0030015 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1917416 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1109 | 182011109 | FUSE | 948327 | 20240217 | 1309 | 20240218 | 1857 | 2378906 | 1788 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 14304 | 36.6776 | -121.5908 | No | Overcast-Strong Winds;32-90 F |  |  | 24-0030239 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1917526 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | FUSE | 23113 | 20240217 | 1317 | 20240218 | 955 | 2378909 | 1238 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 11142 | 36.5963 | -121.621 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0030222 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1917514 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1103 | 182201103 | OTHER | WIRE DOWN AT CGC 412436049084 | 20240217 | 1456 | 20240218 | 1141 | 2379061 | 1245 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 1498 | 36.6528 | -121.5812 | No | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0030259 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1917541 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5611 | 20240217 | 1711 | 20240218 | 220 | 2379114 | 549 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 13176 | 37.1001 | -122.0362 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0030272 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1917554 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 6999 | 20240217 | 1751 | 20240217 | 1857 | 2379144 | 66 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 1386 | 36.4908 | -121.9382 | No | Overcast-Drizzle;32-90 F |  |  | 24-0030279 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1917561 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 445933 | 20240217 | 1926 | 20240218 | 328 | 2379213 | 482 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 26992 | 37.1372 | -122.1004 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 24-0030282 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1917562 | 0 | EPSS Ckt | N | 2024 | A & C
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 8915 | 20240217 | 1939 | 20240218 | 1329 | 2379224 | 1070 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 12840 | 37.1665 | -122.1671 | No | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0030355 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1917634 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | FUSE | 7749 | 20240217 | 2014 | 20240218 | 1417 | 2379262 | 1083 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 8664 | 36.2585 | -121.185 | No | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken | 24-0030347 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | No | No | 1917627 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 5277 | 20240217 | 2049 | 20240217 | 2154 | 2379270 | 65 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 2600 | 36.7758 | -121.6878 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0030342 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1917621 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRIP-SAVER | 834583 | 20240218 | 29 | 20240218 | 801 | 2379353 | 452 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 15368 | 37.0442 | -122.0777 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0030376 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917653 | 0 | EPSS Ckt | N | 2024 | POS 1
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 12122 | 20240218 | 110 | 20240218 | 1318 | 2379362 | 728 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 15574 | 37.0666 | -122.2288 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0030360 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1917639 | 0 | EPSS Ckt | N | 2024 | B C 51 TIME
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | TRANSFORMER | 412169053560 | 20240218 | 351 | 20240218 | 1543 | 2379376 | 712 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 4272 | 36.7744 | -121.6754 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0030368 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1917646 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 3287 | 20240218 | 613 | 20240218 | 700 | 2379402 | 47 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 626 | 36.6786 | -121.7086 | No | Clear;32-90 F | Fuse | Broken | 24-0030374 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1917650 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 7747 | 20240218 | 635 | 20240218 | 1041 | 2379392 | 246 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1476 | 36.5756 | -121.9707 | No | Partly Cloudy-Fog;32-90 F | Other | Deteriorated | 24-0030371 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1917648 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 9605 | 20240218 | 638 | 20240218 | 750 | 2379411 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 432 | 36.9836 | -121.778 | No | Fog;32-90 F |  |  | 24-0030375 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1917651 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | OTHER | WIRE DOWN @ 900 JARVIS RD | 20240218 | 935 | 20240219 | 1818 | 2379531 | 1963 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 5691 | 37.065 | -121.9794 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0030411 | OH | Sus | 35532242 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1917674 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1102 | 182011102 | TRANSFORMER | 412239650463 | 20240218 | 943 | 20240218 | 1321 | 2379458 | 218 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 436 | 36.6902 | -121.6478 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0030401 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917668 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | TRANSFORMER | 315474417301 | 20240218 | 1140 | 20240218 | 1548 | 2379498 | 248 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 2976 | 36.9639 | -122.0489 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0030418 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917679 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | JUMPER | OJ 20 SPANS LD SIDE 5587 | 20240218 | 1205 | 20240219 | 1056 | 2379650 | 1371 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 9821 | 36.6633 | -121.7157 | No | Clear;32-90 F | Jumper | Burned Open | 24-0030475 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1917714 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 137352 | 20240218 | 1344 | 20240218 | 1351 | 2379657 | 7 | Distribution Circuit | Company Initiated | Return Circuit Normal | 14 | 98 | 37.1129 | -122.2988 | No | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Normal | 24-0030360 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1917693 | 0 | EPSS Ckt | N | 2024 | NONE
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | FUSE | 50575 | 20240218 | 1348 | 20240218 | 1720 | 2379682 | 212 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 770 | 36.8519 | -121.4447 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0030482 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917720 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 64219 | 20240218 | 1612 | 20240218 | 1636 | 2379820 | 24 | Distribution Circuit | Vegetation | Tree - branch fell on line | 31 | 744 | 36.9879 | -122.0184 | No | Overcast-Drizzle;32-90 F | Jumper | Normal | 24-0030489 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917729 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 2913 | 20240218 | 1714 | 20240219 | 235 | 2379871 | 561 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3927 | 37.1752 | -122.1446 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0030518 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1917759 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 90678 | 20240218 | 1733 | 20240219 | 1724 | 2379882 | 1431 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 64878 | 37.0954 | -122.1281 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0030499 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1917739 | 0 | EPSS Ckt | N | 2024 | B&C PHASE
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | TRANSFORMER | 411430746605 | 20240218 | 1947 | 20240219 | 927 | 2380052 | 820 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 4100 | 36.5781 | -121.9199 | No | Overcast-Rain;32-90 F | Secondary | Broken- wire on ground | 24-0030539 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | Yes | 1917778 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | TRANSFORMER | 315691718394 | 20240218 | 2132 | 20240219 | 439 | 2380139 | 427 | Transformer only | Vegetation | Tree - bark fell into line | 3 | 1281 | 36.9957 | -121.9765 | No | Overcast-Fog-Rain;32-90 F | Fuse | Failed/Faulted | 24-0030607 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917847 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 11663 | 20240218 | 2147 | 20240219 | 1020 | 2380153 | 753 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 2259 | 36.9616 | -122.0894 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 24-0030623 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | No | No | 1917862 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | FUSE | 5919 | 20240218 | 2148 | 20240219 | 852 | 2380154 | 664 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 20584 | 36.5295 | -121.7008 | No | Clear;32-90 F |  |  | 24-0030574 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1917814 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1112 | 182371112 | RECLOSER | 438 | 20240218 | 2149 | 20240218 | 2336 | 2380156 | 107 | Distribution Circuit | Equipment Failure/Involved | Overhead | 247 | 26429 | 36.4967 | -121.7313 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0030567 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1917807 | 0 | EPSS Ckt | N | 2024 | A & C
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | TRANSFORMER | 412951857120 | 20240218 | 2154 | 20240219 | 35 | 2380159 | 161 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 483 | 36.8779 | -121.4109 | No | Partly Cloudy-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0030586 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917826 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1109 | 182011109 | FUSE | 948327 | 20240218 | 2205 | 20240219 | 1325 | 2380164 | 920 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 6320 | 36.6776 | -121.5908 | No | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Deteriorated | 24-0030581 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1917821 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 6999 | 20240218 | 2229 | 20240219 | 108 | 2380172 | 159 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 3339 | 36.4908 | -121.9382 | No | Overcast-Fog-Heavy Rain;32-90 F |  |  | 24-0030587 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1917827 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | FUSE | 7495 | 20240218 | 2238 | 20240219 | 1832 | 2380178 | 1194 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 56619 | 36.9828 | -121.9278 | No | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0030603 | OH | Sus | 35532242 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1917843 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 675 | 20240218 | 2247 | 20240219 | 414 | 2380180 | 327 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 2396 | 36.8681 | -121.6715 | No | Clear;32-90 F |  |  | 24-0030604 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917844 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 6477 | 20240218 | 2305 | 20240219 | 503 | 2380294 | 358 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 358 | 36.6035 | -121.9089 | No | Overcast-Fog-Heavy Rain;32-90 F | Pothead(Riser Termination) | Failed/Faulted | 24-0030609 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917849 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 12473 | 20240218 | 2342 | 20240219 | 234 | 2380212 | 172 | Distribution Circuit | Vegetation | Tree - branch fell on line | 83 | 14276 | 36.9718 | -121.8759 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 24-0030590 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917830 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 346475 | 20240219 | 140 | 20240219 | 641 | 2380353 | 301 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 2408 | 37.058 | -121.9416 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 24-0030624 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917863 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 900581 | 20240219 | 240 | 20240219 | 2245 | 2380267 | 1205 | Distribution Circuit | 3rd Party | Vehicle | 1 | 1205 | 36.8909 | -121.6698 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken | 24-0030596 | OH | Sus | 35532442 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1917836 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | FUSE | 5251 | 20240219 | 642 | 20240219 | 1506 | 2380379 | 504 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 2106 | 36.7258 | -121.5946 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0030706 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1917926 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | OCB | 1102/2 | 20240219 | 656 | 20240219 | 1924 | 2380401 | 748 | Distribution Circuit | Vegetation | Tree - fell into line | 1703 | 308708 | 37.1312 | -122.1723 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 24-0030627 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1917865 | 0 | EPSS Ckt | N | 2024 | GRD SGF I
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 7259 | 20240219 | 719 | 20240219 | 1919 | 2380416 | 720 | Distribution Circuit | 3rd Party | Vehicle | 46 | 33120 | 36.5752 | -121.9365 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 24-0030678 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1917903 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9709 | 20240219 | 728 | 20240219 | 935 | 2380436 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 1905 | 37.1163 | -122.1184 | No | Clear;32-90 F |  |  | 24-0030707 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1917927 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | TRANSFORMER | 412869034355 | 20240219 | 736 | 20240219 | 1358 | 2380443 | 382 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 764 | 36.2528 | -121.4194 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Broken | 24-0030714 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917932 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 316151020915 | 20240219 | 912 | 20240219 | 1624 | 2380580 | 432 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 432 | 37.066 | -121.8208 | No | Partly Cloudy-Fog;32-90 F | Transformer | Failed/Faulted | 24-0030786 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917988 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5225 | 20240219 | 1019 | 20240219 | 1931 | 2381377 | 552 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3664 | 37.0496 | -122.0856 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0030890 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1918064 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 346475 | 20240219 | 1255 | 20240219 | 1827 | 2381251 | 332 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 2656 | 37.058 | -121.9416 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0030876 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1918051 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 5269 | 20240219 | 1337 | 20240219 | 1442 | 2381470 | 65 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 563 | 36.9894 | -122.0312 | No | Overcast-Drizzle;32-90 F |  |  | 24-0030895 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1918069 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRANSFORMER | 315232223574 | 20240219 | 1355 | 20240220 | 1154 | 2381537 | 1319 | Transformer only | Environmental/External | Water | 1 | 1319 | 37.1354 | -122.1369 | No | Strong Winds-Clear;32-90 F | Transformer | Broken- wire on ground | 24-0030966 | OH | Sus | 35532242 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1918113 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | TRANSFORMER | 411460247093 | 20240219 | 1418 | 20240219 | 2245 | 2381608 | 507 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 4563 | 36.5911 | -121.9111 | No | Rain-Partly Cloudy;32-90 F | Service conductor | Failed/Faulted | 24-0030968 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1918114 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | TRANSFORMER | T0479 | 20240219 | 1421 | 20240219 | 1832 | 2381603 | 251 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 251 | 36.6956 | -121.5831 | No | Overcast;32-90 F | Jumper | Broken | 24-0030936 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1918097 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRANSFORMER | 315157924442 | 20240219 | 1422 | 20240219 | 2032 | 2381606 | 370 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 2220 | 37.1594 | -122.1627 | No | Strong Winds-Clear;32-90 F | Transformer | Failed/Faulted | 24-0030995 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1918130 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | OTHER | WRIE DOWN AT CGC 315219821719 | 20240219 | 1451 | 20240219 | 2332 | 2381957 | 521 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 5731 | 37.0851 | -122.1397 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0031039 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1918162 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | TRANSFORMER | 411463746804 | 20240219 | 1451 | 20240219 | 1726 | 2381668 | 155 | Transformer only | Unknown Cause | Patrol - found nothing | 8 | 1240 | 36.5832 | -121.9094 | No | Rain-Partly Cloudy;32-90 F |  |  | 24-0031001 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1918136 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | TRANSFORMER | 412904260038 | 20240219 | 1640 | 20240219 | 1900 | 2381856 | 140 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 420 | 36.9577 | -121.4299 | No | Partly Cloudy;32-90 F | Secondary | Burned/flashed | 24-0031003 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1918138 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 6775 | 20240219 | 1700 | 20240220 | 136 | 2381884 | 516 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 38700 | 36.8813 | -121.6414 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0031035 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1918158 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | KING CITY-1103 | 182031103 | TRANSFORMER | 413488430321 | 20240219 | 1806 | 20240220 | 1 | 2381952 | 355 | Transformer only | Vegetation | Tree - fell into line | 1 | 355 | 36.1474 | -121.2055 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0031069 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1918185 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | RECLOSER | 2000 | 20240220 | 659 | 20240220 | 826 | 2382449 | 87 | Distribution Circuit | Equipment Failure/Involved | Underground | 1520 | 109488 | 36.5852 | -121.8743 | No | Partly Cloudy;32-90 F | Stepdown | Broken | 24-0031172 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1918269 | 0 | EPSS Ckt | N | 2024 | C GRD
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316338717140 | 20240220 | 818 | 20240220 | 1501 | 2382458 | 403 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 403 | 36.9639 | -121.754 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0031238 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1918309 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 412073149815 | 20240220 | 927 | 20240220 | 1400 | 2382609 | 273 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 273 | 36.6709 | -121.7047 | No | Clear;32-90 F | Transformer | Broken | 24-0031279 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1918369 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 995261 | 20240220 | 1038 | 20240220 | 1100 | 2382552 | 22 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 1122 | 37.0986 | -121.9896 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0031332 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1918394 | 0 | EPSS Ckt | N | 2024 | N/A
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 5461 | 20240220 | 1155 | 20240220 | 1215 | 2382861 | 20 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 440 | 37.1383 | -122.1436 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0031397 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1918414 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1101 | 182201101 | TRANSFORMER | 412534247027 | 20240220 | 1320 | 20240220 | 1451 | 2383015 | 91 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 91 | 36.5985 | -121.5446 | No | Clear;32-90 F | Transformer | Broken | 24-0031465 | OH | Sus | 46193223 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1918435 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 5269 | 20240220 | 1343 | 20240220 | 1458 | 2383055 | 75 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 649 | 36.9894 | -122.0312 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0031549 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1918461 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 6999 | 20240220 | 1401 | 20240220 | 2346 | 2383068 | 585 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 12285 | 36.4908 | -121.9382 | No | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0031613 | OH | Sus | 35532685 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1918472 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | TRANSFORMER | 315520816985 | 20240220 | 1413 | 20240220 | 1427 | 2383038 | 14 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 140 | 36.9563 | -122.0339 | No | Overcast-Drizzle;32-90 F | Transformer | Deteriorated | 24-0031512 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1918452 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | RECLOSER | 12990 | 20240220 | 1618 | 20240220 | 2245 | 2382854 | 387 | Distribution Circuit | Vegetation | Tree - fell into line | 791 | 113229 | 37.039 | -122.0214 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0031618 | OH | Sus | 46193227 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1918474 | 0 | EPSS Ckt | N | 2024 | N/A
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 63989 | 20240220 | 1741 | 20240221 | 1133 | 2383312 | 1072 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1072 | 37.0809 | -122.0504 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0031681 | OH | Sus | 46193376 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1918513 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 7791 | 20240220 | 1755 | 20240221 | 249 | 2383242 | 534 | Distribution Circuit | 3rd Party | Vehicle | 17 | 9078 | 36.2642 | -121.798 | No | Clear;32-90 F | Pothead(Riser Termination) | Broken | 24-0031663 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1918499 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | TRANSFORMER | 412147649885 | 20240220 | 1851 | 20240221 | 211 | 2383333 | 440 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 4400 | 36.6735 | -121.6793 | No | Overcast;32-90 F | Transformer | Failed/Faulted | 24-0031672 | OH | Sus | 35532691 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1918507 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | TRANSFORMER | 315769418104 | 20240221 | 332 | 20240221 | 405 | 2383458 | 33 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 198 | 36.9881 | -121.9494 | No | Partly Cloudy-Fog;32-90 F | Transformer | Deteriorated | 24-0031810 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1918595 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | FUSE | 868789 | 20240221 | 711 | 20240221 | 900 | 2383636 | 109 | Distribution Circuit | Animal | Bird found | 5 | 545 | 36.5697 | -121.729 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0031911 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1918731 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | FUSE | 6001 | 20240221 | 1157 | 20240221 | 1254 | 2384210 | 57 | Distribution Circuit | Vegetation | Tree - bark fell into line | 111 | 6302 | 36.9898 | -121.9328 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0032092 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1918822 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | TRANSFORMER | 315520816985 | 20240221 | 1230 | 20240221 | 1448 | 2384359 | 138 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 1380 | 36.9563 | -122.0339 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0032124 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1918827 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316405717533 | 20240221 | 1243 | 20240221 | 2109 | 2384263 | 506 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1012 | 36.9753 | -121.731 | No | Clear;32-90 F | Service conductor | Deteriorated | 24-0032197 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1918846 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411855551897 | 20240221 | 1245 | 20240221 | 2033 | 2384268 | 468 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1872 | 36.7268 | -121.7799 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0032206 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1918848 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | OTHER | WIRE DOWN AT CGC 411383343350 | 20240221 | 1307 | 20240221 | 1807 | 2384314 | 300 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 5008 | 36.4871 | -121.9321 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0032212 | OH | Sus | 31684846 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1918849 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 75803 | 20240221 | 1437 | 20240221 | 1740 | 2384430 | 183 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 4575 | 36.5442 | -121.753 | No | Clear;32-90 F |  |  | 24-0032297 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1918867 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 7541 | 20240221 | 1719 | 20240221 | 1926 | 2384577 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 635 | 36.9449 | -121.8179 | No | Clear;32-90 F |  |  | 24-0032310 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1918873 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1112 | 182371112 | TRANSFORMER | 411906845248 | 20240221 | 1759 | 20240222 | 1016 | 2384610 | 977 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 977 | 36.544 | -121.7567 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0032355 | OH | Sus | 31684872 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1918918 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | FUSE | 4211 | 20240221 | 1829 | 20240221 | 1928 | 2384628 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 1829 | 36.9688 | -121.4325 | No | Partly Cloudy;32-90 F |  |  | 24-0032311 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1918875 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | OCB | 1102/2 | 20240222 | 642 | 20240222 | 1216 | 2384816 | 334 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2137 | 188258 | 36.6242 | -121.6886 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0032379 | OH | Sus | 46193882 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1918941 | 0 | EPSS Ckt | N | 2024 | SGF INST GRD
CENTRAL COAST | SALINAS | SPENCE-1103 | 182201103 | TRANSFORMER | 412459248532 | 20240222 | 949 | 20240222 | 1819 | 2385145 | 510 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 510 | 36.6382 | -121.5696 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0032636 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1919185 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1102 | 182011102 | TRANSFORMER | 412231750859 | 20240222 | 1151 | 20240222 | 1536 | 2385315 | 225 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 2025 | 36.7008 | -121.6515 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0032589 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1919162 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | SWITCH | 3837 | 20240222 | 1342 | 20240222 | 1355 | 2385442 | 13 | Distribution Circuit | Company Initiated | Return Circuit Normal | 5 | 65 | 36.6247 | -121.6828 | No | Clear;32-90 F | Connector or Splice (OH) | Normal | 24-0032379 | OH | Sus | 46193882 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1919206 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | TRANSFORMER | 412669444591 | 20240222 | 1547 | 20240223 | 851 | 2385551 | 1024 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1024 | 36.5322 | -121.4956 | No | Clear;32-90 F | Jumper | Broken | 24-0032783 | OH | Sus | 46194382 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1919235 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | TRANSFORMER | 315204521858 | 20240222 | 1906 | 20240222 | 2207 | 2385647 | 181 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 181 | 37.0888 | -122.145 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0032805 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1919245 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | RECLOSER | 2000 | 20240222 | 2119 | 20240222 | 2138 | 2385728 | 19 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1520 | 28880 | 36.5852 | -121.8743 | No | Partly Cloudy;32-90 F | Regulator | Arcing | 24-0032880 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1919322 | 0 | EPSS Ckt | N | 2024 | N/A
CENTRAL COAST | MONTEREY | DEL MONTE-1101 | 182221101 | TRANSFORMER | 411719447985 | 20240222 | 2320 | 20240223 | 224 | 2385769 | 184 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 2208 | 36.6174 | -121.8231 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0032952 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1919376 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-1101 | 182221101 | TRANSFORMER | 411717947997 | 20240222 | 2324 | 20240223 | 224 | 2385770 | 180 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 2340 | 36.6177 | -121.8237 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0032953 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1919377 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 3621 | 20240223 | 631 | 20240223 | 836 | 2385841 | 125 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 343 | 42875 | 36.7789 | -121.6493 | No | Clear;32-90 F |  |  | 24-0033063 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1919470 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 316133418066 | 20240223 | 1019 | 20240223 | 1240 | 2386078 | 141 | Transformer only | Equipment Failure/Involved | Underground | 4 | 564 | 36.9885 | -121.825 | No | Partly Cloudy;32-90 F | Secondary | Deteriorated | 24-0033092 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1919542 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2106 | 182402106 | FUSE | 9815 | 20240223 | 1249 | 20240223 | 1321 | 2386304 | 32 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 992 | 36.6395 | -121.8022 | No | Partly Cloudy;32-90 F |  |  | 24-0033273 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1919612 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 5949 | 20240223 | 1517 | 20240223 | 1721 | 2386428 | 124 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 124 | 36.7833 | -121.7201 | No | Clear;32-90 F |  |  | 24-0033383 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1919639 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | SWITCH | 704757 | 20240223 | 1735 | 20240223 | 2010 | 2386497 | 155 | Distribution Circuit | Equipment Failure/Involved | Underground | 5 | 775 | 36.8904 | -121.8218 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0033376 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1919635 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | TRANSFORMER | 316328313809 | 20240223 | 2012 | 20240224 | 1008 | 2386580 | 836 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 836 | 36.8725 | -121.7563 | No | Partly Cloudy;32-90 F | Transformer | Broken | 24-0033398 | OH | Sus | 46195159 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1919648 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | FUSE | 3995 | 20240223 | 2230 | 20240224 | 527 | 2386609 | 417 | Distribution Circuit | Vegetation | Tree - grew into line | 243 | 84570 | 36.6704 | -121.6797 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 24-0033354 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1919683 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | TRANSFORMER | 316295114675 | 20240224 | 1058 | 20240224 | 2108 | 2386810 | 610 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1830 | 36.8961 | -121.768 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0033480 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1919758 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | SWITCH | 2225 | 20240224 | 1452 | 20240225 | 1938 | 2386903 | 1726 | Distribution Circuit | Equipment Failure/Involved | Overhead | 379 | 654154 | 36.3198 | -121.2409 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0033513 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1919778 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2102 | 182222102 | SWITCH | 40061 | 20240224 | 2113 | 20240224 | 2141 | 2387069 | 28 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2351 | 65828 | 36.6084 | -121.8432 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0033541 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1919828 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | FUSE | 4837 | 20240225 | 1812 | 20240225 | 1901 | 2387558 | 49 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 441 | 36.8909 | -121.4227 | No | Clear;32-90 F |  |  | 24-0033670 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1919918 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8241 | 20240225 | 2052 | 20240226 | 1354 | 2387652 | 1022 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 8225 | 37.1179 | -121.9648 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0033691 | OH | Sus | 46199641 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1919939 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 12887 | 20240226 | 642 | 20240226 | 900 | 2387912 | 138 | Distribution Circuit | Vegetation | Tree - branch fell on line | 48 | 6663 | 37.0385 | -122.0681 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0033752 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1920079 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6583 | 20240226 | 749 | 20240226 | 1135 | 2388059 | 226 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 301 | 36.9239 | -121.6972 | No | Clear;32-90 F |  |  | 24-0033869 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1920166 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1102 | 182201102 | TRANSFORMER | 412626047850 | 20240226 | 750 | 20240226 | 1659 | 2387730 | 549 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1647 | 36.6209 | -121.5141 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0033759 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1920108 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1103 | 182201103 | JUMPER | 412436049084 | 20240226 | 816 | 20240226 | 1309 | 2387772 | 293 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 293 | 36.6535 | -121.5799 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 24-0033782 | OH | Sus | 46199770 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1920141 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 912058 | 20240226 | 1139 | 20240226 | 1203 | 2388119 | 24 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 43 | 1032 | 36.9623 | -121.7302 | No | Partly Cloudy;32-90 F |  |  | 24-0033865 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1920163 | 0 | EPSS Ckt | N | 2024 | NONE
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | JUMPER | WIRE DOWN 1 SPAN SW/OF 315346819855 | 20240226 | 1319 | 20240226 | 1811 | 2388278 | 292 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 3340 | 37.0336 | -122.0956 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0034004 | OH | Sus | 46200045 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1920207 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 50899 | 20240226 | 1813 | 20240227 | 932 | 2388442 | 917 | Distribution Circuit | Animal | Other | 3 | 2443 | 36.8323 | -121.3483 | No | Overcast;32-90 F | Transformer (OH) | Normal | 24-0034106 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1920231 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | FUSE | 23129 | 20240227 | 702 | 20240227 | 1050 | 2388638 | 228 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1065 | 36.5439 | -121.5146 | No | Clear;32-90 F |  |  | 24-0034326 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1920479 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 7747 | 20240227 | 905 | 20240227 | 1219 | 2388812 | 194 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1164 | 36.5756 | -121.9707 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0034247 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1920389 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | FUSE | 9193 | 20240227 | 926 | 20240227 | 1147 | 2388841 | 141 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 3 | 423 | 35.9664 | -121.1324 | No | Partly Cloudy;32-90 F | Pole-Wood | Normal | 24-0034251 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1920411 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | SWITCH | 704757 | 20240227 | 1010 | 20240227 | 1829 | 2388853 | 499 | Distribution Circuit | Equipment Failure/Involved | Underground | 5 | 2495 | 36.8904 | -121.8218 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0034256 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1920419 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 9979 | 20240227 | 1013 | 20240227 | 1143 | 2388961 | 90 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 540 | 36.7172 | -121.2194 | No | Clear;32-90 F |  |  | 24-0034377 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1920495 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1101 | 182201101 | TRANSFORMER | 412451147594 | 20240227 | 1300 | 20240227 | 1406 | 2389155 | 66 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 66 | 36.613 | -121.5729 | No | Clear;32-90 F | Fuse | Broken | 24-0034481 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1920523 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | BUENA VISTA-1104 | 182261104 | TRANSFORMER | 412303749434 | 20240227 | 1435 | 20240227 | 1511 | 2389186 | 36 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 72 | 36.6621 | -121.6255 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0034567 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1920540 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 7013 | 20240227 | 1638 | 20240228 | 842 | 2389352 | 964 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 5784 | 36.9713 | -121.7919 | No | Clear;32-90 F | Jumper | Broken | 24-0034620 | OH | Sus | 46200502 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1920568 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | TRANSFORMER | 412009242720 | 20240227 | 1753 | 20240228 | 1125 | 2389458 | 1052 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1052 | 36.4759 | -121.7189 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0034639 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1920588 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6639 | 20240227 | 1940 | 20240228 | 1004 | 2389464 | 864 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 29376 | 37.0075 | -121.809 | No | Clear;32-90 F | Cutout- fuse holder | Arcing | 24-0034616 | OH | Sus | 31685201 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1920564 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 912058 | 20240228 | 424 | 20240228 | 629 | 2389584 | 125 | Distribution Circuit | Equipment Failure/Involved | Overhead | 43 | 5375 | 36.9623 | -121.7302 | No | Clear;32-90 F | Recloser | Malfunctioning | 24-0034654 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1920608 | 0 | EPSS Ckt | N | 2024 | UNKNOWN
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 6033 | 20240228 | 629 | 20240228 | 847 | 2389598 | 138 | Distribution Circuit | Animal | Bird found | 82 | 11316 | 37.081 | -122.0049 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0034746 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1920691 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 68191 | 20240228 | 639 | 20240228 | 934 | 2389877 | 175 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 3325 | 36.9816 | -121.9026 | No | Clear;32-90 F |  |  | 24-0034803 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1920797 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | FUSE | 3575 | 20240228 | 941 | 20240228 | 1105 | 2389912 | 84 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 252 | 36.7297 | -121.7326 | No | Clear;32-90 F |  |  | 24-0034876 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1920819 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | RECLOSER | BL 1101 | 20240228 | 1045 | 20240228 | 1052 | 2389976 | 7 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 744 | 5208 | 37.0926 | -122.0966 | No | Clear;32-90 F |  |  | 24-0034861 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1920816 | 0 | EPSS Ckt | N | 2024 | C-B
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411902252789 | 20240228 | 1331 | 20240228 | 1855 | 2390043 | 324 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 324 | 36.7513 | -121.7656 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0034979 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1920851 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 412031954456 | 20240228 | 1350 | 20240228 | 2201 | 2390187 | 491 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 3437 | 36.7992 | -121.7231 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0035046 | OH | Sus | 46200638 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1920866 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 9495 | 20240228 | 1453 | 20240228 | 1555 | 2390248 | 62 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 992 | 36.7617 | -121.7465 | No | Clear;32-90 F |  |  | 24-0035092 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1920878 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | TRANSFORMER | 411439145244 | 20240229 | 1129 | 20240229 | 1348 | 2390992 | 139 | Transformer only | 3rd Party | Thrown Object | 13 | 1807 | 36.5401 | -121.9159 | No | Overcast;32-90 F | Secondary | Broken- wire on ground | 24-0035454 | OH | Sus | 31685272 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1921092 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | INTERRUPTER | 977600 | 20240229 | 1311 | 20240229 | 1405 | 2391319 | 54 | Distribution Circuit | Vegetation | Tree - branch fell on line | 254 | 13716 | 36.9801 | -121.9084 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0035586 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1921146 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 9975 | 20240229 | 1321 | 20240301 | 137 | 2391338 | 736 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 2208 | 36.9823 | -121.8292 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0035630 | OH | Sus | 46201325 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1921167 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 6121 | 20240229 | 1406 | 20240229 | 1549 | 2391379 | 103 | Distribution Circuit | Vegetation | Tree - branch fell on line | 109 | 11227 | 36.9835 | -121.8848 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0035686 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1921187 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | JUMPER | OJ @ CGC 316638013415 | 20240229 | 1411 | 20240229 | 1551 | 2391378 | 100 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 600 | 36.8634 | -121.6501 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 24-0035510 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1921150 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 5269 | 20240229 | 1419 | 20240229 | 1457 | 2391413 | 38 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 329 | 36.9894 | -122.0312 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0035633 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1921169 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 551 | 20240229 | 1456 | 20240229 | 1537 | 2391451 | 41 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 173 | 7093 | 36.9664 | -121.9983 | No | Overcast-Drizzle;32-90 F |  |  | 24-0035660 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1921179 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 5983 | 20240229 | 1621 | 20240229 | 1920 | 2391532 | 179 | Distribution Circuit | Vegetation | Tree - bark fell into line | 5 | 895 | 37.0399 | -121.9427 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0035766 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1921212 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 9963 | 20240229 | 1931 | 20240229 | 2335 | 2391649 | 244 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 4392 | 36.9736 | -121.8067 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 24-0035814 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1921242 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 12333 | 20240229 | 1945 | 20240301 | 119 | 2391660 | 334 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 334 | 36.8597 | -121.7947 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0035821 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1921246 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 5413 | 20240229 | 2041 | 20240301 | 908 | 2391679 | 747 | Distribution Circuit | Vegetation | Tree - branch fell on line | 35 | 9467 | 37.0443 | -122.1497 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0035816 | OH | Sus | 46201480 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1921243 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 7011 | 20240229 | 2302 | 20240301 | 22 | 2391711 | 80 | Distribution Circuit | Vegetation | Tree - branch fell on line | 50 | 4000 | 36.9739 | -121.7971 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 24-0035818 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1921244 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | OCB | 2201/2 | 20240301 | 235 | 20240301 | 1217 | 2391724 | 582 | Distribution Circuit | Vegetation | Tree - fell into line | 1939 | 115078 | 36.5786 | -121.9085 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0035822 | OH | Sus | 31685408 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | Yes | No | 1921247 | 0 | EPSS Ckt | N | 2024 | TIME OC
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 4953 | 20240301 | 758 | 20240301 | 1105 | 2391836 | 187 | Distribution Circuit | Animal | Bird found | 170 | 31790 | 36.8253 | -121.6618 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0036031 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1921300 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0424 | 182440424 | FUSE | 2997 | 20240301 | 907 | 20240301 | 1030 | 2391879 | 83 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 913 | 36.6335 | -121.9253 | Yes | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0035938 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1921273 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | FUSE | 479233 | 20240301 | 917 | 20240301 | 1136 | 2391959 | 139 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 1 | 93 | 36.8339 | -121.4394 | Yes | Overcast;32-90 F | Pole-Wood | Burned/flashed | 24-0036004 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1921291 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 2300/2 | 20240301 | 1303 | 20240301 | 1447 | 2392098 | 104 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3349 | 125758 | 36.9522 | -121.76 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Together | 24-0036123 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1921324 | 0 | EPSS Ckt | N | 2024 | BC
CENTRAL COAST | MONTEREY | DEL MONTE-1101 | 182221101 | FUSE | 10157 | 20240301 | 1727 | 20240301 | 1817 | 2392596 | 50 | Distribution Circuit | 3rd Party | Metallic Balloon | 27 | 1350 | 36.6196 | -121.8297 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0036367 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1921418 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0422 | 182440422 | TRANSFORMER | 411436847861 | 20240301 | 1811 | 20240301 | 1852 | 2392750 | 41 | Transformer only | Unknown Cause | Patrol - not conducted | 4 | 164 | 36.612 | -121.9198 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0036395 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1921440 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 2799 | 20240301 | 1833 | 20240301 | 2020 | 2392768 | 107 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 642 | 36.5731 | -121.9443 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0036379 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1921425 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 2447 | 20240301 | 2012 | 20240301 | 2250 | 2393927 | 158 | Distribution Circuit | Vegetation | Tree - bark fell into line | 3 | 474 | 36.998 | -121.9852 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0036580 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1921619 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 2689 | 20240301 | 2026 | 20240302 | 850 | 2393351 | 744 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 23808 | 37.1274 | -122.0181 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0036766 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1921793 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 5269 | 20240301 | 2121 | 20240301 | 2234 | 2393625 | 73 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 632 | 36.9894 | -122.0312 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Together | 24-0036550 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1921593 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6543 | 20240301 | 2142 | 20240301 | 2259 | 2393669 | 77 | Distribution Circuit | Vegetation | Tree - bark fell into line | 26 | 2002 | 36.9267 | -121.8459 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0036574 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1921613 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9557 | 20240301 | 2205 | 20240302 | 1645 | 2393802 | 1120 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3360 | 37.1324 | -122.106 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036745 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1921777 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2103 | 83252103 | FUSE | 1985 | 20240301 | 2223 | 20240302 | 836 | 2393842 | 613 | Distribution Circuit | Equipment Failure/Involved | Overhead | 62 | 38006 | 36.9707 | -122.0188 | Yes | Overcast-Drizzle;32-90 F | Connector or Splice (OH) | Broken | 24-0036681 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1921725 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | TRANSFORMER | 315292422842 | 20240301 | 2236 | 20240302 | 1248 | 2393879 | 852 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 1704 | 37.1167 | -122.1138 | Yes | Clear;32-90 F | Transformer | Normal | 24-0036852 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1921859 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 9271 | 20240301 | 2253 | 20240302 | 810 | 2393913 | 557 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 7241 | 37.036 | -121.86 | Yes | Clear-Lightning;32-90 F |  |  | 24-0036743 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1921776 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 8861 | 20240301 | 2311 | 20240302 | 700 | 2393951 | 469 | Distribution Circuit | Vegetation | Tree - branch fell on line | 115 | 53935 | 37.0117 | -122.0315 | Yes | Overcast-Drizzle-Lightning;32-90 F | Conductor- Overhead | Normal | 24-0036699 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1921742 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 9989 | 20240301 | 2316 | 20240302 | 1441 | 2393953 | 925 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 12025 | 37.0186 | -121.8172 | Yes | Clear-Lightning;32-90 F |  |  | 24-0036964 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1921928 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | TRANSFORMER | 315540718266 | 20240301 | 2321 | 20240302 | 1646 | 2393968 | 1045 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1045 | 36.9911 | -122.0273 | Yes | Overcast-Drizzle-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 24-0036736 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1921770 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 5335 | 20240302 | 15 | 20240302 | 1300 | 2394147 | 765 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 55080 | 37.028 | -121.9873 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036695 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1921738 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 6911 | 20240302 | 34 | 20240302 | 940 | 2394116 | 546 | Distribution Circuit | Vegetation | Tree - branch fell on line | 98 | 53508 | 37.0171 | -121.7217 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0036753 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1921783 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | FUSE | 7227 | 20240302 | 36 | 20240302 | 1025 | 2394109 | 589 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 2356 | 35.9778 | -121.2147 | No | Clear;32-90 F |  |  | 24-0036755 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1921785 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | JUMPER | OJ 1 SS OF 23797 | 20240302 | 46 | 20240302 | 952 | 2394431 | 546 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1638 | 36.762 | -121.7876 | No | Clear;32-90 F | Jumper | Broken | 24-0036691 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1921734 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | RECLOSER | 70782 | 20240302 | 47 | 20240302 | 952 | 2394142 | 545 | Distribution Circuit | Equipment Failure/Involved | Overhead | 165 | 89925 | 36.7798 | -121.7788 | No | Overcast;32-90 F | Jumper | Broken | 24-0036624 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1921665 | 0 | Non-EPSS | N | 2024 | B-C
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | JUMPER | OJ HIGH SIDE OF 841 | 20240302 | 47 | 20240302 | 1126 | 2394423 | 639 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 4457 | 36.7598 | -121.7866 | No | Clear;32-90 F | Jumper | Broken | 24-0036688 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1921731 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 711 | 20240302 | 106 | 20240302 | 910 | 2394160 | 484 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 10648 | 37.0529 | -122.1604 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0036763 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1921791 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 8983 | 20240302 | 115 | 20240302 | 810 | 2394284 | 415 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 20335 | 37.0307 | -122.1429 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0036713 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1921752 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 5365 | 20240302 | 120 | 20240302 | 1228 | 2394173 | 668 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 14696 | 36.9946 | -122.0283 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036692 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1921735 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | RECLOSER | 2760 | 20240302 | 122 | 20240302 | 128 | 2394165 | 6 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 176 | 1056 | 36.5581 | -121.7506 | No | Clear;32-90 F |  |  | 24-0036637 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1921680 | 0 | EPSS Ckt | N | 2024 | A-C
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 6809 | 20240302 | 139 | 20240302 | 1456 | 2394193 | 797 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 16737 | 36.8451 | -121.6349 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036719 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1921757 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 7525 | 20240302 | 143 | 20240303 | 925 | 2394267 | 1902 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 1902 | 37.07 | -122.0158 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036805 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1921820 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 389907 | 20240302 | 143 | 20240302 | 1229 | 2394529 | 646 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 10336 | 36.9796 | -122.0377 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036729 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1921762 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 68191 | 20240302 | 144 | 20240302 | 1122 | 2394494 | 578 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 10982 | 36.9816 | -121.9026 | No | Overcast-Drizzle;32-90 F |  |  | 24-0036790 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1921809 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | JUMPER | BURNT OJ C PHASE | 20240302 | 147 | 20240302 | 1100 | 2394675 | 553 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 2212 | 36.916 | -121.4323 | No | Partly Cloudy;32-90 F |  |  | 24-0036814 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1921828 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6641 | 20240302 | 156 | 20240303 | 1139 | 2394328 | 2023 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 65961 | 37.016 | -121.8161 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036798 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1921816 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2107 | 182402107 | TRANSFORMER | 411821150563 | 20240302 | 303 | 20240302 | 1325 | 2394253 | 622 | Distribution Circuit | Vegetation | Tree - grew into line | 14 | 4818 | 36.6896 | -121.7914 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0036683 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1921727 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 5269 | 20240302 | 305 | 20240302 | 653 | 2394264 | 228 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1974 | 36.9894 | -122.0312 | No | Overcast-Drizzle;32-90 F |  |  | 24-0036697 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1921740 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315402219845 | 20240302 | 308 | 20240302 | 1130 | 2394465 | 502 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 6224 | 37.0341 | -122.0764 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0036698 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1921741 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 5819 | 20240302 | 357 | 20240302 | 1922 | 2394566 | 925 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 55500 | 37.0449 | -121.8139 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036848 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1921856 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2108 | 83252108 | TRANSFORMER | 315600117721 | 20240302 | 441 | 20240302 | 1824 | 2394359 | 823 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 9053 | 36.9768 | -122.0063 | No | Overcast-Drizzle;32-90 F | Transformer | Failed/Faulted | 24-0037017 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1921963 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | OTHER | WIRE DOWN | 20240302 | 550 | 20240303 | 439 | 2394414 | 1369 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 17725 | 36.9284 | -121.819 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036734 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | Yes | 1921768 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 6491 | 20240302 | 559 | 20240302 | 1201 | 2394392 | 362 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 7964 | 36.9325 | -121.7435 | No | Overcast-Drizzle;32-90 F |  |  | 24-0036900 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1921888 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 7605 | 20240302 | 608 | 20240302 | 852 | 2394424 | 164 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 2624 | 37.0866 | -122.0058 | No | Clear;32-90 F |  |  | 24-0036748 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1921779 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 9051 | 20240302 | 707 | 20240302 | 1446 | 2394467 | 459 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4131 | 36.996 | -121.8957 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036758 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1921786 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | TRANSFORMER | 316297015112 | 20240302 | 815 | 20240303 | 627 | 2394611 | 1332 | Transformer only | Environmental/External | Water | 1 | 1332 | 36.9081 | -121.7673 | No | Overcast;32-90 F | Transformer | Deteriorated | 24-0036780 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1921803 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | SWITCH | 2429 | 20240302 | 957 | 20240302 | 1305 | 2394609 | 188 | Distribution Circuit | Vegetation | Tree - branch fell on line | 49 | 9212 | 37.0068 | -121.8562 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0036778 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1921802 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 5269 | 20240302 | 1058 | 20240302 | 1152 | 2394751 | 54 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 1404 | 36.9894 | -122.0312 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0036878 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1921874 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | OTHER | WIRE DWN 7701 | 20240302 | 1102 | 20240303 | 12 | 2394876 | 790 | Distribution Circuit | Vegetation | Tree - fell into line | 299 | 57816 | 36.9914 | -121.97 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036888 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | Yes | Yes | 1921882 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 5957 | 20240302 | 1109 | 20240302 | 1244 | 2394777 | 95 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 1900 | 37.0051 | -121.9393 | No | Overcast-Drizzle;32-90 F |  |  | 24-0036907 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1921893 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 934561 | 20240302 | 1405 | 20240303 | 740 | 2395039 | 1055 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 26375 | 37.012 | -121.8249 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0037033 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1921977 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 5269 | 20240302 | 1447 | 20240302 | 1515 | 2395105 | 28 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 728 | 36.9894 | -122.0312 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Together | 24-0036962 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1921927 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2108 | 83252108 | TRANSFORMER | 315600517708 | 20240302 | 1724 | 20240302 | 1944 | 2395420 | 140 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 140 | 36.9764 | -122.0062 | No | Overcast-Drizzle;32-90 F | Transformer | Deteriorated | 24-0037019 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1921966 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 10714 | 20240302 | 1753 | 20240303 | 1920 | 2395469 | 1527 | Distribution Circuit | Vegetation | Tree - fell into line | 422 | 235538 | 36.9779 | -121.8666 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0037030 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1921975 | 0 | EPSS Ckt | N | 2024 | ABC
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | JUMPER | OJ @ 3741 CORNER | 20240302 | 1753 | 20240303 | 1105 | 2395556 | 1032 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 28896 | 36.947 | -121.8531 | No | Partly Cloudy-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0037050 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1921991 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 2207 | 20240302 | 1753 | 20240304 | 1955 | 2395588 | 3002 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 18012 | 36.9517 | -121.8354 | No | Partly Cloudy-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0037058 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1921998 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | SOQUEL-0402 | 83300402 | TRANSFORMER | 315771317543 | 20240302 | 2058 | 20240302 | 2250 | 2395607 | 112 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 112 | 36.9727 | -121.9484 | No | Overcast-Drizzle;32-90 F | Fuse | Burned Open | 24-0037083 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1922026 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2105 | 182402105 | TRANSFORMER | 411736048851 | 20240302 | 2145 | 20240303 | 1257 | 2395639 | 912 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 5472 | 36.6422 | -121.8179 | No | Overcast;32-90 F | Transformer | Burned/flashed | 24-0037089 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1922032 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 8983 | 20240303 | 18 | 20240303 | 1006 | 2395670 | 588 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 28812 | 37.0307 | -122.1429 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0037174 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1922102 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 11797 | 20240303 | 722 | 20240303 | 820 | 2395832 | 58 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 290 | 36.8677 | -121.7087 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0037142 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1922074 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412265354829 | 20240303 | 729 | 20240303 | 1652 | 2395781 | 563 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1689 | 36.8105 | -121.6437 | No | Clear;32-90 F | Bushing | Failed/Faulted | 24-0037150 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1922081 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2103 | 83252103 | FUSE | 96853 | 20240303 | 747 | 20240303 | 909 | 2395801 | 82 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 49 | 4018 | 36.972 | -122.0217 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0037153 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1922083 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 6667 | 20240303 | 814 | 20240303 | 1100 | 2395823 | 166 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 996 | 36.9464 | -121.8211 | No | Overcast-Fog;32-90 F |  |  | 24-0037183 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1922113 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | TRANSFORMER | 316297015112 | 20240303 | 956 | 20240303 | 1618 | 2395854 | 382 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 382 | 36.9081 | -121.7673 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0037178 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1922107 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 12760 | 20240303 | 1028 | 20240303 | 1510 | 2395995 | 282 | Distribution Circuit | Company Initiated | Return Circuit Normal | 850 | 97360 | 37.0674 | -121.9966 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036888 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1922108 | 0 | EPSS Ckt | N | 2024 | A & B
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 3347 | 20240303 | 1117 | 20240303 | 1230 | 2396057 | 73 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 2482 | 36.8707 | -121.6898 | No | Clear;32-90 F |  |  | 24-0037200 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1922126 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 8983 | 20240303 | 1148 | 20240303 | 1305 | 2396085 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 2517 | 37.0307 | -122.1429 | No | Clear;32-90 F |  |  | 24-0037213 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1922134 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | TRANSFORMER | 316295114675 | 20240303 | 1157 | 20240303 | 1449 | 2396018 | 172 | Transformer only | Equipment Failure/Involved | Electrical Overload | 3 | 516 | 36.8961 | -121.768 | No | Rain-Overcast;32-90 F | Transformer | Deteriorated | 24-0037195 | OH | Sus | 35534491 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1922122 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 1013 | 20240303 | 1508 | 20240303 | 1742 | 2396182 | 154 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 5082 | 36.8382 | -121.7843 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 24-0037226 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | Yes | 1922144 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | SWITCH | 533841 | 20240303 | 1621 | 20240303 | 1702 | 2396255 | 41 | Distribution Circuit | Company Initiated | Return Circuit Normal | 21 | 861 | 36.9995 | -121.9703 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0036888 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1922155 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316666912702 | 20240303 | 1754 | 20240304 | 1630 | 2396292 | 1356 | Transformer only | Vegetation | Tree - fell into line | 2 | 2712 | 36.8436 | -121.6401 | No | Clear;32-90 F | Pole-Wood | On Ground | 24-0037271 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1922178 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 24463 | 20240303 | 1827 | 20240304 | 311 | 2396301 | 524 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 3144 | 36.7977 | -121.6995 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0037276 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1922182 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 10361 | 20240303 | 1925 | 20240303 | 2059 | 2396331 | 94 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 752 | 36.9494 | -121.8272 | No | Partly Cloudy-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 24-0037278 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1922184 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DEL MONTE-2104 | 182222104 | FUSE | 56001 | 20240303 | 2209 | 20240304 | 318 | 2396387 | 309 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 3704 | 36.5535 | -121.7434 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0037340 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1922240 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 12401 | 20240304 | 730 | 20240304 | 1304 | 2396480 | 334 | Distribution Circuit | Equipment Failure/Involved | Overhead | 107 | 35738 | 36.9726 | -121.765 | No | Overcast-Fog;32-90 F | Connector or Splice (OH) | Broken- wire on object | 24-0037422 | OH | Sus | 46202547 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | Yes | 1922262 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 1997 | 20240304 | 829 | 20240304 | 2329 | 2396554 | 894 | Distribution Circuit | Environmental/External | Flood/Erosion | 10 | 8940 | 36.9795 | -121.75 | No | Overcast;32-90 F | Pole-Wood | Normal | 24-0037413 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1922260 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | TRANSFORMER | T1335 | 20240304 | 1058 | 20240305 | 242 | 2396724 | 944 | Distribution Circuit | Equipment Failure/Involved | Underground | 186 | 10429 | 36.6227 | -121.9199 | No | Overcast;32-90 F | Transformer (UG) | Broken | 24-0037597 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1922316 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | TRANSFORMER | 411491947272 | 20240304 | 1118 | 20240304 | 1419 | 2396744 | 181 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 2896 | 36.5963 | -121.9003 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Arcing | 24-0037655 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1922336 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | TRANSFORMER | 315917217294 | 20240304 | 1130 | 20240304 | 1148 | 2396729 | 18 | Transformer only | Equipment Failure/Involved | Underground | 8 | 144 | 36.9665 | -121.8984 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0037514 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1922299 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 12399 | 20240304 | 1143 | 20240304 | 1305 | 2396769 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 82 | 36.9413 | -121.7405 | No | Partly Cloudy;32-90 F |  |  | 24-0037619 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1922322 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2103 | 83252103 | RECLOSER | 12075 | 20240304 | 1555 | 20240304 | 1713 | 2396993 | 78 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2887 | 105429 | 36.9736 | -122.0175 | No | Overcast;32-90 F |  |  | 24-0037725 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | No | No | 1922349 | 0 | EPSS Ckt | N | 2024 | A- B- C- & GD
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 16000 | 20240305 | 656 | 20240305 | 756 | 2397325 | 60 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3255 | 52102 | 37.0464 | -122.0243 | No | Overcast;32-90 F |  |  | 24-0037934 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1922483 | 0 | EPSS Ckt | N | 2024 | B & C
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 9143 | 20240305 | 722 | 20240305 | 932 | 2397337 | 130 | Distribution Circuit | Animal | Bird found | 38 | 4892 | 36.6196 | -121.9082 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 24-0038024 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1922564 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 412084949439 | 20240305 | 931 | 20240305 | 1448 | 2397524 | 317 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 317 | 36.6605 | -121.6998 | No | Clear;32-90 F |  |  | 24-0038192 | OH | Sus | 46203292 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1922617 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | JUMPER | OJS 2 SPANS SSD OF CGC 412130145448 | 20240305 | 949 | 20240305 | 1256 | 2397542 | 187 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 561 | 36.5519 | -121.6801 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0038042 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1922573 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | OCB | 2102/2 | 20240305 | 1037 | 20240305 | 1334 | 2397594 | 177 | Distribution Circuit | Equipment Failure/Involved | Overhead | 233 | 17309 | 36.2938 | -121.1999 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0038079 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | Yes | No | 1922589 | 0 | EPSS Ckt | N | 2024 | AB GRD & TIME OC
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 3541 | 20240305 | 1244 | 20240305 | 1810 | 2397580 | 326 | Distribution Circuit | Vegetation | Tree - grew into line | 27 | 8802 | 36.8789 | -121.6911 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0038187 | OH | Sus | 46203380 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1922616 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | SOQUEL-0402 | 83300402 | TRANSFORMER | 100000159433 | 20240305 | 1248 | 20240305 | 1512 | 2397751 | 144 | Transformer only | Vegetation | Tree - branch fell on line | 5 | 720 | 36.9777 | -121.9557 | No | Overcast;32-90 F | Transformer | Normal | 24-0038286 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1922635 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | BUENA VISTA-1106 | 182261106 | TRANSFORMER | 412337448432 | 20240305 | 1349 | 20240305 | 1652 | 2397765 | 183 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 183 | 36.6357 | -121.6127 | No | Partly Cloudy;32-90 F | Transformer | Burned Open | 24-0038255 | OH | Sus | 31685768 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1922629 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | JUMPER | OJS HIGH SIDE OF 7877 FUCO | 20240305 | 1733 | 20240305 | 1952 | 2397952 | 139 | Distribution Circuit | Equipment Failure/Involved | Overhead | 49 | 6811 | 36.9265 | -121.7588 | No | Overcast;32-90 F | Crossarm- Wood | Deteriorated | 24-0038280 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1922662 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | TRANSFORMER | 412219152606 | 20240305 | 2017 | 20240306 | 310 | 2398028 | 413 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 826 | 36.7486 | -121.6574 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0038447 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1922718 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | RECLOSER | 5020 | 20240306 | 243 | 20240306 | 1148 | 2398088 | 527 | Distribution Circuit | Vegetation | Tree - fell into line | 385 | 91854 | 37.1024 | -121.9847 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0038520 | OH | Sus | 46203820 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1922769 | 0 | EPSS Ckt | N | 2024 | B & C
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 10199 | 20240306 | 504 | 20240306 | 1440 | 2398106 | 576 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 2584 | 36.9669 | -121.8828 | No | Overcast-Fog;32-90 F | Transformer (OH) | Burned/flashed | 24-0038568 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1922811 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 709 | 20240306 | 644 | 20240306 | 845 | 2398271 | 121 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 242 | 37.0515 | -122.1609 | No | Clear;32-90 F |  |  | 24-0038596 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1922855 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 12017 | 20240306 | 937 | 20240306 | 1040 | 2398449 | 63 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 189 | 36.9339 | -121.702 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0038696 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1922931 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412194554809 | 20240306 | 1139 | 20240306 | 1729 | 2398488 | 350 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 350 | 36.8096 | -121.6682 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0038739 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1922940 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2101 | 182492101 | FUSE | 50501 | 20240306 | 1342 | 20240306 | 1429 | 2398590 | 47 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 159 | 7473 | 36.8354 | -121.4205 | No | Partly Cloudy-Drizzle;32-90 F |  |  | 24-0038829 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1922957 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 7685 | 20240306 | 2024 | 20240307 | 437 | 2398846 | 493 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2465 | 36.9826 | -121.8177 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 24-0039012 | OH | Sus | 31685873 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1923051 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | JUMPER | OJ @ 535 TWIN LANE | 20240306 | 2148 | 20240306 | 2320 | 2398860 | 92 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 92 | 37.0554 | -121.9517 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0039008 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1923049 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 5825 | 20240306 | 2236 | 20240307 | 357 | 2398876 | 321 | Distribution Circuit | Vegetation | Tree - branch fell on line | 72 | 23112 | 37.0127 | -121.7935 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0039021 | OH | Sus | 46204057 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1923057 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | LLAGAS-2106 | 83182106 | JUMPER | 2 SPANS SOURCE SIDE 4239 | 20240307 | 826 | 20240307 | 1338 | 2399042 | 312 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 936 | 36.9637 | -121.4923 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken | 24-0039099 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1923118 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 1009 | 20240307 | 954 | 20240307 | 1348 | 2399471 | 234 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 1 | 234 | 36.9892 | -121.8643 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0039414 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1923301 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | FUSE | 43533 | 20240307 | 1046 | 20240307 | 1154 | 2399371 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 136 | 36.7285 | -121.595 | No | Overcast;32-90 F |  |  | 24-0039271 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1923268 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 51053 | 20240307 | 1340 | 20240307 | 1515 | 2399441 | 95 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 285 | 36.6195 | -121.2226 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0039360 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1923293 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRIP-SAVER | 6577 | 20240307 | 1607 | 20240307 | 1747 | 2399556 | 100 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 49 | 4900 | 37.0487 | -121.8085 | No | Clear;32-90 F |  |  | 24-0039527 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1923321 | 0 | EPSS Ckt | N | 2024 | NA
CENTRAL COAST | HOLLISTER | HOLLISTER-2101 | 182492101 | TRANSFORMER | 412929255482 | 20240307 | 1651 | 20240307 | 2216 | 2399584 | 325 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 650 | 36.8328 | -121.4175 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0039512 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1923318 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | JUMPER | DDE 4 S/O CGC 413698135647 | 20240307 | 1824 | 20240307 | 2250 | 2399624 | 266 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 266 | 36.2907 | -121.1398 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0039531 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1923323 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | FUSE | 4775 | 20240308 | 34 | 20240308 | 1235 | 2399743 | 721 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 27778 | 36.9768 | -121.9217 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0039599 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1923388 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 7987 | 20240308 | 606 | 20240308 | 748 | 2399784 | 102 | Distribution Circuit | Vegetation | Tree - branch fell on line | 44 | 4488 | 36.8458 | -121.6363 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0039639 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1923409 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316400015610 | 20240308 | 610 | 20240308 | 1332 | 2400109 | 442 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 442 | 36.922 | -121.7322 | No | Fog;32-90 F | Transformer (OH) | Broken | 24-0039750 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1923555 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | TRANSFORMER | T0836 | 20240308 | 610 | 20240308 | 1037 | 2399787 | 267 | Transformer only | Equipment Failure/Involved | Overhead | 41 | 10947 | 36.9197 | -121.7353 | No | Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0039611 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1923399 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 4953 | 20240308 | 1829 | 20240309 | 245 | 2400451 | 496 | Distribution Circuit | Equipment Failure/Involved | Overhead | 170 | 61004 | 36.8253 | -121.6618 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0040011 | OH | Sus | 46205657 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | Yes | 1923628 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 412019655789 | 20240309 | 519 | 20240309 | 1718 | 2400543 | 719 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 2157 | 36.8337 | -121.7286 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0040076 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1923732 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 24901 | 20240309 | 718 | 20240309 | 835 | 2400593 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 1540 | 36.7976 | -121.7324 | No | Clear;32-90 F |  |  | 24-0040067 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1923717 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1102 | 182201102 | TRANSFORMER | T200180 | 20240309 | 720 | 20240309 | 1615 | 2400594 | 535 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 1070 | 36.6233 | -121.5531 | No | Overcast;32-90 F | Bus | Failed/Faulted | 24-0040085 | UG | Sus | 31686060 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1923746 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1102 | 182011102 | TRANSFORMER | 412344850349 | 20240309 | 1603 | 20240310 | 18 | 2400918 | 495 | Transformer only | Equipment Failure/Involved | Overhead | 77 | 38115 | 36.6879 | -121.6122 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0040128 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1923789 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | TRANSFORMER | 411420546860 | 20240309 | 2005 | 20240309 | 2011 | 2400970 | 6 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 12 | 36.5843 | -121.924 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0040162 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1923816 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 7883 | 20240309 | 2250 | 20240310 | 1220 | 2401073 | 810 | Distribution Circuit | Equipment Failure/Involved | Overhead | 56 | 45360 | 36.9237 | -121.7527 | No | Overcast;32-90 F | Crossarm- Wood | Burned/flashed | 24-0040176 | OH | Sus | 31686105 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1923834 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | TRANSFORMER | 314989619772 | 20240310 | 39 | 20240310 | 524 | 2401031 | 285 | Transformer only | Environmental/External | Flood/Erosion | 2 | 570 | 37.0306 | -122.2175 | No | Partly Cloudy;32-90 F | Other | Failed/Faulted | 24-0040168 | OH | Sus | 35536441 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1923826 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | TRANSFORMER | 315521417165 | 20240310 | 2049 | 20240311 | 1027 | 2401312 | 818 | Transformer only | Equipment Failure/Involved | Electrical Overload | 9 | 7362 | 36.9613 | -122.0339 | No | Overcast;32-90 F | Transformer | Arcing | 24-0040236 | OH | Sus | 31686182 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1923902 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | TRANSFORMER | 411406448082 | 20240311 | 3 | 20240311 | 306 | 2401335 | 183 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 2196 | 36.6178 | -121.9304 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 24-0040238 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1923903 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 4321 | 20240311 | 132 | 20240311 | 315 | 2401344 | 103 | Distribution Circuit | Animal | Other | 3 | 274 | 36.7647 | -121.2994 | No | Clear;32-90 F | Fuse | Normal | 24-0040245 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1923909 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411892852574 | 20240311 | 811 | 20240311 | 1335 | 2401417 | 324 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 324 | 36.7454 | -121.7685 | No | Overcast;32-90 F | Transformer | Broken | 24-0040329 | OH | Sus | 46209511 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1923997 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 3877 | 20240311 | 916 | 20240311 | 1906 | 2401560 | 590 | Distribution Circuit | 3rd Party | Vehicle | 112 | 52412 | 36.8654 | -121.7351 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0040424 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1924097 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 976963 | 20240311 | 943 | 20240311 | 1550 | 2401617 | 367 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 367 | 36.9269 | -121.3896 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 24-0040365 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1924067 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411943253756 | 20240311 | 954 | 20240311 | 1843 | 2401623 | 529 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 529 | 36.7782 | -121.7525 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0040518 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1924125 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | FUSE | 72277 | 20240311 | 1004 | 20240311 | 1350 | 2401639 | 226 | Distribution Circuit | 3rd Party | Metallic Balloon | 4 | 904 | 36.6934 | -121.5699 | No | Overcast;32-90 F | Conductor- Overhead | Annealed | 24-0040522 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1924129 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 6071 | 20240311 | 1043 | 20240311 | 1433 | 2401671 | 230 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 9 | 1991 | 36.9757 | -121.8899 | No | Partly Cloudy;32-90 F |  |  | 24-0040584 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1924146 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | RECLOSER | 3034 | 20240311 | 1251 | 20240311 | 1821 | 2401781 | 330 | Distribution Circuit | Equipment Failure/Involved | Overhead | 542 | 36347 | 36.7317 | -121.6129 | No | Overcast;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0040516 | OH | Sus | 46210452 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1924124 | 0 | EPSS Ckt | N | 2024 | SGF
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | SWITCH | 12899 | 20240311 | 1346 | 20240311 | 1856 | 2401660 | 310 | Distribution Circuit | Vegetation | Tree - grew into line | 71 | 22010 | 37.0536 | -121.9394 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0040548 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1924139 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 10361 | 20240311 | 1510 | 20240311 | 1641 | 2401948 | 91 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 728 | 36.9494 | -121.8272 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0040642 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1924161 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 23291 | 20240311 | 1545 | 20240311 | 1853 | 2401815 | 188 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 188 | 36.7248 | -121.7849 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 24-0040616 | OH | Sus | 46210704 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1924154 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 39126 | 20240311 | 1613 | 20240311 | 1637 | 2402020 | 24 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 383 | 9192 | 37.0778 | -122.1322 | No | Overcast;32-90 F |  |  | 24-0003788 | OH | Sus | 46013271 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | No | No | 1924156 | 0 | EPSS Ckt | N | 2024 | ABC
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6603 | 20240311 | 1910 | 20240311 | 1926 | 2402158 | 16 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 176 | 36.9534 | -121.7243 | No | Overcast;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0040679 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1924180 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1101 | 182201101 | TRANSFORMER | 412543046070 | 20240312 | 915 | 20240312 | 1006 | 2402556 | 51 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 51 | 36.5715 | -121.5412 | No | Clear;32-90 F | Fuse | Broken | 24-0040886 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1924371 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 412054849515 | 20240312 | 1117 | 20240312 | 1415 | 2402626 | 178 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 178 | 36.6625 | -121.7111 | No | Clear;32-90 F | Transformer | Broken | 24-0040960 | OH | Sus | 46210908 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1924389 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1101 | 182201101 | TRANSFORMER | 412705246316 | 20240312 | 1142 | 20240312 | 1915 | 2402703 | 453 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 906 | 36.5799 | -121.485 | No | Overcast;32-90 F | Transformer (OH) | Leaking | 24-0040985 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1924399 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 5273 | 20240313 | 1250 | 20240313 | 1427 | 2403574 | 95 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 32 | 3040 | 36.8291 | -121.6761 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0041598 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1924735 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS COCHES-1101 | 182151101 | TRANSFORMER | 7773 | 20240313 | 1348 | 20240313 | 1815 | 2403567 | 267 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 501 | 36.3598 | -121.2955 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0041587 | OH | Sus | 31686272 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1924731 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | JUMPER | OJ 2 SS OF CGC # 316594613966 | 20240313 | 1530 | 20240313 | 1703 | 2403730 | 93 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 186 | 36.877 | -121.6655 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0041643 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1924745 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 11939 | 20240313 | 1722 | 20240313 | 1832 | 2403828 | 70 | Distribution Circuit | Vegetation | Tree - branch fell on line | 71 | 4970 | 37.0106 | -122.0442 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0041727 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1924775 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | RECLOSER | 75558 | 20240313 | 2056 | 20240314 | 1225 | 2403919 | 929 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 929 | 36.6795 | -121.7079 | No | Clear;32-90 F | Jumper | Arcing | 24-0041747 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1924791 | 0 | Non-EPSS | N | 2024 | N/A
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 10103 | 20240313 | 2308 | 20240314 | 1522 | 2404155 | 974 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1948 | 37.1127 | -122.1513 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0041871 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1924877 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 7799 | 20240314 | 206 | 20240314 | 950 | 2404010 | 464 | Distribution Circuit | Vegetation | Tree - branch fell on line | 61 | 28304 | 37.091 | -122.1396 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0041806 | OH | Sus | 31686485 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1924836 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 2517 | 20240314 | 217 | 20240314 | 908 | 2404014 | 411 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 1644 | 37.1361 | -122.0272 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0041919 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1924964 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 8515 | 20240314 | 332 | 20240314 | 1313 | 2404021 | 581 | Distribution Circuit | Equipment Failure/Involved | Overhead | 107 | 62167 | 37.0483 | -122.1607 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0041936 | OH | Sus | 46211538 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1925002 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 39126 | 20240314 | 401 | 20240314 | 517 | 2404081 | 76 | Distribution Circuit | Vegetation | Tree - branch fell on line | 383 | 29108 | 37.0778 | -122.1322 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0041802 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1924832 | 0 | EPSS Ckt | N | 2024 | A B
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 5020 | 20240314 | 508 | 20240314 | 2310 | 2404101 | 1082 | Distribution Circuit | Vegetation | Tree - fell into line | 385 | 115848 | 37.1024 | -121.9847 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0041808 | OH | Sus | 46211566 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | No | No | 1924838 | 0 | EPSS Ckt | N | 2024 | A B & C PHSE
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 374097 | 20240314 | 513 | 20240314 | 1533 | 2404110 | 620 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 49600 | 36.9777 | -121.9026 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0041849 | OH | Sus | 46211620 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1924861 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 621 | 20240314 | 703 | 20240314 | 854 | 2404162 | 111 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 151 | 16761 | 36.5298 | -121.8305 | No | Clear;32-90 F |  |  | 24-0041899 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1924930 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | OTHER | WIRE DOWN 4 LD SIDE OF CGC# 315563723460 | 20240314 | 905 | 20240314 | 2021 | 2404857 | 676 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 12721 | 37.1353 | -122.0237 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0042058 | OH | Sus | 31686558 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1925086 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 2191 | 20240314 | 1031 | 20240314 | 1429 | 2404769 | 238 | Distribution Circuit | Vegetation | Tree - branch fell on line | 56 | 13328 | 37.0515 | -122.0216 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0042260 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1925183 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | TRANSFORMER | 315521317822 | 20240314 | 1041 | 20240314 | 1152 | 2404792 | 71 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 1207 | 36.9787 | -122.0329 | No | Clear;32-90 F | Secondary | Broken | 24-0042022 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1925068 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | JUMPER | UN # SBCO SS OF CGC#315219821719 | 20240314 | 1243 | 20240314 | 2219 | 2404116 | 576 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 6336 | 37.0851 | -122.1392 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0042228 | OH | Sus | 31686641 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1925174 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | TRANSFORMER | 315643517088 | 20240314 | 1258 | 20240314 | 1319 | 2405166 | 21 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 252 | 36.9597 | -121.9921 | No | Clear;32-90 F | Secondary | Broken | 24-0042186 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1925156 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | RECLOSER | 9118 | 20240314 | 1414 | 20240314 | 1439 | 2405223 | 25 | Distribution Circuit | Equipment Failure/Involved | Overhead | 186 | 4650 | 36.6037 | -121.9359 | No | Clear;32-90 F | Cutout- fuse holder | Arcing | 24-0042249 | OH | Sus | 31686660 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1925180 | 0 | EPSS Ckt | N | 2024 | NONE
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 24947 | 20240314 | 1428 | 20240316 | 2337 | 2405278 | 1098 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1752 | 36.7394 | -121.7236 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0042387 | OH | Sus | 31686821 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1925217 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRANSFORMER | 315468522228 | 20240314 | 1545 | 20240314 | 1658 | 2405354 | 73 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 73 | 37.0999 | -122.0549 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0042343 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1925204 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315683621000 | 20240314 | 1746 | 20240314 | 1911 | 2405447 | 85 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 255 | 37.0675 | -121.9805 | No | Clear;32-90 F |  |  | 24-0042436 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1925250 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | TRANSFORMER | 315948717426 | 20240314 | 2156 | 20240315 | 223 | 2405548 | 267 | Transformer only | Vegetation | Tree - grew into line | 9 | 2403 | 36.9702 | -121.8878 | No | Clear;32-90 F | Secondary | Normal | 24-0042469 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1925264 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 6687 | 20240315 | 26 | 20240315 | 735 | 2405609 | 429 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 3003 | 36.888 | -121.8045 | No | Clear;32-90 F |  |  | 24-0042571 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1925351 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 8125 | 20240315 | 205 | 20240315 | 633 | 2405650 | 268 | Distribution Circuit | Vegetation | Tree - grew into line | 21 | 5628 | 37.099 | -122.1424 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0042517 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1925309 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 7299 | 20240315 | 456 | 20240315 | 1216 | 2405666 | 440 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 5720 | 37.0308 | -122.0939 | No | Clear;32-90 F |  |  | 24-0042763 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1925551 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | FUSE | 3345 | 20240315 | 539 | 20240315 | 826 | 2405675 | 167 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 2339 | 36.721 | -121.6205 | No | Clear;32-90 F |  |  | 24-0042603 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1925387 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 5901 | 20240315 | 547 | 20240315 | 911 | 2405691 | 204 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 3264 | 37.0944 | -121.9716 | No | Clear;32-90 F |  |  | 24-0042645 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1925488 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 35874 | 20240315 | 624 | 20240315 | 810 | 2405701 | 106 | Distribution Circuit | Vegetation | Tree - branch fell on line | 671 | 62404 | 37.0312 | -122.1882 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0042535 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1925329 | 0 | EPSS Ckt | N | 2024 | B-C
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | TRIP-SAVER | 5401 | 20240315 | 715 | 20240315 | 936 | 2405755 | 141 | Distribution Circuit | Vegetation | Tree - branch fell on line | 69 | 9099 | 37.0647 | -122.1232 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0042631 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1925458 | 0 | EPSS Ckt | N | 2024 | N/A
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 8511 | 20240315 | 858 | 20240315 | 1320 | 2405971 | 262 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 3668 | 37.0617 | -122.1474 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0042817 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1925579 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | TRES PINOS-1111 | 183221111 | TRANSFORMER | 413064654577 | 20240315 | 900 | 20240315 | 1240 | 2405878 | 220 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 660 | 36.8088 | -121.3699 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0042593 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1925379 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 12533 | 20240315 | 919 | 20240315 | 1005 | 2406041 | 46 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 1150 | 36.9135 | -121.7702 | No | Clear;32-90 F |  |  | 24-0043000 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1925644 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1102 | 182201102 | FUSE | 163697 | 20240315 | 1250 | 20240315 | 1538 | 2406579 | 168 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 168 | 36.6167 | -121.5608 | No | Clear;32-90 F |  |  | 24-0042941 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1925621 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1103 | 182011103 | TRANSFORMER | 412217251089 | 20240315 | 1357 | 20240315 | 1825 | 2406643 | 268 | Transformer only | Equipment Failure/Involved | Overhead | 25 | 6700 | 36.707 | -121.6567 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0042866 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1925599 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 8125 | 20240315 | 1435 | 20240315 | 2013 | 2406687 | 338 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 7098 | 37.099 | -122.1424 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0042890 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1925606 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | TRANSFORMER | 412910042477 | 20240315 | 1518 | 20240315 | 1630 | 2406753 | 72 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 72 | 36.4756 | -121.4131 | No | Clear;32-90 F |  |  | 24-0042973 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1925633 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | SWITCH | 10969 | 20240315 | 1612 | 20240315 | 1637 | 2406798 | 25 | Distribution Circuit | Vegetation | Tree - branch fell on line | 100 | 2500 | 37.1064 | -122.0572 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0042966 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1925630 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | 83500401 | 83500401 | FUSE | 6005 | 20240315 | 1649 | 20240315 | 2121 | 2406821 | 272 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 5440 | 36.9959 | -121.9233 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0043003 | OH | Sus | 31686596 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1925647 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | TRANSFORMER | 411491947272 | 20240316 | 1008 | 20240316 | 2047 | 2407184 | 639 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 10224 | 36.5963 | -121.9003 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0043138 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1925806 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | RECLOSER | 36920 | 20240316 | 1750 | 20240317 | 748 | 2407468 | 838 | Distribution Circuit | Equipment Failure/Involved | Overhead | 104 | 60827 | 36.7833 | -121.6326 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0043171 | OH | Sus | 35538107 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | No | No | 1925834 | 0 | EPSS Ckt | N | 2024 | A B C
CENTRAL COAST | SALINAS | SALINAS-1103 | 182011103 | TRANSFORMER | 412219450985 | 20240316 | 1929 | 20240316 | 1937 | 2407501 | 8 | Transformer only | Equipment Failure/Involved | Overhead | 19 | 152 | 36.7042 | -121.6558 | No | Clear;32-90 F | Secondary | Annealed | 24-0043181 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1925843 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2108 | 83252108 | OCB | 2108/2 | 20240316 | 2307 | 20240317 | 1958 | 2407558 | 1251 | Distribution Circuit | 3rd Party | Vehicle | 6476 | 390902 | 36.9926 | -121.982 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0043208 | OH | Sus | 35538060 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1925871 | 0 | EPSS Ckt | N | 2024 | A C PHSE
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | TRANSFORMER | 315760818855 | 20240316 | 2324 | 20240317 | 938 | 2407568 | 614 | Transformer only | Environmental/External | Water | 3 | 1842 | 37.0084 | -121.9511 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0043231 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1925910 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | TRANSFORMER | 316450213606 | 20240316 | 2333 | 20240317 | 1307 | 2407573 | 814 | Transformer only | Unknown Cause | Patrol - not conducted | 2 | 1628 | 36.8677 | -121.7144 | No | Clear;32-90 F |  |  | 24-0043221 | OH | Sus | 35538106 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1925889 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | RECLOSER | 36920 | 20240317 | 656 | 20240317 | 702 | 2407629 | 6 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 234 | 36.7833 | -121.6326 | No | Clear;32-90 F |  |  | 24-0043171 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1925892 | 0 | EPSS Ckt | N | 2024 | B C
CENTRAL COAST | MONTEREY | LAURELES-1112 | 182371112 | FUSE | 6709 | 20240317 | 837 | 20240317 | 1012 | 2407653 | 95 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 115 | 10925 | 36.4917 | -121.7443 | No | Clear;32-90 F |  |  | 24-0043237 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1925919 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 2469 | 20240317 | 1006 | 20240317 | 1110 | 2407698 | 64 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 2048 | 36.8825 | -121.7078 | No | Clear;32-90 F |  |  | 24-0043242 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1925924 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | RECLOSER | 22428 | 20240317 | 2022 | 20240318 | 320 | 2407868 | 418 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 3762 | 36.7339 | -121.6791 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0043287 | OH | Sus | 31686845 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1925963 | 0 | EPSS Ckt | N | 2024 | N/A
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 615 | 20240318 | 105 | 20240318 | 415 | 2407913 | 190 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1710 | 36.9393 | -121.8056 | No | Fog;32-90 F |  |  | 24-0043363 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1926043 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | RECLOSER | 696967 | 20240318 | 237 | 20240318 | 1612 | 2407923 | 815 | Distribution Circuit | Equipment Failure/Involved | Overhead | 73 | 59495 | 36.3938 | -121.878 | No | Clear;32-90 F | Woodpin | Broken | 24-0043414 | OH | Sus | 46212710 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1926099 | 0 | EPSS Ckt | N | 2024 | NA
CENTRAL COAST | SALINAS | SALINAS-1101 | 182011101 | TRANSFORMER | 412279049910 | 20240318 | 449 | 20240318 | 949 | 2407925 | 300 | Transformer only | Equipment Failure/Involved | Overhead | 54 | 16200 | 36.6752 | -121.6345 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0043365 | OH | Sus | 46212766 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1926045 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | TRANSFORMER | 412376053435 | 20240318 | 720 | 20240318 | 949 | 2407962 | 149 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 298 | 36.7727 | -121.6044 | No | Clear;32-90 F |  |  | 24-0043469 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1926225 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 9641 | 20240318 | 810 | 20240318 | 1123 | 2408004 | 193 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 193 | 36.8761 | -121.7727 | No | Fog;32-90 F |  |  | 24-0043531 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1926265 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2108 | 83252108 | TRANSFORMER | 315586417451 | 20240318 | 838 | 20240318 | 1526 | 2408055 | 408 | Transformer only | Equipment Failure/Involved | Electrical Overload | 9 | 3672 | 36.969 | -122.0105 | No | Clear;32-90 F | Transformer | Leaking | 24-0043434 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1926134 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 709 | 20240318 | 839 | 20240318 | 1215 | 2408058 | 216 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 432 | 37.0515 | -122.1609 | No | Clear;32-90 F |  |  | 24-0043567 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1926292 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | KING CITY-1105 | 182031105 | INTERRUPTER | 466730 | 20240318 | 1148 | 20240318 | 1405 | 2408388 | 137 | Distribution Circuit | 3rd Party | Vehicle | 5 | 685 | 36.2236 | -121.1335 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0043552 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1926275 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | TRANSFORMER | 412773743438 | 20240318 | 1418 | 20240318 | 1534 | 2408029 | 76 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 76 | 36.5011 | -121.459 | No | Clear;32-90 F | Jumper | Burned Open | 24-0043639 | OH | Sus | 46213228 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1926316 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 6033 | 20240318 | 1753 | 20240319 | 808 | 2408730 | 855 | Distribution Circuit | 3rd Party | Vehicle | 82 | 70110 | 37.081 | -122.0049 | No | Clear;32-90 F | Anchor or Guy | Broken | 24-0043777 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1926368 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 16000 | 20240318 | 1912 | 20240319 | 808 | 2408812 | 776 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2785 | 88196 | 37.0464 | -122.0243 | No | Clear;32-90 F |  |  | 24-0043767 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1926362 | 0 | EPSS Ckt | N | 2024 | B & C PHSE
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0421 | 182440421 | TRANSFORMER | 411471048040 | 20240318 | 1953 | 20240318 | 2235 | 2408839 | 162 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 1458 | 36.6172 | -121.9084 | No | Partly Cloudy;32-90 F | Transformer (OH) | Deteriorated | 24-0043784 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1926372 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | TRANSFORMER | 315925717304 | 20240319 | 1008 | 20240319 | 1054 | 2409239 | 46 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 598 | 36.9665 | -121.8946 | No | Partly Cloudy;32-90 F | Secondary | Burned/flashed | 24-0043999 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1926611 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | RECLOSER | BL 1101 | 20240319 | 1254 | 20240319 | 1306 | 2409413 | 12 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 744 | 7776 | 37.0926 | -122.0966 | No | Clear;32-90 F |  |  | 24-0044136 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1926654 | 0 | EPSS Ckt | N | 2024 | A-GRD
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0424 | 182440424 | TRANSFORMER | 411419148320 | 20240319 | 1359 | 20240319 | 1530 | 2409477 | 91 | Transformer only | Unknown Cause | Patrol - found nothing | 56 | 5096 | 36.6251 | -121.9264 | No | Clear;32-90 F |  |  | 24-0044268 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1926682 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1112 | 182371112 | TRANSFORMER | 411973643148 | 20240319 | 1403 | 20240320 | 52 | 2409481 | 649 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1947 | 36.4875 | -121.7315 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0044318 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1926690 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | BUENA VISTA-1106 | 182261106 | TRANSFORMER | 412418947652 | 20240319 | 1424 | 20240319 | 1555 | 2409498 | 91 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 91 | 36.6146 | -121.584 | No | Clear;32-90 F |  |  | 24-0044286 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1926684 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | SAN ARDO-1101 | 182191101 | FUSE | 7099 | 20240319 | 1955 | 20240320 | 554 | 2409712 | 599 | Distribution Circuit | 3rd Party | Vandalism | 11 | 6589 | 36.0566 | -121.0005 | No | Clear;32-90 F | Pole-Wood | On Ground | 24-0044366 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | No | No | 1926712 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | LOS GATOS-1107 | 82021107 | FUSE | 29195 | 20240320 | 920 | 20240320 | 2238 | 2410102 | 798 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 6384 | 37.0763 | -121.9397 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0044575 | OH | Sus | 46214114 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1926937 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 11321 | 20240320 | 1427 | 20240320 | 1927 | 2410392 | 300 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 300 | 37.0277 | -121.8779 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0044721 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1926989 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 4685 | 20240320 | 2003 | 20240320 | 2244 | 2410632 | 161 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 644 | 36.8927 | -121.7352 | No | Clear;32-90 F |  |  | 24-0044950 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1927088 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315450420671 | 20240321 | 830 | 20240321 | 1320 | 2411008 | 290 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 290 | 37.0572 | -122.0601 | No | Clear;32-90 F | Fuse | Burned Open | 24-0045034 | OH | Sus | 46214580 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1927146 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | TRANSFORMER | 412352546793 | 20240321 | 1507 | 20240322 | 1314 | 2411322 | 1327 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 2654 | 36.5901 | -121.6063 | No | Clear;32-90 F |  |  | 24-0045278 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1927232 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1101 | 182201101 | TRANSFORMER | 412740546072 | 20240321 | 1637 | 20240322 | 23 | 2411329 | 466 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 466 | 36.5739 | -121.473 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0045301 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1927240 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | FUSE | 4463 | 20240322 | 643 | 20240322 | 757 | 2411566 | 74 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 1554 | 36.5772 | -121.6292 | No | Clear;32-90 F |  |  | 24-0045422 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1927302 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315638821175 | 20240322 | 1057 | 20240322 | 1421 | 2411902 | 204 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 3264 | 37.072 | -121.9961 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0045638 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1927492 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 5397 | 20240322 | 1443 | 20240322 | 2150 | 2412145 | 427 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 9821 | 37.076 | -122.1429 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0045773 | OH | Sus | 31687671 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1927547 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 9813 | 20240322 | 1544 | 20240322 | 1730 | 2412202 | 106 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 1271 | 36.861 | -121.6873 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0045811 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1927555 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | FUSE | 25527 | 20240322 | 1657 | 20240322 | 2250 | 2412259 | 353 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 1177 | 36.5508 | -121.4737 | No | Partly Cloudy;32-90 F |  |  | 24-0045868 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1927606 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0424 | 182440424 | FUSE | 8005 | 20240322 | 1802 | 20240322 | 1940 | 2412283 | 98 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 113 | 11096 | 36.6253 | -121.9243 | No | Overcast-Rain;32-90 F |  |  | 24-0045830 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1927567 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 4999 | 20240322 | 1922 | 20240322 | 2140 | 2412317 | 138 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 2208 | 36.9914 | -121.9845 | No | Overcast-Rain;32-90 F |  |  | 24-0045842 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1927579 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | FUSE | 4167 | 20240322 | 1932 | 20240322 | 2042 | 2412335 | 70 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 7 | 514 | 36.8626 | -121.5401 | No | Partly Cloudy-Rain;32-90 F |  |  | 24-0045839 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1927576 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 5957 | 20240322 | 2031 | 20240322 | 2318 | 2412385 | 167 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 3340 | 37.0051 | -121.9393 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0045876 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1927613 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 89447 | 20240322 | 2041 | 20240323 | 1300 | 2412538 | 979 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 979 | 36.8343 | -121.6562 | No | Clear;32-90 F |  |  | 24-0045898 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1927634 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 2469 | 20240322 | 2058 | 20240323 | 205 | 2412406 | 307 | Distribution Circuit | Vegetation | Tree - bark fell into line | 32 | 9824 | 36.8825 | -121.7078 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0045889 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1927625 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | JUMPER | WIRE DOWN | 20240322 | 2153 | 20240323 | 1100 | 2412489 | 787 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 5509 | 36.8941 | -121.8157 | No | Partly Cloudy-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0045877 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | Yes | 1927614 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | OTHER | 7235 | 20240323 | 451 | 20240323 | 1443 | 2412579 | 592 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 8880 | 37.1169 | -121.9917 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0045941 | OH | Sus | 46215606 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1927682 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 6543 | 20240323 | 613 | 20240323 | 808 | 2412599 | 115 | Distribution Circuit | Vegetation | Tree - bark fell into line | 26 | 2990 | 36.9267 | -121.8459 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 24-0045930 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1927667 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | FUSE | 9195 | 20240323 | 756 | 20240323 | 916 | 2412642 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 720 | 35.9509 | -121.1175 | No | Clear;32-90 F |  |  | 24-0045944 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1927692 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | FUSE | 8603 | 20240323 | 951 | 20240323 | 1108 | 2412777 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 901 | 69377 | 36.3243 | -121.2327 | No | Partly Cloudy;32-90 F |  |  | 24-0045977 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1927723 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | KING CITY-1105 | 182031105 | JUMPER | 1 PHASE BROKEN MAINLINE @ 75797 | 20240323 | 1120 | 20240323 | 1708 | 2412811 | 348 | Distribution Circuit | Equipment Failure/Involved | Overhead | 205 | 69885 | 36.3361 | -121.2082 | No | Partly Cloudy-Drizzle;32-90 F | Insulator | Broken | 24-0046023 | OH | Sus | 31687710 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1927747 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | TRANSFORMER | 413203657890 | 20240323 | 1229 | 20240323 | 1751 | 2412763 | 322 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 644 | 36.9005 | -121.3262 | No | Partly Cloudy-Drizzle;32-90 F | Secondary | Broken- wire on ground | 24-0046018 | OH | Sus | 31687709 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1927743 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | TRES PINOS-1111 | 183221111 | TRANSFORMER | 413013154442 | 20240323 | 1414 | 20240323 | 1704 | 2412916 | 170 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 340 | 36.8046 | -121.3875 | No | Clear;32-90 F | Transformer | Broken- wire on object | 24-0046060 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1927768 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | FUSE | 75627 | 20240323 | 2058 | 20240324 | 143 | 2412928 | 285 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 325 | 36.5361 | -121.4639 | No | Partly Cloudy-Drizzle;32-90 F | Pole-Wood | Deteriorated | 24-0046104 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1927814 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | FUSE | 8971 | 20240323 | 2247 | 20240324 | 10 | 2413196 | 83 | Distribution Circuit | Vegetation | Tree - branch fell on line | 296 | 21016 | 36.4727 | -121.7254 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0046128 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1927830 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | TRANSFORMER | 412764144712 | 20240324 | 737 | 20240324 | 1017 | 2413283 | 160 | Transformer only | Company Initiated | Operating error | 1 | 160 | 36.5361 | -121.4638 | No | Partly Cloudy-Fog-Rain;32-90 F | Fuse | Normal | 24-0046162 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1927878 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 40321 | 20240324 | 947 | 20240324 | 1124 | 2413343 | 97 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 2522 | 36.6039 | -121.9501 | No | Overcast;32-90 F |  |  | 24-0046173 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1927885 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | RECLOSER | 7086 | 20240324 | 1048 | 20240324 | 1921 | 2413370 | 513 | Distribution Circuit | Equipment Failure/Involved | Overhead | 132 | 38775 | 36.2942 | -121.1997 | No | Partly Cloudy-Rain;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0046166 | OH | Sus | 46215722 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1927881 | 0 | EPSS Ckt | N | 2024 | A GRD
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 2653 | 20240324 | 1053 | 20240325 | 222 | 2413372 | 929 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 7 | 6503 | 36.895 | -121.8145 | No | Overcast-Drizzle;32-90 F |  |  | 24-0046177 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | No | No | 1927888 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 5020 | 20240325 | 24 | 20240325 | 304 | 2413666 | 160 | Distribution Circuit | Vegetation | Tree - fell into line | 294 | 27736 | 37.1024 | -121.9847 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0046278 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1927971 | 0 | EPSS Ckt | N | 2024 | C/GRD
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | FUSE | 9195 | 20240325 | 510 | 20240325 | 850 | 2413729 | 220 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1980 | 35.9509 | -121.1175 | No | Clear;32-90 F |  |  | 24-0046383 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1928091 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | TRANSFORMER | 315206321584 | 20240325 | 844 | 20240325 | 943 | 2413893 | 59 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 59 | 37.0812 | -122.1447 | No | Clear;32-90 F |  |  | 24-0046409 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1928149 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | TRANSFORMER | 412227250096 | 20240325 | 1058 | 20240325 | 2221 | 2414144 | 683 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 4098 | 36.6799 | -121.6521 | No | Overcast;32-90 F | Transformer | Failed/Faulted | 24-0046694 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1928230 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 9811 | 20240325 | 1222 | 20240325 | 1936 | 2414258 | 420 | Distribution Circuit | Vegetation | Tree - fell into line | 164 | 29577 | 36.8591 | -121.6955 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0046544 | OH | Sus | 31687931 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1928196 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | OCB | 2102/2 | 20240325 | 1551 | 20240326 | 246 | 2414421 | 655 | Distribution Circuit | 3rd Party | Vehicle | 752 | 60227 | 36.8629 | -121.4059 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 24-0046642 | OH | Sus | 31687951 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1928217 | 0 | EPSS Ckt | N | 2024 | PH TIM OC GRD TIME OC
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | FUSE | 281488 | 20240326 | 509 | 20240326 | 600 | 2414581 | 51 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 102 | 36.8612 | -121.4349 | No | Partly Cloudy;32-90 F |  |  | 24-0046740 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1928275 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | OTHER | WIRE DOWN | 20240326 | 540 | 20240326 | 1438 | 2414600 | 538 | Distribution Circuit | Vegetation | Tree - fell into line | 220 | 113534 | 36.5575 | -121.9164 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0046743 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | Yes | 1928277 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 12887 | 20240326 | 702 | 20240326 | 1008 | 2414619 | 186 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 48 | 8981 | 37.0385 | -122.0681 | No | Partly Cloudy;32-90 F |  |  | 24-0046840 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1928469 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6311 | 20240326 | 1345 | 20240326 | 1359 | 2415672 | 14 | Distribution Circuit | Vegetation | Tree - grew into line | 1 | 14 | 36.9783 | -121.8668 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0047010 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1928524 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SAN ARDO-1101 | 182191101 | FUSE | 9681 | 20240326 | 1649 | 20240326 | 1656 | 2415888 | 7 | Distribution Circuit | 3rd Party | Customer Equipment | 3 | 21 | 36.0879 | -120.8942 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0047123 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1928547 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | TRANSFORMER | 316338015958 | 20240326 | 1825 | 20240327 | 1159 | 2415774 | 1054 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1054 | 36.9315 | -121.7537 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Burned/flashed | 24-0047138 | OH | Sus | 46216646 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1928557 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1101 | 182201101 | OTHER | WIRE DOWN 1 SP LD SIDE OF 5657 | 20240326 | 1919 | 20240327 | 315 | 2415965 | 471 | Distribution Circuit | Equipment Failure/Involved | Overhead | 731 | 14850 | 36.6169 | -121.5729 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0047159 | OH | Sus | 31687956 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | Yes | 1928574 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 11835 | 20240326 | 2041 | 20240326 | 2133 | 2416035 | 52 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 1404 | 36.9833 | -121.8841 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0047160 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1928575 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | RECLOSER | 5096 | 20240326 | 2231 | 20240327 | 657 | 2416082 | 506 | Distribution Circuit | 3rd Party | Vehicle | 527 | 175418 | 37.0509 | -122.0368 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 24-0047213 | OH | Sus | 35540127 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1928629 | 0 | EPSS Ckt | N | 2024 | A & GRD
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | FUSE | 5557 | 20240327 | 648 | 20240327 | 853 | 2416191 | 125 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 3085 | 36.7876 | -121.5893 | No | Clear;32-90 F |  |  | 24-0047316 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1928733 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411875151854 | 20240327 | 722 | 20240327 | 1526 | 2416204 | 484 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 484 | 36.7263 | -121.7734 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0047368 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1928801 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | TRANSFORMER | 412803243596 | 20240327 | 1505 | 20240327 | 1930 | 2416674 | 265 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 265 | 36.5056 | -121.4504 | No | Overcast;32-90 F | Bushing | Failed/Faulted | 24-0047613 | OH | Sus | 46217051 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1928874 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 3807 | 20240327 | 2053 | 20240328 | 1317 | 2416871 | 984 | Distribution Circuit | Equipment Failure/Involved | Underground | 248 | 66943 | 36.9243 | -121.7723 | No | Overcast-Fog;32-90 F | Conductor- Underground | Deteriorated | 24-0047736 | UG | Sus | 46217077 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1928940 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | OTHER | 7347 | 20240327 | 2309 | 20240328 | 1102 | 2416908 | 713 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 7843 | 37.0409 | -121.9423 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken | 24-0047745 | OH | Sus | 46217079 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1928951 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | JUMPER | OJ'S 2 SPANS NORTH OF CGC# 411436246748 | 20240328 | 851 | 20240328 | 1913 | 2417151 | 622 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 6220 | 36.5823 | -121.919 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0047823 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1929035 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | RECLOSER | 2491 | 20240328 | 1905 | 20240329 | 435 | 2417650 | 570 | Distribution Circuit | Vegetation | Tree - fell into line | 478 | 132185 | 36.583 | -121.8562 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0048171 | OH | Sus | 31689049 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1929212 | 0 | EPSS Ckt | N | 2024 | A- GRD- TIME OC
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8903 | 20240328 | 2002 | 20240328 | 2021 | 2417680 | 19 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 60 | 1139 | 37.0414 | -122.0284 | No | Overcast;32-90 F | Fuse | Normal | 24-0035486 | OH | Sus | 35329368 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1929220 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 2491 | 20240329 | 443 | 20240329 | 451 | 2417777 | 8 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 400 | 36.583 | -121.8562 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0048171 | OH | Sus | 31689049 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1929283 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | RECLOSER | 4724 | 20240329 | 729 | 20240329 | 809 | 2417810 | 40 | Distribution Circuit | 3rd Party | Other | 483 | 19320 | 36.7269 | -121.2708 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0048237 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | No | No | 1929293 | 0 | EPSS Ckt | N | 2024 | A-B-GRD
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | OTHER | WIRE DOWN SS OF CGC#1000001631 | 20240329 | 1004 | 20240329 | 1844 | 2417983 | 520 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2484 | 37.0946 | -122.1464 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0048383 | OH | Sus | 46218227 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1929401 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SOLEDAD-2105 | 182052105 | FUSE | 7601 | 20240329 | 1014 | 20240329 | 1240 | 2417993 | 146 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 486 | 36.4708 | -121.394 | No | Overcast-Rain;32-90 F |  |  | 24-0048408 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1929411 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1101 | 182201101 | TRANSFORMER | 412421447249 | 20240329 | 1049 | 20240329 | 1756 | 2418014 | 427 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 427 | 36.6032 | -121.5827 | No | Overcast;32-90 F | Transformer | Failed/Faulted | 24-0048464 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1929431 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 11865 | 20240329 | 1314 | 20240329 | 1520 | 2418141 | 126 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 73 | 9198 | 37.001 | -121.7398 | No | Overcast-Rain;32-90 F |  |  | 24-0048477 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1929435 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 11103 | 20240329 | 1330 | 20240329 | 1533 | 2418171 | 123 | Distribution Circuit | Vegetation | Tree - bark fell into line | 14 | 1761 | 36.9935 | -122.0701 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0048515 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1929446 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 24425 | 20240329 | 1752 | 20240329 | 2028 | 2418435 | 156 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 2964 | 36.6786 | -121.7229 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0048544 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1929463 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 1751 | 20240329 | 1821 | 20240329 | 1925 | 2418461 | 64 | Distribution Circuit | Vegetation | Tree - bark fell into line | 9 | 576 | 36.8681 | -121.6647 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0048590 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1929475 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | DOLAN ROAD-1101 | 182381101 | FUSE | 2223 | 20240329 | 1947 | 20240330 | 937 | 2418522 | 830 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 5810 | 36.8319 | -121.7798 | No | Overcast;32-90 F |  |  | 24-0048599 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1929482 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | OCB | 2104/2 | 20240329 | 1953 | 20240330 | 1558 | s1929630 | 1097 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2893 | 297680 | 37.0417 | -122.0256 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0048592 | OH | Sus | 35540721 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1929630 | 0 | EPSS Ckt | N | 2024 | A-GRD-INST
CENTRAL COAST | KING CITY | SOLEDAD-2105 | 182052105 | FUSE | 30067 | 20240329 | 2031 | 20240330 | 1622 | 2418558 | 1191 | Distribution Circuit | 3rd Party | Vehicle | 253 | 301323 | 36.4313 | -121.3336 | No | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0048606 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1929490 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 2239 | 20240329 | 2032 | 20240330 | 1114 | 2418557 | 882 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 7608 | 36.9509 | -121.8322 | No | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0048660 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1929540 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412243354318 | 20240330 | 1128 | 20240330 | 1814 | 2419003 | 406 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1624 | 36.7961 | -121.651 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0048791 | OH | Sus | 35540722 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1929614 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | FUSE | 4167 | 20240330 | 1942 | 20240330 | 2100 | 2419251 | 78 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 572 | 36.8626 | -121.5401 | No | Clear;32-90 F |  |  | 24-0048853 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1929667 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | RECLOSER | 10932 | 20240330 | 2009 | 20240331 | 1631 | 2419271 | 1222 | Distribution Circuit | Vegetation | Tree - fell into line | 932 | 399464 | 36.938 | -121.7772 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0048847 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1929660 | 0 | EPSS Ckt | N | 2024 | A- B- C
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | TRANSFORMER | 1687 | 20240330 | 2028 | 20240401 | 1803 | 2420060 | 2735 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 18772 | 36.8937 | -121.833 | No | Overcast-Fog;32-90 F |  |  | 24-0049058 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1929917 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 4321 | 20240331 | 1157 | 20240401 | 42 | 2419516 | 765 | Distribution Circuit | Equipment Failure/Involved | Underground | 8 | 6120 | 36.7647 | -121.2994 | No | Clear;32-90 F | Elbow | Failed/Faulted | 24-0048920 | UG | Sus | 46218563 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1929730 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | PANOCHE-1103 | 253671103 | TRANSFORMER | 414658946875 | 20240331 | 1303 | 20240401 | 258 | 2419536 | 835 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 835 | 36.6068 | -120.8218 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0048944 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1929760 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | FUSE | 4207 | 20240331 | 1411 | 20240401 | 2320 | 2419556 | 1989 | Distribution Circuit | 3rd Party | Metallic Balloon | 7 | 13923 | 36.4665 | -121.4285 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0049451 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1930081 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 211305 | 20240331 | 1611 | 20240401 | 1226 | 2419596 | 1215 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2430 | 37.1986 | -122.1544 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0048964 | OH | Sus | 46218539 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1929782 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | SWITCH | 11099 | 20240331 | 1637 | 20240331 | 1646 | 2419605 | 9 | Distribution Circuit | Company Initiated | Return Circuit Normal | 274 | 2466 | 36.9392 | -121.8054 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0048847 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1929744 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 7681 | 20240331 | 1842 | 20240401 | 945 | 2419704 | 903 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 9030 | 36.5832 | -121.865 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 24-0048946 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1929763 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | FUSE | 5233 | 20240401 | 635 | 20240401 | 931 | 2419821 | 176 | Distribution Circuit | Equipment Failure/Involved | Overhead | 91 | 16016 | 36.5694 | -121.7079 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0049062 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1929922 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 3823 | 20240401 | 644 | 20240401 | 1148 | 2419831 | 304 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 73 | 22192 | 36.9736 | -121.727 | No | Clear;32-90 F |  |  | 24-0049149 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1929972 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 465 | 20240401 | 711 | 20240401 | 2040 | 2419841 | 809 | Distribution Circuit | Environmental/External | Lightning | 2 | 1528 | 36.304 | -121.8762 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0049294 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1930005 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | TRANSFORMER | 412748244199 | 20240401 | 1035 | 20240401 | 1512 | 2420137 | 277 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 277 | 36.5219 | -121.4693 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0049124 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1929963 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 709 | 20240401 | 1159 | 20240402 | 830 | 2420238 | 1231 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 2462 | 37.0515 | -122.1609 | No | Clear;32-90 F |  |  | 24-0049416 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1930040 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | BUENA VISTA-1104 | 182261104 | FUSE | 63907 | 20240401 | 1202 | 20240401 | 1352 | 2420240 | 110 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 660 | 36.6671 | -121.6135 | No | Clear;32-90 F | Anchor or Guy | Broken | 24-0049254 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1929997 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | TRANSFORMER | 411509536727 | 20240401 | 1213 | 20240401 | 2312 | 2420246 | 659 | Transformer only | Environmental/External | Lightning | 1 | 659 | 36.3072 | -121.8837 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0049171 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1929976 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 12122 | 20240401 | 1412 | 20240402 | 559 | 2420329 | 947 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 59661 | 37.0666 | -122.2288 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0049262 | OH | Sus | 46218756 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1930001 | 0 | EPSS Ckt | N | 2024 | N/A
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 23797 | 20240401 | 1430 | 20240402 | 235 | 2420270 | 725 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 725 | 36.762 | -121.7872 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0049289 | UG | Sus | 31689372 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1930004 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | FUSE | 25761 | 20240401 | 1515 | 20240401 | 1912 | 2420372 | 237 | Distribution Circuit | 3rd Party | Customer Equipment | 2 | 474 | 36.5332 | -121.4685 | No | Clear;32-90 F | Other | Burned/flashed | 24-0049410 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1930037 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 5153 | 20240401 | 1820 | 20240401 | 1837 | 2420340 | 17 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 629 | 37.0876 | -122.0887 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0049405 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1930033 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 9497 | 20240402 | 639 | 20240402 | 915 | 2420645 | 156 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 2340 | 37.0296 | -122.0228 | No | Clear;32-90 F |  |  | 24-0049561 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1930228 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | BORONDA-1101 | 182461101 | TRANSFORMER | 412188451629 | 20240402 | 826 | 20240402 | 958 | 2420741 | 92 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 92 | 36.7217 | -121.6672 | No | Clear;32-90 F |  |  | 24-0049604 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | None | 0 | No | No | No | 1930275 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6933 | 20240402 | 1018 | 20240402 | 1200 | 2420941 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 510 | 36.9296 | -121.7331 | No | Clear;32-90 F |  |  | 24-0049646 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1930292 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 7083 | 20240402 | 1714 | 20240403 | 153 | 2421246 | 519 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 32550 | 37.1744 | -122.1449 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0049930 | OH | Sus | 46219639 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | Yes | No | 1930359 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 54959 | 20240403 | 1106 | 20240403 | 2013 | 2421764 | 547 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 547 | 36.7979 | -121.7406 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 24-0050325 | OH | Sus | 31689477 | SOUTH BAY AND CENTRAL COAST | APR | None | 0 | No | No | No | 1930648 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | OTHER | J973 TWD T0587 | 20240403 | 1237 | 20240403 | 1405 | 2421909 | 88 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 176 | 36.5801 | -121.9728 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0050187 | UG | Sus | 47039429 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1930636 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | BUENA VISTA-1106 | 182261106 | TRANSFORMER | 412376547957 | 20240403 | 1454 | 20240403 | 1504 | 2421897 | 10 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 10 | 36.6215 | -121.599 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 24-0050329 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1930649 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 411978354453 | 20240403 | 1828 | 20240404 | 312 | 2422054 | 524 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1572 | 36.7985 | -121.7412 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0050424 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1930677 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2108 | 83252108 | RECLOSER | 467366 | 20240403 | 1852 | 20240403 | 2315 | 2422074 | 263 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3496 | 100280 | 36.9657 | -122.0137 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0050429 | OH | Sus | 46219875 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1930682 | 0 | EPSS Ckt | N | 2024 | A PHASE AND GRD
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | FUSE | 9195 | 20240403 | 2024 | 20240403 | 2302 | 2422125 | 158 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1422 | 35.9509 | -121.1175 | No | Clear;32-90 F |  |  | 24-0050450 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1930701 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | FUSE | 4165 | 20240404 | 812 | 20240404 | 921 | 2422270 | 69 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 240 | 16560 | 36.982 | -121.96 | No | Overcast-Rain;32-90 F |  |  | 24-0050589 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1930813 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 3639 | 20240404 | 1025 | 20240404 | 1737 | 2422415 | 120 | Distribution Circuit | Equipment Failure/Involved | Underground | 54 | 11906 | 36.9312 | -121.789 | No | Partly Cloudy-Heavy Rain;32-90 F | Conductor- Underground | Burned/flashed | 24-0050722 | UG | Sus | 46220386 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1930849 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | TRANSFORMER | 412603144049 | 20240404 | 1125 | 20240404 | 2015 | 2422456 | 530 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 530 | 36.5161 | -121.5176 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0050859 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1930889 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 412034053475 | 20240404 | 1304 | 20240405 | 15 | 2422464 | 671 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 671 | 36.7712 | -121.7211 | No | Partly Cloudy;32-90 F | Transformer (OH) | Burned/flashed | 24-0050790 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1930863 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-1101 | 182221101 | TRANSFORMER | 411719548074 | 20240404 | 1338 | 20240405 | 236 | 2422561 | 778 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 4668 | 36.6198 | -121.8233 | No | Partly Cloudy-Drizzle;32-90 F | Crossarm- Wood | Broken | 24-0050842 | OH | Sus | 31689516 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1930883 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | TRANSFORMER | 413418035095 | 20240404 | 1348 | 20240404 | 2002 | 2422631 | 374 | Transformer only | Vegetation | Tree - fell into line | 1 | 374 | 36.276 | -121.2343 | No | Partly Cloudy-Drizzle;32-90 F | Transformer (OH) | Broken- wire on ground | 24-0050955 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1930906 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-1101 | 182221101 | FUSE | 10171 | 20240404 | 1432 | 20240404 | 1550 | 2422619 | 78 | Distribution Circuit | 3rd Party | Metallic Balloon | 47 | 2889 | 36.606 | -121.8333 | No | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0050923 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1930898 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 3823 | 20240404 | 1922 | 20240404 | 2141 | 2423139 | 139 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 73 | 10147 | 36.9736 | -121.727 | No | Overcast-Rain-Lightning;32-90 F |  |  | 24-0051044 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1930965 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 236923 | 20240404 | 1924 | 20240405 | 755 | 2423142 | 751 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 41 | 31010 | 36.9929 | -121.7354 | No | Overcast-Rain-Lightning;32-90 F |  |  | 24-0051155 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1931068 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | FUSE | 9207 | 20240405 | 630 | 20240405 | 822 | 2423557 | 112 | Distribution Circuit | Animal | Bird found | 164 | 18368 | 36.61 | -121.8979 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Normal | 24-0051182 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1931089 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | FUSE | 5151 | 20240405 | 846 | 20240405 | 2037 | 2423750 | 711 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3555 | 37.111 | -122.0899 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0051343 | OH | Sus | 31689765 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1931239 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | SWITCH | 209531 | 20240405 | 913 | 20240405 | 1257 | 2423863 | 224 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 1792 | 37.0206 | -122.1296 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0051255 | OH | Sus | 46220396 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1931196 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | RECLOSER | 22412 | 20240405 | 916 | 20240405 | 2127 | 2423821 | 731 | Distribution Circuit | Equipment Failure/Involved | Overhead | 127 | 25187 | 36.4699 | -121.4635 | No | Clear;32-90 F | Pothead(Riser Termination) | Failed/Faulted | 24-0051348 | OH | Sus | 31689767 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1931241 | 0 | EPSS Ckt | N | 2024 | C-GRD
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316453117936 | 20240405 | 1045 | 20240405 | 2300 | 2423999 | 735 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 735 | 36.9861 | -121.7173 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0051522 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1931318 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | OTHER | WIRE DOWN HOT 3 LD SIDE OF CGC 316224819668 | 20240405 | 1100 | 20240405 | 1736 | 2424020 | 396 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 396 | 37.0337 | -121.7955 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0051454 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | Yes | 1931278 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 1563 | 20240405 | 1142 | 20240405 | 1438 | 2424072 | 176 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 528 | 37.045 | -122.0754 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0051508 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1931309 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | TRANSFORMER | 412108749353 | 20240405 | 1334 | 20240405 | 2006 | 2424188 | 392 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 784 | 36.6585 | -121.6917 | No | Partly Cloudy-Drizzle;32-90 F | Transformer | Failed/Faulted | 24-0051473 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1931288 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | TRANSFORMER | 412223050179 | 20240405 | 1433 | 20240406 | 408 | 2424269 | 807 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 10491 | 36.6822 | -121.6538 | No | Clear-Strong Winds;32-90 F | Transformer (OH) | Deteriorated | 24-0051641 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1931405 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | BORONDA-1101 | 182461101 | TRANSFORMER | 412165151298 | 20240405 | 1443 | 20240406 | 1545 | 2424281 | 1502 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1502 | 36.7131 | -121.6747 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0051515 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1931311 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 23395 | 20240405 | 1559 | 20240406 | 225 | 2424584 | 626 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 7512 | 36.7774 | -121.6572 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0051573 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | Yes | No | 1931348 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 9449 | 20240405 | 1751 | 20240406 | 1648 | 2424777 | 1377 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1377 | 37.0783 | -122.0589 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0051621 | OH | Sus | 31689769 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1931384 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | FUSE | 10261 | 20240405 | 1907 | 20240405 | 1951 | 2424837 | 44 | Distribution Circuit | Animal | Bird found | 1230 | 54120 | 36.9672 | -121.9853 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0051625 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1931389 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | FUSE | 25031 | 20240405 | 2000 | 20240406 | 1104 | 2424970 | 904 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 904 | 36.3181 | -121.2641 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0051666 | OH | Sus | 46221232 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | Yes | 1931431 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | BUENA VISTA-1102 | 182261102 | RECLOSER | 3730 | 20240406 | 2305 | 20240407 | 1345 | 2425494 | 880 | Distribution Circuit | 3rd Party | Vehicle | 347 | 34208 | 36.6431 | -121.6349 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0051846 | OH | Sus | 35542422 | SOUTH BAY AND CENTRAL COAST | APR | Three Phase Fault | 0 | No | No | No | 1931587 | 0 | Non-EPSS | N | 2024 | ABC
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 11829 | 20240407 | 640 | 20240407 | 818 | 2425568 | 98 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 490 | 37.009 | -122.0756 | No | Clear;32-90 F |  |  | 24-0051867 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1931611 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | FUSE | 4447 | 20240407 | 651 | 20240407 | 725 | 2425572 | 34 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 1020 | 36.7894 | -121.36 | No | Clear;32-90 F |  |  | 24-0051861 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1931604 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 6137 | 20240407 | 1318 | 20240408 | 537 | 2425705 | 979 | Distribution Circuit | Equipment Failure/Involved | Underground | 120 | 66738 | 36.5945 | -121.8932 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0051906 | UG | Sus | 35542401 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1931654 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 9875 | 20240408 | 357 | 20240408 | 723 | 2425900 | 206 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 2472 | 36.8601 | -121.7708 | No | Clear;32-90 F |  |  | 24-0051959 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1931715 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 3193 | 20240408 | 627 | 20240408 | 704 | 2425917 | 33 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 41 | 1353 | 36.8575 | -121.6448 | No | Clear;32-90 F |  |  | 24-0051970 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1931728 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1103 | 182201103 | JUMPER | OJ SOURCE SD CGC# 412548448217 | 20240408 | 1044 | 20240408 | 1345 | 2426225 | 181 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 181 | 36.6309 | -121.5406 | No | Clear;32-90 F | Jumper | Burned Open | 24-0052093 | OH | Sus | 46221999 | SOUTH BAY AND CENTRAL COAST | APR | Open Circuit | 0 | No | No | No | 1931873 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 4953 | 20240408 | 1445 | 20240409 | 35 | 2426435 | 590 | Distribution Circuit | Equipment Failure/Involved | Overhead | 170 | 18820 | 36.8253 | -121.6618 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0052275 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1931922 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 2901 | 20240408 | 1918 | 20240408 | 2332 | 2426643 | 254 | Distribution Circuit | Animal | Bird found | 145 | 29251 | 36.9671 | -122.0079 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0052335 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1931962 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 67520 | 20240408 | 2341 | 20240409 | 529 | 2426650 | 348 | Distribution Circuit | 3rd Party | Vehicle | 18 | 6264 | 36.9577 | -121.8525 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0052331 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1932027 | 0 | EPSS Ckt | N | 2024 | N/A
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | TRANSFORMER | 412061746082 | 20240409 | 553 | 20240409 | 1421 | 2426687 | 508 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 2032 | 36.5683 | -121.7051 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0052471 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1932087 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | TRANSFORMER | 316207914208 | 20240409 | 600 | 20240409 | 1342 | 2426692 | 462 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 462 | 36.883 | -121.7976 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0052502 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1932140 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | DOLAN ROAD-1101 | 182381101 | FUSE | 2223 | 20240409 | 1255 | 20240409 | 1440 | 2427118 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 735 | 36.8319 | -121.7798 | No | Clear;32-90 F |  |  | 24-0052737 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1932262 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 10279 | 20240409 | 1412 | 20240409 | 1422 | 2426977 | 10 | Distribution Circuit | Vegetation | Tree - branch fell on line | 59 | 590 | 36.9781 | -122.0336 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0052685 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1932257 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 9442 | 20240410 | 307 | 20240411 | 208 | 2427486 | 1381 | Distribution Circuit | Equipment Failure/Involved | Underground | 125 | 52875 | 36.6222 | -121.9167 | No | Partly Cloudy-Fog;32-90 F | Secondary | Contaminated | 24-0052920 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1932335 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | TRANSFORMER | 412026949209 | 20240410 | 953 | 20240410 | 1129 | 2427756 | 96 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 96 | 36.6539 | -121.719 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0053063 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1932514 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 23321 | 20240410 | 1032 | 20240410 | 1151 | 2427788 | 79 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1027 | 36.8262 | -121.7261 | No | Clear;32-90 F |  |  | 24-0053081 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1932523 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | FUSE | 9593 | 20240410 | 1359 | 20240410 | 1441 | s1934182 | 42 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 64 | 2689 | 36.8134 | -121.3951 | No | Clear;32-90 F |  |  | 24-0053168 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1934182 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | FUSE | 9477 | 20240410 | 1422 | 20240410 | 1642 | 2427969 | 140 | Distribution Circuit | Equipment Failure/Involved | Underground | 280 | 37359 | 36.8454 | -121.3954 | No | Clear;32-90 F | Connector or Splice (UG) | Burned/flashed | 24-0053232 | UG | Sus | 31690262 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1932548 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | KING CITY-1103 | 182031103 | FUSE | 9633 | 20240410 | 2029 | 20240411 | 45 | 2428148 | 256 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1280 | 36.2094 | -121.1318 | No | Partly Cloudy;32-90 F | Lightning Arrestor | Broken | 24-0053346 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1932602 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 3193 | 20240411 | 624 | 20240411 | 700 | 2428214 | 36 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 41 | 1476 | 36.8575 | -121.6448 | No | Clear;32-90 F |  |  | 24-0053371 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1932622 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 9639 | 20240411 | 835 | 20240411 | 1452 | 2428417 | 377 | Distribution Circuit | Animal | Other | 2 | 754 | 36.8808 | -121.7784 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0053664 | OH | Sus | 46227645 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1932832 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 11961 | 20240411 | 1319 | 20240411 | 1438 | 2428647 | 79 | Distribution Circuit | 3rd Party | Vehicle | 18 | 1422 | 36.9619 | -121.8779 | No | Clear;32-90 F | Anchor or Guy | Broken | 24-0053661 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1932830 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | SWITCH | 4518 | 20240411 | 1331 | 20240411 | 1356 | 2428651 | 25 | Distribution Circuit | Equipment Failure/Involved | Underground | 280 | 2529 | 36.8397 | -121.3918 | No | Clear;32-90 F | Connector or Splice (UG) | Normal | 24-0053232 | UG | Sus | 31690262 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1932815 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 3287 | 20240412 | 837 | 20240412 | 930 | 2429242 | 53 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 706 | 36.6786 | -121.7086 | No | Clear;32-90 F | Fuse | Broken | 24-0053975 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1933092 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2101 | 182492101 | SWITCH | 80843 | 20240412 | 1400 | 20240412 | 1500 | 2429551 | 60 | Distribution Circuit | Animal | Other | 2 | 120 | 36.8298 | -121.4017 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0054114 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1933132 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | FUSE | 8971 | 20240412 | 1414 | 20240413 | 53 | 2429588 | 639 | Distribution Circuit | Equipment Failure/Involved | Overhead | 296 | 26424 | 36.4727 | -121.7254 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0054203 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1933165 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-1101 | 182221101 | TRANSFORMER | 411661247582 | 20240412 | 1433 | 20240412 | 2225 | 2429607 | 472 | Transformer only | Equipment Failure/Involved | Overhead | 23 | 10856 | 36.6062 | -121.8428 | No | Overcast;32-90 F | Transformer (OH) | Deteriorated | 24-0054202 | OH | Sus | 31690573 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1933164 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 2987 | 20240412 | 1433 | 20240412 | 1825 | 2429608 | 232 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 114 | 26448 | 36.9761 | -121.7506 | No | Overcast;32-90 F |  |  | 24-0054263 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1933192 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 7159 | 20240412 | 1444 | 20240412 | 1718 | 2429896 | 154 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 3696 | 36.578 | -121.9068 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0054245 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Three Phase Fault | 0 | No | No | No | 1933183 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | BORONDA-1101 | 182461101 | FUSE | 20199 | 20240412 | 1521 | 20240412 | 1610 | 2429788 | 49 | Distribution Circuit | 3rd Party | Metallic Balloon | 99 | 4851 | 36.6992 | -121.6716 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0054212 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1933168 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | SOLEDAD-2101 | 182052101 | FUSE | 9003 | 20240412 | 1716 | 20240412 | 1902 | 2429909 | 106 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 318 | 36.4213 | -121.2849 | No | Clear;32-90 F |  |  | 24-0054268 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1933195 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 9653 | 20240412 | 1736 | 20240412 | 1900 | 2429907 | 84 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 84 | 36.8644 | -121.7708 | No | Clear;32-90 F |  |  | 24-0054273 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1933197 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | FUSE | 7093 | 20240413 | 222 | 20240415 | 1126 | 2430087 | 3424 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 13696 | 36.096 | -120.6843 | No | Clear;32-90 F |  |  | 24-0054338 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1933262 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | RECLOSER | BL 1101 | 20240413 | 235 | 20240413 | 1620 | 2430096 | 825 | Distribution Circuit | 3rd Party | Vehicle | 743 | 150645 | 37.0926 | -122.0966 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0054320 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1933250 | 0 | EPSS Ckt | N | 2024 | B-C- GRD
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 737 | 20240413 | 358 | 20240413 | 855 | 2430114 | 297 | Distribution Circuit | Vegetation | Tree - bark fell into line | 59 | 17523 | 37.0046 | -121.8551 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0054357 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1933276 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 2987 | 20240413 | 750 | 20240413 | 1622 | 2430171 | 512 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 37376 | 36.9761 | -121.7506 | No | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0054384 | OH | Sus | 31690584 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | Yes | No | 1933290 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | SWITCH | 1514 | 20240413 | 1007 | 20240413 | 1511 | 2430245 | 304 | Distribution Circuit | Equipment Failure/Involved | Underground | 93 | 1224 | 36.9211 | -121.7718 | No | Overcast-Rain;32-90 F | Conductor- Underground | Deteriorated | 24-0054366 | UG | Sus | 35541506 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1933296 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 280116 | 20240413 | 1030 | 20240413 | 1801 | 2430258 | 451 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2131 | 98326 | 36.939 | -121.7423 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0054397 | OH | Sus | 46228591 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1933299 | 0 | EPSS Ckt | N | 2024 | BC GRD TIME
CENTRAL COAST | SALINAS | SALINAS-1106 | 182011106 | TRANSFORMER | 412211849578 | 20240413 | 1040 | 20240413 | 1551 | 2430291 | 311 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 311 | 36.6656 | -121.6573 | No | Overcast-Rain;32-90 F | Fuse | Failed/Faulted | 24-0054515 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1933378 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | FUSE | 4587 | 20240413 | 1553 | 20240413 | 1638 | 2430691 | 45 | Distribution Circuit | Animal | Squirrel | 71 | 3195 | 36.9879 | -121.9718 | No | Overcast-Drizzle;32-90 F | Pothead(Riser Termination) | Normal | 24-0054529 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1933392 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 1645 | 20240413 | 2000 | 20240413 | 2145 | 2430933 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 1785 | 37.0217 | -121.7655 | No | Clear;32-90 F |  |  | 24-0054581 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1933446 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316318017067 | 20240413 | 2205 | 20240413 | 2349 | 2430655 | 104 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 1144 | 36.9619 | -121.7613 | No | Overcast;32-90 F | Transformer | Failed/Faulted | 24-0054526 | OH | Sus | 35544522 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1933389 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | RECLOSER | 11056 | 20240414 | 125 | 20240414 | 1905 | 2431003 | 1060 | Distribution Circuit | Vegetation | Tree - fell into line | 448 | 432740 | 36.9937 | -122.0299 | No | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0054612 | OH | Sus | 35544601 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1933479 | 0 | EPSS Ckt | N | 2024 | C- GRD
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 7563 | 20240414 | 155 | 20240414 | 913 | 2431017 | 438 | Distribution Circuit | Vegetation | Tree - grew into line | 1 | 438 | 36.994 | -121.8962 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0054613 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1933480 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9733 | 20240414 | 401 | 20240414 | 1337 | 2431039 | 576 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 28224 | 37.158 | -122.1357 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0054622 | OH | Sus | 31690700 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1933489 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | FUSE | 868789 | 20240414 | 1051 | 20240414 | 1217 | 2431238 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 430 | 36.5697 | -121.729 | No | Clear;32-90 F |  |  | 24-0054680 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1933554 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | FUSE | 8977 | 20240414 | 1225 | 20240414 | 2154 | 2431295 | 569 | Distribution Circuit | Equipment Failure/Involved | Overhead | 101 | 57469 | 36.9673 | -121.9674 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Failed/Faulted | 24-0054700 | OH | Sus | 46228747 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1933565 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | RECLOSER | 10952 | 20240414 | 1621 | 20240415 | 251 | 2431376 | 591 | Distribution Circuit | Equipment Failure/Involved | Overhead | 360 | 186742 | 36.8841 | -121.7552 | No | Overcast;32-90 F | Conductor- Overhead | Together | 24-0054717 | OH | Sus | 46228749 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1933579 | 0 | EPSS Ckt | N | 2024 | A GRD
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 1113 | 20240415 | 543 | 20240415 | 730 | 2431553 | 107 | Distribution Circuit | Animal | Bird found | 95 | 10165 | 36.926 | -121.7457 | No | Overcast-Fog;32-90 F | Fuse | Normal | 24-0054783 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1933652 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1105 | 182011105 | TRANSFORMER | 412301450958 | 20240415 | 916 | 20240415 | 1221 | 2431658 | 185 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 3145 | 36.7039 | -121.6279 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0054810 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1933689 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411985550110 | 20240415 | 947 | 20240415 | 1403 | 2431793 | 256 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 512 | 36.6781 | -121.735 | No | Clear;32-90 F | Connector- Bolted | Failed/Faulted | 24-0054941 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1933808 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 7831 | 20240415 | 1516 | 20240416 | 253 | 2432093 | 697 | Distribution Circuit | Equipment Failure/Involved | Overhead | 47 | 9953 | 36.9646 | -121.7926 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0055163 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1933872 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 6283 | 20240415 | 1654 | 20240416 | 2213 | 2432139 | 1759 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 14072 | 37.0683 | -121.9858 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0055180 | OH | Sus | 46229171 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1933884 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | JUMPER | WIRE DOWN | 20240415 | 2012 | 20240416 | 257 | 2432269 | 405 | Distribution Circuit | Vegetation | Tree - fell into line | 189 | 76053 | 36.9785 | -121.9577 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0055188 | OH | Sus | 35545402 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | Yes | 1933894 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | TRANSFORMER | 412351039485 | 20240415 | 2036 | 20240416 | 1352 | 2432244 | 1036 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 1036 | 36.3886 | -121.6 | No | Clear;32-90 F |  |  | 24-0055228 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | None | 0 | No | No | No | 1933933 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1101 | 182201101 | FUSE | 24437 | 20240416 | 525 | 20240416 | 645 | 2432325 | 80 | Distribution Circuit | 3rd Party | Vehicle | 16 | 1280 | 36.6143 | -121.5699 | No | Fog;32-90 F | Pole-Wood | Normal | 24-0055245 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1933952 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 12989 | 20240416 | 556 | 20240416 | 707 | 2432350 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 46 | 3266 | 36.9908 | -121.9569 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0055257 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1933956 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | FUSE | 7941 | 20240416 | 915 | 20240417 | 131 | 2432493 | 976 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 12 | 11712 | 36.3927 | -121.0658 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0055329 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1934056 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | BUENA VISTA-1102 | 182261102 | OTHER | WIRE DOWN BTWN 4245 & 23475 | 20240416 | 1322 | 20240416 | 1715 | 2432813 | 233 | Distribution Circuit | Equipment Failure/Involved | Overhead | 510 | 2269 | 36.6478 | -121.6327 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0055524 | OH | Sus | 46229485 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | Yes | 1934177 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 316174917190 | 20240416 | 1337 | 20240416 | 1823 | 2432742 | 286 | Transformer only | 3rd Party | Vehicle | 9 | 2574 | 36.9647 | -121.8103 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0055500 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1934174 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | INTERRUPTER | 325932 | 20240416 | 1443 | 20240416 | 1652 | 2432921 | 129 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 258 | 36.3275 | -121.2551 | No | Clear;32-90 F | Customer Equipment | Burned/flashed | 24-0055592 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1934206 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | FUSE | 10545 | 20240416 | 1821 | 20240416 | 1959 | 2433015 | 98 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 98 | 36.9916 | -122.0064 | No | Partly Cloudy;32-90 F |  |  | 24-0055621 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1934228 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | SWITCH | 10128 | 20240417 | 2234 | 20240418 | 222 | 2433856 | 228 | Distribution Circuit | Equipment Failure/Involved | Underground | 472 | 107616 | 37.042 | -122.0243 | No | Partly Cloudy;32-90 F | Interrupter | Leaking | 24-0055831 | UG | Sus | 35545953 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1934630 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 12453 | 20240418 | 1059 | 20240418 | 1225 | 2434116 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 77 | 6644 | 36.9225 | -121.7475 | No | Partly Cloudy;32-90 F |  |  | 24-0056380 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1934751 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 4605 | 20240418 | 1252 | 20240418 | 1459 | 2434195 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 127 | 36.9123 | -121.7575 | No | Clear;32-90 F |  |  | 24-0056504 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1934776 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | FUSE | 91389 | 20240418 | 1258 | 20240419 | 227 | 2434099 | 809 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 18528 | 36.7326 | -121.5973 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0056394 | OH | Sus | 31691111 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1934755 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | TRANSFORMER | 412337452422 | 20240418 | 1354 | 20240419 | 305 | 2434126 | 791 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 791 | 36.7447 | -121.6165 | No | Clear;32-90 F | Service conductor | Broken | 24-0056546 | OH | Sus | 31691042 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1934786 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | JUMPER | OJ NW/OF 7039 | 20240418 | 1838 | 20240418 | 2206 | 2434384 | 208 | Distribution Circuit | Vegetation | Tree - grew into line | 18 | 3744 | 36.5799 | -121.9201 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0056616 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1934801 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | OTHER | WIRE DOWN E/OF 11745 | 20240419 | 601 | 20240419 | 1302 | 2434559 | 391 | Distribution Circuit | Equipment Failure/Involved | Overhead | 292 | 35155 | 36.8979 | -121.7776 | No | Overcast-Fog;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0056683 | OH | Sus | 46231538 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | Yes | 1934851 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 147207 | 20240419 | 628 | 20240419 | 831 | 2434574 | 123 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 1353 | 36.7871 | -121.665 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0056749 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1934914 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | FUSE | 4447 | 20240419 | 815 | 20240419 | 912 | 2434680 | 57 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 1710 | 36.7894 | -121.36 | No | Partly Cloudy;32-90 F |  |  | 24-0056782 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1934970 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | TRANSFORMER | 412831659291 | 20240419 | 1024 | 20240419 | 1036 | 2434682 | 12 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 12 | 36.9369 | -121.454 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 24-0056838 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1935002 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 12474 | 20240419 | 1248 | 20240419 | 1625 | 2435007 | 217 | Distribution Circuit | Vegetation | Tree - fell into line | 6142 | 503898 | 36.9713 | -121.8735 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 24-0056927 | OH | Sus | 46231627 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1935031 | 0 | EPSS Ckt | N | 2024 | B PHSE & GRD
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 4081 | 20240420 | 1049 | 20240420 | 1230 | 2435487 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 101 | 36.7395 | -121.3924 | No | Clear;32-90 F |  |  | 24-0057170 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1935211 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 412042749393 | 20240420 | 1104 | 20240421 | 1654 | 2434915 | 1790 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1790 | 36.659 | -121.7153 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0057151 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1935201 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | KING CITY-1101 | 182031101 | OCB | 1101/12 | 20240420 | 2040 | 20240421 | 1137 | 2435698 | 897 | Distribution Circuit | 3rd Party | Metallic Balloon | 1663 | 282039 | 36.2171 | -121.1269 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0057238 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | Yes | No | 1935244 | 0 | Non-EPSS | N | 2024 | AB
CENTRAL COAST | KING CITY | SOLEDAD-2104 | 182052104 | RECLOSER | 7248 | 20240421 | 1153 | 20240422 | 213 | 2435855 | 860 | Distribution Circuit | 3rd Party | Vehicle | 72 | 21840 | 36.4351 | -121.3426 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0057301 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1935317 | 0 | EPSS Ckt | N | 2024 | C & GRD
CENTRAL COAST | SALINAS | DEL MONTE-2104 | 182222104 | FUSE | 5835 | 20240421 | 2009 | 20240421 | 2241 | 2435980 | 152 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 62 | 9424 | 36.5695 | -121.7533 | No | Clear;32-90 F |  |  | 24-0057349 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1935355 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 6687 | 20240422 | 106 | 20240422 | 845 | 2436089 | 459 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 1070 | 36.888 | -121.8045 | No | Fog;32-90 F |  |  | 24-0057432 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1935442 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 9497 | 20240422 | 607 | 20240422 | 844 | 2436119 | 157 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 2355 | 37.0296 | -122.0228 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0057427 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1935434 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 9703 | 20240422 | 903 | 20240422 | 1035 | 2436306 | 92 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1288 | 36.9006 | -121.5985 | No | Partly Cloudy-Rain;32-90 F |  |  | 24-0057510 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1935526 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SOLEDAD-2104 | 182052104 | TRANSFORMER | 413126041803 | 20240422 | 954 | 20240422 | 1724 | 2436438 | 450 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 450 | 36.4585 | -121.3389 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0057478 | OH | Sus | 31691682 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1935510 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | TRANSFORMER | 411621546656 | 20240422 | 1131 | 20240423 | 145 | 2436639 | 854 | Distribution Circuit | Equipment Failure/Involved | Overhead | 55 | 9818 | 36.5808 | -121.855 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 24-0057671 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1935578 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 6277 | 20240422 | 1852 | 20240422 | 2130 | 2436900 | 158 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 12 | 1896 | 37.213 | -122.1502 | No | Partly Cloudy;32-90 F |  |  | 24-0057791 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1935648 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | FUSE | 4211 | 20240422 | 2023 | 20240422 | 2115 | 2436968 | 52 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 31 | 1612 | 36.9688 | -121.4325 | No | Overcast;32-90 F |  |  | 24-0057773 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1935630 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | JUMPER | OJ CGC 415081829114 | 20240422 | 2109 | 20240423 | 122 | 2436970 | 253 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 253 | 36.1214 | -120.6688 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0057769 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1935624 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SOLEDAD-2105 | 182052105 | FUSE | 7601 | 20240423 | 846 | 20240423 | 1048 | 2437235 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 406 | 36.4708 | -121.394 | No | Partly Cloudy;32-90 F |  |  | 24-0057976 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1935816 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | SWITCH | 12016SW | 20240423 | 939 | 20240423 | 1420 | 2437242 | 281 | Distribution Circuit | Equipment Failure/Involved | Underground | 5 | 574 | 37.0111 | -122.195 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0057858 | UG | Sus | 35547413 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1935731 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | JUMPER | OJ 2 P SS OF CGC 412367438985 | 20240423 | 1047 | 20240423 | 1426 | 2437406 | 219 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 876 | 36.3774 | -121.5937 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0057984 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1935818 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | FUSE | 4447 | 20240424 | 945 | 20240424 | 1002 | 2438071 | 17 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 510 | 36.7894 | -121.36 | No | Partly Cloudy;32-90 F |  |  | 24-0058420 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1936114 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | TRANSFORMER | T502022 | 20240424 | 1606 | 20240425 | 1525 | 2438583 | 1399 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 2798 | 36.5711 | -121.9416 | No | Overcast;32-90 F | Transformer (UG) | Failed/Faulted | 24-0058683 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1936236 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1106 | 182011106 | TRANSFORMER | 100000100521 | 20240424 | 1636 | 20240425 | 258 | 2438310 | 622 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1244 | 36.6762 | -121.6536 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0058661 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1936185 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | TRANSFORMER | T50213 | 20240424 | 1716 | 20240425 | 238 | 2438425 | 554 | Distribution Circuit | Equipment Failure/Involved | Underground | 11 | 3423 | 36.5716 | -121.9433 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 24-0058683 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1936192 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 6935 | 20240425 | 1 | 20240425 | 124 | 2438560 | 83 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 1328 | 36.5538 | -121.9124 | No | Overcast;32-90 F |  |  | 24-0058732 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1936231 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | TRANSFORMER | 315283822713 | 20240425 | 750 | 20240425 | 1945 | 2438632 | 715 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1430 | 37.1131 | -122.1168 | No | Partly Cloudy-Fog;32-90 F | Transformer | Failed/Faulted | 24-0058819 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1936381 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | TRANSFORMER | 412716556089 | 20240425 | 836 | 20240425 | 949 | 2438651 | 73 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 73 | 36.8476 | -121.4905 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0058825 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1936392 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 5269 | 20240425 | 1224 | 20240425 | 1328 | 2439009 | 64 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 554 | 36.9894 | -122.0312 | No | Partly Cloudy;32-90 F |  |  | 24-0058970 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1936451 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 12465 | 20240426 | 1759 | 20240426 | 2210 | 2440119 | 251 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 251 | 36.9691 | -121.8707 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0059493 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1936809 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 3193 | 20240426 | 1937 | 20240426 | 2022 | 2440209 | 45 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 41 | 1845 | 36.8575 | -121.6448 | No | Clear;32-90 F |  |  | 24-0059526 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1936837 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | FUSE | 5561 | 20240426 | 2102 | 20240427 | 238 | 2440282 | 336 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 4482 | 36.7763 | -121.5987 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0059572 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1936886 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | FUSE | 23545 | 20240427 | 109 | 20240427 | 648 | 2440342 | 339 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 678 | 36.5641 | -121.4841 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0059587 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1936899 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1102 | 182201102 | RECLOSER | 276712 | 20240427 | 307 | 20240427 | 1715 | 2440355 | 848 | Distribution Circuit | 3rd Party | Vehicle | 198 | 51030 | 36.6279 | -121.5432 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 24-0059576 | OH | Sus | 31692172 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | Yes | No | 1936890 | 0 | EPSS Ckt | N | 2024 | C& GRD
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 9955 | 20240427 | 848 | 20240427 | 1300 | 2440427 | 252 | Distribution Circuit | 3rd Party | Thrown Object | 3 | 756 | 36.9144 | -121.7387 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Normal | 24-0059636 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1936972 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 9097 | 20240427 | 1036 | 20240427 | 1138 | 2440476 | 62 | Distribution Circuit | Vegetation | Tree - grew into line | 18 | 1116 | 36.9798 | -122.0393 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0059600 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1936945 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | SWITCH | 11803 | 20240427 | 1309 | 20240427 | 1549 | s1936977 | 117 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 120 | 3431 | 37.0782 | -122.0318 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0059628 | OH | Sus | 31692171 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1936977 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | TRANSFORMER | 315865517948 | 20240427 | 1818 | 20240427 | 2004 | 2440782 | 106 | Transformer only | Vegetation | Tree - fell into line | 12 | 1272 | 36.9843 | -121.9165 | No | Clear;32-90 F | Secondary | Normal | 24-0059691 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1937008 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 3811 | 20240427 | 1819 | 20240427 | 1940 | 2440788 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 486 | 36.9047 | -121.6453 | No | Clear;32-90 F |  |  | 24-0059695 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1937014 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8961 | 20240427 | 1856 | 20240427 | 2207 | 2440801 | 191 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 382 | 37.0432 | -122.0518 | No | Clear;32-90 F |  |  | 24-0059721 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1937043 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 1153 | 20240427 | 1907 | 20240427 | 2041 | 2440802 | 94 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 146 | 13724 | 36.9786 | -121.8924 | No | Clear;32-90 F |  |  | 24-0059698 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1937018 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | OTHER | WIRE DOWN @ 24959 | 20240427 | 1912 | 20240428 | 1117 | 2440804 | 965 | Distribution Circuit | 3rd Party | Vehicle | 244 | 4124 | 36.6999 | -121.704 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0059694 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | Yes | 1937011 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | FUSE | 50951 | 20240428 | 250 | 20240428 | 422 | 2440886 | 92 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1288 | 36.9584 | -121.4301 | No | Clear;32-90 F |  |  | 24-0059735 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1937057 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 2887 | 20240428 | 718 | 20240428 | 1515 | 2440927 | 477 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 954 | 37.1394 | -122.0948 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0059751 | OH | Sus | 46235862 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | Yes | No | 1937075 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 538096 | 20240428 | 1150 | 20240428 | 2112 | 2441039 | 562 | Distribution Circuit | 3rd Party | Vehicle | 987 | 411586 | 37.0578 | -122.0595 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0059765 | OH | Sus | 31692481 | SOUTH BAY AND CENTRAL COAST | APR | Multi-Fault | 0 | No | Yes | No | 1937093 | 0 | EPSS Ckt | N | 2024 | ABC GRD
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 6333 | 20240428 | 1812 | 20240428 | 1925 | 2441148 | 73 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 15 | 1095 | 36.6268 | -121.9359 | No | Clear;32-90 F | Fuse | Burned Open | 24-0059798 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1937120 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 5129 | 20240428 | 2041 | 20240429 | 1017 | 2441175 | 816 | Distribution Circuit | 3rd Party | Vehicle | 6 | 4896 | 36.8215 | -121.7842 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0059801 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | Yes | No | 1937125 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | JUMPER | BURNED OJ @ 5607 | 20240428 | 2129 | 20240429 | 1103 | 2441533 | 814 | Distribution Circuit | Equipment Failure/Involved | Overhead | 218 | 158156 | 37.1266 | -122.0185 | No | Clear;32-90 F | Jumper | Burned Open | 24-0059909 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Open Circuit | 0 | No | No | No | 1937285 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | FUSE | 9467 | 20240429 | 1351 | 20240429 | 1735 | 2441833 | 224 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 5600 | 36.977 | -121.9446 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0060045 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1937359 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | JUMPER | JUMPERS 1P N/OF CGC# 411387048393 | 20240429 | 1416 | 20240429 | 1723 | 2441846 | 183 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1098 | 36.6267 | -121.9372 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 24-0060057 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | None | 0 | No | No | No | 1937364 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | JUMPER | OPEN JPR @ 52877 | 20240429 | 1434 | 20240429 | 2115 | 2441884 | 401 | Distribution Circuit | Equipment Failure/Involved | Overhead | 205 | 1217 | 36.337 | -121.2065 | No | Clear;32-90 F | Jumper | Burned Open | 24-0060129 | OH | Sus | 46236249 | SOUTH BAY AND CENTRAL COAST | APR | Open Circuit | 0 | No | No | No | 1937395 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | SOLEDAD-2104 | 182052104 | TRANSFORMER | 413159640624 | 20240429 | 2216 | 20240430 | 538 | 2442103 | 442 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 4862 | 36.4264 | -121.3262 | No | Clear;32-90 F | Jumper | Broken | 24-0060217 | OH | Sus | 31692497 | SOUTH BAY AND CENTRAL COAST | APR | Open Circuit | 0 | No | No | No | 1937464 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315384819828 | 20240429 | 2312 | 20240430 | 337 | 2442097 | 265 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 795 | 37.0336 | -122.0824 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0060189 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1937434 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | TRANSFORMER | 315893817576 | 20240430 | 419 | 20240430 | 1226 | 2442136 | 487 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 4870 | 36.9741 | -121.9066 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0060224 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1937473 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | SWITCH | 300345 | 20240430 | 725 | 20240430 | 752 | 2442247 | 27 | Distribution Circuit | Company Initiated | Improper Construction | 37 | 999 | 36.5757 | -121.9506 | No | Clear;32-90 F | Switch (OH) | Normal | 24-0046608 | OH | Sus | 35125717 | SOUTH BAY AND CENTRAL COAST | APR | None | 0 | No | No | No | 1937507 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 601610 | 20240430 | 1237 | 20240430 | 1252 | 2442708 | 15 | Distribution Circuit | Company Initiated | Personnel- company | 76 | 1140 | 37.1117 | -122.0207 | No | Clear;32-90 F | Jumper | Normal | 24-0060479 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Multi-Fault | 0 | No | No | No | 1937728 | 0 | EPSS Ckt | N | 2024 | ABC-SGF
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 6725 | 20240501 | 907 | 20240501 | 1120 | 2443411 | 133 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 665 | 36.8776 | -121.7681 | No | Clear;32-90 F |  |  | 24-0060873 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1938015 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 10717 | 20240501 | 937 | 20240501 | 1040 | 2443324 | 63 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 1575 | 37.0913 | -122.1045 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0055512 | OH | Sus | 45567606 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1937993 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | FUSE | 865 | 20240501 | 1037 | 20240501 | 1121 | 2443348 | 44 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 176 | 36.9841 | -121.9658 | No | Clear;32-90 F |  |  | 24-0060869 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1938014 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | JUMPER | OJ 1 N/OF CGC 411506347701 | 20240501 | 1303 | 20240501 | 1446 | 2443503 | 103 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 412 | 36.6084 | -121.896 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0060884 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1938035 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | SWITCH | 40001 | 20240501 | 1516 | 20240501 | 1528 | 2443636 | 12 | Distribution Circuit | Company Initiated | Operating error | 6515 | 78180 | 36.6138 | -121.9107 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 24-0060884 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | None | 0 | No | No | No | 1938082 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | TRANSFORMER | 315938917238 | 20240501 | 1631 | 20240501 | 1717 | 2443692 | 46 | Transformer only | Vegetation | Tree - bark fell into line | 8 | 368 | 36.9648 | -121.8901 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0061074 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1938099 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | JUMPER | OJ 1 N/OF CGC #411813250825 | 20240501 | 1729 | 20240501 | 1858 | 2443728 | 89 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 1780 | 36.6969 | -121.7942 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0061067 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1938094 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | FUSE | 865 | 20240501 | 1750 | 20240501 | 1843 | 2443756 | 53 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 212 | 36.9841 | -121.9658 | No | Clear;32-90 F |  |  | 24-0061088 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1938109 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1103 | 182201103 | FUSE | 23491 | 20240501 | 2011 | 20240502 | 527 | 2443802 | 556 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 3336 | 36.635 | -121.5541 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0061118 | OH | Sus | 46236968 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1938136 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | SWITCH | 96707 | 20240501 | 2208 | 20240502 | 532 | 2443825 | 444 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 12876 | 36.0123 | -121.168 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0061064 | OH | Sus | 35549823 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1938135 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411916853344 | 20240502 | 307 | 20240502 | 1321 | 2443845 | 614 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 1228 | 36.7668 | -121.7605 | No | Clear;32-90 F |  |  | 24-0061128 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | None | 0 | No | No | No | 1938146 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | BEN LOMOND SUB | 8304 | OCB | 401/2 | 20240502 | 602 | 20240502 | 828 | 2443863 | 146 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 887 | 115502 | 37.0923 | -122.0965 | No | Clear;32-90 F |  |  | 24-0061136 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Three Phase Fault | 0 | No | No | No | 1938152 | 0 | Non-EPSS | N | 2024 | GRD TIE OC
CENTRAL COAST | MONTEREY | FORT ORD-2107 | 182402107 | TRANSFORMER | 411847050065 | 20240502 | 1101 | 20240502 | 1132 | 2444062 | 31 | Transformer only | Equipment Failure/Involved | Overhead | 19 | 589 | 36.6761 | -121.7821 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0061260 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1938346 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | INDUSTRIAL ACRES-0413 | 182300413 | FUSE | 4383 | 20240502 | 1123 | 20240502 | 1156 | 2444240 | 33 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 38 | 1254 | 36.6705 | -121.6367 | No | Clear;32-90 F |  |  | 24-0061292 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1938359 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6597 | 20240502 | 1245 | 20240502 | 1830 | 2444208 | 345 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 2070 | 36.9966 | -121.7163 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0061318 | OH | Sus | 46237231 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1938375 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 1735 | 20240502 | 1710 | 20240502 | 1906 | 2444516 | 116 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 51 | 5916 | 36.9987 | -121.8318 | No | Clear;32-90 F |  |  | 24-0061490 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1938425 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 11539 | 20240502 | 1807 | 20240502 | 2035 | 2444518 | 148 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 296 | 36.865 | -121.6887 | No | Clear;32-90 F |  |  | 24-0061502 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1938435 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | INDUSTRIAL ACRES-0413 | 182300413 | JUMPER | FB 1 S/OF CGC#412297549745 | 20240502 | 2105 | 20240503 | 227 | 2444578 | 322 | Distribution Circuit | 3rd Party | Vehicle | 6 | 1932 | 36.6711 | -121.6276 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0061500 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1938433 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | OTHER | T0037 TWD T0872 | 20240503 | 127 | 20240503 | 350 | 2444655 | 143 | Distribution Circuit | Equipment Failure/Involved | Underground | 35 | 1765 | 36.5317 | -121.9222 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 24-0061504 | UG | Sus | 35550440 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1938489 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 985 | 20240503 | 657 | 20240503 | 850 | 2444827 | 113 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 715 | 36.8521 | -121.7712 | No | Clear;32-90 F |  |  | 24-0061613 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1938588 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | RECLOSER | 36982 | 20240503 | 926 | 20240503 | 1718 | 2444893 | 472 | Distribution Circuit | Equipment Failure/Involved | Overhead | 394 | 50973 | 36.5301 | -121.4747 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0061649 | OH | Sus | 46237437 | SOUTH BAY AND CENTRAL COAST | MAY | Multi-Fault | 0 | No | Yes | No | 1938638 | 0 | EPSS Ckt | N | 2024 | A-B-C-GRD-TIME OC
CENTRAL COAST | SALINAS | SPENCE-1102 | 182201102 | SWITCH | 377233 | 20240503 | 1355 | 20240503 | 1443 | 2445123 | 48 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 48 | 36.6215 | -121.5057 | No | Clear;32-90 F | Insulator | Burned/flashed | 24-0061774 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1938707 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 12957 | 20240503 | 1754 | 20240503 | 1900 | 2445255 | 66 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 51 | 3366 | 36.9885 | -122.0304 | No | Clear;32-90 F |  |  | 24-0061887 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1938738 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 8881 | 20240503 | 1905 | 20240504 | 1033 | 2445338 | 774 | Distribution Circuit | Equipment Failure/Involved | Underground | 298 | 114048 | 36.9346 | -121.7654 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0061899 | UG | Sus | 46238358 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1938752 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | FUSE | 9857 | 20240503 | 2157 | 20240504 | 37 | 2445398 | 160 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 3200 | 36.2979 | -121.1929 | No | Partly Cloudy;32-90 F |  |  | 24-0061951 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1938809 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | OCB | 1101/2 | 20240503 | 2350 | 20240504 | 47 | 2445430 | 57 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3541 | 154107 | 36.5569 | -121.8976 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0061952 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1938810 | 0 | EPSS Ckt | N | 2024 | A-B
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 23311 | 20240504 | 116 | 20240504 | 250 | 2445446 | 94 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 116 | 10904 | 36.7616 | -121.7473 | No | Clear;32-90 F |  |  | 24-0061962 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1938820 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | OTHER | WIRE DOWN 3 SP SSD OF FUCO 9857 | 20240504 | 457 | 20240504 | 1904 | 2445669 | 847 | Distribution Circuit | Equipment Failure/Involved | Overhead | 845 | 40674 | 36.3189 | -121.1992 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0062030 | OH | Sus | 31693013 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | Yes | 1938875 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 985 | 20240504 | 520 | 20240504 | 705 | 2445480 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 2100 | 36.8521 | -121.7712 | No | Clear;32-90 F |  |  | 24-0061990 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1938846 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | FUSE | 96665 | 20240504 | 916 | 20240504 | 948 | 2445625 | 32 | Distribution Circuit | Vegetation | Tree - bark fell into line | 2 | 64 | 37.0054 | -121.9695 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0062024 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1938871 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | FUSE | 4447 | 20240504 | 1014 | 20240504 | 1045 | 2445672 | 31 | Distribution Circuit | Animal | Bird found | 30 | 930 | 36.7894 | -121.36 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0062046 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1938882 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 1871 | 20240504 | 1022 | 20240504 | 1150 | 2445685 | 88 | Distribution Circuit | Vegetation | Tree - bark fell into line | 29 | 2552 | 36.9559 | -121.8113 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 24-0062058 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1938890 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6645 | 20240504 | 1038 | 20240504 | 2112 | 2445697 | 634 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 8242 | 37.0118 | -121.7937 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0062074 | OH | Sus | 46238542 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1938896 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 6897 | 20240504 | 1224 | 20240504 | 1310 | 2445774 | 46 | Distribution Circuit | 3rd Party | Metallic Balloon | 65 | 2990 | 36.8561 | -121.7958 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 24-0062083 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1938900 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 11545 | 20240504 | 1253 | 20240504 | 1340 | 2445802 | 47 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 1189 | 36.8579 | -121.6938 | No | Clear;32-90 F |  |  | 24-0062092 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1938906 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 2341 | 20240504 | 1718 | 20240505 | 1841 | 2446023 | 1523 | Distribution Circuit | Equipment Failure/Involved | Underground | 10 | 14708 | 37.0427 | -122.0268 | No | Overcast-Drizzle;32-90 F | Connector or Splice (UG) | Failed/Faulted | 24-0062200 | UG | Sus | 46238546 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1938979 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 10449 | 20240505 | 834 | 20240505 | 1105 | 2446349 | 151 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 1057 | 37.1105 | -122.047 | No | Overcast-Drizzle;32-90 F | Anchor or Guy | Broken- wire on ground | 24-0062351 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | Yes | No | 1939115 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 3635 | 20240505 | 852 | 20240505 | 922 | 2446356 | 30 | Distribution Circuit | Company Initiated | Return Circuit Normal | 54 | 1588 | 36.9325 | -121.7869 | No | Partly Cloudy;32-90 F | Conductor- Underground | Normal | 24-0050722 | UG | Sus | 46220386 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1939097 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | SAN BENITO-2102 | 182742102 | FUSE | 250677 | 20240505 | 1109 | 20240505 | 1120 | 2446439 | 11 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 11 | 36.8389 | -121.5286 | No | Clear;32-90 F |  |  | 24-0062353 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1939117 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 764889 | 20240505 | 1512 | 20240505 | 1558 | 2446519 | 43 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 343 | 14749 | 37.0019 | -122.0376 | No | Clear;32-90 F |  |  | 24-0062394 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1939151 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 6875 | 20240506 | 553 | 20240506 | 655 | 2446668 | 62 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 103 | 6386 | 36.8864 | -121.6325 | No | Clear-Rain;32-90 F |  |  | 24-0062450 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1939204 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | TRANSFORMER | T2802 | 20240506 | 1522 | 20240507 | 233 | 2447347 | 671 | Distribution Circuit | Equipment Failure/Involved | Underground | 5 | 2026 | 36.787 | -121.6164 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0062803 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1939445 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 8195 | 20240507 | 704 | 20240507 | 750 | 2447582 | 46 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 966 | 36.6047 | -121.9397 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0062901 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1939523 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | OTHER | T2308 TWD J351 | 20240507 | 1003 | 20240507 | 1149 | 2447826 | 106 | Distribution Circuit | Equipment Failure/Involved | Underground | 7 | 277 | 36.7956 | -121.6682 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0062929 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1939635 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | SOQUEL-0402 | 83300402 | SWITCH | 816907 | 20240507 | 1233 | 20240507 | 1500 | 2447968 | 147 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 6615 | 36.9772 | -121.9546 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0063084 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1939678 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | BUENA VISTA-1106 | 182261106 | TRANSFORMER | 412337448432 | 20240508 | 821 | 20240508 | 1205 | 2448442 | 224 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 224 | 36.6357 | -121.6127 | No | Clear;32-90 F | Jumper | Broken | 24-0063463 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1939946 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2101 | 182492101 | TRANSFORMER | 412873055317 | 20240508 | 1125 | 20240508 | 1227 | 2448602 | 62 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 62 | 36.8281 | -121.4361 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0063666 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1940059 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 4525 | 20240508 | 1200 | 20240508 | 1427 | 2448855 | 147 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 294 | 36.8749 | -121.6424 | No | Clear;32-90 F |  |  | 24-0063763 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1940091 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 24915 | 20240508 | 1405 | 20240508 | 1450 | 2448999 | 45 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 45 | 36.7991 | -121.6983 | No | Clear;32-90 F |  |  | 24-0063801 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1940104 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 64823 | 20240508 | 1423 | 20240508 | 1535 | 2449020 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 216 | 36.9139 | -121.7412 | No | Clear;32-90 F |  |  | 24-0063824 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1940113 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | TRANSFORMER | 412070253016 | 20240508 | 1614 | 20240509 | 1130 | 2449015 | 1156 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1156 | 36.7598 | -121.7087 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0063866 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1940120 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 890827 | 20240508 | 1646 | 20240508 | 2154 | 2449140 | 308 | Distribution Circuit | Vegetation | Tree - grew into line | 29 | 8932 | 37.0411 | -122.0382 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0063876 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1940125 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DEL MONTE-2104 | 182222104 | FUSE | 4847 | 20240508 | 1932 | 20240509 | 859 | 2449230 | 807 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 11298 | 36.5458 | -121.7285 | No | Clear;32-90 F |  |  | 24-0063964 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1940182 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SOLEDAD-2105 | 182052105 | FUSE | 25005 | 20240508 | 2159 | 20240509 | 50 | 2449271 | 171 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 342 | 36.4852 | -121.4178 | No | Clear;32-90 F | Fuse | Broken | 24-0063968 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | None | 0 | No | No | No | 1940191 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | SWITCH | 330565 | 20240508 | 2249 | 20240509 | 205 | 2449291 | 196 | Distribution Circuit | Equipment Failure/Involved | Overhead | 114 | 22344 | 36.9726 | -122.1279 | No | Clear;32-90 F | Insulator | Broken | 24-0063815 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1940179 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | RECLOSER | 2204 | 20240509 | 624 | 20240509 | 846 | 2449389 | 118 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 250 | 34250 | 36.5568 | -121.8979 | No | Clear;32-90 F |  |  | 24-0051353 | OH | Sus | 35515354 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1940209 | 0 | EPSS Ckt | N | 2024 | SGF
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | TRANSFORMER | 316339915642 | 20240509 | 1200 | 20240509 | 1345 | 2449820 | 105 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 1785 | 36.9228 | -121.7531 | No | Clear;32-90 F | Secondary | Broken | 24-0064263 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1940426 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | SWITCH | 464844 | 20240509 | 1459 | 20240509 | 1854 | 2449899 | 235 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 7520 | 37.0157 | -121.82 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0064348 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1940448 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 23385 | 20240509 | 1917 | 20240510 | 1220 | 2450156 | 1023 | Distribution Circuit | Equipment Failure/Involved | Overhead | 88 | 12194 | 36.8434 | -121.6756 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0064475 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1940508 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRANSFORMER | 315463520387 | 20240509 | 2148 | 20240509 | 2352 | 2450199 | 124 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 1364 | 37.0493 | -122.0555 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0064471 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1940499 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | TRANSFORMER | 315485816901 | 20240509 | 2210 | 20240510 | 250 | 2450222 | 280 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 4480 | 36.953 | -122.0445 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0064478 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1940512 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 9813 | 20240510 | 538 | 20240510 | 1210 | 2450299 | 392 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 36 | 14112 | 36.861 | -121.6873 | No | Clear;32-90 F |  |  | 24-0064611 | OH | Sus | 31693753 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1940676 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | OCB | 1102/2 | 20240510 | 810 | 20240510 | 1301 | 2450371 | 291 | Distribution Circuit | Equipment Failure/Involved | Overhead | 653 | 117661 | 36.0734 | -120.9364 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0064557 | OH | Sus | 46245301 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1940573 | 0 | EPSS Ckt | N | 2024 | C GRD
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | SWITCH | 1483 | 20240510 | 1050 | 20240510 | 2143 | 2450791 | 653 | Distribution Circuit | Vegetation | Tree - grew into line | 18 | 11754 | 36.5606 | -121.9239 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0064560 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1940697 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 9485 | 20240510 | 1145 | 20240510 | 1341 | 2450848 | 116 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 3712 | 37.0125 | -122.0312 | No | Clear;32-90 F |  |  | 24-0064779 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1940742 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | TRANSFORMER | T0830 | 20240510 | 1323 | 20240510 | 1652 | 2450917 | 209 | Distribution Circuit | Equipment Failure/Involved | Underground | 61 | 3439 | 36.9764 | -121.9662 | No | Clear;32-90 F | Fuse | Burned Open | 24-0064817 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1940757 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | TRANSFORMER | 315526719134 | 20240510 | 1422 | 20240510 | 2145 | 2450982 | 443 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1329 | 37.0147 | -122.0328 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0064838 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1940767 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | TRIP-SAVER | 3571 | 20240510 | 2004 | 20240511 | 1450 | 2451195 | 1126 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 2250 | 36.723 | -121.7268 | No | Clear;32-90 F | Crossarm- Wood | Normal | 24-0064885 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1940793 | 1 | EPSS Ckt | N | 2024 | A
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 8853 | 20240511 | 51 | 20240511 | 856 | 2451258 | 485 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 2261 | 36.9631 | -121.8524 | No | Fog;32-90 F |  |  | 24-0064954 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1940866 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2101 | 182492101 | RECLOSER | 4792 | 20240511 | 617 | 20240511 | 1453 | 2451298 | 516 | Distribution Circuit | 3rd Party | Vehicle | 995 | 57366 | 36.8401 | -121.4082 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0064930 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1940846 | 0 | EPSS Ckt | N | 2024 | NA
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 9899 | 20240511 | 948 | 20240511 | 1248 | 2451407 | 180 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 52 | 9360 | 36.9284 | -121.7664 | No | Clear;32-90 F |  |  | 24-0065002 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1940904 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | T1739 | 20240511 | 953 | 20240512 | 442 | 2451414 | 1129 | Distribution Circuit | Equipment Failure/Involved | Underground | 7 | 4906 | 36.9672 | -121.8532 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0064980 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1940892 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 24425 | 20240511 | 1145 | 20240514 | 424 | 2451463 | 3879 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 12042 | 36.6786 | -121.7229 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0065045 | OH | Sus | 35552426 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1940918 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1101 | 182131101 | RECLOSER | 65704 | 20240511 | 1312 | 20240511 | 2102 | 2451495 | 470 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 7938 | 36.5271 | -121.4178 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0065017 | OH | Sus | 46245943 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1940908 | 0 | EPSS Ckt | N | 2024 | A&GRD
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | TRANSFORMER | 413091059920 | 20240511 | 1533 | 20240513 | 1110 | 2451611 | 2617 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 2617 | 36.9561 | -121.3657 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0065072 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1940942 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8345 | 20240511 | 1952 | 20240511 | 2213 | 2451711 | 141 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 1692 | 37.0568 | -121.9682 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0065084 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1940952 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | TRANSFORMER | 315749217514 | 20240512 | 1826 | 20240513 | 958 | 2452095 | 914 | Transformer only | Equipment Failure/Involved | Overhead | 22 | 20108 | 36.9715 | -121.9552 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0065203 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1941054 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 50899 | 20240513 | 234 | 20240513 | 804 | 2452279 | 330 | Distribution Circuit | Animal | Other | 3 | 879 | 36.8323 | -121.3483 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0065251 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1941105 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2102 | 182222102 | TRANSFORMER | 411638447872 | 20240513 | 817 | 20240513 | 914 | 2452385 | 57 | Transformer only | Equipment Failure/Involved | Overhead | 22 | 1254 | 36.6146 | -121.8503 | No | Overcast;32-90 F | Secondary | Deteriorated | 24-0065301 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1941161 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | KING CITY-1104 | 182031104 | FUSE | 9989 | 20240513 | 822 | 20240513 | 1454 | 2452504 | 392 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 3857 | 36.2066 | -121.1173 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0065326 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1941236 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | FUSE | 977577 | 20240513 | 947 | 20240513 | 1115 | 2452545 | 88 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 176 | 36.8489 | -121.4653 | No | Overcast-Fog;32-90 F | Anchor or Guy | Normal | 24-0065383 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1941297 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | JUMPER | COIS @ T3145 TWD T3146 | 20240514 | 2241 | 20240515 | 143 | 2453970 | 182 | Distribution Circuit | Equipment Failure/Involved | Underground | 66 | 12012 | 36.9063 | -121.7765 | No | Overcast-Fog;32-90 F | Transformer (UG) | Leaking | 24-0066027 | UG | Sus | 35553036 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1941706 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6671 | 20240515 | 825 | 20240515 | 1627 | 2454113 | 482 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 16388 | 36.9652 | -121.8484 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0066254 | OH | Sus | 46247153 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1941903 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | TRANSFORMER | 412100553720 | 20240515 | 1506 | 20240516 | 1153 | 2454049 | 1247 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1247 | 36.7783 | -121.7003 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0066514 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1941964 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 50999 | 20240515 | 1550 | 20240515 | 1730 | 2454582 | 100 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 200 | 36.9329 | -121.3643 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0066570 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1941976 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | BUENA VISTA-1102 | 182261102 | SWITCH | 3968 | 20240516 | 1309 | 20240516 | 1748 | 2460908 | 279 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 3069 | 36.6205 | -121.6428 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0066975 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1942150 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | FUSE | 3587 | 20240516 | 1807 | 20240517 | 126 | 2460938 | 439 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 878 | 36.7513 | -121.742 | No | Overcast;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0066985 | OH | Sus | 46247616 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1942157 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | FUSE | 9657 | 20240516 | 1915 | 20240517 | 259 | 2461021 | 464 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 3464 | 36.2615 | -121.1796 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0066991 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1942161 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 9989 | 20240516 | 2028 | 20240516 | 2258 | 2461046 | 150 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 1950 | 37.0186 | -121.8172 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0066999 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1942169 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | TRANSFORMER | 316666514755 | 20240517 | 520 | 20240517 | 650 | 2461190 | 90 | Transformer only | 3rd Party | Vehicle | 12 | 1080 | 36.8998 | -121.6409 | No | Overcast-Fog;32-90 F | Pole-Wood | Normal | 24-0067087 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1942242 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 23517 | 20240517 | 552 | 20240517 | 908 | 2461212 | 196 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 226 | 44296 | 36.7888 | -121.694 | No | Clear;32-90 F |  |  | 24-0067146 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1942333 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 6357 | 20240517 | 840 | 20240517 | 1354 | 2461408 | 314 | Distribution Circuit | Equipment Failure/Involved | Overhead | 101 | 31714 | 36.9018 | -121.8246 | No | Overcast;32-90 F | Jumper | Burned/flashed | 24-0067175 | OH | Sus | 31694439 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1942373 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | SWITCH | 6653 | 20240517 | 900 | 20240517 | 1155 | 2461411 | 175 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 525 | 37.0165 | -121.7906 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 24-0067134 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1942315 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1101 | 182131101 | TRANSFORMER | 412836044650 | 20240517 | 1230 | 20240517 | 1751 | 2461674 | 321 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 321 | 36.5351 | -121.4394 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0067347 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1942435 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6933 | 20240517 | 1632 | 20240517 | 1931 | 2461824 | 179 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 895 | 36.9296 | -121.7331 | No | Clear;32-90 F |  |  | 24-0067419 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1942464 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 6357 | 20240517 | 1653 | 20240517 | 1819 | 2461835 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 101 | 8686 | 36.9018 | -121.8246 | No | Clear;32-90 F |  |  | 24-0067410 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1942456 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | JUMPER | OJ SS OF CGC 413668335410 | 20240517 | 1727 | 20240517 | 2242 | 2461856 | 315 | Distribution Circuit | Vegetation | Tree - grew into line | 3 | 945 | 36.2856 | -121.1503 | No | Clear;32-90 F | Service conductor | Normal | 24-0067404 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1942451 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 4303 | 20240517 | 2344 | 20240518 | 947 | 2461986 | 603 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 3618 | 36.7265 | -121.7874 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0067445 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1942491 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 6721 | 20240518 | 255 | 20240518 | 608 | 2462011 | 193 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 83 | 16019 | 36.9342 | -121.7832 | No | Overcast-Fog;32-90 F |  |  | 24-0067456 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1942503 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | TRANSFORMER | 411947349938 | 20240518 | 908 | 20240518 | 1526 | 2462135 | 378 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 378 | 36.6731 | -121.7472 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0067485 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1942557 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | JUMPER | OJS 1 SP SS OF CGC 316280316018 | 20240518 | 1310 | 20240518 | 1919 | 2462223 | 369 | Distribution Circuit | Equipment Failure/Involved | Overhead | 44 | 16236 | 36.9331 | -121.7735 | No | Overcast;32-90 F | Pole-Wood | Deteriorated | 24-0067507 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1942571 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | TRANSFORMER | 411440345880 | 20240518 | 1412 | 20240518 | 2016 | 2462262 | 364 | Transformer only | Vegetation | Tree - cutting- PG&E contractor | 13 | 4732 | 36.5576 | -121.9164 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0067523 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1942574 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | FUSE | 1733 | 20240518 | 1549 | 20240518 | 1733 | 2462305 | 104 | Distribution Circuit | 3rd Party | Metallic Balloon | 4 | 416 | 36.5443 | -121.4945 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0067552 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1942592 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | TRANSFORMER | 412299351670 | 20240518 | 1550 | 20240518 | 1638 | 2462306 | 48 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 48 | 36.7235 | -121.6289 | No | Overcast;32-90 F |  |  | 24-0067547 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1942589 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | FUSE | 5191 | 20240518 | 1711 | 20240518 | 1821 | 2462343 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 140 | 36.7178 | -121.6232 | No | Overcast;32-90 F |  |  | 24-0067562 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1942598 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | RECLOSER | 3030 | 20240519 | 222 | 20240519 | 401 | 2462452 | 99 | Distribution Circuit | 3rd Party | Vehicle | 152 | 11898 | 36.5854 | -121.6002 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0067593 | OH | Sus | 35554142 | SOUTH BAY AND CENTRAL COAST | MAY | Three Phase Fault | 0 | No | No | No | 1942622 | 0 | EPSS Ckt | N | 2024 | ABC
CENTRAL COAST | KING CITY | OILFIELDS-1103 | 182391103 | FUSE | 9217 | 20240519 | 939 | 20240519 | 1113 | 2462537 | 94 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 940 | 35.8758 | -120.8871 | No | Partly Cloudy;32-90 F |  |  | 24-0067623 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1942659 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | BUENA VISTA-1103 | 182261103 | FUSE | 5115 | 20240519 | 1050 | 20240519 | 2237 | 2462561 | 707 | Distribution Circuit | Vegetation | Tree - branch fell on line | 216 | 152712 | 36.6527 | -121.6465 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0067624 | OH | Sus | 46249100 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | Yes | 1942660 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | SWITCH | 3067 | 20240519 | 1225 | 20240519 | 1234 | 2462607 | 9 | Distribution Circuit | Company Initiated | Return Circuit Normal | 28 | 252 | 36.5638 | -121.5195 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0067593 | OH | Sus | 35554142 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1942665 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | SWITCH | 3157 | 20240519 | 1245 | 20240519 | 1254 | 2462622 | 9 | Distribution Circuit | Company Initiated | Return Circuit Normal | 47 | 423 | 36.5127 | -121.5176 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0067593 | OH | Sus | 35554142 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1942669 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | FUSE | 53217 | 20240519 | 1643 | 20240519 | 1807 | 2462714 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 91 | 7371 | 36.9693 | -121.9812 | No | Clear;32-90 F |  |  | 24-0067653 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1942688 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 2689 | 20240519 | 1705 | 20240520 | 905 | 2462720 | 960 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 30720 | 37.1274 | -122.0181 | No | Clear;32-90 F |  |  | 24-0067786 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1942840 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 12425 | 20240519 | 1823 | 20240519 | 2032 | 2462736 | 129 | Distribution Circuit | 3rd Party | Metallic Balloon | 49 | 6321 | 36.9604 | -121.7649 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0067666 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1942697 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | RECLOSER | 5018 | 20240519 | 2039 | 20240520 | 1015 | 2462762 | 438 | Distribution Circuit | Equipment Failure/Involved | Overhead | 503 | 101188 | 36.7629 | -121.7347 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0067667 | OH | Sus | 46249006 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | Yes | 1942698 | 0 | Non-EPSS | N | 2024 | A/GRD
CENTRAL COAST | SALINAS | DOLAN ROAD-1104 | 182381104 | OCB | 1104/2 | 20240520 | 201 | 20240520 | 225 | 2462816 | 24 | Distribution Circuit | Equipment Failure/Involved | Overhead | 260 | 6240 | 36.8001 | -121.7691 | No | Partly Cloudy;32-90 F | Woodpin | Broken | 24-0067689 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1942724 | 0 | Non-EPSS | N | 2024 | N/A
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 412065454315 | 20240520 | 641 | 20240520 | 1936 | 2462881 | 775 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 3875 | 36.7947 | -121.7115 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0067879 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1942907 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 12453 | 20240520 | 703 | 20240520 | 850 | 2462897 | 107 | Distribution Circuit | 3rd Party | Metallic Balloon | 77 | 8266 | 36.9225 | -121.7475 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0067759 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1942793 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 24423 | 20240520 | 1047 | 20240520 | 2214 | 2463222 | 687 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1374 | 36.6778 | -121.7198 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0067944 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | Yes | 1942932 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 166904 | 20240520 | 1143 | 20240520 | 1318 | 2463278 | 95 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 243 | 23085 | 37.12 | -122.1208 | No | Clear;32-90 F |  |  | 24-0067925 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1942928 | 0 | EPSS Ckt | N | 2024 | C PHASE AND GRD AND SGF
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6769 | 20240520 | 2333 | 20240521 | 638 | 2463767 | 425 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 8075 | 36.8579 | -121.6469 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0068114 | OH | Sus | 46249520 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | Yes | Yes | 1943012 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 4995 | 20240520 | 2358 | 20240521 | 345 | 2463702 | 227 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 594 | 36.7715 | -121.7875 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0068106 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1943004 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | OTHER | J856 TWD T0493 | 20240521 | 125 | 20240521 | 426 | 2463858 | 181 | Distribution Circuit | Equipment Failure/Involved | Underground | 89 | 5285 | 36.8559 | -121.3888 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0068109 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1943014 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | FUSE | 11603 | 20240521 | 517 | 20240521 | 823 | 2463922 | 186 | Distribution Circuit | Animal | Bird found | 169 | 31434 | 36.9627 | -121.965 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Normal | 24-0068180 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1943075 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | BUENA VISTA-1106 | 182261106 | TRANSFORMER | 412418947652 | 20240521 | 1255 | 20240521 | 1715 | 2464257 | 260 | Transformer only | 3rd Party | Customer Equipment | 1 | 260 | 36.6146 | -121.584 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0068404 | OH | Sus | 35554961 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1943234 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | TRANSFORMER | 411498047553 | 20240521 | 2320 | 20240522 | 32 | 2464285 | 72 | Transformer only | Equipment Failure/Involved | Overhead | 26 | 1872 | 36.6047 | -121.898 | No | Clear;32-90 F | Transformer (OH) | Contaminated | 24-0068357 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1943219 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | KING CITY-1105 | 182031105 | FUSE | 9587 | 20240522 | 753 | 20240522 | 850 | 2464828 | 57 | Distribution Circuit | 3rd Party | Metallic Balloon | 65 | 3705 | 36.2172 | -121.1318 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 24-0068649 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1943406 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 4991 | 20240522 | 1745 | 20240522 | 2110 | 2465329 | 205 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 410 | 36.7621 | -121.7862 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 24-0068945 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1943554 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | SOLEDAD-2105 | 182052105 | OCB | 2105/2 | 20240522 | 1821 | 20240523 | 332 | 2465391 | 551 | Distribution Circuit | 3rd Party | Metallic Balloon | 697 | 71669 | 36.4297 | -121.3323 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0068969 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1943562 | 0 | EPSS Ckt | N | 2024 | C GRD TIME OC SET A
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 40457 | 20240522 | 2009 | 20240522 | 2104 | 2465456 | 55 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 1137 | 36.5513 | -121.9086 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0068998 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1943586 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 5533 | 20240522 | 2242 | 20240522 | 2321 | 2465504 | 39 | Distribution Circuit | 3rd Party | Vehicle | 100 | 3900 | 36.9874 | -121.9468 | No | Clear;32-90 F | Pole-Wood | Normal | 24-0069035 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1943619 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 12785 | 20240523 | 709 | 20240523 | 915 | 2465554 | 126 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 378 | 36.9552 | -121.7496 | No | Overcast;32-90 F |  |  | 24-0069117 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1943726 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | FUSE | 4811 | 20240523 | 808 | 20240523 | 1000 | 2465596 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 112 | 36.9361 | -121.4853 | No | Partly Cloudy;32-90 F |  |  | 24-0069143 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1943779 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | FUSE | 84523 | 20240523 | 837 | 20240524 | 610 | 2465636 | 1293 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 5172 | 36.4259 | -121.6777 | No | Clear;32-90 F |  |  | 24-0069370 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1943849 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | TRANSFORMER | 316102814786 | 20240523 | 1027 | 20240523 | 1944 | 2465828 | 557 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1114 | 36.8985 | -121.8339 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0069196 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1943797 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1103 | 182201103 | TRANSFORMER | 412498547919 | 20240523 | 1115 | 20240524 | 1147 | 2465867 | 1472 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1472 | 36.6225 | -121.5571 | No | Clear;32-90 F | Service conductor | Broken | 24-0069414 | OH | Sus | 31695142 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1943859 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 412004354280 | 20240523 | 1606 | 20240523 | 1720 | 2466106 | 74 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 148 | 36.793 | -121.7321 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0069376 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1943853 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | RECLOSER | 3032 | 20240523 | 1634 | 20240523 | 1741 | 2466128 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 109 | 7303 | 36.634 | -121.6988 | No | Clear;32-90 F |  |  | 24-0069408 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1943857 | 0 | EPSS Ckt | N | 2024 | SGF
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | FUSE | 24847 | 20240524 | 550 | 20240524 | 931 | 2466319 | 221 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 2431 | 36.5536 | -121.6936 | No | Clear;32-90 F |  |  | 24-0069617 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1944027 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 9113 | 20240524 | 753 | 20240524 | 850 | 2466422 | 57 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 323 | 36.866 | -121.4014 | No | Overcast;32-90 F |  |  | 24-0069590 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1943990 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1104 | 182381104 | JUMPER | OJ SS OF 3014 | 20240524 | 754 | 20240524 | 1034 | 2466383 | 160 | Distribution Circuit | Equipment Failure/Involved | Overhead | 142 | 22719 | 36.6964 | -121.7003 | No | Clear;32-90 F | Jumper | Burned Open | 24-0069538 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Open Circuit | 0 | No | No | No | 1943939 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | TRANSFORMER | 412992059666 | 20240524 | 833 | 20240524 | 1505 | 2466576 | 392 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 392 | 36.9483 | -121.3998 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0069765 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1944061 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | TRANSFORMER | 412047346053 | 20240524 | 1252 | 20240524 | 2031 | 2466676 | 459 | Transformer only | Vegetation | Tree - grew into line | 3 | 1377 | 36.5671 | -121.7096 | No | Clear;32-90 F | Conductor- Overhead | Arcing | 24-0069849 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1944086 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | DOLAN ROAD-1101 | 182381101 | JUMPER | OJ TO POS #1 C/OUT @ FUCO 6989 | 20240524 | 1908 | 20240524 | 2225 | 2467044 | 197 | Distribution Circuit | Equipment Failure/Involved | Overhead | 57 | 11229 | 36.831 | -121.7776 | No | Clear;32-90 F | Jumper | Burned Open | 24-0069917 | OH | Sus | 46251378 | SOUTH BAY AND CENTRAL COAST | MAY | Open Circuit | 0 | No | No | No | 1944117 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 12379 | 20240524 | 1913 | 20240524 | 2025 | 2466920 | 72 | Distribution Circuit | Equipment Failure/Involved | Underground | 7 | 504 | 36.9116 | -121.7673 | No | Partly Cloudy;32-90 F | Customer Equipment | Failed/Faulted | 24-0069912 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Three Phase Fault | 0 | No | No | No | 1944112 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 412001654427 | 20240524 | 2140 | 20240524 | 2245 | 2467047 | 65 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 650 | 36.797 | -121.7331 | No | Overcast;32-90 F | Transformer (OH) | Leaking | 24-0069918 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1944119 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 87067 | 20240524 | 2207 | 20240525 | 952 | 2467075 | 705 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 705 | 36.8744 | -121.746 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0069936 | OH | Sus | 35555964 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1944146 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | TRANSFORMER | 413132455133 | 20240524 | 2347 | 20240525 | 1010 | 2467081 | 623 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 623 | 36.8247 | -121.3477 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0069934 | OH | Sus | 35555872 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1944144 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1108 | 182011108 | FUSE | 23773 | 20240525 | 1500 | 20240526 | 56 | 2467541 | 596 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 3510 | 36.6758 | -121.6425 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0070028 | OH | Sus | 35555699 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1944227 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | BUENA VISTA-1104 | 182261104 | FUSE | 4609 | 20240525 | 1706 | 20240526 | 2039 | 2467633 | 1653 | Distribution Circuit | Equipment Failure/Involved | Underground | 215 | 4158 | 36.6533 | -121.6212 | No | Overcast;32-90 F | Conductor- Underground | Broken | 24-0070037 | UG | Sus | 46251800 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1944236 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | FUSE | 7109 | 20240526 | 12 | 20240526 | 1229 | 2467680 | 737 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 21373 | 36.1946 | -120.7075 | No | Clear;32-90 F |  |  | 24-0070057 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1944256 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2108 | 83252108 | FUSE | 11659 | 20240526 | 541 | 20240526 | 615 | 2467713 | 34 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 62 | 2108 | 36.9707 | -122.0275 | No | Partly Cloudy;32-90 F |  |  | 24-0070064 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1944263 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 6205 | 20240526 | 906 | 20240526 | 1151 | 2467757 | 165 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 165 | 36.9115 | -121.7467 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0070077 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1944273 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | FUSE | 9759 | 20240526 | 1424 | 20240526 | 1618 | 2467893 | 114 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 40 | 4560 | 36.3157 | -121.2443 | No | Clear;32-90 F |  |  | 24-0070127 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1944303 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | RECLOSER | 2020 | 20240527 | 658 | 20240528 | 2157 | 2468088 | 2339 | Distribution Circuit | Vegetation | Tree - branch fell on line | 841 | 192419 | 36.4632 | -121.7119 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0070175 | OH | Sus | 31695350 | SOUTH BAY AND CENTRAL COAST | MAY | Multi-Fault | 0 | No | Yes | No | 1944351 | 0 | EPSS Ckt | N | 2024 | AB PHASE AND SGF
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | TRANSFORMER | 316703014320 | 20240527 | 731 | 20240527 | 1541 | 2468126 | 490 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 490 | 36.8877 | -121.6284 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0070187 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1944362 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | TRANSFORMER | 315972817717 | 20240527 | 1011 | 20240527 | 1426 | 2468163 | 255 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 1785 | 36.9783 | -121.8796 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0070201 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1944371 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1101 | 182201101 | OTHER | HOT WIRE DOWN E/OF 20169 | 20240527 | 1544 | 20240528 | 131 | 2468338 | 587 | Distribution Circuit | 3rd Party | Metallic Balloon | 167 | 97165 | 36.5906 | -121.4538 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0070233 | OH | Sus | 31695324 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | Yes | 1944398 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | JUMPER | OJ @ 535285 | 20240527 | 1559 | 20240528 | 149 | 2468382 | 590 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 2159 | 36.3196 | -121.1814 | No | Clear;32-90 F | Jumper | Burned Open | 24-0070252 | OH | Sus | 46251856 | SOUTH BAY AND CENTRAL COAST | MAY | Open Circuit | 0 | No | No | No | 1944416 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | RECLOSER | 3030 | 20240527 | 1603 | 20240528 | 420 | 2468329 | 737 | Distribution Circuit | 3rd Party | Vehicle | 152 | 26081 | 36.5854 | -121.6002 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0070234 | OH | Sus | 35556141 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | Yes | No | 1944396 | 0 | EPSS Ckt | N | 2024 | BC GRD
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | TRANSFORMER | 413354937590 | 20240528 | 1021 | 20240528 | 1516 | 2468778 | 295 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 295 | 36.3444 | -121.2574 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0070585 | OH | Sus | 31695384 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1944667 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | TRANSFORMER | 412023652134 | 20240528 | 1111 | 20240528 | 1406 | 2468751 | 175 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 175 | 36.7339 | -121.7233 | No | Clear;32-90 F | Transformer | Burned/flashed | 24-0070486 | OH | Sus | 31695542 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1944622 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1101 | 182011101 | TRANSFORMER | 412233549813 | 20240528 | 1552 | 20240529 | 20 | 2469183 | 508 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 7620 | 36.6722 | -121.6499 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0070660 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1944688 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 5066 | 20240528 | 1757 | 20240528 | 2254 | 2469297 | 297 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 11583 | 37.1706 | -122.1655 | No | Clear;32-90 F |  |  | 24-0070711 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1944707 | 0 | EPSS Ckt | Y | 2024 | A & C PHSE
CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | FUSE | 7227 | 20240528 | 2128 | 20240529 | 610 | 2469400 | 522 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 2088 | 35.9778 | -121.2147 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0070733 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1944725 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | OCB | 1102/2 | 20240529 | 557 | 20240529 | 1516 | 2469471 | 559 | Distribution Circuit | 3rd Party | Vehicle | 6126 | 148815 | 36.7313 | -121.6135 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 24-0070775 | OH | Sus | 35556588 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1944764 | 0 | Non-EPSS | N | 2024 | TRIP TGT
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 12124 | 20240529 | 826 | 20240529 | 1003 | 2469566 | 97 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 478 | 22379 | 37.1677 | -122.1662 | No | Clear;32-90 F |  |  | 24-0070826 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1944818 | 0 | EPSS Ckt | Y | 2024 | A&B
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 1855 | 20240529 | 1300 | 20240529 | 1309 | 2469654 | 9 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 9 | 37.0369 | -122.1006 | No | Clear;32-90 F | Customer Equipment | Failed/Faulted | 24-0070960 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1944956 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | SWITCH | 10741 | 20240529 | 1958 | 20240529 | 2208 | 2470329 | 130 | Distribution Circuit | Equipment Failure/Involved | Underground | 5867 | 260610 | 36.9757 | -121.8946 | No | Clear;32-90 F | Connector or Splice (UG) | Failed/Faulted | 24-0071132 | UG | Sus | 46252839 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1945029 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | RECLOSER | 10260 | 20240529 | 2047 | 20240529 | 2143 | 2470417 | 56 | Distribution Circuit | Company Initiated | Coordination failure | 441 | 24696 | 36.9154 | -121.7787 | No | Clear;32-90 F | Recloser | Normal | 24-0071141 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1945037 | 0 | Non-EPSS | N | 2024 | SGF- & INST OC
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | JUMPER | 10797 | 20240529 | 2050 | 20240530 | 124 | s1945082 | 274 | Distribution Circuit | Equipment Failure/Involved | Overhead | 923 | 213667 | 36.9151 | -121.7777 | No | Clear;32-90 F | Switch (OH) | Burned/flashed | 24-0071141 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Open Circuit | 0 | No | No | No | 1945082 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | RECLOSER | 283170 | 20240530 | 718 | 20240530 | 1420 | 2470541 | 419 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2128 | 447156 | 36.8829 | -121.7979 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0071216 | OH | Sus | 46252906 | SOUTH BAY AND CENTRAL COAST | MAY | Multi-Fault | 0 | No | Yes | No | 1945101 | 0 | EPSS Ckt | N | 2024 | ABCGRD
CENTRAL COAST | SALINAS | SPENCE-1103 | 182201103 | FUSE | 933105 | 20240530 | 1444 | 20240531 | 255 | 2471079 | 731 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 3655 | 36.6377 | -121.5621 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0071587 | OH | Sus | 31695770 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1945331 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 8219 | 20240530 | 1650 | 20240530 | 2123 | 2470897 | 273 | Distribution Circuit | Vegetation | Tree - fell into line | 343 | 93639 | 36.9707 | -121.8976 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0071578 | OH | Sus | 46253166 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1945333 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | TRANSFORMER | 315868317688 | 20240530 | 1819 | 20240530 | 1934 | 2471222 | 75 | Transformer only | Equipment Failure/Involved | Overhead | 28 | 2100 | 36.9771 | -121.9155 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0071611 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1945344 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 10728 | 20240530 | 2031 | 20240530 | 2304 | 2471293 | 153 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1318 | 98703 | 37.0665 | -122.0797 | No | Clear;32-90 F |  |  | 24-0071629 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1945360 | 0 | EPSS Ckt | Y | 2024 | A & GRD
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 86399 | 20240530 | 2100 | 20240530 | 2226 | 2471297 | 86 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 516 | 36.7716 | -121.7907 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0071630 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1945361 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | SWITCH | 437 | 20240531 | 105 | 20240531 | 159 | 2471385 | 54 | Distribution Circuit | Company Initiated | Return Circuit Normal | 2417 | 128178 | 36.9224 | -121.7737 | No | Partly Cloudy-Fog;32-90 F | Switch (OH) | Burned/flashed | 24-0071141 | OH | Sus | 35556870 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1945400 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 3621 | 20240531 | 146 | 20240531 | 421 | 2471401 | 155 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 343 | 53165 | 36.7789 | -121.6493 | No | Clear;32-90 F |  |  | 24-0071687 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1945409 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | RECLOSER | 3010 | 20240531 | 716 | 20240531 | 1158 | 2471476 | 282 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 428 | 120696 | 36.28 | -121.3077 | No | Clear;32-90 F |  |  | 24-0071711 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1945421 | 0 | EPSS Ckt | Y | 2024 | A & C
CENTRAL COAST | HOLLISTER | PANOCHE-1103 | 253671103 | TRANSFORMER | 414562047517 | 20240531 | 750 | 20240531 | 1017 | 2471495 | 147 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 147 | 36.6212 | -120.8554 | No | Clear;32-90 F |  |  | 24-0071889 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | None | 0 | No | No | No | 1945582 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 23337 | 20240531 | 929 | 20240531 | 1155 | 2471647 | 146 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 584 | 36.7761 | -121.7853 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken | 24-0071787 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1945527 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 95871 | 20240531 | 1100 | 20240531 | 1316 | 2471737 | 136 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 272 | 37.0155 | -122.0286 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0071852 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1945554 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SOLEDAD-2102 | 182052102 | TRANSFORMER | 413144840559 | 20240531 | 1253 | 20240531 | 1715 | 2471851 | 262 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 524 | 36.4246 | -121.3314 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0071980 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1945618 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2105 | 182402105 | SWITCH | 9450 | 20240531 | 1303 | 20240531 | 2324 | 2471836 | 621 | Distribution Circuit | Equipment Failure/Involved | Overhead | 197 | 122337 | 36.6288 | -121.8351 | No | Clear;32-90 F | Switch (OH) | Arcing | 24-0071926 | OH | Sus | 31695943 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1945596 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 9284 | 20240531 | 1303 | 20240601 | 242 | 2471855 | 819 | Distribution Circuit | Equipment Failure/Involved | Underground | 5 | 4095 | 36.4485 | -121.802 | No | Clear;32-90 F | Elbow | Failed/Faulted | 24-0072012 | UG | Sus | 46253935 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1945622 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 555 | 20240531 | 1451 | 20240531 | 1541 | 2471975 | 50 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 92 | 4600 | 36.9641 | -121.9987 | No | Clear;32-90 F |  |  | 24-0072036 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1945631 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 7371 | 20240531 | 1609 | 20240601 | 1123 | 2472043 | 1154 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 6924 | 37.0585 | -122.142 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0072144 | OH | Sus | 46254044 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1945721 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | FUSE | 9857 | 20240531 | 1801 | 20240531 | 2158 | 2472121 | 237 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 4740 | 36.2979 | -121.1929 | No | Clear;32-90 F |  |  | 24-0072081 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1945653 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SOLEDAD-2102 | 182052102 | RECLOSER | 7008 | 20240531 | 1824 | 20240531 | 2046 | 2472135 | 142 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 98 | 13916 | 36.4058 | -121.3538 | No | Clear;32-90 F |  |  | 24-0072073 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1945650 | 0 | EPSS Ckt | Y | 2024 | B & C
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 2467 | 20240531 | 2026 | 20240531 | 2112 | 2472198 | 46 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 414 | 36.9376 | -121.8611 | No | Partly Cloudy;32-90 F |  |  | 24-0072094 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1945663 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SOLEDAD-2102 | 182052102 | FUSE | 7975 | 20240531 | 2102 | 20240601 | 835 | 2472263 | 693 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 15939 | 36.4025 | -121.3612 | No | Clear;32-90 F |  |  | 24-0072142 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1945715 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | OCB | 1102/2 | 20240601 | 1713 | 20240602 | 1419 | 2472685 | 1266 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1698 | 737834 | 37.1312 | -122.1723 | No | Clear;32-90 F |  |  | 24-0072225 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1945784 | 0 | EPSS Ckt | Y | 2024 | B-C INCST OC
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 39126 | 20240601 | 2240 | 20240602 | 21 | 2472986 | 101 | Distribution Circuit | Vegetation | Tree - branch fell on line | 384 | 38784 | 37.0778 | -122.1322 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0072280 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1945838 | 0 | EPSS Ckt | Y | 2024 | A/ GRD
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 6087 | 20240602 | 31 | 20240602 | 1300 | 2473035 | 749 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 14763 | 37.0665 | -122.0336 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0072286 | OH | Sus | 31696040 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | Yes | No | 1945848 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 10225 | 20240602 | 150 | 20240602 | 550 | 2473026 | 240 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 1680 | 37.0995 | -122.0494 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0072291 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1945857 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 9047 | 20240602 | 1207 | 20240602 | 1407 | 2473186 | 120 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 4560 | 36.6212 | -121.9135 | No | Overcast;32-90 F | Transformer (OH) | Broken | 24-0072330 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1945897 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | RECLOSER | 698634 | 20240602 | 1334 | 20240602 | 1555 | 2473210 | 107 | Distribution Circuit | Vegetation | Tree - branch fell on line | 123 | 13161 | 37.0954 | -122.0857 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0072329 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1945896 | 0 | EPSS Ckt | Y | 2024 | C-GRD
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | TRANSFORMER | 315209721186 | 20240602 | 2126 | 20240603 | 1105 | 2473402 | 819 | Transformer only | Vegetation | Tree - fell into line | 1 | 819 | 37.0704 | -122.143 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 24-0072372 | OH | Sus | 46254150 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | No | 1945928 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | DOLAN ROAD-1101 | 182381101 | FUSE | 10539 | 20240603 | 244 | 20240603 | 451 | 2473569 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 889 | 36.8381 | -121.7923 | No | Clear;32-90 F |  |  | 24-0072420 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1945980 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1101 | 182131101 | TRANSFORMER | 412870045310 | 20240603 | 841 | 20240603 | 1735 | 2473798 | 534 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1068 | 36.5533 | -121.428 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0072521 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1946131 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 922576 | 20240603 | 1249 | 20240603 | 1825 | 2474172 | 336 | Distribution Circuit | Vegetation | Tree - fell into line | 305 | 23571 | 37.0994 | -122.0532 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0072610 | OH | Sus | 46254690 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | No | 1946164 | 0 | EPSS Ckt | Y | 2024 | A & GRD
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | OTHER | J914 TWD T0644 | 20240603 | 1304 | 20240603 | 1346 | 2474180 | 42 | Distribution Circuit | Equipment Failure/Involved | Underground | 18 | 756 | 36.8316 | -121.3966 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0072602 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1946167 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | RECLOSER | 16010 | 20240603 | 1602 | 20240603 | 1854 | s1946222 | 172 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 266 | 31829 | 37.0886 | -122.0874 | No | Clear;32-90 F |  |  | 24-0072715 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1946222 | 0 | EPSS Ckt | Y | 2024 | A & C
CENTRAL COAST | HOLLISTER | SAN BENITO-2102 | 182742102 | TRANSFORMER | 412822056636 | 20240603 | 1911 | 20240603 | 2044 | 2474480 | 93 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 558 | 36.8632 | -121.4547 | No | Clear;32-90 F | Fuse | Burned Open | 24-0072775 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1946233 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | TRANSFORMER | 413101856400 | 20240603 | 2110 | 20240603 | 2257 | 2474522 | 107 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 107 | 36.8592 | -121.3589 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0072788 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1946246 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2102 | 182222102 | FUSE | 9064 | 20240604 | 555 | 20240604 | 705 | 2474609 | 70 | Distribution Circuit | Animal | Bird found | 47 | 3290 | 36.6043 | -121.8624 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 24-0072826 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1946264 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1104 | 182381104 | FUSE | 24943 | 20240604 | 909 | 20240604 | 1850 | 2474795 | 581 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 387 | 36.7548 | -121.7308 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0072954 | OH | Sus | 31696127 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1946438 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 4969 | 20240604 | 1220 | 20240604 | 1513 | 2475031 | 173 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 5363 | 36.8843 | -121.3204 | No | Clear;32-90 F | Insulator | Broken | 24-0073021 | OH | Sus | 31696235 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1946461 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SAN ARDO-1101 | 182191101 | FUSE | 7597 | 20240604 | 1420 | 20240604 | 1449 | 2475202 | 29 | Distribution Circuit | Animal | Other | 10 | 290 | 36.1107 | -121.0831 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0073146 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1946499 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | JUMPER | 10102 | 20240604 | 1825 | 20240604 | 1916 | 2475458 | 51 | Distribution Circuit | Company Initiated | Personnel- company | 177 | 9027 | 36.9873 | -121.921 | No | Clear;32-90 F | Switch (UG) | Normal | 24-0061658 | UG | Sus | 35352489 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1946563 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | TRANSFORMER | 413076856517 | 20240604 | 1848 | 20240604 | 2253 | 2475481 | 245 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 490 | 36.8619 | -121.3676 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0073309 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1946578 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 538096 | 20240605 | 254 | 20240605 | 442 | 2475745 | 108 | Distribution Circuit | Vegetation | Tree - branch fell on line | 987 | 106596 | 37.0578 | -122.0595 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0073363 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1946634 | 0 | EPSS Ckt | Y | 2024 | A- B- INST OC- & DCD
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | FUSE | 977577 | 20240605 | 1014 | 20240605 | 1115 | 2476105 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 122 | 36.8489 | -121.4653 | No | Clear;32-90 F |  |  | 24-0073569 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1946816 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1104 | 182381104 | FUSE | 24943 | 20240605 | 1400 | 20240605 | 1512 | 2476338 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 48 | 36.7548 | -121.7308 | No | Clear;32-90 F |  |  | 24-0073712 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1946883 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5239 | 20240605 | 1445 | 20240606 | 110 | 2476375 | 625 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 14982 | 37.0682 | -122.0827 | No | Clear;Above 90 | Conductor- Overhead | Broken- wire on ground | 24-0073751 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | No | 1946897 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 12760 | 20240605 | 1635 | 20240606 | 315 | 2476471 | 640 | Distribution Circuit | Equipment Failure/Involved | Overhead | 552 | 70122 | 37.0674 | -121.9966 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0073758 | OH | Sus | 35558596 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1946901 | 0 | EPSS Ckt | Y | 2024 | C GRD
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 7171 | 20240605 | 1738 | 20240605 | 1835 | 2476578 | 57 | Distribution Circuit | Vegetation | Tree - bark fell into line | 5 | 285 | 37.007 | -122.0095 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0073793 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1946923 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | TRANSFORMER | 412365551170 | 20240605 | 1747 | 20240606 | 1715 | 2476456 | 1408 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1408 | 36.7109 | -121.606 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0073783 | OH | Sus | 35558630 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1946914 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | RECLOSER | 4048 | 20240605 | 1834 | 20240606 | 1120 | 2476729 | 1006 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 124 | 12304 | 36.719 | -121.2811 | No | Clear;32-90 F |  |  | 24-0073799 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1946927 | 0 | EPSS Ckt | Y | 2024 | A&B INST
CENTRAL COAST | SALINAS | SALINAS-1102 | 182011102 | OCB | 1102/2 | 20240605 | 1929 | 20240606 | 846 | 2476859 | 797 | Distribution Circuit | Equipment Failure/Involved | Underground | 6908 | 249715 | 36.6828 | -121.6513 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 24-0073818 | UG | Sus | 35558612 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1946943 | 0 | Non-EPSS | N | 2024 | B PHASE & GRD
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | RECLOSER | 1132 | 20240606 | 217 | 20240606 | 1531 | 2477280 | 794 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 163 | 129422 | 36.3584 | -121.2034 | No | Clear;32-90 F |  |  | 24-0073930 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1947041 | 0 | Non-EPSS | Y | 2024 | B&C PHASE
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | SWITCH | 69550 | 20240606 | 932 | 20240606 | 1602 | 2477634 | 390 | Distribution Circuit | Vegetation | Tree - fell into line | 330 | 126995 | 37.1319 | -122.1095 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0074040 | OH | Sus | 31696273 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1947176 | 0 | EPSS Ckt | Y | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316467516420 | 20240606 | 1218 | 20240607 | 209 | 2477794 | 831 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1662 | 36.9448 | -121.71 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0074148 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1947232 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | FUSE | 10387 | 20240606 | 1235 | 20240606 | 2315 | 2477917 | 640 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 285 | 54104 | 36.9738 | -121.9623 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0074174 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1947243 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2108 | 83252108 | FUSE | 10063 | 20240606 | 1303 | 20240606 | 2344 | 2477948 | 641 | Distribution Circuit | 3rd Party | Vehicle | 48 | 28962 | 36.9712 | -122.0358 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0074202 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1947249 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | FUSE | 4201 | 20240606 | 1552 | 20240606 | 1652 | 2478137 | 60 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 1380 | 36.9076 | -121.4397 | No | Clear;32-90 F |  |  | 24-0074377 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1947309 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | SWITCH | 12955 | 20240606 | 1639 | 20240606 | 1735 | 2478222 | 56 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 51 | 2856 | 36.9886 | -122.0298 | No | Clear;32-90 F | Transformer (UG) | Normal | 24-0074354 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1947290 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 69550 | 20240606 | 1724 | 20240606 | 2130 | 2478316 | 246 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 330 | 81180 | 37.1319 | -122.1095 | No | Clear;32-90 F |  |  | 24-0074363 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1947298 | 0 | EPSS Ckt | Y | 2024 | B-C
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 12992 | 20240606 | 1944 | 20240607 | 1325 | 2478589 | 1061 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 697 | 739517 | 37.1991 | -122.1532 | No | Clear;32-90 F |  |  | 24-0074397 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1947324 | 0 | EPSS Ckt | Y | 2024 | B PHASE AND GRD
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | TRANSFORMER | 412170550118 | 20240606 | 1951 | 20240607 | 232 | 2478432 | 401 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 4411 | 36.6801 | -121.6717 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0074406 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1947328 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ERTA-0403 | 83510403 | FUSE | 12291 | 20240606 | 1958 | 20240606 | 2215 | 2478608 | 137 | Distribution Circuit | 3rd Party | Metallic Balloon | 72 | 9864 | 36.923 | -121.7599 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0074437 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1947353 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 2953 | 20240606 | 2153 | 20240607 | 1430 | 2478888 | 997 | Distribution Circuit | Animal | Bird found | 3 | 2991 | 37.1622 | -122.0815 | No | Clear;32-90 F | Fuse | Broken | 24-0074619 | OH | Sus | 31696335 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1947527 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | FUSE | 77559 | 20240607 | 23 | 20240607 | 131 | 2478766 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 476 | 36.7316 | -121.5992 | No | Overcast;32-90 F |  |  | 24-0074478 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1947388 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 10728 | 20240607 | 1007 | 20240607 | 1123 | 2479135 | 76 | Distribution Circuit | Animal | Bird found | 1318 | 43072 | 37.0665 | -122.0797 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0074613 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1947525 | 0 | EPSS Ckt | Y | 2024 | A-GRD
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 7691 | 20240607 | 1505 | 20240607 | 1931 | 2479479 | 266 | Distribution Circuit | Vegetation | Tree - branch fell on line | 134 | 35644 | 36.5817 | -121.8589 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0074835 | OH | Sus | 31696502 | SOUTH BAY AND CENTRAL COAST | JUN | Three Phase Fault | 0 | No | Yes | No | 1947596 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | FUSE | 9891 | 20240607 | 1507 | 20240607 | 2110 | 2479481 | 363 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 7506 | 35.9295 | -121.082 | No | Clear;32-90 F |  |  | 24-0074869 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1947621 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 974520 | 20240607 | 1611 | 20240608 | 1420 | 2479551 | 1329 | Distribution Circuit | Vegetation | Tree - fell into line | 316 | 82128 | 36.9908 | -121.8063 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0074825 | OH | Sus | 46257574 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | No | 1947590 | 0 | EPSS Ckt | N | 2024 | B-GRD
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | FUSE | 4837 | 20240607 | 2144 | 20240608 | 1434 | 2479791 | 1010 | Distribution Circuit | 3rd Party | Vehicle | 9 | 9090 | 36.8909 | -121.4227 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0074899 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Three Phase Fault | 0 | No | Yes | No | 1947652 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | TRANSFORMER | 411387043213 | 20240607 | 2232 | 20240607 | 2329 | 2479757 | 57 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 57 | 36.4835 | -121.931 | No | Partly Cloudy;32-90 F | Jumper | Broken | 24-0074903 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1947657 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 50877 | 20240608 | 810 | 20240608 | 844 | 2479927 | 34 | Distribution Circuit | Animal | Bird found | 13 | 442 | 36.9197 | -121.3418 | No | Overcast;32-90 F | Transformer (OH) | Normal | 24-0074932 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1947695 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | TRANSFORMER | 411785550657 | 20240608 | 825 | 20240608 | 1732 | 2479940 | 547 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 547 | 36.6919 | -121.8036 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0074943 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1947716 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | TRANSFORMER | 412812555560 | 20240608 | 957 | 20240608 | 1222 | 2480026 | 145 | Transformer only | Animal | Other | 1 | 145 | 36.8336 | -121.4574 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 24-0074963 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1947728 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | FUSE | 345541 | 20240608 | 1443 | 20240608 | 1625 | 2480203 | 102 | Distribution Circuit | 3rd Party | Metallic Balloon | 8 | 816 | 36.5097 | -121.4735 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0074998 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1947746 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 6639 | 20240608 | 1655 | 20240608 | 1809 | 2480252 | 74 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 2516 | 37.0075 | -121.809 | No | Overcast;32-90 F | Fuse | Broken | 24-0075007 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1947752 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6863 | 20240609 | 30 | 20240609 | 1135 | 2480367 | 665 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 10625 | 36.9822 | -121.8011 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0075067 | OH | Sus | 46257703 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | No | 1947822 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | RECLOSER | 3716 | 20240609 | 41 | 20240609 | 1026 | 2480369 | 585 | Distribution Circuit | Vegetation | Tree - branch fell on line | 449 | 82217 | 36.8245 | -121.6753 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0075048 | OH | Sus | 46257720 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | Yes | No | 1947799 | 0 | EPSS Ckt | N | 2024 | A & B
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | FUSE | 10239 | 20240609 | 109 | 20240609 | 1046 | 2480378 | 577 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 15002 | 36.9626 | -121.9865 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0075059 | OH | Sus | 46257702 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1947814 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315561521863 | 20240609 | 823 | 20240609 | 1334 | 2480448 | 311 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 311 | 37.0909 | -122.0225 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0075077 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1947837 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | FUSE | 9351 | 20240609 | 1019 | 20240609 | 1411 | 2480534 | 232 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 374 | 36.7891 | -121.3487 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0075103 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1947856 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 8419 | 20240609 | 1108 | 20240609 | 2216 | 2480577 | 668 | Distribution Circuit | Equipment Failure/Involved | Underground | 107 | 19897 | 36.5693 | -121.7917 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 24-0075115 | UG | Sus | 46257805 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1947861 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | SWITCH | 10162 | 20240609 | 1350 | 20240609 | 1449 | 2480605 | 59 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 590 | 36.9875 | -121.9216 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0073624 | OH | Sus | 35557943 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1947862 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 737 | 20240609 | 1801 | 20240609 | 2110 | 2480657 | 189 | Distribution Circuit | Vegetation | Tree - branch fell on line | 59 | 11151 | 37.0046 | -121.8551 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0075138 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1947881 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2101 | 182492101 | FUSE | 9951 | 20240609 | 1927 | 20240609 | 2032 | 2480682 | 65 | Distribution Circuit | Animal | Bird found | 25 | 1625 | 36.8361 | -121.4191 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0075136 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1947877 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | RECLOSER | 5394 | 20240610 | 201 | 20240610 | 1309 | 2480752 | 668 | Distribution Circuit | Vegetation | Tree - fell into line | 299 | 66985 | 36.9884 | -121.9697 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0075181 | OH | Sus | 46257727 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | Yes | No | 1947922 | 0 | EPSS Ckt | N | 2024 | B & C
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | RECLOSER | 975548 | 20240610 | 547 | 20240610 | 724 | 2480833 | 97 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2256 | 60902 | 36.6214 | -121.6846 | No | Clear;32-90 F |  |  | 24-0075191 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1947932 | 0 | EPSS Ckt | Y | 2024 | A-B SGF
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | FUSE | 24559 | 20240610 | 836 | 20240611 | 245 | 2481071 | 1089 | Distribution Circuit | 3rd Party | Vehicle | 3 | 3267 | 36.478 | -121.4106 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 24-0075256 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | Yes | 1948066 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SOLEDAD-2101 | 182052101 | RECLOSER | 775342 | 20240610 | 853 | 20240610 | 1354 | 2481096 | 301 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 301 | 36.4297 | -121.3318 | No | Partly Cloudy;32-90 F | Transformer (OH) | Arcing | 24-0075233 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1948013 | 0 | EPSS Ckt | N | 2024 | NA
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | RECLOSER | 648928 | 20240610 | 1038 | 20240610 | 1057 | 2481308 | 19 | Distribution Circuit | Company Initiated | Operating error | 1524 | 28956 | 36.5332 | -121.9152 | No | Partly Cloudy;32-90 F | Regulator | Normal | 24-0075285 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1948085 | 0 | EPSS Ckt | N | 2024 | SGF
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 11797 | 20240610 | 1623 | 20240610 | 1720 | 2481655 | 57 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 285 | 36.8677 | -121.7087 | No | Clear;32-90 F |  |  | 24-0075474 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1948162 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | RECLOSER | 258878 | 20240610 | 1921 | 20240610 | 2052 | 2481803 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 1456 | 36.2313 | -121.1769 | No | Clear;32-90 F |  |  | 24-0075502 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1948176 | 0 | EPSS Ckt | Y | 2024 | B- C- & INST OC
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 2077 | 20240611 | 733 | 20240611 | 1228 | 2481947 | 295 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1572 | 36.5808 | -121.9535 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0048063 | OH | Sus | 35125717 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1948448 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | PANOCHE-1103 | 253671103 | TRANSFORMER | 414614346769 | 20240611 | 920 | 20240611 | 1538 | 2482137 | 378 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 378 | 36.6037 | -120.8369 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0075758 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1948446 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411832553562 | 20240611 | 943 | 20240611 | 1159 | 2482182 | 136 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 136 | 36.7721 | -121.7901 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0075762 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1948450 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 4311 | 20240611 | 944 | 20240611 | 1144 | 2482183 | 120 | Distribution Circuit | Animal | Bird found | 38 | 4560 | 36.9142 | -121.753 | No | Partly Cloudy;32-90 F | Other | Normal | 24-0075751 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1948440 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | TRANSFORMER | 412641543478 | 20240611 | 1046 | 20240612 | 42 | 2482200 | 836 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 836 | 36.5012 | -121.5043 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0075731 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1948430 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 50073 | 20240611 | 1322 | 20240611 | 1337 | 2482400 | 15 | Distribution Circuit | Animal | Bird found | 7 | 100 | 36.8556 | -121.3988 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0075820 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1948467 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 36516 | 20240612 | 503 | 20240612 | 657 | 2483012 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 400 | 45280 | 37.0787 | -122.1336 | No | Clear;32-90 F |  |  | 24-0076051 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1948581 | 0 | EPSS Ckt | Y | 2024 | B&C PHASE
CENTRAL COAST | KING CITY | SOLEDAD-2105 | 182052105 | FUSE | 8709 | 20240612 | 517 | 20240612 | 735 | 2483015 | 138 | Distribution Circuit | Animal | Bird found | 6 | 828 | 36.4525 | -121.3575 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0076099 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1948598 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 3347 | 20240612 | 630 | 20240612 | 1306 | 2483034 | 396 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 5976 | 36.8707 | -121.6898 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0076143 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1948690 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | RECLOSER | 2768 | 20240612 | 722 | 20240612 | 742 | 2483067 | 20 | Distribution Circuit | Company Initiated | Operating error | 3270 | 65400 | 36.5029 | -121.759 | No | Clear;32-90 F | Recloser | Normal | 24-0076090 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Three Phase Fault | 0 | No | No | No | 1948594 | 0 | EPSS Ckt | N | 2024 | ABC
CENTRAL COAST | COAST | PAUL SWEET-2108 | 83252108 | TRANSFORMER | 315541517497 | 20240612 | 925 | 20240612 | 1503 | 2483417 | 338 | Transformer only | Equipment Failure/Involved | Overhead | 26 | 8788 | 36.9701 | -122.026 | No | Partly Cloudy;32-90 F | Secondary | Deteriorated | 24-0076225 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1948763 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | FUSE | 4447 | 20240612 | 1011 | 20240612 | 1037 | 2483499 | 26 | Distribution Circuit | Animal | Bird found | 30 | 780 | 36.7894 | -121.36 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0076205 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1948753 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 20379 | 20240612 | 1015 | 20240613 | 315 | 2483496 | 1020 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 3060 | 36.7886 | -121.688 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0076440 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1948832 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | JUMPER | BLOWN JMPR @ 8903 | 20240612 | 1044 | 20240612 | 1100 | 2483548 | 16 | Distribution Circuit | Equipment Failure/Involved | Overhead | 384 | 6144 | 37.0414 | -122.0284 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 24-0058442 | OH | Sus | 35207715 | SOUTH BAY AND CENTRAL COAST | JUN | Open Circuit | 0 | No | No | No | 1948754 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | KING CITY-1105 | 182031105 | SWITCH | 81553 | 20240612 | 1153 | 20240612 | 1650 | 2483595 | 297 | Distribution Circuit | 3rd Party | Vehicle | 591 | 175527 | 36.2186 | -121.1308 | No | Clear;32-90 F | Anchor or Guy | Broken | 24-0076221 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1948766 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | RECLOSER | 258688 | 20240612 | 1211 | 20240613 | 8 | 2483623 | 717 | Distribution Circuit | 3rd Party | Vehicle | 13 | 9321 | 36.2774 | -121.2298 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0076259 | OH | Sus | 35560155 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1948772 | 0 | EPSS Ckt | Y | 2024 | A&B
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | OCB | 2101/2 | 20240612 | 1229 | 20240612 | 2314 | 2483648 | 645 | Distribution Circuit | Vegetation | Tree - fell into line | 2334 | 216500 | 37.0953 | -122.1437 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0076269 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1948776 | 0 | EPSS Ckt | Y | 2024 | B-C-INST
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8903 | 20240612 | 1323 | 20240612 | 1335 | s1948818 | 12 | Distribution Circuit | Equipment Failure/Involved | Overhead | 60 | 719 | 37.0414 | -122.0284 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 24-0058442 | OH | Sus | 35207715 | SOUTH BAY AND CENTRAL COAST | JUN | Open Circuit | 0 | No | No | No | 1948818 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | RECLOSER | 502 | 20240612 | 1444 | 20240612 | 1657 | 2483789 | 133 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 163 | 21679 | 36.1289 | -121.0147 | No | Clear;32-90 F |  |  | 24-0076359 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1948804 | 0 | EPSS Ckt | Y | 2024 | A C INST OC
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | JUMPER | S PHSE OPEN JPR 2 W/OF 3019 | 20240613 | 1019 | 20240613 | 1253 | 2484556 | 154 | Distribution Circuit | Equipment Failure/Involved | Overhead | 57 | 8090 | 36.315 | -121.3106 | No | Clear;32-90 F | Jumper | Burned Open | 24-0076680 | OH | Sus | 46262958 | SOUTH BAY AND CENTRAL COAST | JUN | Open Circuit | 0 | No | No | No | 1949087 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS COCHES-1102 | 182151102 | FUSE | 8895 | 20240613 | 1500 | 20240613 | 2203 | 2484842 | 423 | Distribution Circuit | 3rd Party | Metallic Balloon | 18 | 7614 | 36.3894 | -121.2686 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0076886 | OH | Sus | 31697073 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | Yes | No | 1949146 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1109 | 182011109 | FUSE | 23279 | 20240614 | 715 | 20240614 | 835 | 2485215 | 80 | Distribution Circuit | 3rd Party | Vehicle | 4 | 320 | 36.6564 | -121.5867 | No | Overcast;32-90 F | Anchor or Guy | Normal | 24-0077008 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1949288 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | TRANSFORMER | 411899446170 | 20240614 | 934 | 20240614 | 1954 | 2485446 | 620 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 620 | 36.5703 | -121.7605 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0077099 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1949379 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | RECLOSER | 3092 | 20240614 | 2041 | 20240615 | 1655 | 2486042 | 1214 | Distribution Circuit | 3rd Party | Vehicle | 289 | 49496 | 36.4672 | -121.3913 | No | Clear;32-90 F | Anchor or Guy | Broken- wire on ground | 24-0077288 | OH | Sus | 31697236 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | No | 1949455 | 0 | EPSS Ckt | N | 2024 | B-C GRD
CENTRAL COAST | MONTEREY | FORT ORD-2107 | 182402107 | FUSE | 10291 | 20240614 | 2217 | 20240615 | 1312 | 2486154 | 895 | Distribution Circuit | 3rd Party | Vehicle | 2786 | 52540 | 36.6739 | -121.7806 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0077315 | OH | Sus | 35560813 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | Yes | 1949482 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 6809 | 20240615 | 452 | 20240615 | 856 | 2486239 | 244 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 185 | 45140 | 36.573 | -121.9271 | No | Partly Cloudy;32-90 F |  |  | 24-0077337 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1949507 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | TRANSFORMER | 316249714113 | 20240615 | 1415 | 20240615 | 1522 | 2486540 | 67 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 67 | 36.8804 | -121.7831 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0077392 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1949557 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | RECLOSER | 7014 | 20240615 | 1752 | 20240617 | 201 | 2486627 | 1929 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 106 | 204474 | 36.3875 | -121.0045 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0077405 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1949568 | 0 | Non-EPSS | N | 2024 | N/A
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 5300 | 20240615 | 1812 | 20240615 | 2003 | 2486684 | 111 | Distribution Circuit | Vegetation | Tree - branch fell on line | 919 | 74968 | 37.0383 | -122.0708 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0077411 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1949573 | 0 | EPSS Ckt | Y | 2024 | A-C
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | FUSE | 7027 | 20240616 | 545 | 20240616 | 1813 | 2486861 | 748 | Distribution Circuit | Animal | Other | 10 | 7484 | 36.165 | -120.8631 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0077512 | OH | Sus | 46264245 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1949665 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | OILFIELDS-1102 | 182391102 | RECLOSER | 93788 | 20240616 | 810 | 20240616 | 1443 | 2486899 | 393 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 100 | 12360 | 35.9567 | -120.851 | No | Clear;32-90 F |  |  | 24-0077451 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1949611 | 0 | EPSS Ckt | Y | 2024 | B & GRD
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | TRANSFORMER | 413538063847 | 20240616 | 1221 | 20240617 | 1441 | 2486970 | 1580 | Transformer only | Environmental/External | Fire- Forest/Grass | 3 | 4740 | 37.0668 | -121.2159 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0077479 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1949634 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | TRANSFORMER | 315282722743 | 20240616 | 1637 | 20240617 | 1117 | 2487092 | 1120 | Transformer only | Vegetation | Tree - fell into line | 2 | 2240 | 37.1141 | -122.117 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 24-0077548 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | No | 1949694 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 5300 | 20240616 | 1647 | 20240617 | 333 | 2487095 | 646 | Distribution Circuit | Vegetation | Tree - branch fell on line | 919 | 227803 | 37.0383 | -122.0708 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0077501 | OH | Sus | 31697503 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | Yes | No | 1949655 | 0 | EPSS Ckt | Y | 2024 | A & B
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 117818 | 20240616 | 1753 | 20240616 | 2214 | 2487142 | 261 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 6003 | 37.1248 | -122.1265 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0077515 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1949667 | 0 | EPSS Ckt | Y | 2024 | A-C
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 10214 | 20240616 | 1803 | 20240617 | 1128 | 2487147 | 1045 | Distribution Circuit | Vegetation | Tree - fell into line | 218 | 105593 | 37.0909 | -122.0439 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0077514 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1949666 | 0 | EPSS Ckt | Y | 2024 | C-GRD
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | RECLOSER | 16010 | 20240616 | 1818 | 20240617 | 125 | 2487155 | 427 | Distribution Circuit | Equipment Failure/Involved | Overhead | 889 | 76571 | 37.0886 | -122.0874 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0077518 | OH | Sus | 31697464 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1949670 | 0 | EPSS Ckt | Y | 2024 | A-GRD
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | TRANSFORMER | T826 | 20240616 | 1820 | 20240618 | 416 | 2487159 | 2036 | Distribution Circuit | Equipment Failure/Involved | Underground | 64 | 63222 | 36.596 | -121.8943 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0077863 | UG | Sus | 46264303 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1949969 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | RECLOSER | 64348 | 20240616 | 1849 | 20240616 | 2009 | 2487182 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 99 | 7920 | 36.3307 | -121.2258 | No | Clear;32-90 F |  |  | 24-0077522 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1949674 | 0 | Non-EPSS | Y | 2024 | A-B
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 3979 | 20240616 | 1947 | 20240617 | 1142 | 2487220 | 955 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 21010 | 37.0209 | -122.0097 | No | Clear;32-90 F |  |  | 24-0077553 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1949698 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6711 | 20240616 | 2206 | 20240617 | 1732 | 2487302 | 1166 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 58300 | 36.9982 | -121.8687 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0077555 | OH | Sus | 31697504 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | No | 1949700 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | RECLOSER | 2020 | 20240617 | 655 | 20240617 | 1425 | 2487404 | 450 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 841 | 298926 | 36.4632 | -121.7119 | No | Clear;32-90 F |  |  | 24-0077569 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1949716 | 0 | EPSS Ckt | Y | 2024 | A & C PHSE
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | TRANSFORMER | 412545848730 | 20240617 | 1122 | 20240617 | 1245 | 2487777 | 83 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 83 | 36.6453 | -121.5421 | No | Clear;32-90 F |  |  | 24-0077696 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1949887 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | RECLOSER | 944178 | 20240617 | 1215 | 20240618 | 231 | 2487696 | 856 | Distribution Circuit | Vegetation | Tree - fell into line | 889 | 27661 | 37.0926 | -122.0964 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0077685 | OH | Sus | 46264569 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | Yes | Yes | 1949873 | 0 | EPSS Ckt | N | 2024 | N/A
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 10214 | 20240617 | 1517 | 20240617 | 2210 | 2488060 | 413 | Distribution Circuit | Vegetation | Tree - fell into line | 218 | 43936 | 37.0909 | -122.0439 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0077779 | OH | Sus | 31697657 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | Yes | No | 1949922 | 0 | EPSS Ckt | Y | 2024 | A & B PHASE
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 95690 | 20240617 | 1602 | 20240617 | 1656 | 2488135 | 54 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2127 | 91911 | 37.1249 | -122.125 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0077805 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1949929 | 0 | EPSS Ckt | Y | 2024 | B & C PHASE
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | TRANSFORMER | 315711517604 | 20240617 | 1719 | 20240618 | 105 | 2488447 | 466 | Transformer only | Unknown Cause | Patrol - not conducted | 6 | 2796 | 36.9738 | -121.9684 | No | Clear;32-90 F |  |  | 24-0077867 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1949973 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | OILFIELDS-1102 | 182391102 | RECLOSER | 93788 | 20240617 | 1803 | 20240617 | 2127 | 2488530 | 204 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 100 | 12192 | 35.9567 | -120.851 | No | Clear;32-90 F |  |  | 24-0077848 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1949957 | 0 | EPSS Ckt | Y | 2024 | B-C
CENTRAL COAST | HOLLISTER | HOLLISTER-2101 | 182492101 | FUSE | 9929 | 20240617 | 1931 | 20240617 | 2010 | 2488585 | 39 | Distribution Circuit | Animal | Bird found | 23 | 883 | 36.8468 | -121.4127 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0077870 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1949975 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | KING CITY-1105 | 182031105 | SWITCH | 582221 | 20240617 | 2218 | 20240617 | 2230 | 2488721 | 12 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 12 | 36.2253 | -121.1346 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0077832 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1950021 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | KING CITY-1105 | 182031105 | JUMPER | OJ W OF CGC 3176 | 20240617 | 2256 | 20240618 | 315 | 2488722 | 259 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 259 | 36.2247 | -121.1361 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0077832 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1950022 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | RECLOSER | 5404 | 20240618 | 429 | 20240618 | 706 | 2488860 | 157 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 739 | 60298 | 37.0157 | -122.0254 | No | Clear;32-90 F |  |  | 24-0077937 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1950046 | 0 | EPSS Ckt | Y | 2024 | B-C
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | RECLOSER | 2624 | 20240618 | 550 | 20240618 | 747 | 2488869 | 117 | Distribution Circuit | Animal | Bird found | 5006 | 585702 | 36.569 | -121.7955 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0077949 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950048 | 0 | EPSS Ckt | N | 2024 | A-C GRD
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | TRANSFORMER | 414202241254 | 20240618 | 733 | 20240618 | 1752 | 2488928 | 619 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 619 | 36.4478 | -120.9785 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0078133 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950237 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 7797 | 20240618 | 816 | 20240618 | 1332 | 2489156 | 316 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 316 | 36.6293 | -121.9317 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0078196 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950254 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 9113 | 20240618 | 1143 | 20240618 | 1240 | 2489302 | 57 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 323 | 36.866 | -121.4014 | No | Clear;32-90 F |  |  | 24-0078159 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950247 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | TRANSFORMER | 414207541535 | 20240618 | 1154 | 20240618 | 2030 | 2489311 | 516 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 516 | 36.4553 | -120.981 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 24-0078153 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950243 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | TRANSFORMER | 412111549426 | 20240618 | 1349 | 20240618 | 2327 | 2489404 | 578 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 578 | 36.6605 | -121.691 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0078246 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950272 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | TRANSFORMER | 411450448203 | 20240618 | 1745 | 20240619 | 629 | 2489574 | 764 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 7640 | 36.6215 | -121.9156 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0078307 | OH | Sus | 35561687 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950296 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | KING CITY-1103 | 182031103 | TRANSFORMER | T0979 | 20240618 | 2127 | 20240619 | 934 | 2489659 | 727 | Transformer only | Company Initiated | Construction Activity/equip- company | 18 | 13086 | 36.2131 | -121.1392 | No | Partly Cloudy;32-90 F | Transformer (UG) | Normal | 24-0078432 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950438 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | PANOCHE-1103 | 253671103 | RECLOSER | 4008 | 20240619 | 9 | 20240619 | 1028 | 2489728 | 619 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 118 | 73042 | 36.6116 | -120.9293 | No | Clear;32-90 F |  |  | 24-0078359 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1950339 | 0 | EPSS Ckt | Y | 2024 | B-C
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | RECLOSER | 68454 | 20240619 | 731 | 20240619 | 832 | 2489802 | 61 | Distribution Circuit | Company Initiated | Personnel- company | 2504 | 152744 | 36.4832 | -121.7378 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0078382 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950361 | 0 | EPSS Ckt | Y | 2024 | SGF & DCD
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6793 | 20240619 | 831 | 20240619 | 949 | 2489856 | 78 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 234 | 36.9225 | -121.6794 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0078398 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1950386 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | RECLOSER | 491190 | 20240619 | 942 | 20240619 | 1613 | 2489947 | 391 | Distribution Circuit | Equipment Failure/Involved | Overhead | 808 | 82705 | 36.8008 | -121.7217 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0078428 | OH | Sus | 46265608 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | No | 1950433 | 0 | EPSS Ckt | N | 2024 | C/SGF/ INST OC
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | TRANSFORMER | 316290712804 | 20240619 | 1003 | 20240619 | 1615 | 2489875 | 372 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 372 | 36.8446 | -121.7687 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0078438 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950441 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | SWITCH | 5553BP | 20240619 | 1053 | 20240619 | 1328 | 2490006 | 155 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1085 | 36.9915 | -122.1653 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0078435 | OH | Sus | 46265535 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1950447 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | RECLOSER | 460414 | 20240619 | 1410 | 20240620 | 344 | 2490102 | 814 | Distribution Circuit | 3rd Party | Vehicle | 543 | 80999 | 36.7777 | -121.5971 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0078496 | OH | Sus | 31697751 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | No | 1950472 | 0 | Non-EPSS | N | 2024 | GRD & SGF
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 538096 | 20240619 | 1829 | 20240619 | 2050 | 2490230 | 141 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 987 | 139167 | 37.0578 | -122.0595 | No | Clear;32-90 F |  |  | 24-0078521 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1950485 | 0 | EPSS Ckt | Y | 2024 | B-C
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | TRANSFORMER | 412129948810 | 20240619 | 1953 | 20240620 | 210 | 2490267 | 377 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 377 | 36.6437 | -121.6837 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 24-0078526 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950489 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 412037455686 | 20240619 | 2024 | 20240620 | 1925 | 2490665 | 1381 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 4143 | 36.8316 | -121.7224 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0078610 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950574 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | RECLOSER | 2624 | 20240620 | 548 | 20240621 | 244 | 2490443 | 1256 | Distribution Circuit | Equipment Failure/Involved | Underground | 5006 | 151139 | 36.569 | -121.7955 | No | Overcast;32-90 F | Conductor- Underground | Deteriorated | 24-0078565 | UG | Sus | 31697455 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950531 | 0 | EPSS Ckt | N | 2024 | C & GRD
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | FUSE | 1377 | 20240620 | 640 | 20240620 | 1119 | 2490542 | 279 | Distribution Circuit | Animal | Bird found | 111 | 30969 | 36.5965 | -121.8589 | No | Overcast;32-90 F | Cutout- fuse holder | Broken | 24-0078592 | OH | Sus | 31697777 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1950561 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 12992 | 20240620 | 752 | 20240620 | 1057 | 2490612 | 185 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 697 | 67687 | 37.1991 | -122.1532 | No | Clear;32-90 F |  |  | 24-0078586 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950555 | 0 | EPSS Ckt | Y | 2024 | C & GRD
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | SWITCH | 469831 | 20240620 | 952 | 20240621 | 316 | 2490779 | 1044 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 5220 | 36.8252 | -121.7029 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0078676 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1950607 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | FUSE | 3481 | 20240620 | 1018 | 20240620 | 1147 | 2490722 | 89 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 445 | 36.5765 | -121.457 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0078634 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1950592 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | RECLOSER | 383718 | 20240620 | 1343 | 20240620 | 1700 | 2490902 | 197 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2256 | 262122 | 36.5788 | -121.7198 | No | Clear;32-90 F |  |  | 24-0078741 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950624 | 0 | EPSS Ckt | Y | 2024 | SGF & DCD
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | FUSE | 20153 | 20240620 | 1517 | 20240620 | 1649 | 2490980 | 92 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 188 | 17296 | 36.6019 | -121.6971 | No | Clear;32-90 F |  |  | 24-0078812 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950651 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | TRANSFORMER | T0695 | 20240620 | 1647 | 20240620 | 1920 | 2491039 | 153 | Transformer only | Unknown Cause | Patrol - found nothing | 10 | 1530 | 36.8147 | -121.4057 | No | Clear;32-90 F |  |  | 24-0078833 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1950665 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SOLEDAD-2102 | 182052102 | FUSE | 2061 | 20240621 | 157 | 20240621 | 1221 | 2491224 | 624 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 844 | 36.4056 | -121.3498 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Failed/Faulted | 24-0078893 | OH | Sus | 31697903 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1950727 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | TRANSFORMER | 412319351207 | 20240621 | 718 | 20240621 | 1915 | 2491314 | 717 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 5019 | 36.7109 | -121.622 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0079004 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950855 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 181438 | 20240621 | 856 | 20240621 | 1022 | 2491501 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 139 | 11954 | 37.1536 | -122.1621 | No | Clear;32-90 F |  |  | 24-0078979 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1950823 | 0 | EPSS Ckt | Y | 2024 | A/B
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | RECLOSER | 68454 | 20240621 | 904 | 20240621 | 942 | 2491516 | 38 | Distribution Circuit | Company Initiated | Personnel- company | 2223 | 84474 | 36.4832 | -121.7378 | No | Clear;32-90 F | Recloser | Normal | 24-0078986 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950836 | 0 | EPSS Ckt | Y | 2024 | SGF/DCD
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 316228018375 | 20240621 | 938 | 20240621 | 1002 | 2491583 | 24 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 48 | 36.9973 | -121.7927 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Failed/Faulted | 24-0078997 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1950853 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SOLEDAD-2101 | 182052101 | TRANSFORMER | 413206641372 | 20240621 | 941 | 20240621 | 1405 | 2491600 | 264 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 264 | 36.4471 | -121.3113 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 24-0079096 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950903 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DEL MONTE-2104 | 182222104 | JUMPER | JUMPERS 1/2 SPAN E/OF CGC# 412103842991 | 20240621 | 1250 | 20240621 | 1513 | 2491835 | 143 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 1573 | 36.5126 | -121.6873 | No | Clear;32-90 F | Insulator | Broken | 24-0079117 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1950910 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | TRANSFORMER | 412842645128 | 20240621 | 1347 | 20240621 | 2202 | 2491743 | 495 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 990 | 36.5476 | -121.4381 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0079197 | OH | Sus | 46267339 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950937 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 764889 | 20240621 | 1532 | 20240621 | 1820 | 2492024 | 168 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 343 | 57624 | 37.0019 | -122.0376 | No | Clear;32-90 F |  |  | 24-0079303 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950956 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | RECLOSER | 2012 | 20240622 | 25 | 20240622 | 420 | 2492225 | 235 | Distribution Circuit | Equipment Failure/Involved | Overhead | 493 | 115855 | 36.3306 | -121.8831 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0079307 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1950988 | 0 | EPSS Ckt | N | 2024 | N/A
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | RECLOSER | 68454 | 20240622 | 105 | 20240622 | 448 | 2492232 | 223 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2697 | 601431 | 36.4832 | -121.7378 | No | Clear;32-90 F |  |  | 24-0079346 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950993 | 0 | EPSS Ckt | Y | 2024 | SGF DCD
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | RECLOSER | 201311 | 20240622 | 159 | 20240622 | 659 | 2492241 | 300 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 167 | 50100 | 36.8682 | -121.5546 | No | Partly Cloudy;32-90 F |  |  | 24-0079350 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1950998 | 0 | EPSS Ckt | Y | 2024 | A-B
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | FUSE | 281488 | 20240622 | 241 | 20240622 | 429 | 2492255 | 108 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 216 | 36.8612 | -121.4349 | No | Clear;32-90 F |  |  | 24-0079353 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1951002 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 4549 | 20240622 | 858 | 20240622 | 1044 | 2492392 | 106 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 2118 | 36.7691 | -121.7616 | No | Clear;32-90 F |  |  | 24-0079387 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1951040 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 796388 | 20240622 | 1528 | 20240623 | 41 | 2492607 | 553 | Distribution Circuit | Equipment Failure/Involved | Overhead | 269 | 110543 | 36.9818 | -121.901 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0079439 | OH | Sus | 46267663 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | No | 1951071 | 0 | EPSS Ckt | N | 2024 | GRD & TIME OC
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | SWITCH | 2881 | 20240623 | 108 | 20240623 | 116 | s1951237 | 8 | Distribution Circuit | Company Initiated | Return Circuit Normal | 8 | 64 | 37.018 | -121.8957 | No | Clear;32-90 F | Connector or Splice (OH) | Normal | 24-0079439 | OH | Sus | 46267663 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1951237 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | RECLOSER | 383718 | 20240623 | 930 | 20240623 | 1013 | 2492933 | 43 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 711 | 30573 | 36.5788 | -121.7198 | No | Clear;32-90 F |  |  | 24-0079515 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1951142 | 0 | EPSS Ckt | Y | 2024 | A&B
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | SWITCH | 777828 | 20240623 | 1036 | 20240623 | 1122 | 2492949 | 46 | Distribution Circuit | Animal | Bird found | 1658 | 15033 | 36.9871 | -122.0358 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0079523 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Multi-Fault | 0 | No | No | No | 1951147 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | RECLOSER | 7070 | 20240623 | 1258 | 20240624 | 836 | 2492990 | 1178 | Distribution Circuit | 3rd Party | Customer Equipment | 260 | 81020 | 35.9644 | -121.1175 | No | Clear;32-90 F | Customer Equipment | Failed/Faulted | 24-0079537 | OH | Sus | 46267843 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1951159 | 0 | EPSS Ckt | Y | 2024 | A SGF
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 8157 | 20240623 | 1422 | 20240624 | 356 | 2493010 | 814 | Distribution Circuit | Equipment Failure/Involved | Underground | 3 | 2442 | 36.4098 | -121.9139 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0079557 | UG | Sus | 46267809 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1951176 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2107 | 182402107 | TRANSFORMER | 411834550268 | 20240624 | 618 | 20240624 | 2007 | 2493330 | 829 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 829 | 36.6815 | -121.7866 | No | Clear;32-90 F | Transformer | Deteriorated | 24-0079728 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1951390 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 12992 | 20240624 | 730 | 20240624 | 948 | 2493368 | 138 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 698 | 96324 | 37.1991 | -122.1532 | No | Clear;32-90 F |  |  | 24-0079635 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1951242 | 0 | EPSS Ckt | Y | 2024 | B&C
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 9609 | 20240624 | 730 | 20240624 | 829 | 2493367 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 354 | 36.9724 | -121.763 | No | Clear;32-90 F |  |  | 24-0079661 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1951295 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1108 | 182011108 | TRANSFORMER | T0242 | 20240624 | 747 | 20240624 | 1120 | 2493380 | 213 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 213 | 36.668 | -121.6374 | No | Clear;32-90 F |  |  | 24-0079749 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1951404 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 492378 | 20240624 | 1042 | 20240624 | 1213 | 2493690 | 91 | Distribution Circuit | Vegetation | Tree - branch fell on line | 107 | 9737 | 37.1244 | -122.1245 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0079722 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1951384 | 0 | EPSS Ckt | Y | 2024 | NA
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 50093 | 20240624 | 1146 | 20240624 | 1434 | 2493779 | 168 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 168 | 36.8608 | -121.3557 | No | Clear;32-90 F | Fuse | Broken | 24-0079799 | OH | Sus | 31698184 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1951434 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412281055428 | 20240624 | 1202 | 20240624 | 1517 | 2493795 | 195 | Transformer only | Vegetation | Tree - bark fell into line | 4 | 780 | 36.8271 | -121.639 | No | Clear;32-90 F | Secondary | Together | 24-0079886 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1951483 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | TRANSFORMER | 412428056868 | 20240624 | 1711 | 20240624 | 1747 | 2494520 | 36 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 36 | 36.8679 | -121.5898 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0079931 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1951513 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 9875 | 20240624 | 1753 | 20240624 | 1850 | 2494593 | 57 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 228 | 36.8601 | -121.7708 | No | Clear;32-90 F |  |  | 24-0079972 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1951544 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | TRANSFORMER | 316329713364 | 20240624 | 1908 | 20240625 | 106 | 2494667 | 358 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 358 | 36.8603 | -121.7556 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0079988 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1951555 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6785 | 20240625 | 1138 | 20240625 | 1224 | 2495397 | 46 | Distribution Circuit | 3rd Party | Metallic Balloon | 17 | 782 | 36.9175 | -121.6845 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0080333 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1951890 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 50845 | 20240625 | 1740 | 20240625 | 1855 | 2495760 | 75 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 300 | 36.9257 | -121.3551 | No | Clear;32-90 F |  |  | 24-0080543 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1951967 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 524397 | 20240625 | 1812 | 20240625 | 1920 | 2495909 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 204 | 36.8798 | -121.3638 | No | Clear;32-90 F |  |  | 24-0080547 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1951972 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | OILFIELDS-1103 | 182391103 | FUSE | 9219 | 20240625 | 2254 | 20240626 | 425 | 2495998 | 331 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 331 | 35.8705 | -120.8652 | No | Clear;32-90 F |  |  | 24-0080644 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1952030 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | FUSE | 5111 | 20240625 | 2330 | 20240626 | 1019 | 2496005 | 649 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 5841 | 36.6754 | -121.678 | No | Overcast-Fog;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0080617 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | Yes | 1952016 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | FUSE | 11603 | 20240626 | 29 | 20240626 | 455 | 2496012 | 266 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 169 | 44954 | 36.9627 | -121.965 | No | Partly Cloudy;32-90 F | Pole-Wood | Burned/flashed | 24-0080612 | OH | Sus | 46268642 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1952015 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SOLEDAD-2102 | 182052102 | RECLOSER | 858388 | 20240626 | 852 | 20240626 | 1242 | 2496456 | 230 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 116 | 26680 | 36.4021 | -121.3443 | No | Clear;32-90 F |  |  | 24-0080746 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1952151 | 0 | EPSS Ckt | Y | 2024 | B C INST OC
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | JUMPER | OJ 3 SPANS EAST OF CGC 414355525621 | 20240626 | 1105 | 20240626 | 1705 | 2496309 | 360 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 360 | 36.023 | -120.9071 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0080811 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1952198 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | RECLOSER | 549180 | 20240626 | 1331 | 20240626 | 1417 | 2496870 | 46 | Distribution Circuit | 3rd Party | Customer Equipment | 9 | 414 | 36.0057 | -121.2422 | No | Clear;Above 90 | Switch (OH) | Normal | 24-0080914 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Three Phase Fault | 0 | No | No | No | 1952227 | 0 | EPSS Ckt | Y | 2024 | ABC
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | OTHER | 117328 | 20240626 | 1429 | 20240626 | 2126 | 2496952 | 417 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 14940 | 36.8827 | -121.3274 | No | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0080953 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | Yes | 1952246 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | RECLOSER | 5144 | 20240626 | 1454 | 20240626 | 1629 | 2496977 | 95 | Distribution Circuit | Company Initiated | Coordination failure | 149 | 14155 | 37.0911 | -122.0774 | No | Clear;32-90 F | Recloser | Normal | 24-0080971 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1952251 | 0 | EPSS Ckt | Y | 2024 | SGF DCD
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 5947 | 20240626 | 1529 | 20240626 | 2120 | 2497000 | 351 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 702 | 36.9822 | -121.7387 | No | Clear;32-90 F |  |  | 24-0081085 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1952300 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | RECLOSER | 989608 | 20240626 | 1647 | 20240627 | 348 | 2497063 | 661 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 5288 | 36.6615 | -121.5473 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0081027 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1952263 | 0 | Non-EPSS | N | 2024 | FORCE OUT
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 6133 | 20240626 | 1717 | 20240626 | 1920 | 2497072 | 123 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 209 | 25707 | 36.9741 | -121.904 | No | Clear;32-90 F |  |  | 24-0081055 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1952279 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CASSERLY-0401 | 83110401 | SWITCH | 6381 | 20240626 | 1753 | 20240626 | 1817 | 2497096 | 24 | Distribution Circuit | Equipment Failure/Involved | Substation | 215 | 5160 | 36.9695 | -121.7667 | No | Clear;32-90 F | Insulator | Broken | 24-0080998 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1952270 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | ERTA-0404 | 83510404 | SWITCH | 5757 | 20240626 | 2042 | 20240626 | 2048 | 2497173 | 6 | Distribution Circuit | Equipment Failure/Involved | Substation | 215 | 1290 | 36.9563 | -121.765 | No | Clear;32-90 F | Insulator | Broken | 24-0080998 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1952288 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | TRANSFORMER | 316329115651 | 20240627 | 36 | 20240627 | 456 | 2497270 | 260 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 3120 | 36.9231 | -121.7568 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0081121 | OH | Sus | 35563237 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1952332 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | OILFIELDS-1103 | 182391103 | FUSE | 9219 | 20240627 | 1122 | 20240627 | 2213 | 2497664 | 651 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 650 | 35.8705 | -120.8652 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0081500 | OH | Sus | 31698353 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1952551 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | RECLOSER | 5144 | 20240627 | 1710 | 20240627 | 1911 | 2497923 | 121 | Distribution Circuit | Company Initiated | Coordination failure | 149 | 18029 | 37.0911 | -122.0774 | No | Clear;32-90 F | Recloser | Normal | 24-0081506 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1952555 | 0 | EPSS Ckt | Y | 2024 | SGF & DCD
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | TRANSFORMER | 315374621425 | 20240627 | 1744 | 20240627 | 2031 | 2497939 | 167 | Transformer only | Unknown Cause | Patrol - found nothing | 6 | 1002 | 37.0776 | -122.0864 | No | Clear;32-90 F |  |  | 24-0081539 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1952578 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | TRANSFORMER | 315473517128 | 20240627 | 1852 | 20240628 | 318 | 2497970 | 506 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 6072 | 36.9592 | -122.0491 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0081530 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1952572 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | TRANSFORMER | 411436246748 | 20240627 | 1935 | 20240627 | 2015 | 2497583 | 40 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 400 | 36.5814 | -121.9186 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 24-0081414 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1952529 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2101 | 182492101 | TRANSFORMER | 412928355152 | 20240627 | 2330 | 20240628 | 36 | 2498148 | 66 | Transformer only | Animal | Bird found | 4 | 264 | 36.824 | -121.4172 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0081618 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1952668 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | FUSE | 1843 | 20240628 | 420 | 20240628 | 606 | 2498207 | 106 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 636 | 36.4906 | -121.4278 | No | Partly Cloudy;32-90 F |  |  | 24-0081630 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1952676 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | OTHER | WIRE DOWN BETWEEN 6891 & 6685 | 20240628 | 710 | 20240628 | 1027 | 2498273 | 197 | Distribution Circuit | Equipment Failure/Involved | Overhead | 238 | 3734 | 36.8845 | -121.7956 | No | Overcast-Fog;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0081678 | OH | Sus | 46269599 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | Yes | 1952730 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | RECLOSER | 549180 | 20240628 | 757 | 20240628 | 954 | 2498296 | 117 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1053 | 36.0057 | -121.2422 | No | Clear;32-90 F |  |  | 24-0081665 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1952696 | 0 | EPSS Ckt | Y | 2024 | B- GRD- INST OC
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | FUSE | 65647 | 20240628 | 804 | 20240628 | 1148 | 2498303 | 224 | Distribution Circuit | 3rd Party | Vehicle | 28 | 3864 | 36.6176 | -121.9029 | No | Overcast-Fog;32-90 F | Bushing | Broken | 24-0081690 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1952742 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 12271 | 20240628 | 1045 | 20240628 | 1530 | 2498828 | 285 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 285 | 36.9366 | -121.7464 | No | Partly Cloudy;32-90 F |  |  | 24-0081918 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1952887 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | RECLOSER | 5144 | 20240628 | 1423 | 20240628 | 1505 | 2498784 | 42 | Distribution Circuit | Company Initiated | Coordination failure | 149 | 6258 | 37.0911 | -122.0774 | No | Clear;32-90 F | Recloser | Normal | 24-0081881 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1952882 | 0 | EPSS Ckt | Y | 2024 | SGF/DCD
CENTRAL COAST | SALINAS | SALINAS-1103 | 182011103 | FUSE | 20261 | 20240628 | 1522 | 20240628 | 2138 | 2498818 | 363 | Distribution Circuit | Equipment Failure/Involved | Underground | 40 | 11660 | 36.699 | -121.6683 | No | Clear;32-90 F | Elbow | Failed/Faulted | 24-0081911 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1952886 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | SWITCH | 7955BP | 20240628 | 1647 | 20240628 | 2059 | 2498915 | 252 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 7560 | 36.2781 | -121.162 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0081943 | OH | Sus | 46269494 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1952896 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | LAURELES-1112 | 182371112 | SWITCH | 3019 | 20240629 | 243 | 20240629 | 456 | 2499082 | 133 | Distribution Circuit | Equipment Failure/Involved | Overhead | 63 | 8135 | 36.529 | -121.7464 | No | Clear;32-90 F | Jumper | Broken | 24-0082000 | OH | Sus | 46270251 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1952942 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 10293 | 20240629 | 328 | 20240629 | 702 | 2499089 | 214 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 2996 | 36.8675 | -121.6212 | No | Clear;32-90 F |  |  | 24-0082009 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1952949 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | RECLOSER | 2760 | 20240629 | 505 | 20240629 | 511 | 2499098 | 6 | Distribution Circuit | Company Initiated | Return Circuit Normal | 62 | 372 | 36.5581 | -121.7506 | No | Clear;32-90 F | Jumper | Broken | 24-0082000 | OH | Sus | 46270251 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1952945 | 0 | EPSS Ckt | N | 2024 | N/A
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 3257 | 20240629 | 722 | 20240629 | 1546 | 2499132 | 504 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 4032 | 36.7804 | -121.7774 | No | Clear;32-90 F |  |  | 24-0082095 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1953017 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | RECLOSER | 3030 | 20240629 | 806 | 20240629 | 1834 | 2499165 | 628 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 152 | 29060 | 36.5854 | -121.6002 | No | Clear;32-90 F |  |  | 24-0082022 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1952962 | 0 | EPSS Ckt | Y | 2024 | A & B
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | JUMPER | 493 HIGH SIDE JUMPERS | 20240629 | 915 | 20240629 | 1117 | 2499235 | 122 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 3050 | 37.0865 | -122.0783 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0082032 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1952975 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | BUENA VISTA-1103 | 182261103 | OCB | 1103/2 | 20240629 | 952 | 20240629 | 1251 | 2499248 | 179 | Distribution Circuit | Equipment Failure/Involved | Overhead | 674 | 22998 | 36.654 | -121.6294 | No | Partly Cloudy;32-90 F | Insulator | Broken | 24-0082036 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1952979 | 0 | Non-EPSS | N | 2024 | N/A
CENTRAL COAST | MONTEREY | DEL MONTE-2102 | 182222102 | FUSE | 40621 | 20240629 | 1142 | 20240629 | 1208 | 2499298 | 26 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 832 | 36.6123 | -121.8524 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Arcing | 24-0082055 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1952990 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | TRANSFORMER | 412143150092 | 20240629 | 1252 | 20240629 | 1704 | 2499341 | 252 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 252 | 36.6791 | -121.6807 | No | Clear;32-90 F | Jumper | Broken | 24-0082068 | OH | Sus | 46270359 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1952999 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6595 | 20240629 | 1857 | 20240630 | 1106 | 2499533 | 969 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1938 | 36.9245 | -121.6964 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0082122 | OH | Sus | 31698880 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | No | 1953042 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | RECLOSER | 7030 | 20240629 | 1920 | 20240630 | 1250 | 2499499 | 1050 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 107 | 112350 | 36.2025 | -120.8432 | No | Clear;32-90 F |  |  | 24-0082118 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1953035 | 0 | EPSS Ckt | Y | 2024 | BC
CENTRAL COAST | SALINAS | SPENCE-1102 | 182201102 | FUSE | 356545 | 20240630 | 129 | 20240630 | 1125 | 2499655 | 596 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 10132 | 36.6266 | -121.4965 | No | Clear;32-90 F |  |  | 24-0082194 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1953108 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1103 | 182381103 | FUSE | 23721 | 20240630 | 409 | 20240630 | 541 | 2499583 | 92 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 184 | 36.7874 | -121.7817 | No | Clear;32-90 F |  |  | 24-0082156 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1953076 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 11044 | 20240630 | 1124 | 20240630 | 1350 | 2499734 | 73 | Distribution Circuit | Animal | Bird found | 2248 | 181405 | 37.0401 | -122.0297 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0082193 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1953107 | 0 | EPSS Ckt | Y | 2024 | B & GRD
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRANSFORMER | 315393721001 | 20240630 | 1125 | 20240630 | 1411 | 2499737 | 166 | Transformer only | Unknown Cause | Patrol - not conducted | 5 | 830 | 37.066 | -122.0796 | No | Clear;32-90 F |  |  | 24-0082212 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1953124 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 7427 | 20240630 | 1428 | 20240630 | 1727 | 2499802 | 179 | Distribution Circuit | Equipment Failure/Involved | Overhead | 144 | 25776 | 36.6001 | -121.8504 | No | Clear;32-90 F | Pothead(Riser Termination) | Failed/Faulted | 24-0082221 | OH | Sus | 46270504 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1953135 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | RECLOSER | 698634 | 20240630 | 1538 | 20240630 | 2243 | 2499882 | 425 | Distribution Circuit | Vegetation | Tree - bark fell into line | 123 | 22803 | 37.0954 | -122.0857 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0082222 | OH | Sus | 46270505 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1953136 | 0 | EPSS Ckt | Y | 2024 | A-GRD
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | JUMPER | WIRE DWN 4 SW/OF 5157 | 20240630 | 1639 | 20240630 | 2102 | 2499987 | 263 | Distribution Circuit | Vegetation | Tree - fell into line | 168 | 43824 | 37.083 | -122.09 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0082231 | OH | Sus | 46270506 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | No | 1953144 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 10728 | 20240630 | 1937 | 20240701 | 253 | 2500154 | 436 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1150 | 70280 | 37.0665 | -122.0797 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 24-0082241 | OH | Sus | 46270507 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1953154 | 0 | EPSS Ckt | Y | 2024 | AB
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 12590 | 20240630 | 1937 | 20240630 | 2038 | 2500158 | 61 | Distribution Circuit | Company Initiated | Coordination failure | 349 | 21289 | 37.0633 | -122.0798 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 24-0082242 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1953155 | 0 | EPSS Ckt | Y | 2024 | B GRD
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | RECLOSER | 42086 | 20240630 | 2147 | 20240701 | 1448 | 2500218 | 1021 | Distribution Circuit | 3rd Party | Vehicle | 179 | 48482 | 36.9036 | -121.7361 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 24-0082256 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | No | 1953169 | 0 | EPSS Ckt | N | 2024 | C GRD
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | RECLOSER | 78676 | 20240701 | 145 | 20240701 | 202 | 2500280 | 17 | Distribution Circuit | Equipment Failure/Involved | Overhead | 364 | 6188 | 36.5984 | -121.8492 | No | Overcast-Fog;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0082221 | OH | Sus | 46270504 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1953188 | 0 | EPSS Ckt | N | 2024 | N/A
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 10293 | 20240701 | 624 | 20240701 | 818 | 2500471 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1596 | 36.8675 | -121.6212 | No | Clear;32-90 F |  |  | 24-0082303 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1953210 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRANSFORMER | 315226324463 | 20240701 | 1448 | 20240701 | 1838 | 2500972 | 230 | Transformer only | Vegetation | Tree - branch fell on line | 5 | 1150 | 37.1608 | -122.1365 | No | Clear;32-90 F | Service conductor | Normal | 24-0082642 | OH | Sus | 46271153 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1953372 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5625 | 20240701 | 1826 | 20240701 | 1846 | 2501156 | 20 | Distribution Circuit | Vegetation | Tree - branch fell on line | 130 | 2600 | 37.105 | -122.0512 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0082697 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1953390 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 12518 | 20240701 | 1910 | 20240702 | 1002 | 2501193 | 892 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 618 | 551256 | 37.0791 | -122.0037 | No | Clear;32-90 F |  |  | 24-0082711 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1953397 | 0 | EPSS Ckt | Y | 2024 | B GRD
CENTRAL COAST | SALINAS | SALINAS-1105 | 182011105 | SWITCH | 21046 | 20240701 | 2249 | 20240702 | 359 | 2501414 | 310 | Distribution Circuit | Equipment Failure/Involved | Underground | 584 | 181040 | 36.7039 | -121.6057 | No | Partly Cloudy;32-90 F | Switch (UG) | Leaking | 24-0082709 | UG | Sus | 35564143 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1953429 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1105 | 182011105 | OTHER | J415 TWD T0515 | 20240702 | 7 | 20240702 | 435 | 2501423 | 268 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 268 | 36.7088 | -121.6383 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0082703 | UG | Sus | 35563943 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1953438 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | RECLOSER | 549180 | 20240702 | 407 | 20240702 | 704 | 2501509 | 177 | Distribution Circuit | 3rd Party | Customer Equipment | 9 | 1593 | 36.0057 | -121.2422 | No | Clear;32-90 F | Metering Equipment | Normal | 24-0082770 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1953465 | 0 | EPSS Ckt | Y | 2024 | A GRD
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 315473721362 | 20240702 | 926 | 20240702 | 2011 | 2501779 | 645 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1290 | 37.0763 | -122.0527 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0082978 | OH | Sus | 31698912 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1953597 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 11357 | 20240702 | 1014 | 20240702 | 1238 | 2501790 | 144 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 288 | 37.0902 | -121.9647 | No | Clear;32-90 F |  |  | 24-0083015 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1953605 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | RECLOSER | 88772 | 20240702 | 1739 | 20240703 | 225 | 2502602 | 526 | Distribution Circuit | 3rd Party | Vehicle | 1254 | 96412 | 36.904 | -121.6085 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0083200 | OH | Sus | 35564457 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | Yes | No | 1953670 | 0 | EPSS Ckt | Y | 2024 | A-B
CENTRAL COAST | MONTEREY | FORT ORD-2107 | 182402107 | RECLOSER | 36596 | 20240702 | 2216 | 20240703 | 1017 | 2503235 | 721 | Distribution Circuit | 3rd Party | Vehicle | 2857 | 149504 | 36.6736 | -121.7807 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0083349 | OH | Sus | 46271632 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1953774 | 0 | EPSS Ckt | N | 2024 | A GRD
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | RECLOSER | 22136 | 20240703 | 23 | 20240703 | 1725 | 2503334 | 1022 | Distribution Circuit | 3rd Party | Vehicle | 218 | 17597 | 36.5969 | -121.6245 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0083377 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | Yes | No | 1953801 | 0 | EPSS Ckt | Y | 2024 | BC
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | RECLOSER | 36982 | 20240703 | 721 | 20240703 | 1800 | 2503498 | 639 | Distribution Circuit | Equipment Failure/Involved | Overhead | 422 | 53419 | 36.5301 | -121.4747 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0083417 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Three Phase Fault | 0 | No | No | No | 1953855 | 0 | EPSS Ckt | Y | 2024 | A- B- C- & INST OC
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | RECLOSER | 2020 | 20240703 | 758 | 20240703 | 804 | 2503485 | 6 | Distribution Circuit | Vegetation | Tree - branch fell on line | 841 | 5046 | 36.4632 | -121.7119 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0083425 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1953863 | 0 | EPSS Ckt | N | 2024 | NONE
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | TRANSFORMER | 412625756458 | 20240703 | 825 | 20240703 | 956 | 2503570 | 91 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 91 | 36.8571 | -121.5216 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0083489 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1953900 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | TRANSFORMER | 413163050775 | 20240703 | 1352 | 20240703 | 1639 | 2503854 | 167 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 167 | 36.7055 | -121.3327 | No | Clear;32-90 F |  |  | 24-0083742 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1953957 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | JUMPER | #2 POTHEAD BLOWN | 20240703 | 1421 | 20240703 | 2006 | 2504073 | 345 | Distribution Circuit | Equipment Failure/Involved | Overhead | 59 | 13281 | 36.761 | -121.7388 | No | Clear;32-90 F | Pothead(Riser Termination) | Failed/Faulted | 24-0083750 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Open Circuit | 0 | No | No | No | 1953962 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | SWITCH | 3067 | 20240703 | 1732 | 20240703 | 1741 | 2504164 | 9 | Distribution Circuit | Company Initiated | Return Circuit Normal | 18 | 162 | 36.5638 | -121.5195 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0083377 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1953975 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | SWITCH | 21039 | 20240703 | 1759 | 20240703 | 1825 | 2504176 | 26 | Distribution Circuit | Company Initiated | Return Circuit Normal | 91 | 1574 | 36.498 | -121.501 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0083377 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1953976 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | RECLOSER | 549180 | 20240704 | 1003 | 20240704 | 1115 | 2504891 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 648 | 36.0057 | -121.2422 | No | Clear;32-90 F |  |  | 24-0083971 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954124 | 0 | EPSS Ckt | Y | 2024 | A PHASE AND GRD
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 7427 | 20240704 | 1009 | 20240704 | 1119 | 2504898 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 144 | 10080 | 36.6001 | -121.8504 | No | Clear;32-90 F |  |  | 24-0083983 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1954129 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRANSFORMER | 315501021670 | 20240704 | 1049 | 20240704 | 1314 | 2504963 | 145 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 145 | 37.0845 | -122.0434 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0083982 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954128 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 12992 | 20240704 | 1230 | 20240704 | 2041 | 2505029 | 491 | Distribution Circuit | 3rd Party | Vehicle | 698 | 119794 | 37.1991 | -122.1532 | No | Clear;Above 90 | Pole-Wood | Broken | 24-0084007 | OH | Sus | 35564698 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1954142 | 0 | EPSS Ckt | Y | 2024 | A & B
CENTRAL COAST | SALINAS | INDUSTRIAL ACRES-0412 | 182300412 | TRANSFORMER | 412343850285 | 20240704 | 1400 | 20240704 | 1451 | 2505093 | 51 | Transformer only | 3rd Party | Metallic Balloon | 14 | 714 | 36.6859 | -121.6128 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0084064 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954166 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 10719 | 20240704 | 1412 | 20240704 | 1857 | 2505092 | 285 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2280 | 37.0863 | -122.1043 | No | Clear;Above 90 | Conductor- Overhead | Broken- wire on ground | 24-0084066 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1954167 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | RECLOSER | 549180 | 20240704 | 1507 | 20240704 | 1607 | 2505165 | 60 | Distribution Circuit | 3rd Party | Customer Equipment | 9 | 540 | 36.0057 | -121.2422 | No | Clear;Above 90 | Customer Equipment | Normal | 24-0084045 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Three Phase Fault | 0 | No | No | No | 1954157 | 0 | EPSS Ckt | Y | 2024 | ABC PHASE
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | TRANSFORMER | 315961019330 | 20240704 | 1612 | 20240705 | 1042 | 2505495 | 1110 | Transformer only | Vegetation | Tree - fell into line | 1 | 1110 | 37.0222 | -121.8847 | No | Partly Cloudy;32-90 F | Service conductor | Broken- wire on ground | 24-0084168 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954253 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-1101 | 182221101 | OTHER | WIRE DOWN 1 N/O 10151 | 20240704 | 2100 | 20240705 | 159 | s1954210 | 299 | Distribution Circuit | Equipment Failure/Involved | Overhead | 49 | 13701 | 36.619 | -121.8271 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0084128 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | Yes | 1954210 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | RECLOSER | 549180 | 20240705 | 200 | 20240705 | 439 | 2505644 | 159 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1431 | 36.0057 | -121.2422 | No | Clear;32-90 F |  |  | 24-0084181 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954266 | 0 | EPSS Ckt | Y | 2024 | A&GRD
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | TRANSFORMER | 315870518348 | 20240705 | 936 | 20240705 | 1454 | 2505869 | 318 | Transformer only | Equipment Failure/Involved | Electrical Overload | 9 | 2862 | 36.9954 | -121.9144 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0084288 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954325 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2107 | 182402107 | JUMPER | FAIL BUMP 1 SPAN N/OF CGC 411812350210 | 20240705 | 1241 | 20240705 | 1549 | 2506061 | 188 | Distribution Circuit | Equipment Failure/Involved | Overhead | 717 | 119192 | 36.6799 | -121.7935 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0084328 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Open Circuit | 0 | No | No | No | 1954351 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | T1323 | 20240705 | 1247 | 20240706 | 119 | 2505910 | 752 | Distribution Circuit | Equipment Failure/Involved | Underground | 4 | 3008 | 36.8011 | -121.6657 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0084316 | UG | Sus | 35564882 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954345 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | FUSE | 23843 | 20240705 | 1302 | 20240706 | 1358 | 2506041 | 1496 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 4488 | 36.7221 | -121.6785 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 24-0084375 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1954376 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 11054 | 20240705 | 1402 | 20240705 | 1556 | 2506101 | 114 | Distribution Circuit | Vegetation | Tree - branch fell on line | 309 | 35226 | 36.9775 | -121.7415 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0084340 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1954358 | 0 | EPSS Ckt | Y | 2024 | A- C- & INST OC
CENTRAL COAST | KING CITY | LOS COCHES-1101 | 182151101 | TRANSFORMER | 413176237496 | 20240705 | 1436 | 20240705 | 1716 | 2506135 | 160 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 160 | 36.3409 | -121.3184 | No | Clear;Above 90 | Pole-Wood | Deteriorated | 24-0084354 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1954362 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1112 | 182371112 | TRANSFORMER | T0812 | 20240705 | 1515 | 20240706 | 1153 | 2506154 | 1238 | Distribution Circuit | Equipment Failure/Involved | Underground | 4 | 4952 | 36.4791 | -121.7288 | No | Clear;32-90 F | Elbow | Failed/Faulted | 24-0084561 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954513 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | TRANSFORMER | 315359121886 | 20240705 | 1552 | 20240705 | 2057 | 2506243 | 305 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 610 | 37.0904 | -122.0913 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0084399 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954385 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | TRANSFORMER | 412976456384 | 20240705 | 1651 | 20240705 | 2140 | 2506297 | 289 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1156 | 36.858 | -121.4019 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0084408 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954389 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | RECLOSER | 4042 | 20240705 | 1802 | 20240705 | 2046 | 2506454 | 164 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 264 | 38714 | 36.8611 | -121.3623 | No | Clear;Above 90 |  |  | 24-0084414 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1954392 | 0 | EPSS Ckt | Y | 2024 | A-C
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | FUSE | 55025 | 20240705 | 1934 | 20240706 | 1135 | 2506571 | 961 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 491 | 131315 | 36.8269 | -121.3819 | No | Clear;32-90 F |  |  | 24-0084472 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954443 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | TRANSFORMER | 315855717742 | 20240705 | 2126 | 20240706 | 1036 | 2506583 | 790 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 5530 | 36.9785 | -121.9198 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0084464 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954435 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | RECLOSER | 4060 | 20240705 | 2308 | 20240706 | 7 | 2507222 | 59 | Distribution Circuit | Company Initiated | Personnel- company | 1003 | 59177 | 36.801 | -121.3379 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0084490 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954463 | 0 | EPSS Ckt | Y | 2024 | GRD
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | TRANSFORMER | 411779150195 | 20240706 | 15 | 20240706 | 1912 | 2507242 | 1137 | Transformer only | Equipment Failure/Involved | Overhead | 19 | 21603 | 36.6791 | -121.8055 | No | Partly Cloudy;32-90 F | Transformer | Deteriorated | 24-0084503 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954478 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0422 | 182440422 | FUSE | 2581 | 20240706 | 555 | 20240706 | 851 | 2507303 | 176 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 5685 | 36.5918 | -121.9454 | No | Partly Cloudy;32-90 F |  |  | 24-0084531 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954501 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | TRANSFORMER | T0547 | 20240706 | 1247 | 20240706 | 1950 | 2507580 | 423 | Distribution Circuit | Equipment Failure/Involved | Underground | 19 | 8037 | 36.8256 | -121.3704 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 24-0084613 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954530 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | SWITCH | 4908 | 20240706 | 1950 | 20240706 | 2009 | 2508316 | 19 | Distribution Circuit | 3rd Party | Other | 589 | 11191 | 36.8837 | -121.4167 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0084710 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954610 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | KING CITY-1103 | 182031103 | RECLOSER | 7038 | 20240707 | 347 | 20240707 | 1145 | 2508669 | 478 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 796 | 380488 | 36.1935 | -121.1442 | No | Clear;32-90 F |  |  | 24-0084803 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954701 | 0 | EPSS Ckt | Y | 2024 | SGF & DCD ALARM
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | RECLOSER | 88772 | 20240707 | 557 | 20240707 | 1350 | 2508720 | 473 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1254 | 149392 | 36.904 | -121.6085 | No | Partly Cloudy;32-90 F |  |  | 24-0084810 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1954709 | 0 | EPSS Ckt | Y | 2024 | B C
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | FUSE | 25503 | 20240707 | 1220 | 20240707 | 1343 | 2508912 | 83 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 221 | 36.5297 | -121.4742 | No | Clear;32-90 F |  |  | 24-0084872 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954748 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 4439 | 20240708 | 14 | 20240708 | 123 | 2509638 | 69 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 207 | 36.7754 | -121.6769 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0085039 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1954885 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 2463 | 20240708 | 55 | 20240708 | 947 | 2509586 | 532 | Distribution Circuit | Equipment Failure/Involved | Overhead | 45 | 4811 | 36.9345 | -121.8615 | No | Partly Cloudy-Fog;32-90 F | Crossarm- Wood | Burned/flashed | 24-0085036 | OH | Sus | 31699233 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1954883 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | INTERRUPTER | 977600 | 20240708 | 329 | 20240708 | 559 | 2509724 | 150 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 254 | 38100 | 36.9801 | -121.9084 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0085054 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954905 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | RECLOSER | 88772 | 20240708 | 541 | 20240708 | 646 | 2509776 | 65 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1254 | 81510 | 36.904 | -121.6085 | No | Partly Cloudy-Fog;32-90 F | Connector or Splice (OH) | Broken | 24-0085055 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1954906 | 0 | EPSS Ckt | Y | 2024 | B-C
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | RECLOSER | 7002 | 20240708 | 643 | 20240708 | 838 | 2509796 | 115 | Distribution Circuit | Animal | Bird found | 139 | 15985 | 35.9663 | -121.1146 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0085069 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954914 | 0 | EPSS Ckt | N | 2024 | B PHASE INST OC
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | FUSE | 24163 | 20240708 | 644 | 20240708 | 940 | 2509885 | 176 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 176 | 36.528 | -121.4737 | No | Partly Cloudy;32-90 F |  |  | 24-0085149 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1955015 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 10293 | 20240708 | 654 | 20240708 | 1234 | 2509833 | 340 | Distribution Circuit | Equipment Failure/Involved | Overhead | 94 | 30040 | 36.8675 | -121.6212 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0085087 | OH | Sus | 46273169 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1954924 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | RECLOSER | 648928 | 20240708 | 702 | 20240708 | 811 | 2509806 | 69 | Distribution Circuit | Company Initiated | Personnel- company | 1522 | 105018 | 36.5332 | -121.9152 | No | Partly Cloudy-Fog;32-90 F | Bus | Normal | 24-0085078 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954916 | 0 | EPSS Ckt | Y | 2024 | SGF/DCD
CENTRAL COAST | SALINAS | SOLEDAD-2105 | 182052105 | TRANSFORMER | 412921642596 | 20240708 | 1312 | 20240708 | 1707 | 2510402 | 235 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 235 | 36.4792 | -121.4092 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 24-0085261 | OH | Sus | 46273524 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1955076 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | T0590 | 20240708 | 1322 | 20240709 | 222 | 2510233 | 780 | Transformer only | Equipment Failure/Involved | Underground | 1 | 780 | 36.944 | -121.7937 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0085227 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1955062 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | RECLOSER | 7014 | 20240708 | 1937 | 20240709 | 1221 | 2510812 | 1004 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 163 | 106709 | 36.3875 | -121.0045 | No | Clear;32-90 F |  |  | 24-0085371 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1955112 | 0 | Non-EPSS | Y | 2024 | A&C
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | RECLOSER | 975548 | 20240708 | 2331 | 20240709 | 26 | 2510996 | 55 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2256 | 124080 | 36.6214 | -121.6846 | No | Clear;32-90 F |  |  | 24-0085429 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1955153 | 0 | EPSS Ckt | Y | 2024 | SGF & DCD ALARM
CENTRAL COAST | SALINAS | SALINAS-1109 | 182011109 | TRANSFORMER | 412381449776 | 20240709 | 40 | 20240709 | 859 | 2511074 | 499 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 8982 | 36.6724 | -121.5996 | No | Overcast-Fog;32-90 F | Cutout- fuse holder | Broken | 24-0085444 | OH | Sus | 31699350 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1955171 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 2553 | 20240709 | 410 | 20240709 | 744 | 2511116 | 214 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 2423 | 36.5766 | -121.97 | No | Overcast-Fog;32-90 F |  |  | 24-0085492 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1955197 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 9359 | 20240709 | 804 | 20240709 | 925 | 2511235 | 71 | Distribution Circuit | Animal | Bird found | 18 | 1278 | 36.593 | -121.8503 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 24-0085548 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1955287 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 2177 | 20240709 | 1555 | 20240709 | 1640 | 2511728 | 45 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 405 | 36.9517 | -121.8417 | No | Clear;32-90 F |  |  | 24-0085781 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1955366 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1112 | 182371112 | RECLOSER | 2028 | 20240709 | 1731 | 20240710 | 1205 | 2511787 | 1099 | Distribution Circuit | Vegetation | Tree - fell into line | 977 | 953169 | 36.4728 | -121.7175 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0085801 | OH | Sus | 31700524 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1955370 | 0 | EPSS Ckt | Y | 2024 | C GRD
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 8877 | 20240709 | 1947 | 20240710 | 14 | 2511901 | 267 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 54 | 14425 | 36.5384 | -121.9021 | No | Overcast;32-90 F |  |  | 24-0085878 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1955432 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | RECLOSER | 37088 | 20240709 | 2102 | 20240710 | 932 | 2511945 | 750 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3040 | 819344 | 36.5465 | -121.8985 | No | Overcast;32-90 F |  |  | 24-0085841 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1955395 | 0 | EPSS Ckt | Y | 2024 | SGF DCD ALARM
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | TRANSFORMER | T0764 | 20240710 | 37 | 20240710 | 1901 | 2512021 | 1104 | Distribution Circuit | Equipment Failure/Involved | Underground | 81 | 26903 | 36.5376 | -121.9032 | No | Overcast-Fog;32-90 F | Transformer (UG) | Broken | 24-0085895 | UG | Sus | 35565484 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1955457 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 412023352325 | 20240710 | 849 | 20240710 | 2228 | 2512231 | 819 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 819 | 36.7394 | -121.7237 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0086291 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1955654 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | JUMPER | OJ 3 S/S OF CGC 413433535729 | 20240710 | 920 | 20240710 | 1254 | 2512111 | 214 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 214 | 36.2949 | -121.2281 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0085934 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1955481 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | RECLOSER | 198478 | 20240710 | 1236 | 20240710 | 1855 | 2512504 | 379 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 238 | 90202 | 36.3913 | -121.6195 | No | Clear;Above 90 |  |  | 24-0086145 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1955628 | 0 | EPSS Ckt | Y | 2024 | UNKNOWN
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | RECLOSER | 113634 | 20240710 | 1349 | 20240710 | 1456 | 2512571 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 90 | 6030 | 36.961 | -121.4309 | No | Clear;32-90 F |  |  | 24-0086230 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1955640 | 0 | EPSS Ckt | Y | 2024 | A B
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | TRANSFORMER | 412871561015 | 20240710 | 1804 | 20240710 | 2316 | 2512805 | 312 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 312 | 36.9836 | -121.4403 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0086461 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1955725 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | FUSE | 5021 | 20240711 | 106 | 20240711 | 254 | 2513089 | 108 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 3564 | 36.5548 | -121.6955 | No | Clear;32-90 F |  |  | 24-0086481 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1955741 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | OILFIELDS-1103 | 182391103 | RECLOSER | 643162 | 20240711 | 624 | 20240711 | 1115 | 2513164 | 291 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 196 | 57036 | 35.8871 | -120.9207 | No | Clear;32-90 F |  |  | 24-0086493 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1955752 | 0 | EPSS Ckt | Y | 2024 | C GRD
CENTRAL COAST | SALINAS | SALINAS-1103 | 182011103 | OTHER | T0700 TWD T0899 | 20240711 | 1033 | 20240711 | 1603 | 2513610 | 330 | Distribution Circuit | Equipment Failure/Involved | Underground | 106 | 9140 | 36.6955 | -121.6614 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0086533 | UG | Sus | 35565528 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1955919 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | FUSE | 9891 | 20240711 | 1151 | 20240711 | 1315 | 2513708 | 84 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 2604 | 35.9295 | -121.082 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0086682 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1955949 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 445933 | 20240711 | 1244 | 20240711 | 1319 | 2513793 | 35 | Distribution Circuit | Company Initiated | Personnel- company | 20 | 700 | 37.1372 | -122.1004 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0086753 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1955962 | 0 | EPSS Ckt | Y | 2024 | A C
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 382362 | 20240711 | 1359 | 20240711 | 1553 | 2513873 | 114 | Distribution Circuit | Company Initiated | Personnel- company | 91 | 10374 | 37.0467 | -122.0756 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0086809 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1955973 | 0 | EPSS Ckt | Y | 2024 | UNKNOWN
CENTRAL COAST | SALINAS | SALINAS-1103 | 182011103 | OTHER | T2756 TWD T2757 | 20240711 | 1747 | 20240711 | 2241 | s1955957 | 294 | Distribution Circuit | Equipment Failure/Involved | Underground | 84 | 24696 | 36.694 | -121.6698 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0086598 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1955957 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | RECLOSER | 37088 | 20240711 | 2002 | 20240712 | 1210 | 2514387 | 855 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3037 | 1530679 | 36.5465 | -121.8985 | No | Partly Cloudy;32-90 F |  |  | 24-0086958 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956039 | 0 | EPSS Ckt | Y | 2024 | SGF- DCD
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | FUSE | 994287 | 20240712 | 817 | 20240712 | 1020 | 2514781 | 123 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 4305 | 36.8402 | -121.463 | No | Clear;32-90 F |  |  | 24-0087168 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1956244 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316347417149 | 20240712 | 932 | 20240712 | 1408 | 2514723 | 276 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 276 | 36.9644 | -121.7512 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 24-0087149 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956236 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 382362 | 20240712 | 1058 | 20240712 | 1121 | 2515010 | 23 | Distribution Circuit | Company Initiated | Personnel- company | 84 | 1932 | 37.0467 | -122.0756 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0087215 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956263 | 0 | EPSS Ckt | Y | 2024 | N/A
CENTRAL COAST | SALINAS | SPENCE-1101 | 182201101 | TRANSFORMER | 412374547377 | 20240712 | 1219 | 20240712 | 1905 | 2515079 | 406 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 406 | 36.6068 | -121.5989 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0087320 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956309 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 6071 | 20240712 | 1412 | 20240712 | 2032 | 2515232 | 380 | Distribution Circuit | Equipment Failure/Involved | Underground | 50 | 16200 | 36.5796 | -121.931 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0087379 | UG | Sus | 46279469 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956325 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DEL MONTE-2104 | 182222104 | TRANSFORMER | 411954745538 | 20240712 | 1812 | 20240713 | 1040 | 2515446 | 988 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 988 | 36.5517 | -121.7405 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0087460 | OH | Sus | 35566151 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956393 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1103 | 182131103 | FUSE | 25749 | 20240712 | 1844 | 20240712 | 1959 | 2515521 | 75 | Distribution Circuit | 3rd Party | Metallic Balloon | 60 | 4500 | 36.5068 | -121.4429 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0087426 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1956353 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | OTHER | WIRE DOWN 3 LD SIDE OF 9789 | 20240712 | 1856 | 20240713 | 1115 | 2515632 | 979 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3667 | 37.1832 | -122.1405 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0087437 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | Yes | 1956363 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | FUSE | 994287 | 20240712 | 2202 | 20240713 | 718 | 2515682 | 556 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 6480 | 36.8402 | -121.463 | No | Clear;32-90 F |  |  | 24-0087459 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956392 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 6801 | 20240713 | 48 | 20240713 | 556 | 2515724 | 308 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 2464 | 36.9039 | -121.7239 | No | Overcast-Fog;32-90 F |  |  | 24-0087466 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1956407 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | TRANSFORMER | 411668047394 | 20240713 | 237 | 20240713 | 827 | 2515750 | 327 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 2616 | 36.601 | -121.8405 | No | Overcast-Fog;32-90 F | Transformer (OH) | Deteriorated | 24-0087464 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956401 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | OCB | 1104/2 | 20240713 | 1355 | 20240713 | 1424 | 2516048 | 29 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 588 | 17052 | 36.5092 | -121.4466 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0087564 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1956486 | 0 | EPSS Ckt | N | 2024 | NONE
CENTRAL COAST | KING CITY | KING CITY-1106 | 182031106 | OCB | 1106/2 | 20240713 | 1728 | 20240714 | 1418 | 2516186 | 1250 | Distribution Circuit | Equipment Failure/Involved | Overhead | 337 | 259601 | 36.217 | -121.1269 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 24-0087598 | OH | Sus | 35566200 | SOUTH BAY AND CENTRAL COAST | JUL | Multi-Fault | 0 | No | Yes | No | 1956507 | 0 | EPSS Ckt | N | 2024 | A-B-GRD
CENTRAL COAST | SALINAS | SALINAS-1102 | 182011102 | FUSE | 24683 | 20240713 | 2040 | 20240713 | 2202 | 2516289 | 82 | Distribution Circuit | 3rd Party | Metallic Balloon | 46 | 3772 | 36.6985 | -121.6473 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0087641 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1956554 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | FUSE | 7993 | 20240714 | 541 | 20240714 | 1003 | 2516467 | 262 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 4192 | 36.4739 | -121.4711 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0087694 | OH | Sus | 46279782 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | Yes | 1956604 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 50763 | 20240714 | 1119 | 20240714 | 1410 | 2516632 | 171 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 7 | 1197 | 36.9407 | -121.3863 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0087711 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1956624 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | KING CITY-1106 | 182031106 | FUSE | 9283 | 20240714 | 1418 | 20240714 | 1803 | 2516710 | 225 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 300 | 36.2087 | -121.1169 | No | Clear;32-90 F |  |  | 24-0087598 | OH | Sus | 35566200 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956642 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2101 | 182492101 | FUSE | 50577 | 20240714 | 1439 | 20240714 | 1611 | 2516706 | 92 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 2208 | 36.8466 | -121.4078 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0087732 | OH | Sus | 31701022 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1956644 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | TRANSFORMER | 412745042350 | 20240714 | 1550 | 20240715 | 305 | 2516734 | 675 | Transformer only | Animal | Bird found | 1 | 675 | 36.4705 | -121.4716 | No | Clear;32-90 F | Fuse | Arcing | 24-0087748 | OH | Sus | 31701023 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956657 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | RECLOSER | 7014 | 20240714 | 1846 | 20240715 | 1345 | 2516795 | 1139 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 163 | 121874 | 36.3875 | -121.0045 | No | Clear;32-90 F |  |  | 24-0087754 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1956662 | 0 | Non-EPSS | Y | 2024 | B-C
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316686013190 | 20240715 | 820 | 20240715 | 1132 | 2517223 | 192 | Transformer only | Animal | Bird found | 1 | 192 | 36.8571 | -121.6336 | No | Clear;32-90 F | Transformer (OH) |  | 24-0088001 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956897 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | RECLOSER | 698634 | 20240715 | 840 | 20240715 | 1108 | 2517051 | 148 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 123 | 18204 | 37.0954 | -122.0857 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0087865 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956784 | 0 | EPSS Ckt | Y | 2024 | A PHSE GRD
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | TRANSFORMER | 315688217045 | 20240715 | 843 | 20240715 | 913 | 2517016 | 30 | Transformer only | Equipment Failure/Involved | Overhead | 19 | 570 | 36.9588 | -121.9767 | No | Partly Cloudy;32-90 F | Transformer (OH) | Deteriorated | 24-0087852 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1956767 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412160954172 | 20240715 | 911 | 20240715 | 2338 | 2517116 | 867 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 6936 | 36.7918 | -121.6785 | No | Clear;32-90 F | Transformer | Deteriorated | 24-0087964 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956882 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | RECLOSER | 4060 | 20240715 | 1016 | 20240715 | 1104 | 2517258 | 48 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1002 | 48096 | 36.801 | -121.3379 | No | Partly Cloudy;32-90 F |  |  | 24-0087934 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1956869 | 0 | EPSS Ckt | N | 2024 | A 7 B PHSE
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 12760 | 20240715 | 1246 | 20240715 | 1606 | 2517434 | 200 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 552 | 110400 | 37.0674 | -121.9966 | No | Clear;32-90 F |  |  | 24-0088043 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956913 | 0 | EPSS Ckt | Y | 2024 | B & GRD
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | TRANSFORMER | T2594 | 20240715 | 1246 | 20240716 | 520 | 2517391 | 994 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 1988 | 36.7062 | -121.6665 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0088042 | UG | Sus | 35566500 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956912 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | TRANSFORMER | 316629014563 | 20240715 | 1400 | 20240716 | 1145 | 2517376 | 1305 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1305 | 36.8954 | -121.6538 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0088090 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956922 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9743 | 20240715 | 1405 | 20240715 | 1509 | 2517502 | 64 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 256 | 37.1586 | -122.127 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0088093 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1956925 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8341 | 20240715 | 1919 | 20240716 | 1419 | 2517714 | 1140 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 5700 | 37.0555 | -121.9604 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0088216 | OH | Sus | 46280250 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1956966 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | SWITCH | 7915 | 20240716 | 154 | 20240716 | 200 | s1957005 | 6 | Distribution Circuit | Company Initiated | Return Circuit Normal | 50 | 300 | 36.577 | -121.9382 | No | Clear;32-90 F | Conductor- Underground | Normal | 24-0087379 | UG | Sus | 46279469 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1957005 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SOLEDAD-2101 | 182052101 | RECLOSER | 107872 | 20240716 | 913 | 20240716 | 1106 | 2518085 | 113 | Distribution Circuit | 3rd Party | Customer Equipment | 33 | 3729 | 36.4233 | -121.2905 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0088354 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1957151 | 0 | EPSS Ckt | Y | 2024 | SGF & DCD
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | TRANSFORMER | 315959417429 | 20240716 | 926 | 20240716 | 938 | 2518056 | 12 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 48 | 36.9701 | -121.8829 | No | Partly Cloudy;32-90 F | Bushing | Broken | 24-0088346 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1957129 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SOLEDAD-2101 | 182052101 | RECLOSER | 107872 | 20240716 | 1118 | 20240717 | 1301 | s1957455 | 1543 | Distribution Circuit | 3rd Party | Customer Equipment | 33 | 41913 | 36.4233 | -121.2905 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0088354 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1957455 | 0 | EPSS Ckt | Y | 2024 | SGF/DCD
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 9519 | 20240716 | 1122 | 20240716 | 1214 | 2518208 | 52 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 156 | 37.0195 | -122.0167 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 24-0088436 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1957200 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | TRANSFORMER | 316187214017 | 20240716 | 1235 | 20240716 | 1308 | 2518278 | 33 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 33 | 36.8777 | -121.8046 | No | Clear;32-90 F | Fuse | Broken | 24-0088516 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1957227 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | RECLOSER | 3030 | 20240716 | 1813 | 20240717 | 642 | 2518529 | 749 | Distribution Circuit | 3rd Party | Vehicle | 151 | 98287 | 36.5854 | -121.6002 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0088644 | OH | Sus | 35566765 | SOUTH BAY AND CENTRAL COAST | JUL | Multi-Fault | 0 | No | Yes | No | 1957263 | 0 | EPSS Ckt | N | 2024 | A-B-GRD
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | RECLOSER | 975548 | 20240716 | 1814 | 20240716 | 1929 | 2518544 | 75 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2248 | 168600 | 36.6214 | -121.6846 | No | Clear;32-90 F |  |  | 24-0088645 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1957264 | 0 | EPSS Ckt | Y | 2024 | SGF- DCD
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 24919 | 20240716 | 2250 | 20240717 | 2237 | 2518938 | 1427 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 4281 | 36.7912 | -121.7105 | No | Clear;32-90 F | Connector or Splice (OH) | Arcing | 24-0088686 | OH | Sus | 31701266 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1957303 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 4849 | 20240716 | 2344 | 20240717 | 212 | 2518994 | 148 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 1184 | 36.9772 | -121.816 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0088689 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Three Phase Fault | 0 | No | No | No | 1957309 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 11469 | 20240717 | 153 | 20240717 | 318 | 2519020 | 85 | Distribution Circuit | Animal | Bird found | 27 | 2295 | 36.8677 | -121.7463 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0088694 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1957317 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | BUENA VISTA-1103 | 182261103 | FUSE | 5115 | 20240717 | 958 | 20240717 | 2034 | 2519281 | 636 | Distribution Circuit | Vegetation | Tree - branch fell on line | 216 | 137376 | 36.6527 | -121.6465 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0088809 | OH | Sus | 46280963 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1957472 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 5300 | 20240717 | 1056 | 20240717 | 1157 | 2519406 | 61 | Distribution Circuit | Vegetation | Tree - branch fell on line | 919 | 25483 | 37.0383 | -122.0708 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0088833 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1957484 | 0 | EPSS Ckt | Y | 2024 | A&C
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 412028855901 | 20240717 | 1305 | 20240718 | 1352 | 2519602 | 1487 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 2974 | 36.8376 | -121.7251 | No | Clear;32-90 F |  |  | 24-0089009 | OH | Sus | 31701303 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1957530 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 4873 | 20240717 | 1416 | 20240717 | 1526 | 2519637 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 45 | 3150 | 36.8538 | -121.3637 | No | Clear;32-90 F |  |  | 24-0089015 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1957532 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | FUSE | 9439 | 20240717 | 1453 | 20240717 | 1629 | 2519657 | 96 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 384 | 36.2662 | -121.1799 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0088979 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1957526 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | OTHER | WIRE DOWN 2 POLES LD SIDE OF CGC 315671420425 | 20240717 | 1648 | 20240718 | 215 | 2519881 | 567 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 6258 | 37.052 | -121.9842 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0089092 | OH | Sus | 46281089 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1957562 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | TRANSFORMER | 413571834793 | 20240717 | 1716 | 20240717 | 1809 | 2519832 | 53 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 106 | 36.269 | -121.1827 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0089073 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1957555 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | OILFIELDS-1103 | 182391103 | RECLOSER | 643162 | 20240718 | 349 | 20240718 | 1157 | 2519975 | 488 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 228 | 50376 | 35.8871 | -120.9207 | No | Clear;32-90 F |  |  | 24-0089140 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1957607 | 0 | EPSS Ckt | Y | 2024 | A B
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | OCB | 2105/2 | 20240718 | 553 | 20240718 | 1113 | 2519980 | 320 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6019 | 319770 | 36.9926 | -121.9821 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0089143 | OH | Sus | 31701305 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1957609 | 0 | EPSS Ckt | N | 2024 | TRIP TGT
CENTRAL COAST | SALINAS | SPENCE-1102 | 182201102 | TRANSFORMER | 412571047717 | 20240718 | 1032 | 20240718 | 2054 | 2520180 | 622 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 622 | 36.6174 | -121.5324 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0089254 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1957675 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 10683 | 20240718 | 1401 | 20240718 | 1537 | 2520327 | 96 | Distribution Circuit | Animal | Bird found | 7 | 703 | 37.0506 | -122.0154 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0089424 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1957720 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2107 | 182402107 | TRANSFORMER | 411827050478 | 20240718 | 1606 | 20240718 | 1714 | 2520429 | 68 | Transformer only | 3rd Party | Metallic Balloon | 12 | 816 | 36.6872 | -121.7894 | No | Clear;32-90 F | Transformer (OH) | Contaminated | 24-0089487 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1957735 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | OCB | 2106/2 | 20240718 | 1812 | 20240719 | 127 | 2520466 | 435 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4598 | 531614 | 36.9926 | -121.9821 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0089505 | OH | Sus | 46281616 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1957745 | 0 | EPSS Ckt | Y | 2024 | C-GRD
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 3073 | 20240718 | 1847 | 20240719 | 1250 | 2520487 | 1083 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 1083 | 37.0534 | -122.1538 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0089523 | OH | Sus | 46281516 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | Yes | No | 1957760 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | RECLOSER | 549180 | 20240718 | 2148 | 20240719 | 3 | 2520588 | 135 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1215 | 36.0057 | -121.2422 | No | Clear;32-90 F |  |  | 24-0089526 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1957761 | 0 | EPSS Ckt | Y | 2024 | A GRD
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0422 | 182440422 | FUSE | 2581 | 20240719 | 607 | 20240719 | 725 | 2520752 | 78 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 2519 | 36.5918 | -121.9454 | No | Partly Cloudy;32-90 F |  |  | 24-0089604 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1957815 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 10298 | 20240719 | 625 | 20240719 | 825 | 2520765 | 120 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 225 | 16596 | 36.9935 | -121.7994 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0089578 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1957800 | 0 | EPSS Ckt | Y | 2024 | A-G
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | TRANSFORMER | 315723417296 | 20240719 | 836 | 20240719 | 1040 | 2521020 | 124 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 620 | 36.9652 | -121.9638 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 24-0089682 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1957923 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | TRANSFORMER | 315847417675 | 20240719 | 1152 | 20240719 | 1353 | 2520960 | 121 | Transformer only | Equipment Failure/Involved | Underground | 13 | 1573 | 36.9767 | -121.9226 | No | Clear;32-90 F | Service conductor | Burned Open | 24-0089734 | UG | Sus | 46282215 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1957944 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 46311 | 20240719 | 1358 | 20240719 | 1405 | 2521195 | 7 | Distribution Circuit | Company Initiated | Personnel- company | 116 | 812 | 37.0417 | -122.0726 | No | Clear;32-90 F | Fuse | Normal | 24-0089813 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1957979 | 0 | EPSS Ckt | Y | 2024 | B-C
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | JUMPER | OPEN JMPRS 4 POLES SS OF 25243 | 20240720 | 6 | 20240720 | 545 | 2521524 | 339 | Distribution Circuit | 3rd Party | Vehicle | 2 | 678 | 36.469 | -121.3959 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0089949 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1958038 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 985275 | 20240720 | 111 | 20240720 | 1236 | 2521543 | 685 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 6165 | 36.8629 | -121.6657 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0089966 | OH | Sus | 46282446 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1958055 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | RECLOSER | 590402 | 20240720 | 655 | 20240720 | 1614 | 2521579 | 559 | Distribution Circuit | Equipment Failure/Involved | Overhead | 185 | 29631 | 36.8257 | -121.7195 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0089971 | OH | Sus | 35567551 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1958059 | 0 | EPSS Ckt | Y | 2024 | A B INST
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | RECLOSER | 196060 | 20240720 | 720 | 20240720 | 1801 | 2521582 | 640 | Distribution Circuit | 3rd Party | Vehicle | 8 | 5120 | 36.7702 | -121.7645 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken | 24-0089974 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1958063 | 0 | Non-EPSS | N | 2024 | N/A
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 3685 | 20240720 | 947 | 20240720 | 1657 | 2521679 | 430 | Distribution Circuit | Equipment Failure/Involved | Overhead | 43 | 6518 | 36.8254 | -121.7073 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0090028 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1958117 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DEL MONTE-2104 | 182222104 | TRANSFORMER | 412161244720 | 20240720 | 1501 | 20240720 | 2014 | 2521873 | 313 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 626 | 36.5319 | -121.6695 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0090078 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1958155 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | FUSE | 6045 | 20240720 | 2021 | 20240720 | 2053 | s1958167 | 32 | Distribution Circuit | Company Initiated | Personnel- company | 297 | 9519 | 36.6825 | -121.7986 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0065339 | OH | Sus | 35488539 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1958167 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | KING CITY-1106 | 182031106 | RECLOSER | 944510 | 20240720 | 2315 | 20240721 | 1054 | 2522212 | 699 | Distribution Circuit | Equipment Failure/Involved | Overhead | 123 | 50115 | 36.2071 | -121.1151 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0090122 | OH | Sus | 31701448 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1958198 | 0 | EPSS Ckt | N | 2024 | A GRD
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 4447 | 20240721 | 312 | 20240721 | 425 | 2522238 | 73 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 2190 | 36.7894 | -121.36 | No | Partly Cloudy;32-90 F |  |  | 24-0090128 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1958205 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 4433 | 20240721 | 901 | 20240721 | 1309 | 2522350 | 248 | Distribution Circuit | 3rd Party | Vehicle | 33 | 8184 | 36.9903 | -121.807 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0090148 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1958224 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | RECLOSER | 7062 | 20240721 | 917 | 20240721 | 1330 | 2522363 | 253 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 51 | 12903 | 36.2789 | -121.3033 | No | Clear;32-90 F |  |  | 24-0090153 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1958229 | 0 | EPSS Ckt | Y | 2024 | B C
CENTRAL COAST | MONTEREY | DEL MONTE-2101 | 182222101 | TRANSFORMER | 411661447484 | 20240721 | 1244 | 20240721 | 1445 | 2522462 | 121 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 242 | 36.6043 | -121.8422 | No | Overcast;32-90 F | Fuse | Broken | 24-0090192 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1958258 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | TRANSFORMER | 413392551849 | 20240721 | 2350 | 20240722 | 828 | 2522717 | 518 | Transformer only | Animal | Bird found | 1 | 518 | 36.736 | -121.2561 | No | Fog;32-90 F | Fuse | Failed/Faulted | 24-0090307 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1958387 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | FUSE | 3699 | 20240722 | 517 | 20240722 | 620 | 2522758 | 63 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 2224 | 36.9968 | -121.9371 | No | Partly Cloudy;32-90 F |  |  | 24-0090251 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1958313 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2103 | 83252103 | OTHER | J43440 TWD T1798 | 20240722 | 945 | 20240722 | 1156 | 2523040 | 131 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 131 | 36.9721 | -122.0175 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0090306 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1958455 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 389090 | 20240722 | 1130 | 20240722 | 1844 | 2523201 | 434 | Distribution Circuit | Vegetation | Tree - fell into line | 1712 | 140355 | 37.0933 | -122.1295 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0090415 | OH | Sus | 35567810 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1958483 | 0 | EPSS Ckt | Y | 2024 | A C
CENTRAL COAST | SALINAS | SPENCE-1101 | 182201101 | OCB | 1101/2 | 20240722 | 1203 | 20240723 | 313 | 2523231 | 910 | Distribution Circuit | 3rd Party | Vehicle | 463 | 102864 | 36.6139 | -121.5668 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0090428 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1958490 | 0 | Non-EPSS | N | 2024 | A PHASE & GRD
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 95690 | 20240722 | 1310 | 20240722 | 1420 | 2523304 | 70 | Distribution Circuit | 3rd Party | Metallic Balloon | 2127 | 97997 | 37.1249 | -122.125 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0090474 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1958507 | 0 | EPSS Ckt | Y | 2024 | A C
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 4453 | 20240722 | 1326 | 20240722 | 1555 | 2523343 | 149 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 3278 | 36.8419 | -121.6746 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0090589 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1958528 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1105 | 182011105 | SWITCH | 3562 | 20240722 | 1847 | 20240723 | 520 | 2523621 | 633 | Distribution Circuit | Equipment Failure/Involved | Underground | 156 | 18682 | 36.7057 | -121.6531 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0090403 | UG | Sus | 35567661 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1958536 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | TRANSFORMER | 315805818605 | 20240722 | 1849 | 20240723 | 246 | 2523638 | 477 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 477 | 37.002 | -121.9373 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0090667 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1958560 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1103 | 182011103 | FUSE | 5999 | 20240722 | 2019 | 20240722 | 2112 | 2523681 | 53 | Distribution Circuit | Equipment Failure/Involved | Overhead | 97 | 5126 | 36.7071 | -121.656 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0090666 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1958559 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 9665 | 20240722 | 2259 | 20240723 | 42 | 2523756 | 103 | Distribution Circuit | Animal | Bird found | 7 | 721 | 36.8549 | -121.7925 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0090707 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1958598 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 9403 | 20240723 | 335 | 20240723 | 548 | 2523855 | 133 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 109 | 14497 | 36.8779 | -121.7526 | No | Fog;32-90 F |  |  | 24-0090716 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1958610 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 667 | 20240723 | 618 | 20240723 | 1356 | 2523869 | 458 | Distribution Circuit | 3rd Party | Vehicle | 2 | 916 | 36.8997 | -121.6889 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken | 24-0090715 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1958609 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 801 | 20240723 | 1302 | 20240724 | 129 | 2524397 | 747 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 747 | 36.8894 | -121.6228 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0091054 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1958841 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | OTHER | WIRE DOWN @ CGC 315498322429 | 20240723 | 2034 | 20240724 | 537 | 2524976 | 543 | Distribution Circuit | Vegetation | Tree - branch fell on line | 305 | 40425 | 37.1041 | -122.0449 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0091186 | OH | Sus | 46283474 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | Yes | 1958894 | 0 | EPSS Ckt | Y | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411917553412 | 20240724 | 800 | 20240724 | 1046 | 2525268 | 166 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 830 | 36.769 | -121.7607 | No | Clear;32-90 F | Fuse | Broken | 24-0091411 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1959143 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | RECLOSER | 2020 | 20240724 | 1101 | 20240724 | 1127 | 2525653 | 26 | Distribution Circuit | Company Initiated | Personnel- company | 805 | 20930 | 36.4632 | -121.7119 | No | Clear;32-90 F | Recloser | Normal | 24-0091422 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1959148 | 0 | EPSS Ckt | Y | 2024 | SGF
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 117818 | 20240724 | 1516 | 20240724 | 1524 | s1968360 | 8 | Distribution Circuit | Company Initiated | Personnel- company | 19 | 152 | 37.1248 | -122.1265 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0085782 | OH | Sus | 31626266 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1968360 | 0 | EPSS Ckt | N | 2024 | A
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | RECLOSER | 11056 | 20240724 | 1623 | 20240724 | 1634 | s1959393 | 11 | Distribution Circuit | Company Initiated | Personnel- company | 105 | 1155 | 36.9937 | -122.0299 | No | Clear;32-90 F | Recloser | Normal | 24-0082647 | OH | Sus | 35323475 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1959393 | 0 | EPSS Ckt | N | 2024 | A GRD
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | JUMPER | #2 HIGH SIDE JMPR OPEN | 20240724 | 1723 | 20240724 | 2321 | 2526026 | 358 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1421 | 36.9452 | -121.7524 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 24-0091682 | OH | Sus | 31702012 | SOUTH BAY AND CENTRAL COAST | JUL | Open Circuit | 0 | No | No | No | 1959223 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | JUMPER | 485 SS JMPRS | 20240724 | 2032 | 20240725 | 333 | 2526088 | 421 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 2105 | 36.2256 | -121.7615 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0091693 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1959230 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6711 | 20240725 | 57 | 20240725 | 913 | 2526234 | 496 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 24800 | 36.9982 | -121.8687 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0091758 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1959305 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6711 | 20240725 | 943 | 20240725 | 1042 | 2526572 | 59 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 2950 | 36.9982 | -121.8687 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0091905 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1959477 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | TRANSFORMER | 414694938071 | 20240725 | 1827 | 20240726 | 2040 | 2526957 | 1573 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 1573 | 36.3652 | -120.8024 | No | Clear;Above 90 | Service conductor | Broken- wire on ground | 24-0092215 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1959598 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | TRANSFORMER | 411451844142 | 20240725 | 1947 | 20240726 | 1520 | 2526995 | 1173 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 4365 | 36.5094 | -121.9097 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0092198 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1959583 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 4363 | 20240725 | 2203 | 20240726 | 149 | 2527064 | 226 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1356 | 36.9383 | -121.8265 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Deteriorated | 24-0092201 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1959584 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | RECLOSER | 4724 | 20240726 | 401 | 20240726 | 500 | 2527136 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 483 | 28497 | 36.7268 | -121.2707 | No | Clear;32-90 F |  |  | 24-0092231 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1959622 | 0 | EPSS Ckt | N | 2024 | SGF
CENTRAL COAST | KING CITY | SOLEDAD-2102 | 182052102 | RECLOSER | 7008 | 20240726 | 803 | 20240726 | 946 | 2527228 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 98 | 10094 | 36.4058 | -121.3538 | No | Clear;32-90 F |  |  | 24-0092284 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1959656 | 0 | EPSS Ckt | Y | 2024 | A&B
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 1995 | 20240726 | 1112 | 20240726 | 1327 | 2527513 | 135 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 270 | 37.0556 | -122.1209 | No | Clear;32-90 F |  |  | 24-0092505 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1959807 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2103 | 83252103 | INTERRUPTER | 227982 | 20240726 | 1458 | 20240726 | 1644 | 2527720 | 106 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 85 | 9010 | 36.9772 | -122.0267 | No | Clear;32-90 F |  |  | 24-0092606 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1959831 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 11028 | 20240726 | 1606 | 20240726 | 2145 | 2527772 | 339 | Distribution Circuit | Vegetation | Tree - fell into line | 1237 | 72687 | 36.9714 | -121.8908 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0092513 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1959825 | 0 | EPSS Ckt | N | 2024 | NONE
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 389090 | 20240726 | 1614 | 20240726 | 1707 | 2527741 | 53 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1712 | 89331 | 37.0933 | -122.1295 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0092598 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1959827 | 0 | EPSS Ckt | N | 2024 | N/A
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315653121350 | 20240726 | 1713 | 20240726 | 2035 | 2527826 | 202 | Transformer only | Unknown Cause | Patrol - not conducted | 3 | 606 | 37.077 | -121.9913 | No | Clear;32-90 F |  |  | 24-0092641 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1959863 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | TRANSFORMER | 315390422406 | 20240727 | 127 | 20240727 | 930 | 2528093 | 483 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1449 | 37.1047 | -122.0818 | No | Clear;32-90 F | Jumper | Burned Open | 24-0092703 | OH | Sus | 46285288 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1959913 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | JUMPER | OJS 1 SPAN SOURCE SIDE OF CGC 316089916188 | 20240727 | 724 | 20240727 | 1310 | 2528147 | 346 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 692 | 36.9363 | -121.8398 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken | 24-0092719 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1959928 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | OTHER | 8883 | 20240727 | 1335 | 20240728 | 415 | 2528341 | 880 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 15840 | 37.0832 | -122.0958 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0092781 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | Yes | 1960003 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 2665 | 20240727 | 1344 | 20240727 | 2111 | 2528347 | 447 | Distribution Circuit | Vegetation | Tree - branch fell on line | 64 | 28608 | 36.5897 | -121.8932 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0092777 | OH | Sus | 46285293 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1960000 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | RECLOSER | 9704 | 20240727 | 1417 | 20240727 | 1906 | 2528363 | 215 | Distribution Circuit | 3rd Party | Vehicle | 443 | 26790 | 36.5672 | -121.9274 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0092771 | OH | Sus | 31702565 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1959997 | 0 | EPSS Ckt | N | 2024 | NONE
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | FUSE | 863 | 20240727 | 1728 | 20240727 | 1840 | 2528429 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 1080 | 36.9847 | -121.9657 | No | Clear;32-90 F |  |  | 24-0092800 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1960015 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 5188 | 20240728 | 1033 | 20240728 | 1049 | 2528666 | 16 | Distribution Circuit | Company Initiated | Personnel- company | 898 | 14368 | 37.0756 | -122.0567 | No | Clear;32-90 F | Recloser | Normal | 24-0058103 | OH | Sus | 35505603 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1960094 | 0 | EPSS Ckt | Y | 2024 | SGF
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6639 | 20240728 | 1707 | 20240728 | 2317 | 2528752 | 370 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 12580 | 37.0075 | -121.809 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0092924 | OH | Sus | 46285681 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1960123 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 454176 | 20240728 | 1732 | 20240728 | 1850 | 2528758 | 78 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 51 | 3978 | 36.994 | -121.7761 | No | Clear;32-90 F |  |  | 24-0092910 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1960113 | 0 | EPSS Ckt | Y | 2024 | B/C DCD
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | RECLOSER | 7014 | 20240728 | 1808 | 20240729 | 1322 | 2528771 | 1154 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 106 | 122324 | 36.3875 | -121.0045 | No | Clear;32-90 F |  |  | 24-0092914 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1960116 | 0 | Non-EPSS | Y | 2024 | A/C
CENTRAL COAST | SALINAS | SALINAS-1106 | 182011106 | TRANSFORMER | 412201649771 | 20240728 | 2124 | 20240728 | 2207 | 2528814 | 43 | Transformer only | Unknown Cause | Patrol - found nothing | 28 | 1204 | 36.6707 | -121.6608 | No | Overcast;32-90 F |  |  | 24-0092946 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1960146 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1101 | 182201101 | FUSE | 20005 | 20240728 | 2207 | 20240729 | 1311 | 2528824 | 904 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 2656 | 36.5956 | -121.547 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0092948 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Three Phase Fault | 0 | No | No | No | 1960149 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | RECLOSER | 428102 | 20240729 | 601 | 20240729 | 713 | 2528869 | 72 | Distribution Circuit | Animal | Bird found | 346 | 24912 | 36.9976 | -121.9515 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Normal | 24-0092966 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1960163 | 0 | EPSS Ckt | Y | 2024 | C GRD
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 316121016683 | 20240729 | 954 | 20240729 | 1102 | 2529138 | 68 | Transformer only | Unknown Cause | Patrol - found nothing | 7 | 476 | 36.9504 | -121.8288 | No | Overcast;32-90 F |  |  | 24-0093124 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1960334 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SOLEDAD-2102 | 182052102 | RECLOSER | 7008 | 20240729 | 1023 | 20240729 | 1208 | 2529183 | 105 | Distribution Circuit | Equipment Failure/Involved | Overhead | 98 | 10290 | 36.4058 | -121.3538 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0093109 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1960324 | 0 | EPSS Ckt | Y | 2024 | A & B
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | TRANSFORMER | 412763145112 | 20240729 | 1110 | 20240729 | 1149 | 2529182 | 39 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 39 | 36.5472 | -121.4651 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Contaminated | 24-0093201 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1960349 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316442016795 | 20240729 | 1356 | 20240730 | 107 | 2529350 | 671 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 671 | 36.9552 | -121.7188 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0093366 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1960392 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2101 | 182492101 | TRANSFORMER | 412954256214 | 20240729 | 1425 | 20240729 | 2031 | 2529389 | 366 | Transformer only | 3rd Party | Vehicle | 31 | 11346 | 36.8529 | -121.4094 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0093356 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1960386 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 6147 | 20240729 | 2317 | 20240730 | 402 | 2529862 | 285 | Distribution Circuit | Equipment Failure/Involved | Underground | 8 | 2280 | 36.5876 | -121.9434 | No | Partly Cloudy-Fog;32-90 F | Transformer (UG) | Failed/Faulted | 24-0093474 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1960453 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 9651 | 20240730 | 107 | 20240730 | 256 | 2529894 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 545 | 36.8577 | -121.7717 | No | Overcast-Fog;32-90 F |  |  | 24-0093480 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1960460 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 4439 | 20240730 | 500 | 20240730 | 551 | 2529932 | 51 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 102 | 36.9497 | -121.7918 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0093485 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1960469 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 4563 | 20240730 | 701 | 20240730 | 901 | 2529979 | 120 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 2760 | 36.7259 | -121.6536 | No | Partly Cloudy;32-90 F |  |  | 24-0093581 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1960608 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | OCB | 1104/2 | 20240730 | 712 | 20240730 | 1134 | 2529954 | 262 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 588 | 36774 | 36.5092 | -121.4466 | No | Partly Cloudy;32-90 F | Insulator | Burned/flashed | 24-0093512 | OH | Sus | 31702841 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1960486 | 0 | EPSS Ckt | N | 2024 | FORCE OUT
CENTRAL COAST | KING CITY | SOLEDAD-2102 | 182052102 | RECLOSER | 7008 | 20240730 | 922 | 20240730 | 1641 | 2530184 | 439 | Distribution Circuit | Animal | Bird found | 98 | 17006 | 36.4058 | -121.3538 | No | Fog;32-90 F | Jumper | Burned/flashed | 24-0093584 | OH | Sus | 31702849 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1960622 | 0 | EPSS Ckt | Y | 2024 | A-B
CENTRAL COAST | KING CITY | KING CITY-1105 | 182031105 | OCB | 1105/2 | 20240730 | 923 | 20240730 | 948 | 2530188 | 25 | Distribution Circuit | Animal | Bird found | 1022 | 25550 | 36.217 | -121.1269 | No | Clear;32-90 F | Lightning Arrestor | Burned/flashed | 24-0093587 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1960624 | 0 | Non-EPSS | N | 2024 | A-GRD
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | TRANSFORMER | 412939356864 | 20240730 | 1055 | 20240730 | 1354 | 2530251 | 179 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 179 | 36.8706 | -121.4153 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0093656 | OH | Sus | 46286376 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1960673 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | RECLOSER | 64348 | 20240730 | 1422 | 20240730 | 1758 | 2530447 | 216 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 205 | 44238 | 36.3307 | -121.2258 | No | Clear;32-90 F |  |  | 24-0093813 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1960725 | 0 | Non-EPSS | Y | 2024 | A&C
CENTRAL COAST | HOLLISTER | HOLLISTER-2101 | 182492101 | FUSE | 9941 | 20240730 | 1517 | 20240730 | 1615 | 2530476 | 58 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 44 | 2530 | 36.8575 | -121.4146 | No | Clear;32-90 F |  |  | 24-0093873 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1960739 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | RECLOSER | 109138 | 20240730 | 1537 | 20240730 | 2250 | 2530497 | 433 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3452 | 290061 | 36.3182 | -121.2407 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0093864 | OH | Sus | 31702673 | SOUTH BAY AND CENTRAL COAST | JUL | Multi-Fault | 0 | No | Yes | No | 1960735 | 0 | Non-EPSS | N | 2024 | AB&GRD
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | T1327 | 20240730 | 1734 | 20240730 | 2101 | 2530574 | 207 | Transformer only | Equipment Failure/Involved | Underground | 9 | 1863 | 36.8174 | -121.659 | No | Partly Cloudy;32-90 F | Connector or Splice (UG) | Deteriorated | 24-0093958 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1960781 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | RECLOSER | 698634 | 20240730 | 1751 | 20240731 | 349 | 2530588 | 598 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 17845 | 37.0954 | -122.0857 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0093920 | OH | Sus | 31702855 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1960755 | 0 | EPSS Ckt | Y | 2024 | C PHSE & GRD
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 3685 | 20240730 | 1835 | 20240730 | 1906 | 2530527 | 31 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 1333 | 36.8254 | -121.7073 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0093934 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1960761 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | SWITCH | 10148 | 20240730 | 2336 | 20240731 | 251 | 2530728 | 195 | Distribution Circuit | Equipment Failure/Involved | Underground | 192 | 6360 | 36.8603 | -121.8142 | No | Partly Cloudy-Fog;32-90 F | Transformer (UG) | Failed/Faulted | 24-0093959 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1960803 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 1669 | 20240731 | 802 | 20240731 | 1140 | 2530850 | 218 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 218 | 36.9102 | -121.7909 | No | Overcast-Fog;32-90 F |  |  | 24-0094208 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1961026 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | RECLOSER | 383718 | 20240731 | 836 | 20240731 | 846 | 2530956 | 10 | Distribution Circuit | Company Initiated | Personnel- company | 621 | 6210 | 36.5788 | -121.7198 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0094053 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1960932 | 0 | EPSS Ckt | Y | 2024 | SGF/DCD
CENTRAL COAST | SALINAS | SPENCE-1101 | 182201101 | TRANSFORMER | 412341447410 | 20240731 | 1015 | 20240731 | 1116 | 2531058 | 61 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 61 | 36.6071 | -121.6039 | No | Overcast;32-90 F | Fuse | Burned Open | 24-0094187 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1961024 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | TRANSFORMER | 412766845888 | 20240731 | 1153 | 20240731 | 1234 | 2531167 | 41 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 41 | 36.5681 | -121.464 | No | Clear;32-90 F | Fuse | Burned Open | 24-0094248 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1961040 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | RECLOSER | 174580 | 20240731 | 1246 | 20240731 | 1427 | 2531280 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 73 | 7373 | 36.3398 | -121.2351 | No | Clear;32-90 F |  |  | 24-0094258 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Three Phase Fault | 0 | No | No | No | 1961043 | 0 | EPSS Ckt | Y | 2024 | A-B-C
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411916053427 | 20240731 | 1424 | 20240731 | 1706 | 2531375 | 162 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 1620 | 36.7694 | -121.7612 | No | Clear;32-90 F | Fuse | Broken | 24-0094449 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1961105 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 6801 | 20240731 | 1439 | 20240801 | 226 | 2531386 | 707 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 5656 | 36.9039 | -121.7239 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0094431 | OH | Sus | 46287315 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1961091 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | INDUSTRIAL ACRES-0412 | 182300412 | TRANSFORMER | 412310350148 | 20240731 | 1500 | 20240731 | 1647 | 2531405 | 107 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 1605 | 36.682 | -121.6241 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0094376 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1961076 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1103 | 182011103 | TRANSFORMER | 412225150795 | 20240801 | 157 | 20240801 | 344 | 2531621 | 107 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 107 | 36.699 | -121.6538 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0094495 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1961140 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | FUSE | 5743 | 20240801 | 713 | 20240801 | 1412 | 2531648 | 419 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2514 | 37.1049 | -122.116 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0094564 | OH | Sus | 46287490 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1961199 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 454176 | 20240801 | 1633 | 20240801 | 1821 | 2532237 | 108 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 51 | 3558 | 36.994 | -121.7761 | No | Partly Cloudy;32-90 F |  |  | 24-0094849 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1961353 | 0 | EPSS Ckt | Y | 2024 | B-C
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 9265 | 20240801 | 2234 | 20240802 | 1327 | 2532487 | 893 | Distribution Circuit | 3rd Party | Vehicle | 21 | 18753 | 36.9662 | -121.8295 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 24-0094945 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1961424 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411928053325 | 20240801 | 2336 | 20240802 | 332 | 2532518 | 236 | Transformer only | Equipment Failure/Involved | Fire- pole | 5 | 1180 | 36.7664 | -121.7572 | No | Clear;32-90 F | Crossarm- Wood | Burned/flashed | 24-0094947 | OH | Sus | 31703087 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1961426 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 40707 | 20240802 | 555 | 20240802 | 705 | 2532595 | 70 | Distribution Circuit | Animal | Bird found | 22 | 1540 | 36.5942 | -121.8954 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Normal | 24-0094988 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1961468 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | RECLOSER | 2102/2/NORM | 20240802 | 558 | 20240802 | 1234 | 2532607 | 396 | Distribution Circuit | Vegetation | Tree - fell into line | 822 | 149686 | 36.8686 | -121.5496 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0094961 | OH | Sus | 31703182 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1961451 | 0 | EPSS Ckt | N | 2024 | C GRD
CENTRAL COAST | SALINAS | SPENCE-1101 | 182201101 | OTHER | 1 PHASE WIRE DOWN 1 SS OF 20005 | 20240802 | 702 | 20240802 | 1054 | 2532630 | 232 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 5800 | 36.5957 | -121.5469 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0094996 | OH | Sus | 31703249 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | Yes | 1961508 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | FUSE | 4817 | 20240802 | 829 | 20240802 | 942 | 2532777 | 73 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 1168 | 36.9193 | -121.4497 | No | Clear;32-90 F |  |  | 24-0095051 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1961565 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | TRANSFORMER | 412468057750 | 20240802 | 832 | 20240802 | 1435 | 2532780 | 363 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1089 | 36.8922 | -121.5768 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0095054 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1961567 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2107 | 182402107 | FUSE | 7273 | 20240802 | 852 | 20240802 | 955 | 2532808 | 63 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 1449 | 36.6758 | -121.7872 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0095063 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1961570 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 665 | 20240802 | 901 | 20240802 | 1132 | 2532793 | 151 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 453 | 36.9034 | -121.6765 | No | Overcast-Fog;32-90 F | Transformer (OH) | Broken | 24-0095006 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1961528 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | TRANSFORMER | 413588335376 | 20240802 | 919 | 20240802 | 1532 | 2532912 | 373 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 373 | 36.2852 | -121.1771 | No | Partly Cloudy;32-90 F | Transformer (OH) | Contaminated | 24-0095159 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1961600 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6487 | 20240802 | 1021 | 20240802 | 1635 | 2532929 | 374 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 5610 | 36.8972 | -121.6758 | No | Partly Cloudy;32-90 F |  |  | 24-0095278 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1961637 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ERTA-0403 | 83510403 | FUSE | 6823 | 20240802 | 1749 | 20240802 | 1953 | 2533241 | 124 | Distribution Circuit | Equipment Failure/Involved | Overhead | 119 | 14756 | 36.9272 | -121.7694 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 24-0095257 | OH | Sus | 31703298 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1961653 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 4609 | 20240802 | 2051 | 20240802 | 2133 | 2533310 | 42 | Distribution Circuit | Equipment Failure/Involved | Underground | 14 | 588 | 36.9561 | -121.8358 | No | Overcast;32-90 F | Other | Deteriorated | 24-0095327 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1961665 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | FUSE | 25511 | 20240803 | 535 | 20240803 | 816 | 2533437 | 161 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 537 | 36.5506 | -121.4993 | No | Clear;32-90 F |  |  | 24-0095361 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1961704 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2107 | 182402107 | TRANSFORMER | 411824050321 | 20240803 | 756 | 20240803 | 937 | 2533486 | 101 | Transformer only | Unknown Cause | Patrol - found nothing | 8 | 808 | 36.683 | -121.7903 | No | Clear;32-90 F |  |  | 24-0095388 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1961733 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 439972 | 20240803 | 1922 | 20240804 | 1550 | 2533899 | 1228 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 58542 | 37.0195 | -121.8841 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0095459 | OH | Sus | 31703402 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1961773 | 0 | EPSS Ckt | Y | 2024 | C GRD
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 11006 | 20240803 | 2310 | 20240804 | 118 | 2533986 | 127 | Distribution Circuit | Vegetation | Tree - fell into line | 1969 | 148552 | 37.05 | -122.0657 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0095493 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1961815 | 0 | EPSS Ckt | N | 2024 | A & C PHASE
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | RECLOSER | 113634 | 20240804 | 222 | 20240804 | 1400 | 2534047 | 698 | Distribution Circuit | 3rd Party | Vehicle | 90 | 5532 | 36.961 | -121.4309 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0095502 | OH | Sus | 31703440 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1961824 | 0 | EPSS Ckt | Y | 2024 | A GRD
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | RECLOSER | 99672 | 20240805 | 448 | 20240805 | 502 | 2534563 | 14 | Distribution Circuit | Equipment Failure/Involved | Overhead | 98 | 1372 | 36.7642 | -121.7605 | No | Overcast-Fog;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0095638 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1961932 | 0 | Non-EPSS | N | 2024 | N/A
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 11517 | 20240805 | 1045 | 20240805 | 1454 | 2534687 | 249 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 1992 | 36.8924 | -121.714 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0095811 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1962070 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | TRANSFORMER | 412169850185 | 20240805 | 1152 | 20240805 | 1731 | 2534952 | 339 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 4068 | 36.6819 | -121.672 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0095975 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1962125 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 14130 | 20240805 | 1230 | 20240805 | 1445 | 2535001 | 135 | Distribution Circuit | Vegetation | Tree - branch fell on line | 108 | 14580 | 37.0476 | -122.1607 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0095897 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1962099 | 0 | EPSS Ckt | Y | 2024 | B-C
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | JUMPER | FB W/OF CGC-412214655064 | 20240805 | 1914 | 20240806 | 59 | 2535336 | 345 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1725 | 36.8167 | -121.6618 | No | Overcast;32-90 F | Transformer (OH) | Deteriorated | 24-0096086 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1962158 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412306254819 | 20240805 | 2112 | 20240805 | 2258 | 2535182 | 106 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 212 | 36.8101 | -121.6295 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 24-0096048 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1962139 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | RECLOSER | 781810 | 20240805 | 2216 | 20240806 | 1220 | 2535391 | 844 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 185 | 145352 | 36.9615 | -122.0627 | No | Partly Cloudy;32-90 F |  |  | 24-0096129 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1962198 | 0 | EPSS Ckt | Y | 2024 | A-B INST OC
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 12529 | 20240805 | 2217 | 20240806 | 15 | 2535425 | 118 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 2360 | 36.9659 | -122.0174 | No | Partly Cloudy;32-90 F |  |  | 24-0096145 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1962211 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | TRANSFORMER | 315980017505 | 20240806 | 8 | 20240806 | 151 | 2535413 | 103 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 206 | 36.972 | -121.8757 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 24-0096143 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1962208 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | FUSE | 9057 | 20240806 | 1048 | 20240806 | 1131 | 2535773 | 43 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 86 | 36.9251 | -121.4619 | No | Clear;32-90 F | Conductor- Overhead | Burned/flashed | 24-0096288 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1962385 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 12590 | 20240806 | 1433 | 20240806 | 1611 | 2535970 | 98 | Distribution Circuit | Vegetation | Tree - branch fell on line | 349 | 34202 | 37.0633 | -122.0798 | No | Clear;Above 90 | Secondary | Broken | 24-0096444 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1962456 | 0 | EPSS Ckt | Y | 2024 | C GRD
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 2845 | 20240806 | 1545 | 20240806 | 1902 | 2536091 | 197 | Distribution Circuit | Animal | Bird found | 1 | 197 | 36.9551 | -121.7395 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 24-0096551 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1962496 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 64763 | 20240807 | 934 | 20240807 | 1202 | 2536620 | 148 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 148 | 36.8611 | -121.7951 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0096785 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Three Phase Fault | 0 | No | No | No | 1962727 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | TRANSFORMER | 413325155080 | 20240807 | 1005 | 20240807 | 1200 | 2536651 | 115 | Transformer only | Animal | Bird found | 2 | 230 | 36.8242 | -121.2826 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0096777 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1962724 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | OTHER | 3030 | 20240807 | 1153 | 20240807 | 2358 | 2536711 | 725 | Distribution Circuit | Equipment Failure/Involved | Overhead | 151 | 2825 | 36.5854 | -121.6002 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0096780 | OH | Sus | 46291910 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | Yes | 1962725 | 0 | EPSS Ckt | Y | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412125754272 | 20240807 | 1215 | 20240807 | 1246 | 2536742 | 31 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 62 | 36.7938 | -121.6907 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0096788 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1962729 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | TRANSFORMER | 412823359346 | 20240807 | 1336 | 20240807 | 1400 | 2536831 | 24 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 48 | 36.9385 | -121.4569 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0096848 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1962751 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 9813 | 20240807 | 1509 | 20240807 | 1726 | 2536909 | 128 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 36 | 4608 | 36.861 | -121.6873 | No | Clear;32-90 F |  |  | 24-0096963 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1962785 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | RECLOSER | 7004 | 20240807 | 1912 | 20240807 | 2331 | 2537088 | 259 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 150 | 38850 | 35.9367 | -121.0781 | No | Clear;32-90 F |  |  | 24-0096981 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1962796 | 0 | EPSS Ckt | Y | 2024 | B & C
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 4771 | 20240807 | 2027 | 20240807 | 2043 | 2537133 | 16 | Distribution Circuit | Equipment Failure/Involved | Overhead | 303 | 4848 | 36.9769 | -121.9169 | No | Clear;32-90 F | Connector or Splice (OH) | Burned/flashed | 24-0097001 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1962809 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | RECLOSER | 10788 | 20240807 | 2345 | 20240808 | 1328 | 2537231 | 823 | Distribution Circuit | 3rd Party | Vehicle | 890 | 82292 | 36.9044 | -121.7438 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 24-0097040 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Multi-Fault | 0 | No | Yes | No | 1962832 | 0 | EPSS Ckt | N | 2024 | A- B- C- & GRD
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | RECLOSER | 974130 | 20240808 | 1401 | 20240808 | 1503 | 2537901 | 62 | Distribution Circuit | 3rd Party | Customer Equipment | 91 | 5642 | 37.0448 | -121.9382 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0097331 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1963043 | 0 | EPSS Ckt | Y | 2024 | GRD
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 7427 | 20240808 | 1647 | 20240808 | 1915 | 2538168 | 148 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 144 | 21312 | 36.6001 | -121.8504 | No | Clear;32-90 F |  |  | 24-0097450 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1963085 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | KING CITY-1106 | 182031106 | FUSE | 768062 | 20240808 | 2048 | 20240808 | 2353 | 2538324 | 185 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 370 | 36.2299 | -121.0564 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0097467 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1963101 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | RECLOSER | 4048 | 20240809 | 39 | 20240809 | 623 | 2538399 | 344 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 123 | 31101 | 36.719 | -121.2811 | No | Clear;32-90 F |  |  | 24-0097484 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1963134 | 0 | EPSS Ckt | Y | 2024 | A & GRD
CENTRAL COAST | COAST | PAUL SWEET-2108 | 83252108 | TRANSFORMER | 315548417405 | 20240809 | 632 | 20240809 | 1331 | 2538442 | 419 | Transformer only | Equipment Failure/Involved | Electrical Overload | 7 | 2933 | 36.9677 | -122.0235 | No | Partly Cloudy-Fog;32-90 F | Transformer | Failed/Faulted | 24-0097542 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1963160 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | FUSE | 65633 | 20240809 | 940 | 20240809 | 1045 | 2538643 | 65 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 455 | 36.0937 | -120.9635 | No | Clear;32-90 F |  |  | 24-0097684 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1963297 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | RECLOSER | 5178 | 20240810 | 231 | 20240810 | 521 | 2539132 | 170 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 268 | 27184 | 37.0324 | -121.9467 | No | Clear;Above 90 |  |  | 24-0097941 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1963390 | 0 | EPSS Ckt | Y | 2024 | B & C
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 6029 | 20240810 | 604 | 20240810 | 1433 | 2539157 | 509 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 57008 | 36.6089 | -121.9306 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0097956 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1963403 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0421 | 182440421 | RECLOSER | 2616 | 20240810 | 831 | 20240811 | 611 | 2539226 | 1300 | Distribution Circuit | Vegetation | Tree - fell into line | 652 | 125509 | 36.6191 | -121.9159 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0097961 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Multi-Fault | 0 | No | Yes | No | 1963416 | 0 | Non-EPSS | N | 2024 | A-C-GRD
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316245518385 | 20240810 | 910 | 20240810 | 1039 | 2539242 | 89 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 356 | 36.9978 | -121.7869 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Deteriorated | 24-0097966 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1963424 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1102 | 182011102 | TRANSFORMER | 412330950525 | 20240810 | 1356 | 20240811 | 1200 | 2539605 | 1324 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1324 | 36.6925 | -121.6173 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0098037 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1963496 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | RECLOSER | 613162 | 20240810 | 1518 | 20240811 | 4 | 2539497 | 526 | Distribution Circuit | Equipment Failure/Involved | Overhead | 56 | 21938 | 36.5183 | -121.46 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0098014 | OH | Sus | 31704440 | SOUTH BAY AND CENTRAL COAST | AUG | Multi-Fault | 0 | No | Yes | No | 1963470 | 0 | EPSS Ckt | N | 2024 | A-B-GRD
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 10960 | 20240810 | 1641 | 20240810 | 2102 | 2539528 | 261 | Distribution Circuit | Equipment Failure/Involved | Underground | 2394 | 438194 | 36.9866 | -121.8582 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0098024 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1963479 | 0 | EPSS Ckt | Y | 2024 | B-GRD
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 9403 | 20240810 | 1644 | 20240810 | 1720 | 2539531 | 36 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 144 | 36.8682 | -121.3758 | No | Clear;32-90 F |  |  | 24-0098027 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1963482 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 9933 | 20240810 | 2231 | 20240811 | 1628 | 2539629 | 1040 | Distribution Circuit | Equipment Failure/Involved | Underground | 25 | 26925 | 36.943 | -121.7921 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0098043 | UG | Sus | 46297560 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1963504 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 280116 | 20240810 | 2349 | 20240811 | 1618 | 2539643 | 989 | Distribution Circuit | 3rd Party | Vehicle | 2245 | 341348 | 36.939 | -121.7423 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 24-0098045 | OH | Sus | 35572782 | SOUTH BAY AND CENTRAL COAST | AUG | Multi-Fault | 0 | No | Yes | No | 1963505 | 0 | EPSS Ckt | N | 2024 | AB GRD T/OC
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | FUSE | 4547 | 20240812 | 544 | 20240812 | 655 | 2539984 | 71 | Distribution Circuit | Animal | Bird found | 5 | 378 | 36.9791 | -121.965 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Normal | 24-0098141 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1963591 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | FUSE | 10241 | 20240812 | 559 | 20240812 | 854 | 2539986 | 175 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 2040 | 36.9625 | -121.9857 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken | 24-0098150 | OH | Sus | 46297648 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1963599 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | DEL MONTE-2104 | 182222104 | FUSE | 80489 | 20240812 | 704 | 20240812 | 915 | 2540006 | 131 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 655 | 36.5509 | -121.7377 | No | Clear;32-90 F |  |  | 24-0098204 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1963691 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | TRANSFORMER | 412299351670 | 20240812 | 755 | 20240812 | 940 | 2540094 | 105 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 105 | 36.7235 | -121.6289 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0098230 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1963737 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316494516090 | 20240812 | 834 | 20240812 | 936 | 2540163 | 62 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 62 | 36.9355 | -121.7005 | No | Overcast-Fog;32-90 F |  |  | 24-0098225 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1963732 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | FUSE | 24187 | 20240812 | 1829 | 20240813 | 447 | 2540657 | 618 | Distribution Circuit | Vegetation | Tree - branch fell on line | 218 | 36512 | 36.6755 | -121.665 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0098548 | OH | Sus | 31704507 | SOUTH BAY AND CENTRAL COAST | AUG | Three Phase Fault | 0 | No | Yes | No | 1963827 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 4975 | 20240812 | 2227 | 20240812 | 2314 | 2540826 | 47 | Distribution Circuit | 3rd Party | Metallic Balloon | 745 | 35015 | 36.9111 | -121.7612 | No | Partly Cloudy;32-90 F | Fuse | Normal | 24-0098579 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1963861 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316494516090 | 20240813 | 11 | 20240813 | 1240 | 2540482 | 749 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 749 | 36.9355 | -121.7005 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 24-0098580 | OH | Sus | 31704953 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1963864 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | SWITCH | 5439 | 20240813 | 520 | 20240813 | 528 | s1964201 | 8 | Distribution Circuit | Company Initiated | Return Circuit Normal | 110 | 880 | 36.6701 | -121.6685 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0098548 | OH | Sus | 31704507 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1964201 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | TRANSFORMER | 412189048681 | 20240813 | 1127 | 20240813 | 2108 | 2540897 | 581 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 581 | 36.6401 | -121.6643 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0098822 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1964073 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | TRANSFORMER | 411426845922 | 20240813 | 2042 | 20240813 | 2319 | 2541609 | 157 | Transformer only | Equipment Failure/Involved | Overhead | 20 | 3140 | 36.5587 | -121.921 | No | Partly Cloudy;32-90 F | Transformer (OH) | Deteriorated | 24-0099097 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1964155 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | RECLOSER | 281712 | 20240814 | 451 | 20240814 | 1805 | 2541699 | 794 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 8150 | 36.8038 | -121.4072 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0099128 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | Yes | No | 1964184 | 0 | EPSS Ckt | Y | 2024 | A & C PHASE
CENTRAL COAST | SALINAS | SPENCE-1101 | 182201101 | TRANSFORMER | 412905047160 | 20240814 | 951 | 20240814 | 1138 | 2541973 | 107 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 214 | 36.6046 | -121.4184 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0099245 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1964347 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | KING CITY-1106 | 182031106 | TRANSFORMER | 413920131590 | 20240814 | 1322 | 20240814 | 1724 | 2542168 | 242 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 242 | 36.1826 | -121.061 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0099367 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1964404 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | TRANSFORMER | 412511554280 | 20240814 | 1345 | 20240814 | 1410 | 2542159 | 25 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 25 | 36.7969 | -121.5581 | No | Clear;32-90 F | Fuse | Broken | 24-0099352 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1964400 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | TRANSFORMER | 315332422480 | 20240814 | 1405 | 20240815 | 502 | 2542087 | 897 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 897 | 37.106 | -122.1013 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0099381 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1964409 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | TRANSFORMER | 412423946111 | 20240814 | 1559 | 20240814 | 1805 | 2542284 | 126 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 504 | 36.5723 | -121.5804 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0099433 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1964429 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | OCB | 2109/2 | 20240814 | 1805 | 20240815 | 49 | 2542399 | 286 | Distribution Circuit | Equipment Failure/Involved | Underground | 11809 | 2578242 | 36.9926 | -121.982 | No | Clear;32-90 F | Connector or Splice (UG) | Failed/Faulted | 24-0099495 | UG | Sus | 46299264 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1964442 | 0 | EPSS Ckt | N | 2024 | B PHASE AND GRD
CENTRAL COAST | KING CITY | SOLEDAD-2104 | 182052104 | RECLOSER | 7248 | 20240814 | 1938 | 20240815 | 52 | 2542546 | 314 | Distribution Circuit | Equipment Failure/Involved | Overhead | 72 | 22608 | 36.4351 | -121.3426 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0099319 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1964448 | 0 | EPSS Ckt | N | 2024 | N/A
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 2113 | 20240814 | 2057 | 20240815 | 220 | 2542573 | 323 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 7752 | 36.6014 | -121.9339 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0099510 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1964454 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | RECLOSER | 4068 | 20240814 | 2136 | 20240815 | 340 | 2542594 | 364 | Distribution Circuit | Vegetation | Tree - fell into line | 1204 | 130520 | 36.8693 | -121.4001 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0099516 | OH | Sus | 31705240 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1964461 | 0 | EPSS Ckt | N | 2024 | A & C GRD
CENTRAL COAST | KING CITY | KING CITY-1106 | 182031106 | RECLOSER | 338712 | 20240815 | 100 | 20240815 | 415 | 2542655 | 195 | Distribution Circuit | 3rd Party | Metallic Balloon | 12 | 2340 | 36.1781 | -121.0463 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0099534 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1964470 | 0 | EPSS Ckt | Y | 2024 | B&C PHASE
CENTRAL COAST | KING CITY | SOLEDAD-2105 | 182052105 | SWITCH | 399550 | 20240815 | 122 | 20240815 | 237 | 2542660 | 75 | Distribution Circuit | Equipment Failure/Involved | Overhead | 414 | 24077 | 36.4565 | -121.3559 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0099512 | OH | Sus | 31705128 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1964471 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS COCHES-1102 | 182151102 | JUMPER | WIRE DOWN 1 LD SIDE OF 712011 | 20240815 | 551 | 20240815 | 1521 | 2542947 | 570 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 570 | 36.3755 | -121.2908 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0099670 | OH | Sus | 31705241 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1964550 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | FUSE | 9857 | 20240815 | 652 | 20240815 | 1602 | 2542709 | 550 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 8397 | 36.2979 | -121.1929 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0099693 | OH | Sus | 31705303 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1964557 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | RECLOSER | 91096 | 20240815 | 803 | 20240815 | 1116 | 2542737 | 170 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5630 | 176550 | 36.949 | -121.7922 | No | Partly Cloudy;32-90 F |  |  | 24-0099577 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1964497 | 0 | EPSS Ckt | Y | 2024 | A GRD
CENTRAL COAST | MONTEREY | FORT ORD-2106 | 182402106 | FUSE | 9781 | 20240815 | 1203 | 20240816 | 111 | 2542968 | 788 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 788 | 36.6406 | -121.8079 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 24-0099709 | OH | Sus | 31705224 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1964559 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | RECLOSER | 5002 | 20240815 | 1516 | 20240816 | 2335 | 2543071 | 1939 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 406 | 118254 | 36.7448 | -121.7388 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0099776 | OH | Sus | 46299658 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1964578 | 0 | EPSS Ckt | N | 2024 | N/A
CENTRAL COAST | KING CITY | KING CITY-1101 | 182031101 | FUSE | 9923 | 20240815 | 1648 | 20240815 | 1955 | 2542954 | 187 | Distribution Circuit | Equipment Failure/Involved | Underground | 3 | 561 | 36.2149 | -121.1246 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0099673 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1964552 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | FUSE | 281488 | 20240815 | 2100 | 20240816 | 754 | 2543308 | 654 | Distribution Circuit | 3rd Party | Vehicle | 6 | 3924 | 36.8612 | -121.4349 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0099848 | OH | Sus | 35574711 | SOUTH BAY AND CENTRAL COAST | AUG | Three Phase Fault | 0 | No | No | No | 1964612 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | RECLOSER | 478624 | 20240815 | 2257 | 20240816 | 57 | 2543336 | 120 | Distribution Circuit | Animal | Other | 643 | 77160 | 36.8828 | -121.7979 | No | Partly Cloudy;32-90 F | Switch (OH) | Normal | 24-0099854 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1964628 | 0 | EPSS Ckt | N | 2024 | NONE
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | RECLOSER | 7070 | 20240816 | 241 | 20240816 | 502 | 2543352 | 141 | Distribution Circuit | Equipment Failure/Involved | Overhead | 260 | 36660 | 35.9644 | -121.1175 | No | Clear;32-90 F | Capacitor | Failed/Faulted | 24-0099861 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1964634 | 0 | EPSS Ckt | Y | 2024 | B AND C PHASE
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | FUSE | 9201 | 20240816 | 557 | 20240816 | 1351 | 2543370 | 474 | Distribution Circuit | Equipment Failure/Involved | Overhead | 651 | 70068 | 36.6109 | -121.8988 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0099881 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1964647 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | RECLOSER | 91096 | 20240816 | 625 | 20240816 | 915 | 2543387 | 170 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5630 | 581468 | 36.949 | -121.7922 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0099865 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1964642 | 0 | EPSS Ckt | Y | 2024 | A-GRD
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | RECLOSER | 7014 | 20240816 | 708 | 20240816 | 1057 | 2543414 | 229 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 163 | 25186 | 36.3875 | -121.0045 | No | Fog;32-90 F |  |  | 24-0099883 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1964648 | 0 | Non-EPSS | Y | 2024 | A-B
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | TRANSFORMER | 412871142482 | 20240816 | 907 | 20240816 | 1017 | 2543566 | 70 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 70 | 36.4761 | -121.427 | No | Clear;32-90 F |  |  | 24-0099972 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1964793 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 5919 | 20240816 | 1010 | 20240816 | 1148 | 2543638 | 98 | Distribution Circuit | Animal | Bird found | 4 | 392 | 36.9609 | -122.0862 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 24-0100017 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1964808 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | RECLOSER | 91096 | 20240816 | 1642 | 20240816 | 2245 | 2543945 | 363 | Distribution Circuit | Vegetation | Tree - bark fell into line | 5634 | 2019482 | 36.949 | -121.7922 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0100200 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1964888 | 0 | EPSS Ckt | Y | 2024 | B PHASE
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 36514 | 20240816 | 1734 | 20240817 | 1302 | 2543980 | 1168 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 31568 | 37.0395 | -122.1518 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0100174 | OH | Sus | 46300476 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | Yes | No | 1964871 | 0 | EPSS Ckt | Y | 2024 | A-B
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | JUMPER | OJ 1 POLE NOTH OF CGC 413351636690 | 20240816 | 1857 | 20240816 | 2107 | 2544026 | 130 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 130 | 36.3205 | -121.2579 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0100183 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1964877 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRANSFORMER | 315590423766 | 20240816 | 2211 | 20240817 | 1430 | 2544077 | 979 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 979 | 37.1429 | -122.0141 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0100207 | OH | Sus | 35574974 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1964899 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DEL MONTE-2104 | 182222104 | FUSE | 5897 | 20240817 | 729 | 20240818 | 1641 | 2544169 | 1992 | Distribution Circuit | Equipment Failure/Involved | Underground | 5 | 9960 | 36.568 | -121.7484 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 24-0100237 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1964952 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | RECLOSER | 11046 | 20240817 | 1058 | 20240817 | 1432 | 2544296 | 214 | Distribution Circuit | Animal | Squirrel | 351 | 75114 | 36.9995 | -122.0078 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Normal | 24-0100254 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1964966 | 0 | EPSS Ckt | Y | 2024 | B GRD DCD
CENTRAL COAST | KING CITY | OILFIELDS-1103 | 182391103 | FUSE | 7381 | 20240817 | 1217 | 20240817 | 1455 | 2544357 | 158 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 474 | 35.8574 | -120.9653 | No | Clear;32-90 F |  |  | 24-0100284 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1964991 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | TRANSFORMER | 316395513921 | 20240817 | 1403 | 20240817 | 1513 | 2544397 | 70 | Transformer only | 3rd Party | Vehicle | 12 | 840 | 36.8757 | -121.7334 | No | Clear;32-90 F | Pole-Wood | Normal | 24-0100290 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1964994 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 11044 | 20240817 | 1947 | 20240818 | 833 | 2544558 | 766 | Distribution Circuit | Animal | Bird found | 2245 | 737566 | 37.0401 | -122.0297 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 24-0100326 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1965018 | 0 | EPSS Ckt | Y | 2024 | A PHASE AND GRD
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 11219 | 20240817 | 2032 | 20240818 | 1240 | 2544593 | 968 | Distribution Circuit | Animal | Squirrel | 4 | 3872 | 37.0318 | -121.9954 | No | Clear;32-90 F | Fuse | Normal | 24-0100342 | OH | Sus | 46300803 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1965034 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | TRANSFORMER | 316923515955 | 20240818 | 223 | 20240818 | 1422 | 2544636 | 719 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1438 | 36.9309 | -121.7903 | No | Overcast-Fog;32-90 F | Cutout- fuse holder | Arcing | 24-0100346 | OH | Sus | 31705520 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1965039 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | TRANSFORMER | 411467347937 | 20240818 | 457 | 20240818 | 1019 | 2544664 | 322 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 3864 | 36.6146 | -121.9091 | No | Overcast-Fog;32-90 F | Transformer | Failed/Faulted | 24-0100351 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1965045 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1103 | 182011103 | FUSE | 4981 | 20240818 | 809 | 20240818 | 2048 | 2544881 | 759 | Distribution Circuit | Equipment Failure/Involved | Underground | 5 | 3795 | 36.6979 | -121.6543 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0100417 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1965108 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | RECLOSER | 1132 | 20240818 | 904 | 20240818 | 1508 | 2544720 | 364 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 163 | 39895 | 36.3584 | -121.2034 | No | Fog;32-90 F |  |  | 24-0100364 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1965065 | 0 | Non-EPSS | Y | 2024 | A B
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | TRANSFORMER | 316075016720 | 20240818 | 1141 | 20240818 | 2325 | 2544743 | 704 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 2816 | 36.9514 | -121.8441 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0100387 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1965082 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1102 | 182011102 | OCB | 1102/2 | 20240818 | 1152 | 20240818 | 1638 | 2544771 | 286 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6885 | 294168 | 36.6828 | -121.6513 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0100385 | OH | Sus | 46300905 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1965080 | 0 | Non-EPSS | N | 2024 | B- GRD
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | TRANSFORMER | 411815550064 | 20240818 | 1353 | 20240818 | 2120 | 2544820 | 447 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 7152 | 36.6758 | -121.793 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0100405 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1965095 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 8937 | 20240818 | 2035 | 20240818 | 2327 | 2544936 | 172 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 8256 | 36.5029 | -121.9344 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0100439 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1965129 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | FUSE | 564785 | 20240818 | 2211 | 20240819 | 940 | 2544953 | 689 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 4134 | 36.286 | -121.2383 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0100441 | OH | Sus | 31705568 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | Yes | No | 1965131 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 11054 | 20240819 | 336 | 20240819 | 1125 | 2544995 | 469 | Distribution Circuit | Vegetation | Tree - branch fell on line | 309 | 34041 | 36.9775 | -121.7415 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0100446 | OH | Sus | 46300846 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1965137 | 0 | EPSS Ckt | Y | 2024 | A PHASE AND GRD INST
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | RECLOSER | 2020 | 20240819 | 824 | 20240819 | 1020 | 2545135 | 116 | Distribution Circuit | Company Initiated | Personnel- company | 830 | 10896 | 36.4632 | -121.7119 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0100486 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1965183 | 0 | EPSS Ckt | Y | 2024 | AC
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 33542 | 20240819 | 852 | 20240819 | 1406 | 2545210 | 314 | Distribution Circuit | Vegetation | Tree - fell into line | 399 | 36004 | 37.0906 | -122.0456 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0100500 | OH | Sus | 46302087 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1965215 | 0 | EPSS Ckt | Y | 2024 | BC
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | TRANSFORMER | 316528713075 | 20240819 | 1048 | 20240819 | 2205 | 2545420 | 677 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 677 | 36.8529 | -121.6877 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0100707 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1965346 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 316271012314 | 20240819 | 1839 | 20240819 | 1858 | 2545798 | 19 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 171 | 36.831 | -121.7751 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0100797 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1965373 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | RECLOSER | 3030 | 20240819 | 2200 | 20240820 | 12 | 2545961 | 132 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 217 | 21054 | 36.5854 | -121.6002 | No | Clear;32-90 F |  |  | 24-0100818 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1965398 | 0 | EPSS Ckt | Y | 2024 | B & C PHASE
CENTRAL COAST | MONTEREY | FORT ORD-2107 | 182402107 | TRANSFORMER | T1365 | 20240819 | 2331 | 20240820 | 38 | 2545975 | 67 | Transformer only | Unknown Cause | Patrol - found nothing | 5 | 335 | 36.6831 | -121.791 | No | Clear;32-90 F |  |  | 24-0100826 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1965412 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | JUMPER | OJ 3 POLES NORTH OF CGC 412088949888 | 20240820 | 55 | 20240820 | 437 | 2545984 | 222 | Distribution Circuit | 3rd Party | Vehicle | 1 | 222 | 36.6742 | -121.6985 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0100823 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1965407 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | HOLLISTER | TRES PINOS-1111 | 183221111 | FUSE | 9405 | 20240820 | 1320 | 20240820 | 1419 | 2546517 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 531 | 36.8028 | -121.3656 | No | Clear;32-90 F |  |  | 24-0101137 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1965653 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | TRANSFORMER | 412242852919 | 20240820 | 1432 | 20240820 | 2058 | 2546604 | 386 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1158 | 36.758 | -121.6502 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0101189 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1965667 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | RECLOSER | 2026 | 20240820 | 1520 | 20240821 | 2200 | 2546641 | 1840 | Distribution Circuit | Equipment Failure/Involved | Underground | 1288 | 184396 | 36.5315 | -121.8375 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0101169 | UG | Sus | 46302989 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1965659 | 0 | EPSS Ckt | Y | 2024 | A GRD
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | RECLOSER | 781810 | 20240820 | 1921 | 20240820 | 2133 | 2546778 | 132 | Distribution Circuit | Equipment Failure/Involved | Underground | 185 | 9370 | 36.9615 | -122.0627 | No | Clear;32-90 F | Recloser | Malfunctioning | 24-0101225 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Three Phase Fault | 0 | No | No | No | 1965682 | 0 | EPSS Ckt | Y | 2024 | ABC INST
CENTRAL COAST | SALINAS | SALINAS-1102 | 182011102 | FUSE | 24271 | 20240820 | 1951 | 20240820 | 2040 | 2546786 | 49 | Distribution Circuit | 3rd Party | Vehicle | 52 | 2548 | 36.6967 | -121.6391 | No | Clear;32-90 F | Pole-Wood | Normal | 24-0101235 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1965692 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2107 | 182402107 | FUSE | 40187 | 20240820 | 2045 | 20240820 | 2200 | 2546799 | 75 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 150 | 36.6775 | -121.779 | No | Clear;32-90 F | Transformer (UG) | Deteriorated | 24-0101234 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1965691 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1102 | 182011102 | SWITCH | 3864 | 20240820 | 2309 | 20240821 | 214 | s1966227 | 185 | Distribution Circuit | Equipment Failure/Involved | Underground | 16 | 2960 | 36.6978 | -121.6489 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0101148 | UG | Sus | 35575598 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1966227 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | KING CITY-1106 | 182031106 | RECLOSER | 202402 | 20240821 | 742 | 20240821 | 1036 | 2546950 | 174 | Distribution Circuit | 3rd Party | Vehicle | 8 | 1392 | 36.1765 | -121.0454 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0101293 | OH | Sus | 31705983 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1965758 | 0 | EPSS Ckt | N | 2024 | NA
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | OTHER | J530 TWD 668350 | 20240821 | 1148 | 20240821 | 1235 | 2547246 | 47 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 47 | 36.9163 | -121.7773 | No | Clear;32-90 F | Elbow | Failed/Faulted | 24-0101348 | UG | Sus | 46303066 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1965925 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 24955 | 20240821 | 1239 | 20240821 | 1816 | 2547309 | 337 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 337 | 36.7071 | -121.7023 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0101510 | OH | Sus | 31706080 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | Yes | 1965947 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | RECLOSER | 22158 | 20240821 | 1546 | 20240822 | 207 | 2547474 | 621 | Distribution Circuit | Vegetation | Tree - fell into line | 466 | 59751 | 36.7999 | -121.6992 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0101613 | OH | Sus | 46303296 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1965972 | 0 | EPSS Ckt | Y | 2024 | A GRD
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 9341 | 20240821 | 1927 | 20240821 | 2352 | 2547599 | 265 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 6360 | 36.9403 | -121.8592 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0101683 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1965987 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1106 | 182011106 | TRANSFORMER | 412194349635 | 20240821 | 1946 | 20240822 | 634 | 2547611 | 648 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 9072 | 36.6669 | -121.6632 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0101696 | OH | Sus | 35576044 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1965992 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 6137 | 20240822 | 254 | 20240822 | 2159 | 2547742 | 1145 | Distribution Circuit | Equipment Failure/Involved | Underground | 120 | 55686 | 36.5945 | -121.8932 | No | Overcast;32-90 F | Transformer (UG) | Failed/Faulted | 24-0101727 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Three Phase Fault | 0 | No | No | No | 1966031 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 40709 | 20240822 | 731 | 20240822 | 827 | 2547817 | 56 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 1846 | 36.5932 | -121.8935 | No | Overcast;32-90 F |  |  | 24-0101803 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1966107 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | SWITCH | 54167 | 20240822 | 732 | 20240822 | 2116 | 2547819 | 824 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 7416 | 37.0422 | -122.0486 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0101722 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1966049 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | RECLOSER | 974130 | 20240822 | 752 | 20240822 | 819 | 2547833 | 27 | Distribution Circuit | 3rd Party | Customer Equipment | 91 | 2457 | 37.0448 | -121.9382 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0101782 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1966053 | 0 | EPSS Ckt | Y | 2024 | GRD
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 5074 | 20240822 | 1725 | 20240822 | 2006 | 2548549 | 161 | Distribution Circuit | Company Initiated | Coordination failure | 154 | 24794 | 37.0208 | -122.2073 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0102142 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1966277 | 0 | EPSS Ckt | Y | 2024 | SGF DCD
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | OCB | 1111/2 | 20240822 | 1904 | 20240822 | 2151 | 2548603 | 167 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1603 | 267701 | 36.4778 | -121.7269 | No | Clear;32-90 F |  |  | 24-0102171 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1966289 | 0 | EPSS Ckt | Y | 2024 | B & C PHSE
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | TRANSFORMER | 315679517474 | 20240822 | 1920 | 20240823 | 159 | 2548610 | 399 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 5586 | 36.9703 | -121.9801 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 24-0102174 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1966291 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 5074 | 20240822 | 2030 | 20240822 | 2101 | 2548646 | 31 | Distribution Circuit | Company Initiated | Coordination failure | 154 | 4774 | 37.0208 | -122.2073 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0102189 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1966304 | 0 | EPSS Ckt | Y | 2024 | SGF DCD
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | SWITCH | 8844 | 20240822 | 2117 | 20240822 | 2231 | 2548658 | 74 | Distribution Circuit | Company Initiated | Return Circuit Normal | 18 | 1332 | 36.5344 | -121.8001 | No | Partly Cloudy;32-90 F | Conductor- Underground | Normal | 24-0101169 | UG | Sus | 46302989 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1966309 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | FUSE | 9073 | 20240823 | 535 | 20240823 | 652 | 2548806 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 539 | 36.952 | -121.4741 | No | Partly Cloudy;32-90 F |  |  | 24-0102231 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1966353 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 12417 | 20240823 | 1524 | 20240823 | 1940 | 2549383 | 256 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 2048 | 37.1377 | -122.0133 | No | Overcast;32-90 F |  |  | 24-0102640 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1966594 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1104 | 182381104 | JUMPER | FLYING BELLS 1P W/OF C643 | 20240824 | 100 | 20240824 | 422 | 2549581 | 202 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 202 | 36.77 | -121.7379 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0102454 | OH | Sus | 31705999 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1966605 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 316170918048 | 20240824 | 302 | 20240824 | 1040 | 2549594 | 458 | Distribution Circuit | Equipment Failure/Involved | Overhead | 106 | 19904 | 36.9883 | -121.812 | No | Overcast-Fog;32-90 F | Secondary | Broken- wire on object | 24-0102677 | OH | Sus | 46304764 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1966610 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 9107 | 20240824 | 937 | 20240824 | 1153 | 2550059 | 136 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 4216 | 36.5971 | -121.8988 | No | Partly Cloudy;32-90 F |  |  | 24-0102776 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1966715 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315368419807 | 20240824 | 1357 | 20240824 | 1502 | 2550233 | 65 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 390 | 37.033 | -122.0879 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0102796 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1966728 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 6477 | 20240825 | 217 | 20240825 | 626 | 2550624 | 249 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 427 | 106323 | 36.8655 | -121.7346 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0102870 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1966815 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | SWITCH | 6317 | 20240825 | 1306 | 20240825 | 2026 | 2550853 | 440 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 7722 | 36.9586 | -122.0575 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0102895 | OH | Sus | 35576604 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1966866 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | TRANSFORMER | 413058659518 | 20240826 | 702 | 20240826 | 1500 | 2551115 | 478 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 956 | 36.945 | -121.3769 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0103013 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1966997 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | FUSE | 994287 | 20240826 | 800 | 20240826 | 940 | 2551218 | 100 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 35 | 3500 | 36.8402 | -121.463 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0103028 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1967035 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2108 | 83252108 | FUSE | 4533 | 20240826 | 854 | 20240826 | 1400 | 2551290 | 306 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 7182 | 36.9775 | -122.0095 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0103140 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1967141 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1102 | 182201102 | JUMPER | JMPRS 1 S/S OF CGC 412647347765 | 20240826 | 1115 | 20240826 | 1537 | 2551453 | 262 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 262 | 36.6195 | -121.5063 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0103108 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1967124 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | TRANSFORMER | T1008 | 20240826 | 1519 | 20240826 | 1645 | 2551778 | 86 | Transformer only | Equipment Failure/Involved | Underground | 12 | 1032 | 36.9208 | -121.7835 | No | Clear;32-90 F | Connector or Splice (UG) | Broken | 24-0103270 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1967191 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SAN ARDO-1101 | 182191101 | RECLOSER | 7094 | 20240826 | 1552 | 20240826 | 1654 | 2551804 | 62 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 52 | 3224 | 36.1124 | -121.038 | No | Clear;Above 90 |  |  | 24-0103288 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1967196 | 0 | EPSS Ckt | Y | 2024 | A-B
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | RECLOSER | 91096 | 20240826 | 1713 | 20240826 | 2122 | 2551884 | 163 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5543 | 1049738 | 36.949 | -121.7922 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0103322 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1967207 | 0 | EPSS Ckt | Y | 2024 | A&C
CENTRAL COAST | MONTEREY | FORT ORD-2106 | 182402106 | TRANSFORMER | 411741748714 | 20240826 | 2133 | 20240826 | 2207 | 2552068 | 34 | Transformer only | Unknown Cause | Patrol - not conducted | 9 | 306 | 36.6384 | -121.8157 | No | Clear;32-90 F |  |  | 24-0103376 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1967238 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | FUSE | 265 | 20240827 | 1000 | 20240827 | 1028 | 2552379 | 28 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 392 | 37.0003 | -121.912 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0103530 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1967477 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | RECLOSER | 88772 | 20240827 | 1112 | 20240827 | 1225 | 2552585 | 73 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 1253 | 30170 | 36.904 | -121.6085 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0103562 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1967492 | 0 | EPSS Ckt | Y | 2024 | B&GRD
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | JUMPER | OJ 3 P/SS CGC 316115614895 | 20240827 | 1223 | 20240828 | 217 | 2552684 | 834 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 3336 | 36.9006 | -121.8291 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0103820 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1967609 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS COCHES-1101 | 182151101 | JUMPER | 9025 | 20240827 | 1229 | 20240827 | 1420 | 2552603 | 111 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 221 | 36.3432 | -121.319 | No | Clear;32-90 F | Jumper | Broken | 24-0103613 | OH | Sus | 46305823 | SOUTH BAY AND CENTRAL COAST | AUG | Open Circuit | 0 | No | No | No | 1967518 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | SWITCH | 2063 | 20240827 | 1310 | 20240827 | 1343 | 2552708 | 33 | Distribution Circuit | Equipment Failure/Involved | Overhead | 106 | 3498 | 36.8762 | -121.6275 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0103618 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1967520 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | FUSE | 9201 | 20240827 | 1421 | 20240827 | 1527 | 2552798 | 66 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 651 | 42966 | 36.6109 | -121.8988 | No | Clear;32-90 F |  |  | 24-0103673 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1967546 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1101 | 182131101 | SWITCH | 20243SB | 20240827 | 2343 | 20240828 | 335 | 2553255 | 232 | Distribution Circuit | Equipment Failure/Involved | Underground | 323 | 56372 | 36.5133 | -121.4341 | No | Clear;32-90 F | Transformer (UG) | Deteriorated | 24-0103668 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1967608 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SOLEDAD-2105 | 182052105 | OCB | 2105/2 | 20240828 | 546 | 20240828 | 1349 | 2553321 | 483 | Distribution Circuit | Equipment Failure/Involved | Overhead | 696 | 336168 | 36.4297 | -121.3323 | No | Partly Cloudy;32-90 F | Insulator | Broken- wire on ground | 24-0103840 | OH | Sus | 31706792 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1967632 | 0 | EPSS Ckt | N | 2024 | B-GRD
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | TRANSFORMER | 412638243538 | 20240828 | 655 | 20240828 | 2257 | 2553342 | 962 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 2886 | 36.5029 | -121.5061 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0103979 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1967825 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SOLEDAD-2102 | 182052102 | RECLOSER | 7008 | 20240828 | 702 | 20240828 | 906 | 2553346 | 124 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 98 | 12152 | 36.4058 | -121.3538 | No | Clear;32-90 F |  |  | 24-0103861 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1967643 | 0 | EPSS Ckt | Y | 2024 | B-GRD
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | RECLOSER | 2020 | 20240828 | 949 | 20240828 | 1010 | 2553672 | 21 | Distribution Circuit | Company Initiated | Personnel- company | 835 | 17535 | 36.4632 | -121.7119 | No | Clear;32-90 F | Fuse | Normal | 24-0104006 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1967838 | 0 | EPSS Ckt | Y | 2024 | SGF- DCD
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | TRANSFORMER | 412222650130 | 20240828 | 1219 | 20240828 | 2054 | 2553764 | 515 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 3605 | 36.6808 | -121.6539 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 24-0104125 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1967872 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0424 | 182440424 | OTHER | WIRE DOWN 1 POLE S/OF FUCO 10335 | 20240828 | 1315 | 20240829 | 47 | 2553981 | 692 | Distribution Circuit | Vegetation | Tree - fell into line | 106 | 73318 | 36.6247 | -121.9194 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0104237 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | Yes | 1967910 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | FUSE | 994287 | 20240828 | 1413 | 20240828 | 1559 | 2553961 | 106 | Distribution Circuit | Animal | Bird found | 35 | 3710 | 36.8402 | -121.463 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0104317 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1967925 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 7655 | 20240829 | 422 | 20240829 | 636 | 2554429 | 134 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1608 | 36.9728 | -122.0372 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0104475 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1967996 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | TRANSFORMER | 315526217868 | 20240829 | 910 | 20240829 | 2300 | 2555110 | 830 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 6640 | 36.9801 | -122.0314 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0104953 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1968279 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 4885 | 20240829 | 1016 | 20240829 | 1957 | 2554873 | 581 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 581 | 36.7587 | -121.7765 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 24-0104728 | OH | Sus | 31706655 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1968246 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | KING CITY-1106 | 182031106 | RECLOSER | 944510 | 20240829 | 1018 | 20240830 | 45 | 2554875 | 867 | Distribution Circuit | Equipment Failure/Involved | Overhead | 122 | 6796 | 36.2071 | -121.1151 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0104654 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Multi-Fault | 0 | No | No | No | 1968211 | 0 | EPSS Ckt | N | 2024 | ABC GRD INST OC
CENTRAL COAST | SALINAS | SOLEDAD-2105 | 182052105 | TRANSFORMER | 413039842005 | 20240829 | 1330 | 20240830 | 200 | 2554954 | 750 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 750 | 36.4648 | -121.3671 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0104811 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1968262 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 3721 | 20240829 | 1714 | 20240829 | 1729 | 2555234 | 15 | Distribution Circuit | Vegetation | Tree - grew into line | 19 | 285 | 37.0685 | -122.0584 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0104988 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1968287 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1103 | 182381103 | SWITCH | 25579 | 20240830 | 1003 | 20240830 | 1326 | 2555842 | 203 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 812 | 36.8028 | -121.7812 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 24-0105245 | OH | Sus | 46306770 | SOUTH BAY AND CENTRAL COAST | AUG | Open Circuit | 0 | No | No | No | 1968512 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 3721 | 20240830 | 1241 | 20240830 | 1532 | 2555971 | 171 | Distribution Circuit | Vegetation | Tree - grew into line | 19 | 3249 | 37.0685 | -122.0584 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0105334 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1968535 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | JUMPER | 4357 BLOWN HS JUMPER | 20240830 | 1349 | 20240830 | 1618 | 2556017 | 149 | Distribution Circuit | Equipment Failure/Involved | Overhead | 141 | 4009 | 36.9468 | -121.3843 | No | Clear;32-90 F | Jumper | Burned Open | 24-0105393 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1968548 | 1 | EPSS Ckt | Y | 2024
CENTRAL COAST | COAST | DOLAN ROAD-1101 | 182381101 | FUSE | 10539 | 20240830 | 2008 | 20240830 | 2200 | 2556249 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1008 | 36.8381 | -121.7923 | No | Clear;32-90 F |  |  | 24-0105519 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1968594 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | SWITCH | 557716 | 20240831 | 1520 | 20240831 | 1626 | 2556582 | 66 | Distribution Circuit | 3rd Party | Vehicle | 333 | 21978 | 36.831 | -121.6794 | No | Clear;32-90 F | Anchor or Guy | Broken | 24-0105604 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1968662 | 0 | EPSS Ckt | Y | 2024
CENTRAL COAST | SALINAS | BUENA VISTA-1106 | 182261106 | TRANSFORMER | 3967 | 20240831 | 1701 | 20240901 | 1212 | 2556624 | 1151 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 2217 | 36.633 | -121.6211 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0105624 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1968674 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | RECLOSER | 566352 | 20240901 | 218 | 20240901 | 431 | 2556989 | 133 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 665 | 36.7687 | -121.6076 | No | Clear;32-90 F |  |  | 24-0105652 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1968695 | 0 | Non-EPSS | Y | 2024 | C GRD
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | RECLOSER | 566352 | 20240901 | 436 | 20240901 | 548 | 2556998 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 360 | 36.7687 | -121.6076 | No | Clear;32-90 F |  |  | 24-0105655 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1968699 | 0 | Non-EPSS | Y | 2024 | A C
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 12590 | 20240901 | 823 | 20240901 | 1649 | 2557074 | 506 | Distribution Circuit | Vegetation | Tree - fell into line | 349 | 29894 | 37.0633 | -122.0798 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0105671 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1968714 | 0 | EPSS Ckt | Y | 2024 | B-G
CENTRAL COAST | SALINAS | BORONDA-1102 | 182461102 | TRANSFORMER | 412171250213 | 20240901 | 1013 | 20240901 | 1935 | 2557114 | 562 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 2248 | 36.6827 | -121.6713 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0105712 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1968745 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412199055256 | 20240901 | 1021 | 20240901 | 1532 | 2557155 | 311 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 1601 | 36.8222 | -121.6667 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0105708 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1968742 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 23577 | 20240901 | 1320 | 20240901 | 1540 | s1968752 | 140 | Distribution Circuit | Animal | Bird found | 4 | 560 | 36.8224 | -121.6668 | No | Clear;32-90 F | Fuse | Normal | 24-0105719 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1968752 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | RECLOSER | 1132 | 20240901 | 1343 | 20240901 | 1811 | 2557167 | 268 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 163 | 43684 | 36.3584 | -121.2034 | No | Clear;32-90 F |  |  | 24-0105711 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1968744 | 0 | Non-EPSS | Y | 2024 | C- INST OC
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | OCB | 2104/2 | 20240902 | 429 | 20240902 | 1410 | 2557442 | 581 | Distribution Circuit | 3rd Party | Vehicle | 683 | 76283 | 36.7632 | -121.7354 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 24-0105764 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | Yes | No | 1968793 | 0 | EPSS Ckt | N | 2024 | A B TIME
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 9265 | 20240902 | 846 | 20240902 | 934 | 2557487 | 48 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 1008 | 36.9662 | -121.8295 | No | Clear;32-90 F |  |  | 24-0105797 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1968812 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | TRANSFORMER | 315696917749 | 20240902 | 914 | 20240902 | 948 | 2557511 | 34 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 306 | 36.9779 | -121.973 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0105790 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1968810 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 6359 | 20240903 | 114 | 20240903 | 324 | 2557805 | 130 | Distribution Circuit | Animal | Bird found | 61 | 7930 | 36.8676 | -121.7489 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0105876 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1968871 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 23831 | 20240903 | 1121 | 20240903 | 1802 | 2558276 | 401 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 802 | 36.7403 | -121.6556 | No | Clear;32-90 F | Cutout- fuse holder | Failed/Faulted | 24-0106149 | OH | Sus | 31707250 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1969110 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 412059051584 | 20240903 | 1155 | 20240903 | 2240 | 2558008 | 645 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 645 | 36.7195 | -121.7107 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0106119 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1969103 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | TRANSFORMER | 412022452682 | 20240903 | 1501 | 20240903 | 1828 | 2558567 | 207 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 207 | 36.7492 | -121.7242 | No | Clear;32-90 F | Fuse | Broken | 24-0106403 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1969170 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | RECLOSER | 7082 | 20240903 | 1607 | 20240903 | 1725 | 2558617 | 78 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 675 | 49280 | 36.2872 | -121.2483 | No | Clear;Above 90 |  |  | 24-0106352 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1969156 | 0 | EPSS Ckt | Y | 2024 | A C
CENTRAL COAST | SALINAS | BUENA VISTA-1102 | 182261102 | TRANSFORMER | 412197848095 | 20240903 | 1827 | 20240904 | 1653 | 2558609 | 1346 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1346 | 36.6248 | -121.66 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0106442 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1969194 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | CASTROVILLE-2103 | 182352103 | JUMPER | BURNT OJ SS OF 23573 | 20240903 | 1848 | 20240904 | 350 | 2558806 | 542 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 4958 | 36.7126 | -121.7695 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 24-0106436 | OH | Sus | 31707254 | SOUTH BAY AND CENTRAL COAST | SEP | Open Circuit | 0 | No | No | No | 1969186 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 5074 | 20240903 | 2114 | 20240904 | 13 | 2558811 | 179 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 154 | 27566 | 37.0208 | -122.2073 | No | Clear;32-90 F |  |  | 24-0106438 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1969189 | 0 | EPSS Ckt | Y | 2024 | C INST OC
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | TRIP-SAVER | 3959 | 20240903 | 2115 | 20240903 | 2247 | 2558808 | 92 | Distribution Circuit | Vegetation | Tree - branch fell on line | 378 | 34776 | 36.959 | -122.0316 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0106443 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1969195 | 0 | EPSS Ckt | N | 2024 | NA
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 50899 | 20240904 | 612 | 20240904 | 740 | 2558930 | 88 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 704 | 36.8323 | -121.3483 | No | Clear;32-90 F |  |  | 24-0106508 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1969237 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1101 | 182201101 | OCB | 1101/2 | 20240904 | 2042 | 20240905 | 520 | 2559757 | 518 | Distribution Circuit | 3rd Party | Vehicle | 463 | 30793 | 36.6139 | -121.5668 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 24-0107008 | OH | Sus | 35579163 | SOUTH BAY AND CENTRAL COAST | SEP | Multi-Fault | 0 | No | Yes | No | 1969532 | 0 | Non-EPSS | N | 2024 | AB GRD
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 6689 | 20240905 | 349 | 20240905 | 623 | 2559800 | 154 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1694 | 36.8881 | -121.8071 | No | Clear;32-90 F |  |  | 24-0107027 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1969551 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | RECLOSER | 174580 | 20240905 | 430 | 20240905 | 936 | 2559806 | 306 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 73 | 22338 | 36.3398 | -121.2351 | No | Clear;32-90 F | Crossarm- Wood | Burned/flashed | 24-0107026 | OH | Sus | 31707649 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1969549 | 0 | EPSS Ckt | Y | 2024 | A GRD
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 1445 | 20240905 | 1409 | 20240905 | 1545 | 2560409 | 96 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 1152 | 36.5735 | -121.9108 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0107449 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Three Phase Fault | 0 | No | No | No | 1969787 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | TRANSFORMER | 412475354234 | 20240905 | 1531 | 20240905 | 1637 | 2560334 | 66 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 132 | 36.796 | -121.5736 | No | Clear;32-90 F | Transformer | Normal | 24-0107480 | OH | Sus | 46309403 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1969795 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | JUMPER | OJ AT CGC 411327447127 | 20240905 | 2125 | 20240906 | 648 | 2560676 | 563 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 10697 | 36.591 | -121.956 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0107607 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1969834 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | INTERRUPTER | 977600 | 20240906 | 937 | 20240906 | 2009 | 2561121 | 543 | Distribution Circuit | 3rd Party | Vehicle | 257 | 57794 | 36.9801 | -121.9084 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0107859 | OH | Sus | 35579513 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | No | 1970058 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1101 | 182201101 | TRANSFORMER | 412564447876 | 20240906 | 1002 | 20240906 | 1334 | 2561041 | 212 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 212 | 36.6217 | -121.5349 | No | Clear;32-90 F | Fuse | Burned Open | 24-0107989 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1970090 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 412098954163 | 20240906 | 1322 | 20240906 | 1350 | 2561280 | 28 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 252 | 36.7912 | -121.7001 | No | Clear;32-90 F | Connector or Splice (OH) | Burned/flashed | 24-0107979 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1970087 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 799851 | 20240906 | 1326 | 20240907 | 1535 | 2561286 | 1569 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1569 | 37.0763 | -121.9949 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0108113 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1970139 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | RECLOSER | 2166 | 20240906 | 1513 | 20240909 | 1625 | 2561402 | 4392 | Distribution Circuit | Equipment Failure/Involved | Overhead | 474 | 60918 | 36.2769 | -121.8264 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0108065 | OH | Sus | 46310589 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1970124 | 0 | EPSS Ckt | Y | 2024 | C
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 315988517392 | 20240906 | 1753 | 20240906 | 1911 | 2561546 | 78 | Transformer only | Unknown Cause | Patrol - found nothing | 6 | 468 | 36.9692 | -121.8729 | No | Clear;32-90 F |  |  | 24-0108129 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | None | 0 | No | No | No | 1970150 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 9229 | 20240906 | 2025 | 20240907 | 12 | 2561618 | 227 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 11804 | 37.0693 | -122.0577 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0108134 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1970156 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | RECLOSER | 196060 | 20240906 | 2220 | 20240908 | 119 | 2561672 | 1619 | Distribution Circuit | Equipment Failure/Involved | Underground | 200 | 57389 | 36.7702 | -121.7645 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 24-0108147 | UG | Sus | 35579751 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1970167 | 0 | Non-EPSS | N | 2024 | C GRD
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0421 | 182440421 | TRANSFORMER | 411462048065 | 20240906 | 2243 | 20240907 | 210 | 2561693 | 207 | Transformer only | Equipment Failure/Involved | Overhead | 35 | 7245 | 36.6178 | -121.9115 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0108149 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1970169 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 7939 | 20240906 | 2358 | 20240907 | 804 | 2561718 | 486 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 6318 | 36.9466 | -121.7165 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0108182 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1970225 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | RECLOSER | 781810 | 20240907 | 523 | 20240907 | 829 | 2561764 | 186 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 185 | 34410 | 36.9615 | -122.0627 | No | Clear;32-90 F |  |  | 24-0108162 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1970186 | 0 | EPSS Ckt | Y | 2024 | AB
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | FUSE | 9079 | 20240907 | 551 | 20240907 | 1430 | 2561806 | 519 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1038 | 36.8376 | -121.4551 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0108177 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | Yes | No | 1970201 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1101 | 182201101 | TRANSFORMER | 412543046070 | 20240907 | 1311 | 20240907 | 1611 | 2562043 | 180 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 180 | 36.5715 | -121.5412 | No | Clear;32-90 F | Fuse | Burned Open | 24-0108281 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1970302 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 90678 | 20240907 | 1657 | 20240907 | 1839 | 2562130 | 102 | Distribution Circuit | Vegetation | Tree - branch fell on line | 92 | 9384 | 37.0954 | -122.1281 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0108292 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1970306 | 0 | EPSS Ckt | Y | 2024 | A GRD
CENTRAL COAST | MONTEREY | DEL MONTE-1101 | 182221101 | TRANSFORMER | 411678748042 | 20240907 | 1711 | 20240907 | 1838 | 2562142 | 87 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 957 | 36.6187 | -121.837 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0108299 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1970312 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | RECLOSER | 96738 | 20240907 | 2146 | 20240908 | 1141 | 2562231 | 835 | Distribution Circuit | Vegetation | Tree - fell into line | 287 | 66024 | 37.1111 | -122.1142 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0108314 | OH | Sus | 31708060 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | No | 1970324 | 0 | EPSS Ckt | Y | 2024 | B GRD
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | RECLOSER | 491190 | 20240908 | 246 | 20240908 | 1248 | 2562277 | 455 | Distribution Circuit | Vegetation | Tree - branch fell on line | 808 | 112789 | 36.8008 | -121.7217 | No | Fog-Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0108325 | OH | Sus | 31708100 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | No | 1970337 | 0 | EPSS Ckt | Y | 2024 | SGF DCD
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 179 | 20240908 | 758 | 20240908 | 1231 | 2562437 | 273 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 936 | 37.0661 | -122.0336 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0108341 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1970357 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | TRANSFORMER | 316392613737 | 20240908 | 852 | 20240908 | 1921 | 2562464 | 629 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 6290 | 36.8708 | -121.7343 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0108354 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1970370 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1112 | 182371112 | FUSE | 2957 | 20240908 | 1305 | 20240908 | 1448 | 2562563 | 103 | Distribution Circuit | Vegetation | Tree - branch fell on line | 90 | 9275 | 36.4806 | -121.7357 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0108394 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1970393 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 3383 | 20240908 | 1536 | 20240908 | 1640 | 2562658 | 64 | Distribution Circuit | Vegetation | Tree - grew into line | 16 | 1024 | 36.8864 | -121.6337 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0108402 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1970397 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1112 | 182371112 | TRANSFORMER | 100000161056 | 20240908 | 1639 | 20240909 | 34 | 2562859 | 475 | Transformer only | Vegetation | Tree - fell into line | 4 | 1900 | 36.482 | -121.741 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 24-0108432 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1970435 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9181 | 20240909 | 27 | 20240909 | 319 | 2562895 | 172 | Distribution Circuit | 3rd Party | Vehicle | 13 | 2236 | 37.2288 | -122.148 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0108437 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1970445 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411829852938 | 20240909 | 801 | 20240909 | 1831 | 2563006 | 630 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 630 | 36.7556 | -121.7903 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 24-0108670 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1970652 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 11505 | 20240909 | 811 | 20240909 | 930 | 2563032 | 79 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 158 | 36.9042 | -121.7231 | No | Overcast-Fog;32-90 F |  |  | 24-0108536 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1970614 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 412088949888 | 20240909 | 935 | 20240909 | 1702 | 2563121 | 447 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 447 | 36.6729 | -121.6996 | No | Clear;32-90 F | Fuse | Burned Open | 24-0108572 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1970629 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316428517240 | 20240909 | 1217 | 20240909 | 2239 | 2563407 | 622 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 622 | 36.9673 | -121.7234 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0108768 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1970680 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | RECLOSER | 383718 | 20240909 | 1231 | 20240909 | 1345 | 2563431 | 74 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 713 | 39842 | 36.5788 | -121.7198 | No | Clear;32-90 F |  |  | 24-0108690 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1970657 | 0 | EPSS Ckt | Y | 2024 | A B
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | FUSE | 4752 | 20240909 | 1243 | 20240909 | 2326 | 2563445 | 643 | Distribution Circuit | Equipment Failure/Involved | Underground | 46 | 25918 | 36.8501 | -121.5423 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0108786 | UG | Sus | 35580214 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1970687 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | TRANSFORMER | 316204024110 | 20240909 | 1544 | 20240909 | 2340 | 2563655 | 476 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 476 | 36.882 | -121.7989 | No | Clear;32-90 F | Transformer (OH) | Contaminated | 24-0108891 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1970705 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | RECLOSER | 86338 | 20240909 | 1800 | 20240909 | 1831 | 2563760 | 31 | Distribution Circuit | Vegetation | Tree - branch fell on line | 230 | 7130 | 37.1125 | -122.1145 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0108906 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1970713 | 0 | EPSS Ckt | N | 2024 | NONE
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | TRANSFORMER | 413108059525 | 20240910 | 111 | 20240910 | 1330 | 2564074 | 739 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 739 | 36.9455 | -121.3607 | No | Overcast;32-90 F | Cutout- fuse holder | Broken | 24-0109045 | OH | Sus | 31708346 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1970883 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 412096055060 | 20240910 | 945 | 20240910 | 1915 | 2564245 | 570 | Transformer only | Vegetation | Tree - grew into line | 9 | 5130 | 36.816 | -121.7016 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0109110 | OH | Sus | 46319900 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | No | 1970972 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2102 | 182222102 | RECLOSER | 9060 | 20240910 | 946 | 20240910 | 954 | 2564393 | 8 | Distribution Circuit | Company Initiated | Operating error | 6 | 48 | 36.608 | -121.8536 | No | Overcast;32-90 F | Recloser | Normal | 24-0107914 | OH | Sus | 35379685 | SOUTH BAY AND CENTRAL COAST | SEP | None | 0 | No | No | No | 1970950 | 0 | EPSS Ckt | N | 2024 | NONE
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | TRANSFORMER | 316178514908 | 20240910 | 1132 | 20240910 | 1253 | 2564514 | 81 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 81 | 36.902 | -121.8079 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Burned Open | 24-0109206 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1971013 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1106 | 182011106 | TRANSFORMER | 412205149716 | 20240910 | 1753 | 20240911 | 1147 | 2564745 | 1074 | Transformer only | Vegetation | Tree - branch fell on line | 18 | 19332 | 36.6693 | -121.6593 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0109383 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1971062 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | KING CITY-1102 | 182031102 | FUSE | 7845 | 20240910 | 2022 | 20240910 | 2320 | 2564859 | 178 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 890 | 36.2594 | -121.0851 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0109406 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1971068 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | SWITCH | 12474 | 20240910 | 2212 | 20240911 | 1817 | 2564936 | 1205 | Distribution Circuit | Vegetation | Tree - fell into line | 8167 | 2250158 | 36.9713 | -121.8735 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0109420 | OH | Sus | 31708484 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | Yes | No | 1971085 | 0 | EPSS Ckt | Y | 2024
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | OCB | 2204/2 | 20240911 | 25 | 20240911 | 151 | 2564958 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8530 | 482762 | 36.5786 | -121.9084 | No | Overcast;32-90 F |  |  | 24-0109427 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1971093 | 0 | EPSS Ckt | Y | 2024 | AC
CENTRAL COAST | KING CITY | SOLEDAD-2105 | 182052105 | TRANSFORMER | 413095442502 | 20240911 | 1032 | 20240911 | 1222 | 2565372 | 110 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 110 | 36.4774 | -121.3497 | No | Clear;32-90 F |  |  | 24-0109714 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | None | 0 | No | No | No | 1971331 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRANSFORMER | 315470520521 | 20240911 | 1133 | 20240911 | 1854 | 2565441 | 441 | Transformer only | Vegetation | Tree - branch fell on line | 9 | 3969 | 37.0529 | -122.0525 | No | Clear;32-90 F | Jumper | Normal | 24-0109799 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1971363 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 12069 | 20240911 | 1415 | 20240911 | 1518 | 2565635 | 63 | Distribution Circuit | Vegetation | Tree - branch fell on line | 32 | 2016 | 37.1239 | -122.1197 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0109846 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1971377 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | TRANSFORMER | 412268246608 | 20240911 | 1433 | 20240911 | 1624 | 2565703 | 111 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 111 | 36.5848 | -121.6351 | No | Clear;32-90 F | Fuse | Burned Open | 24-0109907 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1971396 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRANSFORMER | 315220225728 | 20240911 | 1518 | 20240912 | 355 | 2565716 | 757 | Transformer only | Vegetation | Tree - fell into line | 3 | 2271 | 37.1948 | -122.142 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0109948 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1971419 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 10728 | 20240911 | 1518 | 20240911 | 1704 | 2565734 | 106 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1305 | 93042 | 37.0665 | -122.0797 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0109858 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1971379 | 0 | EPSS Ckt | Y | 2024 | A & GRD
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRANSFORMER | 315217425763 | 20240911 | 1559 | 20240912 | 149 | 2565787 | 590 | Transformer only | Vegetation | Tree - fell into line | 8 | 4720 | 37.1957 | -122.1429 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0109940 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1971412 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | SWITCH | 337544 | 20240911 | 1625 | 20240911 | 1829 | 2565815 | 124 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1364 | 36.9937 | -121.985 | No | Clear;32-90 F |  |  | 24-0109909 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1971397 | 0 | EPSS Ckt | Y | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | RECLOSER | 11056 | 20240911 | 1627 | 20240911 | 1951 | 2565827 | 204 | Distribution Circuit | Vegetation | Tree - branch fell on line | 448 | 91392 | 36.9937 | -122.0299 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0109912 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1971399 | 0 | EPSS Ckt | Y | 2024 | A/GRD
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 4807 | 20240911 | 1716 | 20240912 | 253 | 2565872 | 577 | Distribution Circuit | Equipment Failure/Involved | Underground | 109 | 62893 | 36.9193 | -121.7758 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0109971 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1971437 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | FUSE | 5743 | 20240911 | 1728 | 20240911 | 1930 | 2565879 | 122 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 732 | 37.1049 | -122.116 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0109956 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1971424 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | KING CITY-1101 | 182031101 | TRANSFORMER | 413716332496 | 20240911 | 1845 | 20240912 | 400 | 2565904 | 555 | Transformer only | Vegetation | Tree - grew into line | 10 | 5550 | 36.2063 | -121.1311 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0109951 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1971422 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | TRANSFORMER | 315931417672 | 20240911 | 1857 | 20240911 | 2212 | 2565937 | 195 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 585 | 36.9773 | -121.8928 | No | Clear;32-90 F |  |  | 24-0109983 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | None | 0 | No | No | No | 1971449 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 4959 | 20240911 | 2122 | 20240912 | 829 | 2566022 | 667 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 3335 | 36.9637 | -121.8096 | No | Clear;32-90 F |  |  | 24-0110000 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1971463 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | FUSE | 3515 | 20240911 | 2242 | 20240912 | 520 | 2566040 | 398 | Distribution Circuit | Equipment Failure/Involved | Underground | 142 | 15344 | 36.663 | -121.6711 | No | Overcast;32-90 F | Conductor- Underground | Burned/flashed | 24-0109994 | UG | Sus | 46320684 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1971455 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411832553562 | 20240912 | 745 | 20240912 | 1143 | 2566229 | 238 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 238 | 36.7721 | -121.7901 | No | Clear;32-90 F |  |  | 24-0110245 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1971681 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 931192 | 20240912 | 955 | 20240912 | 1100 | 2566478 | 65 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1057 | 68705 | 36.9754 | -121.8942 | No | Clear;32-90 F |  |  | 24-0110171 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1971654 | 0 | EPSS Ckt | Y | 2024 | B & GRD
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 315988517392 | 20240912 | 1820 | 20240913 | 233 | 2566903 | 493 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 2958 | 36.9692 | -121.8729 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0110517 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1971735 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | TRANSFORMER | MTR#1008553573 | 20240912 | 2055 | 20240913 | 43 | 2566973 | 214 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1070 | 36.5681 | -121.8953 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0110525 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1971746 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | RECLOSER | 4002 | 20240912 | 2212 | 20240913 | 847 | 2567003 | 635 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 171 | 31317 | 36.8322 | -121.5312 | No | Clear;32-90 F |  |  | 24-0110529 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1971757 | 0 | EPSS Ckt | Y | 2024 | B/C- INST
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | RECLOSER | 741002 | 20240912 | 2257 | 20240913 | 1242 | 2567012 | 825 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 306 | 190242 | 36.5969 | -121.6247 | No | Clear;32-90 F |  |  | 24-0110531 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1971762 | 0 | EPSS Ckt | Y | 2024 | C-G
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | FUSE | 861 | 20240913 | 607 | 20240913 | 733 | 2567146 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 2666 | 36.9875 | -121.9653 | No | Partly Cloudy;32-90 F |  |  | 24-0110600 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1971812 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | FUSE | 4587 | 20240913 | 734 | 20240913 | 804 | 2567132 | 30 | Distribution Circuit | Animal | Squirrel | 71 | 2130 | 36.9879 | -121.9718 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0110623 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1971853 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2103 | 83252103 | TRANSFORMER | 315571817456 | 20240913 | 759 | 20240913 | 1116 | 2567158 | 197 | Transformer only | Equipment Failure/Involved | Overhead | 26 | 5122 | 36.9692 | -122.0156 | No | Partly Cloudy;32-90 F | Transformer | Broken | 24-0110631 | OH | Sus | 31708726 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1971863 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2106 | 182402106 | TRANSFORMER | 411771948706 | 20240913 | 804 | 20240913 | 933 | 2567179 | 89 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 801 | 36.6384 | -121.8057 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken | 24-0110686 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1971930 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | TRANSFORMER | 413001854702 | 20240913 | 846 | 20240913 | 923 | 2567331 | 37 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 74 | 36.8116 | -121.3919 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0110671 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1971920 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | BUENA VISTA-1106 | 182261106 | TRANSFORMER | 100000025599 | 20240913 | 910 | 20240913 | 1810 | 2567306 | 540 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1080 | 36.6348 | -121.6308 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0110667 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1971916 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412139054056 | 20240913 | 1845 | 20240914 | 1506 | 2567792 | 1221 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2442 | 36.7885 | -121.6868 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0110946 | OH | Sus | 35581384 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1972023 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | TRANSFORMER | 411451247192 | 20240914 | 813 | 20240914 | 1810 | 2568040 | 597 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 4776 | 36.5937 | -121.9142 | No | Partly Cloudy-Fog;32-90 F | Secondary | Burned/flashed | 24-0111009 | OH | Sus | 46321896 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1972124 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | TRANSFORMER | 411373647468 | 20240914 | 1137 | 20240914 | 1549 | 2568177 | 252 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 1764 | 36.6008 | -121.9407 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0111048 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1972141 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | RECLOSER | 22412 | 20240914 | 1150 | 20240915 | 932 | 2568199 | 1302 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 126 | 25893 | 36.4699 | -121.4635 | No | Clear;32-90 F |  |  | 24-0111054 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1972144 | 0 | EPSS Ckt | Y | 2024 | C- GRD- INST OC
CENTRAL COAST | HOLLISTER | TRES PINOS-1111 | 183221111 | FUSE | 4391 | 20240914 | 1842 | 20240914 | 2100 | 2568416 | 138 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1932 | 36.8004 | -121.2712 | No | Clear;32-90 F |  |  | 24-0111115 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1972194 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 95690 | 20240915 | 856 | 20240915 | 1508 | 2568639 | 372 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2125 | 145894 | 37.1249 | -122.125 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0111149 | OH | Sus | 35581527 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1972227 | 0 | EPSS Ckt | Y | 2024 | A&B PHASE
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | OTHER | WIRE DOWN 1 SS OF 279434 | 20240915 | 1134 | 20240915 | 1741 | 2568737 | 367 | Distribution Circuit | Vegetation | Tree - branch fell on line | 554 | 63066 | 37.0694 | -121.9951 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0111172 | OH | Sus | 46321982 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | Yes | 1972254 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | RECLOSER | 741002 | 20240915 | 1329 | 20240915 | 1714 | 2568826 | 225 | Distribution Circuit | Equipment Failure/Involved | Underground | 306 | 51570 | 36.5969 | -121.6247 | No | Overcast;32-90 F | Transformer (UG) | Failed/Faulted | 24-0111184 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1972265 | 0 | EPSS Ckt | Y | 2024 | GRD
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 4953 | 20240915 | 1340 | 20240915 | 1925 | 2568843 | 345 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 113 | 39120 | 36.8253 | -121.6618 | No | Clear;32-90 F |  |  | 24-0111224 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1972301 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | OCB | 1101/2 | 20240915 | 1439 | 20240915 | 1652 | 2568871 | 133 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2413 | 306867 | 36.6242 | -121.6887 | No | Clear;32-90 F |  |  | 24-0111194 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1972274 | 0 | EPSS Ckt | Y | 2024 | A C
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | FUSE | 23809 | 20240915 | 1730 | 20240916 | 310 | 2568972 | 580 | Distribution Circuit | Equipment Failure/Involved | Underground | 3 | 1740 | 36.5759 | -121.6292 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0111213 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1972286 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | RECLOSER | 648928 | 20240916 | 931 | 20240916 | 1000 | 2569514 | 29 | Distribution Circuit | Company Initiated | Personnel- company | 405 | 9041 | 36.5332 | -121.9152 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0111390 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1972519 | 0 | EPSS Ckt | Y | 2024 | SGF DCD
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | FUSE | 977577 | 20240916 | 1214 | 20240916 | 1300 | 2569732 | 46 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 92 | 36.8489 | -121.4653 | No | Overcast;32-90 F |  |  | 24-0111560 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1972589 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | FUSE | 7819 | 20240916 | 1445 | 20240916 | 1545 | 2569876 | 60 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 360 | 36.5413 | -121.4555 | No | Overcast;32-90 F |  |  | 24-0111693 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1972633 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | JUMPER | OJS 2 SPANS SS OF CGC 412814556404 | 20240916 | 1630 | 20240916 | 1935 | 2569923 | 185 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 185 | 36.8566 | -121.456 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0111726 | OH | Sus | 46322365 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1972641 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | FUSE | 4167 | 20240916 | 1646 | 20240916 | 1827 | 2569972 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1111 | 36.8626 | -121.5401 | No | Partly Cloudy;32-90 F |  |  | 24-0111752 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1972654 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1102 | 182011102 | TRANSFORMER | 412341550463 | 20240916 | 1826 | 20240916 | 1839 | 2570039 | 13 | Transformer only | Equipment Failure/Involved | Overhead | 21 | 273 | 36.6908 | -121.6137 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken | 24-0111749 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1972653 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | RECLOSER | 440 | 20240917 | 48 | 20240917 | 805 | 2570209 | 437 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 382 | 59826 | 36.4389 | -121.9203 | No | Clear;32-90 F |  |  | 24-0111796 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1972692 | 0 | EPSS Ckt | Y | 2024 | B-C INST
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 4441 | 20240917 | 754 | 20240917 | 919 | 2570291 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 1275 | 36.8205 | -121.6462 | No | Clear;32-90 F |  |  | 24-0111899 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1972859 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | FUSE | 7819 | 20240917 | 1212 | 20240917 | 1322 | 2570729 | 70 | Distribution Circuit | 3rd Party | Metallic Balloon | 6 | 420 | 36.5413 | -121.4555 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0112031 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1972946 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | FUSE | 4746 | 20240917 | 1659 | 20240918 | 1822 | 2570943 | 1523 | Distribution Circuit | Equipment Failure/Involved | Underground | 363 | 271978 | 36.8278 | -121.3736 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0112173 | UG | Sus | 35581899 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1972987 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 63161 | 20240917 | 2021 | 20240917 | 2248 | 2570976 | 147 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 294 | 36.7949 | -121.7125 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Deteriorated | 24-0112168 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1972984 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9579 | 20240917 | 2210 | 20240917 | 2221 | 2571098 | 11 | Distribution Circuit | Vegetation | Tree - grew into line | 165 | 1815 | 37.1732 | -122.1382 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0112197 | OH | Sus | 46322805 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1973002 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | SWITCH | 4111 | 20240917 | 2210 | 20240918 | 1057 | s1973581 | 767 | Distribution Circuit | Vegetation | Tree - grew into line | 58 | 44486 | 37.1754 | -122.1386 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0112197 | OH | Sus | 46322805 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1973581 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | RECLOSER | 586340 | 20240918 | 645 | 20240918 | 825 | 2571179 | 100 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 217 | 13872 | 36.5537 | -121.694 | No | Clear;32-90 F |  |  | 24-0112245 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1973033 | 0 | EPSS Ckt | Y | 2024 | A- B & INST OC
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | SWITCH | 25307 | 20240918 | 1248 | 20240918 | 1442 | 2571676 | 114 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 228 | 36.5566 | -121.4461 | No | Overcast;32-90 F | Metering Equipment | Deteriorated | 24-0112443 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1973284 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | SWITCH | 7081 | 20240918 | 1316 | 20240918 | 1325 | 2571734 | 9 | Distribution Circuit | Company Initiated | Return Circuit Normal | 165 | 1485 | 37.1745 | -122.1444 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0112197 | OH | Sus | 46322805 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1973307 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1102 | 182011102 | TRANSFORMER | T1995 | 20240918 | 1439 | 20240918 | 2137 | 2571639 | 418 | Transformer only | Equipment Failure/Involved | Underground | 14 | 5852 | 36.6926 | -121.6103 | No | Partly Cloudy;32-90 F | Connector or Splice (UG) | Deteriorated | 24-0112632 | UG | Sus | 46323273 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1973335 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | RECLOSER | 432 | 20240918 | 1517 | 20240918 | 1552 | 2571845 | 35 | Distribution Circuit | Company Initiated | Personnel- company | 324 | 11340 | 36.398 | -121.6493 | No | Partly Cloudy;32-90 F | Capacitor | Normal | 24-0112674 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1973342 | 0 | EPSS Ckt | Y | 2024 | A B
CENTRAL COAST | KING CITY | LOS COCHES-1101 | 182151101 | FUSE | 7703 | 20240918 | 1935 | 20240918 | 2134 | 2572034 | 119 | Distribution Circuit | Animal | Bird found | 10 | 1190 | 36.3357 | -121.3167 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Normal | 24-0112786 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1973382 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | TRANSFORMER | 315793717809 | 20240918 | 2312 | 20240919 | 106 | 2572102 | 114 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 456 | 36.98 | -121.9403 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 24-0112790 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1973384 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | RECLOSER | 7030 | 20240919 | 244 | 20240920 | 2054 | 2572148 | 2530 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 107 | 270710 | 36.2025 | -120.8432 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0112806 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Multi-Fault | 0 | No | No | No | 1973396 | 0 | EPSS Ckt | Y | 2024 | A-C-GRD
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | RECLOSER | 502 | 20240919 | 514 | 20240920 | 1421 | 2572164 | 1987 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 111272 | 36.1289 | -121.0147 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0112812 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1973402 | 0 | EPSS Ckt | Y | 2024 | C.GRD
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | RECLOSER | 94020 | 20240919 | 530 | 20240919 | 1109 | 2572167 | 339 | Distribution Circuit | Environmental/External | Lightning | 25 | 8475 | 36.1282 | -121.0198 | No | Partly Cloudy-Fog;32-90 F | Jumper | Broken | 24-0112814 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1973403 | 0 | EPSS Ckt | N | 2024 | A-GRD
CENTRAL COAST | KING CITY | KING CITY-1101 | 182031101 | FUSE | 8935 | 20240919 | 634 | 20240919 | 1947 | 2572209 | 793 | Distribution Circuit | Environmental/External | Lightning | 34 | 15970 | 36.2097 | -121.1218 | No | Overcast-Fog;32-90 F | Transformer (OH) | Burned/flashed | 24-0112882 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1973466 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | RECLOSER | 2020 | 20240919 | 805 | 20240919 | 1644 | 2572269 | 519 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 839 | 435441 | 36.4632 | -121.7119 | No | Clear;32-90 F |  |  | 24-0112871 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1973449 | 0 | EPSS Ckt | Y | 2024 | A- B- & INST OC
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | RECLOSER | 91894 | 20240919 | 859 | 20240919 | 1845 | 2572334 | 586 | Distribution Circuit | Environmental/External | Lightning | 261 | 152946 | 36.0206 | -120.9005 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0112897 | OH | Sus | 31709343 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | No | 1973491 | 0 | EPSS Ckt | N | 2024 | A GRD
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | RECLOSER | 7004 | 20240919 | 901 | 20240919 | 930 | 2572348 | 29 | Distribution Circuit | Environmental/External | Lightning | 149 | 4321 | 35.9367 | -121.0781 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0112896 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1973488 | 0 | EPSS Ckt | Y | 2024 | A-C
CENTRAL COAST | KING CITY | OILFIELDS-1102 | 182391102 | FUSE | 7429 | 20240919 | 938 | 20240919 | 1650 | 2572422 | 432 | Distribution Circuit | Environmental/External | Lightning | 4 | 1694 | 35.9674 | -120.8586 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Normal | 24-0113239 | OH | Sus | 46323841 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1973612 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2106 | 182402106 | TRANSFORMER | 411793048896 | 20240919 | 1014 | 20240920 | 1313 | 2572454 | 1619 | Transformer only | Equipment Failure/Involved | Underground | 1 | 1619 | 36.6436 | -121.7989 | No | Overcast;32-90 F | Transformer | Failed/Faulted | 24-0113142 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1973586 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | TRANSFORMER | 413938423499 | 20240919 | 1514 | 20240920 | 101 | 2572719 | 587 | Transformer only | Environmental/External | Lightning | 2 | 1174 | 35.9611 | -121.0456 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0113260 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1973618 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | OTHER | J914 TWD T0645 | 20240919 | 1636 | 20240919 | 1712 | 2572782 | 36 | Distribution Circuit | Equipment Failure/Involved | Underground | 27 | 972 | 36.8316 | -121.3966 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0113207 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1973613 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | RECLOSER | 258878 | 20240919 | 1653 | 20240920 | 905 | 2572794 | 972 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 15552 | 36.2313 | -121.1769 | No | Partly Cloudy;32-90 F |  |  | 24-0113253 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1973616 | 0 | EPSS Ckt | Y | 2024 | B C TIME INST
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | RECLOSER | 91424 | 20240919 | 1913 | 20240919 | 2150 | 2572894 | 157 | Distribution Circuit | Company Initiated | Coordination failure | 142 | 22294 | 36.9335 | -121.3885 | No | Clear;32-90 F | Recloser | Normal | 24-0113304 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1973633 | 0 | EPSS Ckt | Y | 2024 | SGF & DCD
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0424 | 182440424 | TRANSFORMER | 411417148435 | 20240919 | 2017 | 20240919 | 2333 | 2572882 | 196 | Transformer only | Vegetation | Tree - branch fell on line | 4 | 784 | 36.6276 | -121.9271 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 24-0113302 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1973632 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | TRANSFORMER | 414365825454 | 20240920 | 452 | 20240920 | 1259 | 2573030 | 487 | Transformer only | Environmental/External | Lightning | 2 | 974 | 36.017 | -120.9067 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0113441 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1973695 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | TRANSFORMER | 414359025438 | 20240920 | 713 | 20240920 | 1050 | 2573084 | 217 | Transformer only | Environmental/External | Lightning | 2 | 434 | 36.0169 | -120.9085 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0113453 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1973701 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | TRANSFORMER | 315817218889 | 20240920 | 1356 | 20240920 | 1501 | 2573586 | 65 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 65 | 37.0088 | -121.9328 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0113804 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1973934 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | FUSE | 23351 | 20240921 | 524 | 20240921 | 744 | 2573832 | 140 | Distribution Circuit | 3rd Party | Metallic Balloon | 4 | 560 | 36.529 | -121.4753 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 24-0113906 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1973982 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | TRANSFORMER | 316747013498 | 20240921 | 746 | 20240922 | 733 | 2573857 | 1427 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 4281 | 36.8655 | -121.6122 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0113948 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1974065 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1103 | 182011103 | SWITCH | 59416 | 20240921 | 1422 | 20240921 | 1432 | 2574103 | 10 | Distribution Circuit | 3rd Party | Metallic Balloon | 426 | 4260 | 36.7015 | -121.6522 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0114034 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1974110 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 7371 | 20240922 | 906 | 20240922 | 1055 | 2574454 | 109 | Distribution Circuit | Animal | Squirrel | 6 | 654 | 37.0585 | -122.142 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0114120 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1974220 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | OCB | 2204/2 | 20240922 | 1710 | 20240923 | 242 | 2574648 | 375 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8532 | 1412691 | 36.5786 | -121.9084 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 24-0114150 | OH | Sus | 46325051 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1974261 | 0 | EPSS Ckt | N | 2024 | UNKNOWN
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 67520 | 20240922 | 1958 | 20240922 | 2311 | 2574705 | 193 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2732 | 114538 | 36.9577 | -121.8525 | No | Partly Cloudy;32-90 F |  |  | 24-0114160 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1974273 | 0 | EPSS Ckt | Y | 2024 | B-C
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | FUSE | 2315 | 20240923 | 509 | 20240923 | 1700 | 2574864 | 711 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 6399 | 36.275 | -121.1874 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0114192 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | Yes | Yes | 1974300 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 9733 | 20240923 | 651 | 20240923 | 1336 | 2574891 | 375 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 765 | 36.8755 | -121.3546 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0114208 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1974323 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | PANOCHE-1103 | 253671103 | RECLOSER | 4010 | 20240923 | 800 | 20240923 | 1256 | 2574973 | 296 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 151 | 39416 | 36.5951 | -120.7911 | No | Clear;32-90 F |  |  | 24-0114221 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1974342 | 0 | EPSS Ckt | N | 2024 | A & B PHASE
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | TRANSFORMER | 315479616969 | 20240923 | 808 | 20240923 | 901 | 2575016 | 53 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 318 | 36.9558 | -122.0479 | No | Clear;32-90 F | Fuse | Broken | 24-0114247 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1974436 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 10599 | 20240923 | 1011 | 20240923 | 1119 | 2575303 | 68 | Distribution Circuit | Animal | Bird found | 1 | 68 | 36.9386 | -121.7424 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 24-0114324 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1974512 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 23385 | 20240923 | 1012 | 20240923 | 1436 | 2575260 | 264 | Distribution Circuit | Vegetation | Tree - branch fell on line | 87 | 5166 | 36.8434 | -121.6756 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0114310 | OH | Sus | 46325099 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | Yes | 1974511 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | TRANSFORMER | 316646014451 | 20240923 | 1037 | 20240923 | 1229 | 2575282 | 112 | Transformer only | 3rd Party | Vehicle | 2 | 224 | 36.8913 | -121.6478 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0114377 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1974535 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1108 | 182011108 | FUSE | 4529 | 20240923 | 1107 | 20240923 | 2050 | 2575297 | 583 | Distribution Circuit | 3rd Party | Vandalism | 1 | 583 | 36.6673 | -121.635 | No | Clear;32-90 F | Pothead(Riser Termination) | Broken | 24-0114330 | OH | Sus | 46325557 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1974519 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 10954 | 20240923 | 1331 | 20240924 | 0 | 2575446 | 629 | Distribution Circuit | Vegetation | Tree - fell into line | 501 | 30200 | 36.9873 | -121.86 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0114427 | OH | Sus | 46325728 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | No | 1974549 | 0 | EPSS Ckt | Y | 2024 | C GRD
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 4557 | 20240923 | 1356 | 20240923 | 1430 | 2575469 | 34 | Distribution Circuit | Animal | Bird found | 6 | 215 | 36.9276 | -121.7673 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 24-0114473 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1974559 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8961 | 20240923 | 1427 | 20240923 | 2200 | 2575502 | 453 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 906 | 37.0432 | -122.0518 | No | Clear;32-90 F |  |  | 24-0114614 | OH | Sus | 46325691 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1974625 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | RECLOSER | 91424 | 20240923 | 1950 | 20240923 | 2142 | 2575756 | 112 | Distribution Circuit | Company Initiated | Coordination failure | 142 | 15904 | 36.9335 | -121.3885 | No | Clear;32-90 F | Recloser | Normal | 24-0114593 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1974604 | 0 | EPSS Ckt | Y | 2024 | SGF/DCD
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | TRANSFORMER | 412328252718 | 20240923 | 2144 | 20240923 | 2237 | 2575812 | 53 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 477 | 36.7527 | -121.6218 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0114611 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1974622 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | RECLOSER | 91424 | 20240923 | 2244 | 20240923 | 2253 | 2575836 | 9 | Distribution Circuit | Company Initiated | Coordination failure | 142 | 1278 | 36.9335 | -121.3885 | No | Clear;32-90 F | Recloser | Normal | 24-0114625 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1974631 | 0 | EPSS Ckt | Y | 2024 | SGF-DCD
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 9097 | 20240923 | 2250 | 20240924 | 618 | 2575832 | 448 | Distribution Circuit | Vegetation | Tree - grew into line | 18 | 8064 | 36.9798 | -122.0393 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Arcing | 24-0114624 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1974629 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 40345 | 20240924 | 439 | 20240924 | 1050 | 2575885 | 371 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1113 | 36.5314 | -121.837 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0114847 | OH | Sus | 31709884 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1974865 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | RECLOSER | 11048 | 20240924 | 821 | 20240924 | 1543 | 2576081 | 442 | Distribution Circuit | 3rd Party | Vehicle | 747 | 89265 | 37.0482 | -122.0339 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0114719 | OH | Sus | 35583326 | SOUTH BAY AND CENTRAL COAST | SEP | Multi-Fault | 0 | No | No | No | 1974731 | 0 | EPSS Ckt | Y | 2024 | A C GRD
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | SWITCH | 417233 | 20240924 | 950 | 20240924 | 1440 | 2576235 | 290 | Distribution Circuit | 3rd Party | Vehicle | 120 | 34800 | 36.7103 | -121.6237 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0114785 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1974827 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 6647 | 20240924 | 1209 | 20240924 | 1304 | 2576428 | 55 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 1410 | 36.6035 | -121.8967 | No | Clear;32-90 F |  |  | 24-0114916 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1974911 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | TRANSFORMER | 414802231825 | 20240924 | 1507 | 20240924 | 1940 | 2576530 | 273 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 273 | 36.1943 | -120.7632 | No | Clear;Above 90 | Transformer | Burned/flashed | 24-0115049 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1974951 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 4219 | 20240924 | 1547 | 20240924 | 1740 | 2576615 | 113 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 394 | 44522 | 36.9353 | -121.7736 | No | Partly Cloudy;32-90 F |  |  | 24-0115113 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1974973 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | RECLOSER | 4002 | 20240925 | 644 | 20240925 | 810 | 2576976 | 86 | Distribution Circuit | Animal | Bird found | 171 | 12714 | 36.8322 | -121.5312 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0115194 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1975037 | 0 | EPSS Ckt | Y | 2024 | B & C PHSE
CENTRAL COAST | MONTEREY | DEL MONTE-2102 | 182222102 | TRANSFORMER | T0666 | 20240925 | 726 | 20240926 | 342 | 2576999 | 1216 | Distribution Circuit | Equipment Failure/Involved | Underground | 24 | 8903 | 36.6086 | -121.8541 | No | Overcast;32-90 F | Transformer (UG) | Broken | 24-0115718 | UG | Sus | 46326937 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1975380 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2108 | 83252108 | FUSE | 1991 | 20240925 | 1032 | 20240925 | 1617 | 2577320 | 343 | Distribution Circuit | Equipment Failure/Involved | Overhead | 77 | 26411 | 36.9684 | -122.0108 | No | Overcast;32-90 F | Pole-Wood | Deteriorated | 24-0115357 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1975251 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | TRANSFORMER | 413035359574 | 20240925 | 1037 | 20240925 | 1137 | 2577324 | 60 | Transformer only | Animal | Squirrel | 4 | 240 | 36.9469 | -121.3849 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0115419 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1975275 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 11054 | 20240925 | 1137 | 20240925 | 1241 | 2577420 | 64 | Distribution Circuit | Vegetation | Tree - branch fell on line | 309 | 19776 | 36.9775 | -121.7415 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0115423 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1975276 | 0 | EPSS Ckt | Y | 2024 | C PHSE & GRD
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 2667 | 20240925 | 1645 | 20240925 | 2001 | 2577711 | 196 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1176 | 37.0258 | -121.7751 | No | Clear;32-90 F |  |  | 24-0115694 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1975367 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1106 | 182011106 | TRANSFORMER | 412219649272 | 20240925 | 2125 | 20240925 | 2329 | 2577839 | 124 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 2108 | 36.6571 | -121.6543 | No | Overcast;32-90 F | Transformer (OH) | Leaking | 24-0115716 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1975378 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | KING CITY-1103 | 182031103 | RECLOSER | 7038 | 20240926 | 727 | 20240926 | 935 | 2577939 | 128 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 796 | 101888 | 36.1935 | -121.1442 | No | Fog;32-90 F |  |  | 24-0115772 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1975412 | 0 | EPSS Ckt | Y | 2024 | A C INST
CENTRAL COAST | SALINAS | BUENA VISTA-1102 | 182261102 | RECLOSER | 555392 | 20240926 | 1114 | 20240926 | 2323 | 2578312 | 729 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 5832 | 36.6177 | -121.6354 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0115944 | OH | Sus | 46327427 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | No | 1975590 | 0 | Non-EPSS | N | 2024 | C PHSE & GRD
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | FUSE | 4299 | 20240926 | 1154 | 20240927 | 652 | 2578427 | 1138 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 4552 | 36.7426 | -121.684 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0116095 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Three Phase Fault | 0 | No | Yes | No | 1975641 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 2553 | 20240926 | 1211 | 20240926 | 2012 | 2578390 | 481 | Distribution Circuit | Vegetation | Tree - grew into line | 2 | 962 | 36.9551 | -121.7478 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0116001 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1975613 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | TRANSFORMER | 315512817052 | 20240926 | 1700 | 20240926 | 2000 | 2578575 | 180 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 1800 | 36.9582 | -122.0368 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0116203 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1975664 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 5065 | 20240926 | 2147 | 20240927 | 1155 | 2578846 | 848 | Distribution Circuit | 3rd Party | Vehicle | 129 | 9824 | 36.9636 | -121.9986 | No | Partly Cloudy;32-90 F | Anchor or Guy | Broken | 24-0116287 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1975724 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6933 | 20240927 | 538 | 20240927 | 910 | 2579322 | 212 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1060 | 36.9296 | -121.7331 | No | Overcast-Fog;32-90 F |  |  | 24-0116467 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1975916 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | FUSE | 7483 | 20240927 | 829 | 20240927 | 1715 | 2579182 | 526 | Distribution Circuit | 3rd Party | Vehicle | 10 | 5260 | 36.0026 | -120.8946 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0116428 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | Yes | No | 1975887 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6809 | 20240927 | 856 | 20240927 | 1900 | 2579237 | 604 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 12772 | 36.8451 | -121.6349 | No | Clear;32-90 F | Fuse | Broken | 24-0116592 | OH | Sus | 46328051 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1975945 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | SWITCH | 12101 | 20240927 | 937 | 20240927 | 1331 | 2579180 | 234 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 702 | 37.0027 | -121.8314 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0116390 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1975830 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SOLEDAD-2101 | 182052101 | RECLOSER | 823854 | 20240927 | 1037 | 20240927 | 1407 | 2579378 | 210 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 245 | 51450 | 36.4271 | -121.313 | No | Clear;32-90 F |  |  | 24-0116510 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1975935 | 0 | EPSS Ckt | Y | 2024 | A B
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | RECLOSER | 4018 | 20240927 | 1407 | 20240928 | 1755 | 2579522 | 1668 | Distribution Circuit | Equipment Failure/Involved | Overhead | 239 | 88577 | 36.6885 | -121.2715 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0116727 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | No | 1975981 | 0 | EPSS Ckt | Y | 2024 | SGF DCD ALARM
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | TRANSFORMER | 412733535900 | 20240927 | 1418 | 20240928 | 2028 | 2579529 | 1810 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 3620 | 36.2948 | -121.4683 | No | Clear;Above 90 | Transformer | Deteriorated | 24-0116900 | OH | Sus | 31710322 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1976180 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 5945 | 20240927 | 1508 | 20240927 | 1630 | 2579573 | 82 | Distribution Circuit | 3rd Party | Metallic Balloon | 335 | 27470 | 36.7919 | -121.7232 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0116802 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1976012 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | TRANSFORMER | 315903417736 | 20240927 | 1532 | 20240927 | 2125 | 2579512 | 353 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 353 | 36.9785 | -121.9036 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0116782 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1976003 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0422 | 182440422 | FUSE | 1359 | 20240927 | 1655 | 20240928 | 1108 | 2579630 | 1093 | Distribution Circuit | Equipment Failure/Involved | Overhead | 47 | 12815 | 36.5997 | -121.9564 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0116834 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1976034 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 10996 | 20240927 | 2013 | 20240927 | 2201 | 2579711 | 108 | Distribution Circuit | Vegetation | Tree - branch fell on line | 255 | 22700 | 37.0748 | -122.0845 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0116836 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1976037 | 0 | EPSS Ckt | Y | 2024 | A B
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 11555 | 20240928 | 523 | 20240928 | 915 | 2579798 | 232 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 6258 | 36.865 | -121.7224 | No | Clear;32-90 F |  |  | 24-0116877 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1976154 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | TRANSFORMER | 412888756610 | 20240928 | 533 | 20240928 | 704 | 2579805 | 91 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 182 | 36.8631 | -121.4323 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0116856 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1976067 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 68191 | 20240928 | 821 | 20240928 | 1102 | 2579970 | 161 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 3059 | 36.9816 | -121.9026 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 24-0116871 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1976143 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | RECLOSER | 3010 | 20240928 | 904 | 20240928 | 918 | 2579946 | 14 | Distribution Circuit | Company Initiated | Personnel- company | 423 | 5922 | 36.28 | -121.3077 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0116866 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1976129 | 0 | EPSS Ckt | Y | 2024 | A & C PHASE
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 543817 | 20240928 | 1433 | 20240928 | 1711 | 2580184 | 159 | Distribution Circuit | Equipment Failure/Involved | Overhead | 49 | 7791 | 37.0487 | -121.8085 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0116936 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1976220 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | TRANSFORMER | 316215813439 | 20240928 | 1512 | 20240928 | 2155 | 2580199 | 403 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 403 | 36.8618 | -121.7947 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0116944 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1976228 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | RECLOSER | 37088 | 20240929 | 153 | 20240929 | 1408 | 2580404 | 735 | Distribution Circuit | 3rd Party | Vehicle | 3037 | 309359 | 36.5465 | -121.8985 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 24-0116990 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | Yes | No | 1976261 | 0 | EPSS Ckt | Y | 2024 | B C
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | RECLOSER | 648928 | 20240929 | 153 | 20240929 | 254 | 2580375 | 61 | Distribution Circuit | Company Initiated | Coordination failure | 1529 | 93269 | 36.5332 | -121.9152 | No | Overcast-Fog;32-90 F | Recloser | Normal | 24-0116989 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1976260 | 0 | EPSS Ckt | Y | 2024 | SGF DCD
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 71630 | 20240929 | 523 | 20240929 | 610 | 2580476 | 47 | Distribution Circuit | Animal | Bird found | 622 | 23998 | 36.9761 | -121.8948 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Normal | 24-0116998 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1976273 | 0 | EPSS Ckt | Y | 2024 | B C
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 5232 | 20240929 | 701 | 20240929 | 904 | 2580500 | 123 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 789 | 23528 | 37.0752 | -122.054 | No | Clear;32-90 F |  |  | 24-0117002 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1976279 | 0 | EPSS Ckt | Y | 2024 | B GRD
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | FUSE | 8551 | 20240929 | 1057 | 20240929 | 1907 | 2580635 | 490 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 490 | 36.3238 | -121.2179 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0117062 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1976342 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 9009 | 20240929 | 1258 | 20240929 | 1348 | 2580732 | 50 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 1550 | 37.0453 | -122.0276 | No | Clear;32-90 F | Fuse | Broken | 24-0117081 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Open Circuit | 0 | No | No | No | 1976357 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 454176 | 20240929 | 1413 | 20240929 | 1540 | 2580761 | 87 | Distribution Circuit | Vegetation | Tree - branch fell on line | 51 | 3179 | 36.994 | -121.7761 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0117085 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1976358 | 0 | EPSS Ckt | Y | 2024 | BC
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 4645 | 20240929 | 1945 | 20240930 | 16 | 2580845 | 271 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 183 | 48558 | 36.5668 | -121.7548 | No | Clear;32-90 F |  |  | 24-0117136 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1976390 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | TRANSFORMER | 411364547317 | 20240930 | 42 | 20240930 | 1029 | 2580886 | 587 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 5870 | 36.5965 | -121.9437 | No | Partly Cloudy;32-90 F | Transformer (OH) | Deteriorated | 24-0117148 | OH | Sus | 35584276 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1976406 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | KING CITY-1104 | 182031104 | RECLOSER | 7092 | 20240930 | 1305 | 20240930 | 1343 | 2581458 | 38 | Distribution Circuit | 3rd Party | Vehicle | 58 | 2204 | 36.2036 | -121.1157 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0117364 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1976611 | 0 | EPSS Ckt | N | 2024 | FORCE OUT
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | JUMPER | OPEN JUMPERS 1 SP SS. OF FUCO 5099 TO EOL | 20240930 | 1345 | 20240930 | 1447 | 2581517 | 62 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 62 | 36.7531 | -121.7637 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 24-0117378 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1976616 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | FUSE | 40307 | 20240930 | 1700 | 20240930 | 1827 | 2581660 | 87 | Distribution Circuit | Equipment Failure/Involved | Overhead | 86 | 7482 | 36.6975 | -121.7924 | No | Clear;32-90 F | Insulator | Broken | 24-0117490 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1976652 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | TRES PINOS-1111 | 183221111 | RECLOSER | 1111/2 | 20240930 | 2153 | 20241001 | 1100 | 2581795 | 787 | Distribution Circuit | Equipment Failure/Involved | Overhead | 387 | 42298 | 36.7844 | -121.3196 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0117549 | OH | Sus | 31710561 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | No | 1976682 | 0 | EPSS Ckt | N | 2024 | A GRD
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 1699 | 20240930 | 2200 | 20240930 | 2336 | 2581810 | 96 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 864 | 36.9707 | -121.797 | No | Clear;32-90 F |  |  | 24-0117562 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1976692 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | KING CITY-1104 | 182031104 | RECLOSER | 7092 | 20240930 | 2221 | 20240930 | 2253 | s1976687 | 32 | Distribution Circuit | 3rd Party | Vehicle | 58 | 1856 | 36.2036 | -121.1157 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0117364 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1976687 | 0 | EPSS Ckt | N | 2024 | FORCE OUT
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 90207 | 20241001 | 936 | 20241001 | 1143 | 2582181 | 127 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 254 | 37.0785 | -122.1366 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0117693 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1976888 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS COCHES-1102 | 182151102 | SWITCH | 7207BP | 20241001 | 1149 | 20241002 | 343 | 2582333 | 954 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 2331 | 36.3742 | -121.2635 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0117799 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1976944 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 10960 | 20241001 | 1231 | 20241001 | 1413 | 2582365 | 102 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 2396 | 244392 | 36.9866 | -121.8582 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0117845 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1976964 | 0 | EPSS Ckt | N | 2024 | NONE
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | FUSE | 8543 | 20241001 | 1435 | 20241001 | 2330 | 2582857 | 535 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 535 | 36.295 | -121.1982 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0118073 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1977064 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1106 | 182011106 | SWITCH | 3652 | 20241001 | 1555 | 20241001 | 2208 | 2582584 | 373 | Distribution Circuit | Vegetation | Tree - grew into line | 424 | 104363 | 36.6701 | -121.6594 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0117903 | OH | Sus | 46329947 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1977023 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | BUENA VISTA-1106 | 182261106 | TRANSFORMER | 412326748248 | 20241001 | 1608 | 20241002 | 445 | 2582597 | 757 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 757 | 36.6303 | -121.6158 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0118036 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977039 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6805 | 20241001 | 1635 | 20241002 | 236 | 2582706 | 601 | Distribution Circuit | Animal | Other | 2 | 1001 | 36.9396 | -121.7419 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0118049 | OH | Sus | 46330047 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977050 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | RECLOSER | 4018 | 20241001 | 1825 | 20241002 | 817 | 2582785 | 832 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 239 | 198848 | 36.6885 | -121.2715 | No | Clear;32-90 F |  |  | 24-0118043 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1977045 | 0 | EPSS Ckt | Y | 2024 | A C
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 7601 | 20241001 | 2217 | 20241002 | 323 | 2582883 | 303 | Distribution Circuit | Vegetation | Tree - grew into line | 13 | 3939 | 37.0847 | -122.0061 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0118081 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1977071 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | FUSE | 3581 | 20241002 | 241 | 20241003 | 223 | 2582943 | 1422 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1978 | 36.7274 | -121.7456 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0118103 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1977094 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | RECLOSER | 5178 | 20241002 | 727 | 20241002 | 1500 | 2583032 | 453 | Distribution Circuit | Vegetation | Tree - branch fell on line | 268 | 20204 | 37.0324 | -121.9467 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0118141 | OH | Sus | 31710455 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1977114 | 0 | EPSS Ckt | Y | 2024 | A GRD
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 10960 | 20241002 | 924 | 20241002 | 1132 | 2583286 | 128 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2377 | 131660 | 36.9866 | -121.8582 | No | Clear;32-90 F |  |  | 24-0118223 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977256 | 0 | EPSS Ckt | Y | 2024 | A GRD
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 11054 | 20241002 | 1113 | 20241002 | 1337 | 2583461 | 144 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 309 | 44496 | 36.9775 | -121.7415 | No | Clear;32-90 F |  |  | 24-0118307 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1977305 | 0 | EPSS Ckt | Y | 2024 | B GRD INST
CENTRAL COAST | HOLLISTER | TRES PINOS-1111 | 183221111 | RECLOSER | 4064 | 20241002 | 1119 | 20241002 | 1257 | 2583473 | 98 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 387 | 15165 | 36.788 | -121.3161 | No | Clear;Above 90 |  |  | 24-0118309 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977306 | 0 | EPSS Ckt | Y | 2024 | C-GRD
CENTRAL COAST | MONTEREY | FORT ORD-2106 | 182402106 | RECLOSER | 9658 | 20241002 | 1246 | 20241002 | 1351 | 2583564 | 65 | Distribution Circuit | Company Initiated | Coordination failure | 1158 | 75270 | 36.6556 | -121.7474 | No | Clear;32-90 F | Recloser | Normal | 24-0118357 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977331 | 0 | EPSS Ckt | Y | 2024 | SGF
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315693021521 | 20241002 | 1254 | 20241003 | 335 | 2583521 | 881 | Transformer only | Vegetation | Tree - branch fell on line | 3 | 2643 | 37.082 | -121.9775 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0118405 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1977343 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2106 | 182402106 | RECLOSER | 9658 | 20241002 | 1357 | 20241002 | 1459 | 2583634 | 62 | Distribution Circuit | Company Initiated | Coordination failure | 1158 | 50721 | 36.6556 | -121.7474 | No | Clear;32-90 F | Recloser | Normal | 24-0118433 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977349 | 0 | EPSS Ckt | Y | 2024 | SGF
CENTRAL COAST | HOLLISTER | TRES PINOS-1111 | 183221111 | RECLOSER | 1111/2 | 20241002 | 1458 | 20241002 | 1536 | 2583705 | 38 | Distribution Circuit | 3rd Party | Customer Equipment | 387 | 14425 | 36.7844 | -121.3196 | No | Clear;Above 90 | Conductor- Underground | Broken | 24-0118511 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977361 | 0 | EPSS Ckt | Y | 2024 | C&GRD
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | SWITCH | 894556 | 20241002 | 1459 | 20241002 | 1522 | s1993421 | 23 | Distribution Circuit | Company Initiated | Coordination failure | 8 | 184 | 37.058 | -121.9416 | No | Clear;32-90 F | Recloser | Normal | 24-0118141 | OH | Sus | 31710455 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1993421 | 0 | EPSS Ckt | Y | 2024
CENTRAL COAST | COAST | GREEN VALLEY SUB | 8319 | OCB | 3059 | 20241002 | 1623 | 20241002 | 1654 | 2583686 | 31 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 744 | 36.929 | -121.7939 | No | Clear;Above 90 | Switch (OH) | Broken | 24-0118552 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1977366 | 0 | Non-EPSS | N | 2024 | NONE
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 16586 | 20241002 | 1910 | 20241002 | 2124 | 2584109 | 134 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 730 | 48140 | 36.9365 | -121.8625 | No | Clear;32-90 F |  |  | 24-0118624 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1977399 | 0 | EPSS Ckt | Y | 2024 | A- B- & INST OC
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | JUMPER | WIRE DOWN 4 SP LD SIDE OF FUCO 7201 | 20241002 | 2016 | 20241003 | 1329 | 2584143 | 1033 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 2066 | 37.1143 | -122.0228 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0118661 | OH | Sus | 46330544 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1977424 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 69466 | 20241002 | 2107 | 20241003 | 410 | 2584278 | 423 | Transformer only | Vegetation | Tree - branch fell on line | 240 | 101520 | 36.8266 | -121.7254 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0118702 | OH | Sus | 46330438 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977448 | 0 | EPSS Ckt | Y | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | RECLOSER | 258878 | 20241002 | 2109 | 20241002 | 2258 | 2584179 | 109 | Distribution Circuit | Animal | Bird found | 16 | 1744 | 36.2313 | -121.1769 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0118655 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1977419 | 0 | EPSS Ckt | Y | 2024 | B- C- TIME & INST OC
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | TRANSFORMER | 315624320366 | 20241002 | 2301 | 20241003 | 1104 | 2584208 | 723 | Distribution Circuit | Equipment Failure/Involved | Overhead | 65 | 5352 | 37.0498 | -122.0003 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0118697 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977447 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8961 | 20241003 | 849 | 20241003 | 1220 | 2584486 | 211 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 422 | 37.0432 | -122.0518 | No | Clear;32-90 F |  |  | 24-0118849 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Three Phase Fault | 0 | No | No | No | 1977585 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | BORONDA-1102 | 182461102 | FUSE | 23375 | 20241003 | 927 | 20241003 | 1426 | 2584570 | 299 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 2194 | 36.6839 | -121.673 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0119058 | OH | Sus | 46330981 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977636 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | TRANSFORMER | 411956040740 | 20241003 | 1138 | 20241004 | 2102 | 2584784 | 2004 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 2004 | 36.4212 | -121.7352 | No | Clear;32-90 F | Transformer (OH) | Broken- wire on ground | 24-0119168 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1977665 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | SWITCH | 8745 | 20241003 | 1807 | 20241003 | 2320 | 2585073 | 313 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 52 | 16276 | 36.5891 | -121.9105 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0118982 | OH | Sus | 46331161 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1977663 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2103 | 182492103 | FUSE | 9859 | 20241003 | 1822 | 20241003 | 2315 | 2585142 | 293 | Distribution Circuit | Equipment Failure/Involved | Underground | 29 | 3506 | 36.8469 | -121.3717 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 24-0119229 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977688 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 287578 | 20241003 | 1832 | 20241004 | 429 | 2585149 | 597 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2247 | 310826 | 37.0438 | -122.0755 | No | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0119206 | OH | Sus | 31711020 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1977678 | 0 | EPSS Ckt | Y | 2024 | B&GRD INST & TIME OC
CENTRAL COAST | KING CITY | LOS COCHES-1101 | 182151101 | FUSE | 7775 | 20241003 | 2034 | 20241005 | 350 | 2585269 | 1876 | Distribution Circuit | 3rd Party | Vehicle | 2 | 3752 | 36.3592 | -121.2951 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0119251 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Three Phase Fault | 0 | No | Yes | No | 1977715 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | FUSE | 8703 | 20241004 | 135 | 20241004 | 408 | 2585332 | 153 | Distribution Circuit | Equipment Failure/Involved | Underground | 100 | 6368 | 36.324 | -121.2536 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0119274 | UG | Sus | 35585498 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1977733 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | FUSE | 4727 | 20241004 | 303 | 20241004 | 342 | 2585336 | 39 | Distribution Circuit | Equipment Failure/Involved | Overhead | 150 | 3554 | 36.6816 | -121.6548 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 24-0119137 | OH | Sus | 31710866 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1977734 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0421 | 182440421 | TRANSFORMER | 411472648023 | 20241004 | 307 | 20241004 | 1153 | 2585349 | 526 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 6838 | 36.6168 | -121.9078 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0119281 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977741 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | OCB | 2102/2 | 20241004 | 533 | 20241004 | 1335 | 2585397 | 482 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 3029 | 472917 | 36.952 | -121.7601 | No | Partly Cloudy;32-90 F | Elbow | Failed/Faulted | 24-0119284 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977747 | 0 | Non-EPSS | N | 2024 | A GRD
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | TRANSFORMER | 316297015112 | 20241004 | 659 | 20241004 | 1013 | 2585426 | 194 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 194 | 36.9081 | -121.7673 | No | Clear;32-90 F |  |  | 24-0119428 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1977883 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | RECLOSER | 96738 | 20241004 | 835 | 20241004 | 1029 | 2585532 | 114 | Distribution Circuit | Vegetation | Tree - branch fell on line | 287 | 28182 | 37.1111 | -122.1142 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0119347 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1977810 | 0 | EPSS Ckt | Y | 2024 | A-C
CENTRAL COAST | KING CITY | SOLEDAD-2102 | 182052102 | FUSE | 9705 | 20241004 | 1058 | 20241004 | 2216 | 2585663 | 678 | Distribution Circuit | 3rd Party | Vehicle | 3 | 2034 | 36.4087 | -121.3578 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0119467 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1977902 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 6801 | 20241004 | 1214 | 20241004 | 1328 | 2585859 | 74 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 592 | 36.9039 | -121.7239 | No | Clear;32-90 F |  |  | 24-0119588 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1977925 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | OTHER | 5871 | 20241004 | 1643 | 20241005 | 956 | 2586029 | 1033 | Distribution Circuit | 3rd Party | Vehicle | 6432 | 1376541 | 36.9204 | -121.7473 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0119687 | OH | Sus | 35585555 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | Yes | 1977944 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | OTHER | WIRE DOWN 2 SP LD SIDE OF CGC 31518723726 | 20241004 | 2140 | 20241005 | 110 | 2586171 | 210 | Distribution Circuit | Vegetation | Tree - branch fell on line | 282 | 30553 | 37.1393 | -122.1516 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0119717 | OH | Sus | 46331839 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | Yes | 1977974 | 0 | EPSS Ckt | Y | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | RECLOSER | 1132 | 20241005 | 142 | 20241005 | 1058 | 2586522 | 556 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 205 | 92140 | 36.3584 | -121.2034 | No | Partly Cloudy;32-90 F |  |  | 24-0119729 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1977985 | 0 | Non-EPSS | Y | 2024 | B & C
CENTRAL COAST | MONTEREY | DEL MONTE-1101 | 182221101 | TRANSFORMER | 411700347437 | 20241005 | 1515 | 20241005 | 1610 | 2586878 | 55 | Transformer only | Unknown Cause | Patrol - found nothing | 20 | 1100 | 36.6023 | -121.8294 | No | Clear;32-90 F |  |  | 24-0119851 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1978100 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | RECLOSER | 781810 | 20241006 | 612 | 20241006 | 908 | 2587146 | 176 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 185 | 20795 | 36.9615 | -122.0627 | No | Partly Cloudy;32-90 F |  |  | 24-0119905 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1978145 | 0 | EPSS Ckt | Y | 2024 | A/B
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 428972 | 20241006 | 825 | 20241007 | 140 | 2587285 | 1035 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 21300 | 37.1056 | -121.9724 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0119921 | OH | Sus | 31711242 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1978176 | 0 | EPSS Ckt | Y | 2024 | A
CENTRAL COAST | SALINAS | BUENA VISTA-1102 | 182261102 | FUSE | 3729 | 20241006 | 1001 | 20241006 | 1300 | 2587339 | 179 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 2148 | 36.6237 | -121.651 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0119949 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1978201 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | JUMPER | JUMPERS 2PSW/OF CGC# 412085550009 | 20241006 | 1145 | 20241006 | 1354 | 2587383 | 129 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 129 | 36.6756 | -121.7007 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0119942 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1978193 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2106 | 182402106 | RECLOSER | 9658 | 20241006 | 1445 | 20241006 | 1552 | 2587447 | 67 | Distribution Circuit | Company Initiated | Coordination failure | 1158 | 77586 | 36.6556 | -121.7474 | No | Clear;32-90 F | Recloser | Normal | 24-0119960 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1978209 | 0 | EPSS Ckt | Y | 2024 | SGF
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | RECLOSER | 258878 | 20241006 | 1451 | 20241006 | 1612 | 2587448 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 1296 | 36.2313 | -121.1769 | No | Clear;Above 90 |  |  | 24-0119961 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1978210 | 0 | EPSS Ckt | Y | 2024 | BC
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | RECLOSER | 12656 | 20241006 | 1811 | 20241007 | 1535 | 2587675 | 1284 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1258 | 308383 | 36.9118 | -121.7973 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0119991 | OH | Sus | 31711223 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1978239 | 0 | EPSS Ckt | N | 2024 | A- B- & INST OC
CENTRAL COAST | KING CITY | OILFIELDS-1102 | 182391102 | SWITCH | 7051 | 20241006 | 1856 | 20241007 | 908 | 2587728 | 852 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 11 | 9372 | 35.961 | -120.8317 | No | Clear;32-90 F |  |  | 24-0120006 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1978257 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | RECLOSER | 117328 | 20241006 | 2231 | 20241006 | 2355 | 2587823 | 84 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 36 | 3024 | 36.8827 | -121.3274 | No | Clear;32-90 F |  |  | 24-0120024 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Multi-Fault | 0 | No | No | No | 1978274 | 0 | EPSS Ckt | N | 2024 | B- C- & GRD
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | RECLOSER | 4072 | 20241006 | 2342 | 20241007 | 17 | 2587858 | 35 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 387 | 13545 | 36.7843 | -121.3196 | No | Clear;32-90 F |  |  | 24-0120031 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Multi-Fault | 0 | No | No | No | 1978282 | 0 | EPSS Ckt | N | 2024 | A- B- & GRD
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | JUMPER | OJS HIGHSIDE OF CGC 412064850539 | 20241007 | 144 | 20241007 | 411 | 2587867 | 147 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 1170 | 36.6908 | -121.7078 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0120039 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1978290 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | RECLOSER | 88772 | 20241007 | 436 | 20241007 | 1019 | 2587903 | 343 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1253 | 93716 | 36.904 | -121.6085 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0120045 | OH | Sus | 46332369 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1978297 | 0 | EPSS Ckt | Y | 2024 | C & GRD
CENTRAL COAST | SALINAS | BUENA VISTA-1104 | 182261104 | JUMPER | WIRE DOWN JUST SOURCE SIDE OF FUCO 4661 | 20241007 | 455 | 20241007 | 1052 | 2587906 | 357 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 357 | 36.6664 | -121.6146 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0120052 | OH | Sus | 46332370 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1978306 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | FUSE | 24769 | 20241007 | 717 | 20241007 | 958 | 2587956 | 161 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 483 | 36.7479 | -121.7139 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0120172 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1978487 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 38430 | 20241007 | 833 | 20241007 | 925 | 2588084 | 52 | Distribution Circuit | 3rd Party | Vehicle | 5533 | 144740 | 36.9756 | -121.8885 | No | Partly Cloudy;32-90 F | Anchor or Guy | Broken | 24-0120108 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1978408 | 0 | EPSS Ckt | Y | 2024 | A
CENTRAL COAST | KING CITY | OILFIELDS-1102 | 182391102 | FUSE | 479707 | 20241007 | 927 | 20241007 | 2324 | 2588202 | 837 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 7533 | 35.9518 | -120.8104 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0120335 | OH | Sus | 46332897 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1978579 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1106 | 182011106 | TRANSFORMER | 412197349113 | 20241007 | 1109 | 20241007 | 1233 | 2588300 | 84 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 168 | 36.6526 | -121.6616 | No | Clear;32-90 F | Fuse | Burned Open | 24-0120244 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1978534 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 11459 | 20241007 | 1309 | 20241008 | 208 | 2588445 | 779 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1558 | 36.8684 | -121.789 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0120304 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1978570 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 11797 | 20241007 | 1549 | 20241008 | 251 | 2588603 | 662 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 9930 | 36.8677 | -121.7087 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0120402 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | Yes | No | 1978611 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | RECLOSER | 325334 | 20241007 | 1917 | 20241008 | 129 | 2588900 | 372 | Distribution Circuit | Equipment Failure/Involved | Underground | 741 | 275652 | 36.5421 | -121.9072 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0120425 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1978628 | 0 | EPSS Ckt | Y | 2024 | B- GRD- & INST OC
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 841 | 20241007 | 2021 | 20241007 | 2259 | 2588943 | 158 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 948 | 36.7594 | -121.7869 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 24-0120439 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1978639 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | RECLOSER | 109138 | 20241008 | 321 | 20241008 | 338 | 2589046 | 17 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3447 | 58599 | 36.3182 | -121.2407 | No | Clear;32-90 F | Jumper | Burned/flashed | 24-0120485 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1978661 | 0 | Non-EPSS | N | 2024 | NONE
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 6713 | 20241008 | 936 | 20241008 | 1438 | 2589397 | 302 | Distribution Circuit | Vegetation | Tree - branch fell on line | 87 | 26274 | 36.8964 | -121.8374 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0120589 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1978848 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 5277 | 20241008 | 1102 | 20241008 | 1135 | 2589508 | 33 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 1320 | 36.776 | -121.6876 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0120686 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1978894 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | RECLOSER | 2020 | 20241008 | 1500 | 20241011 | 1939 | 2589747 | 4560 | Distribution Circuit | Vegetation | Tree - fell into line | 840 | 532708 | 36.4632 | -121.7119 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0120828 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1978942 | 0 | EPSS Ckt | Y | 2024 | SGF/DCD
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | RECLOSER | 96738 | 20241008 | 1945 | 20241008 | 2139 | 2589977 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 285 | 32382 | 37.1111 | -122.1142 | No | Clear;32-90 F |  |  | 24-0120932 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1978977 | 0 | EPSS Ckt | Y | 2024 | B & C
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411999050635 | 20241008 | 2108 | 20241009 | 315 | 2589958 | 367 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 367 | 36.6932 | -121.7311 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0120942 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1978982 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 11044 | 20241008 | 2248 | 20241009 | 120 | 2590096 | 152 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2247 | 144388 | 37.0401 | -122.0297 | No | Clear;32-90 F | Crossarm- Wood | Normal | 24-0120955 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1978991 | 0 | EPSS Ckt | Y | 2024 | B & GRD
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 889 | 20241008 | 2325 | 20241009 | 620 | 2590087 | 407 | Distribution Circuit | Vegetation | Tree - branch fell on line | 350 | 71005 | 36.8047 | -121.6671 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0120959 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1978993 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS COCHES-1101 | 182151101 | JUMPER | BROKEN OH 1 S/OF 7773 | 20241008 | 2334 | 20241009 | 2205 | 2590107 | 1351 | Distribution Circuit | Equipment Failure/Involved | Overhead | 100 | 5130 | 36.3597 | -121.2953 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0121118 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Open Circuit | 0 | No | No | No | 1979143 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1112 | 182371112 | TRANSFORMER | 411988142927 | 20241009 | 49 | 20241009 | 926 | 2590112 | 517 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 6204 | 36.4814 | -121.7264 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0120965 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1979003 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1112 | 182371112 | TRANSFORMER | T1197 | 20241009 | 831 | 20241009 | 931 | 2590329 | 60 | Transformer only | Unknown Cause | Patrol - found nothing | 64 | 3840 | 36.4786 | -121.7318 | No | Clear;32-90 F |  |  | 24-0121135 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1979188 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | SAN BENITO-2102 | 182742102 | TRANSFORMER | 412702856564 | 20241009 | 910 | 20241009 | 1553 | 2590445 | 403 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 403 | 36.8607 | -121.4948 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0121160 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1979201 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2108 | 83252108 | TRANSFORMER | 315599517655 | 20241009 | 1223 | 20241009 | 1305 | 2590719 | 42 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 756 | 36.9748 | -122.0064 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0121303 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1979261 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 6781 | 20241009 | 1458 | 20241009 | 1535 | 2590802 | 37 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 148 | 36.9045 | -121.6444 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 24-0121388 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1979278 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | TRANSFORMER | 100000179163 | 20241009 | 1558 | 20241010 | 2013 | 2590889 | 1695 | Transformer only | Vegetation | Tree - grew into line | 4 | 6780 | 36.5824 | -121.6313 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0121539 | OH | Sus | 46333749 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1979314 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 11054 | 20241009 | 1727 | 20241009 | 1839 | 2590978 | 72 | Distribution Circuit | Vegetation | Tree - fell into line | 309 | 16890 | 36.9775 | -121.7415 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 24-0121505 | OH | Sus | 46333748 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1979306 | 0 | EPSS Ckt | Y | 2024 | AC
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | TRANSFORMER | 413425636459 | 20241010 | 411 | 20241010 | 1512 | 2591211 | 661 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1619 | 36.3138 | -121.2326 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0121607 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1979359 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 4749 | 20241010 | 1239 | 20241010 | 1408 | 2591609 | 89 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 267 | 37.0921 | -122.1146 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0121880 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1979559 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | JUMPER | OJ'S @ LINE & BUCK 4 SP S/OF FUCO 614463 | 20241010 | 2036 | 20241010 | 2333 | 2591873 | 177 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 177 | 36.6862 | -121.7169 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0122008 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1979593 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 3907 | 20241010 | 2056 | 20241010 | 2340 | 2591878 | 164 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 656 | 36.6932 | -121.7258 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0122012 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1979596 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | TRANSFORMER | 315675317106 | 20241011 | 224 | 20241011 | 1250 | 2591949 | 626 | Transformer only | Equipment Failure/Involved | Electrical Overload | 11 | 6886 | 36.9601 | -121.9804 | No | Partly Cloudy-Fog;32-90 F | Transformer | Failed/Faulted | 24-0122043 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1979630 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | OTHER | DOWN WIRE SS OF FUCO 40423 | 20241011 | 345 | 20241011 | 1710 | 2591963 | 805 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 18055 | 36.554 | -121.8991 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0122044 | OH | Sus | 46338101 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | Yes | 1979632 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1102 | 182201102 | RECLOSER | 276712 | 20241011 | 513 | 20241011 | 1607 | 2591975 | 654 | Distribution Circuit | Equipment Failure/Involved | Overhead | 198 | 45569 | 36.6279 | -121.5432 | No | Partly Cloudy-Fog;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0122045 | OH | Sus | 46338227 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1979638 | 0 | EPSS Ckt | N | 2024 | C PHSE & GRD
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | RECLOSER | 3010 | 20241011 | 654 | 20241011 | 1502 | 2592011 | 488 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 467 | 227896 | 36.28 | -121.3077 | No | Partly Cloudy;32-90 F |  |  | 24-0122063 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1979648 | 0 | EPSS Ckt | Y | 2024 | B&C
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | TRANSFORMER | 411913551824 | 20241011 | 1016 | 20241011 | 1326 | 2592282 | 190 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 190 | 36.7251 | -121.7606 | No | Clear;32-90 F | Fuse | Broken | 24-0122348 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1979845 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1106 | 182011106 | FUSE | 25165 | 20241011 | 1157 | 20241011 | 1345 | 2592348 | 108 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 144 | 36.6492 | -121.6621 | No | Clear;32-90 F | Fuse | Broken | 24-0122357 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1979851 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 3621 | 20241012 | 703 | 20241012 | 857 | 2592723 | 114 | Distribution Circuit | Animal | Bird found | 123 | 14022 | 36.7789 | -121.6493 | No | Clear;Below 32 F | Conductor- Overhead | Normal | 24-0122519 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1979951 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 1117 | 20241012 | 843 | 20241012 | 1925 | 2592815 | 642 | Distribution Circuit | Vegetation | Tree - grew into line | 20 | 12840 | 37.1156 | -121.971 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0122374 | OH | Sus | 46338231 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1979960 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | JUMPER | BURNT CENTER PHASE OJ @ CGC# 316333114043 | 20241012 | 1111 | 20241012 | 2128 | 2592957 | 617 | Distribution Circuit | Equipment Failure/Involved | Overhead | 360 | 48091 | 36.879 | -121.7549 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 24-0122559 | OH | Sus | 46338580 | SOUTH BAY AND CENTRAL COAST | OCT | Open Circuit | 0 | No | No | No | 1979998 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | FUSE | 40711 | 20241012 | 1232 | 20241012 | 1312 | 2593025 | 40 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 440 | 36.5994 | -121.8791 | No | Clear;32-90 F |  |  | 24-0122586 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1980017 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1102 | 182011102 | JUMPER | FB 2P/S/S OF CGC 412248750850 | 20241013 | 1054 | 20241013 | 1446 | 2593508 | 232 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 8816 | 36.7012 | -121.646 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 24-0122678 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1980124 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 2273 | 20241013 | 1710 | 20241013 | 1810 | 2593661 | 60 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 59 | 3540 | 36.5433 | -121.913 | No | Overcast-Fog;32-90 F |  |  | 24-0122722 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1980152 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 2701 | 20241014 | 144 | 20241014 | 1430 | 2593829 | 766 | Distribution Circuit | Vegetation | Tree - grew into line | 1 | 766 | 37.0215 | -121.8267 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0122749 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1980179 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | FUSE | 977577 | 20241014 | 536 | 20241014 | 846 | 2593840 | 190 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1140 | 36.8489 | -121.4653 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken | 24-0122758 | OH | Sus | 46338727 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1980189 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2106 | 182402106 | FUSE | 40137 | 20241014 | 623 | 20241014 | 728 | 2593854 | 65 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 99 | 6435 | 36.6345 | -121.8108 | No | Overcast-Fog;32-90 F |  |  | 24-0122775 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1980200 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 97574 | 20241014 | 701 | 20241014 | 832 | 2593875 | 91 | Distribution Circuit | Animal | Bird found | 73 | 6625 | 36.9865 | -121.752 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Normal | 24-0122763 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1980191 | 0 | EPSS Ckt | Y | 2024 | B & GRD
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 412080455011 | 20241014 | 742 | 20241014 | 849 | 2593880 | 67 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 670 | 36.8147 | -121.7071 | No | Clear;Below 32 F | Connector or Splice (OH) | Broken | 24-0122805 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1980302 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | TRANSFORMER | 411451247192 | 20241014 | 1137 | 20241014 | 1315 | 2594338 | 98 | Transformer only | Animal | Other | 8 | 784 | 36.5937 | -121.9142 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Arcing | 24-0122997 | OH | Sus | 46339053 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1980452 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | RECLOSER | 7070 | 20241014 | 1232 | 20241015 | 1359 | 2594399 | 1527 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 455 | 409085 | 35.9644 | -121.1175 | No | Clear;32-90 F |  |  | 24-0122944 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1980433 | 0 | EPSS Ckt | Y | 2024 | SGF & DCD
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | TRANSFORMER | T0413 | 20241014 | 1356 | 20241014 | 1554 | 2594348 | 118 | Transformer only | Unknown Cause | Patrol - found nothing | 26 | 3068 | 36.5943 | -121.9139 | No | Partly Cloudy;32-90 F |  |  | 24-0122998 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1980454 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2108 | 83252108 | TRANSFORMER | 315538317470 | 20241014 | 1526 | 20241014 | 2054 | 2594680 | 328 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 2296 | 36.9698 | -122.0283 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0123123 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1980493 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 8571 | 20241014 | 1601 | 20241014 | 2143 | 2594541 | 342 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 11628 | 36.6061 | -121.9186 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0123060 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1980470 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | FUSE | 7109 | 20241015 | 8 | 20241015 | 215 | 2594742 | 127 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 3683 | 36.1946 | -120.7075 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0123147 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1980510 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 9089 | 20241015 | 440 | 20241015 | 647 | 2594783 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 889 | 36.7764 | -121.3109 | No | Clear;32-90 F |  |  | 24-0123167 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1980535 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 3609 | 20241015 | 952 | 20241015 | 1050 | 2595142 | 58 | Distribution Circuit | Equipment Failure/Involved | Overhead | 109 | 6306 | 36.7827 | -121.7058 | No | Clear;Below 32 F | Cutout- fuse holder | Broken | 24-0123327 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1980724 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | RECLOSER | 4002 | 20241015 | 1206 | 20241015 | 1858 | 2595314 | 412 | Distribution Circuit | 3rd Party | Vehicle | 171 | 70452 | 36.8322 | -121.5312 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0123366 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | Yes | No | 1980757 | 0 | EPSS Ckt | Y | 2024 | B & C
CENTRAL COAST | HOLLISTER | SAN BENITO-2102 | 182742102 | TRANSFORMER | 412709056338 | 20241015 | 1225 | 20241015 | 2259 | 2595332 | 634 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 634 | 36.8545 | -121.4932 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0123507 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1980808 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | SWITCH | 2237 | 20241015 | 1924 | 20241015 | 1938 | 2595657 | 14 | Distribution Circuit | Company Initiated | Return Circuit Normal | 27 | 378 | 36.3339 | -121.499 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0114389 | OH | Sus | 35541161 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1980843 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | FUSE | 3955 | 20241015 | 2049 | 20241016 | 750 | 2595680 | 661 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 661 | 36.6205 | -121.6537 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0123604 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1980852 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DEL MONTE-2104 | 182222104 | TRANSFORMER | 411927346149 | 20241016 | 345 | 20241016 | 2015 | 2595751 | 990 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1980 | 36.5696 | -121.7507 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0123650 | OH | Sus | 35589342 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1980887 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DEL MONTE-2104 | 182222104 | FUSE | 5835 | 20241016 | 359 | 20241016 | 843 | 2595749 | 284 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 61 | 17324 | 36.5695 | -121.7533 | No | Clear;32-90 F |  |  | 24-0123766 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1980957 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 4301 | 20241016 | 736 | 20241016 | 1010 | 2595930 | 154 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 103 | 36.7352 | -121.781 | No | Clear;Below 32 F |  |  | 24-0123898 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1981057 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2107 | 182402107 | TRANSFORMER | 411823350620 | 20241016 | 831 | 20241016 | 911 | 2595875 | 40 | Transformer only | Unknown Cause | Patrol - found nothing | 14 | 560 | 36.6913 | -121.7907 | No | Clear;32-90 F |  |  | 24-0123807 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1981018 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 1633 | 20241016 | 852 | 20241016 | 1231 | 2595920 | 219 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 1971 | 37.0365 | -122.0834 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken | 24-0123791 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1980980 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | OTHER | T1759 TWD T1760 | 20241016 | 1012 | 20241017 | 1639 | 2596067 | 1827 | Distribution Circuit | 3rd Party | Vehicle | 2 | 3654 | 36.5459 | -121.8366 | No | Overcast;32-90 F | Transformer (UG) | Broken | 24-0123874 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1981054 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 6371 | 20241016 | 1104 | 20241016 | 1315 | 2596125 | 131 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1441 | 36.8639 | -121.7228 | No | Clear;Above 90 |  |  | 24-0124068 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1981134 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411948453310 | 20241016 | 1105 | 20241016 | 1242 | 2596128 | 97 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 970 | 36.7665 | -121.7501 | No | Clear;Above 90 | Connector or Splice (OH) | Burned/flashed | 24-0124039 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1981109 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 4813 | 20241016 | 1128 | 20241016 | 1634 | 2596149 | 306 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 2448 | 36.9602 | -121.7334 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0123966 | OH | Sus | 31712733 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1981079 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | RECLOSER | 11046 | 20241016 | 1438 | 20241016 | 1656 | 2596388 | 138 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 352 | 48576 | 36.9995 | -122.0078 | No | Partly Cloudy;32-90 F |  |  | 24-0124108 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1981147 | 0 | EPSS Ckt | Y | 2024 | GRD DCD INSTOC
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 3225 | 20241017 | 508 | 20241018 | 2329 | 2596783 | 2541 | Distribution Circuit | Equipment Failure/Involved | Underground | 14 | 35574 | 36.995 | -121.8719 | Yes | Partly Cloudy-Fog;32-90 F | Conductor- Underground | Broken | 24-0124374 | UG | Sus | 46340472 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1981237 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | SWITCH | 2307 | 20241017 | 959 | 20241017 | 1045 | 2596981 | 46 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 184 | 37.0318 | -121.9938 | Yes | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 24-0124441 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1981285 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 316131315310 | 20241017 | 1128 | 20241017 | 1458 | 2596984 | 210 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 210 | 36.9128 | -121.8245 | Yes | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0124504 | OH | Sus | 46340569 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1981306 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SOLEDAD-2102 | 182052102 | TRANSFORMER | 413044339797 | 20241017 | 1137 | 20241017 | 1515 | 2597033 | 218 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 218 | 36.4031 | -121.3643 | Yes | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0124506 | OH | Sus | 31713044 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1981307 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | RECLOSER | 83518 | 20241017 | 1921 | 20241017 | 2121 | 2597805 | 120 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 174 | 20880 | 36.8183 | -121.3881 | Yes | Clear;32-90 F |  |  | 24-0124785 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1981507 | 0 | EPSS Ckt | Y | 2024 | A/B
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | FUSE | 24805 | 20241017 | 2209 | 20241018 | 1425 | 2598022 | 976 | Distribution Circuit | 3rd Party | Vehicle | 2135 | 129080 | 36.6311 | -121.6796 | Yes | Clear;32-90 F | Pothead(Riser Termination) | Broken | 24-0124817 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1981583 | 0 | EPSS Ckt | Y | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 14130 | 20241018 | 13 | 20241018 | 343 | 2598079 | 210 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 108 | 22680 | 37.0476 | -122.1607 | No | Clear;32-90 F |  |  | 24-0124829 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1981601 | 0 | EPSS Ckt | Y | 2024 | B/C
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | SWITCH | 5817 | 20241018 | 17 | 20241019 | 1224 | 2598067 | 2167 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 91 | 197197 | 37.042 | -121.8179 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124827 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1981596 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | LOS GATOS-1107 | 82021107 | RECLOSER | 872428 | 20241018 | 38 | 20241019 | 1353 | 2598104 | 2235 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 2 | 4470 | 37.0992 | -121.8613 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124181 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1981605 | 0 | EPSS Ckt | N | 2024 | NONE
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 10254 | 20241018 | 223 | 20241018 | 526 | 2598118 | 183 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1098 | 37.1392 | -122.1787 | No | Clear;32-90 F |  |  | 24-0124834 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1981611 | 0 | EPSS Ckt | Y | 2024 | B&C
CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | OCB | 1103/2 | 20241018 | 231 | 20241019 | 1134 | 2598120 | 1983 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 11 | 21813 | 36.0134 | -121.1673 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0124333 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1981613 | 0 | EPSS Ckt | N | 2024 | N/A
CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | RECLOSER | 549180 | 20241018 | 231 | 20241019 | 1136 | 2598123 | 1985 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 9 | 17865 | 36.0057 | -121.2422 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124333 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1981615 | 0 | EPSS Ckt | N | 2024 | N/A
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | OCB | 1102/2 | 20241018 | 246 | 20241019 | 1127 | 2598127 | 1961 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 115 | 225515 | 36.0134 | -121.1674 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124331 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1981617 | 0 | EPSS Ckt | N | 2024 | NONE
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | RECLOSER | 7040 | 20241018 | 246 | 20241019 | 1129 | 2598131 | 1963 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 92 | 180596 | 36.0464 | -121.1764 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124331 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1981621 | 0 | EPSS Ckt | N | 2024 | NONE
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | RECLOSER | 7002 | 20241018 | 246 | 20241019 | 1135 | 2598133 | 1969 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 138 | 271722 | 35.9663 | -121.1146 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124331 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1981622 | 0 | EPSS Ckt | N | 2024 | NONE
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | RECLOSER | 7070 | 20241018 | 246 | 20241019 | 1257 | 2598134 | 2051 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 106 | 217406 | 35.9644 | -121.1175 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124331 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1981623 | 0 | EPSS Ckt | N | 2024 | NONE
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | RECLOSER | 7004 | 20241018 | 246 | 20241019 | 1300 | 2598135 | 2054 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 134 | 275236 | 35.9367 | -121.0781 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124331 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1981624 | 0 | EPSS Ckt | N | 2024 | NONE
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | RECLOSER | 7068 | 20241018 | 246 | 20241019 | 1306 | 2598138 | 2060 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 16 | 32960 | 35.9224 | -121.0376 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124331 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1981625 | 0 | EPSS Ckt | N | 2024 | NONE
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | FUSE | 7725 | 20241018 | 246 | 20241019 | 1257 | 2598818 | 2051 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 4 | 8204 | 35.9403 | -121.1212 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124331 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1981830 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | PANOCHE-1103 | 253671103 | SWITCH | 51085 | 20241018 | 255 | 20241019 | 913 | 2598130 | 1818 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 23 | 41814 | 36.4912 | -120.8042 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124836 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1981620 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | TRANSFORMER | 411792134773 | 20241018 | 506 | 20241020 | 1620 | 2598151 | 3554 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 31986 | 36.2551 | -121.7867 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 24-0124944 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1981709 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 14130 | 20241018 | 510 | 20241018 | 639 | 2598152 | 89 | Distribution Circuit | Vegetation | Tree - bark fell into line | 108 | 9612 | 37.0476 | -122.1607 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124848 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1981632 | 0 | EPSS Ckt | Y | 2024 | B/C
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 36516 | 20241018 | 606 | 20241018 | 835 | 2598161 | 149 | Distribution Circuit | Vegetation | Tree - branch fell on line | 399 | 57323 | 37.0787 | -122.1336 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124855 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1981636 | 0 | EPSS Ckt | Y | 2024 | B & C
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 280116 | 20241018 | 632 | 20241018 | 1955 | 2598167 | 803 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2230 | 442394 | 36.939 | -121.7423 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0124861 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Multi-Fault | 0 | No | Yes | No | 1981638 | 0 | EPSS Ckt | Y | 2024 | A&B & DCD ALARM
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | RECLOSER | 929132 | 20241018 | 657 | 20241018 | 828 | 2598178 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 127 | 11557 | 36.9919 | -121.927 | No | Clear;32-90 F |  |  | 24-0124869 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1981641 | 0 | EPSS Ckt | Y | 2024 | B
CENTRAL COAST | COAST | PAUL SWEET-2103 | 83252103 | TRANSFORMER | 315588217954 | 20241018 | 701 | 20241018 | 830 | 2598207 | 89 | Transformer only | Unknown Cause | Patrol - found nothing | 19 | 1691 | 36.9829 | -122.0105 | No | Clear;32-90 F |  |  | 24-0124878 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1981645 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 2931 | 20241018 | 711 | 20241018 | 1247 | 2598214 | 336 | Distribution Circuit | Animal | Bird found | 6033 | 792222 | 36.9859 | -122.0304 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124882 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1981646 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 974520 | 20241018 | 723 | 20241018 | 1148 | 2598227 | 265 | Distribution Circuit | Vegetation | Tree - fell into line | 881 | 47357 | 36.9908 | -121.8063 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0124885 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1981647 | 0 | EPSS Ckt | Y | 2024 | GRD & INST OC
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 4473 | 20241018 | 730 | 20241018 | 1357 | 2598259 | 387 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 6579 | 37.003 | -122.0141 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0125151 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1981818 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | RECLOSER | 92582 | 20241018 | 731 | 20241019 | 42 | 2598246 | 1031 | Distribution Circuit | Vegetation | Tree - fell into line | 416 | 306672 | 36.9911 | -122.02 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0124896 | OH | Sus | 46340774 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1981652 | 0 | EPSS Ckt | Y | 2024 | C GRD
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | RECLOSER | 12850 | 20241018 | 733 | 20241019 | 128 | 2598263 | 1075 | Distribution Circuit | Vegetation | Tree - fell into line | 2171 | 443091 | 36.9887 | -122.0069 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0124894 | OH | Sus | 46340774 | SOUTH BAY AND CENTRAL COAST | OCT | Three Phase Fault | 0 | No | Yes | No | 1981651 | 0 | EPSS Ckt | Y | 2024 | ABC GRD
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 11737 | 20241018 | 843 | 20241018 | 1006 | 2598377 | 83 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 1992 | 37.0695 | -122.1302 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124985 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1981758 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 5090 | 20241018 | 908 | 20241018 | 1048 | 2598423 | 100 | Distribution Circuit | Vegetation | Tree - branch fell on line | 435 | 31059 | 36.9804 | -121.892 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124960 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1981733 | 0 | EPSS Ckt | Y | 2024 | A & B
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 1563 | 20241018 | 920 | 20241018 | 1628 | 2598462 | 428 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 1284 | 37.045 | -122.0754 | No | Clear;32-90 F |  |  | 24-0125216 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1981836 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 11829 | 20241018 | 952 | 20241018 | 1632 | 2598493 | 400 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 2000 | 37.009 | -122.0756 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0125222 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1981838 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 1833 | 20241018 | 955 | 20241018 | 1024 | 2598510 | 29 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 551 | 36.9975 | -121.8161 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0125007 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1981771 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 37210 | 20241018 | 1005 | 20241019 | 1026 | 2598520 | 1461 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 143 | 32643 | 37.0809 | -122.0047 | No | Clear;32-90 F |  |  | 24-0124990 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1981763 | 0 | EPSS Ckt | Y | 2024 | A-G
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6639 | 20241018 | 1022 | 20241019 | 1410 | 2598538 | 1668 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 56712 | 37.0075 | -121.809 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0125037 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | Yes | No | 1981782 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 14130 | 20241018 | 1034 | 20241018 | 1213 | 2598549 | 99 | Distribution Circuit | Vegetation | Tree - bark fell into line | 108 | 10692 | 37.0476 | -122.1607 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0125014 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1981772 | 0 | EPSS Ckt | Y | 2024 | B&C
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 9681 | 20241018 | 1055 | 20241018 | 1332 | 2598581 | 157 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 1099 | 37.0117 | -121.8132 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0125132 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1981812 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 100715 | 20241018 | 1222 | 20241019 | 1545 | 2598647 | 1643 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 10996 | 37.0157 | -121.82 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0125220 | OH | Sus | 35591313 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1981837 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 6371 | 20241018 | 1426 | 20241018 | 1630 | 2598762 | 124 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 1364 | 36.8639 | -121.7228 | No | Clear;Above 90 | Fuse | Normal | 24-0125183 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1981828 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | RECLOSER | 23818 | 20241018 | 1631 | 20241019 | 1158 | 2598881 | 1167 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 24507 | 36.5428 | -121.6522 | No | Clear;32-90 F |  |  | 24-0125229 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1981840 | 0 | EPSS Ckt | Y | 2024 | A & C
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | RECLOSER | 777828 | 20241019 | 210 | 20241019 | 234 | 2599055 | 24 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2782 | 60908 | 36.9871 | -122.0358 | No | Partly Cloudy;32-90 F | Switch (OH) | Burned/flashed | 24-0125283 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1981881 | 0 | EPSS Ckt | Y | 2024 | SGF
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | OTHER | 36912 | 20241019 | 517 | 20241019 | 828 | 2599089 | 191 | Distribution Circuit | Equipment Failure/Involved | Overhead | 277 | 19633 | 36.8384 | -121.5204 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0125287 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | Yes | 1981885 | 1 | EPSS Ckt | Y | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 3225 | 20241019 | 644 | 20241019 | 1939 | 2599097 | 775 | Distribution Circuit | Equipment Failure/Involved | Underground | 14 | 7650 | 36.995 | -121.8719 | No | Clear;32-90 F | Conductor- Underground | Normal | 24-0125412 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1982003 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SOLEDAD-2105 | 182052105 | RECLOSER | 315500 | 20241019 | 744 | 20241019 | 1414 | 2599135 | 390 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 3462 | 36.4743 | -121.3523 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0125301 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1981899 | 0 | EPSS Ckt | Y | 2024 | B-C
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 7807 | 20241019 | 1240 | 20241019 | 1745 | 2599362 | 305 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 5185 | 36.9884 | -121.7391 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0125404 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1981998 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | TRANSFORMER | 412145745324 | 20241019 | 1310 | 20241020 | 442 | 2599384 | 932 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1864 | 36.5496 | -121.6753 | No | Clear;32-90 F | Transformer | Deteriorated | 24-0125418 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1982007 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | JUMPER | JPRS 2 SE/OF CGC 411448147709 | 20241019 | 1330 | 20241019 | 1758 | 2599398 | 268 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 7504 | 36.6076 | -121.9154 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0125375 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1982009 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | RECLOSER | 9094 | 20241019 | 1406 | 20241019 | 1618 | 2599426 | 132 | Distribution Circuit | Animal | Bird found | 373 | 49236 | 36.5607 | -121.915 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0125428 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1982018 | 0 | EPSS Ckt | Y | 2024 | A-GRD
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 20103 | 20241019 | 1727 | 20241019 | 1857 | 2599520 | 90 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1169 | 36.7642 | -121.7504 | No | Clear;Above 90 |  |  | 24-0125475 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1982037 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | RECLOSER | 624200 | 20241020 | 806 | 20241020 | 908 | 2599683 | 62 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 310 | 36.2515 | -121.1984 | No | Clear;32-90 F |  |  | 24-0125502 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1982076 | 0 | EPSS Ckt | Y | 2024 | B-C
CENTRAL COAST | COAST | PAUL SWEET-2103 | 83252103 | FUSE | 5395 | 20241020 | 1120 | 20241020 | 1148 | 2599745 | 28 | Distribution Circuit | Vegetation | Tree - branch fell on line | 100 | 2800 | 36.9737 | -122.0156 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0125532 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1982106 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 23827 | 20241020 | 1300 | 20241020 | 1314 | 2599833 | 14 | Distribution Circuit | 3rd Party | Other | 5 | 70 | 36.7388 | -121.6718 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0125545 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1982116 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 10019 | 20241020 | 2122 | 20241020 | 2151 | 2599926 | 29 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 261 | 37.022 | -121.9515 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0125576 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1982137 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | RECLOSER | 7058 | 20241020 | 2147 | 20241021 | 1129 | 2599951 | 822 | Distribution Circuit | 3rd Party | Vehicle | 419 | 79029 | 36.3369 | -121.2541 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 24-0125578 | OH | Sus | 35591579 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1982138 | 0 | Non-EPSS | N | 2024 | B/GRD
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | RECLOSER | 83518 | 20241021 | 135 | 20241021 | 311 | 2599970 | 96 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 174 | 16704 | 36.8183 | -121.3881 | No | Partly Cloudy;32-90 F |  |  | 24-0125585 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1982148 | 0 | EPSS Ckt | Y | 2024 | B/C
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | TRANSFORMER | 412629544690 | 20241021 | 956 | 20241021 | 1053 | 2600294 | 57 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 57 | 36.535 | -121.5098 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0125756 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1982342 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 1641 | 20241021 | 1350 | 20241021 | 1435 | 2600541 | 45 | Distribution Circuit | 3rd Party | Other | 52 | 2340 | 36.9326 | -121.8121 | No | Clear;32-90 F | Pole-Wood | Normal | 24-0125879 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1982382 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | JUMPER | JUMPERS 2P SS OF CGC# 315966117045 | 20241021 | 2118 | 20241022 | 100 | 2600782 | 222 | Distribution Circuit | Vegetation | Tree - grew into line | 18 | 3996 | 36.9602 | -121.8805 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0126041 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1982422 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SOLEDAD-2104 | 182052104 | FUSE | 179381 | 20241022 | 1244 | 20241022 | 1408 | 2601361 | 84 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 84 | 36.4292 | -121.3572 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0126328 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1982680 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 10599 | 20241022 | 1443 | 20241022 | 1520 | 2601510 | 37 | Distribution Circuit | Animal | Bird found | 1 | 37 | 36.9386 | -121.7424 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0126473 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1982715 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | RECLOSER | LAGUNA SECA TPG | 20241022 | 1832 | 20241022 | 1847 | 2601619 | 15 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 3078 | 46170 | 36.5582 | -121.7504 | No | Clear;32-90 F | Generator | Normal | 24-0118575 | OH | Sus | 35507124 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1982732 | 0 | EPSS Ckt | N | 2024 | NONE
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | RECLOSER | 2020 | 20241022 | 1927 | 20241022 | 2016 | 2601643 | 49 | Distribution Circuit | Company Initiated | Personnel- company | 840 | 41160 | 36.4632 | -121.7119 | No | Clear;32-90 F | Recloser | Normal | 24-0126578 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1982736 | 0 | EPSS Ckt | Y | 2024 | SGF/DCD
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | SWITCH | 7595BP | 20241022 | 2117 | 20241022 | 2335 | 2601667 | 138 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 690 | 36.5551 | -121.9195 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 24-0126541 | OH | Sus | 35591316 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1982744 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 5061 | 20241023 | 39 | 20241023 | 850 | 2601719 | 491 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 4 | 1964 | 36.7591 | -121.7642 | No | Clear;32-90 F |  |  | 24-0126625 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1982766 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | RECLOSER | 549180 | 20241023 | 541 | 20241023 | 548 | 2601759 | 7 | Distribution Circuit | 3rd Party | Customer Equipment | 9 | 63 | 36.0062 | -121.2421 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0126630 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Three Phase Fault | 0 | No | No | No | 1982772 | 0 | EPSS Ckt | Y | 2024 | A B & C PHSE
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | RECLOSER | 2020 | 20241023 | 955 | 20241023 | 1105 | 2602086 | 70 | Distribution Circuit | Company Initiated | Personnel- company | 840 | 58800 | 36.4632 | -121.7119 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0126767 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1982961 | 0 | EPSS Ckt | Y | 2024 | SGF & DCD
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | RECLOSER | 22412 | 20241023 | 1033 | 20241024 | 150 | 2602128 | 917 | Distribution Circuit | Equipment Failure/Involved | Overhead | 126 | 87390 | 36.4699 | -121.4635 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0126800 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1982980 | 0 | EPSS Ckt | Y | 2024 | BC INST
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 12760 | 20241023 | 1552 | 20241023 | 1814 | 2602391 | 142 | Distribution Circuit | Vegetation | Tree - fell into line | 554 | 26836 | 37.0674 | -121.9966 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0127042 | OH | Sus | 46343762 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1983047 | 0 | EPSS Ckt | Y | 2024 | A & GRD
CENTRAL COAST | KING CITY | SOLEDAD-2104 | 182052104 | FUSE | 179381 | 20241023 | 1614 | 20241023 | 1913 | 2602406 | 179 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 179 | 36.4292 | -121.3572 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0127050 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1983050 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 7723 | 20241023 | 1758 | 20241023 | 1954 | 2602475 | 116 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 77 | 36.5852 | -121.7531 | No | Clear;32-90 F |  |  | 24-0127090 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1983071 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 7655 | 20241024 | 159 | 20241024 | 410 | 2602657 | 131 | Distribution Circuit | Animal | Other | 22 | 2882 | 36.9728 | -122.0373 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 24-0127119 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1983088 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | TRANSFORMER | 411450247934 | 20241024 | 1129 | 20241024 | 1630 | 2603054 | 301 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 3913 | 36.6142 | -121.9153 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0127321 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1983293 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411836653826 | 20241024 | 1547 | 20241024 | 1831 | 2603212 | 164 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 328 | 36.7795 | -121.7889 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0127558 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1983342 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 64803 | 20241024 | 1551 | 20241024 | 2002 | 2603216 | 251 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 753 | 36.9963 | -122.0288 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0127617 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1983357 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 11427 | 20241024 | 2203 | 20241025 | 445 | 2603458 | 402 | Distribution Circuit | Company Initiated | Personnel- company | 9 | 3410 | 37.0545 | -122.0222 | No | Clear;32-90 F |  |  | 24-0117679 | OH | Sus | 47130572 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1983382 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 412084949439 | 20241025 | 206 | 20241025 | 1148 | 2603504 | 582 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 582 | 36.6605 | -121.6998 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0127662 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1983392 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | KING CITY-1106 | 182031106 | RECLOSER | 944510 | 20241025 | 832 | 20241025 | 1112 | 2603645 | 160 | Distribution Circuit | Equipment Failure/Involved | Overhead | 439 | 70240 | 36.2071 | -121.1151 | No | Partly Cloudy;32-90 F | Other | Deteriorated | 24-0127547 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1983464 | 0 | EPSS Ckt | N | 2024 | N/A
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | TRANSFORMER | 411466247763 | 20241025 | 930 | 20241025 | 1433 | 2603795 | 300 | Transformer only | Equipment Failure/Involved | Overhead | 20 | 6000 | 36.6096 | -121.9097 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0127792 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1983546 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 6663 | 20241025 | 1328 | 20241025 | 1935 | 2603927 | 367 | Distribution Circuit | Vegetation | Tree - grew into line | 7 | 559 | 36.9234 | -121.8103 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0127942 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1983582 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | TRANSFORMER | 412327352580 | 20241025 | 1730 | 20241026 | 1611 | 2604259 | 1361 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1361 | 36.7488 | -121.6203 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0128091 | OH | Sus | 35592777 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1983640 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | RECLOSER | 2624 | 20241025 | 1742 | 20241026 | 426 | 2604244 | 524 | Distribution Circuit | Animal | Bird found | 4667 | 2097515 | 36.569 | -121.7955 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0128068 | OH | Sus | 31713748 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1983621 | 0 | EPSS Ckt | Y | 2024 | C & GRD
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | RECLOSER | 3090 | 20241025 | 1916 | 20241026 | 644 | 2604286 | 688 | Distribution Circuit | 3rd Party | Vehicle | 1773 | 239576 | 36.7322 | -121.61 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0128080 | OH | Sus | 35592861 | SOUTH BAY AND CENTRAL COAST | OCT | Three Phase Fault | 0 | No | Yes | No | 1983628 | 0 | Non-EPSS | N | 2024 | ABC
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | TRANSFORMER | 316381815356 | 20241025 | 2009 | 20241026 | 957 | 2604115 | 828 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 828 | 36.915 | -121.7388 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0128085 | OH | Sus | 46344834 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1983630 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SOLEDAD-2105 | 182052105 | OCB | 2105/2 | 20241026 | 59 | 20241026 | 434 | 2604423 | 215 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 696 | 149640 | 36.4297 | -121.3323 | No | Clear;32-90 F |  |  | 24-0128101 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1983649 | 0 | EPSS Ckt | N | 2024 | A & B PHASE- SET A RLY- OC
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 509068 | 20241026 | 818 | 20241026 | 1133 | 2604603 | 195 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 37 | 7215 | 36.9915 | -121.7765 | No | Partly Cloudy;32-90 F |  |  | 24-0128121 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1983704 | 0 | EPSS Ckt | Y | 2024 | B-GRD
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | RECLOSER | 69608 | 20241026 | 944 | 20241026 | 1154 | 2604732 | 130 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3533 | 179707 | 36.5203 | -121.7901 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0128142 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1983748 | 0 | EPSS Ckt | Y | 2024 | A
CENTRAL COAST | COAST | CAMP EVERS-2107 | 83622107 | TRANSFORMER | 315429719945 | 20241026 | 1057 | 20241026 | 1221 | 2604794 | 84 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 252 | 37.0369 | -122.0669 | No | Partly Cloudy;32-90 F |  |  | 24-0128183 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1983787 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 7795 | 20241026 | 1110 | 20241026 | 1304 | 2604800 | 114 | Distribution Circuit | Animal | Squirrel | 2 | 228 | 37.0658 | -122.1497 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0128188 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1983793 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 4557 | 20241026 | 1435 | 20241026 | 1617 | 2604965 | 102 | Distribution Circuit | Animal | Bird found | 6 | 645 | 36.9276 | -121.7673 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0128212 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1983819 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 10599 | 20241026 | 1600 | 20241026 | 1653 | 2605003 | 53 | Distribution Circuit | Animal | Bird found | 1 | 53 | 36.9386 | -121.7424 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Normal | 24-0128216 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1983823 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | RECLOSER | 3094 | 20241026 | 1817 | 20241026 | 2000 | 2605085 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 67 | 6901 | 36.5164 | -121.4331 | No | Overcast;32-90 F |  |  | 24-0128226 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1983834 | 0 | EPSS Ckt | Y | 2024 | A & B PHASE
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | TRANSFORMER | 411997542509 | 20241026 | 1948 | 20241026 | 2059 | 2605124 | 71 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 213 | 36.4697 | -121.7231 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0128232 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1983841 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 3567 | 20241027 | 449 | 20241027 | 840 | 2605211 | 231 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 60 | 13846 | 36.8799 | -121.6939 | No | Clear;32-90 F |  |  | 24-0128262 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1983880 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 351054 | 20241027 | 959 | 20241027 | 1325 | 2605349 | 206 | Distribution Circuit | Animal | Squirrel | 828 | 78930 | 37.1971 | -122.1543 | No | Overcast;32-90 F | Transformer (OH) | Normal | 24-0128278 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1983906 | 0 | EPSS Ckt | Y | 2024 | A B
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | SWITCH | 6136 | 20241027 | 1402 | 20241027 | 1759 | 2605441 | 237 | Distribution Circuit | Equipment Failure/Involved | Underground | 314 | 5281 | 36.5382 | -121.9047 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0120425 | UG | Sus | 46332778 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1983935 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2102 | 182222102 | TRANSFORMER | 411705347987 | 20241027 | 1730 | 20241027 | 2346 | 2605576 | 376 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 3760 | 36.6174 | -121.828 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0128334 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1983955 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | FUSE | 9019 | 20241027 | 2224 | 20241028 | 38 | 2605619 | 134 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 52 | 6968 | 36.9054 | -121.4034 | No | Partly Cloudy;32-90 F |  |  | 24-0128350 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1983970 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 7637 | 20241027 | 2232 | 20241028 | 1025 | 2605621 | 713 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 19251 | 37.0078 | -121.9385 | No | Partly Cloudy;32-90 F |  |  | 24-0128348 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1983969 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | RECLOSER | 3712 | 20241027 | 2338 | 20241028 | 1203 | 2605627 | 745 | Distribution Circuit | Vegetation | Tree - branch fell on line | 655 | 116660 | 36.7758 | -121.6691 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0128347 | OH | Sus | 46344992 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1983968 | 0 | EPSS Ckt | N | 2024 | SGF
CENTRAL COAST | KING CITY | SAN ARDO-1101 | 182191101 | FUSE | 8571 | 20241028 | 735 | 20241028 | 1016 | 2605770 | 161 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 644 | 36.1208 | -121.0869 | No | Clear;32-90 F |  |  | 24-0128475 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1984141 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 8259 | 20241029 | 301 | 20241029 | 1258 | 2606736 | 142 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 3611 | 36.5764 | -121.968 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0128795 | OH | Sus | 31713905 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1984285 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | KING CITY-1106 | 182031106 | FUSE | 9293 | 20241029 | 1105 | 20241029 | 1218 | 2607233 | 73 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 73 | 36.2145 | -121.0928 | No | Clear;32-90 F |  |  | 24-0128994 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1984543 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | TRANSFORMER | 316355813612 | 20241029 | 1310 | 20241029 | 1356 | 2607342 | 46 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 276 | 36.8675 | -121.7468 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0129026 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1984556 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | RECLOSER | 557716 | 20241029 | 1536 | 20241030 | 810 | 2607619 | 994 | Distribution Circuit | 3rd Party | Vehicle | 331 | 111058 | 36.831 | -121.6794 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0129162 | OH | Sus | 35593354 | SOUTH BAY AND CENTRAL COAST | OCT | Three Phase Fault | 0 | No | Yes | No | 1984591 | 0 | EPSS Ckt | N | 2024 | ABC
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | TRANSFORMER | 315896517404 | 20241030 | 1423 | 20241031 | 115 | 2608532 | 652 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 9128 | 36.9695 | -121.9045 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0129731 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1984962 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | TRANSFORMER | 315854617690 | 20241030 | 1552 | 20241030 | 1819 | 2608605 | 147 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 1911 | 36.9771 | -121.9202 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0129720 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1984959 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | OTHER | WIRE DOWN @ 5837 | 20241030 | 2227 | 20241031 | 921 | 2608814 | 654 | Distribution Circuit | 3rd Party | Vehicle | 1551 | 8404 | 36.7977 | -121.6666 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0129804 | OH | Sus | 31714626 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | Yes | 1985005 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 266307 | 20241030 | 2348 | 20241031 | 119 | 2608759 | 91 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 12 | 1092 | 36.81 | -121.7218 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Deteriorated | 24-0129809 | OH | Sus | 31714173 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1985009 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 355 | 20241031 | 342 | 20241031 | 1530 | 2608982 | 708 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 5664 | 36.9622 | -122.0689 | No | Overcast-Fog-Drizzle;32-90 F | Insulator | Burned/flashed | 24-0129853 | OH | Sus | 31714671 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1985046 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | TRIP-SAVER | 3959 | 20241031 | 431 | 20241031 | 641 | 2609003 | 100 | Distribution Circuit | Vegetation | Tree - branch fell on line | 378 | 33687 | 36.959 | -122.0316 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0129856 | OH | Sus | 46353954 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1985049 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2101 | 182492101 | FUSE | 9951 | 20241031 | 701 | 20241031 | 1758 | 2609108 | 657 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 3345 | 36.8361 | -121.4191 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0129902 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1985074 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | JUMPER | FB LD SIDE OF CGC 315346622110 | 20241031 | 916 | 20241031 | 1528 | 2609280 | 372 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 6696 | 37.0969 | -122.0953 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0129951 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1985151 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 4969 | 20241031 | 1105 | 20241031 | 1614 | 2609546 | 309 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 1546 | 36.8843 | -121.3204 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0130084 | OH | Sus | 31714701 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1985249 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | RECLOSER | 2070 | 20241031 | 1213 | 20241101 | 334 | 2609623 | 921 | Distribution Circuit | 3rd Party | Vehicle | 444 | 111212 | 36.5447 | -121.9082 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0130114 | OH | Sus | 35593937 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1985265 | 0 | EPSS Ckt | N | 2024 | C GRD
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | TRANSFORMER | 412165351036 | 20241031 | 1311 | 20241031 | 2250 | 2609666 | 579 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 579 | 36.7051 | -121.6748 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 24-0130172 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1985288 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | TRES PINOS-1111 | 183221111 | TRANSFORMER | 413013154442 | 20241031 | 1440 | 20241031 | 1552 | 2609761 | 72 | Transformer only | Animal | Other | 2 | 144 | 36.8046 | -121.3875 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0130271 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1985318 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 614053 | 20241031 | 1920 | 20241031 | 2138 | 2609906 | 138 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 276 | 36.9042 | -121.7736 | No | Clear;32-90 F | Secondary | Burned/flashed | 24-0130333 | UG | Sus | 46354431 | SOUTH BAY AND CENTRAL COAST | OCT | Three Phase Fault | 0 | No | No | No | 1985344 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 6103 | 20241031 | 2011 | 20241101 | 919 | 2609916 | 788 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 43340 | 37.0115 | -122.0121 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0130335 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1985346 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | BORONDA-1101 | 182461101 | TRANSFORMER | 412176850915 | 20241031 | 2151 | 20241031 | 2212 | 2609855 | 21 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 231 | 36.7019 | -121.6699 | No | Partly Cloudy;32-90 F | Transformer | Deteriorated | 24-0130342 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1985351 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | RECLOSER | 4048 | 20241101 | 331 | 20241101 | 1457 | 2609979 | 686 | Distribution Circuit | Equipment Failure/Involved | Overhead | 125 | 55978 | 36.719 | -121.2811 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0130348 | OH | Sus | 31714708 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | Yes | No | 1985357 | 0 | EPSS Ckt | Y | 2024 | A & B INST
CENTRAL COAST | SALINAS | SOLEDAD-2105 | 182052105 | TRANSFORMER | 413065243972 | 20241101 | 816 | 20241101 | 2055 | 2610075 | 759 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1518 | 36.518 | -121.3613 | No | Clear;32-90 F | Transformer | Broken | 24-0130449 | OH | Sus | 46354528 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1985486 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2101 | 182492101 | TRANSFORMER | 412931455457 | 20241101 | 926 | 20241101 | 1054 | 2610190 | 88 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 264 | 36.8317 | -121.4167 | No | Partly Cloudy;32-90 F |  |  | 24-0130499 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1985534 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | FUSE | 23711 | 20241101 | 1542 | 20241101 | 2330 | 2610717 | 468 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 936 | 36.7042 | -121.6731 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0130735 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1985614 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 974520 | 20241102 | 149 | 20241102 | 848 | 2611075 | 418 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2398 | 732588 | 36.9908 | -121.8063 | No | Overcast-Fog-Rain;32-90 F | Jumper | Burned Open | 24-0130805 | OH | Sus | 46369784 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1985671 | 0 | EPSS Ckt | N | 2024 | B & GRD TIME
CENTRAL COAST | HOLLISTER | HOLLISTER SUB | 18249 | FUSE | 50961 | 20241102 | 214 | 20241102 | 700 | 2611112 | 286 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 572 | 36.9535 | -121.4151 | No | Partly Cloudy-Drizzle;32-90 F |  |  | 24-0130814 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1985677 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 6033 | 20241102 | 327 | 20241102 | 903 | 2611164 | 336 | Distribution Circuit | Vegetation | Tree - branch fell on line | 82 | 27552 | 37.081 | -122.0049 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0130890 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1985799 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 316053316589 | 20241102 | 640 | 20241102 | 1127 | 2611280 | 287 | Transformer only | Vegetation | Tree - bark fell into line | 3 | 861 | 36.9476 | -121.8517 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0130860 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1985733 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | RECLOSER | 198478 | 20241102 | 714 | 20241102 | 1459 | 2611357 | 465 | Distribution Circuit | Equipment Failure/Involved | Overhead | 239 | 71711 | 36.3913 | -121.6195 | No | Overcast;32-90 F | Crossarm- Wood | Burned/flashed | 24-0130848 | OH | Sus | 31715158 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1985719 | 0 | EPSS Ckt | Y | 2024 | A & C
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | FUSE | 7971 | 20241102 | 921 | 20241102 | 1039 | 2611549 | 78 | Distribution Circuit | Vegetation | Tree - bark fell into line | 1 | 78 | 36.9612 | -121.9766 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0130930 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1985831 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | BUENA VISTA-1102 | 182261102 | TRANSFORMER | T0927 | 20241102 | 1004 | 20241103 | 540 | 2611578 | 1176 | Distribution Circuit | Equipment Failure/Involved | Underground | 104 | 6942 | 36.6518 | -121.6273 | No | Overcast;32-90 F | Transformer (UG) | Failed/Faulted | 24-0130955 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1985850 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRANSFORMER | 315231923973 | 20241102 | 1126 | 20241102 | 2013 | 2611649 | 527 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 1054 | 37.1474 | -122.1345 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0130963 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1985863 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | SWITCH | 9245 | 20241102 | 1859 | 20241103 | 1040 | 2611940 | 941 | Distribution Circuit | Equipment Failure/Involved | Overhead | 62 | 24722 | 36.9446 | -121.5041 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0131047 | OH | Sus | 31715319 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1985912 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | SWITCH | 4908 | 20241102 | 1903 | 20241102 | 2034 | s1985904 | 91 | Distribution Circuit | Equipment Failure/Involved | Overhead | 515 | 38787 | 36.8837 | -121.4167 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0131035 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | Yes | No | 1985904 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | FUSE | 7443 | 20241103 | 529 | 20241103 | 958 | 2612156 | 269 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1256 | 36.0294 | -120.9113 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0131108 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1985976 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | RECLOSER | 113634 | 20241103 | 858 | 20241103 | 1035 | 2612274 | 97 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 90 | 5662 | 36.961 | -121.4309 | No | Partly Cloudy;32-90 F |  |  | 24-0131099 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1985966 | 0 | EPSS Ckt | Y | 2024 | AB
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 718066 | 20241103 | 1052 | 20241103 | 1158 | 2612370 | 66 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1830 | 120780 | 37.0649 | -122.0793 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0131116 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1985987 | 0 | EPSS Ckt | N | 2024 | GRD
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | JUMPER | WIRE DOWN PN BOTH SIDES OF CGC 315368821077 | 20241103 | 1210 | 20241103 | 1835 | 2612437 | 385 | Distribution Circuit | Vegetation | Tree - branch fell on line | 36 | 13758 | 37.068 | -122.0882 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0131135 | OH | Sus | 31716382 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1986004 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1101 | 182201101 | TRANSFORMER | 412668546468 | 20241103 | 1242 | 20241104 | 150 | 2612446 | 788 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 788 | 36.5836 | -121.4974 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0131149 | OH | Sus | 46374964 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1986016 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | RECLOSER | 944178 | 20241103 | 1450 | 20241103 | 1632 | 2612572 | 102 | Distribution Circuit | Vegetation | Tree - branch fell on line | 888 | 62163 | 37.0926 | -122.0964 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0131152 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1986018 | 0 | EPSS Ckt | Y | 2024 | A & GRD
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | TRANSFORMER | 411443440540 | 20241103 | 1551 | 20241105 | 1451 | 2612623 | 2820 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 2820 | 36.4122 | -121.9096 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0131195 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1986035 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 14130 | 20241104 | 44 | 20241104 | 524 | 2612794 | 280 | Distribution Circuit | Vegetation | Tree - branch fell on line | 108 | 30240 | 37.0476 | -122.1607 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0131221 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1986054 | 0 | EPSS Ckt | N | 2024 | B & C
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 428972 | 20241104 | 552 | 20241104 | 902 | 2612820 | 190 | Distribution Circuit | Vegetation | Tree - branch fell on line | 86 | 8529 | 37.1056 | -121.9724 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0131229 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1986064 | 0 | EPSS Ckt | Y | 2024 | B
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | TRANSFORMER | 315210019765 | 20241104 | 632 | 20241104 | 1356 | 2612810 | 444 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 444 | 37.0321 | -122.1411 | No | Clear;32-90 F | Service conductor | Broken | 24-0131248 | OH | Sus | 31716502 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1986082 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | TRANSFORMER | 412912359586 | 20241104 | 1259 | 20241104 | 1324 | 2613418 | 25 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 25 | 36.9447 | -121.4267 | No | Clear;32-90 F | Service conductor | Deteriorated | 24-0131456 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1986311 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | TRANSFORMER | 412970558782 | 20241104 | 1410 | 20241104 | 1517 | 2613500 | 67 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 67 | 36.9236 | -121.4062 | No | Clear;32-90 F | Bushing | Broken | 24-0131536 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1986329 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0421 | 182440421 | SWITCH | 6515 | 20241104 | 1859 | 20241105 | 434 | 2613710 | 575 | Distribution Circuit | Equipment Failure/Involved | Overhead | 137 | 24312 | 36.6161 | -121.9077 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0130981 | OH | Sus | 35593808 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1986382 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1108 | 182011108 | SWITCH | 259746 | 20241104 | 2016 | 20241105 | 1316 | 2613741 | 1020 | Distribution Circuit | 3rd Party | Vehicle | 2 | 2040 | 36.6642 | -121.6326 | No | Clear;32-90 F | Switch (UG) | Broken | 24-0124634 | UG | Sus | 35588026 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1986390 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 9613 | 20241105 | 348 | 20241105 | 518 | 2613837 | 90 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 270 | 36.869 | -121.3875 | Yes | Clear;32-90 F |  |  | 24-0131808 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1986423 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9771 | 20241105 | 827 | 20241105 | 1056 | 2614011 | 149 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 38 | 5662 | 37.1313 | -122.1209 | Yes | Clear;32-90 F |  |  | 24-0132011 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1986608 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CASSERLY-0401 | 83110401 | TRANSFORMER | 316314616985 | 20241105 | 955 | 20241105 | 1128 | 2614189 | 93 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 744 | 36.9596 | -121.7624 | Yes | Clear;32-90 F | Transformer (OH) | Leaking | 24-0131974 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1986591 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | OCB | 2204/2 | 20241105 | 1843 | 20241106 | 225 | 2614703 | 366 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8532 | 2131434 | 36.5786 | -121.9084 | Yes | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0132279 | OH | Sus | 46381935 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1986696 | 0 | EPSS Ckt | N | 2024 | A GRD
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 6559 | 20241105 | 2040 | 20241105 | 2215 | 2614953 | 95 | Distribution Circuit | 3rd Party | Metallic Balloon | 31 | 2945 | 36.9267 | -121.7459 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0132295 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1986815 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | SWITCH | 216684 | 20241105 | 2311 | 20241106 | 1703 | 2615125 | 1072 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 59 | 63248 | 37.0197 | -121.8186 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0131208 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | Yes | No | 1986848 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 543817 | 20241105 | 2311 | 20241106 | 2307 | 2617170 | 1436 | Distribution Circuit | Vegetation | Tree - branch fell on line | 49 | 70364 | 37.0487 | -121.8085 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0131208 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | Yes | No | 1987318 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | LOS GATOS-1107 | 82021107 | RECLOSER | 872428 | 20241105 | 2329 | 20241107 | 1517 | 2615155 | 2388 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 2 | 4776 | 37.0992 | -121.8613 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0131754 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1986867 | 0 | EPSS Ckt | N | 2024 | n/a
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 14130 | 20241106 | 29 | 20241106 | 143 | 2615319 | 74 | Distribution Circuit | Equipment Failure/Involved | Overhead | 108 | 7992 | 37.0476 | -122.1607 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 24-0132317 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1986880 | 0 | EPSS Ckt | Y | 2024 | B-C
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 10954 | 20241106 | 117 | 20241106 | 959 | 2615344 | 522 | Distribution Circuit | Vegetation | Tree - branch fell on line | 500 | 245556 | 36.9873 | -121.86 | No | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0132323 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1986895 | 0 | EPSS Ckt | Y | 2024 | B- GRD
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | RECLOSER | 428102 | 20241106 | 142 | 20241106 | 455 | 2615353 | 193 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 346 | 66778 | 36.9976 | -121.9515 | No | Partly Cloudy;32-90 F |  |  | 24-0132328 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1986900 | 0 | EPSS Ckt | Y | 2024 | B-GRD
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 12760 | 20241106 | 148 | 20241106 | 355 | 2615359 | 127 | Distribution Circuit | Vegetation | Tree - branch fell on line | 552 | 69272 | 37.0674 | -121.9966 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0132330 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1986901 | 0 | EPSS Ckt | Y | 2024 | A GRD
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | OTHER | WIRE DOWN 1 LD SIDE OF CGC 315755021200 | 20241106 | 148 | 20241106 | 1555 | 2616720 | 847 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 6248 | 37.0734 | -121.9556 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0132641 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | Yes | 1987239 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2103 | 83252103 | RECLOSER | 49370 | 20241106 | 209 | 20241106 | 843 | 2615376 | 394 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 590 | 232460 | 36.9816 | -122.0251 | No | Partly Cloudy;32-90 F |  |  | 24-0132333 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1986903 | 0 | EPSS Ckt | Y | 2024 | A/GRD
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 12957 | 20241106 | 214 | 20241106 | 1615 | 2616434 | 841 | Distribution Circuit | Vegetation | Tree - branch fell on line | 51 | 42891 | 36.9885 | -122.0304 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0132699 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1987279 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | OCB | 2105/2 | 20241106 | 216 | 20241106 | 955 | 2615380 | 459 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6320 | 2880360 | 36.9926 | -121.9821 | No | Partly Cloudy;32-90 F |  |  | 24-0132337 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1986906 | 0 | EPSS Ckt | Y | 2024 | PHASE OC-GRD
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 14130 | 20241106 | 233 | 20241106 | 2201 | 2615386 | 1168 | Distribution Circuit | Vegetation | Tree - fell into line | 466 | 83371 | 37.0476 | -122.1607 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0132339 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | Yes | No | 1986909 | 0 | EPSS Ckt | Y | 2024 | B-C
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 5411 | 20241106 | 233 | 20241106 | 1620 | 2616641 | 827 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 14059 | 37.0548 | -122.161 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0132601 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | Yes | No | 1987223 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 280116 | 20241106 | 237 | 20241106 | 1452 | 2615387 | 735 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2246 | 939759 | 36.939 | -121.7423 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0132340 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1986910 | 0 | EPSS Ckt | Y | 2024 | C/ SGF/DCD/ INST
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 36514 | 20241106 | 237 | 20241106 | 1141 | 2615388 | 544 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 76 | 41344 | 37.0395 | -122.1518 | No | Partly Cloudy;32-90 F |  |  | 24-0132341 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1986911 | 0 | EPSS Ckt | Y | 2024 | B-C
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 33542 | 20241106 | 242 | 20241106 | 1058 | 2615390 | 496 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 400 | 198115 | 37.0906 | -122.0456 | No | Clear;32-90 F |  |  | 24-0132342 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1986912 | 0 | EPSS Ckt | Y | 2024 | B
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 5300 | 20241106 | 245 | 20241106 | 1707 | 2615392 | 862 | Distribution Circuit | Vegetation | Tree - branch fell on line | 919 | 501079 | 37.0383 | -122.0708 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0132344 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | Yes | No | 1986913 | 0 | EPSS Ckt | Y | 2024 | A & B PHASE- INST OC
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | RECLOSER | 10726 | 20241106 | 300 | 20241106 | 1137 | 2615397 | 517 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 234 | 103818 | 37.061 | -122.1493 | No | Clear;32-90 F |  |  | 24-0132346 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1986914 | 0 | EPSS Ckt | Y | 2024 | B-C-
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | RECLOSER | 5178 | 20241106 | 305 | 20241106 | 1528 | 2615401 | 743 | Distribution Circuit | Vegetation | Tree - fell into line | 268 | 133473 | 37.0324 | -121.9467 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0132350 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1986918 | 0 | EPSS Ckt | Y | 2024 | C-GRD
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 5090 | 20241106 | 336 | 20241106 | 749 | 2615410 | 253 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 435 | 78075 | 36.9804 | -121.892 | No | Partly Cloudy;32-90 F |  |  | 24-0132354 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1986921 | 0 | EPSS Ckt | Y | 2024 | A/B
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 718066 | 20241106 | 405 | 20241106 | 629 | 2615542 | 144 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1830 | 263520 | 37.0649 | -122.0793 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0132379 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1986956 | 0 | EPSS Ckt | Y | 2024 | GRD
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8137 | 20241106 | 406 | 20241106 | 1554 | 2615419 | 708 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 9912 | 37.0581 | -121.9802 | No | Clear;32-90 F |  |  | 24-0132831 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1987306 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 5232 | 20241106 | 449 | 20241106 | 1608 | 2615438 | 679 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 389 | 77913 | 37.0752 | -122.054 | No | Clear;32-90 F |  |  | 24-0132365 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1986929 | 0 | EPSS Ckt | Y | 2024 | G/GRD
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 12518 | 20241106 | 519 | 20241106 | 1433 | 2615555 | 554 | Distribution Circuit | Vegetation | Tree - branch fell on line | 615 | 161455 | 37.0791 | -122.0037 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0132373 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1986942 | 0 | EPSS Ckt | Y | 2024 | B-GRD
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 1529 | 20241106 | 534 | 20241106 | 1141 | 2615601 | 367 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 3303 | 37.0317 | -121.9345 | No | Clear;32-90 F |  |  | 24-0132639 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1987237 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | SWITCH | 12895 | 20241106 | 603 | 20241107 | 1229 | 2617031 | 1826 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 12782 | 37.0883 | -121.9718 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0132792 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | Yes | No | 1987299 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 243760 | 20241106 | 604 | 20241106 | 1342 | 2615621 | 458 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1691 | 409225 | 37.1386 | -122.1775 | No | Clear;32-90 F |  |  | 24-0132380 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1986957 | 0 | EPSS Ckt | Y | 2024 | B&C PHASE
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 1907 | 20241106 | 624 | 20241106 | 2018 | 2615665 | 834 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 10008 | 37.0973 | -121.9748 | No | Clear;32-90 F | Jumper | Broken | 24-0132834 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1987307 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 3621 | 20241106 | 635 | 20241106 | 2310 | 2615684 | 995 | Distribution Circuit | Equipment Failure/Involved | Overhead | 123 | 39125 | 36.7789 | -121.6493 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0132511 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1987157 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 3317 | 20241106 | 705 | 20241106 | 1825 | 2615707 | 680 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1360 | 37.0644 | -121.9832 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 24-0132743 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1987287 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | RECLOSER | 4042 | 20241106 | 758 | 20241106 | 1132 | 2615846 | 214 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 158 | 33812 | 36.8611 | -121.3623 | No | Clear;32-90 F |  |  | 24-0132429 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1987008 | 0 | EPSS Ckt | Y | 2024 | B & C
CENTRAL COAST | HOLLISTER | HOLLISTER-2101 | 182492101 | SWITCH | 80843 | 20241106 | 821 | 20241106 | 1113 | 2615908 | 172 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 344 | 36.8298 | -121.4017 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0132439 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1987024 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | TRANSFORMER | 411367343677 | 20241106 | 915 | 20241106 | 2015 | 2616367 | 660 | Transformer only | 3rd Party | Other | 8 | 5280 | 36.4962 | -121.9378 | No | Clear;32-90 F | Service conductor | Normal | 24-0132560 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1987202 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 10912 | 20241106 | 957 | 20241107 | 1736 | 2616459 | 1899 | Distribution Circuit | Vegetation | Tree - fell into line | 1647 | 800885 | 37.0913 | -122.0961 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0132545 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | Yes | No | 1987188 | 0 | EPSS Ckt | Y | 2024 | A & C
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 6343 | 20241106 | 1445 | 20241106 | 2032 | 2617241 | 347 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 5916 | 37.2223 | -122.1449 | No | Clear;32-90 F |  |  | 24-0132889 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1987328 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 128618 | 20241106 | 1617 | 20241107 | 348 | 2617115 | 691 | Distribution Circuit | 3rd Party | Vehicle | 602 | 61951 | 36.9203 | -121.687 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0132848 | OH | Sus | 35596412 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | Yes | No | 1987311 | 0 | EPSS Ckt | Y | 2024 | B & C PHASE & INST OC
CENTRAL COAST | KING CITY | KING CITY-1105 | 182031105 | OTHER | J698 TWD T0820 | 20241106 | 1851 | 20241106 | 2131 | 2617257 | 160 | Distribution Circuit | Equipment Failure/Involved | Underground | 130 | 3643 | 36.2164 | -121.1333 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0132793 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1987330 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1101 | 182011101 | OTHER | WIRE DOWN 1 E/OF 4605 | 20241106 | 1943 | 20241107 | 901 | 2617283 | 798 | Distribution Circuit | Equipment Failure/Involved | Overhead | 709 | 181422 | 36.6762 | -121.6489 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0132899 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | Yes | 1987335 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 67520 | 20241107 | 733 | 20241107 | 850 | 2617446 | 77 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2732 | 136290 | 36.9577 | -121.8525 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0132980 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1987387 | 0 | EPSS Ckt | Y | 2024 | B & C PHASE- INST OC
CENTRAL COAST | MONTEREY | DEL MONTE-1101 | 182221101 | TRANSFORMER | 411675848032 | 20241107 | 1002 | 20241107 | 1055 | 2617786 | 53 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 795 | 36.6184 | -121.838 | No | Clear;32-90 F | Service conductor | Deteriorated | 24-0133043 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1987529 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | RECLOSER | 22158 | 20241107 | 1151 | 20241108 | 9 | 2617908 | 738 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 465 | 50805 | 36.7999 | -121.6992 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0133116 | OH | Sus | 31716795 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1987558 | 0 | EPSS Ckt | Y | 2024 | A & GRD
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | JUMPER | WIRE DOWN 4 SPANS LD SIDE OF 86399 | 20241108 | 820 | 20241108 | 1558 | 2618550 | 458 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 2720 | 36.7688 | -121.794 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0133453 | OH | Sus | 46383606 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1987774 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | TRANSFORMER | 316422513546 | 20241108 | 943 | 20241108 | 2029 | 2618495 | 646 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 3876 | 36.8659 | -121.7243 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0133484 | OH | Sus | 46383608 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1987839 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | TRANSFORMER | 316343415550 | 20241108 | 1209 | 20241108 | 1237 | 2618777 | 28 | Transformer only | Equipment Failure/Involved | Overhead | 23 | 644 | 36.9203 | -121.7518 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0133595 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1987905 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | FUSE | 295566 | 20241108 | 1519 | 20241108 | 1722 | 2619210 | 123 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 36 | 4388 | 36.8262 | -121.4972 | No | Clear;32-90 F |  |  | 24-0133684 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1987929 | 0 | EPSS Ckt | Y | 2024
CENTRAL COAST | SALINAS | SPENCE-1101 | 182201101 | RECLOSER | 965598 | 20241109 | 615 | 20241109 | 846 | 2619424 | 151 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 168 | 25368 | 36.5774 | -121.4917 | No | Clear;32-90 F |  |  | 24-0133760 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1987987 | 0 | Non-EPSS | Y | 2024 | B- C- INST
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 6695 | 20241109 | 1821 | 20241109 | 2008 | 2619953 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 963 | 36.902 | -121.772 | No | Clear;32-90 F |  |  | 24-0133869 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1988130 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 23401 | 20241110 | 621 | 20241110 | 947 | 2620035 | 206 | Distribution Circuit | Animal | Bird found | 8 | 1648 | 36.792 | -121.6268 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0133904 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1988184 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DEL MONTE-2104 | 182222104 | JUMPER | BURNT OPEN JMPR E/O 5467 NORTH AND SOUTH | 20241110 | 733 | 20241110 | 1049 | 2620057 | 196 | Distribution Circuit | Equipment Failure/Involved | Overhead | 340 | 3073 | 36.5497 | -121.7326 | No | Clear;32-90 F | Jumper | Burned Open | 24-0133917 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Open Circuit | 0 | No | No | No | 1988195 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | KING CITY-1103 | 182031103 | RECLOSER | 7038 | 20241110 | 1526 | 20241110 | 1712 | 2620277 | 106 | Distribution Circuit | Animal | Bird found | 796 | 84376 | 36.1935 | -121.1442 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0133955 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1988227 | 0 | EPSS Ckt | Y | 2024 | A&C
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 38430 | 20241111 | 426 | 20241111 | 1244 | 2620419 | 460 | Distribution Circuit | Vegetation | Tree - bark fell into line | 5533 | 157182 | 36.9756 | -121.8885 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0133998 | OH | Sus | 31717143 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | Yes | No | 1988274 | 0 | EPSS Ckt | N | 2024 | AB
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 3621 | 20241111 | 632 | 20241111 | 812 | 2620466 | 100 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 82 | 8204 | 36.7789 | -121.6493 | No | Clear;32-90 F |  |  | 24-0134030 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1988313 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | FUSE | 9707 | 20241111 | 732 | 20241111 | 1013 | 2620585 | 161 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 644 | 37.1114 | -122.1139 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0134087 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1988397 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6153 | 20241111 | 732 | 20241111 | 1858 | 2620505 | 686 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 6174 | 36.9995 | -121.774 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 24-0134082 | OH | Sus | 46385418 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1988393 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 181438 | 20241111 | 1015 | 20241111 | 1144 | 2620815 | 89 | Distribution Circuit | Vegetation | Tree - branch fell on line | 139 | 12371 | 37.1536 | -122.1621 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0134085 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1988395 | 0 | EPSS Ckt | N | 2024 | A & B PHASE
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | RECLOSER | 586340 | 20241111 | 1138 | 20241111 | 1346 | 2620980 | 128 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 218 | 27904 | 36.5537 | -121.694 | No | Clear;32-90 F |  |  | 24-0134117 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1988425 | 0 | EPSS Ckt | N | 2024 | A- B- & INST OC
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | OCB | 1111/2 | 20241111 | 1147 | 20241111 | 1436 | 2620985 | 169 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1602 | 266431 | 36.4778 | -121.7269 | No | Clear;32-90 F |  |  | 24-0134116 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1988424 | 0 | EPSS Ckt | Y | 2024 | C&GRD INST OC
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | RECLOSER | 406496 | 20241111 | 1157 | 20241112 | 109 | 2620999 | 792 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 645 | 63029 | 36.8698 | -121.4103 | No | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0134122 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | Yes | No | 1988430 | 0 | EPSS Ckt | N | 2024 | A & B
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | RECLOSER | 888750 | 20241111 | 1209 | 20241111 | 1708 | 2621074 | 299 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 1794 | 36.2298 | -121.7643 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0134124 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1988435 | 0 | EPSS Ckt | N | 2024 | A & C
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | FUSE | 7931 | 20241111 | 1224 | 20241112 | 957 | 2621388 | 1293 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 5172 | 36.3168 | -121.19 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken | 24-0134302 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1988603 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | OILFIELDS-1102 | 182391102 | RECLOSER | 41992 | 20241111 | 1328 | 20241112 | 29 | 2621183 | 661 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 30406 | 35.9889 | -120.88 | No | Overcast;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0134149 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1988459 | 0 | EPSS Ckt | N | 2024 | SGF
CENTRAL COAST | KING CITY | LOS COCHES-1101 | 182151101 | OTHER | WIRE DOWN AT CGC 413063037431 | 20241111 | 1500 | 20241112 | 405 | 2621685 | 785 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 1278 | 36.3372 | -121.3568 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0134235 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | Yes | 1988545 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 6771 | 20241111 | 1714 | 20241111 | 2229 | 2621892 | 315 | Distribution Circuit | Equipment Failure/Involved | Overhead | 53 | 7387 | 36.8682 | -121.6457 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0134318 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1988619 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 5071 | 20241112 | 636 | 20241112 | 841 | 2622385 | 125 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 1250 | 36.9718 | -121.7895 | No | Overcast-Fog;32-90 F |  |  | 24-0134503 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1988865 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | PANOCHE-1103 | 253671103 | RECLOSER | 4010 | 20241112 | 703 | 20241112 | 1245 | 2622427 | 342 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 204 | 42711 | 36.5951 | -120.7911 | No | Clear;32-90 F |  |  | 24-0134450 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1988775 | 0 | EPSS Ckt | Y | 2024 | A&B
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | TRANSFORMER | 412589455876 | 20241112 | 812 | 20241112 | 1459 | 2622506 | 407 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 407 | 36.8416 | -121.534 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0134554 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1988971 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | JUMPER | OJ 1 WEST OF CGC 315953817361 | 20241112 | 856 | 20241112 | 1011 | 2622612 | 75 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 2400 | 36.9682 | -121.8849 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Deteriorated | 24-0134502 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1988864 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | SAN BENITO-2102 | 182742102 | TRANSFORMER | 412822056636 | 20241112 | 1711 | 20241112 | 1810 | 2623359 | 59 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 354 | 36.8632 | -121.4547 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0134847 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1989107 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2102 | 182222102 | FUSE | 6461 | 20241112 | 2210 | 20241113 | 358 | 2623460 | 348 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 2 | 696 | 36.6045 | -121.8536 | No | Partly Cloudy-Fog;32-90 F | Conductor- Underground | Broken | 24-0134769 | UG | Sus | 46387882 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1989123 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 8461 | 20241113 | 722 | 20241113 | 1200 | 2623596 | 278 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 2224 | 37.1334 | -122.1028 | No | Clear;32-90 F |  |  | 24-0135074 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1989367 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | RECLOSER | 502 | 20241113 | 848 | 20241113 | 1007 | 2623745 | 79 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 163 | 12877 | 36.1289 | -121.0147 | No | Partly Cloudy-Rain;32-90 F |  |  | 24-0134962 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1989262 | 0 | EPSS Ckt | Y | 2024 | A B
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | RECLOSER | 5096 | 20241113 | 925 | 20241113 | 1155 | 2623846 | 150 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 526 | 30084 | 37.0509 | -122.0368 | No | Partly Cloudy;32-90 F |  |  | 24-0134986 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1989318 | 0 | EPSS Ckt | Y | 2024 | A B
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | RECLOSER | 4032 | 20241113 | 1227 | 20241113 | 2330 | 2624056 | 631 | Distribution Circuit | 3rd Party | Vehicle | 218 | 10390 | 36.7834 | -121.3204 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0135095 | OH | Sus | 31717503 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1989387 | 0 | EPSS Ckt | N | 2024 | A GRD
CENTRAL COAST | KING CITY | SAN ARDO-1101 | 182191101 | TRANSFORMER | 414161028060 | 20241113 | 1244 | 20241114 | 46 | 2624008 | 722 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 722 | 36.0873 | -120.9771 | No | Partly Cloudy;32-90 F | Transformer (OH) | Arcing | 24-0135109 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1989392 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | FUSE | 7491 | 20241113 | 1416 | 20241114 | 40 | 2624153 | 624 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1872 | 36.1469 | -121.0422 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0135171 | OH | Sus | 31717502 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1989413 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 7833 | 20241114 | 1239 | 20241114 | 1345 | 2625083 | 66 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 132 | 36.58 | -121.9448 | No | Partly Cloudy;32-90 F | Connector or Splice (UG) | Failed/Faulted | 24-0135517 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1989740 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | RECLOSER | 4032 | 20241114 | 1616 | 20241114 | 1642 | 2625310 | 26 | Distribution Circuit | Company Initiated | Personnel- company | 218 | 5220 | 36.7834 | -121.3204 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0135680 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1989806 | 0 | EPSS Ckt | N | 2024 | SGF
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | TRANSFORMER | 412964355982 | 20241114 | 1627 | 20241114 | 1717 | 2625301 | 50 | Transformer only | Vegetation | Tree - branch fell on line | 14 | 700 | 36.8465 | -121.4056 | No | Overcast;32-90 F | Crossarm- Wood | Deteriorated | 24-0135703 | OH | Sus | 31717450 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1989813 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | JUMPER | WIRE DOWN BET CGC 411789434708 & 8645 | 20241115 | 440 | 20241115 | 1223 | 2625577 | 463 | Distribution Circuit | Vegetation | Tree - branch fell on line | 415 | 190589 | 36.2531 | -121.7874 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0135754 | OH | Sus | 46389803 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | Yes | 1989855 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | RECLOSER | 2020 | 20241115 | 624 | 20241115 | 850 | 2625617 | 146 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 839 | 122494 | 36.4632 | -121.7119 | No | Clear;32-90 F |  |  | 24-0135762 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1989862 | 0 | EPSS Ckt | N | 2024 | A B
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | FUSE | 40639 | 20241115 | 819 | 20241115 | 1523 | 2625753 | 424 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 10600 | 36.6756 | -121.7938 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0135849 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1990006 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | JUMPER | WIRE DOWN SSD OF 6787 | 20241115 | 851 | 20241115 | 1256 | 2625822 | 245 | Distribution Circuit | Equipment Failure/Involved | Overhead | 602 | 15958 | 36.9288 | -121.7063 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0135858 | OH | Sus | 31717622 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | Yes | 1990031 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 942143 | 20241115 | 1140 | 20241115 | 1216 | 2626089 | 36 | Distribution Circuit | Company Initiated | Personnel- company | 75 | 2700 | 36.965 | -121.7331 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0135933 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1990080 | 0 | EPSS Ckt | N | 2024 | N/A
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | FUSE | 9881 | 20241115 | 1429 | 20241115 | 2114 | 2626278 | 405 | Distribution Circuit | 3rd Party | Vehicle | 3 | 1215 | 36.3108 | -121.2071 | No | Partly Cloudy;32-90 F | Anchor or Guy | Broken- wire on ground | 24-0136065 | OH | Sus | 31717533 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | Yes | 1990125 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 4811 | 20241115 | 1623 | 20241115 | 1828 | 2626349 | 125 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1375 | 36.959 | -121.735 | No | Clear;32-90 F |  |  | 24-0136118 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1990138 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | FUSE | 23101 | 20241116 | 630 | 20241116 | 810 | 2626541 | 100 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 36 | 3600 | 36.5833 | -121.6319 | No | Clear;32-90 F |  |  | 24-0136168 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1990195 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1101 | 182011101 | TRANSFORMER | 412267349900 | 20241117 | 805 | 20241117 | 1200 | 2627303 | 235 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 3055 | 36.6748 | -121.6384 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 24-0136317 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1990381 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | TRANSFORMER | 316351315736 | 20241117 | 816 | 20241117 | 1259 | 2627311 | 283 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1132 | 36.9254 | -121.7492 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0136323 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1990389 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | TRANSFORMER | 413288056056 | 20241117 | 901 | 20241117 | 1211 | 2627346 | 190 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 190 | 36.8505 | -121.296 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0136319 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1990383 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 4633 | 20241117 | 907 | 20241117 | 1030 | 2627355 | 83 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 387 | 36.7388 | -121.2787 | No | Clear;32-90 F |  |  | 24-0136307 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1990370 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | TRANSFORMER | 316312915301 | 20241117 | 910 | 20241117 | 1227 | 2627358 | 197 | Transformer only | Equipment Failure/Involved | Overhead | 25 | 4925 | 36.9134 | -121.7622 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 24-0136321 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1990387 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 7827 | 20241117 | 1542 | 20241117 | 1659 | 2627569 | 77 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 1848 | 36.9659 | -121.7932 | No | Overcast;32-90 F | Fuse | Broken | 24-0136355 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1990412 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6641 | 20241117 | 2350 | 20241118 | 604 | 2627713 | 374 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 77 | 28798 | 37.016 | -121.8161 | No | Clear;32-90 F |  |  | 24-0136374 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1990440 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411958253012 | 20241118 | 947 | 20241118 | 1113 | 2628128 | 86 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 1376 | 36.7588 | -121.7459 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0136546 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1990654 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6641 | 20241118 | 1019 | 20241118 | 1125 | 2628185 | 66 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 1692 | 37.016 | -121.8161 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0136543 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1990653 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 10025 | 20241118 | 1041 | 20241118 | 1534 | 2628216 | 293 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 11134 | 37.1398 | -122.1525 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0136585 | OH | Sus | 46390981 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | Yes | No | 1990669 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 11237 | 20241119 | 510 | 20241119 | 749 | 2628773 | 159 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 636 | 37.0904 | -121.9645 | No | Clear;32-90 F |  |  | 24-0136880 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1990788 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | FUSE | 9657 | 20241119 | 722 | 20241119 | 1042 | 2628822 | 200 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 6044 | 36.2615 | -121.1796 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0136964 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1990947 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | TRANSFORMER | 315273520830 | 20241119 | 757 | 20241119 | 1612 | 2628855 | 495 | Transformer only | Animal | Squirrel | 2 | 990 | 37.0608 | -122.1209 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0136975 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1990961 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SOLEDAD-2102 | 182052102 | TRANSFORMER | 413083838999 | 20241119 | 1229 | 20241119 | 2034 | 2629006 | 485 | Transformer only | Vegetation | Tree - grew into line | 1 | 485 | 36.3812 | -121.3507 | No | Partly Cloudy;32-90 F | Service conductor | Broken | 24-0137149 | OH | Sus | 31717757 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1991037 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1102 | 182201102 | FUSE | 20161 | 20241120 | 845 | 20241120 | 1145 | 2630341 | 180 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 4140 | 36.6064 | -121.5148 | No | Partly Cloudy;32-90 F | Cutout- fuse holder |  | 24-0137587 | OH | Sus | 31717997 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1991325 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | OTHER | WIRE DOWN 2 SP N/OF CGC 413559033190 | 20241120 | 1112 | 20241120 | 2055 | 2630749 | 583 | Distribution Circuit | 3rd Party | Vehicle | 16 | 673 | 36.2256 | -121.1855 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0137747 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | Yes | 1991426 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | FUSE | 4211 | 20241120 | 1222 | 20241120 | 1900 | 2631079 | 398 | Distribution Circuit | 3rd Party | Vehicle | 31 | 4874 | 36.9688 | -121.4325 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0137829 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1991473 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SOLEDAD-2101 | 182052101 | FUSE | 9003 | 20241120 | 1411 | 20241120 | 1510 | 2631328 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 177 | 36.4213 | -121.2849 | No | Partly Cloudy;32-90 F |  |  | 24-0137885 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1991509 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | BORONDA-1101 | 182461101 | TRANSFORMER | 412155150853 | 20241120 | 1615 | 20241121 | 250 | 2631586 | 635 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1905 | 36.7087 | -121.6777 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0138074 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1991618 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 601610 | 20241120 | 1630 | 20241120 | 1739 | 2631600 | 69 | Distribution Circuit | Vegetation | Tree - branch fell on line | 99 | 6831 | 37.1117 | -122.0207 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0137992 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1991568 | 0 | EPSS Ckt | N | 2024 | B-C
CENTRAL COAST | SALINAS | SALINAS-1103 | 182011103 | TRANSFORMER | 412210251076 | 20241120 | 2129 | 20241121 | 1329 | 2631974 | 960 | Distribution Circuit | Vegetation | Tree - grew into line | 91 | 37244 | 36.7066 | -121.6591 | No | Clear;32-90 F | Secondary | Together | 24-0138119 | OH | Sus | 46394512 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1991664 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | BUENA VISTA-1103 | 182261103 | TRANSFORMER | 412235849318 | 20241121 | 140 | 20241121 | 551 | 2632022 | 251 | Transformer only | Vegetation | Tree - grew into line | 7 | 1757 | 36.6585 | -121.6488 | No | Partly Cloudy;32-90 F | Transformer | Together | 24-0138148 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1991691 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | RECLOSER | 10976 | 20241121 | 250 | 20241121 | 1338 | 2632148 | 648 | Distribution Circuit | 3rd Party | Vehicle | 419 | 176088 | 36.913 | -121.6773 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 24-0138158 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Multi-Fault | 0 | No | Yes | No | 1991699 | 0 | EPSS Ckt | N | 2024 | A-B-GRD
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | INTERRUPTER | 799896 | 20241121 | 912 | 20241121 | 1115 | 2632469 | 123 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1599 | 36.8328 | -121.3637 | No | Partly Cloudy;32-90 F |  |  | 24-0138363 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1991819 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | OTHER | WIRE DOWN W N/E OF CGC 413387035385 | 20241121 | 1449 | 20241121 | 1815 | 2633017 | 206 | Distribution Circuit | Equipment Failure/Involved | Overhead | 710 | 6274 | 36.2853 | -121.2442 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0138574 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | Yes | 1991909 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 7235 | 20241121 | 1546 | 20241121 | 1617 | 2632749 | 31 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 465 | 37.1169 | -121.9917 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Together | 24-0138491 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1991877 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5599 | 20241121 | 1606 | 20241121 | 1827 | 2633241 | 141 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 2820 | 37.0796 | -122.0513 | No | Overcast-Rain;32-90 F |  |  | 24-0138639 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1991930 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2106 | 182402106 | SWITCH | 534771 | 20241121 | 1733 | 20241121 | 2148 | 2633214 | 255 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 255 | 36.6598 | -121.7809 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0138628 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1991925 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1103 | 182011103 | RECLOSER | 68200 | 20241121 | 1854 | 20241121 | 2042 | 2633275 | 108 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5608 | 591335 | 36.6909 | -121.6535 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 24-0138662 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1991936 | 0 | Non-EPSS | N | 2024 | SGF
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 3617 | 20241121 | 2045 | 20241122 | 1520 | 2633403 | 1115 | Distribution Circuit | Equipment Failure/Involved | Underground | 3 | 3345 | 37.0366 | -121.9497 | No | Overcast-Fog;32-90 F | Conductor- Underground | Broken | 24-0138716 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1991968 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 6319 | 20241122 | 656 | 20241122 | 805 | 2633920 | 69 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 170 | 11730 | 36.6038 | -121.8978 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0138806 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1992025 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9771 | 20241122 | 1001 | 20241122 | 1121 | 2634243 | 80 | Distribution Circuit | Animal | Bird found | 38 | 3040 | 37.1313 | -122.1209 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0138961 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1992141 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 6477 | 20241122 | 1529 | 20241122 | 1702 | 2634950 | 93 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 427 | 39711 | 36.8655 | -121.7346 | No | Clear;32-90 F |  |  | 24-0139209 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1992241 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 12758 | 20241122 | 1904 | 20241122 | 2154 | 2635384 | 170 | Distribution Circuit | Vegetation | Tree - branch fell on line | 282 | 47940 | 37.1486 | -122.1745 | No | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0139266 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Three Phase Fault | 0 | No | No | No | 1992284 | 0 | EPSS Ckt | N | 2024 | A-B-C
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 10714 | 20241122 | 2036 | 20241123 | 1143 | 2635490 | 907 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3197 | 111649 | 36.9779 | -121.8666 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0139301 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1992310 | 0 | EPSS Ckt | N | 2024 | B& GRD
CENTRAL COAST | SALINAS | BUENA VISTA-1103 | 182261103 | FUSE | 5369 | 20241122 | 2134 | 20241123 | 1940 | 2635567 | 1326 | Distribution Circuit | Vegetation | Tree - grew into line | 216 | 74919 | 36.6563 | -121.6452 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0139487 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1992483 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 40581 | 20241122 | 2144 | 20241123 | 1410 | 2635577 | 986 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 56202 | 36.5672 | -121.9132 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0139335 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1992342 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRANSFORMER | 315182724496 | 20241122 | 2149 | 20241124 | 905 | 2635585 | 2116 | Transformer only | Vegetation | Tree - branch fell on line | 5 | 10580 | 37.1612 | -122.1544 | No | Clear;32-90 F | Service conductor | Broken | 24-0139339 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1992346 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 11505 | 20241122 | 2238 | 20241123 | 1502 | 2635662 | 984 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 655 | 36.9042 | -121.7231 | No | Overcast-Fog-Heavy Rain;32-90 F | Insulator | Burned/flashed | 24-0139346 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1992354 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | RECLOSER | 66936 | 20241123 | 404 | 20241123 | 643 | 2635814 | 159 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 57 | 9063 | 36.3067 | -121.3117 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 24-0139393 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1992400 | 0 | EPSS Ckt | N | 2024 | A-B
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | OCB | 2106/2 | 20241123 | 612 | 20241123 | 954 | 2635853 | 222 | Distribution Circuit | Equipment Failure/Involved | Underground | 4605 | 890599 | 36.9926 | -121.9821 | No | Overcast-Fog;32-90 F | Connector or Splice (UG) | Failed/Faulted | 24-0139404 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Multi-Fault | 0 | No | No | No | 1992411 | 0 | EPSS Ckt | N | 2024 | A B GRD
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | FUSE | 9663 | 20241123 | 641 | 20241123 | 1329 | 2635883 | 408 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 2317 | 36.8933 | -121.5961 | No | Overcast-Fog-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 24-0139433 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1992438 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2102 | 83252102 | SWITCH | 777828 | 20241123 | 704 | 20241123 | 1217 | 2635843 | 313 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 1658 | 173456 | 36.9871 | -122.0358 | No | Overcast-Fog;32-90 F | Insulator | Burned/flashed | 24-0139413 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1992422 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 23683 | 20241123 | 715 | 20241123 | 1623 | 2635915 | 548 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1096 | 36.8118 | -121.7037 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0139474 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1992474 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 2989 | 20241123 | 932 | 20241123 | 1540 | 2636137 | 368 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 1104 | 37.1639 | -122.0767 | No | Overcast;32-90 F |  |  | 24-0139565 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1992546 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | FUSE | 9657 | 20241123 | 1021 | 20241123 | 1407 | 2636207 | 226 | Distribution Circuit | 3rd Party | Vehicle | 31 | 7006 | 36.2615 | -121.1796 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0139508 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1992500 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | TRANSFORMER | 411815649884 | 20241123 | 1244 | 20241123 | 1427 | 2636388 | 103 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 103 | 36.671 | -121.7917 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0139564 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1992545 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | TRANSFORMER | 412224152594 | 20241123 | 1253 | 20241123 | 1704 | 2636394 | 251 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 753 | 36.7485 | -121.6561 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0139554 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1992538 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 12333 | 20241123 | 1758 | 20241123 | 1915 | 2636600 | 77 | Distribution Circuit | Vegetation | Tree - bark fell into line | 1 | 77 | 36.8597 | -121.7947 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0139612 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1992571 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 981 | 20241123 | 2232 | 20241124 | 114 | 2636764 | 162 | Distribution Circuit | Company Initiated | Improper Construction | 13 | 2104 | 36.8668 | -121.6216 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0139630 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1992591 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2105 | 182402105 | TRANSFORMER | T2113 | 20241124 | 1019 | 20241125 | 304 | 2636968 | 1005 | Distribution Circuit | Equipment Failure/Involved | Underground | 954 | 20049 | 36.6445 | -121.8128 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 24-0139721 | UG | Sus | 35598964 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1992659 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 412072755475 | 20241124 | 1052 | 20241124 | 1601 | 2636979 | 309 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 618 | 36.8279 | -121.7102 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0139720 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1992657 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 2817 | 20241124 | 1223 | 20241124 | 1338 | 2637032 | 75 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 150 | 37.0532 | -121.9783 | No | Partly Cloudy;32-90 F |  |  | 24-0139723 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1992660 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6933 | 20241124 | 1653 | 20241125 | 1045 | 2637222 | 1072 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 5360 | 36.9296 | -121.7331 | No | Partly Cloudy-Drizzle;32-90 F |  |  | 24-0139776 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1992690 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | FUSE | 10565 | 20241125 | 18 | 20241125 | 550 | 2637282 | 332 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 332 | 37.008 | -121.9266 | No | Overcast-Drizzle;32-90 F |  |  | 24-0139809 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1992706 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 11028 | 20241125 | 41 | 20241125 | 753 | 2637284 | 432 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1240 | 504026 | 36.9714 | -121.8908 | No | Overcast-Drizzle;32-90 F | Connector or Splice (OH) | Broken | 24-0139803 | OH | Sus | 46399410 | SOUTH BAY AND CENTRAL COAST | NOV | Multi-Fault | 0 | No | No | No | 1992701 | 0 | EPSS Ckt | N | 2024 | BC&GRD
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 897 | 20241125 | 657 | 20241125 | 928 | 2637309 | 151 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 1510 | 36.8706 | -121.6202 | No | Overcast-Fog-Rain;32-90 F |  |  | 24-0139865 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1992728 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | TRANSFORMER | 315321017196 | 20241125 | 706 | 20241125 | 1241 | 2637311 | 335 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 335 | 36.9614 | -122.1026 | No | Overcast-Fog-Drizzle;32-90 F | Transformer | Failed/Faulted | 24-0139846 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1992717 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | FUSE | 23113 | 20241125 | 1113 | 20241125 | 1225 | 2637614 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 720 | 36.5963 | -121.621 | No | Partly Cloudy-Strong Winds;32-90 F |  |  | 24-0140016 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1992789 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | SWITCH | 10691 | 20241125 | 1251 | 20241126 | 335 | 2637674 | 396 | Distribution Circuit | Vegetation | Tree - grew into line | 28 | 3780 | 36.5679 | -121.9587 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0139994 | OH | Sus | 46400200 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1992788 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2108 | 83252108 | OCB | 2108/2 | 20241125 | 1401 | 20241125 | 1530 | 2637810 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6542 | 238386 | 36.9926 | -121.982 | No | Overcast-Drizzle;32-90 F |  |  | 24-0140050 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Three Phase Fault | 0 | No | No | No | 1992799 | 0 | EPSS Ckt | N | 2024 | A B C
CENTRAL COAST | SALINAS | SALINAS-1106 | 182011106 | TRANSFORMER | 412201149455 | 20241125 | 1416 | 20241125 | 1650 | 2637833 | 154 | Transformer only | Equipment Failure/Involved | Overhead | 49 | 7546 | 36.662 | -121.6607 | No | Overcast;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0140140 | OH | Sus | 31718627 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1992830 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | FUSE | 7445 | 20241125 | 1444 | 20241126 | 305 | 2637861 | 741 | Distribution Circuit | Equipment Failure/Involved | Overhead | 68 | 7173 | 35.9657 | -121.0819 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0140102 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1992816 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 2667 | 20241125 | 1604 | 20241126 | 101 | 2637927 | 537 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3222 | 37.0258 | -121.7751 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0140148 | OH | Sus | 46400302 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1992834 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 9053 | 20241125 | 2340 | 20241126 | 915 | 2638146 | 575 | Distribution Circuit | 3rd Party | Customer Equipment | 2 | 1150 | 36.9041 | -121.282 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0140360 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1992974 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | RECLOSER | 10952 | 20241126 | 301 | 20241126 | 1307 | 2638196 | 606 | Distribution Circuit | 3rd Party | Vehicle | 360 | 61328 | 36.8841 | -121.7552 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 24-0140224 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | Yes | No | 1992877 | 0 | EPSS Ckt | N | 2024 | A&B
CENTRAL COAST | KING CITY | OILFIELDS-1103 | 182391103 | TRANSFORMER | 414510219826 | 20241126 | 1133 | 20241127 | 1111 | 2638652 | 1418 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1529 | 35.8633 | -120.8542 | No | Overcast;32-90 F | Jumper | Burned Open | 24-0140563 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1993038 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | TRANSFORMER | 316449818152 | 20241126 | 2221 | 20241127 | 750 | 2639001 | 569 | Transformer only | Vegetation | Tree - fell into line | 2 | 1138 | 36.9928 | -121.717 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 24-0140726 | OH | Sus | 46401039 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1993087 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411909953424 | 20241126 | 2302 | 20241127 | 11 | 2639055 | 69 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 69 | 36.7689 | -121.7634 | No | Partly Cloudy;32-90 F | Transformer (OH) | Deteriorated | 24-0140725 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1993086 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRIP-SAVER | 6219 | 20241127 | 516 | 20241127 | 1040 | 2639098 | 324 | Distribution Circuit | Vegetation | Tree - fell into line | 699 | 8482 | 37.1841 | -122.1409 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0140740 | OH | Sus | 31718823 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1993096 | 0 | EPSS Ckt | N | 2024 | A & B
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6867 | 20241127 | 625 | 20241127 | 929 | 2639106 | 184 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 2760 | 37.025 | -121.8275 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0140845 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1993138 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | RECLOSER | 428972 | 20241127 | 633 | 20241127 | 800 | 2639116 | 87 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 7482 | 37.1056 | -121.9724 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0140775 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1993107 | 0 | EPSS Ckt | N | 2024 | A PHASE
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | FUSE | 3571 | 20241127 | 1042 | 20241127 | 1150 | 2639327 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 408 | 36.723 | -121.7268 | No | Clear;32-90 F |  |  | 24-0140959 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1993168 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 7206 | 20241127 | 2149 | 20241128 | 815 | 2639701 | 626 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 13146 | 36.5248 | -121.924 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0141178 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1993223 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | RECLOSER | 2166 | 20241127 | 2349 | 20241128 | 1221 | 2639726 | 752 | Distribution Circuit | 3rd Party | Vehicle | 474 | 356448 | 36.2769 | -121.8264 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0141176 | OH | Sus | 35601486 | SOUTH BAY AND CENTRAL COAST | NOV | Multi-Fault | 0 | No | Yes | No | 1993221 | 0 | EPSS Ckt | N | 2024 | A-B-GRD
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6933 | 20241128 | 803 | 20241128 | 1137 | 2639787 | 214 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 883 | 36.9296 | -121.7331 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0141194 | OH | Sus | 31718816 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | Yes | 1993237 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | TRANSFORMER | 315732817402 | 20241128 | 1317 | 20241128 | 1430 | 2639888 | 73 | Transformer only | Unknown Cause | Patrol - found nothing | 6 | 438 | 36.9682 | -121.9607 | No | Partly Cloudy;32-90 F |  |  | 24-0141219 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1993264 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 9197 | 20241128 | 1417 | 20241128 | 1527 | 2639896 | 70 | Distribution Circuit | Environmental/External | Water | 52 | 3613 | 37.051 | -122.0249 | No | Partly Cloudy;32-90 F | Transformer (UG) | Normal | 24-0141223 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1993269 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | TRANSFORMER | 315732817402 | 20241128 | 1504 | 20241128 | 2243 | 2639918 | 459 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 2754 | 36.9682 | -121.9607 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0141229 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1993275 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | TRANSFORMER | 411455447688 | 20241128 | 2301 | 20241129 | 1100 | 2639992 | 719 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 8628 | 36.6075 | -121.9133 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0141239 | OH | Sus | 35601492 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1993286 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 4385 | 20241129 | 633 | 20241129 | 900 | 2640031 | 147 | Distribution Circuit | Animal | Bird found | 7 | 980 | 36.8384 | -121.6724 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 24-0141259 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1993305 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 563 | 20241129 | 941 | 20241129 | 1824 | 2640067 | 523 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 5753 | 37.0587 | -122.1418 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0141273 | OH | Sus | 46402360 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1993314 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | FUSE | 4679 | 20241130 | 637 | 20241130 | 803 | 2640450 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 36 | 3096 | 36.8334 | -121.5213 | No | Clear;32-90 F |  |  | 24-0141352 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1993373 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 52559 | 20241130 | 638 | 20241130 | 945 | 2640457 | 187 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 1870 | 36.8343 | -121.6603 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0141376 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1993395 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 6121 | 20241201 | 649 | 20241201 | 1207 | 2640954 | 318 | Distribution Circuit | Equipment Failure/Involved | Overhead | 109 | 34662 | 36.9835 | -121.8848 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0141483 | OH | Sus | 31718961 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1993460 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | RECLOSER | 4040 | 20241201 | 925 | 20241201 | 1211 | 2640983 | 166 | Distribution Circuit | Animal | Squirrel | 524 | 83384 | 36.7535 | -121.2907 | No | Partly Cloudy;32-90 F | Recloser | Burned/flashed | 24-0141494 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Multi-Fault | 0 | No | No | No | 1993469 | 0 | EPSS Ckt | N | 2024 | A B & C PHSE
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 6921 | 20241201 | 1116 | 20241202 | 358 | 2641031 | 1002 | Distribution Circuit | Equipment Failure/Involved | Overhead | 49 | 13948 | 36.5546 | -121.9156 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0141517 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1993483 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1109 | 182011109 | FUSE | 64189 | 20241201 | 1358 | 20241201 | 2101 | 2641141 | 423 | Distribution Circuit | Equipment Failure/Involved | Overhead | 352 | 34039 | 36.6774 | -121.6379 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0141539 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1993493 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 52687 | 20241201 | 1540 | 20241202 | 55 | 2641176 | 555 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 2020 | 36.7656 | -121.7589 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0141549 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1993499 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | BUENA VISTA-1106 | 182261106 | TRANSFORMER | 412321848520 | 20241202 | 916 | 20241202 | 1315 | 2641426 | 239 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 239 | 36.6382 | -121.6177 | No | Clear;32-90 F | Jumper | Broken | 24-0141665 | OH | Sus | 46402571 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1993666 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | TRANSFORMER | 316206113328 | 20241202 | 923 | 20241202 | 1113 | 2641597 | 110 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 244 | 36.8587 | -121.798 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 24-0141670 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1993674 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | RECLOSER | 2166 | 20241202 | 1012 | 20241202 | 2018 | 2641728 | 606 | Distribution Circuit | Vegetation | Tree - fell into line | 468 | 283608 | 36.2769 | -121.8264 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0141704 | OH | Sus | 46402815 | SOUTH BAY AND CENTRAL COAST | DEC | Multi-Fault | 0 | No | Yes | No | 1993712 | 0 | EPSS Ckt | N | 2024 | A B & C PHSE
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | TRANSFORMER | 412014551620 | 20241202 | 1115 | 20241203 | 1323 | 2641822 | 1568 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 1568 | 36.7198 | -121.7268 | No | Clear;32-90 F |  |  | 24-0141830 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1993783 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SOLEDAD-2104 | 182052104 | TRANSFORMER | 100000035497 | 20241202 | 1222 | 20241202 | 1524 | 2641654 | 182 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 182 | 36.4558 | -121.4004 | No | Clear;32-90 F | Jumper | Broken | 24-0141758 | OH | Sus | 46402982 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1993741 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1106 | 182011106 | TRANSFORMER | 412201149455 | 20241202 | 1625 | 20241202 | 1716 | 2642262 | 51 | Transformer only | Equipment Failure/Involved | Overhead | 49 | 2499 | 36.662 | -121.6607 | No | Clear;32-90 F | Secondary | Burned/flashed | 24-0141898 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1993801 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | OCB | 2104/2 | 20241202 | 1720 | 20241203 | 245 | 2642298 | 565 | Distribution Circuit | 3rd Party | Vehicle | 683 | 64232 | 36.7632 | -121.7354 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0141913 | OH | Sus | 31718978 | SOUTH BAY AND CENTRAL COAST | DEC | Three Phase Fault | 0 | No | No | No | 1993808 | 0 | EPSS Ckt | N | 2024 | A-B-C
CENTRAL COAST | MONTEREY | DEL MONTE-1101 | 182221101 | FUSE | 296087 | 20241203 | 12 | 20241203 | 2024 | 2642395 | 1212 | Distribution Circuit | Equipment Failure/Involved | Overhead | 51 | 15252 | 36.6194 | -121.8368 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0141978 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1993836 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | TRANSFORMER | 100000205399 | 20241203 | 43 | 20241203 | 445 | 2642403 | 242 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 484 | 36.6286 | -121.9351 | No | Partly Cloudy;32-90 F | Transformer | Broken | 24-0141976 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1993834 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | TRANSFORMER | 413240653077 | 20241203 | 550 | 20241203 | 1609 | 2642430 | 619 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1238 | 36.7694 | -121.3087 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0142000 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1993846 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SOLEDAD-2102 | 182052102 | FUSE | 9965 | 20241203 | 1427 | 20241203 | 2018 | 2643098 | 351 | Distribution Circuit | Animal | Bird found | 3 | 1052 | 36.4061 | -121.37 | No | Partly Cloudy;32-90 F | Pole-Wood | Normal | 24-0142248 | OH | Sus | 31719156 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1994132 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-1101 | 182221101 | TRANSFORMER | 411716148079 | 20241204 | 107 | 20241204 | 219 | 2643372 | 72 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 864 | 36.6199 | -121.8243 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0142340 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1994180 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | TRANSFORMER | MTR#1008066213 | 20241204 | 618 | 20241204 | 1218 | 2643422 | 360 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 720 | 36.2462 | -121.1511 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0142413 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1994282 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | JUMPER | OJ @ 25821 | 20241204 | 841 | 20241204 | 1611 | 2643560 | 450 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 450 | 36.5102 | -121.5164 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 24-0142577 | OH | Sus | 46404175 | SOUTH BAY AND CENTRAL COAST | DEC | Open Circuit | 0 | No | No | No | 1994494 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SOLEDAD-2102 | 182052102 | JUMPER | BLOWN JMPR POS #2 @ CGC 413019939768 | 20241204 | 2038 | 20241205 | 202 | 2644329 | 324 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 2052 | 36.4023 | -121.3724 | No | Clear;32-90 F | Jumper | Burned Open | 24-0142758 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Open Circuit | 0 | No | No | No | 1994560 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 922576 | 20241205 | 822 | 20241205 | 839 | 2644443 | 17 | Distribution Circuit | Company Initiated | Personnel- company | 571 | 9707 | 37.0994 | -122.0532 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0001130 | OH | Sus | 45991980 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1994623 | 0 | EPSS Ckt | N | 2024 | SGF
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | RECLOSER | 5400 | 20241205 | 900 | 20241205 | 913 | 2644554 | 13 | Distribution Circuit | Company Initiated | Personnel- company | 614 | 7982 | 37.0801 | -122.0838 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0001130 | OH | Sus | 45991980 | SOUTH BAY AND CENTRAL COAST | DEC | Multi-Fault | 0 | No | No | No | 1994676 | 0 | EPSS Ckt | N | 2024 | A- C- & GRD
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | TRANSFORMER | 315530119366 | 20241205 | 919 | 20241205 | 1525 | 2644382 | 366 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 732 | 37.0212 | -122.0317 | No | Partly Cloudy;32-90 F | Secondary | Deteriorated | 24-0142854 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1994759 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | RECLOSER | 2026 | 20241205 | 1057 | 20241205 | 1103 | 2644973 | 6 | Distribution Circuit | Company Initiated | Personnel- company | 1072 | 6432 | 36.5315 | -121.8375 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0120833 | OH | Sus | 35466972 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1994795 | 0 | EPSS Ckt | N | 2024 | SGF
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | FUSE | 7981 | 20241205 | 1351 | 20241205 | 1522 | 2645166 | 91 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 637 | 37.0082 | -121.9663 | No | Clear;32-90 F | Insulator | Broken | 24-0142986 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1994850 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412186954162 | 20241206 | 337 | 20241206 | 1222 | 2645521 | 525 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1050 | 36.7915 | -121.6702 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0143209 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1994971 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | FUSE | 5893 | 20241206 | 344 | 20241206 | 525 | 2645525 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 99 | 9999 | 36.9642 | -121.9868 | No | Clear;32-90 F |  |  | 24-0143188 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1994955 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | TRANSFORMER | 412948057013 | 20241206 | 831 | 20241206 | 1944 | 2645631 | 673 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1346 | 36.875 | -121.4123 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0143264 | OH | Sus | 31719193 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1995119 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 6137 | 20241206 | 917 | 20241206 | 1125 | 2645754 | 128 | Distribution Circuit | Equipment Failure/Involved | Underground | 120 | 14775 | 36.5945 | -121.8932 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0143265 | UG | Sus | 46405266 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1995121 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | INTERRUPTER | 799896 | 20241206 | 1006 | 20241209 | 840 | 2645813 | 4234 | Distribution Circuit | Animal | Bird found | 13 | 34162 | 36.8328 | -121.3637 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0143309 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1995151 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SAN ARDO-1101 | 182191101 | FUSE | 9061 | 20241206 | 1011 | 20241206 | 2138 | 2645851 | 687 | Distribution Circuit | Animal | Bird found | 2 | 1374 | 36.1212 | -121.0374 | No | Clear;32-90 F | Conductor- Overhead | Burned/flashed | 24-0143420 | OH | Sus | 46405278 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1995199 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 11523 | 20241206 | 1225 | 20241206 | 1314 | 2645990 | 49 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 686 | 36.8839 | -121.7257 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0143381 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1995185 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | FUSE | 4641 | 20241206 | 1318 | 20241207 | 300 | 2646047 | 822 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 822 | 36.7614 | -121.7442 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0143464 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1995212 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | FUSE | 6001 | 20241206 | 2347 | 20241207 | 312 | s1995235 | 205 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 221 | 45396 | 36.9898 | -121.9328 | No | Clear;32-90 F |  |  | 24-0143513 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1995235 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | TRANSFORMER | 412278654394 | 20241207 | 140 | 20241208 | 441 | 2646288 | 1621 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 3242 | 36.7984 | -121.6386 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0143556 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1995295 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | TRIP-SAVER | 4929 | 20241207 | 335 | 20241207 | 916 | 2646298 | 341 | Distribution Circuit | Equipment Failure/Involved | Overhead | 133 | 45353 | 36.9129 | -121.8055 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0143524 | OH | Sus | 46405316 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | Yes | 1995246 | 1 | EPSS Ckt | N | 2024 | NONE
CENTRAL COAST | SALINAS | GONZALES-1101 | 182131101 | TRANSFORMER | T2018 | 20241207 | 904 | 20241208 | 444 | 2646410 | 1180 | Transformer only | Equipment Failure/Involved | Underground | 8 | 9440 | 36.514 | -121.4369 | No | Clear;32-90 F | Transformer | Broken | 24-0143623 | UG | Sus | 46407743 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1995376 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 985275 | 20241207 | 1739 | 20241207 | 1925 | 2646695 | 106 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 954 | 36.8629 | -121.6657 | No | Partly Cloudy;32-90 F |  |  | 24-0143647 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1995396 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | FUSE | 24972 | 20241209 | 951 | 20241209 | 1119 | 2647586 | 88 | Distribution Circuit | Equipment Failure/Involved | Overhead | 47 | 4136 | 36.6772 | -121.673 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0143870 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1995716 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2103 | 182492103 | SWITCH | 50157 | 20241209 | 1213 | 20241209 | 1323 | 2647775 | 70 | Distribution Circuit | Equipment Failure/Involved | Underground | 398 | 6380 | 36.8392 | -121.3696 | No | Clear;32-90 F | Transformer (UG) | Deteriorated | 24-0143894 | UG | Sus | 35604244 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1995777 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | TRANSFORMER | 315866818260 | 20241209 | 1251 | 20241209 | 1516 | 2647800 | 145 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 1450 | 36.993 | -121.9156 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0143933 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1995783 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | KING CITY-1103 | 182031103 | FUSE | 2529 | 20241209 | 1358 | 20241209 | 1531 | 2647869 | 93 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 2697 | 36.1899 | -121.1514 | No | Clear;32-90 F |  |  | 24-0143967 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1995813 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | FUSE | 24655 | 20241209 | 1502 | 20241209 | 1744 | 2647906 | 162 | Distribution Circuit | Equipment Failure/Involved | Overhead | 97 | 15714 | 36.6638 | -121.6767 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0143970 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1995815 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1106 | 182011106 | TRANSFORMER | 412194349635 | 20241209 | 1639 | 20241209 | 1700 | 2647975 | 21 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 294 | 36.6669 | -121.6632 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0144001 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1995837 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 243760 | 20241209 | 1950 | 20241210 | 1124 | 2648110 | 934 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1689 | 116187 | 37.1386 | -122.1775 | No | Clear;32-90 F |  |  | 24-0144039 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1995858 | 0 | EPSS Ckt | Y | 2024 | B C
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 52559 | 20241210 | 640 | 20241210 | 915 | 2648318 | 155 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1034 | 36.8343 | -121.6603 | No | Clear;32-90 F |  |  | 24-0144125 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1996096 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2103 | 83252103 | TRANSFORMER | 315587617868 | 20241210 | 816 | 20241210 | 923 | 2648421 | 67 | Transformer only | Unknown Cause | Patrol - found nothing | 21 | 1407 | 36.9806 | -122.0107 | No | Clear;32-90 F |  |  | 24-0144126 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1996103 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | FUSE | 9787 | 20241210 | 833 | 20241210 | 943 | 2648461 | 70 | Distribution Circuit | Animal | Bird found | 6 | 420 | 36.3052 | -121.236 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0144121 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1996070 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 1997 | 20241210 | 1101 | 20241210 | 1254 | 2648763 | 113 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 1130 | 36.9795 | -121.75 | No | Clear;32-90 F | Other | Normal | 24-0144170 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1996157 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2103 | 83252103 | OCB | 2103/2 | 20241210 | 1132 | 20241210 | 1252 | 2648835 | 80 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5752 | 281670 | 36.9926 | -121.9822 | No | Clear;32-90 F | Recloser | Failed/Faulted | 24-0144184 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1996181 | 0 | EPSS Ckt | N | 2024 | TRIP TARGET
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 4503 | 20241210 | 1449 | 20241210 | 1632 | 2649038 | 103 | Distribution Circuit | Animal | Bird found | 84 | 8656 | 36.7321 | -121.6559 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0144278 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1996249 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6805 | 20241210 | 1927 | 20241210 | 2005 | 2649214 | 38 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 190 | 36.9396 | -121.7419 | No | Partly Cloudy;32-90 F |  |  | 24-0144302 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1996264 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | FUSE | 24655 | 20241210 | 2022 | 20241210 | 2200 | 2649224 | 98 | Distribution Circuit | 3rd Party | Metallic Balloon | 97 | 9506 | 36.6638 | -121.6767 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0144310 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1996277 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 1997 | 20241211 | 955 | 20241211 | 1109 | 2649600 | 74 | Distribution Circuit | 3rd Party | Other | 10 | 740 | 36.9795 | -121.75 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0144369 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1996493 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2106 | 182402106 | FUSE | 21899 | 20241211 | 1043 | 20241212 | 1133 | 2649762 | 1490 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 1490 | 36.6569 | -121.7852 | No | Clear;32-90 F | Transformer (UG) | Burned/flashed | 24-0144425 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1996573 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 2553 | 20241211 | 1131 | 20241211 | 1230 | 2649774 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 118 | 36.9551 | -121.7478 | No | Clear;32-90 F |  |  | 24-0144424 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1996571 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 12009 | 20241211 | 1233 | 20241211 | 2154 | 2649827 | 561 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 5 | 2805 | 36.8535 | -121.6486 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0144441 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1996590 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | TRANSFORMER | 412977556263 | 20241211 | 1911 | 20241211 | 1950 | 2650214 | 39 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 273 | 36.8546 | -121.4015 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 24-0144496 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1996637 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 9403 | 20241212 | 216 | 20241212 | 348 | 2650385 | 92 | Distribution Circuit | Equipment Failure/Involved | Overhead | 109 | 10028 | 36.8779 | -121.7526 | No | Overcast-Heavy Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0144527 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1996672 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 9197 | 20241212 | 650 | 20241212 | 742 | 2650459 | 52 | Distribution Circuit | Equipment Failure/Involved | Underground | 52 | 2684 | 37.051 | -122.0249 | No | Overcast-Fog-Drizzle;32-90 F | Bushing | Failed/Faulted | 24-0144553 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1996701 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 411946353107 | 20241212 | 726 | 20241212 | 1336 | 2650471 | 370 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 2220 | 36.761 | -121.7505 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0144591 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1996812 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 6779 | 20241212 | 731 | 20241212 | 1356 | 2650477 | 385 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 770 | 36.8936 | -121.6442 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 24-0144600 | OH | Sus | 46415898 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1996836 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 9197 | 20241212 | 801 | 20241212 | 814 | 2650509 | 13 | Distribution Circuit | Equipment Failure/Involved | Underground | 52 | 671 | 37.051 | -122.0249 | No | Overcast-Fog-Drizzle;32-90 F | Bushing | Failed/Faulted | 24-0144562 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1996719 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 9197 | 20241212 | 821 | 20241213 | 301 | 2650547 | 674 | Distribution Circuit | Equipment Failure/Involved | Underground | 155 | 114913 | 37.051 | -122.0249 | No | Overcast-Drizzle;32-90 F | Bushing | Failed/Faulted | 24-0144572 | UG | Sus | 46416078 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1996733 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 1507 | 20241212 | 1410 | 20241212 | 1504 | 2651039 | 54 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 213 | 11502 | 37.0024 | -122.0148 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken | 24-0141941 | OH | Sus | 35567402 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1996918 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | TRANSFORMER | 412993456797 | 20241212 | 1639 | 20241212 | 1843 | 2651173 | 124 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 248 | 36.8691 | -121.3961 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0144703 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1996933 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 412073655023 | 20241212 | 1658 | 20241213 | 310 | 2651185 | 612 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1836 | 36.815 | -121.7094 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 24-0144725 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1996950 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRANSFORMER | 315226324463 | 20241212 | 1904 | 20241212 | 2306 | 2651262 | 242 | Transformer only | Unknown Cause | Patrol - found nothing | 5 | 1210 | 37.1608 | -122.1365 | No | Overcast-Drizzle;32-90 F |  |  | 24-0144743 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1996973 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | KING CITY-1105 | 182031105 | OCB | 1105/2 | 20241212 | 1917 | 20241212 | 2105 | 2651267 | 75 | Distribution Circuit | Company Initiated | Personnel- company | 1230 | 92444 | 36.217 | -121.1269 | No | Overcast;32-90 F | Switch (OH) | Failed/Faulted | 24-0086269 | OH | Sus | 35473200 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1996952 | 0 | Non-EPSS | N | 2024 | NONE
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | RECLOSER | 22428 | 20241212 | 2106 | 20241213 | 255 | 2651315 | 349 | Distribution Circuit | 3rd Party | Vehicle | 312 | 21847 | 36.7339 | -121.6791 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0144735 | OH | Sus | 35605565 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1996961 | 0 | EPSS Ckt | N | 2024 | NONE
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 40349 | 20241212 | 2256 | 20241212 | 2346 | 2651345 | 50 | Distribution Circuit | 3rd Party | Vehicle | 65 | 3263 | 36.5965 | -121.8402 | No | Overcast;32-90 F | Pole-Wood | Normal | 24-0144744 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1996974 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | TRANSFORMER | 315781918603 | 20241213 | 729 | 20241213 | 1502 | 2651485 | 453 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 906 | 37.0018 | -121.9453 | No | Overcast-Fog;32-90 F | Transformer | Failed/Faulted | 24-0144770 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997004 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412231155376 | 20241213 | 838 | 20241213 | 1559 | 2651560 | 441 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 882 | 36.8257 | -121.656 | No | Overcast;32-90 F | Transformer | Failed/Faulted | 24-0144846 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997149 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | TRANSFORMER | 412131751489 | 20241213 | 955 | 20241213 | 1244 | 2651711 | 169 | Transformer only | 3rd Party | Vehicle | 3 | 507 | 36.718 | -121.6863 | No | Clear;32-90 F | Transformer | Normal | 24-0144857 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997161 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 11575 | 20241213 | 1349 | 20241213 | 1520 | 2651993 | 91 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 10 | 910 | 36.9089 | -121.7695 | No | Overcast;32-90 F |  |  | 24-0144910 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1997205 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 3583 | 20241213 | 1412 | 20241213 | 1657 | 2652133 | 165 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 2310 | 37.1389 | -122.1011 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0144914 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1997210 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | TRANSFORMER | 413061056737 | 20241213 | 1416 | 20241213 | 1617 | 2652180 | 121 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 121 | 36.8682 | -121.3736 | No | Partly Cloudy;32-90 F | Transformer (OH) | Deteriorated | 24-0144931 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1997221 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | FUSE | 5173 | 20241213 | 1858 | 20241213 | 1939 | 2652233 | 41 | Distribution Circuit | Equipment Failure/Involved | Overhead | 57 | 2337 | 37.1011 | -122.1017 | No | Overcast;32-90 F | Secondary | Broken- wire on ground | 24-0144958 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | Yes | 1997256 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | KING CITY-1103 | 182031103 | FUSE | 2525 | 20241214 | 17 | 20241214 | 326 | 2652703 | 189 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 167 | 31563 | 36.1632 | -121.1625 | Yes | Overcast;32-90 F |  |  | 24-0145052 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1997357 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 8361 | 20241214 | 114 | 20241215 | 1900 | 2656549 | 2506 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 32578 | 37.0763 | -122.1318 | Yes | Overcast-Rain;32-90 F |  |  | 24-0146431 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998792 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 1519 | 20241214 | 236 | 20241214 | 1325 | 2652894 | 649 | Distribution Circuit | Equipment Failure/Involved | Overhead | 45 | 15313 | 37.0234 | -121.9325 | Yes | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Deteriorated | 24-0145086 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997390 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2101 | 182492101 | FUSE | 44963 | 20241214 | 451 | 20241214 | 600 | 2652964 | 69 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 1104 | 36.84 | -121.4059 | Yes | Partly Cloudy-Rain;32-90 F |  |  | 24-0145094 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1997399 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | FUSE | 23113 | 20241214 | 453 | 20241216 | 1135 | 2652975 | 3282 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 32820 | 36.5963 | -121.621 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Together | 24-0146561 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998946 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | OCB | 2201/2 | 20241214 | 505 | 20241216 | 1633 | 2653007 | 3505 | Distribution Circuit | Vegetation | Tree - fell into line | 1774 | 508016 | 36.5786 | -121.9085 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken | 24-0145137 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997443 | 0 | EPSS Ckt | N | 2024 | PHASE TOC
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 9827 | 20241214 | 552 | 20241215 | 1645 | 2653060 | 2093 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 23422 | 37.0797 | -122.1385 | Yes | Overcast-Heavy Rain;32-90 F |  |  | 24-0145454 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1997775 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1112 | 182371112 | RECLOSER | 68454 | 20241214 | 558 | 20241214 | 730 | 2653098 | 92 | Distribution Circuit | Vegetation | Tree - branch fell on line | 835 | 76820 | 36.4832 | -121.7378 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0145089 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997394 | 0 | EPSS Ckt | N | 2024 | C GRD
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 595388 | 20241214 | 612 | 20241215 | 1350 | 2653232 | 1898 | Distribution Circuit | Vegetation | Tree - fell into line | 174 | 330252 | 37.1517 | -122.136 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145117 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1997421 | 0 | EPSS Ckt | N | 2024 | A GRD
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | FUSE | 7931 | 20241214 | 614 | 20241214 | 1433 | 2653263 | 499 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1996 | 36.3168 | -121.19 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145527 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | No | 1997851 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 8175 | 20241214 | 619 | 20241216 | 2015 | 2660623 | 3716 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 196948 | 36.6038 | -121.9444 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0146085 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998428 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | RECLOSER | 9118 | 20241214 | 620 | 20241216 | 1009 | 2653347 | 3092 | Distribution Circuit | Vegetation | Tree - fell into line | 354 | 395813 | 36.6037 | -121.9359 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Switch (OH) | Normal | 24-0145107 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1997413 | 0 | EPSS Ckt | N | 2024 | B/C
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | RECLOSER | 2606 | 20241214 | 620 | 20241216 | 1329 | 2653353 | 3309 | Distribution Circuit | Vegetation | Tree - branch fell on line | 190 | 628710 | 36.577 | -121.9511 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0145115 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1997420 | 0 | EPSS Ckt | N | 2024 | A/B
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 8185 | 20241214 | 620 | 20241215 | 1933 | 2660624 | 2233 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 22330 | 36.6077 | -121.9403 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0146086 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1998429 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | JUMPER | WIRE DOWN 1 SP LD SIDE OF FUCO 8183 | 20241214 | 620 | 20241217 | 227 | 2662091 | 4087 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 183915 | 36.6074 | -121.9406 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146441 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | Yes | 1998802 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 2875 | 20241214 | 622 | 20241216 | 1658 | 2659107 | 3516 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 31644 | 36.4995 | -121.9313 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145697 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | No | 1998024 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 991420 | 20241214 | 623 | 20241215 | 2113 | 2661180 | 2075 | Distribution Circuit | Equipment Failure/Involved | Overhead | 131 | 289772 | 37.1548 | -122.1331 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146199 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | Yes | No | 1998549 | 0 | EPSS Ckt | N | 2024 | NONE
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRANSFORMER | 315237324260 | 20241214 | 623 | 20241216 | 1220 | 2662042 | 3237 | Transformer only | Vegetation | Tree - branch fell on line | 4 | 12948 | 37.1555 | -122.1327 | Yes | Overcast-Heavy Rain;32-90 F | Secondary | Broken- wire on ground | 24-0146423 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1998786 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9783 | 20241214 | 623 | 20241216 | 1706 | 2662051 | 3523 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 116259 | 37.1573 | -122.1336 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146426 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998788 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 2181 | 20241214 | 623 | 20241214 | 1931 | s1999625 | 788 | Distribution Circuit | Vegetation | Tree - branch fell on line | 84 | 66192 | 36.4895 | -121.9363 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0146988 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1999625 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | RECLOSER | 39126 | 20241214 | 624 | 20241214 | 841 | 2653469 | 137 | Distribution Circuit | Vegetation | Tree - branch fell on line | 300 | 41100 | 37.0778 | -122.1322 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0145126 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Three Phase Fault | 0 | No | No | No | 1997432 | 0 | EPSS Ckt | N | 2024 | ABC
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 12758 | 20241214 | 625 | 20241214 | 632 | 2653395 | 7 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 282 | 1974 | 37.1486 | -122.1745 | Yes | Overcast-Rain;32-90 F |  |  | 24-0145118 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1997422 | 0 | EPSS Ckt | N | 2024 | A-B
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | SWITCH | 11943 | 20241214 | 626 | 20241214 | 2152 | 2660682 | 926 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 79 | 73154 | 37.0112 | -122.0441 | Yes | Overcast-Fog-Heavy Rain;32-90 F |  |  | 24-0146104 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998448 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 7605 | 20241214 | 626 | 20241215 | 816 | 2654751 | 1550 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 23250 | 37.0866 | -122.0058 | Yes | Clear;32-90 F |  |  | 24-0146175 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998524 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9375 | 20241214 | 627 | 20241216 | 1935 | 2653839 | 3668 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 11004 | 37.1334 | -122.1377 | Yes | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0146479 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | No | 1998848 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5577 | 20241214 | 628 | 20241216 | 1601 | 2653383 | 3453 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 236870 | 37.0487 | -122.0616 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146355 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998726 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | RECLOSER | BL 1101 | 20241214 | 629 | 20241214 | 644 | 2653463 | 15 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 747 | 9825 | 37.0926 | -122.0966 | Yes | Overcast-Rain;32-90 F |  |  | 24-0145127 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1997433 | 0 | EPSS Ckt | N | 2024 | B-C
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | OCB | 1102/2 | 20241214 | 629 | 20241216 | 1651 | 2653666 | 3502 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2068 | 1142896 | 36.5569 | -121.8976 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0145143 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | No | 1997449 | 0 | EPSS Ckt | N | 2024 | B-C-GRD
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 1491 | 20241214 | 629 | 20241214 | 1750 | 2658690 | 681 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 27921 | 36.5057 | -121.9352 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145635 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1997960 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | TRANSFORMER | 411456345274 | 20241214 | 629 | 20241215 | 1836 | 2659696 | 2167 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 23837 | 36.5411 | -121.9101 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken | 24-0145798 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1998131 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 6033 | 20241214 | 630 | 20241215 | 1157 | 2653818 | 1767 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 111718 | 37.081 | -122.0049 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145316 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1997629 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 8021 | 20241214 | 631 | 20241215 | 1545 | 2653409 | 1994 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 169490 | 36.5868 | -121.9097 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146256 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998631 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 4349 | 20241214 | 632 | 20241214 | 1039 | 2653510 | 247 | Distribution Circuit | Vegetation | Tree - branch fell on line | 39 | 9633 | 36.9754 | -122.0325 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0145473 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997796 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SOLEDAD-2104 | 182052104 | RECLOSER | 413916 | 20241214 | 632 | 20241214 | 859 | 2653461 | 147 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 4704 | 36.4469 | -121.3318 | Yes | Clear;32-90 F |  |  | 24-0145125 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1997431 | 0 | EPSS Ckt | N | 2024 | B-C
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 5232 | 20241214 | 633 | 20241217 | 1256 | 2654202 | 4703 | Distribution Circuit | Vegetation | Tree - fell into line | 789 | 630832 | 37.0752 | -122.054 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145200 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | No | 1997508 | 0 | EPSS Ckt | N | 2024 | A-B
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315393819787 | 20241214 | 634 | 20241215 | 942 | 2658531 | 1628 | Transformer only | Vegetation | Tree - fell into line | 6 | 9768 | 37.0326 | -122.0793 | Yes | Overcast-Heavy Rain-Fog;32-90 F | Transformer | Broken | 24-0145600 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997924 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 10025 | 20241214 | 635 | 20241216 | 1421 | 2661251 | 3346 | Distribution Circuit | Vegetation | Tree - branch fell on line | 38 | 127148 | 37.1398 | -122.1525 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146217 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | No | 1998565 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 7289 | 20241214 | 635 | 20241216 | 1754 | 2661817 | 3559 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 32031 | 37.1711 | -122.1812 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146358 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998728 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 5457 | 20241214 | 635 | 20241216 | 1550 | 2662014 | 3435 | Distribution Circuit | Vegetation | Tree - bark fell into line | 19 | 65265 | 37.1376 | -122.1414 | Yes | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken | 24-0146410 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998773 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8833 | 20241214 | 635 | 20241216 | 1531 | 2654147 | 3416 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 113448 | 37.1203 | -121.9865 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146259 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998635 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2107 | 83622107 | RECLOSER | 11044 | 20241214 | 635 | 20241215 | 1559 | 2653521 | 1983 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2181 | 528436 | 37.0401 | -122.0297 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145134 | OH | Sus | 35605675 | SOUTH BAY AND CENTRAL COAST | DEC | Three Phase Fault | 0 | No | Yes | No | 1997440 | 0 | Non-EPSS | N | 2024 | ABC
CENTRAL COAST | COAST | CAMP EVERS-2107 | 83622107 | FUSE | 5215 | 20241214 | 635 | 20241215 | 1330 | 2658868 | 1855 | Distribution Circuit | Vegetation | Tree - branch fell on line | 60 | 77436 | 37.0325 | -122.0765 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145665 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | No | 1997990 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 2235 | 20241214 | 635 | 20241215 | 1545 | 2658960 | 1990 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 75620 | 36.5753 | -121.8741 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145679 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | Yes | No | 1998005 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 6743 | 20241214 | 635 | 20241216 | 1540 | 2659446 | 3425 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 44525 | 36.5711 | -121.8898 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145668 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998087 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | OCB | 2204/2 | 20241214 | 635 | 20241215 | 1405 | 2653859 | 1635 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7438 | 12382656 | 36.5786 | -121.9084 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0145184 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997491 | 0 | EPSS Ckt | N | 2024 | PH TOC
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 5945 | 20241214 | 636 | 20241214 | 835 | 2653519 | 119 | Distribution Circuit | Vegetation | Tree - bark fell into line | 223 | 26590 | 36.7919 | -121.7232 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0145253 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997563 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 633 | 20241214 | 636 | 20241215 | 1719 | 2660372 | 2083 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 45826 | 36.4177 | -121.9132 | Yes | Clear;32-90 F |  |  | 24-0146395 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998761 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | RECLOSER | 10290 | 20241214 | 636 | 20241214 | 2119 | 2653490 | 883 | Distribution Circuit | Vegetation | Tree - fell into line | 3177 | 1339660 | 36.977 | -122.0377 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0145153 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997459 | 0 | EPSS Ckt | N | 2024 | A GRD
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 93957 | 20241214 | 636 | 20241214 | 740 | 2653507 | 64 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 1216 | 36.9632 | -121.9987 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0145182 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1997489 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN SUB | 8284 | OCB | 96986 | 20241214 | 637 | 20241215 | 2119 | 2653600 | 2320 | Distribution Circuit | Vegetation | Tree - fell into line | 933 | 1967004 | 37.1719 | -122.1648 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145139 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1997445 | 0 | Non-EPSS | N | 2024 | INST OC TGT SGF- G
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 445933 | 20241214 | 638 | 20241215 | 1845 | 2653522 | 2167 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 121352 | 37.1372 | -122.1004 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken | 24-0145131 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997437 | 0 | EPSS Ckt | N | 2024 | A
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | RECLOSER | 12992 | 20241214 | 638 | 20241215 | 1859 | 2659839 | 2181 | Distribution Circuit | Vegetation | Tree - fell into line | 531 | 1158111 | 37.1991 | -122.1532 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145858 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | Yes | No | 1998193 | 0 | EPSS Ckt | N | 2024 | N/A
CENTRAL COAST | COAST | PAUL SWEET-2104 | 83252104 | RECLOSER | 5394 | 20241214 | 638 | 20241215 | 1333 | 2653603 | 1855 | Distribution Circuit | Vegetation | Tree - fell into line | 299 | 554645 | 36.9884 | -121.9697 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145225 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1997534 | 0 | EPSS Ckt | N | 2024 | B-GRD
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 64803 | 20241214 | 639 | 20241214 | 1539 | 2653639 | 540 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 1620 | 36.9963 | -122.0288 | Yes | Overcast-Fog-Heavy Rain;32-90 F |  |  | 24-0145871 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998205 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | FUSE | 12265 | 20241214 | 639 | 20241214 | 954 | 2653538 | 195 | Distribution Circuit | Equipment Failure/Involved | Overhead | 72 | 14040 | 36.9588 | -121.9805 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Together | 24-0145334 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1997648 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRANSFORMER | 100000035951 | 20241214 | 642 | 20241216 | 19 | 2653568 | 2497 | Transformer only | Vegetation | Tree - branch fell on line | 3 | 7491 | 37.1452 | -122.1325 | Yes | Overcast-Heavy Rain;32-90 F | Fuse | Normal | 24-0146366 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1998737 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 6085 | 20241214 | 644 | 20241215 | 1051 | 2653903 | 1687 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 18557 | 37.0636 | -122.0348 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145725 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | No | 1998054 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | OTHER | WIRE DOWN @ CGC 315654421255 | 20241214 | 645 | 20241215 | 1809 | 2653920 | 2124 | Distribution Circuit | Vegetation | Tree - branch fell on line | 136 | 250920 | 37.0744 | -121.9909 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145811 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Open Circuit | 0 | No | Yes | Yes | 1998144 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2103 | 83252103 | FUSE | 12651 | 20241214 | 645 | 20241214 | 945 | 2653642 | 180 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 3240 | 36.9825 | -122.0124 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0145384 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997704 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 12647 | 20241214 | 647 | 20241214 | 1300 | 2653690 | 373 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1119 | 37.0524 | -121.998 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0145705 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1998032 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | RECLOSER | 13620 | 20241214 | 647 | 20241215 | 1026 | 2661271 | 1659 | Distribution Circuit | Vegetation | Tree - fell into line | 150 | 248850 | 36.557 | -121.9037 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Together | 24-0146222 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1998572 | 0 | EPSS Ckt | N | 2024 | NONE
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | RECLOSER | 37088 | 20241214 | 649 | 20241215 | 1453 | 2654168 | 1924 | Distribution Circuit | Vegetation | Tree - fell into line | 1443 | 2776332 | 36.5465 | -121.8985 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0146028 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998367 | 0 | EPSS Ckt | N | 2024 | SGF
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | RECLOSER | 75304 | 20241214 | 649 | 20241215 | 1845 | 2660541 | 2136 | Distribution Circuit | Vegetation | Tree - fell into line | 920 | 1866965 | 36.5245 | -121.8121 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146054 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998392 | 0 | EPSS Ckt | N | 2024 | SGF
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 6167 | 20241214 | 649 | 20241215 | 1453 | 2661395 | 1924 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 34632 | 36.527 | -121.8164 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Fuse | Normal | 24-0146240 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1998612 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 10201 | 20241214 | 649 | 20241215 | 1453 | 2661397 | 1924 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 46176 | 36.5258 | -121.8159 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0146241 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1998613 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 38430 | 20241214 | 649 | 20241215 | 1845 | 2653777 | 568 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5412 | 3395525 | 36.9756 | -121.8885 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145174 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1997480 | 0 | EPSS Ckt | N | 2024 | C
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | OTHER | WIRE DOWN1 N/OF 7213 | 20241214 | 650 | 20241214 | 1715 | 2657781 | 625 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 40338 | 37.0332 | -121.9821 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145495 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | Yes | 1997818 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 2283 | 20241214 | 650 | 20241215 | 1151 | 2653741 | 1741 | Distribution Circuit | Vegetation | Tree - branch fell on line | 257 | 447437 | 36.5564 | -121.9087 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0146064 | OH | Sus | 35605803 | SOUTH BAY AND CENTRAL COAST | DEC | Multi-Fault | 0 | No | No | No | 1998401 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0422 | 182440422 | RECLOSER | 2608 | 20241214 | 650 | 20241216 | 2136 | 2653786 | 3766 | Distribution Circuit | Vegetation | Tree - fell into line | 301 | 1133566 | 36.5912 | -121.9465 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145224 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Three Phase Fault | 0 | No | Yes | No | 1997533 | 0 | EPSS Ckt | N | 2024 | ABC
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 2221 | 20241214 | 650 | 20241215 | 2016 | 2653812 | 2246 | Distribution Circuit | Vegetation | Tree - bark fell into line | 13 | 29198 | 36.5958 | -121.951 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146311 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998682 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | JUMPER | WIRE DOWN@ CGC#100000035948 | 20241214 | 651 | 20241216 | 1314 | 2661673 | 3261 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 41367 | 37.1475 | -122.1328 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146327 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | Yes | Yes | 1998696 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 5411 | 20241214 | 651 | 20241215 | 1055 | 2654322 | 1684 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 28628 | 37.0548 | -122.161 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0146257 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998632 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 8895 | 20241214 | 651 | 20241215 | 1950 | 2653745 | 2219 | Distribution Circuit | Vegetation | Tree - branch fell on line | 126 | 277974 | 36.5891 | -121.9104 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0146206 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Three Phase Fault | 0 | No | No | No | 1998555 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | JUMPER | UN-NUMBERED SB | 20241214 | 653 | 20241216 | 1540 | 2658909 | 3397 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 74734 | 36.5728 | -121.8875 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145668 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | Yes | No | 1997993 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 8183 | 20241214 | 653 | 20241214 | 1805 | 2654204 | 672 | Distribution Circuit | Vegetation | Tree - fell into line | 115 | 77280 | 36.9646 | -121.8903 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0145345 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1997660 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 82593 | 20241214 | 655 | 20241216 | 1910 | 2653796 | 3615 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 202440 | 36.5953 | -121.9416 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0146546 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998933 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | RECLOSER | 440 | 20241214 | 656 | 20241219 | 1232 | 2654173 | 7152 | Distribution Circuit | Vegetation | Tree - fell into line | 298 | 300965 | 36.4389 | -121.9203 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145240 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | No | 1997550 | 0 | EPSS Ckt | N | 2024 | C-GRD
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | TRANSFORMER | 411410645540 | 20241214 | 656 | 20241216 | 1415 | 2653823 | 3319 | Transformer only | Vegetation | Tree - branch fell on line | 22 | 73018 | 36.548 | -121.9259 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146313 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998684 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2102 | 182222102 | OCB | 2102/2 | 20241214 | 657 | 20241216 | 2011 | 2653911 | 3674 | Distribution Circuit | Vegetation | Tree - fell into line | 9445 | 4118478 | 36.5991 | -121.8542 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0145193 | OH | Sus | 35605803 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1997500 | 0 | EPSS Ckt | N | 2024 | PHASE INST OC
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 1371 | 20241214 | 657 | 20241215 | 953 | 2661234 | 1616 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 24 | 38784 | 36.5929 | -121.8704 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0146210 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998559 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | FUSE | 499 | 20241214 | 657 | 20241218 | 1420 | 2663358 | 6203 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 12406 | 36.3529 | -121.8822 | Yes | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0146695 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1999072 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 7015 | 20241214 | 657 | 20241216 | 1302 | 2653825 | 3245 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 29205 | 36.5556 | -121.9132 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146564 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998949 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | RECLOSER | 42226 | 20241214 | 658 | 20241215 | 1906 | 2653958 | 2168 | Distribution Circuit | Vegetation | Tree - fell into line | 429 | 595496 | 36.5834 | -121.8569 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145201 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1997509 | 0 | EPSS Ckt | N | 2024 | ABC GRD
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 10197 | 20241214 | 658 | 20241215 | 1520 | 2661742 | 1942 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5826 | 36.5291 | -121.8251 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Service conductor | Broken | 24-0146341 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1998712 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | RECLOSER | 617344 | 20241214 | 659 | 20241215 | 1918 | 2653964 | 2179 | Distribution Circuit | Vegetation | Tree - fell into line | 151 | 329029 | 36.5933 | -121.8713 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken | 24-0145207 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997515 | 0 | EPSS Ckt | N | 2024 | ABC GRD
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | FUSE | 1377 | 20241214 | 659 | 20241215 | 1113 | 2653857 | 1694 | Distribution Circuit | Vegetation | Tree - branch fell on line | 111 | 188034 | 36.5965 | -121.8589 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145908 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | No | 1998239 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2106 | 182402106 | FUSE | 40137 | 20241214 | 659 | 20241215 | 1833 | 2654203 | 2134 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 99 | 211266 | 36.6345 | -121.8108 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0146405 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1998768 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-1101 | 182221101 | FUSE | 9333 | 20241214 | 700 | 20241216 | 1415 | 2653890 | 3315 | Distribution Circuit | Vegetation | Tree - fell into line | 173 | 199975 | 36.6161 | -121.8249 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0146048 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998387 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | FUSE | 9223 | 20241214 | 700 | 20241216 | 1758 | 2655415 | 3538 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 3538 | 36.5852 | -121.8468 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146638 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | No | 1999019 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | RECLOSER | 399900 | 20241214 | 700 | 20241216 | 1549 | 2653932 | 3409 | Distribution Circuit | Vegetation | Tree - branch fell on line | 340 | 1159060 | 36.5403 | -121.8762 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145154 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Multi-Fault | 0 | No | Yes | No | 1997460 | 0 | EPSS Ckt | N | 2024 | ABC-GRD
CENTRAL COAST | MONTEREY | FORT ORD-2105 | 182402105 | RECLOSER | 31972 | 20241214 | 701 | 20241215 | 1143 | 2654015 | 1722 | Distribution Circuit | Vegetation | Tree - branch fell on line | 954 | 1020118 | 36.6437 | -121.81 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145171 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1997477 | 0 | EPSS Ckt | N | 2024 | B-C
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | OCB | 1101/2 | 20241214 | 702 | 20241215 | 1608 | 2654053 | 1986 | Distribution Circuit | Vegetation | Tree - fell into line | 4452 | 8841672 | 36.6434 | -121.792 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145161 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1997466 | 0 | EPSS Ckt | N | 2024 | B-C GRD
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | TRANSFORMER | 411793850387 | 20241214 | 702 | 20241215 | 1849 | 2661677 | 2147 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 10735 | 36.6845 | -121.7999 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Transformer (OH) | Broken | 24-0146332 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998701 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2106 | 182402106 | FUSE | 40391 | 20241214 | 702 | 20241216 | 1222 | 2654039 | 3200 | Distribution Circuit | Vegetation | Tree - grew into line | 91 | 291200 | 36.6277 | -121.8138 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0146399 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1998763 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2107 | 182402107 | OCB | 2107/2/NORM | 20241214 | 702 | 20241215 | 1654 | 2653982 | 2032 | Distribution Circuit | Vegetation | Tree - fell into line | 4045 | 8175848 | 36.6433 | -121.7918 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145165 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | No | 1997470 | 0 | EPSS Ckt | N | 2024 | B-C
CENTRAL COAST | MONTEREY | FORT ORD-2106 | 182402106 | FUSE | 9739 | 20241214 | 705 | 20241215 | 2029 | 2654058 | 2244 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 81 | 181764 | 36.6303 | -121.8117 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0146403 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1998767 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 4811 | 20241214 | 705 | 20241214 | 1846 | 2654049 | 701 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 7711 | 36.959 | -121.735 | Yes | Overcast-Heavy Rain;32-90 F |  |  | 24-0146009 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998348 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 9609 | 20241214 | 705 | 20241214 | 745 | 2654046 | 40 | Distribution Circuit | Vegetation | Tree - bark fell into line | 34 | 1360 | 36.8938 | -121.3538 | Yes | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0145209 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997517 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | RECLOSER | 70782 | 20241214 | 706 | 20241214 | 1142 | 2654184 | 276 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 175 | 48300 | 36.7798 | -121.7788 | Yes | Overcast-Fog-Strong Winds;32-90 F |  |  | 24-0145162 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1997467 | 0 | Non-EPSS | N | 2024 | B-C
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | JUMPER | BLOWN JPR AT 7821 | 20241214 | 706 | 20241215 | 1336 | 2659860 | 1830 | Distribution Circuit | Equipment Failure/Involved | Overhead | 928 | 1134708 | 36.6001 | -121.8596 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0145864 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | Yes | 1998198 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | RECLOSER | 99672 | 20241214 | 709 | 20241216 | 29 | 2654888 | 2480 | Distribution Circuit | Equipment Failure/Involved | Overhead | 97 | 203814 | 36.7642 | -121.7605 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | On Ground | 24-0145257 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997567 | 0 | Non-EPSS | N | 2024 | B C GRD
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 4819 | 20241214 | 709 | 20241216 | 349 | 2661630 | 2680 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 2680 | 36.737 | -121.7736 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Transformer (OH) | Failed/Faulted | 24-0146314 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998685 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1112 | 182371112 | RECLOSER | 438 | 20241214 | 709 | 20241215 | 1530 | 2654253 | 1941 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 213 | 221241 | 36.4967 | -121.7313 | Yes | Clear;32-90 F |  |  | 24-0145189 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1997496 | 0 | EPSS Ckt | N | 2024 | AB
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | SWITCH | 5959 | 20241214 | 709 | 20241214 | 1353 | 2655031 | 404 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 3232 | 37.0259 | -121.9324 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0145265 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997575 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 7013 | 20241214 | 710 | 20241216 | 1102 | 2656411 | 3087 | Distribution Circuit | Vegetation | Tree - branch fell on line | 92 | 191692 | 36.555 | -121.9168 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146408 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998771 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | FUSE | 20155 | 20241214 | 712 | 20241215 | 1900 | 2654182 | 2148 | Distribution Circuit | Vegetation | Tree - fell into line | 140 | 300720 | 36.6081 | -121.6933 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0145847 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998181 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | OTHER | WIRE DOWN @ 4233 | 20241214 | 713 | 20241218 | 359 | 2654176 | 5479 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6248 | 1444579 | 36.991 | -121.8407 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145318 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | Yes | 1997631 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | RECLOSER | 2002 | 20241214 | 714 | 20241216 | 1211 | 2654873 | 3177 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 118 | 374886 | 36.2248 | -121.7587 | Yes | Overcast-Rain;32-90 F |  |  | 24-0145248 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1997558 | 0 | EPSS Ckt | N | 2024 | B C
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6911 | 20241214 | 715 | 20241215 | 1559 | 2654272 | 1964 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 192472 | 37.0171 | -121.7217 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Bent or Twisted | 24-0145823 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998156 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | INDUSTRIAL ACRES-0412 | 182300412 | TRANSFORMER | 412318049581 | 20241214 | 715 | 20241214 | 2000 | 2654304 | 765 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 7650 | 36.6662 | -121.621 | Yes | Overcast-Heavy Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0145598 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997922 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | FUSE | 396083 | 20241214 | 715 | 20241217 | 1358 | 2662915 | 4723 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 108629 | 36.2398 | -121.7734 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146574 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998957 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 7759 | 20241214 | 716 | 20241216 | 1750 | 2654237 | 3514 | Distribution Circuit | Vegetation | Tree - grew into line | 18 | 63252 | 36.5479 | -121.9205 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0146359 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998730 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 705 | 20241214 | 718 | 20241215 | 1325 | 2654268 | 1807 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 7228 | 37.0523 | -122.1381 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0146320 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Open Circuit | 0 | No | No | No | 1998691 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | RECLOSER | 63868 | 20241214 | 720 | 20241216 | 1204 | 2653750 | 3164 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 274 | 866936 | 36.264 | -121.7952 | Yes | Overcast-Rain;32-90 F |  |  | 24-0145227 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1997536 | 0 | EPSS Ckt | N | 2024 | A C
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | RECLOSER | 586340 | 20241214 | 725 | 20241214 | 1126 | 2654388 | 241 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 218 | 52538 | 36.5537 | -121.694 | Yes | Clear;32-90 F |  |  | 24-0145220 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1997529 | 0 | EPSS Ckt | N | 2024 | A C TIME
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 2323 | 20241214 | 727 | 20241215 | 1624 | 2654374 | 1977 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 45021 | 36.5822 | -121.9214 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145429 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1997751 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | RECLOSER | 2020 | 20241214 | 730 | 20241216 | 1114 | 2654634 | 3104 | Distribution Circuit | Vegetation | Tree - fell into line | 839 | 1449247 | 36.4632 | -121.7119 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145213 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1997522 | 0 | EPSS Ckt | N | 2024 | SGF
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | OTHER | WIRE DOWN 1 LD SIDE OF 3032 | 20241214 | 733 | 20241216 | 1443 | 2655182 | 3310 | Distribution Circuit | Equipment Failure/Involved | Overhead | 109 | 294284 | 36.6343 | -121.6991 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145283 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | Yes | 1997593 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DEL MONTE-2104 | 182222104 | FUSE | 5919 | 20241214 | 735 | 20241215 | 808 | 2654587 | 1465 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 46880 | 36.5295 | -121.7008 | Yes | Clear;32-90 F |  |  | 24-0146182 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998530 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | OTHER | HOT WIRE DOWN AT CGC 411400645315 | 20241214 | 735 | 20241216 | 1419 | 2654470 | 3284 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 52544 | 36.542 | -121.929 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146450 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Open Circuit | 0 | No | Yes | No | 1998812 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | TRANSFORMER | 315183020717 | 20241214 | 739 | 20241216 | 1010 | 2661839 | 3031 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 6062 | 37.0573 | -122.152 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken | 24-0146362 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998733 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | FUSE | 7869 | 20241214 | 744 | 20241215 | 1913 | 2654593 | 2129 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 113 | 239627 | 36.5511 | -121.9198 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0146436 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998797 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | TRANSFORMER | 411418546800 | 20241214 | 750 | 20241216 | 1849 | 2654651 | 3539 | Transformer only | Vegetation | Tree - branch fell on line | 4 | 14156 | 36.5826 | -121.9248 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0146505 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998878 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1112 | 182371112 | FUSE | 10235 | 20241214 | 757 | 20241215 | 953 | 2654702 | 1556 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 14004 | 36.5187 | -121.7894 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0146208 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998557 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 6165 | 20241214 | 810 | 20241215 | 1453 | 2661340 | 1843 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 18430 | 36.528 | -121.8179 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Fuse | Normal | 24-0146229 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1998590 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 8171 | 20241214 | 810 | 20241215 | 1453 | 2661413 | 1843 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 3686 | 36.5445 | -121.8848 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0146248 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1998622 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | JUMPER | OJ 3 S/OF 6159 | 20241214 | 810 | 20241215 | 1453 | 2661472 | 1843 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 33174 | 36.5317 | -121.8443 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146271 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | Yes | Yes | 1998646 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 7265 | 20241214 | 810 | 20241216 | 1711 | 2661693 | 3421 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 27565 | 36.5289 | -121.8443 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Transformer (UG) | Leaking | 24-0146333 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1998703 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315745221792 | 20241214 | 812 | 20241216 | 1225 | 2654830 | 3133 | Transformer only | Vegetation | Tree - bark fell into line | 1 | 3133 | 37.088 | -121.9612 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146297 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998670 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | RECLOSER | 9496 | 20241214 | 814 | 20241215 | 1549 | 2656515 | 1895 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 268 | 489303 | 36.5583 | -121.7508 | Yes | Clear;32-90 F |  |  | 24-0146146 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998495 | 0 | EPSS Ckt | N | 2024 | C-GRD
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 635 | 20241214 | 819 | 20241217 | 955 | 2663997 | 4416 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 17664 | 36.4188 | -121.9127 | Yes | Clear;32-90 F |  |  | 24-0146763 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999213 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 9005 | 20241214 | 820 | 20241215 | 1715 | 2661444 | 1975 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 41475 | 37.0318 | -122.1369 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146262 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | No | 1998638 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5503 | 20241214 | 823 | 20241215 | 1600 | 2655075 | 1897 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 73983 | 37.1461 | -122.1291 | Yes | Overcast-Heavy Rain;32-90 F |  |  | 24-0146372 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998742 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 2191 | 20241214 | 824 | 20241214 | 1819 | 2655138 | 595 | Distribution Circuit | Vegetation | Tree - branch fell on line | 56 | 33320 | 37.0515 | -122.0216 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Together | 24-0145970 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998308 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | RECLOSER | 5004 | 20241214 | 826 | 20241215 | 1424 | 2655232 | 1798 | Distribution Circuit | Equipment Failure/Involved | Overhead | 59 | 94119 | 36.7504 | -121.7422 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken | 24-0145371 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Multi-Fault | 0 | No | No | No | 1997688 | 0 | EPSS Ckt | N | 2024 | A-C-GRD
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 6897 | 20241214 | 828 | 20241214 | 1947 | 2655190 | 679 | Distribution Circuit | Equipment Failure/Involved | Overhead | 65 | 14336 | 36.8561 | -121.7958 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145500 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Multi-Fault | 0 | No | Yes | No | 1997823 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 9709 | 20241214 | 829 | 20241215 | 1843 | 2655135 | 2054 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 30810 | 37.1163 | -122.1184 | Yes | Overcast-Heavy Rain;32-90 F |  |  | 24-0146447 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998809 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 9337 | 20241214 | 830 | 20241215 | 1658 | 2658986 | 1948 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 89608 | 36.9399 | -121.8573 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken | 24-0145683 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998010 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 11477 | 20241214 | 831 | 20241215 | 1122 | 2659200 | 1611 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1611 | 36.8867 | -121.7466 | Yes | Overcast-Rain-Strong Winds;32-90 F | Insulator | Broken | 24-0145726 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1998056 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 12401 | 20241214 | 833 | 20241214 | 1623 | 2658852 | 470 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 36 | 16747 | 36.9726 | -121.765 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0145917 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998248 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2109 | 83252109 | FUSE | 3623 | 20241214 | 833 | 20241214 | 1216 | 2655367 | 223 | Distribution Circuit | Vegetation | Tree - branch fell on line | 106 | 23638 | 36.9882 | -121.9377 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0145628 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997953 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1104 | 182381104 | OCB | 1104/2 | 20241214 | 834 | 20241217 | 1453 | 2655379 | 4699 | Distribution Circuit | Equipment Failure/Involved | Overhead | 260 | 288986 | 36.8001 | -121.7691 | Yes | Overcast-Fog-Strong Winds;32-90 F | Crossarm- Wood | Broken | 24-0145293 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1997606 | 0 | Non-EPSS | N | 2024 | A C INST
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | RECLOSER | 2101/2 | 20241214 | 834 | 20241215 | 1132 | 2655414 | 1618 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3153 | 1662722 | 36.9032 | -121.7565 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Together | 24-0145717 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998046 | 0 | EPSS Ckt | N | 2024 | B & C
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | OTHER | WIRE DOWN @ CGC# 315926217352 | 20241214 | 836 | 20241215 | 1552 | 2661084 | 1876 | Distribution Circuit | Vegetation | Tree - fell into line | 305 | 21241 | 36.9679 | -121.8956 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146178 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Open Circuit | 0 | No | Yes | Yes | 1998527 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 6787 | 20241214 | 837 | 20241215 | 1851 | 2655394 | 2054 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 41080 | 36.929 | -121.7066 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146149 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998498 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | RECLOSER | 12656 | 20241214 | 838 | 20241214 | 1958 | 2656183 | 680 | Distribution Circuit | Vegetation | Tree - fell into line | 1170 | 277748 | 36.9118 | -121.7973 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145427 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1997749 | 0 | EPSS Ckt | N | 2024 | A/GRD
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 6713 | 20241214 | 838 | 20241215 | 1732 | 2658553 | 1974 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 39606 | 36.8964 | -121.8374 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145699 | OH | Sus | 35605675 | SOUTH BAY AND CENTRAL COAST | DEC | Multi-Fault | 0 | No | Yes | No | 1998026 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 7895 | 20241214 | 839 | 20241215 | 1356 | 2655416 | 1757 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 41 | 72037 | 36.9158 | -121.7501 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F |  |  | 24-0146331 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998700 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 8455 | 20241214 | 840 | 20241215 | 1810 | 2655453 | 2010 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 54270 | 37.1316 | -122.1098 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0146422 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998785 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | OCB | 2104/2 | 20241214 | 841 | 20241215 | 227 | 2659487 | 1066 | Distribution Circuit | 3rd Party | Other | 3012 | 1924260 | 37.0417 | -122.0256 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken | 24-0145830 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998163 | 0 | EPSS Ckt | N | 2024 | TRIP TGT
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 41677 | 20241214 | 842 | 20241214 | 1120 | 2655501 | 158 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 2054 | 36.711 | -121.6997 | Yes | Clear;32-90 F |  |  | 24-0145460 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1997781 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 6875 | 20241214 | 843 | 20241216 | 1748 | 2655537 | 3425 | Distribution Circuit | Vegetation | Tree - fell into line | 103 | 202121 | 36.8864 | -121.6325 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145733 | OH | Sus | 35605675 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998063 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 236923 | 20241214 | 844 | 20241215 | 1849 | 2661072 | 2045 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 44961 | 36.9929 | -121.7354 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146195 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | No | 1998544 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS COCHES-1102 | 182151102 | FUSE | 8505 | 20241214 | 845 | 20241214 | 1350 | 2655615 | 305 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 4575 | 36.3756 | -121.2578 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0145556 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1997877 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 8983 | 20241214 | 845 | 20241215 | 1100 | 2658058 | 1575 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 42525 | 37.0307 | -122.1429 | Yes | Overcast-Heavy Rain;32-90 F |  |  | 24-0146265 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998640 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | RECLOSER | 22428 | 20241214 | 846 | 20241214 | 1914 | 2655633 | 628 | Distribution Circuit | Equipment Failure/Involved | Overhead | 312 | 114408 | 36.7339 | -121.6791 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145514 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1997838 | 0 | EPSS Ckt | N | 2024 | B-GRD
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 3823 | 20241214 | 848 | 20241215 | 1853 | 2655635 | 2045 | Distribution Circuit | Vegetation | Tree - branch fell on line | 73 | 147177 | 36.9729 | -121.7266 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0146287 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998662 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | RECLOSER | 69466 | 20241214 | 849 | 20241215 | 1918 | 2656193 | 2069 | Distribution Circuit | Vegetation | Tree - branch fell on line | 240 | 216037 | 36.8266 | -121.7254 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145805 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | No | 1998138 | 0 | EPSS Ckt | N | 2024 | BC
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | OTHER | WIRE DOWN @ CGC 412111554654 | 20241214 | 850 | 20241214 | 1105 | 2655704 | 135 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 3582 | 36.8044 | -121.6966 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145447 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1997769 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | FUSE | 50975 | 20241214 | 854 | 20241214 | 1107 | 2655852 | 133 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 43 | 5719 | 36.8448 | -121.4566 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F |  |  | 24-0145513 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1997837 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 690651 | 20241214 | 855 | 20241215 | 1831 | 2655899 | 2016 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 18126 | 36.8457 | -121.6356 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146057 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998395 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | FUSE | 994287 | 20241214 | 856 | 20241214 | 1623 | 2659032 | 447 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 12516 | 36.8402 | -121.463 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F |  |  | 24-0145924 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998256 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 9087 | 20241214 | 900 | 20241214 | 1335 | 2656259 | 275 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 7975 | 36.9776 | -122.0425 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken | 24-0145352 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1997667 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 8605 | 20241214 | 901 | 20241214 | 1828 | 2656025 | 567 | Distribution Circuit | Vegetation | Tree - branch fell on line | 243 | 137781 | 36.9612 | -121.888 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145666 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1997991 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | FUSE | 50381 | 20241214 | 902 | 20241214 | 1655 | 2656862 | 473 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 4730 | 37.0625 | -121.2281 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F |  |  | 24-0145961 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998295 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 6701 | 20241214 | 907 | 20241215 | 1445 | 2657823 | 1778 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5334 | 36.8754 | -121.7577 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145503 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | No | 1997826 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRANSFORMER | 100000034971 | 20241214 | 912 | 20241215 | 1909 | 2661944 | 2037 | Transformer only | Vegetation | Tree - fell into line | 2 | 4074 | 37.1484 | -122.1355 | Yes | Overcast-Rain;32-90 F | Transformer (OH) | Broken | 24-0146390 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998758 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | TRIP-SAVER | 5401 | 20241214 | 912 | 20241216 | 1632 | 2656237 | 3320 | Distribution Circuit | Equipment Failure/Involved | Overhead | 69 | 207832 | 37.0647 | -122.1232 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146409 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998772 | 0 | EPSS Ckt | N | 2024 | NONE
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | RECLOSER | 83518 | 20241214 | 912 | 20241214 | 1321 | 2656918 | 249 | Distribution Circuit | Vegetation | Tree - branch fell on line | 174 | 43326 | 36.8183 | -121.3881 | Yes | Overcast;32-90 F | Conductor- Overhead | Together | 24-0145413 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Three Phase Fault | 0 | No | No | No | 1997735 | 0 | EPSS Ckt | N | 2024 | A B C
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | FUSE | 9193 | 20241214 | 920 | 20241214 | 2209 | 2656349 | 769 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 2307 | 35.9664 | -121.1324 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0146081 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998424 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 5941 | 20241214 | 922 | 20241215 | 1432 | 2656379 | 1750 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 14818 | 36.8016 | -121.7217 | Yes | Overcast-Fog-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145649 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1997973 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 4689 | 20241214 | 922 | 20241214 | 1120 | 2656468 | 118 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 944 | 36.9742 | -121.9857 | Yes | Overcast-Fog-Rain;32-90 F |  |  | 24-0145553 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997874 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | RECLOSER | 115450 | 20241214 | 930 | 20241214 | 1555 | 2656529 | 385 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 31 | 11935 | 36.3373 | -121.252 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0145898 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998229 | 0 | Non-EPSS | N | 2024 | B C TIME
CENTRAL COAST | COAST | PAUL SWEET-2105 | 83252105 | FUSE | 10501 | 20241214 | 939 | 20241214 | 1134 | 2656733 | 115 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 51 | 5865 | 36.9734 | -122.0347 | Yes | Overcast-Fog-Rain;32-90 F |  |  | 24-0145569 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997891 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | SWITCH | 50853 | 20241214 | 944 | 20241214 | 1321 | 2656989 | 217 | Distribution Circuit | Equipment Failure/Involved | Underground | 4149 | 845081 | 36.8451 | -121.4013 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Elbow | Burned/flashed | 24-0145420 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997742 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | RECLOSER | 4040 | 20241214 | 945 | 20241214 | 1453 | 2656770 | 308 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 40 | 12320 | 36.7535 | -121.2907 | Yes | Overcast;32-90 F |  |  | 24-0145826 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998159 | 0 | EPSS Ckt | N | 2024 | B C
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | RECLOSER | 7086 | 20241214 | 957 | 20241214 | 1433 | 2657002 | 276 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 128 | 35328 | 36.2942 | -121.1997 | Yes | Overcast-Rain;32-90 F |  |  | 24-0145722 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998051 | 0 | EPSS Ckt | N | 2024 | AB
CENTRAL COAST | MONTEREY | DEL MONTE-1101 | 182221101 | TRANSFORMER | 411680948034 | 20241214 | 1000 | 20241215 | 1811 | 2657000 | 1931 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 25103 | 36.6195 | -121.8363 | Yes | Overcast-Rain-Strong Winds;32-90 F | Secondary | Broken | 24-0146004 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998343 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 7873 | 20241214 | 1007 | 20241216 | 1457 | 2657072 | 3170 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 96955 | 36.5773 | -121.9451 | Yes | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 24-0146508 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | No | 1998882 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | FUSE | 24743 | 20241214 | 1011 | 20241214 | 1255 | 2657765 | 164 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 164 | 36.8345 | -121.6575 | Yes | Partly Cloudy;32-90 F |  |  | 24-0145662 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1997987 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2201 | 182852201 | FUSE | 7879 | 20241214 | 1011 | 20241216 | 1148 | 2657119 | 2977 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 47632 | 36.5783 | -121.9441 | Yes | Partly Cloudy-Fog;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0146528 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998907 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | TRANSFORMER | 316354015501 | 20241214 | 1020 | 20241216 | 1353 | 2661771 | 3093 | Transformer only | Unknown Cause | Patrol - not conducted | 14 | 43302 | 36.919 | -121.7483 | Yes | Rain-Overcast-Fog;32-90 F |  |  | 24-0146349 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1998721 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRIP-SAVER | 9031 | 20241214 | 1028 | 20241215 | 1338 | 2657606 | 1630 | Distribution Circuit | Vegetation | Tree - branch fell on line | 47 | 76610 | 37.0726 | -122.0742 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0146315 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998686 | 0 | EPSS Ckt | N | 2024 | OPEN
CENTRAL COAST | COAST | CAMP EVERS-2103 | 83622103 | FUSE | 2810 | 20241214 | 1031 | 20241214 | 1355 | 2657658 | 204 | Distribution Circuit | Vegetation | Tree - fell into line | 204 | 41616 | 37.0408 | -122.0237 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0145745 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998077 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 2667 | 20241214 | 1031 | 20241216 | 1325 | 2657603 | 3054 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 18324 | 37.0258 | -121.7751 | Yes | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 24-0146427 | OH | Sus | 35605675 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998789 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5475 | 20241214 | 1034 | 20241215 | 1732 | 2657732 | 1856 | Distribution Circuit | Vegetation | Tree - grew into line | 18 | 33408 | 37.1284 | -122.1174 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0146407 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998770 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | FUSE | 869103 | 20241214 | 1040 | 20241215 | 1145 | 2657745 | 1505 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 15050 | 36.8211 | -121.7285 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145660 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1997984 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | FUSE | 3591 | 20241214 | 1051 | 20241214 | 1515 | 2657916 | 264 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 166 | 43824 | 36.5626 | -121.7327 | Yes | Clear;32-90 F |  |  | 24-0146039 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998378 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | FUSE | 9977 | 20241214 | 1052 | 20241215 | 1005 | 2657945 | 1393 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 28803 | 36.7755 | -121.4753 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0146237 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998608 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 9101 | 20241214 | 1053 | 20241215 | 1819 | 2660763 | 1886 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 182942 | 36.42 | -121.7812 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146117 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | No | 1998463 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 8097 | 20241214 | 1115 | 20241215 | 1215 | 2658174 | 1500 | Distribution Circuit | Vegetation | Tree - bark fell into line | 17 | 25500 | 37.0785 | -122.139 | Yes | Partly Cloudy-Drizzle;32-90 F | Transformer (OH) | Normal | 24-0146293 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998666 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2107 | 182492107 | JUMPER | JMPRS 1 SS OF 50743 | 20241214 | 1119 | 20241215 | 1551 | 2656329 | 1712 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3424 | 36.9333 | -121.3841 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0145767 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998100 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | LOS COCHES-1101 | 182151101 | RECLOSER | 625902 | 20241214 | 1128 | 20241214 | 1843 | 2658337 | 435 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 7830 | 36.3482 | -121.3219 | Yes | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145865 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Multi-Fault | 0 | No | Yes | No | 1998199 | 0 | EPSS Ckt | N | 2024 | B- C- GRD- DCD
CENTRAL COAST | MONTEREY | DEL MONTE-2105 | 182222105 | TRANSFORMER | 411599347226 | 20241214 | 1135 | 20241217 | 1313 | 2662197 | 4418 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 8836 | 36.5962 | -121.8636 | Yes | Strong Winds-Rain-Overcast;32-90 F | Transformer | Burned Open | 24-0146463 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998828 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1102 | 182201102 | RECLOSER | 321000 | 20241214 | 1139 | 20241216 | 1554 | 2658496 | 3135 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 37620 | 36.6105 | -121.4925 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0146144 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Multi-Fault | 0 | No | Yes | No | 1998493 | 0 | EPSS Ckt | N | 2024 | ABC
CENTRAL COAST | COAST | BURNS-2101 | 183582101 | FUSE | 2335 | 20241214 | 1208 | 20241215 | 1715 | 2659148 | 1747 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 1747 | 37.0737 | -122.1297 | Yes | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0146388 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998756 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | RECLOSER | 3060 | 20241214 | 1208 | 20241215 | 1926 | 2658966 | 1878 | Distribution Circuit | Equipment Failure/Involved | Overhead | 238 | 446964 | 36.7624 | -121.7341 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 24-0146140 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998489 | 0 | Non-EPSS | N | 2024 | B & C
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | FUSE | 94397 | 20241214 | 1211 | 20241215 | 1311 | 2656519 | 1500 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 40500 | 36.9823 | -121.9791 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 24-0146283 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1998659 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 4407 | 20241214 | 1215 | 20241214 | 1426 | 2658749 | 131 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 36 | 4668 | 36.9026 | -121.3627 | Yes | Strong Winds-Heavy Rain |  |  | 24-0145810 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998143 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 11633 | 20241214 | 1305 | 20241214 | 1818 | 2659209 | 313 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 4695 | 36.9658 | -121.8819 | Yes | Overcast-Drizzle;32-90 F |  |  | 24-0146027 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998366 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1105 | 182201105 | RECLOSER | 345828 | 20241214 | 1306 | 20241216 | 835 | 2655727 | 2609 | Distribution Circuit | Equipment Failure/Involved | Overhead | 93 | 241557 | 36.6446 | -121.5758 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0145719 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1998048 | 0 | Non-EPSS | N | 2024 | N/A
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 11935 | 20241214 | 1314 | 20241215 | 1119 | 2659215 | 1325 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 6625 | 37.0559 | -121.9625 | Yes | Overcast-Drizzle;32-90 F |  |  | 24-0146247 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998621 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRIP-SAVER | 9773 | 20241214 | 1331 | 20241216 | 1750 | 2659435 | 3139 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 58026 | 37.1289 | -122.1142 | Yes | Partly Cloudy-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 24-0146412 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998775 | 0 | EPSS Ckt | N | 2024 | TRIP
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 9963 | 20241214 | 1332 | 20241215 | 1155 | 2659387 | 1343 | Distribution Circuit | Vegetation | Tree - bark fell into line | 18 | 24174 | 36.9736 | -121.8067 | Yes | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0146272 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998647 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRIP-SAVER | 9973 | 20241214 | 1335 | 20241215 | 1459 | 2659437 | 1524 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 10668 | 37.025 | -121.8205 | Yes | Overcast-Drizzle;32-90 F |  |  | 24-0146346 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998717 | 0 | EPSS Ckt | N | 2024 | NA
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 9569 | 20241214 | 1354 | 20241215 | 910 | 2659693 | 1156 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 41 | 47396 | 36.9783 | -121.8269 | Yes | Partly Cloudy-Drizzle;32-90 F |  |  | 24-0146191 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998540 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5219 | 20241214 | 1403 | 20241215 | 1202 | 2659617 | 1319 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 16026 | 37.0371 | -122.066 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146136 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998485 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6543 | 20241214 | 1406 | 20241215 | 436 | 2659629 | 870 | Distribution Circuit | Vegetation | Tree - bark fell into line | 26 | 22620 | 36.9267 | -121.8459 | Yes | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0146152 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998503 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | OTHER | WIRE DOWN @ CGC 315422019956 | 20241214 | 1422 | 20241215 | 1241 | 2659699 | 1339 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 2678 | 37.0367 | -122.0692 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146123 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998469 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | RECLOSER | 9106 | 20241214 | 1426 | 20241215 | 1906 | 2660308 | 1720 | Distribution Circuit | Vegetation | Tree - fell into line | 568 | 976960 | 36.5917 | -121.8675 | Yes | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145977 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | Yes | No | 1998316 | 0 | EPSS Ckt | N | 2024 | A B
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | RECLOSER | 2648 | 20241214 | 1501 | 20241214 | 2349 | 2660750 | 528 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 769 | 406032 | 36.6181 | -121.8423 | Yes | Partly Cloudy-Rain;32-90 F |  |  | 24-0146131 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Multi-Fault | 0 | No | No | No | 1998480 | 0 | EPSS Ckt | N | 2024 | ABC GRD
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | JUMPER | WIRE DOWN 1 SPAN N/OF 40465 | 20241214 | 1524 | 20241215 | 1534 | 2660005 | 1427 | Distribution Circuit | Vegetation | Tree - fell into line | 331 | 294224 | 36.5371 | -121.9127 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145900 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Open Circuit | 0 | No | Yes | No | 1998231 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | RECLOSER | 2070 | 20241214 | 1527 | 20241216 | 1429 | 2659932 | 2822 | Distribution Circuit | Vegetation | Tree - branch fell on line | 444 | 169785 | 36.5447 | -121.9082 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145968 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998306 | 0 | EPSS Ckt | N | 2024 | A/SGF
CENTRAL COAST | MONTEREY | DEL MONTE-2102 | 182222102 | TRANSFORMER | 411665047502 | 20241214 | 1538 | 20241215 | 1630 | 2661822 | 1492 | Transformer only | Vegetation | Tree - branch fell on line | 13 | 19396 | 36.6039 | -121.8414 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0146360 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1998731 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | FUSE | 3971 | 20241214 | 1657 | 20241215 | 615 | 2660207 | 798 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 79 | 63042 | 36.5948 | -121.7026 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0146159 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998511 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 2989 | 20241214 | 1659 | 20241216 | 1553 | 2661353 | 2814 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 8442 | 37.1639 | -122.0767 | Yes | Overcast;32-90 F |  |  | 24-0146460 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998825 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | FUSE | 4211 | 20241214 | 1717 | 20241214 | 1757 | 2660263 | 38 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 1178 | 36.9688 | -121.4325 | Yes | Partly Cloudy;32-90 F |  |  | 24-0145998 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998339 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | SAN BENITO-2101 | 182742101 | FUSE | 994287 | 20241214 | 1718 | 20241214 | 1915 | 2660264 | 117 | Distribution Circuit | Company Initiated | Personnel- company | 12 | 1364 | 36.8402 | -121.463 | Yes | Partly Cloudy;32-90 F | Fuse | Normal | 24-0146046 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Open Circuit | 0 | No | No | No | 1998386 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5599 | 20241214 | 1724 | 20241216 | 1612 | 2660330 | 2808 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 41816 | 37.0796 | -122.0513 | Yes | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146421 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998784 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 3427 | 20241214 | 1731 | 20241215 | 1318 | 2660294 | 1187 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 85 | 100895 | 36.853 | -121.7084 | Yes | Partly Cloudy;32-90 F |  |  | 24-0146312 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998683 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2104 | 83622104 | FUSE | 3279 | 20241214 | 1801 | 20241215 | 1433 | 2660402 | 1232 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 27104 | 37.0434 | -121.9977 | Yes | Overcast;32-90 F |  |  | 24-0146347 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998719 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 5621 | 20241214 | 1826 | 20241215 | 251 | 2660405 | 505 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 45 | 22725 | 37.1016 | -122.0524 | Yes | Overcast;32-90 F |  |  | 24-0146139 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998488 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 6161 | 20241214 | 1828 | 20241216 | 1135 | 2660553 | 2467 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 56741 | 37.1187 | -122.0198 | Yes | Overcast;32-90 F | Conductor- Overhead | Broken | 24-0146063 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998400 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2104 | 83192104 | FUSE | 6491 | 20241214 | 1843 | 20241215 | 1111 | 2661103 | 988 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 7238 | 36.9325 | -121.7436 | Yes | Clear;32-90 F |  |  | 24-0146249 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998623 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | FUSE | 2271 | 20241214 | 1941 | 20241215 | 1804 | 2660536 | 1343 | Distribution Circuit | Vegetation | Tree - branch fell on line | 68 | 91324 | 36.5475 | -121.9107 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0146418 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998781 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | SWITCH | 12675 | 20241214 | 2010 | 20241216 | 1410 | 2660417 | 2520 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 25200 | 37.0376 | -121.8595 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146006 | OH | Sus | 35605675 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | Yes | Yes | 1998345 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 985275 | 20241214 | 2012 | 20241215 | 425 | 2660574 | 493 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 4437 | 36.8629 | -121.6657 | Yes | Partly Cloudy;32-90 F |  |  | 24-0146153 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998504 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ERTA-0403 | 83510403 | JUMPER | OJ'S 1 SPAN SS OF CGC# 316318515663 | 20241214 | 2119 | 20241215 | 928 | 2660645 | 729 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 23 | 16767 | 36.9236 | -121.76 | Yes | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0146092 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1998435 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 5825 | 20241214 | 2151 | 20241217 | 2332 | 2660684 | 2445 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 101859 | 37.0127 | -121.7935 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 24-0145318 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1998450 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 11231 | 20241214 | 2246 | 20241215 | 220 | 2660735 | 214 | Distribution Circuit | Vegetation | Tree - grew into line | 422 | 66128 | 36.989 | -121.8046 | Yes | Clear;32-90 F | Transformer (OH) | Normal | 24-0146129 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998478 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0422 | 182440422 | FUSE | 2581 | 20241215 | 619 | 20241216 | 2215 | s1998597 | 2396 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 232412 | 36.5918 | -121.9454 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145224 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Multi-Fault | 0 | No | Yes | No | 1998597 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 8557 | 20241215 | 730 | 20241215 | 1811 | 2661264 | 641 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3846 | 36.5665 | -121.8863 | No | Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146220 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | Yes | No | 1998569 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | SWITCH | 432074 | 20241215 | 837 | 20241215 | 1735 | 2661105 | 538 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 8070 | 37.0866 | -122.006 | No | Clear;32-90 F |  |  | 24-0146392 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998759 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1101 | 182731101 | FUSE | 868789 | 20241215 | 839 | 20241215 | 925 | 2661115 | 46 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 230 | 36.5697 | -121.729 | No | Clear;32-90 F |  |  | 24-0146203 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998552 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | RESERVATION ROAD-1102 | 182731102 | FUSE | 3725 | 20241215 | 846 | 20241216 | 1417 | 2661126 | 1771 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 5906 | 36.5547 | -121.5365 | No | Clear;32-90 F |  |  | 24-0146245 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998618 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | FUSE | 11663 | 20241215 | 934 | 20241215 | 941 | 2661218 | 7 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 28 | 36.9616 | -122.0894 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0146207 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998556 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 621 | 20241215 | 956 | 20241215 | 1453 | 2661272 | 297 | Distribution Circuit | Vegetation | Tree - branch fell on line | 151 | 44847 | 36.5298 | -121.8305 | No | Overcast-Heavy Rain-Strong Winds;32-90 F | Secondary | Broken | 24-0146223 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1998573 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 8091 | 20241215 | 1001 | 20241215 | 1129 | 2661254 | 88 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 320 | 28160 | 36.6052 | -121.9293 | No | Clear;32-90 F |  |  | 24-0146267 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998642 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 5513 | 20241215 | 1004 | 20241216 | 1729 | 2661263 | 1885 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 58435 | 37.1516 | -122.1359 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 24-0146630 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1999014 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | TRANSFORMER | 315680617660 | 20241215 | 1007 | 20241215 | 1253 | 2661273 | 166 | Transformer only | Unknown Cause | Patrol - found nothing | 7 | 1162 | 36.9756 | -121.98 | No | Clear;32-90 F |  |  | 24-0146292 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1998665 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | RECLOSER | BL 1101 | 20241215 | 1010 | 20241215 | 1751 | 2661288 | 461 | Distribution Circuit | Equipment Failure/Involved | Overhead | 744 | 195364 | 37.0926 | -122.0966 | No | Clear;32-90 F | Insulator | Broken | 24-0146232 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998599 | 0 | EPSS Ckt | N | 2024 | B&C
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 316058815340 | 20241215 | 1141 | 20241216 | 1213 | 2661851 | 1472 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1472 | 36.9131 | -121.8493 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0146438 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998799 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 9181 | 20241215 | 1319 | 20241216 | 1055 | 2661632 | 1296 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 16848 | 37.2288 | -122.148 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146336 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | Yes | 1998705 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 6753 | 20241215 | 1414 | 20241215 | 1915 | 2661712 | 301 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 11438 | 36.5659 | -121.8876 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146389 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998757 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ERTA-0403 | 83510403 | OCB | 403/2 | 20241215 | 1416 | 20241215 | 1541 | 2661710 | 85 | Distribution Circuit | Vegetation | Tree - branch fell on line | 480 | 40800 | 36.9307 | -121.7642 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0146361 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998732 | 0 | Non-EPSS | N | 2024 | NA
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 491331 | 20241215 | 1510 | 20241216 | 1608 | 2662661 | 1498 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1498 | 36.5828 | -121.9497 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146527 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | No | 1998906 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 2233 | 20241215 | 1525 | 20241215 | 1641 | 2661907 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 836 | 36.5728 | -121.8826 | No | Clear;32-90 F |  |  | 24-0146376 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998745 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | TRANSFORMER | 315934417270 | 20241215 | 1533 | 20241216 | 1249 | 2655473 | 1276 | Transformer only | Vegetation | Tree - grew into line | 15 | 19140 | 36.9659 | -121.8926 | No | Overcast-Heavy Rain-Fog;32-90 F | Secondary | Broken | 24-0146367 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998738 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2106 | 182402106 | RECLOSER | 9138 | 20241215 | 1534 | 20241217 | 1324 | 2661826 | 2750 | Distribution Circuit | Vegetation | Tree - fell into line | 189 | 43881 | 36.6413 | -121.8077 | No | Clear;32-90 F | Insulator | Broken- wire on ground | 24-0146387 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998755 | 0 | EPSS Ckt | N | 2024 | NA
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | OCB | 2204/2 | 20241215 | 1609 | 20241215 | 1619 | 2661884 | 10 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 7383 | 73830 | 36.5786 | -121.9084 | No | Clear;32-90 F |  |  | 24-0146374 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998744 | 0 | EPSS Ckt | N | 2024 | PH TOC
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 4439 | 20241215 | 1610 | 20241215 | 2130 | 2661867 | 320 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 960 | 36.7754 | -121.6769 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0146462 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1998827 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRANSFORMER | 315206726434 | 20241215 | 1611 | 20241215 | 1944 | 2661869 | 213 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 213 | 37.2143 | -122.147 | No | Partly Cloudy;32-90 F |  |  | 24-0146444 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1998805 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-1101 | 182401101 | TRANSFORMER | T0845 | 20241215 | 1620 | 20241217 | 1738 | 2661897 | 2958 | Distribution Circuit | Equipment Failure/Involved | Underground | 190 | 111948 | 36.6865 | -121.8036 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 24-0146621 | UG | Sus | 35605804 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999264 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 8235 | 20241215 | 1627 | 20241216 | 1221 | 2661910 | 1194 | Distribution Circuit | Vegetation | Tree - branch fell on line | 70 | 28543 | 36.6254 | -121.9339 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 24-0146377 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998746 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | FUSE | 2811 | 20241215 | 1646 | 20241216 | 1305 | 2661934 | 1219 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 8041 | 36.5143 | -121.8127 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146442 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998803 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | TRANSFORMER | 315906917577 | 20241215 | 1757 | 20241216 | 412 | 2662031 | 615 | Transformer only | Vegetation | Tree - bark fell into line | 4 | 2460 | 36.9744 | -121.902 | No | Partly Cloudy;32-90 F | Transformer | Normal | 24-0146446 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998808 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 4837 | 20241215 | 1805 | 20241216 | 1107 | 2662035 | 1022 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 3066 | 36.9595 | -121.7305 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0146434 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998795 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | PACIFIC GROVE-0424 | 182440424 | TRANSFORMER | 411426548593 | 20241215 | 1810 | 20241215 | 1818 | 2662034 | 8 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 56 | 36.6321 | -121.924 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0146420 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1998783 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRANSFORMER | 315335123694 | 20241215 | 1855 | 20241216 | 1640 | 2662063 | 1305 | Transformer only | Vegetation | Tree - fell into line | 1 | 1305 | 37.1388 | -122.1012 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken- wire on ground | 24-0146470 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998835 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | TRANSFORMER | 315234624251 | 20241215 | 1909 | 20241215 | 2357 | 2662074 | 288 | Transformer only | Unknown Cause | Patrol - found nothing | 5 | 1440 | 37.1549 | -122.1336 | No | Partly Cloudy;32-90 F |  |  | 24-0146474 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1998842 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 2485 | 20241215 | 1918 | 20241216 | 1045 | 2662083 | 927 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 13905 | 36.5866 | -121.8644 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0146565 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998950 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 8183 | 20241215 | 1918 | 20241215 | 2146 | 2662087 | 148 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 115 | 17020 | 36.9646 | -121.8903 | No | Partly Cloudy;32-90 F |  |  | 24-0146467 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998832 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 2479 | 20241215 | 1924 | 20241217 | 1811 | 2662089 | 2807 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 101052 | 36.5788 | -121.8688 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146642 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1999024 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 50823 | 20241215 | 1925 | 20241215 | 2103 | 2662065 | 98 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 294 | 36.93 | -121.3842 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0146435 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1998796 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | FUSE | 24421 | 20241215 | 1926 | 20241217 | 210 | 2662108 | 1844 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1228 | 36.6784 | -121.7172 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0146539 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998926 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 7687 | 20241215 | 1937 | 20241216 | 833 | 2662099 | 776 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 9312 | 36.5819 | -121.8631 | No | Clear;32-90 F |  |  | 24-0146503 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998872 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | TRANSFORMER | 100000034971 | 20241215 | 1939 | 20241216 | 1525 | 2662103 | 1186 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2372 | 37.1484 | -122.1355 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0146468 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998833 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2106 | 182402106 | TRANSFORMER | 411775148859 | 20241215 | 2008 | 20241216 | 1159 | 2662121 | 951 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 6657 | 36.6427 | -121.8047 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0146490 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998859 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 9271 | 20241215 | 2034 | 20241216 | 1423 | 2662142 | 1069 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 13897 | 37.036 | -121.86 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146456 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998821 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 8021 | 20241215 | 2103 | 20241215 | 2208 | 2661513 | 65 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 1625 | 37.1635 | -122.1621 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0146457 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1998822 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | JUMPER | OPEN JMPR 1 SS 6787 | 20241215 | 2214 | 20241216 | 1251 | 2662202 | 877 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 17540 | 36.9287 | -121.7062 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 24-0146475 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Open Circuit | 0 | No | No | No | 1998843 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | FUSE | 9507 | 20241215 | 2254 | 20241216 | 450 | 2662243 | 356 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 1058 | 36.7074 | -121.7312 | No | Clear;32-90 F |  |  | 24-0146484 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998854 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | TRANSFORMER | 411580846778 | 20241215 | 2341 | 20241216 | 1055 | 2662254 | 674 | Transformer only | Vegetation | Tree - fell into line | 14 | 9436 | 36.5835 | -121.8694 | No | Partly Cloudy;32-90 F | Secondary | Broken- wire on ground | 24-0146480 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998849 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | TRANSFORMER | T2243 | 20241216 | 536 | 20241216 | 1006 | 2662318 | 270 | Transformer only | Unknown Cause | Patrol - found nothing | 11 | 2970 | 36.6029 | -121.8631 | No | Partly Cloudy;32-90 F |  |  | 24-0146536 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1998922 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 3315 | 20241216 | 651 | 20241216 | 924 | 2662340 | 153 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 408 | 37.011 | -121.9017 | No | Overcast;32-90 F |  |  | 24-0146520 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998898 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS SUB | 8362 | FUSE | 8961 | 20241216 | 834 | 20241216 | 1013 | 2662478 | 99 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 198 | 37.0432 | -122.0518 | No | Overcast;32-90 F |  |  | 24-0146544 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998932 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 50899 | 20241216 | 909 | 20241216 | 1010 | 2662556 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 163 | 36.8323 | -121.3483 | No | Overcast;32-90 F |  |  | 24-0146551 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998936 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | JUMPER | OJ N OF CGC 315853217966 | 20241216 | 918 | 20241216 | 1422 | 2662396 | 304 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 6080 | 36.9848 | -121.9208 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0146497 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1998864 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2102 | 83192102 | FUSE | 11575 | 20241216 | 943 | 20241216 | 1058 | 2662698 | 75 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 250 | 36.9089 | -121.7695 | No | Overcast-Drizzle;32-90 F |  |  | 24-0146556 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998942 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2101 | 182222101 | TRANSFORMER | 411715348011 | 20241216 | 953 | 20241216 | 1248 | 2662747 | 175 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 1400 | 36.6181 | -121.8245 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 24-0146543 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998927 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | SWITCH | 24501 | 20241216 | 1143 | 20241218 | 1702 | 2662946 | 3180 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 146010 | 36.6962 | -121.6999 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0146397 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1998961 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | FUSE | 7191 | 20241216 | 1217 | 20241218 | 1647 | 2662999 | 3150 | Distribution Circuit | Vegetation | Tree - grew into line | 14 | 44100 | 36.2368 | -121.7875 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0146678 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999057 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | FUSE | 40251 | 20241216 | 1224 | 20241217 | 1239 | 2663013 | 1455 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 30418 | 36.2415 | -121.7971 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146640 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1999022 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2105 | 182402105 | OCB | 2105/2/NORM | 20241216 | 1341 | 20241216 | 1508 | 2663143 | 87 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2017 | 121851 | 36.6433 | -121.7919 | No | Overcast-Rain;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0146613 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | No | 1998994 | 0 | EPSS Ckt | N | 2024 | A&B PHASE TIME
CENTRAL COAST | MONTEREY | FORT ORD-2106 | 182402106 | RECLOSER | 37286 | 20241216 | 1353 | 20241216 | 1513 | 2663182 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2556 | 203054 | 36.6436 | -121.7895 | No | Overcast-Rain;32-90 F |  |  | 24-0146617 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Multi-Fault | 0 | No | No | No | 1998999 | 0 | EPSS Ckt | N | 2024 | ABC PHASE & SGF
CENTRAL COAST | SALINAS | SALINAS-1106 | 182011106 | TRANSFORMER | T220 | 20241216 | 1353 | 20241217 | 645 | 2662966 | 1012 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1012 | 36.669 | -121.6645 | No | Overcast-Drizzle;32-90 F | Secondary | Burned/flashed | 24-0146616 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998998 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 7807 | 20241216 | 1427 | 20241216 | 2342 | 2663238 | 555 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 9435 | 36.9884 | -121.7391 | No | Overcast-Rain;32-90 F | Insulator | Broken | 24-0146663 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999045 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | RECLOSER | 198478 | 20241216 | 1436 | 20241217 | 1210 | 2663099 | 1294 | Distribution Circuit | Equipment Failure/Involved | Overhead | 239 | 5102 | 36.3913 | -121.6195 | No | Overcast;32-90 F | Conductor- Overhead | Together | 24-0146627 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1999010 | 0 | EPSS Ckt | N | 2024 | N/A
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 2469 | 20241216 | 1440 | 20241216 | 1530 | 2663271 | 50 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 1600 | 36.8825 | -121.7078 | No | Overcast-Drizzle;32-90 F |  |  | 24-0146652 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1999036 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | TRANSFORMER | T143715 | 20241216 | 1547 | 20241217 | 2217 | 2663361 | 1830 | Distribution Circuit | Equipment Failure/Involved | Underground | 4 | 1902 | 36.3295 | -121.1953 | No | Partly Cloudy-Drizzle;32-90 F | Transformer (UG) | Broken | 24-0146785 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999275 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412145156153 | 20241216 | 1745 | 20241216 | 1813 | 2663565 | 28 | Transformer only | Company Initiated | Improper Construction | 1 | 28 | 36.8462 | -121.6864 | No | Overcast-Fog;32-90 F | Bushing | Normal | 24-0146682 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1999061 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | TRANSFORMER | 411697344666 | 20241216 | 1851 | 20241217 | 1657 | 2663631 | 1326 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 6630 | 36.5268 | -121.827 | No | Rain-Overcast-Fog;32-90 F | Transformer | Failed/Faulted | 24-0146786 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999276 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | FUSE | 8255 | 20241216 | 1900 | 20241217 | 1330 | 2663640 | 1110 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 3590 | 36.577 | -121.9703 | No | Overcast-Fog-Drizzle;32-90 F | Insulator | Broken | 24-0146709 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999090 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2101 | 182222101 | TRANSFORMER | 411660147502 | 20241216 | 1920 | 20241216 | 2205 | 2663655 | 165 | Transformer only | Equipment Failure/Involved | Overhead | 23 | 3795 | 36.6039 | -121.8432 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146707 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1999086 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | RECLOSER | 7062 | 20241216 | 1957 | 20241216 | 2056 | 2663676 | 59 | Distribution Circuit | Vegetation | Tree - branch fell on line | 51 | 3009 | 36.2789 | -121.3033 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0146699 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1999077 | 0 | EPSS Ckt | N | 2024 | FORCE OUT
CENTRAL COAST | SALINAS | SALINAS-1109 | 182011109 | TRANSFORMER | 412355249868 | 20241216 | 1958 | 20241217 | 115 | 2663678 | 317 | Transformer only | Equipment Failure/Involved | Overhead | 19 | 6023 | 36.6747 | -121.6084 | No | Overcast-Fog;32-90 F | Fuse | Broken | 24-0146718 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999104 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | INDUSTRIAL ACRES-0412 | 182300412 | TRANSFORMER | 412296549787 | 20241216 | 2003 | 20241217 | 1100 | 2663426 | 897 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 5382 | 36.6719 | -121.6283 | No | Overcast;32-90 F | Connector or Splice (OH) | Burned/flashed | 24-0146702 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999079 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2102 | 182082102 | FUSE | 66577 | 20241217 | 843 | 20241217 | 1338 | 2663908 | 295 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 295 | 36.2426 | -121.1464 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0146810 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999302 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 12017 | 20241217 | 913 | 20241217 | 1104 | 2664165 | 111 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 333 | 36.9339 | -121.702 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0146779 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1999268 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 6759 | 20241217 | 1024 | 20241217 | 1230 | 2664105 | 126 | Distribution Circuit | Vegetation | Tree - bark fell into line | 34 | 4284 | 36.8777 | -121.6876 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0146793 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1999286 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GONZALES-1104 | 182131104 | FUSE | 7133 | 20241217 | 1156 | 20241217 | 1455 | 2664214 | 179 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1432 | 36.5087 | -121.4499 | No | Partly Cloudy;32-90 F |  |  | 24-0146830 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1999328 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 12838 | 20241217 | 1235 | 20241217 | 1302 | 2664251 | 27 | Distribution Circuit | Vegetation | Tree - branch fell on line | 241 | 6507 | 37.1272 | -122.1236 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0146796 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1999288 | 0 | EPSS Ckt | N | 2024 | FORCE OUT
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | TRANSFORMER | 411335447200 | 20241217 | 1607 | 20241218 | 1849 | 2664464 | 1602 | Transformer only | Vegetation | Tree - fell into line | 3 | 4806 | 36.5929 | -121.9535 | No | Clear;32-90 F | Transformer | Broken | 24-0146860 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999351 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | TRANSFORMER | 412043255961 | 20241217 | 1611 | 20241218 | 1335 | 2664462 | 1284 | Transformer only | Environmental/External | Water | 1 | 1284 | 36.8399 | -121.7198 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0146890 | OH | Sus | 35605803 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999391 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 6895 | 20241217 | 1626 | 20241217 | 1832 | 2664477 | 126 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 84 | 36.8382 | -121.7668 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0146867 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999359 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1102 | 182331102 | TRANSFORMER | 412263751897 | 20241217 | 1640 | 20241217 | 1723 | 2664168 | 43 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 215 | 36.7296 | -121.6416 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0146856 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999348 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | TRANSFORMER | 412152949912 | 20241217 | 1716 | 20241218 | 304 | 2664531 | 588 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 2940 | 36.6742 | -121.6776 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0146861 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999352 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 6209 | 20241217 | 1739 | 20241217 | 2229 | 2664556 | 290 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 870 | 37.1793 | -122.1392 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0146873 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1999370 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 5071 | 20241217 | 1900 | 20241217 | 2107 | 2664602 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 1270 | 36.9718 | -121.7895 | No | Clear;32-90 F |  |  | 24-0146883 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999380 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DOLAN ROAD-1101 | 182381101 | JUMPER | 412018154199 | 20241217 | 1914 | 20241217 | 2346 | 2664601 | 272 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 544 | 36.7909 | -121.7274 | No | Clear;32-90 F | Insulator | Broken | 24-0146869 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1999363 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2106 | 182492106 | TRANSFORMER | 412917659408 | 20241217 | 2021 | 20241217 | 2121 | 2664657 | 60 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 120 | 36.9405 | -121.425 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0146879 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Three Phase Fault | 0 | No | No | No | 1999385 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | TRANSFORMER | 413439037338 | 20241218 | 345 | 20241218 | 1903 | 2664703 | 918 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 918 | 36.3379 | -121.2288 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0146933 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999536 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | TRANSFORMER | 314994020760 | 20241218 | 1104 | 20241218 | 1317 | 2665109 | 133 | Transformer only | 3rd Party | Tree - cutting- 3rd party | 1 | 133 | 37.0555 | -122.2154 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0146995 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999636 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2203 | 182852203 | TRANSFORMER | T1908 | 20241218 | 1153 | 20241219 | 1535 | 2665171 | 1662 | Distribution Circuit | Equipment Failure/Involved | Underground | 8 | 13296 | 36.5575 | -121.9217 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0147022 | UG | Sus | 35605804 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999659 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 50899 | 20241218 | 1245 | 20241218 | 1358 | 2665195 | 73 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 584 | 36.8323 | -121.3483 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0146974 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1999604 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | TRANSFORMER | 316134014881 | 20241218 | 1335 | 20241219 | 111 | 2665202 | 696 | Transformer only | Vegetation | Tree - fell into line | 1 | 696 | 36.9012 | -121.8237 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0147011 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999651 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | TRANSFORMER | 315149720656 | 20241218 | 1433 | 20241218 | 1705 | 2665335 | 152 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 152 | 37.0555 | -122.1634 | No | Partly Cloudy;32-90 F |  |  | 24-0147037 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1999677 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 6895 | 20241218 | 1535 | 20241218 | 1848 | 2665384 | 193 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 129 | 36.8382 | -121.7668 | No | Partly Cloudy;32-90 F |  |  | 24-0147046 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999684 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | FUSE | 3583 | 20241218 | 1622 | 20241218 | 2130 | 2665420 | 308 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 4312 | 37.1389 | -122.1011 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0147029 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1999671 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | RECLOSER | 3018 | 20241218 | 1757 | 20241218 | 1807 | 2665475 | 10 | Distribution Circuit | Company Initiated | Personnel- company | 55 | 550 | 36.6662 | -121.6858 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0147040 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999679 | 0 | EPSS Ckt | N | 2024 | SGF
CENTRAL COAST | COAST | SAN BENITO-2104 | 182742104 | FUSE | 6875 | 20241218 | 1934 | 20241218 | 2228 | 2665540 | 174 | Distribution Circuit | Equipment Failure/Involved | Overhead | 103 | 17922 | 36.8864 | -121.6325 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 24-0147053 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1999697 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 6343 | 20241218 | 2029 | 20241219 | 156 | 2665558 | 327 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 5821 | 37.2223 | -122.1449 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0147063 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1999713 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | RECLOSER | 3060 | 20241218 | 2029 | 20241218 | 2101 | 2665551 | 32 | Distribution Circuit | Equipment Failure/Involved | Overhead | 238 | 7616 | 36.7624 | -121.7341 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Arcing | 24-0147050 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1999692 | 0 | Non-EPSS | N | 2024 | NA
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 6137 | 20241218 | 2207 | 20241219 | 1422 | 2665590 | 975 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 4221 | 36.5945 | -121.8932 | No | Partly Cloudy-Rain;32-90 F |  |  | 24-0147061 | OH | Sus | 46417963 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999708 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-1101 | 83041101 | RECLOSER | BL 1101 | 20241219 | 1044 | 20241219 | 1234 | 2665890 | 110 | Distribution Circuit | Animal | Squirrel | 744 | 60931 | 37.0926 | -122.0966 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0147106 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1999823 | 0 | EPSS Ckt | N | 2024 | BC
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRIP-SAVER | 9031 | 20241219 | 1137 | 20241219 | 1341 | 2665939 | 124 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 47 | 5828 | 37.0726 | -122.0742 | No | Clear;32-90 F |  |  | 24-0147120 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999850 | 0 | EPSS Ckt | N | 2024 | none
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | TRANSFORMER | 316020018125 | 20241219 | 1356 | 20241219 | 2317 | 2666070 | 561 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1122 | 36.9896 | -121.8635 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0147150 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999879 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | TRANSFORMER | 413091657481 | 20241219 | 1401 | 20241219 | 1455 | 2666055 | 54 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 54 | 36.889 | -121.3636 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0147121 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1999851 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ERTA-0404 | 83510404 | TRIP-SAVER | 5731 | 20241219 | 1454 | 20241219 | 1523 | 2666010 | 29 | Distribution Circuit | Vegetation | Tree - fell into line | 107 | 3103 | 36.9325 | -121.7645 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0147130 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1999863 | 0 | Non-EPSS | N | 2024 | N/A
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | TRANSFORMER | 413091857531 | 20241219 | 1520 | 20241219 | 1621 | 2666118 | 61 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 61 | 36.8904 | -121.3636 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0147139 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1999871 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1102 | 182941102 | FUSE | 205 | 20241219 | 1631 | 20241219 | 1935 | 2666190 | 184 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 552 | 36.2513 | -121.7873 | No | Clear;32-90 F |  |  | 24-0147167 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1999896 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 85602 | 20241219 | 1916 | 20241220 | 4 | 2666255 | 156 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 150 | 43200 | 36.5967 | -121.8961 | No | Clear;32-90 F |  |  | 24-0147170 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999901 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | FUSE | 85602 | 20241220 | 353 | 20241220 | 2305 | 2666339 | 1152 | Distribution Circuit | Equipment Failure/Involved | Underground | 150 | 93117 | 36.5967 | -121.8961 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 24-0147186 | UG | Sus | 46421363 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999924 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | SWITCH | 5051 | 20241220 | 529 | 20241220 | 819 | 2666351 | 170 | Distribution Circuit | Equipment Failure/Involved | Overhead | 70 | 11900 | 36.7187 | -121.7221 | No | Partly Cloudy;32-90 F | Jumper | Burned/flashed | 24-0147187 | OH | Sus | 46421196 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1999925 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2104 | 182222104 | RECLOSER | 2624 | 20241220 | 1133 | 20241220 | 1141 | 2666770 | 8 | Distribution Circuit | Company Initiated | Personnel- company | 1473 | 11784 | 36.569 | -121.7955 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0147230 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000119 | 0 | EPSS Ckt | N | 2024 | C GRD
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | TRANSFORMER | 316353913583 | 20241220 | 1245 | 20241220 | 1342 | 2666821 | 57 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 114 | 36.8659 | -121.7481 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0147238 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000144 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | OCB | 2204/2 | 20241220 | 1342 | 20241220 | 1755 | 2666873 | 253 | Distribution Circuit | Equipment Failure/Involved | Underground | 7438 | 313437 | 36.5786 | -121.9084 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0147240 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Three Phase Fault | 0 | No | No | No | 2000147 | 0 | EPSS Ckt | N | 2024 | A B C
CENTRAL COAST | SALINAS | SALINAS-1103 | 182011103 | SWITCH | 3930 | 20241220 | 1637 | 20241220 | 1705 | 2667016 | 28 | Distribution Circuit | Company Initiated | Return Circuit Normal | 348 | 7314 | 36.6876 | -121.6551 | No | Partly Cloudy;32-90 F | Conductor- Underground | Normal | 24-0141797 | UG | Sus | 35579490 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 2000161 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | TRANSFORMER | 315391521417 | 20241220 | 1814 | 20241220 | 2038 | 2667060 | 144 | Transformer only | Unknown Cause | Patrol - found nothing | 7 | 1008 | 37.0776 | -122.0803 | No | Partly Cloudy;32-90 F |  |  | 24-0147268 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 2000179 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2107 | 83622107 | RECLOSER | 11044 | 20241220 | 1821 | 20241220 | 1949 | 2667070 | 88 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2245 | 147988 | 37.0401 | -122.0297 | No | Partly Cloudy;32-90 F |  |  | 24-0147262 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Three Phase Fault | 0 | No | No | No | 2000173 | 0 | Non-EPSS | N | 2024 | A B C
CENTRAL COAST | KING CITY | SOLEDAD-2101 | 182052101 | FUSE | 8509 | 20241221 | 834 | 20241221 | 1147 | 2667252 | 193 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 900 | 36.3785 | -121.2407 | No | Partly Cloudy;32-90 F |  |  | 24-0147319 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000271 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | RECLOSER | 10714 | 20241221 | 1451 | 20241222 | 54 | 2667465 | 603 | Distribution Circuit | 3rd Party | Vehicle | 3198 | 160210 | 36.9779 | -121.8666 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on object | 24-0147336 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | Yes | No | 2000292 | 0 | EPSS Ckt | N | 2024 | FORCE OUT
CENTRAL COAST | MONTEREY | VIEJO-2202 | 182852202 | TRANSFORMER | 411404948194 | 20241221 | 2054 | 20241222 | 1539 | 2667542 | 1125 | Transformer only | Equipment Failure/Involved | Electrical Overload | 4 | 4500 | 36.6208 | -121.931 | No | Overcast-Fog;32-90 F | Transformer | Burned/flashed | 24-0147350 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000309 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2107 | 83622107 | FUSE | 5241 | 20241222 | 728 | 20241222 | 1445 | 2667625 | 437 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1748 | 37.0699 | -122.0843 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0147379 | OH | Sus | 35607001 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | No | 2000360 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | VIEJO-2204 | 182852204 | OCB | 2204/2 | 20241222 | 750 | 20241222 | 847 | 2667633 | 57 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7511 | 186783 | 36.5786 | -121.9084 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken | 24-0147364 | OH | Sus | 46432620 | SOUTH BAY AND CENTRAL COAST | DEC | Three Phase Fault | 0 | No | No | No | 2000326 | 0 | EPSS Ckt | N | 2024 | TIME OC
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 4691 | 20241222 | 1115 | 20241222 | 1225 | 2667729 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 140 | 36.9347 | -121.8483 | No | Overcast;32-90 F |  |  | 24-0147382 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000366 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1102 | 182011102 | FUSE | 25655 | 20241222 | 1132 | 20241222 | 1300 | 2667735 | 88 | Distribution Circuit | 3rd Party | Metallic Balloon | 119 | 10507 | 36.6859 | -121.6079 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0147381 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000365 | 1 | Non-EPSS | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2102 | 182492102 | RECLOSER | 676164 | 20241222 | 1156 | 20241223 | 411 | 2667743 | 975 | Distribution Circuit | 3rd Party | Vehicle | 36 | 28292 | 36.9953 | -121.3787 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 24-0147380 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Three Phase Fault | 0 | No | Yes | No | 2000362 | 0 | EPSS Ckt | N | 2024 | ABC
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 5901 | 20241222 | 1358 | 20241222 | 2252 | 2667804 | 534 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 8544 | 37.0944 | -121.9716 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0147396 | OH | Sus | 31720761 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 2000380 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 38430 | 20241222 | 1446 | 20241222 | 1528 | 2667825 | 42 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5532 | 149592 | 36.9756 | -121.8885 | No | Overcast;32-90 F |  |  | 24-0147399 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2000383 | 0 | EPSS Ckt | N | 2024 | A AND C PHASE
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 4563 | 20241222 | 1559 | 20241222 | 1859 | 2667853 | 180 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 4140 | 36.7259 | -121.6536 | No | Partly Cloudy;32-90 F |  |  | 24-0147415 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000400 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1104 | 182011104 | TRANSFORMER | 412184550026 | 20241222 | 1837 | 20241222 | 2034 | 2667896 | 117 | Transformer only | Equipment Failure/Involved | Overhead | 19 | 2223 | 36.6776 | -121.6666 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0147421 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000405 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | RECLOSER | 607060 | 20241223 | 651 | 20241223 | 1324 | 2668000 | 393 | Distribution Circuit | Equipment Failure/Involved | Overhead | 845 | 58205 | 36.8188 | -121.6731 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0147444 | OH | Sus | 31720764 | SOUTH BAY AND CENTRAL COAST | DEC | Multi-Fault | 0 | No | Yes | No | 2000430 | 0 | EPSS Ckt | N | 2024 | A C AND GRD
CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 50899 | 20241223 | 913 | 20241223 | 956 | 2668163 | 43 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3 | 115 | 36.8323 | -121.3483 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0147468 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000502 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 2175 | 20241223 | 1430 | 20241223 | 1524 | 2668446 | 54 | Distribution Circuit | 3rd Party | Metallic Balloon | 68 | 3672 | 36.8777 | -121.7341 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0147496 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2000545 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | TRANSFORMER | 412102951638 | 20241223 | 1643 | 20241224 | 447 | 2668490 | 724 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 724 | 36.7219 | -121.6964 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0147502 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000550 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 8615 | 20241223 | 1840 | 20241223 | 2015 | 2668578 | 95 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 285 | 36.9436 | -121.7681 | No | Partly Cloudy;32-90 F |  |  | 24-0147518 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2000567 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | FUSE | 2181 | 20241223 | 2102 | 20241223 | 2300 | 2668624 | 118 | Distribution Circuit | Equipment Failure/Involved | Overhead | 56 | 6611 | 36.4895 | -121.9363 | No | Overcast-Fog;32-90 F | Fuse | Failed/Faulted | 24-0147523 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000573 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2106 | 83252106 | FUSE | 5965 | 20241223 | 2140 | 20241223 | 2158 | 2668638 | 18 | Distribution Circuit | Animal | Other | 259 | 4662 | 36.9975 | -121.9563 | No | Overcast-Fog;32-90 F | Transformer (OH) | Normal | 24-0147520 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 2000570 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1102 | 82841102 | FUSE | 2251 | 20241224 | 330 | 20241224 | 845 | 2668759 | 315 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 6300 | 37.1702 | -122.1646 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0147592 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2000647 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 5277 | 20241224 | 402 | 20241224 | 511 | 2668812 | 69 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 2760 | 36.776 | -121.6876 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0147555 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2000608 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2103 | 83252103 | FUSE | 5395 | 20241224 | 406 | 20241224 | 450 | 2668784 | 44 | Distribution Circuit | Vegetation | Tree - branch fell on line | 100 | 4400 | 36.9737 | -122.0156 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0147552 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000604 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2107 | 83622107 | TRIP-SAVER | 834583 | 20241224 | 421 | 20241224 | 744 | 2668788 | 203 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 6902 | 37.0442 | -122.0777 | No | Overcast-Fog-Rain;32-90 F |  |  | 24-0147571 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000622 | 0 | Non-EPSS | N | 2024 | A PHASE
CENTRAL COAST | MONTEREY | OTTER-1101 | 182941101 | TRANSFORMER | 411374943211 | 20241224 | 439 | 20241224 | 1335 | 2668796 | 536 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1608 | 36.4834 | -121.935 | No | Rain-Overcast-Fog;32-90 F | Transformer | Failed/Faulted | 24-0147574 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000625 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1102 | 182291102 | TRIP-SAVER | 40461 | 20241224 | 538 | 20241224 | 704 | 2668825 | 86 | Distribution Circuit | Vegetation | Tree - branch fell on line | 284 | 24424 | 36.5481 | -121.9108 | No | Partly Cloudy-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 24-0147563 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2000616 | 0 | EPSS Ckt | N | 2024 | B AND C
CENTRAL COAST | COAST | PAUL SWEET-2103 | 83252103 | TRANSFORMER | 315575217550 | 20241224 | 708 | 20241224 | 1035 | 2668856 | 207 | Transformer only | Equipment Failure/Involved | Electrical Overload | 5 | 1035 | 36.9717 | -122.0145 | No | Rain-Overcast-Fog;32-90 F | Transformer | Burned/flashed | 24-0147586 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000639 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 6593 | 20241224 | 718 | 20241224 | 853 | 2668863 | 95 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 1235 | 37.0162 | -121.7201 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 24-0147599 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000653 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | FUSE | 10245 | 20241224 | 749 | 20241224 | 909 | 2668893 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1120 | 36.9633 | -121.9905 | No | Overcast-Fog-Rain;32-90 F |  |  | 24-0147598 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2000652 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | BEN LOMOND-0401 | 83040401 | OTHER | 493 | 20241224 | 832 | 20241224 | 1303 | 2668936 | 271 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 6775 | 37.0866 | -122.0783 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0147600 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | Yes | 2000654 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2107 | 83622107 | RECLOSER | 5300 | 20241224 | 1757 | 20241225 | 39 | 2669434 | 402 | Distribution Circuit | Vegetation | Tree - fell into line | 373 | 53754 | 37.0383 | -122.0708 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0147685 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Three Phase Fault | 0 | No | Yes | No | 2000745 | 0 | Non-EPSS | N | 2024 | A B C TIME
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 2689 | 20241224 | 2309 | 20241225 | 246 | 2669498 | 217 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 6944 | 37.1274 | -122.0181 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 24-0147704 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000764 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1102 | 182011102 | SWITCH | 21078SW | 20241224 | 2322 | 20241225 | 42 | 2669500 | 80 | Distribution Circuit | Equipment Failure/Involved | Underground | 200 | 4342 | 36.6917 | -121.6047 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 24-0147644 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000761 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 10021 | 20241225 | 229 | 20241225 | 1017 | 2669514 | 468 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1091 | 36.8984 | -121.8211 | No | Fog;32-90 F | Cutout- fuse holder | Failed/Faulted | 24-0147708 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000768 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | FUSE | 10021 | 20241225 | 547 | 20241226 | 1345 | 2669624 | 1918 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 2562 | 36.8984 | -121.8211 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0147718 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000779 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | TRANSFORMER | 316115014565 | 20241225 | 1213 | 20241225 | 1320 | 2669648 | 67 | Transformer only | Company Initiated | Other Circuits | 1 | 67 | 36.8924 | -121.8294 | No | Partly Cloudy;32-90 F | Transformer | Deteriorated | 24-0147726 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000787 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | HATTON-1101 | 182291101 | TRANSFORMER | 411765444221 | 20241226 | 658 | 20241226 | 1418 | 2669852 | 440 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1760 | 36.5149 | -121.804 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0147793 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000870 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | PAUL SWEET-2107 | 83252107 | TRANSFORMER | 315539416920 | 20241226 | 903 | 20241226 | 950 | 2669944 | 47 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 141 | 36.9546 | -122.0275 | No | Overcast-Fog;32-90 F | Transformer (OH) | Deteriorated | 24-0147788 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 2000859 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | OTHER | WIRE DOWN 1 SE/OF 89941 | 20241226 | 938 | 20241226 | 1421 | 2669980 | 283 | Distribution Circuit | Equipment Failure/Involved | Overhead | 336 | 33980 | 36.0865 | -120.9497 | No | Partly Cloudy-Rain;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0147799 | OH | Sus | 31720835 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | Yes | 2000885 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | GABILAN-1101 | 182331101 | FUSE | 23501 | 20241226 | 1157 | 20250103 | 58 | 2670318 | 10861 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 21722 | 36.7421 | -121.6022 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0147839 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Three Phase Fault | 0 | No | Yes | No | 2000933 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 7371 | 20241226 | 1212 | 20241226 | 1320 | 2670103 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 408 | 37.0585 | -122.142 | No | Overcast;32-90 F |  |  | 24-0147808 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000905 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | TRANSFORMER | T143715 | 20241226 | 1502 | 20241226 | 1752 | 2670048 | 170 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 170 | 36.3295 | -121.1953 | No | Partly Cloudy-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 24-0147819 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000917 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | BORONDA-1101 | 182461101 | TRANSFORMER | 412188451629 | 20241226 | 1653 | 20241227 | 1256 | 2670181 | 1203 | Transformer only | Environmental/External | Water | 1 | 1203 | 36.7217 | -121.6672 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0147834 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000928 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | POINT MORETTI-1101 | 82931101 | FUSE | 7371 | 20241226 | 1749 | 20241227 | 1550 | 2670308 | 1321 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 5284 | 37.0585 | -122.142 | No | Overcast;32-90 F |  |  | 24-0147929 | OH | Sus | 31721005 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2001055 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | DEL MONTE-2103 | 182222103 | FUSE | 1371 | 20241226 | 2031 | 20241226 | 2114 | 2670350 | 43 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 344 | 36.5929 | -121.8704 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0147851 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000945 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | FUSE | 8163 | 20241227 | 146 | 20241227 | 725 | 2670422 | 339 | Distribution Circuit | Vegetation | Tree - branch fell on line | 132 | 44748 | 36.9659 | -121.8953 | No | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0147892 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000987 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 7989 | 20241227 | 224 | 20241227 | 638 | 2670434 | 254 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 68 | 17255 | 36.9817 | -121.8645 | No | Overcast-Fog-Heavy Rain;32-90 F |  |  | 24-0147888 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000983 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6863 | 20241227 | 239 | 20241227 | 1107 | 2670437 | 508 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 8812 | 36.9822 | -121.8011 | No | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0147901 | OH | Sus | 31721000 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 2001001 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 6371 | 20241227 | 336 | 20241227 | 1438 | 2670454 | 656 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 2403 | 36.8639 | -121.7228 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 24-0147916 | OH | Sus | 46440005 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2001039 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 6819 | 20241227 | 732 | 20241227 | 1321 | 2670535 | 349 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 6757 | 36.9962 | -121.8656 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0147928 | OH | Sus | 31720915 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | No | 2001054 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ERTA-0403 | 83510403 | TRANSFORMER | 316287715609 | 20241227 | 847 | 20241228 | 151 | 2670945 | 1024 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2048 | 36.9217 | -121.771 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0147964 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2001095 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2103 | 83192103 | TRANSFORMER | 316099614643 | 20241227 | 1050 | 20241227 | 2120 | 2670743 | 630 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 630 | 36.8946 | -121.8354 | No | Overcast-Fog;32-90 F | Transformer (OH) | Deteriorated | 24-0147961 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2001092 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 985275 | 20241227 | 1054 | 20241227 | 1315 | 2670750 | 141 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1269 | 36.8629 | -121.6657 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0147952 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2001080 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | ROB ROY-2104 | 83692104 | FUSE | 4241 | 20241227 | 1115 | 20241227 | 1237 | 2670782 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 1840 | 36.9947 | -121.843 | No | Overcast;32-90 F |  |  | 24-0147944 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2001071 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | TRANSFORMER | 412204554672 | 20241227 | 1304 | 20241228 | 1749 | 2670864 | 1725 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 1725 | 36.8059 | -121.6646 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 24-0147965 | OH | Sus | 46440033 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2001096 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | RECLOSER | 922576 | 20241227 | 1731 | 20241227 | 1847 | 2671037 | 76 | Distribution Circuit | Vegetation | Tree - fell into line | 305 | 23180 | 37.0994 | -122.0532 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0147979 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2001110 | 0 | EPSS Ckt | N | 2024 | A/B
CENTRAL COAST | COAST | PAUL SWEET-2101 | 83252101 | TRANSFORMER | 315724317364 | 20241227 | 2016 | 20241227 | 2136 | 2671075 | 80 | Transformer only | Unknown Cause | Patrol - found nothing | 11 | 880 | 36.9671 | -121.9636 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0147991 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 2001123 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | MONTEREY | FORT ORD-2106 | 182402106 | FUSE | 40391 | 20241227 | 2157 | 20241227 | 2313 | 2671103 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 91 | 6916 | 36.6277 | -121.8138 | No | Clear-Rain;32-90 F |  |  | 24-0147998 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2001129 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | DEL MONTE-2104 | 182222104 | FUSE | 80489 | 20241228 | 800 | 20241228 | 1335 | 2671383 | 335 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 558 | 36.5509 | -121.7377 | No | Clear;32-90 F |  |  | 24-0148048 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2001186 | 1 | EPSS Ckt | N | 2024
CENTRAL COAST | MONTEREY | LAURELES-1112 | 182371112 | TRANSFORMER | 411943043136 | 20241228 | 816 | 20241228 | 1046 | 2671206 | 150 | Transformer only | Animal | Squirrel | 5 | 750 | 36.4869 | -121.742 | No | Clear;32-90 F | Other | Normal | 24-0148032 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2001169 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SALINAS-1109 | 182011109 | FUSE | 4465 | 20241228 | 1141 | 20241229 | 1605 | 2671274 | 1704 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 13632 | 36.6641 | -121.5696 | No | Overcast;32-90 F | Anchor or Guy | Broken | 24-0148035 | OH | Sus | 46440816 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 2001174 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | ROB ROY-2105 | 83692105 | RECLOSER | 439972 | 20241228 | 1318 | 20241228 | 1625 | 2671357 | 187 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 13972 | 37.0195 | -121.8841 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0148052 | OH | Sus | 46440864 | SOUTH BAY AND CENTRAL COAST | DEC | Three Phase Fault | 0 | No | Yes | No | 2001189 | 0 | EPSS Ckt | N | 2024 | A-B-C
CENTRAL COAST | KING CITY | KING CITY-1106 | 182031106 | RECLOSER | 944510 | 20241228 | 1359 | 20241228 | 1810 | 2671387 | 251 | Distribution Circuit | Equipment Failure/Involved | Overhead | 122 | 25267 | 36.2071 | -121.1151 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0148050 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Multi-Fault | 0 | No | Yes | No | 2001187 | 0 | EPSS Ckt | N | 2024 | A-C-GRD
CENTRAL COAST | SALINAS | PRUNEDALE-1107 | 182961107 | FUSE | 24165 | 20241228 | 1641 | 20241229 | 1945 | 2671339 | 1624 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 1624 | 36.802 | -121.6162 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 24-0148059 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 2001200 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2106 | 83622106 | FUSE | 8427 | 20241229 | 725 | 20241229 | 1642 | 2671625 | 557 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 27293 | 37.077 | -121.981 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0148123 | OH | Sus | 46440924 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2001271 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | PRUNEDALE-1110 | 182961110 | RECLOSER | 607060 | 20241229 | 806 | 20241229 | 1345 | 2671645 | 339 | Distribution Circuit | Equipment Failure/Involved | Overhead | 845 | 58377 | 36.8188 | -121.6731 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0148088 | OH | Sus | 46440965 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 2001232 | 0 | EPSS Ckt | N | 2024 | SGF
CENTRAL COAST | COAST | WATSONVILLE-2101 | 83332101 | FUSE | 9805 | 20241229 | 951 | 20241229 | 1355 | 2671705 | 244 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 1464 | 36.8534 | -121.704 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 24-0148134 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2001282 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1105 | 182201105 | TRANSFORMER | 412427048743 | 20241229 | 1249 | 20241229 | 2255 | 2671771 | 606 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1212 | 36.6437 | -121.5817 | No | Partly Cloudy-Fog-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0148125 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2001273 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | FUSE | 4295 | 20241229 | 1257 | 20250103 | 1122 | 2671824 | 7105 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 10019 | 36.7467 | -121.6987 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0148148 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2001298 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | HOLLISTER-2104 | 182492104 | FUSE | 4629 | 20241229 | 1301 | 20241229 | 1420 | 2671823 | 79 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 2054 | 36.934 | -121.3606 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0148136 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2001285 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | HOLLISTER | SAN JUSTO-1101 | 183181101 | FUSE | 4497 | 20241230 | 655 | 20241230 | 1043 | 2672240 | 228 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 2736 | 36.8725 | -121.5547 | No | Fog;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0148186 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 2001349 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | BIG BASIN-1101 | 82841101 | RECLOSER | 595388 | 20241230 | 1013 | 20241230 | 1128 | 2672422 | 75 | Distribution Circuit | Vegetation | Tree - branch fell on line | 174 | 13050 | 37.1517 | -122.136 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0148209 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 2001445 | 0 | EPSS Ckt | N | 2024 | N/A
CENTRAL COAST | SALINAS | CASTROVILLE-2104 | 182352104 | TRANSFORMER | 412033451440 | 20241230 | 1017 | 20241230 | 2310 | 2672297 | 773 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 773 | 36.7153 | -121.7193 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0148203 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2001434 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | TRANSFORMER | 413909223381 | 20241230 | 1024 | 20241230 | 1317 | 2672433 | 173 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 173 | 35.9577 | -121.0573 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0148212 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2001449 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | CAMPHORA-1101 | 182071101 | FUSE | 7997 | 20241230 | 1507 | 20241230 | 1905 | 2672663 | 238 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 714 | 36.4689 | -121.4609 | No | Partly Cloudy;32-90 F |  |  | 24-0148243 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2001493 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | CAMP EVERS-2105 | 83622105 | FUSE | 10443 | 20241230 | 1757 | 20241230 | 2143 | 2672768 | 226 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 2034 | 37.1056 | -122.0431 | No | Partly Cloudy;32-90 F |  |  | 24-0148252 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2001504 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SPENCE-1101 | 182201101 | TRANSFORMER | 412554946924 | 20241231 | 853 | 20241231 | 2135 | 2673244 | 762 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 762 | 36.5965 | -121.5386 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0148306 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2001599 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | SALINAS | CASTROVILLE-2103 | 182352103 | OTHER | WIRE DOWN 1 S/OF 4099 | 20241231 | 1338 | 20250101 | 1307 | 2673273 | 1409 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1409 | 36.7464 | -121.7283 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0148314 | OH | Sus | 31721435 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 2001612 | 0 | Non-EPSS | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | FUSE | 10599 | 20241231 | 1618 | 20241231 | 2047 | 2673515 | 269 | Distribution Circuit | Animal | Bird found | 1 | 269 | 36.9386 | -121.7424 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 24-0148343 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2001640 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | COAST | GREEN VALLEY-2101 | 83192101 | JUMPER | JPRS 1 S/OF CGC 316309019155 | 20241231 | 1855 | 20250101 | 306 | 2673477 | 491 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1473 | 37.0182 | -121.7654 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0148329 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 2001625 | 0 | EPSS Ckt | N | 2024
CENTRAL COAST | SALINAS | SOLEDAD-2105 | 182052105 | FUSE | 7913 | 20241231 | 1944 | 20250101 | 740 | 2673646 | 716 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 2864 | 36.4894 | -121.4208 | No | Partly Cloudy;32-90 F |  |  | 25-0004790 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2001671 | 0 | EPSS Ckt | N | 2024
DE ANZA | DE ANZA | HICKS-1114 | 83431114 | TRANSFORMER | 315824027494 | 20230101 | 1330 | 20230102 | 452 | 1908256 | 922 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 12908 | 37.2463 | -121.9359 | No | Clear;32-90 F | Crossarm- Wood | Broken- wire on object | 23-0004424 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1795022 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS 1107 | 82021107 | FUSE | 31447 | 20230102 | 207 | 20230104 | 319 | 1909447 | 2952 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2952 | 37.1322 | -121.9391 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004639 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1795256 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | EL PATIO-1118 | 82921118 | TRANSFORMER | 315841928606 | 20230102 | 800 | 20230102 | 1340 | 1909580 | 340 | Transformer only | Equipment Failure/Involved | Overhead | 24 | 8160 | 37.2768 | -121.9304 | No | Clear;32-90F | Conductor- Overhead | Broken | 23-0004706 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1795312 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | TRIP-SAVER | 11533 | 20230102 | 806 | 20230103 | 2011 | 1909602 | 2165 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 80105 | 37.1428 | -121.9942 | No | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0004658 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1795271 | 0 | EPSS Ckt | N | 2023 | TRIP SAVER (OC)
DE ANZA | DE ANZA | BRITTON-1106 | 83611106 | TRANSFORMER | 315587032025 | 20230102 | 1101 | 20230102 | 1606 | 1910263 | 305 | Transformer only | Vegetation | Tree - branch fell on line | 14 | 4270 | 37.3701 | -122.0196 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0004791 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1795395 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1109 | 83371109 | TRANSFORMER | 100000021762 | 20230102 | 2043 | 20230102 | 2332 | 1910661 | 169 | Transformer only | Vegetation | Tree - grew into line | 6 | 1014 | 37.2801 | -121.9725 | No | Clear;32-90 F | Transformer | Contaminated | 23-0004868 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1795471 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | BRITTON-1113 | 83611113 | TRANSFORMER | 315559232400 | 20230102 | 2150 | 20230102 | 2238 | 1910605 | 48 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 336 | 37.3798 | -122.0292 | No | Clear;32-90 F | Transformer | Burned Open | 23-0004907 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1795511 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1112 | 83421112 | FUSE | 19921 | 20230102 | 2342 | 20230102 | 2352 | 1910804 | 10 | Distribution Circuit | Vegetation | Tree - branch fell on line | 235 | 2350 | 37.3896 | -122.0195 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0004935 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1795540 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1113 | 83371113 | FUSE | 29699 | 20230103 | 943 | 20230103 | 1049 | 1911226 | 66 | Distribution Circuit | Vegetation | Tree - branch fell on line | 128 | 8448 | 37.3041 | -122.01 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0005061 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1795622 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS 1106 | 82021106 | TRANSFORMER | 315704523790 | 20230103 | 1510 | 20230103 | 1556 | 1911767 | 46 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 138 | 37.144 | -121.9748 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0005237 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1795736 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA 1107 | 83371107 | TRANSFORMER | 315528526605 | 20230103 | 2158 | 20230104 | 1429 | 1912116 | 991 | Transformer only | Environmental/External | Water | 1 | 991 | 37.2206 | -122.0376 | No | Clear;32-90 F | Transformer | Arcing | 23-0005474 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1795955 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1109 | 83371109 | TRANSFORMER | 315732028714 | 20230103 | 2315 | 20230104 | 955 | 1912140 | 640 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 10240 | 37.2794 | -121.9681 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on object | 23-0005496 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1795978 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WHISMAN-1108 | 83631108 | RECLOSER | LM34 | 20230104 | 821 | 20230104 | 1231 | 1912650 | 250 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 1060 | 208714 | 37.4016 | -122.0797 | Yes | Clear;32-90F | Conductor- Overhead | Burned/flashed | 23-0005609 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | No | No | 1796054 | 0 | Non-EPSS | N | 2023 | A- B & C
DE ANZA | DE ANZA | WOLFE-1113 | 83671113 | FUSE | 22941 | 20230104 | 831 | 20230104 | 1035 | 1912709 | 124 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 158 | 19592 | 37.3604 | -122.0402 | Yes | Clear;32-90F |  |  | 23-0005687 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796104 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | HICKS 1116 | 83431116 | FUSE | 645 | 20230104 | 944 | 20230104 | 1112 | 1913376 | 88 | Distribution Circuit | Vegetation | Tree - branch fell on line | 203 | 17844 | 37.2362 | -121.9195 | Yes | Clear;32-90F | Fuse | Failed/Faulted | 23-0005780 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796182 | 1 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1108 | 83771108 | FUSE | 698691 | 20230104 | 1033 | 20230104 | 1841 | 1913289 | 488 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 13664 | 37.2494 | -121.9417 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0005815 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796210 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | RECLOSER | 60118 | 20230104 | 1113 | 20230106 | 923 | 1914399 | 2297 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2150 | 1350359 | 37.1247 | -121.9353 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0006051 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796386 | 0 | EPSS Ckt | N | 2023 | SGF
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | JUMPER | 4463 | 20230104 | 1113 | 20230106 | 2009 | 1924673 | 3416 | Distribution Circuit | Equipment Failure/Involved | Overhead | 130 | 444080 | 37.107 | -121.9474 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008221 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798284 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 17431 | 20230104 | 1115 | 20230113 | 1555 | 1923596 | 13240 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 174288 | 37.1103 | -121.9511 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0006051 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798019 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | RECLOSER | 60116 | 20230104 | 1128 | 20230108 | 1354 | 1913522 | 4180 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1716 | 2503417 | 37.1735 | -121.9928 | Yes | Clear;32-90F | Pole-Wood | On Ground | 23-0005849 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796235 | 0 | EPSS Ckt | N | 2023 | B & C
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | FUSE | 957387 | 20230104 | 1128 | 20230105 | 1054 | 1919481 | 1406 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 33744 | 37.1322 | -121.9999 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006790 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1797091 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1111 | 83421111 | OCB | 1111/2 | 20230104 | 1130 | 20230104 | 1745 | 1912860 | 375 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1726 | 139874 | 37.3972 | -122.01 | Yes | Clear;32-90F | Crossarm- Wood | Broken | 23-0005831 | OH | Sus | 35419593 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1796225 | 0 | Non-EPSS | N | 2023 | NONE
DE ANZA | DE ANZA | EL PATIO-1108 | 82921108 | OCB | 1108/2 | 20230104 | 1253 | 20230104 | 1525 | 1913878 | 152 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2131 | 323522 | 37.2915 | -121.9357 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0005939 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796296 | 0 | Non-EPSS | N | 2023 | A & C PHASE TIME OC
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 21297 | 20230104 | 1331 | 20230104 | 1816 | 1914097 | 285 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 11115 | 37.1984 | -122.0115 | Yes | Clear;32-90F |  |  | 23-0006217 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796524 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING 1110 | 83481110 | RECLOSER | 60094 | 20230104 | 1352 | 20230104 | 1520 | 1914280 | 88 | Distribution Circuit | Vegetation | Tree - branch fell on line | 271 | 23848 | 37.2574 | -122.1202 | Yes | Clear;32-90F | Recloser | Normal | 23-0006020 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796364 | 0 | EPSS Ckt | N | 2023 | A & B PH
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | OCB | 1106/2 | 20230104 | 1359 | 20230105 | 1543 | 1916532 | 1544 | Distribution Circuit | Vegetation | Tree - fell into line | 1335 | 583818 | 37.2264 | -121.9771 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006384 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796681 | 0 | EPSS Ckt | N | 2023 | C & GRD (TIME 51 & SET A)
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | RECLOSER | 622226 | 20230104 | 1359 | 20230106 | 1200 | 1917820 | 2761 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 60 | 165660 | 37.1941 | -122.0219 | Yes | Clear;32-90F |  |  | 23-0006516 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1796813 | 0 | EPSS Ckt | N | 2023 | NONE
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 32117 | 20230104 | 1359 | 20230106 | 1754 | 1919049 | 3115 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 74760 | 37.1572 | -121.9855 | Yes | Clear;32-90F | Conductor- Overhead | Contaminated | 23-0006703 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1797004 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | FUSE | 6755 | 20230104 | 1425 | 20230106 | 1833 | 1914467 | 3128 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 34712 | 37.2516 | -122.0206 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006466 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1796763 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA 1103 | 83371103 | OCB | 1103/2 | 20230104 | 1431 | 20230104 | 1625 | 1914536 | 114 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1702 | 94060 | 37.281 | -122.0157 | Yes | Clear;32-90F | Conductor- Overhead | Contaminated | 23-0006088 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796414 | 0 | EPSS Ckt | N | 2023 | NOT SHOWN
DE ANZA | DE ANZA | LAWRENCE-1104 | 83421104 | OCB | 1104/2 | 20230104 | 1433 | 20230104 | 1931 | 1913491 | 298 | Distribution Circuit | Equipment Failure/Involved | Overhead | 168 | 50064 | 37.3972 | -122.0102 | Yes | Clear;32-90F | Crossarm- Wood | Broken | 23-0006048 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1796384 | 0 | Non-EPSS | N | 2023 | NONE
DE ANZA | DE ANZA | HICKS-1116 | 83431116 | FUSE | 18667 | 20230104 | 1453 | 20230107 | 359 | 1921535 | 3666 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 63576 | 37.2359 | -121.9402 | Yes | Clear;32-90 F |  |  | 23-0008655 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798547 | 1 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | TRANSFORMER | C4771 | 20230104 | 1459 | 20230109 | 105 | 1914765 | 6366 | Transformer only | Equipment Failure/Involved | Underground | 4 | 25464 | 37.3577 | -122.1022 | Yes | Clear;32-90 F | Secondary | Deteriorated | 23-0008819 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798678 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING 1108 | 83481108 | RECLOSER | LM42 | 20230104 | 1511 | 20230105 | 1232 | 1915186 | 1281 | Distribution Circuit | Vegetation | Tree - grew into line | 991 | 1269471 | 37.3509 | -122.0789 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006356 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796655 | 0 | EPSS Ckt | N | 2023 | A & C
DE ANZA | DE ANZA | MOUNTAIN VIEW-1111 | 82031111 | OCB | 1111/2 | 20230104 | 1516 | 20230104 | 1632 | 1914759 | 76 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 1592 | 96992 | 37.3826 | -122.0696 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006118 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796440 | 0 | Non-EPSS | N | 2023 | A & B (INST OC 50)
DE ANZA | DE ANZA | LOS ALTOS-1106 | 82241106 | FUSE | 5351 | 20230104 | 1524 | 20230107 | 929 | 1920276 | 3965 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 55372 | 37.3824 | -122.1321 | Yes | Clear;32-90F | Conductor- Overhead | On Ground | 23-0006924 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1797224 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOYOLA-1101 | 82161101 | JUMPER | SINGLE PHASE DOWN IRO 727 VIOLA | 20230104 | 1524 | 20230106 | 1630 | 1919107 | 2946 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 41244 | 37.3695 | -122.1095 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006716 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | Yes | No | 1797018 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | TRANSFORMER | 315584128664 | 20230104 | 1535 | 20230106 | 1143 | 1914857 | 2648 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 23832 | 37.2773 | -122.0187 | Yes | Clear;32-90F | Secondary | Arcing | 23-0008154 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1798243 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MENLO-1103 | 24131103 | RECLOSER | 866118 | 20230104 | 1543 | 20230105 | 504 | 1914903 | 801 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 157 | 125757 | 37.3756 | -122.1668 | Yes | Clear;32-90F |  |  | 23-0006148 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796467 | 0 | EPSS Ckt | N | 2023 | A & B
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | SWITCH | 25979 | 20230104 | 1551 | 20230105 | 653 | 1914980 | 899 | Distribution Circuit | Vegetation | Tree - grew into line | 179 | 87605 | 37.2542 | -122.04 | Yes | Clear;32-90F | Switch (OH) | Normal | 23-0006165 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1796482 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1109 | 83481109 | TRANSFORMER | 315508529808 | 20230104 | 1552 | 20230105 | 1622 | 1917437 | 1470 | Transformer only | Vegetation | Tree - fell into line | 9 | 13230 | 37.3083 | -122.0453 | Yes | Clear;32-90 F | Transformer | Broken | 23-0006368 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1796754 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | HICKS-1116 | 83431116 | FUSE | 18669 | 20230104 | 1637 | 20230105 | 1406 | 1915371 | 1289 | Distribution Circuit | Equipment Failure/Involved | Overhead | 47 | 60583 | 37.2322 | -121.9494 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006533 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796832 | 1 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | FUSE | 7939 | 20230104 | 1733 | 20230106 | 1546 | 1924002 | 2773 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 8319 | 37.2202 | -122.0767 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0008029 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1798160 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | RECLOSER | 991992 | 20230104 | 1746 | 20230107 | 1924 | 1916308 | 4418 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 229736 | 37.1894 | -122.0309 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006344 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796642 | 0 | EPSS Ckt | N | 2023 | A- C & G
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | JUMPER | OJS @ SS OF CGC #3803 | 20230104 | 1750 | 20230109 | 1653 | 1924842 | 7143 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 21429 | 37.1442 | -121.9837 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0008311 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1798334 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING 1109 | 83481109 | OCB | 1109/2 | 20230104 | 1752 | 20230105 | 1727 | 1916428 | 1415 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3981 | 687150 | 37.3358 | -122.043 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006368 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796667 | 0 | EPSS Ckt | N | 2023 | PHASE T OC
DE ANZA | DE ANZA | STELLING-1109 | 83481109 | TRANSFORMER | 315470730003 | 20230104 | 1752 | 20230106 | 1823 | 1917954 | 2911 | Transformer only | Environmental/External | Flood/Erosion | 4 | 11644 | 37.3135 | -122.0587 | Yes | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0006368 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796829 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1109 | 83481109 | FUSE | 31885 | 20230104 | 1752 | 20230108 | 1715 | 1919727 | 5723 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 11446 | 37.2857 | -122.0517 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0006368 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797135 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1114 | 82031114 | RECLOSER | LM12 | 20230104 | 1756 | 20230104 | 2226 | 1916455 | 270 | Distribution Circuit | Vegetation | Tree - bark fell into line | 152 | 41040 | 37.3667 | -122.0788 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006361 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796660 | 0 | Non-EPSS | N | 2023 | A & B
DE ANZA | DE ANZA | WHISMAN-1108 | 83631108 | JUMPER | #3 PHASE N/E OF 29369 | 20230104 | 1756 | 20230105 | 1903 | 1921972 | 1507 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1060 | 1131954 | 37.403 | -122.0828 | Yes | Clear;32-90F | Jumper | Burned Open | 23-0007338 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1797595 | 1 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1106 | 82031106 | FUSE | 341153 | 20230104 | 1757 | 20230104 | 2043 | 1916548 | 166 | Distribution Circuit | Equipment Failure/Involved | Overhead | 116 | 19256 | 37.3861 | -122.0856 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0006561 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796859 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1107 | 82031107 | TRANSFORMER | 315393431609 | 20230104 | 1757 | 20230105 | 1955 | 1916497 | 1558 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 6232 | 37.3573 | -122.0861 | Yes | Clear;32-90F | Connector or Splice (OH) | Broken- wire on object | 23-0007804 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797967 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1105 | 83371105 | FUSE | 8961 | 20230104 | 1758 | 20230106 | 1410 | 1916562 | 2652 | Distribution Circuit | Vegetation | Tree - fell into line | 505 | 45628 | 37.2798 | -122.0382 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0007860 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798024 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1101 | 82161101 | OCB | 1101/2 | 20230104 | 1759 | 20230105 | 413 | 1916582 | 231 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2099 | 360429 | 37.361 | -122.0992 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006375 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796673 | 0 | Non-EPSS | N | 2023 | PH OC
DE ANZA | DE ANZA | BRITTON-1110 | 83611110 | FUSE | 18431 | 20230104 | 1803 | 20230105 | 1600 | 1916591 | 1317 | Distribution Circuit | Vegetation | Tree - fell into line | 194 | 213882 | 37.3558 | -122.0139 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0007008 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1797311 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS 1101 | 82021101 | FUSE | 30941 | 20230104 | 1808 | 20230107 | 1019 | 1926275 | 3851 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 30808 | 37.2062 | -121.9511 | Yes | Clear;32-90 F |  |  | 23-0008711 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798595 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | BRITTON-1110 | 83611110 | FUSE | 18425 | 20230104 | 1812 | 20230105 | 1356 | 1916699 | 1184 | Distribution Circuit | Vegetation | Tree - branch fell on line | 269 | 318260 | 37.3622 | -122.0141 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0007508 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797727 | 1 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA 1106 | 83371106 | RECLOSER | 408318 | 20230104 | 1812 | 20230105 | 2307 | 1916758 | 1735 | Distribution Circuit | Vegetation | Tree - fell into line | 1008 | 994022 | 37.2474 | -122.0138 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0006553 | OH | Sus | 35419593 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796851 | 0 | EPSS Ckt | N | 2023 | A & C TIME
DE ANZA | DE ANZA | LAWRENCE-1113 | 83421113 | FUSE | 67447 | 20230104 | 1821 | 20230106 | 1710 | 1923920 | 2809 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 10 | 21412 | 37.3976 | -122.0226 | Yes | Clear;32-90F | Pothead(Riser Termination) | Broken | 23-0007999 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1798130 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA 1102 | 83771102 | FUSE | 621 | 20230104 | 1821 | 20230107 | 1318 | 1916821 | 4017 | Distribution Circuit | Vegetation | Tree - fell into line | 209 | 360642 | 37.2406 | -121.9645 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0007784 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797952 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | HICKS 1115 | 83431115 | TRANSFORMER | 315797427200 | 20230104 | 1824 | 20230105 | 2310 | 1916905 | 1726 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 10356 | 37.2379 | -121.9447 | Yes | Clear;32-90F | Fuse | Failed/Faulted | 23-0008028 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798159 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | RECLOSER | 725939 | 20230104 | 1850 | 20230105 | 2222 | 1921020 | 1652 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 39648 | 37.3541 | -122.1596 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0007616 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1797823 | 0 | EPSS Ckt | N | 2023 | A-B
DE ANZA | DE ANZA | LAWRENCE-1112 | 83421112 | TRANSFORMER | 315595632768 | 20230104 | 1918 | 20230106 | 1200 | 1917549 | 2442 | Transformer only | Vegetation | Tree - branch fell on line | 12 | 29304 | 37.3904 | -122.0171 | Yes | Clear;32-90F | Secondary | Bent or Twisted | 23-0008255 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798300 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1112 | 83421112 | TRANSFORMER | 315598132798 | 20230104 | 1920 | 20230106 | 1119 | 1917574 | 2399 | Transformer only | Vegetation | Tree - palm frond fell into line | 20 | 47980 | 37.3912 | -122.0162 | Yes | Clear;32-90 F | Secondary | Together | 23-0008013 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798146 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | FUSE | 22487 | 20230104 | 2103 | 20230106 | 2204 | 1918616 | 2941 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 73525 | 37.2495 | -122.0394 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008041 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798172 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1109 | 83371109 | FUSE | 31249 | 20230104 | 2111 | 20230105 | 2027 | 1918762 | 1396 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 18148 | 37.2791 | -121.9629 | Yes | Clear;32-90F |  |  | 23-0007937 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1798073 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1107 | 83481107 | FUSE | 29911 | 20230104 | 2121 | 20230104 | 2251 | 1918777 | 90 | Distribution Circuit | Vegetation | Tree - branch fell on line | 119 | 10710 | 37.3075 | -122.0337 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006799 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1797100 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1105 | 83671105 | TRANSFORMER | 315605630063 | 20230104 | 2125 | 20230105 | 1328 | 1916709 | 963 | Transformer only | Vegetation | Tree - fell into line | 13 | 12519 | 37.3165 | -122.0117 | Yes | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0006730 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797032 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | FUSE | 15735 | 20230104 | 2131 | 20230106 | 1647 | 1924582 | 2596 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 12980 | 37.2231 | -122.0898 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006688 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798267 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | FUSE | 677317 | 20230104 | 2131 | 20230109 | 1402 | 1925191 | 6751 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 77012 | 37.2037 | -122.0315 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008443 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1798389 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | JUMPER | JUMPERS 2/P/N OF 132576 | 20230104 | 2131 | 20230106 | 2040 | 1925368 | 2829 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5658 | 37.2068 | -122.0503 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008499 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1798427 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WOLFE-1113 | 83671113 | FUSE | 2383 | 20230104 | 2131 | 20230108 | 1645 | 1918888 | 5474 | Distribution Circuit | Equipment Failure/Involved | Overhead | 119 | 101961 | 37.3485 | -122.0506 | Yes | Clear;32-90F | Crossarm- Wood | Broken | 23-0006933 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797234 | 1 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1106 | 82031106 | FUSE | 341153 | 20230104 | 2132 | 20230105 | 1657 | 1918927 | 1165 | Distribution Circuit | Equipment Failure/Involved | Overhead | 116 | 135140 | 37.3861 | -122.0856 | Yes | Clear;32-90F | Conductor- Overhead | Arcing | 23-0006828 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1797130 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1108 | 82031108 | RECLOSER | LV12 | 20230104 | 2132 | 20230105 | 1411 | 1918912 | 838 | Distribution Circuit | Vegetation | Tree - fell into line | 2069 | 1660233 | 37.3739 | -122.0477 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006714 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797016 | 0 | Non-EPSS | N | 2023 | A PHASE & GRD
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | RECLOSER | 60094 | 20230104 | 2133 | 20230106 | 1546 | 1918881 | 2486 | Distribution Circuit | Vegetation | Tree - fell into line | 282 | 616298 | 37.2574 | -122.1202 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006688 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796989 | 0 | EPSS Ckt | N | 2023 | C PH GRD
DE ANZA | DE ANZA | STELLING-1108 | 83481108 | RECLOSER | LL08 | 20230104 | 2135 | 20230105 | 1621 | 1918963 | 1126 | Distribution Circuit | Vegetation | Tree - bark fell into line | 444 | 282481 | 37.3502 | -122.075 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0006697 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796998 | 0 | EPSS Ckt | N | 2023 | A PHASE & GRD
DE ANZA | DE ANZA | MOUNTAIN VIEW-1105 | 82031105 | OCB | 1105/2 | 20230104 | 2138 | 20230105 | 1324 | 1919045 | 946 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1810 | 558874 | 37.3826 | -122.0697 | Yes | Clear;32-90F | Pothead(Riser Termination) | Burned/flashed | 23-0006709 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1797011 | 0 | Non-EPSS | N | 2023 | A/C PH- GRD & TIMED OC TRGTS
DE ANZA | DE ANZA | STELLING-1109 | 83481109 | FUSE | 955 | 20230104 | 2141 | 20230105 | 1946 | 1919012 | 1325 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 39750 | 37.3038 | -122.0482 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0008012 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798145 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1104 | 82241104 | FUSE | 31135 | 20230104 | 2146 | 20230107 | 1328 | 1919069 | 3822 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 19980 | 37.38 | -122.1075 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0007946 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798083 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1111 | 83481111 | TRANSFORMER | 315433730865 | 20230104 | 2152 | 20230106 | 814 | 1919127 | 2062 | Transformer only | Vegetation | Tree - branch fell on line | 8 | 16496 | 37.3374 | -122.0715 | Yes | Heavy Rain-Clear;32-90 F | Transformer (OH) | Normal | 23-0008100 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798204 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1105 | 83371105 | FUSE | 3837 | 20230104 | 2159 | 20230106 | 145 | 1919172 | 1666 | Distribution Circuit | Vegetation | Tree - branch fell on line | 258 | 55878 | 37.2609 | -122.0542 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0008055 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798182 | 1 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WHISMAN-1106 | 83631106 | TRANSFORMER | 315367633570 | 20230104 | 2205 | 20230106 | 1315 | 1923539 | 2350 | Transformer only | Vegetation | Tree - grew into line | 5 | 11750 | 37.411 | -122.096 | Yes | Clear;32-90F | Secondary | Arcing | 23-0007836 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798000 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1109 | 82031109 | FUSE | 23181 | 20230104 | 2240 | 20230105 | 2000 | 1919492 | 1280 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 39680 | 37.3586 | -122.0777 | Yes | Clear;32-90F |  |  | 23-0007893 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1798052 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1108 | 83481108 | TRANSFORMER | 315419531349 | 20230104 | 2243 | 20230105 | 1750 | 1914754 | 1147 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 8029 | 37.3508 | -122.0769 | Yes | Clear;32-90 F | Crossarm- Wood | Broken | 23-0006818 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797120 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA 1102 | 82161102 | OCB | 1102/2 | 20230104 | 2246 | 20230105 | 14 | 1916443 | 88 | Distribution Circuit | Vegetation | Tree - fell into line | 2860 | 251680 | 37.361 | -122.0992 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006800 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1797101 | 0 | EPSS Ckt | N | 2023 | PRIM RLY PH TIME
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 4451 | 20230105 | 40 | 20230105 | 1500 | 1921734 | 860 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 24080 | 37.1364 | -121.9687 | Yes | Clear;32-90F |  |  | 23-0007583 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797793 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA 1105 | 83371105 | OTHER | WIRE DOWN LD SIDE OF 257207 | 20230105 | 405 | 20230106 | 1612 | 1920563 | 2167 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 76439 | 37.2481 | -122.0714 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006975 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1797278 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1108 | 83771108 | TRANSFORMER | 315770727531 | 20230105 | 428 | 20230107 | 2340 | 1920577 | 4032 | Transformer only | Animal | Squirrel | 9 | 36288 | 37.2471 | -121.9541 | Yes | Clear;32-90F | Secondary | Broken | 23-0009433 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1799266 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 4435 | 20230105 | 444 | 20230108 | 1623 | 1924107 | 5019 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 147940 | 37.1664 | -121.9895 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0008068 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798191 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | TRANSFORMER | 315172031940 | 20230105 | 857 | 20230107 | 1223 | 1921317 | 3086 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 3086 | 37.3653 | -122.1626 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0008204 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798276 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1103 | 83771103 | FUSE | 8175 | 20230105 | 940 | 20230107 | 1358 | 1921484 | 3138 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 53346 | 37.2533 | -121.9678 | Yes | Clear;32-90 F | Fuse | Failed/Faulted | 23-0008773 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | No | No | 1798645 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1104 | 82241104 | TRANSFORMER | 315331832304 | 20230105 | 955 | 20230105 | 1020 | 1919458 | 25 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 125 | 37.3761 | -122.1072 | Yes | Clear;32-90F | Secondary | Deteriorated | 23-0007184 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1797464 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 31297 | 20230105 | 1529 | 20230106 | 2107 | 1922957 | 1778 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 30226 | 37.139 | -121.9749 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008021 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1798153 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING 1111 | 83481111 | FUSE | 29819 | 20230105 | 1711 | 20230107 | 1429 | 1923360 | 2718 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 30412 | 37.3419 | -122.0856 | Yes | Clear;32-90F | Secondary | Broken- wire on ground | 23-0007775 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1797944 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1104 | 82241104 | TRANSFORMER | 315320232316 | 20230105 | 1729 | 20230106 | 943 | 1923393 | 974 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 1948 | 37.3764 | -122.1117 | Yes | Clear;32-90F | Fuse | Burned Open | 23-0008147 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798237 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1108 | 83481108 | RECLOSER | LM42 | 20230105 | 1753 | 20230105 | 2115 | 1923453 | 202 | Distribution Circuit | Company Initiated | Other Circuits | 991 | 77242 | 37.3509 | -122.0789 | Yes | Clear;32-90F |  |  | 23-0007653 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1797978 | 0 | EPSS Ckt | N | 2023 | NONE
DE ANZA | DE ANZA | SARATOGA-1113 | 83371113 | TRANSFORMER | 315586029276 | 20230105 | 1923 | 20230108 | 1306 | 1923732 | 3943 | Transformer only | Vegetation | Tree - grew into line | 14 | 55202 | 37.2942 | -122.0183 | Yes | Clear;32-90 F | Transformer | Normal | 23-0008831 | OH | Sus | 35419593 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798693 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WHISMAN-1108 | 83631108 | TRANSFORMER | 315390033400 | 20230105 | 1923 | 20230108 | 1231 | 1923728 | 3908 | Transformer only | Equipment Failure/Involved | Electrical Overload | 6 | 23448 | 37.4072 | -122.088 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0007901 | OH | Sus | 35419593 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1798055 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1103 | 82241103 | FUSE | 4773 | 20230105 | 2341 | 20230106 | 115 | 1923227 | 94 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 2632 | 37.3855 | -122.1056 | Yes | Clear;32-90F | Secondary | Arcing | 23-0008035 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1798166 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | RECLOSER | 568350 | 20230106 | 0 | 20230106 | 1107 | 1920568 | 650 | Distribution Circuit | Vegetation | Tree - fell into line | 265 | 175430 | 37.3221 | -122.0795 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008038 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798169 | 0 | EPSS Ckt | N | 2023 | B PH INST
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | FUSE | 18353 | 20230106 | 0 | 20230108 | 1417 | 1924611 | 3737 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 37370 | 37.2779 | -122.1119 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006688 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798270 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1104 | 82241104 | TRANSFORMER | 315319232583 | 20230106 | 101 | 20230107 | 1146 | 1924053 | 2085 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 8340 | 37.3842 | -122.1118 | No | Clear;32-90 F | Service conductor | Broken | 23-0008780 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1798649 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1105 | 83371105 | FUSE | 4997 | 20230106 | 205 | 20230107 | 1112 | 1924068 | 1987 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 156 | 306660 | 37.2646 | -122.0535 | No | Clear;32-90 F |  |  | 23-0008553 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1798477 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WHISMAN-1106 | 83631106 | TRANSFORMER | 315366733540 | 20230106 | 854 | 20230107 | 1532 | 1924313 | 1838 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 16542 | 37.4105 | -122.0965 | No | Clear;32-90F | Secondary | Normal | 23-0008120 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1798219 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1111 | 83481111 | TRANSFORMER | 315440030891 | 20230106 | 1130 | 20230109 | 817 | 1924685 | 4127 | Transformer only | Vegetation | Tree - branch fell on line | 7 | 28889 | 37.338 | -122.0694 | No | Clear;32-90 F | Transformer | Broken | 23-0008340 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798346 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WHISMAN-1106 | 83631106 | JUMPER | OJ 1 P/W/O 19379 | 20230106 | 1208 | 20230106 | 1940 | s1798362 | 452 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1808 | 37.4194 | -122.1004 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 23-0008324 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | Yes | No | 1798362 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 23009 | 20230106 | 2056 | 20230108 | 1513 | 1925684 | 2537 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 197886 | 37.1673 | -122.0363 | No | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0008613 | OH | Sus | 35419593 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1798532 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 5165 | 20230106 | 2056 | 20230108 | 1527 | 1925840 | 2551 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 7653 | 37.1703 | -122.0522 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008630 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798536 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1103 | 83481103 | SWITCH | 25953 | 20230106 | 2110 | 20230106 | 2316 | 1925697 | 126 | Distribution Circuit | Equipment Failure/Involved | Overhead | 165 | 18837 | 37.324 | -122.0195 | No | Clear;32-90 F | Insulator | Broken | 23-0008567 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1798527 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 5617 | 20230106 | 2117 | 20230114 | 1542 | 1925704 | 11185 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 134220 | 37.1591 | -122.0188 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0008799 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798661 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1101 | 82021101 | FUSE | 6643 | 20230107 | 725 | 20230107 | 1427 | s1798687 | 422 | Distribution Circuit | Animal | Squirrel | 60 | 25320 | 37.2273 | -121.9718 | Yes | Clear;32-90 F | Fuse | Burned Open | 23-0008826 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798687 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1107 | 83481107 | TRANSFORMER | 315577029684 | 20230107 | 741 | 20230107 | 1600 | 1926944 | 499 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 1183 | 37.3054 | -122.0219 | Yes | Clear;32-90 F | Secondary | Broken | 23-0008869 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798727 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | TRANSFORMER | T9393 | 20230107 | 802 | 20230108 | 1403 | 1918348 | 1801 | Transformer only | Equipment Failure/Involved | Underground | 1 | 1801 | 37.2206 | -122.0419 | Yes | Clear;32-90 F | Transformer | Burned Open | 23-0008678 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798562 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WOLFE-1104 | 83671104 | TRANSFORMER | 315621529913 | 20230107 | 1054 | 20230108 | 2340 | 1917023 | 2206 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 22060 | 37.3125 | -122.0062 | Yes | Clear;32-90 F | Secondary | Broken | 23-0008732 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1798615 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 21117 | 20230107 | 1057 | 20230108 | 1023 | 1926419 | 1406 | Distribution Circuit | Equipment Failure/Involved | Overhead | 64 | 75954 | 37.1083 | -121.8333 | Yes | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0009028 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1798855 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | FUSE | 29131 | 20230107 | 1412 | 20230107 | 1725 | 1927380 | 193 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 4825 | 37.2449 | -122.0058 | Yes | Clear;32-90 F |  |  | 23-0008967 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1798799 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS 1102 | 82021102 | TRANSFORMER | 315690827046 | 20230107 | 1527 | 20230108 | 2053 | 1926973 | 1766 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 5298 | 37.2335 | -121.9813 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0009304 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1799136 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1107 | 82031107 | FUSE | 16019 | 20230107 | 1533 | 20230107 | 1606 | 1926982 | 33 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 51 | 1683 | 37.365 | -122.0864 | Yes | Clear;32-90 F |  |  | 23-0008890 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1798742 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1106 | 82031106 | FUSE | 341153 | 20230107 | 1537 | 20230107 | 1652 | 1926993 | 75 | Distribution Circuit | Equipment Failure/Involved | Overhead | 116 | 8700 | 37.3861 | -122.0856 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0008931 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1798770 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WHISMAN-1106 | 83631106 | FUSE | 11145 | 20230107 | 1537 | 20230107 | 1700 | 1927165 | 83 | Distribution Circuit | Vegetation | Tree - branch fell on line | 357 | 29631 | 37.4138 | -122.0975 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0008913 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1798760 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1106 | 82241106 | FUSE | 30351 | 20230107 | 1731 | 20230107 | 1925 | 1927344 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 684 | 37.3927 | -122.1479 | Yes | Clear;32-90 F |  |  | 23-0009044 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1798873 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | FUSE | 1809 | 20230107 | 1842 | 20230108 | 2257 | 1927639 | 1695 | Distribution Circuit | Equipment Failure/Involved | Underground | 14 | 23622 | 37.3651 | -122.1259 | Yes | Clear;32-90 F | Transformer (UG) | Burned/flashed | 23-0009065 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798894 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1110 | 82031110 | SWITCH | 3369 | 20230107 | 1918 | 20230107 | 2022 | 1927771 | 64 | Distribution Circuit | Equipment Failure/Involved | Overhead | 444 | 19516 | 37.3663 | -122.0525 | Yes | Clear;32-90 F | Crossarm- Wood | Broken | 23-0009036 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1798863 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1104 | 83671104 | RECLOSER | LC28 | 20230107 | 1945 | 20230107 | 1955 | 1927937 | 10 | Distribution Circuit | Vegetation | Tree - branch fell on line | 934 | 9340 | 37.3224 | -122.0043 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0009054 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1798883 | 0 | Non-EPSS | N | 2023 | N/A
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 3205 | 20230107 | 2048 | 20230109 | 1908 | 1928047 | 2780 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 13900 | 37.1044 | -121.8906 | Yes | Clear;32-90F | Cutout- fuse holder | Broken | 23-0011411 | OH | Sus | 35419595 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801176 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MENLO-1103 | 24131103 | FUSE | 731 | 20230107 | 2130 | 20230108 | 1537 | 1928124 | 1087 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 3261 | 37.3692 | -122.1695 | Yes | Clear;32-90F |  |  | 23-0010269 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1800118 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1108 | 83771108 | FUSE | 32071 | 20230107 | 2211 | 20230108 | 49 | 1928231 | 158 | Distribution Circuit | Vegetation | Tree - branch fell on line | 57 | 9006 | 37.2424 | -121.9496 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0009521 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1799353 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1111 | 82031111 | TRANSFORMER | 315466132476 | 20230107 | 2235 | 20230109 | 823 | 1928089 | 2028 | Transformer only | Vegetation | Tree - fell into line | 25 | 50700 | 37.3816 | -122.0612 | Yes | Clear;32-90 F | Transformer | Arcing | 23-0009282 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1799113 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | FUSE | 29131 | 20230108 | 26 | 20230108 | 148 | 1930885 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 2050 | 37.2449 | -122.0058 | Yes | Clear;32-90F |  |  | 23-0009625 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1799457 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | RECLOSER | 725939 | 20230108 | 1244 | 20230108 | 1304 | 1933456 | 20 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 480 | 37.3541 | -122.1596 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0010141 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1799990 | 0 | EPSS Ckt | N | 2023 | NONE
DE ANZA | DE ANZA | MOUNTAIN VIEW-1103 | 82031103 | FUSE | 31387 | 20230108 | 1319 | 20230108 | 1547 | 1933632 | 148 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 2072 | 37.3868 | -122.0633 | Yes | Clear;32-90F |  |  | 23-0010274 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1800122 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1113 | 83371113 | TRANSFORMER | 315586029276 | 20230108 | 1546 | 20230108 | 1941 | 1933654 | 235 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 3290 | 37.2942 | -122.0183 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0010419 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1800265 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOYOLA-0403 | 82160403 | SWITCH | 12583 | 20230108 | 1754 | 20230108 | 1856 | 1934296 | 62 | Distribution Circuit | Vegetation | Tree - branch fell on line | 155 | 9610 | 37.3698 | -122.0959 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0010378 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1800227 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOYOLA-0403 | 82160403 | FUSE | 46367 | 20230108 | 1754 | 20230108 | 2032 | 1934577 | 158 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 4424 | 37.3698 | -122.0937 | Yes | Clear;32-90F |  |  | 23-0010506 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1800356 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1104 | 83481104 | TRANSFORMER | 315529530266 | 20230108 | 2054 | 20230108 | 2230 | 1934775 | 96 | Transformer only | Vegetation | Tree - grew into line | 8 | 768 | 37.3209 | -122.0383 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0010487 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1800337 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1105 | 83371105 | FUSE | 4999 | 20230109 | 50 | 20230109 | 302 | 1935125 | 132 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 108 | 14256 | 37.2674 | -122.0597 | Yes | Clear;32-90F |  |  | 23-0010698 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1800556 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | RECLOSER | 31959 | 20230109 | 457 | 20230109 | 1839 | 1935712 | 822 | Distribution Circuit | Vegetation | Tree - fell into line | 162 | 41383 | 37.3608 | -122.1698 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0010847 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1800699 | 0 | EPSS Ckt | N | 2023 | N/A
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | RECLOSER | 60116 | 20230109 | 459 | 20230109 | 1438 | 1935720 | 579 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1455 | 162503 | 37.1735 | -121.9928 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0010773 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | No | No | 1800637 | 0 | EPSS Ckt | N | 2023 | A-B-C PH
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | JUMPER | 1 W/OF CGC # 2955 | 20230109 | 710 | 20230112 | 1630 | 1936404 | 4880 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 9760 | 37.1216 | -121.9541 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0011119 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1800929 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1110 | 83421110 | JUMPER | OPEN FUSES 5305 | 20230109 | 728 | 20230110 | 529 | 1939653 | 1321 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 1321 | 37.4082 | -122.0009 | Yes | Clear;32-90F | Conductor- Underground | Deteriorated | 23-0011626 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801389 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1109 | 83671109 | TRANSFORMER | 315566030136 | 20230109 | 814 | 20230109 | 1743 | 1936736 | 569 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 8535 | 37.3178 | -122.0267 | Yes | Clear;32-90F | Secondary | Normal | 23-0010876 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1800726 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 4467 | 20230109 | 838 | 20230112 | 859 | 1936393 | 4341 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 13546 | 37.1041 | -121.9333 | Yes | Clear;32-90F | Secondary | Broken- wire on object | 23-0010890 | OH | Sus | 35419595 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1800738 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | JUMPER | OJS @ 2 P N/OF CGC #5641 | 20230109 | 921 | 20230110 | 2030 | 1937327 | 2109 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 2109 | 37.1949 | -122.0251 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0011220 | OH | Sus | 35419593 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1801016 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | OTHER | WIRE DOWN 3 SPANS LOAD SIDE OF 15777 | 20230109 | 935 | 20230110 | 1754 | 1939535 | 1939 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 28133 | 37.2525 | -122.0903 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011505 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1801354 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1113 | 83371113 | TRANSFORMER | 315588629631 | 20230109 | 959 | 20230109 | 1045 | 1937446 | 46 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 736 | 37.3039 | -122.0176 | Yes | Clear;32-90F | Secondary | Normal | 23-0011004 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1800838 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1114 | 83671114 | TRANSFORMER | 315548832058 | 20230109 | 1110 | 20230109 | 1256 | 1937694 | 106 | Transformer only | Equipment Failure/Involved | Overhead | 20 | 2120 | 37.3707 | -122.0328 | Yes | Clear;32-90F | Crossarm- Wood | Broken | 23-0011068 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1800885 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1114 | 83371114 | TRANSFORMER | 315607429110 | 20230109 | 1134 | 20230109 | 1350 | 1937879 | 136 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 952 | 37.2896 | -122.0109 | Yes | Clear;32-90F | Secondary | Normal | 23-0011124 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1800933 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1103 | 83371103 | TRANSFORMER | T2580 | 20230109 | 1238 | 20230109 | 1302 | 1938125 | 24 | Transformer only | Equipment Failure/Involved | Underground | 3 | 72 | 37.2603 | -122.0471 | Yes | Clear;32-90F | Customer Equipment | Normal | 23-0011191 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1800991 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | BRITTON-1106 | 83611106 | TRANSFORMER | 315561232091 | 20230109 | 1349 | 20230110 | 2131 | 1938361 | 1902 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 19020 | 37.3715 | -122.0286 | Yes | Clear;32-90 F | Secondary | Broken | 23-0011475 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801233 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1113 | 83671113 | SWITCH | 3369 | 20230109 | 1439 | 20230109 | 1629 | 1938486 | 110 | Distribution Circuit | Equipment Failure/Involved | Overhead | 444 | 48484 | 37.3663 | -122.0525 | Yes | Clear;32-90F | Crossarm- Wood | Broken | 23-0009036 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1801099 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | BRITTON-1115 | 83611115 | SWITCH | 686152 | 20230109 | 1646 | 20230109 | 1946 | 1938922 | 180 | Distribution Circuit | Equipment Failure/Involved | Underground | 112 | 12593 | 37.386 | -121.9984 | Yes | Clear;32-90F | Transformer (UG) | Broken | 23-0011362 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1801199 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | RECLOSER | 60124 | 20230110 | 155 | 20230113 | 1301 | 1939884 | 4986 | Distribution Circuit | Vegetation | Tree - branch fell on line | 298 | 1183122 | 37.1462 | -121.9823 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0011719 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801479 | 0 | EPSS Ckt | N | 2023 | B PH GRD
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | FUSE | 32331 | 20230110 | 155 | 20230113 | 1301 | 1949148 | 4986 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 64818 | 37.1445 | -122.0037 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0014113 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1803459 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | FUSE | 19935 | 20230110 | 155 | 20230114 | 2041 | 1949150 | 6886 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 34430 | 37.144 | -121.9932 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0014116 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | Yes | No | 1803462 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | JUMPER | OJS SS OF CGC #3621 | 20230110 | 155 | 20230113 | 249 | 1949151 | 4374 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 8748 | 37.1402 | -121.9708 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0014121 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1803467 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | JUMPER | OPEN JUMPERS | 20230110 | 155 | 20230113 | 1945 | 1948252 | 5390 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 16170 | 37.1621 | -122.0126 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0013745 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1803143 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1105 | 83371105 | FUSE | 4999 | 20230110 | 201 | 20230110 | 1955 | 1940124 | 1074 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 76 | 81624 | 37.2674 | -122.0597 | Yes | Clear;32-90 F |  |  | 23-0012965 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802532 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | FUSE | 17499 | 20230110 | 203 | 20230116 | 1826 | 1952139 | 9623 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 346428 | 37.1521 | -121.9977 | Yes | Clear;32-90F | Pothead(Riser Termination) | Broken | 23-0015436 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1804318 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | FUSE | 17121 | 20230110 | 203 | 20230115 | 1500 | 1952377 | 7977 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 168345 | 37.1635 | -122.0141 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on object | 23-0015502 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1804357 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | RECLOSER | LB48 | 20230110 | 203 | 20230116 | 2226 | 1939974 | 9863 | Distribution Circuit | Equipment Failure/Involved | Overhead | 413 | 1302574 | 37.19 | -121.9942 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0011731 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | No | No | 1801491 | 0 | EPSS Ckt | N | 2023 | NONE
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | JUMPER | OPEN JUMPERS SS 5165 | 20230110 | 203 | 20230116 | 2209 | 1952387 | 9846 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 19692 | 37.1702 | -122.0524 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015503 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1804358 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 30751 | 20230110 | 203 | 20230116 | 2209 | 1952392 | 9846 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 9846 | 37.1706 | -122.0516 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0015505 | OH | Sus | 35419595 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1804360 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | RECLOSER | 622226 | 20230110 | 205 | 20230117 | 1614 | 1945147 | 10929 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 860439 | 37.1941 | -122.0219 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012429 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | Yes | No | 1802148 | 0 | EPSS Ckt | N | 2023 | NONE
DE ANZA | DE ANZA | STELLING-1103 | 83481103 | RECLOSER | 568350 | 20230110 | 205 | 20230110 | 449 | 1940151 | 164 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 466 | 76424 | 37.3221 | -122.0795 | Yes | Clear;32-90F |  |  | 23-0011739 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801500 | 0 | Non-EPSS | N | 2023 | B- C & 51 TIME
DE ANZA | DE ANZA | STELLING-1103 | 83481103 | RECLOSER | 60094 | 20230110 | 205 | 20230112 | 1022 | -1940151 | 3377 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 271 | 915167 | 37.2574 | -122.1202 | Yes | Clear;32-90 F |  |  | 23-0011739 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801667 | 0 | Non-EPSS | N | 2023 | A & C
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | JUMPER | DDE 1 LD SIDE F 18597 | 20230110 | 206 | 20230113 | 1834 | 1945906 | 5308 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 47772 | 37.1463 | -121.9828 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012792 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802381 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 3459 | 20230110 | 206 | 20230112 | 1630 | 1949266 | 3744 | Distribution Circuit | Equipment Failure/Involved | Overhead | 157 | 587808 | 37.1288 | -121.9532 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0014225 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803576 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | JUMPER | OJ'S @ 21912 SUMMIT RD | 20230110 | 207 | 20230115 | 1450 | 1948367 | 7963 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 95544 | 37.1483 | -121.9933 | Yes | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0013769 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1803162 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1102 | 82021102 | OCB | 1102/2 | 20230110 | 208 | 20230112 | 2026 | 1940189 | 3978 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1887 | 2733582 | 37.2264 | -121.9772 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0011745 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801506 | 0 | EPSS Ckt | N | 2023 | C PHASE OC
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | OCB | 1106/2 | 20230110 | 208 | 20230112 | 1222 | 1940143 | 3494 | Distribution Circuit | Equipment Failure/Involved | Overhead | 44 | 153736 | 37.2264 | -121.9771 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0011740 | OH | Sus | 35419593 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801501 | 0 | EPSS Ckt | N | 2023 | B & C PHASE- GRD TIME OC
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 965 | 20230110 | 208 | 20230112 | 406 | 1944456 | 2998 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 11992 | 37.1669 | -121.9866 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0012188 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801951 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | RECLOSER | LB44 | 20230110 | 208 | 20230111 | 1129 | 1944872 | 2001 | Distribution Circuit | Vegetation | Tree - branch fell on line | 223 | 412730 | 37.1938 | -121.9958 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012318 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | Yes | No | 1802065 | 0 | EPSS Ckt | N | 2023 | NONE
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | OTHER | WIRE DOWN @ CGC 315712823428 | 20230110 | 208 | 20230112 | 1555 | 1949245 | 3707 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 29640 | 37.134 | -121.9698 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0014223 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1803574 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | SWITCH | 722931 | 20230110 | 208 | 20230112 | 1200 | 1949272 | 3472 | Distribution Circuit | Equipment Failure/Involved | Overhead | 93 | 322896 | 37.1615 | -121.9816 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0014227 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1803578 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | SWITCH | 26175 | 20230110 | 208 | 20230113 | 2330 | 1949273 | 5602 | Distribution Circuit | Equipment Failure/Involved | Overhead | 367 | 1771220 | 37.1546 | -121.9815 | Yes | Clear;32-90 F | Other | Broken- wire on ground | 23-0014230 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1803581 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 21073 | 20230110 | 208 | 20230112 | 1015 | 1949316 | 3367 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 50505 | 37.1636 | -121.9858 | Yes | Clear;32-90 F |  |  | 23-0014239 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1803590 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 16117 | 20230110 | 208 | 20230113 | 1540 | 1949745 | 5132 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 170751 | 37.1621 | -121.9819 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0014346 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1803662 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | JUMPER | 52322 | 20230110 | 208 | 20230114 | 1832 | 1950065 | 6744 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 276760 | 37.2229 | -121.9822 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on object | 23-0014490 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1803759 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | SWITCH | 60120 | 20230110 | 209 | 20230111 | 1726 | 1946095 | 2357 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 82 | 193274 | 37.1302 | -121.9784 | Yes | Clear;32-90 F |  |  | 23-0012865 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1802444 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | EL PATIO-1108 | 82921108 | OCB | 1108/2 | 20230110 | 209 | 20230114 | 2228 | 1940496 | 6368 | Distribution Circuit | Vegetation | Tree - fell into line | 2131 | 1976023 | 37.2915 | -121.9357 | Yes | Clear;32-90F | Conductor- Overhead | Arcing | 23-0011768 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801528 | 0 | Non-EPSS | N | 2023 | B PHASE OC
DE ANZA | DE ANZA | HICKS-1115 | 83431115 | JUMPER | JUMPERS @ 2425 APPLEY WAY | 20230110 | 210 | 20230110 | 1430 | 1943519 | 740 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 740 | 37.2447 | -121.9466 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012029 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801811 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1106 | 82241106 | RECLOSER | 60028 | 20230110 | 210 | 20230110 | 2113 | 1940409 | 1143 | Distribution Circuit | Vegetation | Tree - branch fell on line | 565 | 376691 | 37.397 | -122.1179 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011769 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801529 | 0 | Non-EPSS | N | 2023 | B PH GRD
DE ANZA | DE ANZA | LOS GATOS-1101 | 82021101 | OCB | 1101/2 | 20230110 | 210 | 20230112 | 1616 | 1940193 | 3697 | Distribution Circuit | Vegetation | Tree - fell into line | 2223 | 2488018 | 37.2264 | -121.9773 | Yes | Clear;32-90F | Crossarm- Wood | Broken | 23-0011746 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801507 | 0 | EPSS Ckt | N | 2023 | A- B- & C OC INST
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 1573 | 20230110 | 210 | 20230113 | 2146 | 1945296 | 5496 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 208560 | 37.1981 | -121.9928 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012507 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802205 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1109 | 83371109 | OCB | 1109/2 | 20230110 | 210 | 20230111 | 240 | 1940602 | 1470 | Distribution Circuit | Vegetation | Tree - fell into line | 4613 | 1886095 | 37.281 | -122.0156 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011786 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1801546 | 0 | Non-EPSS | N | 2023 | B C PHASE OC & GRD
DE ANZA | DE ANZA | HICKS-1115 | 83431115 | RECLOSER | 12494 | 20230110 | 211 | 20230110 | 1741 | 1940386 | 930 | Distribution Circuit | Vegetation | Tree - branch fell on line | 535 | 215116 | 37.2435 | -121.9378 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011777 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1801537 | 0 | EPSS Ckt | N | 2023 | A-B-C
DE ANZA | DE ANZA | LOS GATOS 1108 | 82021108 | OCB | 1108/2 | 20230110 | 211 | 20230112 | 1236 | 1940182 | 3505 | Distribution Circuit | Vegetation | Tree - fell into line | 1225 | 1487008 | 37.2264 | -121.9771 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011744 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801505 | 0 | EPSS Ckt | N | 2023 | N/A
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 967 | 20230110 | 211 | 20230110 | 1623 | 1944096 | 852 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 10224 | 37.1658 | -121.9866 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0012098 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801872 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 4435 | 20230110 | 211 | 20230114 | 1418 | 1949258 | 6487 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 220558 | 37.1664 | -121.9895 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0014224 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1803575 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1108 | 82021108 | TRANSFORMER | 100000031107 | 20230110 | 211 | 20230113 | 1937 | 1946330 | 5366 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 48294 | 37.2274 | -121.9935 | Yes | Clear;32-90 F | Secondary | Broken | 23-0012934 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1802499 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1108 | 82021108 | OTHER | WIRE DOWN 74 ELLENWOOD AVE | 20230110 | 211 | 20230111 | 2045 | 1946398 | 2554 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 33202 | 37.2286 | -121.9908 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012959 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | Yes | Yes | 1802526 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1103 | 83771103 | FUSE | 5273 | 20230110 | 211 | 20230110 | 1052 | 1942357 | 521 | Distribution Circuit | Vegetation | Tree - branch fell on line | 57 | 29697 | 37.2667 | -121.962 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011892 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | Yes | No | 1801660 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | HICKS-1114 | 83431114 | FUSE | 32315 | 20230110 | 212 | 20230112 | 1809 | 1940191 | 3837 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 180339 | 37.2479 | -121.9385 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0014371 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1803686 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1102 | 82021102 | FUSE | 4015 | 20230110 | 212 | 20230111 | 2326 | 1946642 | 2714 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 149270 | 37.23 | -121.9865 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0013055 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802610 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | OCB | 1107/2 | 20230110 | 212 | 20230111 | 1656 | 1940211 | 2324 | Distribution Circuit | Vegetation | Tree - fell into line | 1968 | 3207210 | 37.2264 | -121.9771 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0011778 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801538 | 0 | EPSS Ckt | N | 2023 | B PHASE- GRD & TIME OC
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 31779 | 20230110 | 212 | 20230112 | 2218 | 1944904 | 4086 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 53118 | 37.212 | -121.9724 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012329 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802075 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 4403 | 20230110 | 212 | 20230112 | 2059 | 1945197 | 4007 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 432756 | 37.2199 | -121.9823 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012452 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1802163 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 22965 | 20230110 | 212 | 20230114 | 1449 | 1946645 | 6517 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 421020 | 37.2162 | -121.9664 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0013058 | OH | Sus | 35419593 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1802613 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1112 | 83371112 | OCB | 1112/2 | 20230110 | 212 | 20230111 | 0 | 1940310 | 1308 | Distribution Circuit | Vegetation | Tree - fell into line | 1858 | 1383033 | 37.281 | -122.0155 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0011785 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801545 | 0 | Non-EPSS | N | 2023 | B & C PHASE OC
DE ANZA | DE ANZA | EL PATIO-1119 | 82921119 | RECLOSER | 47306 | 20230110 | 213 | 20230113 | 108 | 1940572 | 4255 | Distribution Circuit | Vegetation | Tree - fell into line | 813 | 2542219 | 37.283 | -121.9226 | Yes | Clear;32-90 F | Crossarm- Wood | Broken | 23-0011810 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1801571 | 0 | Non-EPSS | N | 2023 | N/A
DE ANZA | DE ANZA | SARATOGA-1109 | 83371109 | FUSE | 2091 | 20230110 | 213 | 20230111 | 624 | 1943391 | 1691 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 62567 | 37.2806 | -121.9898 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on object | 23-0012007 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801785 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1109 | 83371109 | FUSE | 3555 | 20230110 | 213 | 20230111 | 1939 | 1943394 | 2486 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 87010 | 37.2766 | -121.9896 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0012008 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1801786 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1109 | 83371109 | FUSE | 12955 | 20230110 | 213 | 20230110 | 2353 | 1943948 | 1300 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 33800 | 37.2809 | -121.9542 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0012073 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801850 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1103 | 83771103 | OCB | 1103/2 | 20230110 | 213 | 20230110 | 1920 | 1940242 | 1027 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4166 | 623102 | 37.2537 | -121.9661 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0011779 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | No | No | 1801539 | 0 | Non-EPSS | N | 2023 | A B C PHASE OC
DE ANZA | DE ANZA | VASONA-1108 | 83771108 | TRANSFORMER | 315767327539 | 20230110 | 213 | 20230112 | 2117 | 1940230 | 4024 | Transformer only | Vegetation | Tree - fell into line | 7 | 28168 | 37.2473 | -121.9553 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0014132 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1803479 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | EL PATIO-1109 | 82921109 | OCB | 1109/2 | 20230110 | 214 | 20230110 | 1643 | 1940520 | 869 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5276 | 4557311 | 37.2915 | -121.9357 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0011772 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801532 | 0 | Non-EPSS | N | 2023 | ABC /50
DE ANZA | DE ANZA | VASONA-1102 | 83771102 | FUSE | 621 | 20230110 | 214 | 20230111 | 1551 | 1940267 | 2257 | Distribution Circuit | Vegetation | Tree - fell into line | 209 | 331865 | 37.2406 | -121.9645 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0013070 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1802625 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | OCB | 1102/2 | 20230110 | 215 | 20230110 | 1257 | 1940561 | 642 | Distribution Circuit | Vegetation | Tree - fell into line | 3602 | 1252180 | 37.361 | -122.0992 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0011788 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801548 | 0 | EPSS Ckt | N | 2023 | PRIMARY PH GRD
DE ANZA | DE ANZA | HICKS-1116 | 83431116 | FUSE | 4399 | 20230110 | 216 | 20230112 | 1756 | 1940303 | 3820 | Distribution Circuit | Vegetation | Tree - branch fell on line | 383 | 430223 | 37.2349 | -121.9038 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012729 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1802350 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1105 | 83771105 | OCB | 1105/2/NORM | 20230110 | 216 | 20230114 | 1927 | 1940312 | 6791 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2689 | 2711364 | 37.2537 | -121.9662 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0011780 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801540 | 0 | Non-EPSS | N | 2023 | B & C PHASE
DE ANZA | DE ANZA | BRITTON-1105 | 83611105 | OCB | 1105/2 | 20230110 | 217 | 20230110 | 401 | 1940515 | 104 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2421 | 251784 | 37.3749 | -122.0166 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0011789 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801549 | 0 | Non-EPSS | N | 2023 | B & C PHASE TIME OC GRD
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | FUSE | 29131 | 20230110 | 217 | 20230111 | 434 | 1940328 | 1577 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 39425 | 37.2449 | -122.0058 | Yes | Clear;32-90F |  |  | 23-0013346 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1802898 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | EL PATIO-1117 | 82921117 | FUSE | 32743 | 20230110 | 218 | 20230111 | 224 | 1946736 | 1446 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 506 | 731676 | 37.2829 | -121.9478 | Yes | Clear;32-90F |  |  | 23-0013207 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802762 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1109 | 83371109 | JUMPER | OJ @ HARD TAP TWD 90011 | 20230110 | 218 | 20230111 | 1659 | 1943377 | 2321 | Distribution Circuit | Vegetation | Tree - fell into line | 723 | 380987 | 37.2774 | -121.9736 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0012006 | OH | Sus | 35419593 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801783 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1102 | 83771102 | FUSE | 22505 | 20230110 | 218 | 20230111 | 1206 | 1940341 | 2028 | Distribution Circuit | Vegetation | Tree - branch fell on line | 123 | 249444 | 37.2373 | -121.9779 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0013586 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1803053 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1104 | 83771104 | FUSE | 31245 | 20230110 | 218 | 20230111 | 1541 | 1940345 | 2243 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 128 | 287104 | 37.2607 | -121.9635 | Yes | Clear;32-90F |  |  | 23-0013793 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1803187 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | TRANSFORMER | 315604227516 | 20230110 | 220 | 20230113 | 1617 | 1940430 | 5157 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 25785 | 37.2458 | -122.0113 | Yes | Heavy Rain-Clear;32-90F | Secondary | Broken | 23-0015188 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1804220 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1113 | 83371113 | FUSE | 30471 | 20230110 | 220 | 20230110 | 2115 | 1940457 | 1135 | Distribution Circuit | Vegetation | Tree - branch fell on line | 56 | 63560 | 37.3089 | -122.0187 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0012971 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1802535 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1104 | 83421104 | FUSE | 2099 | 20230110 | 221 | 20230110 | 1937 | 1940444 | 1036 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 168 | 174048 | 37.3998 | -122.0073 | Yes | Clear;32-90 F |  |  | 23-0012899 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1802469 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | EL PATIO-1113 | 82921113 | FUSE | 32759 | 20230110 | 222 | 20230112 | 1759 | 1940705 | 3817 | Distribution Circuit | Vegetation | Tree - fell into line | 174 | 660933 | 37.2833 | -121.936 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012942 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802506 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1112 | 83481112 | OCB | 1112/2 | 20230110 | 222 | 20230110 | 343 | 1940595 | 81 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 283 | 22923 | 37.3358 | -122.0429 | Yes | Clear;32-90 F |  |  | 23-0011784 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801544 | 0 | Non-EPSS | N | 2023 | PH INST
DE ANZA | DE ANZA | VASONA-1101 | 83771101 | FUSE | 32999 | 20230110 | 222 | 20230111 | 1805 | 1940534 | 2383 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 21447 | 37.2583 | -121.9532 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0013414 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1802942 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1102 | 83771102 | JUMPER | OJ #1 LD SIDE OF 22507 | 20230110 | 222 | 20230110 | 2016 | 1940535 | 1074 | Distribution Circuit | Equipment Failure/Involved | Overhead | 61 | 65514 | 37.2358 | -121.9782 | Yes | Clear;32-90 F | Jumper | Burned Open | 23-0012958 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1802525 | 1 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1108 | 83771108 | FUSE | 32061 | 20230110 | 222 | 20230112 | 401 | 1949307 | 2979 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 49 | 145971 | 37.2413 | -121.9591 | Yes | Clear;32-90 F |  |  | 23-0014236 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1803587 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1106 | 82031106 | FUSE | 341153 | 20230110 | 223 | 20230110 | 1714 | 1940632 | 891 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 116 | 103356 | 37.3861 | -122.0856 | Yes | Clear;32-90 F |  |  | 23-0012830 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1802412 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1103 | 83371103 | RECLOSER | LC82 | 20230110 | 226 | 20230111 | 1853 | 1940782 | 2427 | Distribution Circuit | Vegetation | Tree - fell into line | 1603 | 1565145 | 37.2777 | -122.0259 | Yes | Clear;32-90 F | Crossarm- Wood | Broken | 23-0011811 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | No | No | 1801572 | 0 | EPSS Ckt | N | 2023 | A- B- C & GRD
DE ANZA | DE ANZA | BRITTON-1107 | 83611107 | SWITCH | 22781 | 20230110 | 227 | 20230110 | 1148 | 1941082 | 452 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 2140 | 705500 | 37.3666 | -122.0107 | Yes | Clear;32-90 F |  |  | 23-0011814 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801575 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1104 | 83771104 | TRANSFORMER | 315743728003 | 20230110 | 233 | 20230112 | 308 | 1940874 | 2915 | Transformer only | Unknown Cause | Patrol - found nothing | 7 | 20405 | 37.2597 | -121.9637 | Yes | Clear;32-90 F |  |  | 23-0014229 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1803580 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | RECLOSER | 340986 | 20230110 | 236 | 20230115 | 1420 | 1940930 | 7904 | Distribution Circuit | Vegetation | Tree - branch fell on line | 578 | 963079 | 37.24 | -121.9965 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0013028 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802584 | 0 | EPSS Ckt | N | 2023 | 50 INST
DE ANZA | DE ANZA | EL PATIO-1116 | 82921116 | FUSE | 4797 | 20230110 | 237 | 20230114 | 218 | 1945175 | 5741 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 195194 | 37.2908 | -121.9677 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015694 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1804537 | 1 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1113 | 83371113 | TRANSFORMER | 315617629629 | 20230110 | 258 | 20230111 | 1320 | 1941091 | 2062 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 28868 | 37.3039 | -122.0077 | Yes | Clear;32-90F | Fuse | Failed/Faulted | 23-0013698 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803115 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1104 | 83421104 | FUSE | 63603 | 20230110 | 304 | 20230110 | 1845 | 1940934 | 941 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 25407 | 37.4064 | -121.9888 | Yes | Clear;32-90 F | Jumper | Arcing | 23-0012875 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1802449 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA 1104 | 83371104 | FUSE | 32933 | 20230110 | 317 | 20230111 | 400 | 1946633 | 1483 | Distribution Circuit | Vegetation | Tree - bark fell into line | 5 | 7415 | 37.2595 | -121.992 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0013344 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802896 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1103 | 83771103 | TRANSFORMER | 315700728050 | 20230110 | 442 | 20230110 | 2012 | 1944145 | 930 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 7440 | 37.261 | -121.9783 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0012433 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802151 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1108 | 83371108 | OCB | 1108/2 | 20230110 | 504 | 20230110 | 1236 | 1942170 | 452 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3531 | 108811 | 37.281 | -122.0156 | Yes | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0011903 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1801673 | 0 | Non-EPSS | N | 2023 | N/A
DE ANZA | DE ANZA | VASONA-1103 | 83771103 | FUSE | 57778 | 20230110 | 532 | 20230112 | 1904 | 1942693 | 3692 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 47996 | 37.2641 | -121.9705 | Yes | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0014235 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | Yes | No | 1803586 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WHISMAN-1106 | 83631106 | OCB | 1106/2 | 20230110 | 709 | 20230110 | 822 | 1940731 | 73 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 4073 | 272081 | 37.4048 | -122.0691 | Yes | Clear;32-90 F |  |  | 23-0011979 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801759 | 0 | Non-EPSS | N | 2023 | B-C & TIME
DE ANZA | DE ANZA | SARATOGA-1111 | 83371111 | TRANSFORMER | 315696829200 | 20230110 | 732 | 20230113 | 721 | 1948102 | 4309 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 64635 | 37.2925 | -121.9803 | Yes | Heavy Rain-Clear;32-90 F | Pole-Wood | Broken | 23-0014222 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803573 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1109 | 83371109 | JUMPER | OJ AT 300087 | 20230110 | 756 | 20230112 | 203 | 1949113 | 2527 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2599 | 227545 | 37.2688 | -121.9934 | Yes | Clear;32-90 F | Jumper | Burned/flashed | 23-0014220 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1803571 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1110 | 82031110 | TRANSFORMER | 315476631942 | 20230110 | 808 | 20230110 | 906 | 1943502 | 58 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 174 | 37.3669 | -122.0576 | Yes | Clear;32-90 F | Secondary | Deteriorated | 23-0012027 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1801809 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1101 | 83771101 | FUSE | 31337 | 20230110 | 830 | 20230110 | 1606 | 1943790 | 456 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 8664 | 37.247 | -121.9612 | Yes | Clear;32-90 F | Transformer (OH) | Normal | 23-0012740 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802356 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | FUSE | 273601 | 20230110 | 1005 | 20230110 | 1434 | 1945381 | 269 | Distribution Circuit | Equipment Failure/Involved | Overhead | 161 | 43309 | 37.3565 | -122.1356 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0012540 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802232 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | EL PATIO-1118 | 82921118 | TRANSFORMER | 315858328352 | 20230110 | 1006 | 20230112 | 1806 | 1944379 | 3360 | Transformer only | Vegetation | Tree - fell into line | 10 | 33600 | 37.27 | -121.9245 | Yes | Clear;32-90 F | Secondary | Normal | 23-0014763 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803887 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1108 | 83481108 | TRANSFORMER | MTR#1009594165 | 20230110 | 1034 | 20230113 | 1029 | 1947396 | 4315 | Transformer only | Vegetation | Tree - fell into line | 8 | 34520 | 37.3473 | -122.0687 | Yes | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0014114 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1803460 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1102 | 83771102 | JUMPER | FUCO 3637 - UN-MAPPED | 20230110 | 1713 | 20230114 | 1313 | 1946073 | 5520 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 33120 | 37.2409 | -121.9822 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0016190 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1804964 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1106 | 82031106 | TRANSFORMER | 315394832615 | 20230110 | 2141 | 20230111 | 1318 | 1946650 | 937 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 24 | 22488 | 37.3851 | -122.0862 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0013286 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802839 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | EL PATIO-1118 | 82921118 | TRANSFORMER | 315841428393 | 20230110 | 2323 | 20230112 | 1453 | 1946732 | 2370 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 28440 | 37.2711 | -121.9304 | Yes | Clear;32-90 F | Fuse | Broken | 23-0014647 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803821 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | EL PATIO-1117 | 82921117 | FUSE | 46729 | 20230111 | 32 | 20230111 | 208 | 1946813 | 96 | Distribution Circuit | Vegetation | Tree - branch fell on line | 62 | 5952 | 37.2829 | -121.9489 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0013334 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802885 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1102 | 82021102 | JUMPER | 1102/2 | 20230111 | 108 | 20230111 | 207 | 1946852 | 59 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1704 | 100536 | 37.2264 | -121.9772 | No | Clear;32-90F | Jumper | Burned Open | 23-0013309 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1802862 | 1 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WOLFE-1113 | 83671113 | FUSE | 15977 | 20230111 | 149 | 20230114 | 1645 | 1947028 | 5216 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 5216 | 37.355 | -122.0415 | No | Clear;32-90F | Transformer (UG) | Failed/Faulted | 23-0013863 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803230 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1102 | 82031102 | FUSE | 483 | 20230111 | 211 | 20230113 | 519 | 1946964 | 3068 | Distribution Circuit | Equipment Failure/Involved | Overhead | 85 | 45505 | 37.3867 | -122.0727 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0013348 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1802901 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1108 | 83481108 | TRANSFORMER | 315473531068 | 20230111 | 728 | 20230112 | 1752 | 1939927 | 2064 | Transformer only | Vegetation | Tree - branch fell on line | 10 | 20640 | 37.3429 | -122.058 | No | Clear;32-90 F | Secondary | Broken | 23-0013384 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1802920 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1108 | 83481108 | TRANSFORMER | 315473531068 | 20230111 | 728 | 20230112 | 1752 | 1939927 | 2064 | Transformer only | Vegetation | Tree - branch fell on line | 10 | 20640 | 37.3429 | -122.058 | No | Clear;32-90 F | Secondary | Broken | 23-0013384 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1802920 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | EL PATIO-1112 | 82921112 | OCB | 1112/2 | 20230111 | 825 | 20230111 | 1142 | 1947158 | 139 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5052 | 861595 | 37.2915 | -121.9356 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0013396 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1802931 | 0 | Non-EPSS | N | 2023 | ABC
DE ANZA | DE ANZA | MOUNTAIN VIEW-1107 | 82031107 | TRANSFORMER | 315367431787 | 20230111 | 1034 | 20230111 | 1541 | 1947557 | 307 | Transformer only | Vegetation | Tree - grew into line | 6 | 1842 | 37.3623 | -122.0947 | No | Clear;32-90F | Secondary | Arcing | 23-0013807 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803197 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1106 | 82031106 | JUMPER | FLYING BELLS @ 837 PARK DR | 20230111 | 1051 | 20230111 | 1312 | 1947616 | 141 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 3102 | 37.3849 | -122.0857 | No | Clear;32-90F | Secondary | Broken | 23-0013617 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803075 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 677317 | 20230111 | 1129 | 20230114 | 2000 | 1947736 | 4831 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 82127 | 37.2037 | -122.0315 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0013563 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1803040 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1102 | 83771102 | TRANSFORMER | 315699027191 | 20230111 | 1249 | 20230111 | 2230 | 1947981 | 581 | Transformer only | Vegetation | Tree - fell into line | 12 | 6972 | 37.2374 | -121.9786 | No | Clear;32-90F | Conductor- Overhead | Broken | 23-0013653 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803097 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | SWITCH | 10859 | 20230111 | 1549 | 20230111 | 1818 | 1948282 | 149 | Distribution Circuit | Vegetation | Tree - fell into line | 1060 | 22233 | 37.2558 | -122.0139 | No | Clear;32-90F | Pole-Wood | Normal | 23-0013834 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1803212 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | RECLOSER | 60092 | 20230111 | 1707 | 20230112 | 730 | 1948747 | 863 | Distribution Circuit | Vegetation | Tree - fell into line | 1123 | 840181 | 37.1815 | -121.985 | No | Clear;32-90F | Crossarm- Wood | Broken | 23-0013896 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1803258 | 0 | EPSS Ckt | N | 2023 | A- B- C- PHASE OC
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 2895 | 20230111 | 1708 | 20230112 | 1937 | 1949270 | 1589 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 15890 | 37.1234 | -121.9294 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0014226 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803577 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WOLFE-1113 | 83671113 | TRANSFORMER | 315528831899 | 20230111 | 1903 | 20230112 | 1416 | 1947522 | 1153 | Transformer only | Vegetation | Tree - fell into line | 29 | 33437 | 37.3663 | -122.0401 | No | Clear;32-90 F | Secondary | Normal | 23-0013953 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1803307 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1108 | 82021108 | FUSE | 32195 | 20230111 | 2232 | 20230113 | 1545 | 1951016 | 2473 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 43218 | 37.2231 | -121.988 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0014848 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1803963 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1112 | 83421112 | SWITCH | SV45 | 20230111 | 2340 | 20230112 | 1003 | 1949186 | 623 | Distribution Circuit | Equipment Failure/Involved | Overhead | 763 | 475349 | 37.3884 | -122.008 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0014037 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1803549 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1103 | 83771103 | FUSE | 8653 | 20230112 | 430 | 20230113 | 1720 | 1949323 | 2210 | Distribution Circuit | Equipment Failure/Involved | Overhead | 171 | 84718 | 37.2682 | -121.9809 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0014243 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1803594 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1103 | 83771103 | FUSE | 8653 | 20230112 | 430 | 20230113 | 1720 | 1949323 | 2210 | Distribution Circuit | Equipment Failure/Involved | Overhead | 171 | 84718 | 37.2682 | -121.9809 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0014243 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1803594 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1109 | 83371109 | OTHER | WIRE DOWN SSD 90011 | 20230112 | 618 | 20230113 | 59 | 1949370 | 1121 | Distribution Circuit | Vegetation | Tree - fell into line | 723 | 187787 | 37.2774 | -121.9732 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0014773 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1803895 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 4429 | 20230112 | 642 | 20230112 | 2151 | 1949399 | 909 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 15453 | 37.1728 | -121.9918 | No | Clear;32-90 F |  |  | 23-0014867 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1803981 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 468855 | 20230112 | 648 | 20230112 | 1905 | 1949412 | 737 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 3685 | 37.2066 | -121.9716 | No | Clear;32-90 F |  |  | 23-0014642 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803815 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | TRANSFORMER | 315591225586 | 20230112 | 733 | 20230113 | 1658 | 1952298 | 2005 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 4010 | 37.1934 | -122.0153 | No | Heavy Rain-Clear;32-90F | Secondary | Broken | 23-0015478 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804345 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 15069 | 20230112 | 822 | 20230117 | 1311 | 1949619 | 7489 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 149780 | 37.1038 | -121.8982 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015245 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1804240 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | JUMPER | OPEN UN-NUMBERED SBCO | 20230112 | 822 | 20230117 | 1311 | 1957340 | 7489 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 37445 | 37.0946 | -121.9068 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0017035 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805736 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | EL PATIO-1104 | 82921104 | OCB | 1104/2 | 20230112 | 855 | 20230112 | 1021 | 1949614 | 86 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2965 | 244855 | 37.2915 | -121.9358 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0014305 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | No | No | 1803636 | 0 | Non-EPSS | N | 2023 | A- B- C PH INST- LOCKOUT
DE ANZA | DE ANZA | EL PATIO-1104 | 82921104 | SWITCH | 42260 | 20230112 | 855 | 20230112 | 1026 | -1949614 | 91 | Distribution Circuit | Vegetation | Tree - branch fell on line | 85 | 7735 | 37.2945 | -121.9123 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0014305 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1803679 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | FUSE | 9655 | 20230112 | 1120 | 20230113 | 421 | 1949964 | 1021 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 28588 | 37.2095 | -122.0543 | No | Clear;32-90F |  |  | 23-0015047 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804157 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | RECLOSER | 60124 | 20230112 | 1132 | 20230113 | 249 | 1949684 | 917 | Distribution Circuit | Equipment Failure/Involved | Overhead | 134 | 122878 | 37.1462 | -121.9823 | No | Clear;32-90 F | Conductor- Overhead | Arcing | 23-0014443 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1803731 | 0 | EPSS Ckt | N | 2023 | B & GRD
DE ANZA | DE ANZA | WOLFE-1113 | 83671113 | FUSE | 22955 | 20230112 | 1155 | 20230112 | 1313 | 1949923 | 78 | Distribution Circuit | 3rd Party | Metallic Balloon | 72 | 5616 | 37.3556 | -122.0413 | No | Clear;32-90 F | Conductor- Overhead | Contaminated | 23-0014515 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1803769 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1108 | 83481108 | TRANSFORMER | 315479531318 | 20230112 | 1229 | 20230112 | 1856 | 1949665 | 387 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 3483 | 37.3499 | -122.0554 | No | Clear;32-90 F | Anchor or Guy | Broken | 23-0014513 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1803768 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1108 | 83771108 | FUSE | 32987 | 20230112 | 1251 | 20230112 | 1340 | 1950067 | 49 | Distribution Circuit | Vegetation | Tree - grew into line | 136 | 6664 | 37.2501 | -121.951 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0014526 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1803774 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | TRANSFORMER | 315708923378 | 20230112 | 1814 | 20230113 | 2232 | 1950814 | 1698 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 1698 | 37.1327 | -121.9731 | No | Clear;32-90F | Fuse | Normal | 23-0015637 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804478 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 21117 | 20230112 | 1951 | 20230115 | 844 | 1951121 | 3653 | Distribution Circuit | Equipment Failure/Involved | Overhead | 41 | 149773 | 37.1083 | -121.8333 | No | Clear;32-90F | Crossarm- Wood | Broken | 23-0014938 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1804050 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1104 | 83371104 | FUSE | 3565 | 20230112 | 1951 | 20230113 | 1751 | 1950912 | 1320 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 10560 | 37.2386 | -121.9948 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0014793 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803907 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1109 | 83371109 | TRANSFORMER | 315641828398 | 20230112 | 2023 | 20230114 | 1133 | 1945859 | 2350 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 14100 | 37.2703 | -121.9986 | No | Clear;32-90 F | Secondary | Broken | 23-0014806 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803921 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | TRANSFORMER | 315715926620 | 20230112 | 2054 | 20230112 | 2334 | 1950984 | 160 | Transformer only | Equipment Failure/Involved | Overhead | 26 | 4160 | 37.2219 | -121.9726 | No | Clear;32-90 F | Secondary | Normal | 23-0014889 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1804003 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | EL PATIO-1119 | 82921119 | FUSE | 30803 | 20230113 | 50 | 20230113 | 943 | 1951209 | 533 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 10660 | 37.2885 | -121.9266 | No | Clear;32-90F |  |  | 23-0015165 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804208 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | SWITCH | 2513 | 20230113 | 225 | 20230113 | 442 | 1951240 | 137 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 3562 | 37.2216 | -121.9729 | No | Clear;32-90F | Jumper | Burned Open | 23-0015051 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1804161 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | RECLOSER | 60124 | 20230113 | 346 | 20230113 | 1256 | 1951261 | 550 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 136 | 74800 | 37.1462 | -121.9823 | No | Clear;32-90F |  |  | 23-0015053 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1804163 | 0 | EPSS Ckt | N | 2023 | NONE
DE ANZA | DE ANZA | LOS GATOS-1108 | 82021108 | TRANSFORMER | C263 | 20230113 | 410 | 20230114 | 1020 | 1951264 | 1810 | Transformer only | Vegetation | Tree - fell into line | 19 | 34390 | 37.2265 | -121.9946 | No | Clear;32-90F | Secondary | Broken- wire on ground | 23-0015050 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804160 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | JUMPER | OJ 1 P/W/O 315757122730 | 20230113 | 907 | 20230113 | 1505 | 1951473 | 358 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1074 | 37.1147 | -121.9567 | No | Clear;32-90F | Pole-Wood | Broken | 23-0015119 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1804187 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | FUSE | 805 | 20230113 | 945 | 20230113 | 1345 | 1951552 | 240 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 480 | 37.2569 | -122.1182 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0015376 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804289 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1112 | 83371112 | FUSE | 3765 | 20230113 | 1045 | 20230113 | 1115 | 1951706 | 30 | Distribution Circuit | Vegetation | Tree - branch fell on line | 116 | 3480 | 37.2927 | -121.9836 | No | Clear;32-90F | Conductor- Overhead | Contaminated | 23-0015252 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1804242 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1103 | 83771103 | TRANSFORMER | 315720528057 | 20230113 | 1226 | 20230114 | 120 | 1951945 | 774 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 23220 | 37.2613 | -121.9715 | No | Clear;32-90F | Transformer (OH) | Arcing | 23-0015349 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804278 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1113 | 83371113 | TRANSFORMER | 315617629629 | 20230113 | 1244 | 20230114 | 1639 | 1951924 | 1675 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 23450 | 37.3039 | -122.0077 | No | Clear;32-90F | Conductor- Overhead | Together | 23-0015532 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804379 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1103 | 83771103 | FUSE | 31243 | 20230113 | 1325 | 20230114 | 313 | 1952728 | 828 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 4140 | 37.2594 | -121.9752 | No | Clear;32-90F |  |  | 23-0015824 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN |  | 0 | No | No | No | 1804668 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1102 | 83771102 | FUSE | 1275 | 20230113 | 1548 | 20230113 | 1739 | 1952229 | 111 | Distribution Circuit | Vegetation | Tree - bark fell into line | 1 | 111 | 37.2391 | -121.9734 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0015508 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1804361 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1109 | 83481109 | SWITCH | 463510 | 20230113 | 1601 | 20230113 | 1630 | 1952307 | 29 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 134 | 3886 | 37.2935 | -122.0441 | No | Clear;32-90F |  |  | 23-0015482 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804347 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | EL PATIO-1118 | 82921118 | TRANSFORMER | 315858328352 | 20230113 | 1609 | 20230113 | 1750 | 1952282 | 101 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 1010 | 37.27 | -121.9245 | No | Clear;32-90F | Secondary | Normal | 23-0015473 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1804341 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1105 | 83371105 | FUSE | 473 | 20230113 | 1720 | 20230114 | 1430 | 1952403 | 1255 | Distribution Circuit | Vegetation | Tree - branch fell on line | 231 | 133862 | 37.2838 | -122.0331 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015524 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1804374 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1110 | 82031110 | TRANSFORMER | 315475731907 | 20230113 | 1825 | 20230113 | 2140 | 1952480 | 195 | Transformer only | Vegetation | Tree - fell into line | 2 | 390 | 37.3659 | -122.0579 | No | Clear;32-90F | Secondary | Together | 23-0015527 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1804376 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1109 | 83481109 | SWITCH | 463510 | 20230113 | 1846 | 20230113 | 2021 | 1952499 | 95 | Distribution Circuit | Equipment Failure/Involved | Overhead | 134 | 12730 | 37.2935 | -122.0441 | No | Clear;32-90F | Other | Malfunctioning | 23-0015536 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804382 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1107 | 82031107 | FUSE | 3227 | 20230113 | 1916 | 20230114 | 200 | 1952334 | 404 | Distribution Circuit | Equipment Failure/Involved | Overhead | 93 | 11292 | 37.3751 | -122.0868 | No | Clear;32-90F | Insulator | Arcing | 23-0015540 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1804387 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | TRANSFORMER | 315306332076 | 20230113 | 2032 | 20230115 | 1822 | 1952580 | 2750 | Transformer only | Vegetation | Tree - fell into line | 5 | 13750 | 37.3697 | -122.1163 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0015587 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1804429 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1102 | 82021102 | TRANSFORMER | 315722026993 | 20230113 | 2130 | 20230114 | 401 | 1952605 | 391 | Transformer only | Vegetation | Tree - grew into line | 6 | 2346 | 37.2321 | -121.9706 | No | Clear;32-90F | Secondary | Normal | 23-0015581 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1804423 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | HICKS-1109 | 83431109 | TRANSFORMER | 315822527810 | 20230114 | 313 | 20230114 | 401 | 1952729 | 48 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 432 | 37.255 | -121.9364 | Yes | Clear;32-90F | Secondary | Normal | 23-0015825 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1804669 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | RECLOSER | 5696 | 20230114 | 602 | 20230114 | 2204 | 1952810 | 768 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2455 | 166717 | 37.2552 | -122.0274 | Yes | Clear;32-90F | Pothead(Riser Termination) | Burned/flashed | 23-0015839 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804684 | 0 | EPSS Ckt | N | 2023 | SGF
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | FUSE | 18117 | 20230114 | 849 | 20230114 | 2221 | 1953422 | 812 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 23548 | 37.1417 | -121.9741 | Yes | Clear;32-90F |  |  | 23-0016482 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1805236 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1109 | 83481109 | FUSE | 1177 | 20230114 | 908 | 20230116 | 155 | 1953101 | 2447 | Distribution Circuit | Equipment Failure/Involved | Underground | 15 | 36705 | 37.2921 | -122.0446 | Yes | Clear;32-90F | Conductor- Underground | Deteriorated | 23-0016005 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804823 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 30531 | 20230114 | 921 | 20230116 | 1714 | 1955772 | 3353 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 30177 | 37.1919 | -122.0345 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016605 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | Yes | No | 1805352 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | JUMPER | OJ 1 SPANS SS OF CGC# 315499327752 | 20230114 | 928 | 20230116 | 1410 | 1954862 | 3137 | Distribution Circuit | Equipment Failure/Involved | Overhead | 506 | 102953 | 37.2524 | -122.0461 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016340 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1805098 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1102 | 82021102 | TRANSFORMER | 315721226980 | 20230114 | 944 | 20230114 | 1401 | 1953709 | 257 | Transformer only | Vegetation | Tree - branch fell on line | 6 | 1542 | 37.2317 | -121.9708 | Yes | Clear;32-90F | Secondary | Normal | 23-0016247 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805007 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | RECLOSER | 60118 | 20230114 | 958 | 20230115 | 844 | 1953801 | 1366 | Distribution Circuit | Equipment Failure/Involved | Overhead | 869 | 996760 | 37.1247 | -121.9353 | Yes | Clear;32-90F | Conductor- Overhead | On Ground | 23-0016069 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | Yes | No | 1804874 | 0 | EPSS Ckt | N | 2023 | NONE
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | OTHER | WIRE DOWN AT R124 | 20230114 | 958 | 20230115 | 624 | 1954289 | 1226 | Distribution Circuit | Equipment Failure/Involved | Overhead | 202 | 47411 | 37.151 | -121.9596 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016164 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1804944 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | FUSE | 33577 | 20230114 | 1125 | 20230115 | 1915 | 1954138 | 1910 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5730 | 37.1583 | -122.0046 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0016630 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1805369 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | RECLOSER | 622226 | 20230114 | 1126 | 20230116 | 1714 | 1953856 | 3228 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 177540 | 37.1941 | -122.0219 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016113 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | Yes | No | 1804907 | 0 | EPSS Ckt | N | 2023 | N/A
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | SWITCH | SA07 | 20230114 | 1150 | 20230114 | 2309 | 1954242 | 269 | Distribution Circuit | Vegetation | Tree - fell into line | 499 | 161272 | 37.1538 | -121.9821 | Yes | Clear;32-90F | Conductor- Overhead | Bent or Twisted | 23-0016151 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1804934 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1113 | 83371113 | FUSE | 29699 | 20230114 | 1213 | 20230114 | 1639 | 1954268 | 266 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 30324 | 37.3041 | -122.01 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0016162 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | No | No | 1804942 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1101 | 82021101 | FUSE | 46285 | 20230114 | 1228 | 20230114 | 1430 | 1953675 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 488 | 37.2275 | -121.9726 | Yes | Clear;32-90F |  |  | 23-0016253 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805013 | 1 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1103 | 83771103 | TRANSFORMER | 315688728033 | 20230114 | 1232 | 20230114 | 1334 | 1954243 | 62 | Transformer only | Vegetation | Tree - grew into line | 2 | 124 | 37.2604 | -121.9824 | Yes | Clear;32-90F | Jumper | Arcing | 23-0016191 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804965 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | TRANSFORMER | 315607027448 | 20230114 | 1239 | 20230114 | 1448 | 1954322 | 129 | Transformer only | Vegetation | Tree - grew into line | 2 | 258 | 37.2441 | -122.0103 | Yes | Clear;32-90F | Secondary | Normal | 23-0016179 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1804956 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | TRANSFORMER | 315747826206 | 20230114 | 1723 | 20230115 | 1320 | 1956003 | 1197 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2394 | 37.2107 | -121.9618 | Yes | Clear;32-90F | Secondary | Broken | 23-0016690 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805415 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1108 | 83771108 | TRANSFORMER | 315775727545 | 20230114 | 1815 | 20230114 | 2100 | 1955005 | 165 | Transformer only | Vegetation | Tree - branch fell on line | 20 | 3300 | 37.2475 | -121.9524 | Yes | Clear;32-90F |  |  | 23-0016366 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805121 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | BRITTON-1105 | 83611105 | TRANSFORMER | 315562932326 | 20230114 | 2058 | 20230114 | 2320 | 1955174 | 142 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 568 | 37.3779 | -122.028 | Yes | Clear;32-90 F | Compression Fitting | Burned Open | 23-0016408 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805159 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1108 | 83481108 | TRANSFORMER | 315495731066 | 20230114 | 2107 | 20230115 | 1410 | 1955209 | 1023 | Distribution Circuit | Equipment Failure/Involved | Overhead | 72 | 8376 | 37.3429 | -122.0506 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0016480 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805234 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1105 | 83371105 | FUSE | 15775 | 20230114 | 2152 | 20230115 | 1228 | 1955238 | 876 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 876 | 37.2487 | -122.0792 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0016514 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805271 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | TRANSFORMER | 315538325858 | 20230114 | 2304 | 20230115 | 1329 | 1955293 | 865 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 865 | 37.2002 | -122.0331 | Yes | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0016538 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805293 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315696823865 | 20230115 | 207 | 20230115 | 528 | 1955363 | 201 | Transformer only | Vegetation | Tree - branch fell on line | 3 | 603 | 37.1469 | -121.9793 | No | Clear;32-90F | Fuse | Broken | 23-0016524 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805281 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | TRANSFORMER | 315682623647 | 20230115 | 722 | 20230115 | 1435 | 1955550 | 433 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 433 | 37.1396 | -121.9824 | No | Clear;32-90F |  |  | 23-0016707 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1805426 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1108 | 82021108 | SWITCH | 52322 | 20230115 | 731 | 20230115 | 743 | 1955577 | 12 | Distribution Circuit | Company Initiated | Return Circuit Normal | 17 | 204 | 37.2229 | -121.9822 | No | Clear;32-90F | Other | Normal | 23-0014490 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1805304 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1102 | 82021102 | TRANSFORMER | 315721226980 | 20230115 | 750 | 20230115 | 1010 | 1955566 | 140 | Transformer only | Vegetation | Tree - branch fell on line | 6 | 840 | 37.2317 | -121.9708 | No | Clear;32-90F | Secondary | Normal | 23-0016549 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805301 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | FUSE | 9325 | 20230115 | 919 | 20230115 | 1815 | 1955699 | 536 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 5896 | 37.2471 | -122.0259 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016658 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | Yes | No | 1805395 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1103 | 83371103 | FUSE | 6707 | 20230115 | 1133 | 20230115 | 1145 | 1955866 | 12 | Distribution Circuit | Equipment Failure/Involved | Underground | 3 | 36 | 37.2602 | -122.0462 | No | Clear;32-90F | Secondary | Normal | 23-0016647 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805384 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1102 | 83771102 | SWITCH | SC05 | 20230115 | 1142 | 20230115 | 2025 | 1955793 | 523 | Distribution Circuit | Vegetation | Tree - fell into line | 498 | 44350 | 37.2401 | -121.9767 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0016650 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805387 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 31447 | 20230115 | 1618 | 20230115 | 2210 | 1956169 | 352 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 352 | 37.1322 | -121.9391 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016743 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1805446 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | FUSE | 26059 | 20230115 | 1811 | 20230115 | 2125 | 1956268 | 194 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 26 | 5044 | 37.2391 | -122.0128 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0016763 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805464 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | BIG BASIN-1101 | 82841101 | FUSE | 2829 | 20230115 | 1812 | 20230117 | 1724 | 1956295 | 2832 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1 | 2832 | 37.1683 | -122.0744 | No | Clear;32-90F |  |  | 23-0016787 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805483 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1101 | 82021101 | RECLOSER | 184035 | 20230115 | 2243 | 20230116 | 1045 | 1956433 | 722 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 10438 | 37.2245 | -121.9699 | No | Clear;32-90F | Conductor- Overhead | Broken | 23-0016849 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1805547 | 0 | EPSS Ckt | N | 2023 | B & C PHASE
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | RECLOSER | 60122 | 20230116 | 58 | 20230116 | 104 | 1956470 | 6 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 432 | 2592 | 37.1462 | -121.9823 | Yes | Clear;32-90F |  |  | 23-0016862 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1805560 | 0 | EPSS Ckt | N | 2023 | A-B-C-GRD
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | TRANSFORMER | 315696623994 | 20230116 | 211 | 20230116 | 1601 | 1956547 | 830 | Transformer only | Unknown Cause | Patrol - found nothing | 7 | 5810 | 37.1504 | -121.9794 | Yes | Clear;32-90F |  |  | 23-0017303 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1805980 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | RECLOSER | LA64 | 20230116 | 229 | 20230116 | 1845 | 1956566 | 976 | Distribution Circuit | Vegetation | Tree - fell into line | 338 | 76656 | 37.1372 | -121.9674 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016872 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805572 | 0 | EPSS Ckt | N | 2023 | SGF
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | JUMPER | JUMPERS @ CGC 315773922370 | 20230116 | 241 | 20230117 | 1813 | 1957578 | 2372 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2372 | 37.1056 | -121.9527 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0017103 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | Yes | No | 1805794 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | FUSE | 18351 | 20230116 | 250 | 20230116 | 1610 | 1957333 | 800 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3200 | 37.2808 | -122.1182 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0017028 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | Yes | No | 1805732 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | RECLOSER | 60092 | 20230116 | 457 | 20230116 | 1006 | 1956841 | 309 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1110 | 333744 | 37.1815 | -121.985 | Yes | Clear;32-90F | Conductor- Overhead | Contaminated | 23-0016926 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1805633 | 0 | EPSS Ckt | N | 2023 | A & B PHASE
DE ANZA | DE ANZA | LOS ALTOS-1106 | 82241106 | TRANSFORMER | 315237732842 | 20230116 | 612 | 20230116 | 1421 | 1956937 | 489 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1956 | 37.3898 | -122.1398 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0017048 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805747 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1105 | 83371105 | FUSE | 15767 | 20230116 | 639 | 20230116 | 1720 | 1957030 | 641 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1986 | 37.2364 | -122.0662 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0017111 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1805803 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WOLFE-1114 | 83671114 | INTERRUPTER | 35542 | 20230116 | 643 | 20230118 | 257 | 1957072 | 495 | Distribution Circuit | Equipment Failure/Involved | Underground | 1284 | 578688 | 37.3382 | -122.0324 | Yes | Clear;32-90F | Conductor- Underground | Deteriorated | 23-0017017 | UG | Sus | 35419593 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805721 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | FUSE | 10051 | 20230116 | 743 | 20230117 | 1454 | 1957232 | 1871 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 13097 | 37.2108 | -122.0583 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0017297 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805976 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315615023006 | 20230116 | 837 | 20230116 | 933 | 1957332 | 56 | Transformer only | Vegetation | Tree - grew into line | 2 | 112 | 37.1223 | -122.0044 | Yes | Clear;32-90F | Secondary | Normal | 23-0017027 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805731 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1104 | 83421104 | TRANSFORMER | 315621433031 | 20230116 | 943 | 20230116 | 1408 | 1957519 | 265 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 3180 | 37.3976 | -122.0081 | Yes | Clear;32-90 F | Transformer | Normal | 23-0017082 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805776 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1107 | 82031107 | TRANSFORMER | 315434932253 | 20230116 | 1251 | 20230116 | 2034 | 1958092 | 463 | Transformer only | Equipment Failure/Involved | Overhead | 23 | 10649 | 37.3755 | -122.0719 | Yes | Clear;32-90F | Connector or Splice (OH) | Arcing | 23-0017394 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806065 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | SWITCH | 1837 | 20230116 | 1404 | 20230116 | 1415 | 1958279 | 11 | Distribution Circuit | Company Initiated | Return Circuit Normal | 61 | 671 | 37.2507 | -122.0246 | Yes | Clear;32-90F | Conductor- Underground | Normal | 23-0015839 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1805925 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WOLFE-1107 | 83671107 | FUSE | 33651 | 20230116 | 1501 | 20230117 | 1800 | 1958394 | 1619 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 31485 | 37.3413 | -122.0137 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0017355 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806024 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1103 | 83371103 | SWITCH | 12304 | 20230116 | 1524 | 20230116 | 1642 | 1958458 | 78 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 1079 | 37.2568 | -122.0411 | Yes | Clear;32-90F | Pothead(Riser Termination) | Burned/flashed | 23-0016403 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805965 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315661223750 | 20230116 | 1804 | 20230116 | 2341 | 1958689 | 337 | Transformer only | Vegetation | Tree - fell into line | 2 | 674 | 37.1433 | -121.9916 | Yes | Clear;32-90F | Fuse | Failed/Faulted | 23-0017441 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806109 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1103 | 83371103 | SWITCH | 12296 | 20230116 | 1819 | 20230116 | 1858 | 1958707 | 39 | Distribution Circuit | Company Initiated | Return Circuit Normal | 12 | 468 | 37.2566 | -122.041 | Yes | Clear;32-90F | Conductor- Underground | Normal | 23-0016403 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1806043 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | TRANSFORMER | 315672024756 | 20230116 | 2042 | 20230117 | 405 | 1958874 | 443 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 886 | 37.1705 | -121.9864 | Yes | Clear;32-90 F | Transformer | Malfunctioning | 23-0017436 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806107 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1105 | 83771105 | SWITCH | 9299 | 20230116 | 2220 | 20230117 | 416 | 1958980 | 356 | Distribution Circuit | Company Initiated | Return Circuit Normal | 130 | 16003 | 37.2726 | -121.9548 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0017375 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1806106 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1108 | 83481108 | TRANSFORMER | 315395031589 | 20230117 | 1000 | 20230117 | 1230 | 1959462 | 150 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 1050 | 37.3568 | -122.0856 | No | Clear;32-90F | Secondary | Broken | 23-0017586 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1806187 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1101 | 82021101 | TRANSFORMER | 315744126768 | 20230117 | 1656 | 20230118 | 203 | 1960148 | 547 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 3829 | 37.2259 | -121.9627 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0017936 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1806349 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1102 | 83771102 | RECLOSER | 944560 | 20230117 | 1803 | 20230117 | 2009 | 1960232 | 126 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 3276 | 37.2415 | -121.986 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0017897 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1806307 | 0 | EPSS Ckt | N | 2023 | NONE
DE ANZA | DE ANZA | SARATOGA-1113 | 83371113 | JUMPER | OJS @ 855 BETTE AVE | 20230118 | 2300 | 20230119 | 540 | 1961680 | 390 | Distribution Circuit | Vegetation | Tree - branch fell on line | 63 | 24570 | 37.3146 | -122.0214 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0018630 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1806687 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1102 | 83771102 | FUSE | 32049 | 20230118 | 2349 | 20230119 | 843 | 1961719 | 534 | Distribution Circuit | Vegetation | Tree - grew into line | 15 | 8010 | 37.2415 | -121.9658 | No | Clear;32-90F | Conductor- Overhead | Arcing | 23-0018638 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1806696 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1103 | 83771103 | SWITCH | 12132 | 20230119 | 626 | 20230120 | 241 | 1962018 | 1215 | Distribution Circuit | Equipment Failure/Involved | Underground | 409 | 121685 | 37.2637 | -121.9889 | No | Clear;32-90F | Transformer (UG) | Failed/Faulted | 23-0018712 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1806774 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | TRANSFORMER | 315578025594 | 20230119 | 927 | 20230119 | 1146 | 1961932 | 139 | Transformer only | Company Initiated | Improper Construction | 1 | 139 | 37.1931 | -122.0188 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0018847 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806785 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | EL PATIO-1116 | 82921116 | FUSE | 175 | 20230119 | 947 | 20230119 | 1142 | 1961959 | 115 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 151 | 17365 | 37.2884 | -121.9711 | No | Clear;32-90F |  |  | 23-0018809 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1806777 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1104 | 82241104 | TRANSFORMER | 315325032515 | 20230119 | 1959 | 20230119 | 2208 | 1962787 | 129 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 516 | 37.3819 | -122.1097 | No | Clear;32-90F | Transformer (OH) | Deteriorated | 23-0019122 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806895 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | JUMPER | OJS @ SS OF CGC #2008 | 20230119 | 2131 | 20230120 | 355 | 1962764 | 384 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 2688 | 37.3678 | -122.1304 | No | Clear;32-90F | Conductor- Overhead | Broken | 23-0019110 | OH | Sus | 45645577 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1806884 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | HICKS-1114 | 83431114 | TRANSFORMER | 100000011135 | 20230119 | 2310 | 20230120 | 31 | 1962844 | 81 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 243 | 37.2496 | -121.9283 | No | Clear;32-90F |  |  | 23-0019187 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1806959 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | BRITTON-1115 | 83611115 | SWITCH | SV31 | 20230120 | 951 | 20230120 | 958 | 1963113 | 7 | Distribution Circuit | 3rd Party | Vehicle | 13 | 91 | 37.3733 | -121.9963 | No | Clear;32-90F | Pole-Wood | Broken | 23-0019276 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1807020 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1109 | 83421109 | SWITCH | 14530 | 20230120 | 1023 | 20230120 | 1057 | 1963146 | 34 | Distribution Circuit | 3rd Party | Vehicle | 4 | 136 | 37.3816 | -121.9961 | No | Clear;32-90F | Pole-Wood | Broken | 23-0019276 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1807029 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315639523463 | 20230120 | 2218 | 20230121 | 1447 | 1963160 | 989 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 1978 | 37.1341 | -121.999 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0019662 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807136 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | BRITTON-1115 | 83611115 | SWITCH | 4047 | 20230120 | 2306 | 20230121 | 1228 | 1963720 | 802 | Distribution Circuit | 3rd Party | Vehicle | 1 | 802 | 37.3743 | -121.9963 | No | Clear;32-90F | Pole-Wood | Broken | 23-0019276 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1807143 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | BRITTON-1109 | 83611109 | TRANSFORMER | 315583932565 | 20230121 | 856 | 20230121 | 938 | 1963868 | 42 | Transformer only | Unknown Cause | Patrol - found nothing | 54 | 2268 | 37.3846 | -122.021 | No | Clear;32-90F |  |  | 23-0019694 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1807173 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | SWITCH | 132576 | 20230122 | 1612 | 20230123 | 334 | 1964928 | 682 | Distribution Circuit | Equipment Failure/Involved | Overhead | 205 | 13984 | 37.206 | -122.0491 | No | Clear;32-90F | Pole-Wood | Broken | 23-0019857 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1807346 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | RECLOSER | LA64 | 20230122 | 2216 | 20230124 | 229 | 1965092 | 1693 | Distribution Circuit | Vegetation | Tree - fell into line | 338 | 572234 | 37.1372 | -121.9674 | No | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0019962 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1807395 | 0 | EPSS Ckt | N | 2023 | A/B/C
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | RECLOSER | 60124 | 20230122 | 2217 | 20230124 | 158 | 1965107 | 1661 | Distribution Circuit | Vegetation | Tree - fell into line | 549 | 253770 | 37.1462 | -121.9823 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0019964 | OH | Sus | 45647107 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1807397 | 0 | EPSS Ckt | N | 2023 | C/GRD
DE ANZA | DE ANZA | LAWRENCE SUB | 8342 | OCB | 1300/2 | 20230122 | 2327 | 20230123 | 1201 | 1965123 | 754 | Distribution Circuit | Equipment Failure/Involved | Overhead | 148 | 111592 | 37.3971 | -122.01 | No | Clear;32-90F | Conductor- Overhead | Arcing | 23-0019973 | OH | Sus | 31635045 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1807406 | 0 | Non-EPSS | N | 2023 | N/A
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 4191 | 20230123 | 110 | 20230124 | 1314 | 1965408 | 2164 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 88724 | 37.1068 | -121.904 | No | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0020040 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1807456 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | RECLOSER | 60092 | 20230123 | 220 | 20230125 | 501 | 1965184 | 3041 | Distribution Circuit | Vegetation | Tree - fell into line | 1096 | 1729922 | 37.1815 | -121.985 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0019985 | OH | Sus | 45647266 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1807418 | 0 | EPSS Ckt | N | 2023 | SENSTIVE GRD
DE ANZA | DE ANZA | LOS ALTOS-1106 | 82241106 | FUSE | 23139 | 20230123 | 923 | 20230124 | 251 | 1965589 | 1048 | Distribution Circuit | Equipment Failure/Involved | Underground | 12 | 12576 | 37.3834 | -122.1331 | No | Clear;32-90F | Elbow | Failed/Faulted | 23-0020140 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807566 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | JUMPER | CUT | 20230123 | 1138 | 20230123 | 1553 | 1965778 | 255 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 765 | 37.1442 | -121.9837 | No | Clear;32-90F | Jumper | Normal | 23-0020401 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1807631 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | FUSE | 31605 | 20230123 | 2034 | 20230124 | 1238 | 1966324 | 964 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 9640 | 37.3502 | -122.1258 | No | Clear;32-90F | Conductor- Overhead | Bent or Twisted | 23-0020482 | OH | Sus | 31635363 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1807677 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | TRANSFORMER | 315566525280 | 20230123 | 2112 | 20230124 | 237 | 1966337 | 325 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 650 | 37.184 | -122.0228 | No | Clear;32-90F | Secondary | Deteriorated | 23-0020477 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1807674 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1109 | 83481109 | TRANSFORMER | 315494330060 | 20230124 | 1247 | 20230124 | 1317 | 1966612 | 30 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 90 | 37.3152 | -122.0504 | No | Clear;32-90 F | Transformer | Arcing | 23-0020769 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807882 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1103 | 83771103 | TRANSFORMER | 315691428064 | 20230125 | 600 | 20230125 | 1258 | 1967502 | 418 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 2508 | 37.2613 | -121.9815 | No | Clear;32-90 F | Transformer | Burned Open | 23-0021010 | OH | Sus | 31635561 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807985 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1105 | 83771105 | JUMPER | FLYING BELLS NORTH OF 1 OF CGC 315823028212 | 20230126 | 1237 | 20230127 | 252 | 1968926 | 855 | Distribution Circuit | Equipment Failure/Involved | Overhead | 56 | 47880 | 37.2664 | -121.9363 | No | Clear;32-90F | Crossarm- Wood | Broken | 23-0021816 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1808438 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | JUMPER | UNMARKED SBCO CORNER OF RADONICH RD | 20230126 | 1313 | 20230126 | 1843 | 1968921 | 330 | Distribution Circuit | Vegetation | Tree - grew into line | 12 | 3960 | 37.1009 | -121.9038 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0021812 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1808435 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | OTHER | WIRE DOWN 17433 LOCUST DR | 20230126 | 1424 | 20230127 | 600 | 1969038 | 936 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 39965 | 37.1677 | -121.9753 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0021972 | OH | Sus | 31635726 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1808471 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 18607 | 20230126 | 2205 | 20230126 | 2350 | 1969301 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 45 | 4725 | 37.1613 | -121.9722 | No | Clear;32-90F |  |  | 23-0022074 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1808527 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WOLFE-1104 | 83671104 | TRANSFORMER | T20614 | 20230127 | 820 | 20230128 | 901 | 1969551 | 1481 | Distribution Circuit | Equipment Failure/Involved | Underground | 74 | 109594 | 37.3319 | -122.0122 | No | Clear;32-90F | Transformer (UG) | Failed/Faulted | 23-0022186 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1808640 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | FUSE | 23009 | 20230127 | 1236 | 20230127 | 1430 | 1969912 | 114 | Distribution Circuit | Equipment Failure/Involved | Overhead | 81 | 9234 | 37.1673 | -122.0363 | No | Clear;32-90F | Pole-Wood | Broken | 23-0022367 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1808682 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 4427 | 20230128 | 759 | 20230128 | 1839 | 1970285 | 640 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 12160 | 37.1728 | -121.9926 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0022616 | OH | Sus | 31635800 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1808810 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | HICKS-1116 | 83431116 | TRANSFORMER | C2252 | 20230128 | 822 | 20230129 | 26 | 1970308 | 964 | Transformer only | Equipment Failure/Involved | Underground | 6 | 5784 | 37.2324 | -121.9209 | No | Clear;32-90F | Secondary | Broken | 23-0022695 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1808890 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | FUSE | 23009 | 20230128 | 929 | 20230128 | 1830 | 1970354 | 541 | Distribution Circuit | Equipment Failure/Involved | Overhead | 81 | 43821 | 37.1673 | -122.0363 | No | Clear;32-90F | Pole-Wood | Broken | 23-0022367 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1808807 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1102 | 82021102 | TRANSFORMER | 315685626972 | 20230128 | 1406 | 20230129 | 1620 | 1970569 | 1574 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 26758 | 37.2315 | -121.9831 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0022651 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1808841 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1102 | 83481102 | OCB | 1102/2 | 20230128 | 2333 | 20230130 | 741 | 1970755 | 1789 | Distribution Circuit | Equipment Failure/Involved | Underground | 12 | 2597 | 37.3358 | -122.0431 | No | Clear;32-90F | Interrupter | Failed/Faulted | 23-0022694 | UG | Sus | 35423941 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1808888 | 0 | Non-EPSS | N | 2023 | PH INST ( A- B & C)
DE ANZA | DE ANZA | HICKS-1116 | 83431116 | TRANSFORMER | C2252 | 20230129 | 46 | 20230129 | 1119 | 1970760 | 633 | Transformer only | Equipment Failure/Involved | Underground | 6 | 3798 | 37.2324 | -121.9209 | No | Clear;32-90F | Secondary | Broken | 23-0022721 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1808921 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | EL PATIO-1116 | 82921116 | FUSE | 175 | 20230129 | 853 | 20230129 | 1030 | 1970869 | 97 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 151 | 14647 | 37.2884 | -121.9711 | No | Clear;32-90F |  |  | 23-0022718 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1808918 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1112 | 83371112 | TRANSFORMER | 315636128881 | 20230129 | 1703 | 20230130 | 516 | 1971061 | 733 | Transformer only | Equipment Failure/Involved | Electrical Overload | 3 | 2199 | 37.2836 | -122.0007 | No | Clear;32-90 F | Connector or Splice (UG) | Failed/Faulted | 23-0022747 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1808946 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315477524770 | 20230131 | 2223 | 20230201 | 1421 | 1973299 | 958 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 1916 | 37.1699 | -122.0529 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0023716 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1809567 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WHISMAN-1105 | 83631105 | OCB | 1105/2 | 20230201 | 1419 | 20230201 | 1739 | 1974133 | 200 | Distribution Circuit | Equipment Failure/Involved | Underground | 297 | 58575 | 37.4048 | -122.0691 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0024019 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1809800 | 0 | Non-EPSS | N | 2023 | B INST & GRD INST
DE ANZA | DE ANZA | VASONA-1101 | 83771101 | TRANSFORMER | 315752727697 | 20230201 | 1736 | 20230201 | 2128 | 1974292 | 232 | Transformer only | 3rd Party | Fire- house or bldg. | 2 | 464 | 37.2516 | -121.9605 | No | Clear;32-90F | Conductor- Overhead | Burned/flashed | 23-0024132 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1809825 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WHISMAN-1106 | 83631106 | TRANSFORMER | 315402333668 | 20230202 | 147 | 20230202 | 311 | 1974430 | 84 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 420 | 37.4139 | -122.0842 | No | Clear;32-90 F | Transformer | Burned/flashed | 23-0024202 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1809866 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WHISMAN-1105 | 83631105 | OCB | 1105/2 | 20230202 | 149 | 20230202 | 532 | 1974432 | 223 | Distribution Circuit | Equipment Failure/Involved | Underground | 11 | 2453 | 37.4048 | -122.0691 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0024019 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1809867 | 0 | Non-EPSS | N | 2023 | NONE
DE ANZA | DE ANZA | LOS ALTOS-1107 | 82241107 | TRANSFORMER | 315313032978 | 20230202 | 539 | 20230202 | 1705 | 1974444 | 686 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 6860 | 37.3943 | -122.1142 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0024221 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1809876 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | FUSE | 15775 | 20230202 | 1711 | 20230202 | 1915 | 1975333 | 124 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 124 | 37.2487 | -122.0792 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0024651 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1810125 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | RECLOSER | LA64 | 20230203 | 648 | 20230203 | 1009 | 1975639 | 201 | Distribution Circuit | Vegetation | Tree - branch fell on line | 338 | 67938 | 37.1372 | -121.9674 | No | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Arcing | 23-0024734 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1810196 | 0 | EPSS Ckt | N | 2023 | A & B
DE ANZA | DE ANZA | VASONA-1102 | 83771102 | FUSE | 185363 | 20230203 | 1637 | 20230204 | 118 | 1976220 | 521 | Distribution Circuit | 3rd Party | Vehicle | 980 | 88781 | 37.2361 | -121.963 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0025105 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1810384 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | SWITCH | 15733 | 20230204 | 1157 | 20230204 | 1658 | 1976601 | 301 | Distribution Circuit | Equipment Failure/Involved | Overhead | 183 | 42252 | 37.2227 | -122.0784 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0025184 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1810507 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | EL PATIO-1116 | 82921116 | OCB | 1116/2 | 20230204 | 1246 | 20230204 | 1304 | 1976644 | 16 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2812 | 44992 | 37.2917 | -121.9356 | No | Clear;32-90F | Recloser | Arcing | 23-0025204 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1810514 | 0 | Non-EPSS | N | 2023 | N/A
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | FUSE | 23009 | 20230204 | 1557 | 20230205 | 1629 | 1976736 | 1472 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 81 | 113182 | 37.1673 | -122.0363 | No | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0025400 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1810690 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 1429 | 20230204 | 1714 | 20230205 | 1949 | 1976866 | 1595 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 22330 | 37.1476 | -121.9748 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0025256 | OH | Sus | 31636152 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1810557 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | JUMPER | BURNED OJ SS OF 3173 | 20230204 | 1738 | 20230205 | 1927 | 1976787 | 1549 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 29431 | 37.1706 | -121.9419 | No | Clear;32-90F | Jumper | Burned Open | 23-0025407 | OH | Sus | 45658927 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1810695 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | RECLOSER | 60116 | 20230204 | 1752 | 20230204 | 1928 | 1976777 | 96 | Distribution Circuit | Vegetation | Tree - fell into line | 1124 | 105603 | 37.1735 | -121.9928 | No | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0025247 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1810548 | 0 | EPSS Ckt | N | 2023 | SGF
DE ANZA | DE ANZA | SARATOGA-1109 | 83371109 | TRANSFORMER | 315659928623 | 20230204 | 1755 | 20230204 | 2007 | 1976805 | 132 | Transformer only | Vegetation | Tree - branch fell on line | 13 | 1716 | 37.2765 | -121.9926 | No | Clear;32-90 F | Service conductor | Normal | 23-0025270 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1810573 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | HICKS-1116 | 83431116 | FUSE | 3543 | 20230204 | 1801 | 20230205 | 315 | 1976823 | 554 | Distribution Circuit | Vegetation | Tree - branch fell on line | 60 | 33240 | 37.235 | -121.9194 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0025313 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1810617 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1104 | 82241104 | TRANSFORMER | 315325032515 | 20230205 | 212 | 20230206 | 519 | 1977172 | 1627 | Transformer only | Equipment Failure/Involved | Electrical Overload | 4 | 6508 | 37.3819 | -122.1097 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0025433 | OH | Sus | 35425100 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1810720 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | RECLOSER | 60116 | 20230205 | 423 | 20230208 | 1430 | 1977208 | 4927 | Distribution Circuit | Vegetation | Tree - fell into line | 947 | 204307 | 37.1735 | -121.9928 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0025333 | OH | Sus | 35424938 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1810638 | 0 | EPSS Ckt | N | 2023 | A GRD
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | FUSE | 15777 | 20230205 | 1528 | 20230206 | 415 | 1977566 | 767 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 4602 | 37.2536 | -122.0884 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0025441 | OH | Sus | 31636311 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1810727 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1114 | 82031114 | TRANSFORMER | 315453531997 | 20230206 | 1256 | 20230207 | 503 | 1978309 | 967 | Transformer only | Equipment Failure/Involved | Electrical Overload | 6 | 5802 | 37.3686 | -122.0657 | No | Clear;32-90 F | Other | Arcing | 23-0025784 | OH | Sus | 45659359 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1811013 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | SWITCH | SA01 | 20230206 | 2218 | 20230206 | 2249 | 1978708 | 31 | Distribution Circuit | Company Initiated | Return Circuit Normal | 871 | 23521 | 37.1435 | -121.9745 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0025982 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1811089 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1108 | 83371108 | TRANSFORMER | 315690228776 | 20230207 | 919 | 20230207 | 1032 | 1979001 | 73 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 1168 | 37.2809 | -121.9824 | No | Clear;32-90 F | Secondary | Deteriorated | 23-0026126 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1811262 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1102 | 83771102 | FUSE | 32033 | 20230207 | 1230 | 20230207 | 2219 | 1979198 | 589 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 11780 | 37.2409 | -121.9643 | No | Clear;32-90F | Crossarm- Wood | Broken | 23-0026238 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1811315 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | TRANSFORMER | 315589028638 | 20230207 | 2128 | 20230208 | 1307 | 1979456 | 939 | Transformer only | Vegetation | Tree - grew into line | 9 | 8451 | 37.2766 | -122.017 | No | Clear;32-90 F | Transformer | Contaminated | 23-0026476 | OH | Sus | 45660493 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1811407 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1109 | 83371109 | FUSE | 69417 | 20230208 | 1351 | 20230208 | 1554 | 1980176 | 123 | Distribution Circuit | Vegetation | Tree - grew into line | 16 | 1968 | 37.2684 | -121.9932 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0026763 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1811646 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | EL PATIO-1113 | 82921113 | FUSE | 3985 | 20230209 | 1051 | 20230209 | 1756 | 1981246 | 425 | Distribution Circuit | Equipment Failure/Involved | Underground | 6 | 2550 | 37.2844 | -121.9427 | No | Clear;32-90F | Transformer (UG) | Normal | 23-0027289 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1811982 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | TRANSFORMER | 315701724434 | 20230209 | 1530 | 20230209 | 2112 | 1980977 | 342 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 3762 | 37.1623 | -121.9779 | No | Clear;32-90 F | Service conductor | Failed/Faulted | 23-0027255 | OH | Sus | 45662387 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1811969 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1101 | 82021101 | TRANSFORMER | 315775826973 | 20230210 | 1011 | 20230210 | 1840 | 1981740 | 509 | Transformer only | Vegetation | Tree - grew into line | 18 | 9162 | 37.2317 | -121.952 | No | Clear;32-90F | Secondary | Contaminated | 23-0027712 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1812290 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | EL PATIO-1118 | 82921118 | TRANSFORMER | 315861528531 | 20230210 | 1339 | 20230211 | 631 | 1981908 | 1012 | Transformer only | Equipment Failure/Involved | Overhead | 23 | 23276 | 37.2749 | -121.9237 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0027661 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1812269 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | EL PATIO-1118 | 82921118 | TRANSFORMER | 315862628539 | 20230210 | 1348 | 20230211 | 632 | 1981913 | 1004 | Transformer only | Equipment Failure/Involved | Electrical Overload | 18 | 18072 | 37.2751 | -121.9233 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0027680 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1812279 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | BRITTON-1106 | 83611106 | TRANSFORMER | C4041 | 20230211 | 1239 | 20230213 | 551 | 1982453 | 2472 | Distribution Circuit | Equipment Failure/Involved | Underground | 116 | 76495 | 37.3526 | -122.024 | No | Clear;32-90F | Transformer (UG) | Broken | 23-0027853 | UG | Sus | 35426141 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1812439 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1105 | 83771105 | OCB | 1105/2/NORM | 20230212 | 111 | 20230212 | 1257 | 1982727 | 706 | Distribution Circuit | 3rd Party | Vehicle | 2688 | 348468 | 37.2537 | -121.9662 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0027888 | OH | Sus | 31636641 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1812476 | 0 | Non-EPSS | N | 2023 | B & C PH & GRD- 51 INST
DE ANZA | DE ANZA | WOLFE-1104 | 83671104 | TRANSFORMER | 315637030034 | 20230212 | 1040 | 20230212 | 1840 | 1982884 | 480 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 2880 | 37.3151 | -122.0014 | No | Clear;32-90 F | Transformer | Burned Open | 23-0027925 | OH | Sus | 45669420 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1812516 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1104 | 83671104 | OTHER | 315635430035 | 20230212 | 1047 | 20230212 | 1115 | 1982864 | 28 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 140 | 37.3151 | -122.0019 | No | Clear;32-90F | Jumper | Burned Open | 23-0027920 | OH | Sus | 45669366 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1812511 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1101 | 82021101 | FUSE | 26041 | 20230212 | 2230 | 20230213 | 206 | 1983163 | 216 | Distribution Circuit | Animal | Other | 3 | 648 | 37.2043 | -121.9524 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0027996 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1812591 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1109 | 83371109 | TRANSFORMER | 315713328770 | 20230215 | 907 | 20230215 | 1305 | 1985930 | 238 | Transformer only | Vegetation | Tree - grew into line | 12 | 2856 | 37.2808 | -121.9745 | No | Clear;32-90 F | Transformer | Arcing | 23-0021909 | OH | Sus | 45448426 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1813445 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | TRANSFORMER | 315893622316 | 20230215 | 1235 | 20230215 | 1600 | 1986203 | 205 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 205 | 37.1045 | -121.9102 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0029273 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1813529 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1111 | 83371111 | TRANSFORMER | 315614429140 | 20230215 | 1345 | 20230215 | 1734 | 1986232 | 229 | Transformer only | Vegetation | Tree - grew into line | 11 | 2519 | 37.2905 | -122.0086 | No | Clear;32-90 F | Secondary | Contaminated | 23-0029337 | OH | Sus | 45672793 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1813549 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1106 | 82241106 | FUSE | 18873 | 20230216 | 1219 | 20230216 | 1846 | 1986958 | 215 | Distribution Circuit | Vegetation | Tree - grew into line | 14 | 5320 | 37.3883 | -122.1406 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0029700 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1813759 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1107 | 82241107 | TRANSFORMER | 315310733383 | 20230216 | 1926 | 20230216 | 2114 | 1987220 | 108 | Transformer only | Equipment Failure/Involved | Overhead | 52 | 5616 | 37.4053 | -122.1156 | No | Clear;32-90 F | Fuse | Burned Open | 23-0029950 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1813824 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1109 | 83481109 | TRANSFORMER | 315505429605 | 20230218 | 46 | 20230218 | 2041 | 1988014 | 1195 | Transformer only | Equipment Failure/Involved | Electrical Overload | 8 | 9560 | 37.3028 | -122.0463 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0030399 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1814119 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | EL PATIO-1113 | 82921113 | FUSE | 26255 | 20230218 | 1706 | 20230218 | 1804 | 1988324 | 58 | Distribution Circuit | Animal | Squirrel | 2 | 116 | 37.2757 | -121.9436 | No | Clear;32-90F | Pothead(Riser Termination) | Normal | 23-0030484 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1814218 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | HICKS-2103 | 83432103 | TRANSFORMER | 315896526670 | 20230218 | 1803 | 20230218 | 1935 | 1988341 | 92 | Transformer only | 3rd Party | Customer Equipment | 2 | 184 | 37.224 | -121.9104 | No | Clear;32-90F | Secondary | Broken | 23-0030494 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1814228 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1113 | 82031113 | FUSE | 52254 | 20230219 | 240 | 20230219 | 837 | 1988454 | 357 | Distribution Circuit | Equipment Failure/Involved | Underground | 47 | 16779 | 37.3935 | -122.0786 | Yes | Clear;32-90 F | Fuse | Failed/Faulted | 23-0030523 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1814263 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1111 | 83371111 | FUSE | 12753 | 20230219 | 1233 | 20230219 | 2049 | 1988633 | 496 | Distribution Circuit | 3rd Party | Metallic Balloon | 242 | 120032 | 37.2932 | -121.9765 | Yes | Clear;32-90 F | Cutout- fuse holder | Failed/Faulted | 23-0030549 | OH | Sus | 31638762 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1814302 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | RECLOSER | 60116 | 20230219 | 1427 | 20230220 | 253 | 1988886 | 746 | Distribution Circuit | Equipment Failure/Involved | Overhead | 960 | 25406 | 37.1735 | -121.9928 | Yes | Clear;32-90 F | Crossarm- Wood | Deteriorated | 23-0030552 | OH | Sus | 31638781 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1814305 | 0 | EPSS Ckt | N | 2023 | N/A
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | RECLOSER | 60122 | 20230219 | 1809 | 20230219 | 1816 | 1989009 | 7 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 726 | 5082 | 37.1462 | -121.9823 | Yes | Clear;32-90F |  |  | 23-0030567 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | No | No | 1814318 | 0 | EPSS Ckt | N | 2023 | A/B/C/GRD
DE ANZA | DE ANZA | SARATOGA-1114 | 83371114 | FUSE | 8393 | 20230220 | 1346 | 20230220 | 1401 | 1989450 | 15 | Distribution Circuit | 3rd Party | Metallic Balloon | 196 | 2940 | 37.2759 | -121.9641 | No | Clear;32-90F | Connector or Splice (OH) | Normal | 23-0030687 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1814478 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1112 | 83421112 | TRANSFORMER | 315618132876 | 20230221 | 800 | 20230222 | 1928 | 1996857 | 2124 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 57736 | 37.3934 | -122.0093 | Yes | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0032118 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1815708 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 22965 | 20230221 | 1122 | 20230221 | 1421 | 1990171 | 179 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 90 | 16110 | 37.2162 | -121.9664 | Yes | Clear;32-90F |  |  | 23-0030993 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1814748 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1108 | 83481108 | JUMPER | BURNT OJS @ 2 SPAN OF 5039 | 20230221 | 1132 | 20230221 | 1753 | 1990438 | 381 | Distribution Circuit | Equipment Failure/Involved | Overhead | 65 | 24765 | 37.3457 | -122.0983 | Yes | Clear;32-90F | Jumper | Burned Open | 23-0031045 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1814776 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1104 | 82031104 | FUSE | 371585 | 20230221 | 1153 | 20230221 | 1753 | 1990244 | 360 | Distribution Circuit | Equipment Failure/Involved | Overhead | 102 | 28810 | 37.4074 | -122.0902 | Yes | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0031116 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1814822 | 1 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1105 | 82031105 | OCB | 1105/2 | 20230221 | 1300 | 20230221 | 1836 | 1990511 | 308 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3814 | 888898 | 37.3826 | -122.0697 | Yes | Clear;32-90 F | Cutout- fuse holder | Normal | 23-0031062 | OH | Sus | 31638748 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1814790 | 0 | Non-EPSS | N | 2023 | A & C
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 32639 | 20230221 | 1323 | 20230303 | 1649 | 2016282 | 14606 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 29212 | 37.172 | -122.0607 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0037614 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1819950 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 32637 | 20230221 | 1323 | 20230302 | 1805 | 2016507 | 13242 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 66210 | 37.1703 | -122.057 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0037681 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1820018 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | FUSE | 2847 | 20230221 | 1325 | 20230221 | 1437 | 1990669 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 1800 | 37.3518 | -122.1019 | Yes | Clear;32-90F |  |  | 23-0031206 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1814890 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MENLO-1103 | 24131103 | RECLOSER | 866118 | 20230221 | 1339 | 20230222 | 1111 | 1990845 | 1292 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 157 | 202844 | 37.3756 | -122.1668 | Yes | Clear;32-90 F |  |  | 23-0032026 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1815625 | 0 | EPSS Ckt | N | 2023 | NONE
DE ANZA | DE ANZA | STELLING-1111 | 83481111 | OCB | 1111/2 | 20230221 | 1344 | 20230222 | 1239 | 1990959 | 1281 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3648 | 843182 | 37.3358 | -122.043 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031126 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1814832 | 0 | EPSS Ckt | N | 2023 | C & GC
DE ANZA | DE ANZA | EL PATIO-1119 | 82921119 | RECLOSER | 47306 | 20230221 | 1352 | 20230221 | 1701 | 1991099 | 189 | Distribution Circuit | Vegetation | Tree - branch fell on line | 823 | 155547 | 37.283 | -121.9226 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0031136 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | No | No | 1814839 | 0 | Non-EPSS | N | 2023 | A-B & C PHASE
DE ANZA | DE ANZA | WOLFE-1113 | 83671113 | TRANSFORMER | 315535131135 | 20230221 | 1357 | 20230221 | 2017 | 1991211 | 380 | Transformer only | Unknown Cause | Patrol - found nothing | 11 | 4180 | 37.3448 | -122.0366 | Yes | Clear;32-90 F |  |  | 23-0031892 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1815490 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1104 | 83421104 | OTHER | WIRE DOWN LD SIDE 29137 | 20230221 | 1400 | 20230223 | 419 | 1995459 | 2299 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1467 | 1011362 | 37.3933 | -121.9922 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031777 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | Yes | Yes | 1815376 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 4451 | 20230221 | 1403 | 20230221 | 2046 | 1991382 | 403 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 11284 | 37.1364 | -121.9687 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0031845 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815442 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WOLFE-1113 | 83671113 | FUSE | 22941 | 20230221 | 1404 | 20230221 | 2255 | 1991260 | 531 | Distribution Circuit | Vegetation | Tree - branch fell on line | 158 | 83898 | 37.3604 | -122.0402 | Yes | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0031943 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815541 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1113 | 83671113 | FUSE | 31699 | 20230221 | 1406 | 20230221 | 1601 | 1991324 | 115 | Distribution Circuit | Vegetation | Tree - branch fell on line | 38 | 4370 | 37.3694 | -122.0443 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0031389 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815030 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | FUSE | 21061 | 20230221 | 1407 | 20230222 | 2136 | 1991264 | 1889 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 21860 | 37.1562 | -121.9895 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031397 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815036 | 1 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1113 | 83421113 | FUSE | 29123 | 20230221 | 1419 | 20230221 | 2200 | 1991408 | 461 | Distribution Circuit | Equipment Failure/Involved | Overhead | 107 | 15240 | 37.3937 | -122.0239 | Yes | Clear;32-90 F | Crossarm- Wood | Broken | 23-0031507 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1815136 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | BRITTON-1110 | 83611110 | RECLOSER | LV38 | 20230221 | 1436 | 20230222 | 1004 | 1991765 | 1168 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1833 | 480732 | 37.3667 | -122.0179 | Yes | Clear-Strong Winds;32-90 F | Connector or Splice (OH) | Normal | 23-0031267 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1814927 | 0 | Non-EPSS | N | 2023 | b/c
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | FUSE | 19449 | 20230221 | 1438 | 20230222 | 1139 | 1991769 | 1261 | Distribution Circuit | Vegetation | Tree - branch fell on line | 248 | 312728 | 37.3228 | -122.0638 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0032195 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815768 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WOLFE-1106 | 83671106 | RECLOSER | LV18 | 20230221 | 1438 | 20230221 | 1500 | 1991799 | 22 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1290 | 28380 | 37.3379 | -122.005 | Yes | Partly Cloudy-Strong Winds;32-90 F |  |  | 23-0031286 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1814944 | 0 | Non-EPSS | N | 2023 | A/C
DE ANZA | DE ANZA | LOS ALTOS-1104 | 82241104 | FUSE | 865 | 20230221 | 1444 | 20230222 | 1321 | 1991833 | 1357 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 37996 | 37.3766 | -122.1161 | Yes | Clear;32-90 F |  |  | 23-0032358 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815856 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | BRITTON-1110 | 83611110 | FUSE | 3341 | 20230221 | 1447 | 20230223 | 221 | 1991908 | 2134 | Distribution Circuit | Equipment Failure/Involved | Overhead | 148 | 236697 | 37.3582 | -122.0052 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Arcing | 23-0032270 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815811 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1113 | 83371113 | FUSE | 53025 | 20230221 | 1450 | 20230223 | 948 | 1997991 | 2578 | Distribution Circuit | Vegetation | Tree - grew into line | 45 | 116010 | 37.2938 | -122.0241 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0032519 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1815953 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1109 | 83481109 | FUSE | 31213 | 20230221 | 1451 | 20230222 | 1544 | 1991955 | 1493 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 97 | 145391 | 37.3157 | -122.0598 | Yes | Clear;32-90 F |  |  | 23-0032491 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815933 | 1 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1104 | 83421104 | FUSE | 12181 | 20230221 | 1455 | 20230222 | 1610 | 1995527 | 1515 | Distribution Circuit | Equipment Failure/Involved | Overhead | 379 | 191081 | 37.3959 | -121.9919 | Yes | Clear;32-90 F | Crossarm- Wood | Broken | 23-0031786 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815385 | 1 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | FUSE | 7163 | 20230221 | 1457 | 20230222 | 150 | 1992038 | 653 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 52240 | 37.2274 | -122.0525 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031709 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815316 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | RECLOSER | 408318 | 20230221 | 1506 | 20230222 | 1052 | 1992178 | 1186 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1007 | 119417 | 37.2474 | -122.0138 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031322 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | Yes | No | 1814976 | 0 | EPSS Ckt | N | 2023 | A/B/C/GRD
DE ANZA | DE ANZA | LAWRENCE-1112 | 83421112 | TRANSFORMER | 315625932802 | 20230221 | 1527 | 20230222 | 1520 | 1992911 | 1433 | Distribution Circuit | Equipment Failure/Involved | Overhead | 185 | 15730 | 37.3915 | -122.0067 | Yes | Partly Cloudy-Strong Winds;32-90 F | Secondary | Deteriorated | 23-0031433 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1815067 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | EL PATIO-1108 | 82921108 | OCB | 1108/2 | 20230221 | 1529 | 20230225 | 2049 | 1992481 | 6061 | Distribution Circuit | Vegetation | Tree - fell into line | 2163 | 3134582 | 37.2915 | -121.9357 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 23-0031369 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815017 | 0 | Non-EPSS | N | 2023 | A & SET A RLY
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | RECLOSER | 60092 | 20230221 | 1532 | 20230222 | 1456 | 1992542 | 1404 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1138 | 205814 | 37.1815 | -121.985 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031368 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815016 | 0 | EPSS Ckt | N | 2023 | SENSITIVE GRD
DE ANZA | DE ANZA | LAWRENCE-1111 | 83421111 | FUSE | 8489 | 20230221 | 1538 | 20230222 | 1822 | 1992669 | 1604 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 36892 | 37.3963 | -122.0035 | Yes | Clear;32-90 F | Crossarm- Wood | Broken | 23-0031548 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815174 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | TRANSFORMER | 315181031495 | 20230221 | 1603 | 20230223 | 1830 | 1992904 | 3027 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 6410 | 37.3532 | -122.1591 | Yes | Clear;32-90 F | Transformer (OH) | Leaking | 23-0033138 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816300 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | EL PATIO-1116 | 82921116 | FUSE | 4797 | 20230221 | 1615 | 20230223 | 2358 | 1993055 | 3343 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 34093 | 37.2908 | -121.9677 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031729 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815333 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1106 | 82031106 | OCB | 1106/2 | 20230221 | 1620 | 20230222 | 1820 | 1993131 | 1560 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3549 | 893574 | 37.3826 | -122.0697 | Yes | Partly Cloudy-Strong Winds;32-90 F | Cutout- fuse holder | Broken | 23-0031473 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815107 | 0 | Non-EPSS | N | 2023 | A- B- GRD &
DE ANZA | DE ANZA | MOUNTAIN VIEW-1113 | 82031113 | RECLOSER | 60060 | 20230221 | 1637 | 20230221 | 1913 | 1991698 | 156 | Distribution Circuit | Vegetation | Tree - branch fell on line | 681 | 106236 | 37.3927 | -122.0768 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0031499 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815129 | 0 | Non-EPSS | N | 2023 | A
DE ANZA | DE ANZA | WOLFE-1113 | 83671113 | FUSE | 22939 | 20230221 | 1644 | 20230222 | 1049 | 1993351 | 1085 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 65 | 70525 | 37.3635 | -122.0416 | Yes | Clear;32-90 F |  |  | 23-0032179 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815756 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1114 | 83371114 | FUSE | 8337 | 20230221 | 1645 | 20230222 | 1647 | 1993361 | 1442 | Distribution Circuit | Vegetation | Tree - grew into line | 212 | 305704 | 37.32 | -121.9994 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0032267 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815810 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1110 | 82031110 | OCB | 1110/2 | 20230221 | 1657 | 20230222 | 1459 | 1995186 | 1322 | Distribution Circuit | Vegetation | Tree - fell into line | 2889 | 1579514 | 37.3826 | -122.0696 | Yes | Partly Cloudy-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0031775 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815374 | 0 | Non-EPSS | N | 2023 | A/C/GRD TIME 51
DE ANZA | DE ANZA | MOUNTAIN VIEW-1110 | 82031110 | SWITCH | 6629 | 20230221 | 1657 | 20230222 | 1146 | 1996297 | 1129 | Distribution Circuit | Vegetation | Tree - fell into line | 491 | 554339 | 37.3733 | -122.064 | Yes | Partly Cloudy;32-90 F | Switch (OH) | Burned/flashed | 23-0031775 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815601 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOYOLA-0403 | 82160403 | TRANSFORMER | 315354932419 | 20230221 | 1658 | 20230222 | 102 | 1993530 | 484 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 3588 | 37.3796 | -122.0995 | Yes | Clear;32-90 F | Secondary | Burned/flashed | 23-0031991 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1815588 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1104 | 82241104 | FUSE | 4577 | 20230221 | 1726 | 20230222 | 331 | 1993992 | 605 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 235 | 142175 | 37.3796 | -122.1128 | Yes | Partly Cloudy;32-90 F |  |  | 23-0031980 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815577 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WHISMAN-1106 | 83631106 | RECLOSER | 60000 | 20230221 | 1739 | 20230223 | 45 | 1994104 | 1866 | Distribution Circuit | Equipment Failure/Involved | Overhead | 889 | 161454 | 37.4145 | -122.0946 | Yes | Partly Cloudy-Strong Winds;32-90 F | Jumper | Broken | 23-0031629 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815251 | 0 | Non-EPSS | N | 2023 | A
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | SWITCH | 60120 | 20230221 | 1829 | 20230223 | 259 | 1998033 | 1950 | Distribution Circuit | Vegetation | Tree - fell into line | 691 | 1101940 | 37.1302 | -121.9784 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032528 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815957 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | JUMPER | CREATE OIS FOR SB19 | 20230221 | 1829 | 20230228 | 1930 | 2012199 | 10141 | Distribution Circuit | Environmental/External | Ice or snow | 62 | 628742 | 37.1647 | -122.0152 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036365 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1819030 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | JUMPER | VERTICAL JUMPERS 1 SPAN SS OF 315600224623 | 20230221 | 1829 | 20230305 | 1117 | 2016319 | 16848 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 33696 | 37.1668 | -122.0414 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037622 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1819958 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | JUMPER | VERTICAL JUMPERS 1 SPAN SS OF 315600224623 | 20230221 | 1829 | 20230305 | 1117 | 2016320 | 16848 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 84240 | 37.1668 | -122.0412 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037622 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1819959 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | JUMPER | OPEN JUMPERS @ CGC 315497024625 | 20230221 | 1830 | 20230416 | 1321 | 2016514 | 77451 | Distribution Circuit | Environmental/External | Ice or snow | 5 | 185322 | 37.1666 | -122.0455 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0037682 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1820020 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | OCB | 1107/2 | 20230221 | 1834 | 20230223 | 1830 | 1995007 | 2876 | Distribution Circuit | Vegetation | Tree - fell into line | 2377 | 667467 | 37.281 | -122.0156 | Yes | Clear;32-90 F | Crossarm- Wood | Broken | 23-0031722 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | No | No | 1815328 | 0 | EPSS Ckt | N | 2023 | B/C/GRD
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | JUMPER | OPEN JUMPERS 3 POLES SS OF 4533 | 20230221 | 1839 | 20230302 | 1350 | 2016298 | 12671 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 164723 | 37.1729 | -122.0614 | Yes |  | Conductor- Overhead | Broken- wire on ground | 23-0037619 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1819956 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 2979 | 20230221 | 1839 | 20230222 | 1715 | 1995057 | 1281 | Distribution Circuit | Vegetation | Tree - branch fell on line | 47 | 63732 | 37.1018 | -121.9225 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0032570 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815992 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1114 | 83371114 | TRANSFORMER | 315603629201 | 20230221 | 1857 | 20230222 | 1904 | 1995210 | 1447 | Transformer only | Vegetation | Tree - grew into line | 15 | 21705 | 37.2921 | -122.0123 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 23-0031931 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815529 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | FUSE | 1625 | 20230221 | 1903 | 20230223 | 210 | 1995400 | 1867 | Distribution Circuit | Equipment Failure/Involved | Overhead | 82 | 103744 | 37.3466 | -122.1206 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0032494 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815935 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1102 | 82031102 | JUMPER | FIRE @ W/OF CGC 3153722833222 | 20230221 | 1911 | 20230222 | 1819 | 1995991 | 1388 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 4983 | 568336 | 37.4013 | -122.0937 | Yes | Partly Cloudy;32-90 F | Crossarm- Wood | Burned/flashed | 23-0031886 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1815484 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1114 | 82031114 | RECLOSER | LM12 | 20230221 | 1914 | 20230222 | 605 | 1995674 | 651 | Distribution Circuit | Vegetation | Tree - branch fell on line | 153 | 84903 | 37.3667 | -122.0788 | Yes | Partly Cloudy-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0031866 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815464 | 0 | Non-EPSS | N | 2023 | B/GRD
DE ANZA | DE ANZA | LAWRENCE-1104 | 83421104 | FUSE | 12181 | 20230221 | 2059 | 20230222 | 1038 | 1996037 | 819 | Distribution Circuit | Equipment Failure/Involved | Overhead | 328 | 226584 | 37.3959 | -121.9919 | Yes | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0031960 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815558 | 1 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1102 | 82031102 | TRANSFORMER | 315434632666 | 20230221 | 2100 | 20230222 | 2037 | 1996172 | 1417 | Transformer only | Vegetation | Tree - fell into line | 11 | 15587 | 37.3866 | -122.0724 | Yes | Partly Cloudy-Strong Winds;32-90 F | Secondary | Broken- wire on ground | 23-0031886 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815530 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1104 | 83421104 | TRANSFORMER | 315677232897 | 20230221 | 2132 | 20230222 | 2253 | 1996045 | 1521 | Transformer only | Equipment Failure/Involved | Overhead | 27 | 41067 | 37.394 | -121.9891 | Yes | Partly Cloudy;32-90 F | Secondary | Broken | 23-0032816 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816161 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | JUMPER | OJ 10033 HILL CREST RD | 20230222 | 214 | 20230222 | 1348 | 1996421 | 694 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 16116 | 37.3238 | -122.0651 | No | Clear;32-90 F | Jumper | Burned Open | 23-0032363 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1815859 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1104 | 82241104 | FUSE | 867 | 20230222 | 714 | 20230222 | 1321 | 1996587 | 367 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 14313 | 37.377 | -122.1164 | No | Clear;32-90 F |  |  | 23-0032393 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815875 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1103 | 83371103 | FUSE | 15767 | 20230222 | 826 | 20230222 | 1424 | 1996816 | 358 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 2148 | 37.2364 | -122.0662 | No | Clear;32-90 F |  |  | 23-0032460 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815909 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1107 | 82031107 | FUSE | 1715 | 20230222 | 857 | 20230222 | 2055 | 1996901 | 718 | Distribution Circuit | Vegetation | Tree - branch fell on line | 185 | 83485 | 37.3738 | -122.0827 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0032465 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1815914 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1108 | 83371108 | TRANSFORMER | 315730228957 | 20230222 | 1300 | 20230222 | 1350 | 1994716 | 50 | Transformer only | Vegetation | Tree - grew into line | 12 | 600 | 37.286 | -121.9688 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0032439 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815897 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1102 | 82031102 | TRANSFORMER | 315372833222 | 20230223 | 1 | 20230224 | 1123 | 1998751 | 2122 | Transformer only | Equipment Failure/Involved | Overhead | 30 | 63660 | 37.4014 | -122.0941 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0033321 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816394 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1113 | 82031113 | FUSE | 52254 | 20230223 | 33 | 20230223 | 321 | 1998755 | 168 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 47 | 7896 | 37.3935 | -122.0786 | Yes | Clear;32-90 F |  |  | 23-0032825 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816170 | 1 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOYOLA-0403 | 82160403 | TRANSFORMER | 315354932419 | 20230223 | 834 | 20230224 | 1251 | 1998997 | 1697 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 11879 | 37.3796 | -122.0995 | Yes | Clear;32-90 F | Secondary | Arcing | 23-0033454 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1816484 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | RECLOSER | LA64 | 20230223 | 1038 | 20230302 | 1059 | 1999256 | 10101 | Distribution Circuit | Equipment Failure/Involved | Overhead | 337 | 61072 | 37.1372 | -121.9674 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken | 23-0033038 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816259 | 0 | EPSS Ckt | N | 2023 | C PHASE & GRD
DE ANZA | DE ANZA | HICKS-1109 | 83431109 | TRANSFORMER | 315843727683 | 20230223 | 1117 | 20230223 | 1151 | 1999337 | 34 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 340 | 37.2516 | -121.9291 | Yes | Overcast-Drizzle;32-90 F | Secondary | Broken- wire on ground | 23-0033078 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1816275 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WHISMAN-1108 | 83631108 | FUSE | 18211 | 20230223 | 1404 | 20230223 | 1528 | 1999625 | 84 | Distribution Circuit | Vegetation | Tree - bark fell into line | 264 | 22176 | 37.4026 | -122.0875 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0033258 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816357 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 32135 | 20230223 | 1919 | 20230304 | 1958 | 2010401 | 12999 | Distribution Circuit | Environmental/External | Ice or snow | 13 | 168987 | 37.1648 | -121.9266 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0035858 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818680 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1111 | 83481111 | TRANSFORMER | 315433830908 | 20230223 | 1937 | 20230224 | 1023 | 2000259 | 886 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 4430 | 37.3385 | -122.0714 | Yes | Clear;32-90 F | Conductor- Overhead | Arcing | 23-0033407 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1816441 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | OTHER | WIRE DOWN CGC 315667624022 | 20230223 | 1953 | 20230303 | 1636 | 2000370 | 11323 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 226310 | 37.1524 | -121.9896 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033428 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1816460 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-0403 | 82160403 | TRANSFORMER | 315373432027 | 20230223 | 2031 | 20230224 | 1548 | 2000479 | 1157 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 16198 | 37.3689 | -122.0929 | Yes | Partly Cloudy-Rain;32-90 F | Secondary | Normal | 23-0034015 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1816981 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | FUSE | 32515 | 20230223 | 2055 | 20230303 | 1950 | 2010830 | 11455 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 34365 | 37.1444 | -122.0018 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035946 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818756 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | FUSE | 33577 | 20230223 | 2103 | 20230301 | 1055 | 2014978 | 8032 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 24096 | 37.1583 | -122.0046 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0037262 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1819699 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | HICKS-1115 | 83431115 | RECLOSER | 12494 | 20230223 | 2234 | 20230223 | 2334 | 2000817 | 60 | Distribution Circuit | Vegetation | Tree - branch fell on line | 535 | 32100 | 37.2435 | -121.9378 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0033475 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816505 | 0 | EPSS Ckt | N | 2023 | B & C PHASE
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 3459 | 20230223 | 2323 | 20230304 | 1330 | 2000917 | 12367 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 1156518 | 37.1288 | -121.9532 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on object | 23-0033527 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816559 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-0403 | 82160403 | TRANSFORMER | 315373632072 | 20230223 | 2325 | 20230224 | 54 | 2000982 | 89 | Transformer only | Vegetation | Tree - fell into line | 14 | 1246 | 37.3702 | -122.0929 | Yes | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0033503 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1816535 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 33349 | 20230224 | 23 | 20230304 | 1401 | 2018700 | 12338 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 795922 | 37.1268 | -121.9572 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038343 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1820534 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | RECLOSER | 60124 | 20230224 | 28 | 20230228 | 1313 | 2001285 | 6525 | Distribution Circuit | Environmental/External | Ice or snow | 315 | 627857 | 37.1462 | -121.9823 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Underground | Broken | 23-0033522 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816554 | 0 | EPSS Ckt | N | 2023 | C PHASE & GRD
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | TRIP-SAVER | 11533 | 20230224 | 28 | 20230303 | 1953 | 2010307 | 11245 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 236145 | 37.1428 | -121.9942 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035821 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818643 | 0 | EPSS Ckt | N | 2023 | UNKNOWN
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | FUSE | 32331 | 20230224 | 28 | 20230303 | 1953 | 2010832 | 11245 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 146185 | 37.1445 | -122.0037 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035947 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818757 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | JUMPER | OJ @ NON-EXISTING 33579 | 20230224 | 28 | 20230303 | 112 | 2019120 | 10124 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 50620 | 37.1524 | -121.9949 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken | 23-0038462 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1820652 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | FUSE | 957387 | 20230224 | 28 | 20230303 | 1854 | 2019151 | 11186 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 268464 | 37.1322 | -121.9999 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038472 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1820662 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | FUSE | 29539 | 20230224 | 32 | 20230303 | 1438 | 2019737 | 10926 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 131112 | 37.1284 | -122.0022 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038737 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1820825 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | RECLOSER | 812664 | 20230224 | 32 | 20230301 | 1941 | 2001322 | 8349 | Distribution Circuit | Environmental/External | Ice or snow | 78 | 268950 | 37.1844 | -121.9828 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033525 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1816557 | 0 | EPSS Ckt | N | 2023 | A B C TIME
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | FUSE | 2459 | 20230224 | 33 | 20230304 | 1838 | 2010864 | 12605 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 189075 | 37.1441 | -121.9902 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0035953 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818762 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | SWITCH | 992943 | 20230224 | 33 | 20230303 | 2116 | 2010868 | 11323 | Distribution Circuit | Vegetation | Tree - branch fell on line | 62 | 592725 | 37.1412 | -121.9951 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0035955 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1818765 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | FUSE | 17121 | 20230224 | 33 | 20230304 | 1622 | 2010871 | 12469 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 420528 | 37.1635 | -122.0141 | Yes |  | Conductor- Overhead | Broken- wire on ground | 23-0035957 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818767 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | FUSE | 19947 | 20230224 | 34 | 20230302 | 1917 | 2018079 | 9763 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 419809 | 37.1309 | -122.0006 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038062 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1820332 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | FUSE | 19949 | 20230224 | 34 | 20230304 | 1426 | 2020047 | 12352 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 284096 | 37.1224 | -122.0053 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038852 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1820892 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | JUMPER | OJ 1 N/O CGC# 5295 | 20230224 | 210 | 20230305 | 1745 | 2022883 | 13895 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 13895 | 37.1849 | -122.0255 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035848 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1821823 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1103 | 83371103 | OTHER | WIRE DOWN 16250 SANBON RE | 20230224 | 211 | 20230305 | 2315 | 2001784 | 14224 | Distribution Circuit | Equipment Failure/Involved | Overhead | 161 | 266759 | 37.2339 | -122.0595 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033589 | OH | Sus | 45680844 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1816625 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 7651 | 20230224 | 216 | 20230302 | 1545 | 2008922 | 9449 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 66143 | 37.1945 | -122.0225 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0035375 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1818212 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 7653 | 20230224 | 216 | 20230302 | 1801 | 2009540 | 9585 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 9585 | 37.1987 | -122.0304 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035576 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1818428 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | JUMPER | OPEN JUMPER LOAD SIDE 315532525940 | 20230224 | 236 | 20230305 | 1318 | 2020858 | 13602 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 68010 | 37.2017 | -122.0354 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0039364 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1821243 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | FUSE | 12075 | 20230224 | 240 | 20230303 | 1750 | 2021436 | 10990 | Distribution Circuit | Environmental/External | Ice or snow | 2 | 21980 | 37.259 | -122.1225 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0039517 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1821333 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1103 | 83371103 | FUSE | 11911 | 20230224 | 250 | 20230305 | 2007 | 2005858 | 13997 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 55988 | 37.2502 | -122.0835 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033589 | OH | Sus | 45680844 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | Yes | No | 1817206 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | JUMPER | OJ HS OF 988311 | 20230224 | 250 | 20230301 | 1857 | 2005865 | 8167 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 8167 | 37.2579 | -122.0926 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 23-0033589 | OH | Sus | 45680844 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1817207 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1106 | 82241106 | OCB | 1106/2 | 20230224 | 253 | 20230225 | 124 | 2002047 | 1312 | Distribution Circuit | Equipment Failure/Involved | Underground | 2665 | 242442 | 37.3936 | -122.1149 | Yes | Partly Cloudy-Heavy Rain;32-90 F | Elbow | Broken | 23-0033591 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816627 | 0 | Non-EPSS | N | 2023 | B & GRD
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 4437 | 20230224 | 259 | 20230304 | 400 | 2010524 | 11581 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 173715 | 37.1514 | -121.9783 | Yes | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035894 | OH | Sus | 35427380 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818708 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | JUMPER | OJ 2 POLES N/W OF LA30 | 20230224 | 259 | 20230302 | 1059 | 2011944 | 9120 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 18240 | 37.1244 | -121.9384 | Yes | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036299 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818984 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | JUMPER | FLOATER 2 POLES N/W OF 12437 | 20230224 | 259 | 20230302 | 1059 | 2012464 | 9120 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 72960 | 37.1267 | -121.9432 | Yes | Overcast-Snow;32-90 F | Conductor- Overhead | Normal | 23-0036457 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1819082 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | RECLOSER | 60116 | 20230224 | 304 | 20230302 | 1059 | 2002136 | 9049 | Distribution Circuit | Vegetation | Tree - fell into line | 647 | 2309024 | 37.1735 | -121.9928 | Yes | Overcast-Rain;32-90 F | Jumper | Broken | 23-0033597 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816633 | 0 | EPSS Ckt | N | 2023 | A & C
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 7629 | 20230224 | 304 | 20230225 | 2010 | 2005721 | 2466 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 17262 | 37.1661 | -121.9959 | Yes | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033597 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1817116 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 17431 | 20230224 | 307 | 20230305 | 1355 | 2013160 | 13608 | Distribution Circuit | Environmental/External | Ice or snow | 34 | 462672 | 37.1103 | -121.9511 | Yes | Overcast-Rain;32-90 F | Conductor- Underground | Broken | 23-0036649 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1819221 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 4463 | 20230224 | 307 | 20230306 | 1137 | 2013168 | 14910 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 1477418 | 37.1071 | -121.9472 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036650 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1819222 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 10003 | 20230224 | 307 | 20230305 | 2235 | 2019255 | 14128 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 324944 | 37.1039 | -121.95 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038533 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1820716 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 2911 | 20230224 | 307 | 20230306 | 1138 | 2019263 | 14911 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 29822 | 37.099 | -121.9476 | Yes | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0038538 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1820721 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 21105 | 20230224 | 307 | 20230306 | 1710 | 2020356 | 15243 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 15243 | 37.0984 | -121.9475 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0039013 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | Yes | No | 1821009 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 2909 | 20230224 | 324 | 20230302 | 1141 | 2002133 | 9137 | Distribution Circuit | Environmental/External | Ice or snow | 38 | 347206 | 37.1115 | -121.9459 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken | 23-0033630 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1818843 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 29297 | 20230224 | 324 | 20230302 | 1141 | 2011009 | 9137 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 73096 | 37.1065 | -121.9449 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033630 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818844 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | FUSE | 21061 | 20230224 | 334 | 20230302 | 2019 | 2010887 | 9645 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 114174 | 37.1562 | -121.9895 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035962 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818771 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | FUSE | 21055 | 20230224 | 335 | 20230303 | 344 | 2010874 | 10089 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 221958 | 37.152 | -121.9934 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035959 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818769 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | FUSE | 21063 | 20230224 | 340 | 20230301 | 2051 | 2010880 | 8231 | Distribution Circuit | Environmental/External | Ice or snow | 7 | 57617 | 37.156 | -121.9878 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken | 23-0035960 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1818770 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | JUMPER | OJ 1 P/E/O CGC# 315654024149 | 20230224 | 340 | 20230303 | 1211 | 2019101 | 10591 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 95319 | 37.1535 | -121.9918 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0038457 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1820646 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | JUMPER | OJ 1 P/W/O 315671824133 | 20230224 | 340 | 20230304 | 411 | 2019108 | 11551 | Distribution Circuit | Environmental/External | Ice or snow | 2 | 23102 | 37.1535 | -121.9872 | Yes | Clear;32-90F | Conductor- Underground | Broken | 23-0038459 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1820647 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | SWITCH | SA27 | 20230224 | 340 | 20230301 | 2053 | 2002242 | 8233 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 823300 | 37.157 | -121.9867 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken | 23-0033597 | OH | Sus | 35427380 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816650 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | BIG BASIN-1102 | 82841102 | FUSE | 19873 | 20230224 | 359 | 20230304 | 1731 | 2021010 | 12332 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 123320 | 37.2539 | -122.1238 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039333 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1821228 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | BIG BASIN-1102 | 82841102 | TRANSFORMER | 315285027925 | 20230224 | 359 | 20230305 | 1650 | 2021676 | 13731 | Transformer only | Vegetation | Tree - fell into line | 1 | 13731 | 37.2553 | -122.1218 | Yes | Clear;32-90F | Transformer (OH) | Normal | 23-0039601 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1821381 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | BIG BASIN-1102 | 82841102 | FUSE | 8051 | 20230224 | 359 | 20230304 | 1435 | 2021687 | 12156 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 328212 | 37.254 | -122.1235 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039615 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1821398 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | BIG BASIN-1102 | 82841102 | FUSE | 223709 | 20230224 | 359 | 20230304 | 1500 | 2021690 | 12181 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 60905 | 37.2525 | -122.1249 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039616 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1821399 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | BIG BASIN-1102 | 82841102 | FUSE | 31997 | 20230224 | 359 | 20230304 | 1540 | 2021692 | 12221 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 134431 | 37.2469 | -122.1273 | Yes | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0039617 | OH | Sus | 35427382 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1821400 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | RECLOSER | 568350 | 20230224 | 359 | 20230303 | 1402 | 2002421 | 10683 | Distribution Circuit | Vegetation | Tree - fell into line | 152 | 1387338 | 37.3221 | -122.0795 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033626 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816664 | 0 | EPSS Ckt | N | 2023 | B & TIME
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | FUSE | 805 | 20230224 | 359 | 20230305 | 1610 | 2006239 | 13691 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 27382 | 37.2569 | -122.1182 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034372 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1817241 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | JUMPER | OJS @ 3 SPANS SS OF 805 | 20230224 | 359 | 20230303 | 1745 | 2008437 | 10906 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 10906 | 37.2582 | -122.1203 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0035217 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1818065 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | RECLOSER | 60094 | 20230224 | 359 | 20230304 | 655 | 2016476 | 11696 | Distribution Circuit | Equipment Failure/Involved | Overhead | 216 | 2344655 | 37.2574 | -122.1202 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037670 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1820007 | 0 | EPSS Ckt | N | 2023 | NONE
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 12741 | 20230224 | 407 | 20230303 | 1737 | 2010738 | 10890 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 392040 | 37.1509 | -121.9736 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035925 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1818738 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 4449 | 20230224 | 410 | 20230302 | 1459 | 2009873 | 9289 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 74312 | 37.1396 | -121.9674 | Yes | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on object | 23-0035664 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818507 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 1429 | 20230224 | 410 | 20230227 | 1821 | 2010165 | 5171 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 72394 | 37.1476 | -121.9748 | Yes | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035756 | OH | Sus | 35427380 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818591 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | JUMPER | 8269 CUT IN CLEAR DUE TO TROUBLE | 20230224 | 410 | 20230228 | 2046 | 2010685 | 6756 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 40536 | 37.1513 | -121.9771 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0035898 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818711 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 4457 | 20230224 | 410 | 20230304 | 1729 | 2010780 | 12319 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 123043 | 37.1277 | -121.9467 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035932 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1818745 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 4451 | 20230224 | 410 | 20230303 | 1625 | 2011736 | 10815 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 262189 | 37.1364 | -121.9687 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on object | 23-0036229 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818950 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 3461 | 20230224 | 410 | 20230304 | 1745 | 2012029 | 12335 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 12335 | 37.1253 | -121.9385 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036314 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1819003 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | JUMPER | OJ 2 POLES N/W OF RISER 12437 | 20230224 | 410 | 20230303 | 2105 | 2012471 | 11095 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 11095 | 37.1272 | -121.9441 | Yes | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036459 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1819083 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | SWITCH | 2045 | 20230224 | 410 | 20230305 | 1807 | 2012924 | 13797 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 820443 | 37.1359 | -121.9663 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036600 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1819177 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 21067 | 20230224 | 410 | 20230301 | 1743 | 2015510 | 8013 | Distribution Circuit | Environmental/External | Ice or snow | 15 | 120195 | 37.1574 | -121.9868 | Yes | Overcast-Snow;32-90 F | Conductor- Underground | Broken | 23-0037373 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1819779 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | JUMPER | OPEN FUCO 31437 | 20230224 | 410 | 20230228 | 2103 | 2016480 | 6773 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 13546 | 37.1459 | -121.9713 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0037672 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1820009 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 30285 | 20230224 | 410 | 20230306 | 1438 | 2024024 | 15028 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 15028 | 37.1352 | -121.9763 | Yes | Overcast-Drizzle;32-90 F | Pole-Wood | Broken | 23-0036600 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1822172 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 959 | 20230224 | 414 | 20230304 | 1740 | 2016333 | 12326 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 160238 | 37.1287 | -121.951 | Yes | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken | 23-0035148 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1819964 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | SWITCH | SA53 | 20230224 | 416 | 20230301 | 1349 | 2002461 | 7773 | Distribution Circuit | Environmental/External | Ice or snow | 70 | 544110 | 37.1151 | -121.9392 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken | 23-0033630 | OH | Sus | 35427382 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1816668 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 2903 | 20230224 | 421 | 20230301 | 1723 | 2011917 | 7982 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 103766 | 37.1145 | -121.9385 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036290 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818981 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | FUSE | 4521 | 20230224 | 427 | 20230302 | 1937 | 2018287 | 9550 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 95500 | 37.278 | -122.1118 | Yes | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0038176 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1820406 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | RECLOSER | LB44 | 20230224 | 432 | 20230302 | 1801 | 2002565 | 9449 | Distribution Circuit | Environmental/External | Ice or snow | 103 | 622704 | 37.1938 | -121.9958 | Yes | Overcast-Rain;32-90 F | Crossarm- Wood | Broken | 23-0033645 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816683 | 0 | EPSS Ckt | N | 2023 | SGF
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 4415 | 20230224 | 432 | 20230226 | 2312 | 2009321 | 4000 | Distribution Circuit | Vegetation | Tree - fell into line | 107 | 428000 | 37.1936 | -121.9984 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0035473 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1818320 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | SWITCH | 374035 | 20230224 | 432 | 20230304 | 1921 | 2010375 | 12141 | Distribution Circuit | Environmental/External | Ice or snow | 108 | 1319250 | 37.1941 | -122.0218 | Yes | Overcast-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0035848 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818670 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 29973 | 20230224 | 432 | 20230305 | 500 | 2010916 | 12988 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 12988 | 37.193 | -122.0167 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0035963 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1818772 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | JUMPER | OPEN JUMPERS 4 POLES WEST OF 29533 | 20230224 | 432 | 20230304 | 1138 | 2020336 | 11946 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 35838 | 37.1903 | -122.0399 | Yes | Clear;32-90F | Crossarm- Wood | Broken | 23-0039008 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1821004 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 2917 | 20230224 | 433 | 20230306 | 1130 | 2013582 | 14817 | Distribution Circuit | Equipment Failure/Involved | Overhead | 114 | 1115377 | 37.1092 | -121.9354 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0036733 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1819293 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | FUSE | 8347 | 20230224 | 438 | 20230302 | 322 | 2010859 | 8564 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 453892 | 37.1365 | -121.9843 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035951 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818760 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | RECLOSER | 60118 | 20230224 | 447 | 20230302 | 2018 | 2002559 | 9571 | Distribution Circuit | Vegetation | Tree - fell into line | 350 | 2712272 | 37.1247 | -121.9353 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033649 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1816687 | 0 | EPSS Ckt | N | 2023 | N/A
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 2915 | 20230224 | 447 | 20230303 | 1622 | 2006189 | 10775 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 305512 | 37.1095 | -121.938 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034351 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1817225 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | SWITCH | 386901 | 20230224 | 447 | 20230303 | 1545 | 2009390 | 10738 | Distribution Circuit | Vegetation | Tree - branch fell on line | 130 | 1084499 | 37.1203 | -121.9228 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0035497 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1818345 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 8977 | 20230224 | 450 | 20230228 | 1038 | 2002526 | 6108 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 36648 | 37.1846 | -122.0033 | Yes | Clear;32-90F | Pole-Wood | Normal | 23-0035449 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1818297 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MENLO-1103 | 24131103 | RECLOSER | 866118 | 20230224 | 508 | 20230224 | 1100 | 2002715 | 352 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 157 | 55264 | 37.3756 | -122.1668 | Yes | Overcast-Rain;32-90 F |  |  | 23-0033664 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816702 | 0 | EPSS Ckt | N | 2023 | SGF INST
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | TRIP-SAVER | 2243 | 20230224 | 542 | 20230302 | 1937 | 2018289 | 9475 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 265300 | 37.2777 | -122.1116 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken | 23-0038176 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1820408 | 0 | EPSS Ckt | N | 2023 | N/A
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | FUSE | 17499 | 20230224 | 704 | 20230303 | 1511 | 2010866 | 10567 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 372040 | 37.1521 | -121.9977 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035954 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818764 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | RECLOSER | 60092 | 20230224 | 729 | 20230224 | 2045 | 2003830 | 796 | Distribution Circuit | Equipment Failure/Involved | Overhead | 201 | 159996 | 37.1815 | -121.985 | Yes | Overcast-Snow;32-90 F | Secondary | Deteriorated | 23-0033770 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816793 | 0 | EPSS Ckt | N | 2023 | SGF
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 18123 | 20230224 | 815 | 20230304 | 1608 | 2018351 | 11993 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 215874 | 37.1324 | -121.9571 | Yes | Overcast-Drizzle;32-90 F | Other | Broken | 23-0038200 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1820429 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | JUMPER | OJ @ CGC# 315761323258 | 20230224 | 923 | 20230304 | 2334 | 2018360 | 12371 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 24742 | 37.1297 | -121.9547 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038205 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1820434 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1108 | 83771108 | TRANSFORMER | 315773727393 | 20230224 | 943 | 20230224 | 1226 | 2004816 | 163 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 1793 | 37.2432 | -121.9531 | Yes | Overcast-Rain;32-90 F | Crossarm- Wood | Broken | 23-0033904 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1816896 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1113 | 83421113 | TRANSFORMER | 315561232825 | 20230224 | 957 | 20230224 | 1723 | 2004875 | 446 | Transformer only | Vegetation | Tree - fell into line | 16 | 7136 | 37.3919 | -122.0289 | Yes | Overcast-Rain;32-90 F | Secondary | Normal | 23-0033928 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1816917 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MENLO-1103 | 24131103 | RECLOSER | 866118 | 20230224 | 1101 | 20230224 | 1717 | 2005107 | 376 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 157 | 43277 | 37.3756 | -122.1668 | Yes | Overcast-Drizzle;32-90 F |  |  | 23-0033664 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816985 | 0 | EPSS Ckt | N | 2023 | B- C- 51
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 5051 | 20230224 | 1430 | 20230301 | 1933 | 2016401 | 7503 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 112545 | 37.1056 | -121.911 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037652 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1819988 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 4435 | 20230224 | 1510 | 20230225 | 2022 | 2006550 | 1752 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 47304 | 37.1664 | -121.9895 | Yes | Clear;32-90 F | Conductor- Overhead | On Ground | 23-0034460 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1817313 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1103 | 83371103 | FUSE | 32569 | 20230224 | 2254 | 20230301 | 1615 | 2007372 | 6801 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 20403 | 37.2306 | -122.0423 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0035167 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1818018 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | RECLOSER | 60092 | 20230224 | 2259 | 20230224 | 2310 | 2007375 | 11 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 202 | 2222 | 37.1815 | -121.985 | Yes | Clear;32-90 F |  |  | 23-0034989 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | No | No | 1817854 | 0 | EPSS Ckt | N | 2023 | A & B
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | RECLOSER | 60092 | 20230225 | 6 | 20230228 | 220 | 2007417 | 4454 | Distribution Circuit | Equipment Failure/Involved | Overhead | 201 | 206684 | 37.1815 | -121.985 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0035000 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1817867 | 0 | EPSS Ckt | N | 2023 | A & B
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | OTHER | WIRE DOWN @ SS OF CGC #4771 | 20230225 | 405 | 20230302 | 505 | 2007616 | 7260 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 126660 | 37.1708 | -121.9935 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035379 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1818217 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | FUSE | 29423 | 20230225 | 1936 | 20230226 | 2325 | 2009335 | 1669 | Distribution Circuit | Equipment Failure/Involved | Overhead | 151 | 252019 | 37.3704 | -122.1119 | Yes | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0035490 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1818337 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1103 | 83371103 | FUSE | 15767 | 20230226 | 430 | 20230226 | 1448 | 2009647 | 618 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 3708 | 37.2364 | -122.0662 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0035591 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1818444 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1110 | 82031110 | FUSE | 30617 | 20230226 | 1308 | 20230301 | 128 | 2017242 | 3620 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 101360 | 37.3617 | -122.0562 | Yes | Overcast;32-90 F | Secondary | Broken- wire on ground | 23-0037854 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1820184 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | TRANSFORMER | 315574528521 | 20230226 | 1636 | 20230226 | 1753 | 2010368 | 77 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 847 | 37.2733 | -122.0219 | Yes | Clear;32-90 F | Fuse | Broken | 23-0035887 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1818702 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1108 | 83371108 | RECLOSER | LC106 | 20230226 | 1859 | 20230226 | 1956 | 2010743 | 57 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 2590 | 147630 | 37.2825 | -121.9942 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0035942 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1818753 | 0 | Non-EPSS | N | 2023 | B & C PHASE
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | JUMPER | BURNT OJS 2P E/OF 925 | 20230227 | 457 | 20230227 | 1327 | 2011151 | 510 | Distribution Circuit | Equipment Failure/Involved | Overhead | 151 | 15774 | 37.3714 | -122.1174 | Yes | Clear;32-90F | Conductor- Overhead | Burned/flashed | 23-0036423 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1819064 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1104 | 82031104 | TRANSFORMER | 315383633410 | 20230227 | 2242 | 20230301 | 1050 | 2013961 | 2168 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 39024 | 37.407 | -122.0902 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0037034 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1819568 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1108 | 83371108 | TRANSFORMER | 315720928953 | 20230228 | 1025 | 20230302 | 1306 | 2014843 | 3041 | Transformer only | Vegetation | Tree - palm frond fell into line | 5 | 15205 | 37.2858 | -121.9719 | Yes | Clear;32-90F | Transformer (OH) | Burned/flashed | 23-0037403 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1819811 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1113 | 83671113 | FUSE | 18455 | 20230228 | 2300 | 20230301 | 211 | 2017146 | 191 | Distribution Circuit | Equipment Failure/Involved | Overhead | 58 | 11078 | 37.3486 | -122.0461 | Yes | Clear;32-90F | Crossarm- Wood | Broken | 23-0037844 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1820174 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1102 | 82031102 | TRANSFORMER | 315359533357 | 20230301 | 1245 | 20230301 | 1825 | 2018288 | 340 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 3740 | 37.4051 | -122.0987 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 23-0038428 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1820629 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1109 | 83371109 | FUSE | 2091 | 20230301 | 1826 | 20230301 | 2319 | 2018997 | 293 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 37 | 10841 | 37.2806 | -121.9898 | No | Clear;32-90F |  |  | 23-0038549 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1820732 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1108 | 83371108 | TRANSFORMER | 315738929046 | 20230302 | 16 | 20230303 | 514 | 2018916 | 1738 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 13904 | 37.2884 | -121.9659 | No | Clear;32-90 F | Transformer | Broken | 23-0038550 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1820734 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | RECLOSER | 60116 | 20230302 | 1009 | 20230302 | 1018 | 2019089 | 9 | Distribution Circuit | Vegetation | Tree - branch fell on line | 563 | 5067 | 37.1735 | -121.9928 | No | Clear;32-90 F | Recloser | Normal | 23-0038662 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1820787 | 0 | EPSS Ckt | N | 2023 | NONE
DE ANZA | DE ANZA | EL PATIO-1117 | 82921117 | FUSE | 12819 | 20230302 | 1110 | 20230302 | 1615 | 2019693 | 305 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 4575 | 37.286 | -121.9541 | No | Clear;32-90 F | Fuse | Broken | 23-0038937 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1820949 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | JUMPER | 33579 | 20230302 | 1124 | 20230303 | 646 | 2020510 | 1162 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 6573 | 37.1523 | -121.9929 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0039057 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1821047 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | SWITCH | SA13 | 20230302 | 2039 | 20230304 | 7 | 2020637 | 1648 | Distribution Circuit | Equipment Failure/Involved | Overhead | 64 | 104746 | 37.0991 | -121.8593 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039178 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1821157 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315671024254 | 20230303 | 840 | 20230303 | 1653 | 2020927 | 493 | Transformer only | Vegetation | Tree - fell into line | 6 | 2958 | 37.1565 | -121.9862 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039608 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1821390 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1103 | 83771103 | FUSE | 505 | 20230303 | 1144 | 20230303 | 1313 | 2021223 | 89 | Distribution Circuit | 3rd Party | Metallic Balloon | 124 | 11036 | 37.2691 | -121.9645 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0039470 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1821311 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 2891 | 20230303 | 1308 | 20230304 | 430 | 2021364 | 922 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 3688 | 37.1327 | -121.9415 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0039477 | OH | Sus | 35427380 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1821315 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | FUSE | 15735 | 20230304 | 657 | 20230304 | 1545 | 2022094 | 528 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2640 | 37.2231 | -122.0898 | No | Clear;32-90F | Crossarm- Wood | Broken | 23-0039862 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1821631 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315637023753 | 20230304 | 813 | 20230305 | 2130 | 2022146 | 2237 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 11675 | 37.1435 | -121.9975 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 23-0040337 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1822066 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | TRANSFORMER | 315799022210 | 20230304 | 837 | 20230305 | 2236 | 2022163 | 2279 | Transformer only | Environmental/External | Ice or snow | 1 | 2279 | 37.1011 | -121.9416 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0040289 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1822028 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1111 | 83481111 | FUSE | 89085 | 20230304 | 946 | 20230304 | 1038 | 2022208 | 52 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 1664 | 37.3398 | -122.0701 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0039910 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1821666 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 55449 | 20230304 | 1241 | 20230304 | 1402 | 2022424 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1053 | 37.1275 | -121.9539 | No | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0040008 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1821766 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315607023015 | 20230304 | 1456 | 20230305 | 1829 | 2022568 | 1653 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1653 | 37.1228 | -122.0075 | No | Clear;32-90F | Connector or Splice (OH) | Normal | 23-0040442 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1822175 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315606023057 | 20230304 | 1523 | 20230306 | 537 | 2024043 | 2294 | Transformer only | Environmental/External | Ice or snow | 2 | 4588 | 37.1235 | -122.0081 | No | Clear;32-90 F | Transformer | Normal | 23-0040441 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1822174 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 30193 | 20230304 | 1622 | 20230304 | 1642 | 2022640 | 20 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 60 | 37.1124 | -121.9344 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0040038 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1821786 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | FUSE | 33585 | 20230304 | 1738 | 20230305 | 510 | 2022764 | 692 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 692 | 37.1407 | -121.9714 | No | Clear;32-90F | Crossarm- Wood | Broken | 23-0040057 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1821801 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 611205 | 20230305 | 236 | 20230306 | 1331 | 2023139 | 2095 | Distribution Circuit | Environmental/External | Ice or snow | 53 | 111035 | 37.1087 | -121.8444 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0040213 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1821962 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 23009 | 20230305 | 239 | 20230305 | 1002 | 2023537 | 443 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 69 | 30567 | 37.1673 | -122.0363 | No | Clear;32-90F |  |  | 23-0040284 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1822021 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | TRANSFORMER | 315793322627 | 20230305 | 923 | 20230305 | 1319 | 2023497 | 236 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 472 | 37.1124 | -121.9439 | No | Clear;32-90F |  |  | 23-0040277 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1822015 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | HICKS-1109 | 83431109 | OTHER | J1672 TWD T10201 | 20230305 | 1008 | 20230305 | 1554 | 2023595 | 346 | Distribution Circuit | Equipment Failure/Involved | Underground | 8 | 2768 | 37.2615 | -121.9241 | No | Clear;32-90F | Elbow | Normal | 23-0040408 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1822142 | 1 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 609135 | 20230305 | 1419 | 20230305 | 1745 | 2023792 | 206 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 3708 | 37.1082 | -121.9455 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0040371 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1822094 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 4533 | 20230305 | 1725 | 20230305 | 1816 | 2023971 | 51 | Distribution Circuit | Vegetation | Tree - grew into line | 9 | 459 | 37.1752 | -122.0606 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0040427 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1822157 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | JUMPER | OJ W/OF MTR1010192604 | 20230306 | 1339 | 20230307 | 545 | 2024764 | 966 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1041 | 37.2386 | -122.0729 | No | Clear;32-90F | Conductor- Overhead | Broken | 23-0040778 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1822390 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | BRITTON-1107 | 83611107 | RECLOSER | 79156 | 20230306 | 1432 | 20230307 | 344 | 2024830 | 792 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1051 | 175945 | 37.3656 | -121.9962 | No | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0040813 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1822406 | 0 | Non-EPSS | N | 2023 | B PHASE & GRD
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315628523130 | 20230307 | 1447 | 20230307 | 1946 | 2025748 | 299 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 299 | 37.1256 | -122.0011 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0041337 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1822674 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | TRANSFORMER | 315564728164 | 20230308 | 753 | 20230308 | 1514 | 2026311 | 441 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 3087 | 37.2635 | -122.0251 | No | Overcast-Drizzle;32-90 F | Transformer | Broken | 23-0041622 | OH | Sus | 31639684 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1822887 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1104 | 83371104 | TRANSFORMER | T6345 | 20230308 | 2056 | 20230308 | 2105 | 2027100 | 9 | Transformer only | Equipment Failure/Involved | Underground | 8 | 72 | 37.2533 | -121.9818 | No | Clear;32-90 F | Secondary | Bent or Twisted | 23-0041890 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1823033 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WOLFE-1105 | 83671105 | FUSE | 2621 | 20230309 | 1052 | 20230309 | 1100 | 2027396 | 8 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 224 | 37.3174 | -122.0182 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0042046 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1823092 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | JUMPER | OJ 17700 MONTEBELLO RD | 20230309 | 1350 | 20230310 | 1714 | 2027654 | 1644 | Distribution Circuit | Equipment Failure/Involved | Overhead | 60 | 26965 | 37.301 | -122.1203 | Yes | Overcast-Drizzle;32-90 F | Jumper | Burned Open | 23-0043156 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1823762 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1105 | 83371105 | FUSE | 4999 | 20230309 | 1443 | 20230309 | 1652 | 2027818 | 129 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 108 | 13932 | 37.2674 | -122.0597 | Yes | Clear;32-90F |  |  | 23-0042292 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823167 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | FUSE | 1637 | 20230309 | 1446 | 20230309 | 2125 | 2027807 | 399 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 6265 | 37.3473 | -122.1091 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042264 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1823157 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WOLFE-1106 | 83671106 | FUSE | 29191 | 20230309 | 1455 | 20230309 | 2042 | 2027827 | 347 | Distribution Circuit | Equipment Failure/Involved | Overhead | 44 | 6622 | 37.3404 | -122.0074 | Yes | Overcast-Rain;32-90 F | Secondary | Burned/flashed | 23-0042307 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823174 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1113 | 83671113 | FUSE | 22941 | 20230309 | 1503 | 20230309 | 1734 | 2027857 | 151 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 158 | 23858 | 37.3604 | -122.0402 | Yes | Clear;32-90F |  |  | 23-0042379 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823219 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MENLO-1103 | 24131103 | RECLOSER | 866118 | 20230309 | 1516 | 20230309 | 1522 | 2027820 | 6 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 157 | 942 | 37.3756 | -122.1668 | Yes | Overcast-Drizzle;32-90 F |  |  | 23-0042274 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823160 | 0 | EPSS Ckt | N | 2023 | A & C PHASE
DE ANZA | DE ANZA | MENLO-1103 | 24131103 | FUSE | 731 | 20230309 | 1547 | 20230310 | 1158 | 2027946 | 1211 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 3633 | 37.3692 | -122.1695 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0042399 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823237 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1108 | 83371108 | JUMPER | BURNED OPEN JUMPER TWD 979 | 20230309 | 1610 | 20230309 | 1821 | 2027997 | 130 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3529 | 29131 | 37.2754 | -122.0009 | Yes | Overcast-Drizzle;32-90 F | Jumper | Burned Open | 23-0042389 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1823227 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | JUMPER | OJ'S S/O CGC# 315613825300 | 20230309 | 1612 | 20230309 | 1650 | 2027503 | 38 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 114 | 37.185 | -122.006 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken | 23-0042128 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1823116 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | OCB | 1102/2 | 20230309 | 1614 | 20230310 | 2 | 2028014 | 468 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1357 | 196481 | 37.361 | -122.0992 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042321 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823180 | 0 | EPSS Ckt | N | 2023 | PRI RLY GRD TIME
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | FUSE | 10137 | 20230309 | 1614 | 20230310 | 227 | 2028248 | 613 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 6130 | 37.3629 | -122.1186 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Together | 23-0042369 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | No | No | 1823210 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | FUSE | 15029 | 20230309 | 1614 | 20230310 | 1237 | 2029231 | 1223 | Distribution Circuit | Vegetation | Tree - branch fell on line | 142 | 75758 | 37.3651 | -122.1168 | Yes | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on object | 23-0042512 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1823333 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1106 | 82241106 | FUSE | 30351 | 20230309 | 1619 | 20230309 | 1726 | 2028042 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 402 | 37.3927 | -122.1479 | Yes | Clear;32-90F |  |  | 23-0042358 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823200 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1108 | 83481108 | RECLOSER | LM42 | 20230309 | 1654 | 20230310 | 1317 | 2028145 | 1223 | Distribution Circuit | Vegetation | Tree - bark fell into line | 989 | 289346 | 37.3509 | -122.0789 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Together | 23-0042348 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | No | No | 1823194 | 0 | EPSS Ckt | N | 2023 | ABC
DE ANZA | DE ANZA | SARATOGA-1105 | 83371105 | FUSE | 4999 | 20230309 | 1705 | 20230310 | 1030 | 2028220 | 1045 | Distribution Circuit | Equipment Failure/Involved | Overhead | 108 | 73481 | 37.2674 | -122.0597 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Together | 23-0042388 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823226 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | BRITTON-1111 | 83611111 | INTERRUPTER | 609646 | 20230309 | 1709 | 20230309 | 1925 | 2028182 | 136 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 36 | 4896 | 37.3736 | -122.0136 | Yes | Overcast;32-90 F |  |  | 23-0042457 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823285 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 23009 | 20230309 | 1728 | 20230309 | 2034 | 2028256 | 186 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 79 | 14694 | 37.1673 | -122.0363 | Yes | Clear;32-90F |  |  | 23-0042461 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823289 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | HICKS-1116 | 83431116 | TRANSFORMER | 315843526587 | 20230309 | 1733 | 20230310 | 2040 | 2028307 | 1627 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1627 | 37.2215 | -121.9286 | Yes | Clear;32-90 F | Secondary | Failed/Faulted | 23-0042572 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823391 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1107 | 82031107 | TRANSFORMER | 315367431787 | 20230309 | 1737 | 20230310 | 1710 | 2028422 | 1413 | Distribution Circuit | Vegetation | Tree - grew into line | 10 | 9614 | 37.3623 | -122.0947 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042589 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823406 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1106 | 82241106 | TRANSFORMER | C3283 | 20230309 | 1850 | 20230310 | 2127 | 2031354 | 1597 | Distribution Circuit | Equipment Failure/Involved | Underground | 100 | 24681 | 37.3813 | -122.1166 | Yes | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0043207 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1823800 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | FUSE | 9321 | 20230309 | 1850 | 20230310 | 1232 | 2028673 | 1062 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 18054 | 37.2481 | -122.0243 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0042601 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823415 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1109 | 83481109 | FUSE | 8525 | 20230309 | 1926 | 20230309 | 2227 | 2028989 | 181 | Distribution Circuit | Vegetation | Tree - grew into line | 134 | 24254 | 37.2937 | -122.044 | Yes | Overcast-Heavy Rain;32-90 F | Fuse | Normal | 23-0042587 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823404 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | TRANSFORMER | 315608327682 | 20230309 | 1941 | 20230309 | 2353 | 2029066 | 252 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 504 | 37.2504 | -122.01 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0042646 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823456 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | OCB | 1102/2 | 20230309 | 1948 | 20230310 | 55 | 2028535 | 307 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1125 | 328732 | 37.361 | -122.0992 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0042497 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823321 | 0 | EPSS Ckt | N | 2023 | PHASE
DE ANZA | DE ANZA | SARATOGA-1112 | 83371112 | FUSE | 3769 | 20230309 | 1949 | 20230310 | 1651 | 2029074 | 1262 | Distribution Circuit | Vegetation | Tree - branch fell on line | 205 | 258710 | 37.2864 | -121.998 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0042529 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823349 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MENLO-1103 | 24131103 | TRANSFORMER | T9595 | 20230309 | 1952 | 20230310 | 1350 | 2029123 | 1078 | Distribution Circuit | Equipment Failure/Involved | Underground | 13 | 5289 | 37.3813 | -122.1573 | Yes | Overcast-Rain-Strong Winds;32-90 F | Transformer (UG) | Failed/Faulted | 23-0042726 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823539 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | TRANSFORMER | 315564728164 | 20230309 | 2025 | 20230310 | 1749 | 2029250 | 1284 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 8988 | 37.2635 | -122.0251 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042667 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823475 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1104 | 83371104 | TRANSFORMER | 315660327752 | 20230309 | 2119 | 20230310 | 1241 | 2029417 | 922 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 10142 | 37.2526 | -121.9921 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0042591 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823408 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 30751 | 20230309 | 2140 | 20230312 | 1710 | 2031620 | 4050 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4050 | 37.1706 | -122.0516 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043260 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | Yes | No | 1823847 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 23009 | 20230309 | 2144 | 20230310 | 2126 | 2029506 | 1422 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 78 | 110916 | 37.1673 | -122.0363 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 23-0043139 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1823752 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1106 | 82241106 | FUSE | 30351 | 20230309 | 2146 | 20230310 | 330 | 2029509 | 344 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 2064 | 37.3927 | -122.1479 | Yes | Clear;32-90F |  |  | 23-0042713 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823525 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1108 | 83481108 | TRANSFORMER | 315336631058 | 20230309 | 2159 | 20230310 | 1736 | 2029522 | 1177 | Transformer only | Vegetation | Tree - grew into line | 4 | 4708 | 37.342 | -122.1045 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0042846 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823612 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1111 | 83481111 | RECLOSER | LM40 | 20230309 | 2228 | 20230310 | 1735 | 2029594 | 1127 | Distribution Circuit | Vegetation | Tree - fell into line | 1164 | 165348 | 37.3454 | -122.0781 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042609 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1823422 | 0 | EPSS Ckt | N | 2023 | A & B
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | FUSE | 4767 | 20230310 | 27 | 20230310 | 1517 | 2029663 | 890 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4450 | 37.1492 | -122.0035 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0042668 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1823476 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | FUSE | 1127 | 20230310 | 119 | 20230310 | 800 | 2030355 | 401 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 13233 | 37.3579 | -122.1368 | No | Clear;32-90F |  |  | 23-0042795 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823587 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | SWITCH | 60120 | 20230310 | 208 | 20230310 | 232 | 2029924 | 24 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 718 | 14901 | 37.1302 | -121.9784 | No | Overcast-Rain;32-90 F |  |  | 23-0042691 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1823502 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | RECLOSER | 60118 | 20230310 | 427 | 20230310 | 434 | 2029947 | 7 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 937 | 6559 | 37.1247 | -121.9353 | No | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 23-0042734 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823547 | 0 | EPSS Ckt | N | 2023 | SGF
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 21101 | 20230310 | 548 | 20230311 | 1715 | 2030258 | 2127 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 31905 | 37.1336 | -121.9651 | No | Clear;32-90F | Conductor- Overhead | Broken | 23-0042890 | OH | Sus | 35431142 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1823644 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | FUSE | 123 | 20230310 | 700 | 20230310 | 1223 | 2030254 | 323 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 4522 | 37.3702 | -122.1464 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken | 23-0042828 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1823606 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | RECLOSER | 725939 | 20230310 | 734 | 20230310 | 1937 | 2030538 | 723 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 17352 | 37.3541 | -122.1596 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken | 23-0042926 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823661 | 0 | EPSS Ckt | N | 2023 | N/A
DE ANZA | DE ANZA | LOS GATOS-1101 | 82021101 | FUSE | 46285 | 20230310 | 817 | 20230310 | 1420 | 2030413 | 363 | Distribution Circuit | Animal | Bird found | 4 | 1453 | 37.2275 | -121.9726 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0043140 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823753 | 1 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1108 | 83481108 | FUSE | 5039 | 20230310 | 818 | 20230310 | 1046 | 2030598 | 148 | Distribution Circuit | Vegetation | Tree - branch fell on line | 61 | 9028 | 37.3472 | -122.098 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Contaminated | 23-0042883 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1823639 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | FUSE | 12853 | 20230310 | 841 | 20230310 | 1430 | 2030506 | 349 | Distribution Circuit | Vegetation | Tree - branch fell on line | 58 | 20242 | 37.2432 | -122.0136 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0043174 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823774 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 17431 | 20230310 | 907 | 20230310 | 1903 | 2030083 | 596 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 20264 | 37.1103 | -121.9511 | No | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042871 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823632 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | FUSE | 6873 | 20230310 | 1403 | 20230310 | 1719 | 2031119 | 196 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 4116 | 37.2632 | -122.0248 | No | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken | 23-0043190 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1823786 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | BRITTON-1111 | 83611111 | FUSE | 17073 | 20230310 | 1526 | 20230311 | 1250 | 2031143 | 1284 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 5136 | 37.3769 | -122.0144 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0043181 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823779 | 1 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1111 | 83481111 | TRANSFORMER | 315396031062 | 20230310 | 1538 | 20230310 | 1724 | 2031300 | 106 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 1166 | 37.3424 | -122.085 | No | Clear;32-90 F | Secondary | Broken | 23-0043183 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1823782 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | TRANSFORMER | 315596827334 | 20230310 | 1652 | 20230311 | 1122 | 2031355 | 1110 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 1110 | 37.241 | -122.0139 | No | Overcast-Drizzle;32-90 F | Transformer | Failed/Faulted | 23-0043217 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823810 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | TRANSFORMER | 315330031780 | 20230311 | 436 | 20230311 | 1158 | 2032266 | 442 | Transformer only | Vegetation | Tree - fell into line | 9 | 3978 | 37.3618 | -122.1073 | No | Clear;32-90 F | Service conductor | Broken | 23-0043414 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1823980 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1108 | 83481108 | RECLOSER | LM42 | 20230311 | 550 | 20230311 | 1842 | 2031869 | 772 | Distribution Circuit | Vegetation | Tree - fell into line | 989 | 255637 | 37.3509 | -122.0789 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0043334 | OH | Sus | 35431039 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1823918 | 0 | EPSS Ckt | N | 2023 | NONE
DE ANZA | DE ANZA | VASONA-1102 | 83771102 | JUMPER | FLYING BELLS 1 SPAN SOUTH OF CGC 315773127070 | 20230311 | 1242 | 20230311 | 1508 | 2032380 | 146 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 3796 | 37.2344 | -121.953 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0043449 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1824008 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | FUSE | 2643 | 20230311 | 1245 | 20230311 | 1508 | 2032404 | 143 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 4433 | 37.3726 | -122.1234 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Arcing | 23-0043475 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1824028 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WOLFE-1113 | 83671113 | TRANSFORMER | 315500930986 | 20230311 | 1350 | 20230311 | 1544 | 2032397 | 114 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 798 | 37.3407 | -122.0486 | No | Clear;32-90 F | Secondary | Broken | 23-0043456 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1824013 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | FUSE | 22527 | 20230311 | 1534 | 20230311 | 1951 | 2032486 | 257 | Distribution Circuit | Vegetation | Tree - grew into line | 32 | 8224 | 37.2436 | -122.0168 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0043497 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1824043 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | HICKS-1116 | 83431116 | FUSE | 2443 | 20230312 | 820 | 20230312 | 1043 | 2033106 | 143 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 1430 | 37.2276 | -121.9429 | No | Clear;32-90F |  |  | 23-0043663 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1824197 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1102 | 83771102 | TRANSFORMER | 315742627404 | 20230312 | 853 | 20230312 | 2157 | 2033127 | 784 | Transformer only | Vegetation | Tree - fell into line | 6 | 4704 | 37.2434 | -121.9638 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0043722 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824237 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1102 | 83771102 | FUSE | 1275 | 20230313 | 922 | 20230313 | 1016 | 2034196 | 54 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 54 | 37.2391 | -121.9734 | No | Clear;32-90F |  |  | 23-0044031 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824497 | 1 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | SWITCH | 257207 | 20230313 | 1217 | 20230316 | 1145 | 2034446 | 4288 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 129159 | 37.2482 | -122.0711 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0044130 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1824530 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1104 | 83371104 | FUSE | 2335 | 20230313 | 1532 | 20230316 | 2138 | 2034781 | 4686 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 121836 | 37.2458 | -121.9991 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0044314 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824600 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1109 | 82031109 | FUSE | 496789 | 20230314 | 153 | 20230315 | 354 | 2045064 | 1561 | Distribution Circuit | Vegetation | Tree - grew into line | 18 | 28098 | 37.3715 | -122.0737 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0046037 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1825954 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | TRANSFORMER | 315651124907 | 20230314 | 703 | 20230318 | 1338 | 2035226 | 6155 | Transformer only | Vegetation | Tree - fell into line | 1 | 6155 | 37.1745 | -121.9932 | Yes | Strong Winds-Overcast-Heavy Rain;32-90 F | Cutout- fuse holder | Broken | 23-0044652 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824810 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1101 | 82021101 | FUSE | 30937 | 20230314 | 755 | 20230317 | 1216 | 2047045 | 4581 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 18324 | 37.2108 | -121.954 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046608 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1826325 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | TRANSFORMER | 315695123965 | 20230314 | 802 | 20230314 | 1033 | 2035269 | 151 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 151 | 37.1486 | -121.9782 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0044700 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824846 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 32637 | 20230314 | 841 | 20230318 | 2009 | 2049767 | 6448 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 32240 | 37.1703 | -122.057 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 23-0047475 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1826842 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MENLO-1103 | 24131103 | FUSE | 731 | 20230314 | 952 | 20230316 | 1442 | 2035615 | 3170 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 9510 | 37.3692 | -122.1695 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0044735 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824873 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1101 | 83771101 | JUMPER | OPEN JUMPERS @ 14700 OAK RD | 20230314 | 1002 | 20230318 | 1314 | 2045175 | 5952 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 35712 | 37.2552 | -121.9574 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046059 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825978 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | OCB | 1110/2 | 20230314 | 1017 | 20230317 | 1711 | 2035814 | 4001 | Distribution Circuit | Equipment Failure/Involved | Overhead | 465 | 1015728 | 37.3358 | -122.043 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken | 23-0044674 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1824826 | 0 | EPSS Ckt | N | 2023 | A PHASE & TIME
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | JUMPER | 1 PHASE DWN AT CGC 315449725253 | 20230314 | 1017 | 20230316 | 1710 | 2044572 | 3293 | Distribution Circuit | Vegetation | Tree - fell into line | 183 | 504276 | 37.2101 | -122.0641 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken | 23-0045829 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825751 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | RECLOSER | 991992 | 20230314 | 1032 | 20230317 | 1825 | 2035946 | 4793 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 184066 | 37.1894 | -122.0309 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044703 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824848 | 0 | EPSS Ckt | N | 2023 | SGF TARGET
DE ANZA | DE ANZA | WOLFE-1113 | 83671113 | OCB | 1113/2 | 20230314 | 1035 | 20230314 | 1115 | 2035964 | 40 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7748 | 92268 | 37.3347 | -122.0207 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0044708 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824851 | 0 | Non-EPSS | N | 2023 | ABC & GRD
DE ANZA | DE ANZA | MOUNTAIN VIEW-1107 | 82031107 | FUSE | 16019 | 20230314 | 1038 | 20230315 | 1533 | 2044714 | 1735 | Distribution Circuit | Vegetation | Tree - branch fell on line | 51 | 88485 | 37.365 | -122.0864 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045870 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825793 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | FUSE | 29883 | 20230314 | 1038 | 20230315 | 2201 | 2036000 | 2123 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 192 | 407820 | 37.3159 | -122.0687 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0046721 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826384 | 1 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1101 | 82021101 | TRANSFORMER | T42005 | 20230314 | 1042 | 20230316 | 1946 | 2036017 | 3424 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 6848 | 37.2266 | -121.972 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0046141 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826035 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | HICKS-1114 | 83431114 | FUSE | 5301 | 20230314 | 1044 | 20230315 | 1441 | 2036034 | 1677 | Distribution Circuit | Vegetation | Tree - branch fell on line | 38 | 63726 | 37.2496 | -121.931 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0046438 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826220 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1108 | 83481108 | RECLOSER | LM42 | 20230314 | 1045 | 20230317 | 1710 | 2039064 | 4705 | Distribution Circuit | Vegetation | Tree - fell into line | 406 | 870040 | 37.3509 | -122.0789 | Yes | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045187 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1825232 | 0 | EPSS Ckt | N | 2023 | A & C
DE ANZA | DE ANZA | MOUNTAIN VIEW-1109 | 82031109 | FUSE | 4853 | 20230314 | 1046 | 20230315 | 518 | 2045072 | 1112 | Distribution Circuit | Vegetation | Tree - branch fell on line | 42 | 33949 | 37.3648 | -122.0779 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0046039 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825957 | 1 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1102 | 83771102 | FUSE | 621 | 20230314 | 1048 | 20230315 | 1924 | 2036119 | 1956 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 210 | 410760 | 37.2406 | -121.9645 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0046637 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826343 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1106 | 82241106 | RECLOSER | LL10 | 20230314 | 1049 | 20230316 | 1625 | 2040799 | 3216 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1357 | 4364112 | 37.3854 | -122.1285 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045989 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825915 | 0 | Non-EPSS | N | 2023 | UNKOWN
DE ANZA | DE ANZA | LOYOLA-1101 | 82161101 | FUSE | 1419 | 20230314 | 1049 | 20230317 | 1710 | 2048614 | 4701 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 47010 | 37.3863 | -122.1481 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045989 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | Yes | No | 1826598 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1113 | 83371113 | FUSE | 29827 | 20230314 | 1051 | 20230315 | 1823 | 2044890 | 1892 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 47300 | 37.2931 | -122.023 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045948 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1825873 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1102 | 82021102 | FUSE | 17063 | 20230314 | 1052 | 20230315 | 1326 | 2036157 | 1594 | Distribution Circuit | Vegetation | Tree - fell into line | 258 | 411252 | 37.2327 | -121.9746 | Yes | Overcast-Rain-Strong Winds;32-90 F | Secondary | Broken- wire on ground | 23-0046315 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826142 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1101 | 82021101 | FUSE | 46285 | 20230314 | 1055 | 20230316 | 1946 | 2036194 | 3411 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 13644 | 37.2275 | -121.9726 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0047245 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826705 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | RECLOSER | LB48 | 20230314 | 1056 | 20230318 | 2009 | 2036223 | 6313 | Distribution Circuit | Vegetation | Tree - branch fell on line | 119 | 597369 | 37.19 | -121.9942 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044742 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824877 | 0 | EPSS Ckt | N | 2023 | A/C/GRD
DE ANZA | DE ANZA | VASONA-1103 | 83771103 | FUSE | 4653 | 20230314 | 1056 | 20230316 | 1225 | 2036207 | 2969 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 35628 | 37.2613 | -121.9695 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0046997 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826551 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1111 | 83371111 | OCB | 1111/2 | 20230314 | 1057 | 20230316 | 358 | 2036243 | 2461 | Distribution Circuit | Vegetation | Tree - fell into line | 5851 | 4006459 | 37.281 | -122.0155 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Contaminated | 23-0044753 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824886 | 0 | Non-EPSS | N | 2023 | SET 'A' OC RLY
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | RECLOSER | LA64 | 20230314 | 1058 | 20230318 | 1844 | 2036268 | 6226 | Distribution Circuit | Vegetation | Tree - branch fell on line | 311 | 1515592 | 37.1372 | -121.9674 | Yes | Overcast-Rain-Strong Winds;32-90 F | Insulator | Broken | 23-0044748 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824882 | 0 | EPSS Ckt | N | 2023 | SGF TARGET
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | JUMPER | OPEN JUMPERS 4 P/W/O 31297 | 20230314 | 1058 | 20230317 | 202 | 2048439 | 3784 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 45468 | 37.1388 | -121.9772 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044748 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1826568 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 21101 | 20230314 | 1058 | 20230318 | 1444 | 2048745 | 5986 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 89790 | 37.1336 | -121.9651 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0047105 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826613 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 18607 | 20230314 | 1058 | 20230317 | 1828 | 2049133 | 4770 | Distribution Circuit | Vegetation | Tree - branch fell on line | 70 | 333900 | 37.1613 | -121.9722 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0047226 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1826690 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1108 | 83371108 | OCB | 1108/2 | 20230314 | 1102 | 20230316 | 252 | 2036377 | 2390 | Distribution Circuit | Vegetation | Tree - fell into line | 3477 | 8174319 | 37.281 | -122.0156 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0044763 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824893 | 0 | Non-EPSS | N | 2023 | N/A
DE ANZA | DE ANZA | SARATOGA-1108 | 83371108 | FUSE | 12745 | 20230314 | 1102 | 20230317 | 444 | 2047491 | 3942 | Distribution Circuit | Equipment Failure/Involved | Overhead | 62 | 244404 | 37.2783 | -122.0023 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046813 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | Yes | No | 1826444 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | HICKS-1115 | 83431115 | RECLOSER | 12494 | 20230314 | 1103 | 20230318 | 1300 | 2036347 | 5877 | Distribution Circuit | Vegetation | Tree - branch fell on line | 503 | 563461 | 37.2435 | -121.9378 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044757 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1824889 | 0 | EPSS Ckt | N | 2023 | B & C PHASE
DE ANZA | DE ANZA | HICKS-1115 | 83431115 | JUMPER | WIRE DOWN IRO 134 & 122 LU RAY DR | 20230314 | 1103 | 20230318 | 1300 | 2044998 | 5877 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 41139 | 37.2379 | -121.946 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046018 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825938 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | HICKS-1115 | 83431115 | TRANSFORMER | 315794927416 | 20230314 | 1103 | 20230317 | 1142 | 2045163 | 4359 | Transformer only | Equipment Failure/Involved | Overhead | 25 | 108975 | 37.244 | -121.9458 | Yes | Overcast-Rain-Strong Winds;32-90 F | Transformer (OH) | Failed/Faulted | 23-0044757 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825974 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1106 | 82031106 | FUSE | 341153 | 20230314 | 1103 | 20230315 | 401 | 2036311 | 1018 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 116 | 118088 | 37.3861 | -122.0856 | Yes | Overcast-Drizzle;32-90 F |  |  | 23-0046058 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825977 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1109 | 83481109 | OCB | 1109/2 | 20230314 | 1105 | 20230317 | 1850 | 2036498 | 4785 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3722 | 3431956 | 37.3358 | -122.043 | Yes | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044799 | OH | Sus | 35431719 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824922 | 0 | EPSS Ckt | N | 2023 | GRD TIME & PH TIME
DE ANZA | DE ANZA | STELLING-1109 | 83481109 | FUSE | 11445 | 20230314 | 1105 | 20230317 | 1724 | 2044064 | 4699 | Distribution Circuit | Vegetation | Tree - fell into line | 271 | 1222165 | 37.3129 | -122.0464 | Yes | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0044799 | OH | Sus | 35431719 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825659 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1109 | 83481109 | FUSE | 16049 | 20230314 | 1105 | 20230318 | 1755 | 2044669 | 6170 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 18510 | 37.3127 | -122.0636 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0044799 | OH | Sus | 35431719 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825777 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | FUSE | 4741 | 20230314 | 1106 | 20230317 | 1405 | 2042359 | 4499 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 175131 | 37.2308 | -122.0009 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045365 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1825353 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1104 | 83371104 | FUSE | 32933 | 20230314 | 1107 | 20230317 | 1722 | 2045371 | 4695 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 28170 | 37.2595 | -121.992 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 23-0044833 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826002 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1106 | 82241106 | FUSE | 32865 | 20230314 | 1109 | 20230317 | 1535 | 2036446 | 4586 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 129194 | 37.3999 | -122.1218 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0047148 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826635 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | TRANSFORMER | 315795822305 | 20230314 | 1112 | 20230318 | 1828 | 2049383 | 6196 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 12392 | 37.1031 | -121.9427 | Yes | Overcast-Rain-Strong Winds;32-90 F | Secondary | Broken- wire on ground | 23-0047316 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826776 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1112 | 83371112 | FUSE | 3769 | 20230314 | 1113 | 20230316 | 910 | 2036556 | 2757 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 204 | 562428 | 37.2864 | -121.998 | Yes | Overcast-Drizzle;32-90 F |  |  | 23-0046904 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826496 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA 1115 | 83371115 | FUSE | 583851 | 20230314 | 1115 | 20230318 | 1705 | 2036618 | 6110 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 289865 | 37.2905 | -122.0321 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045712 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825649 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1111 | 83481111 | RECLOSER | LM40 | 20230314 | 1115 | 20230316 | 41 | 2036755 | 2246 | Distribution Circuit | Vegetation | Tree - fell into line | 1081 | 2427926 | 37.3454 | -122.0781 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken | 23-0044798 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824921 | 0 | EPSS Ckt | N | 2023 | B/GRD
DE ANZA | DE ANZA | STELLING-1111 | 83481111 | FUSE | 18291 | 20230314 | 1115 | 20230317 | 1830 | 2047473 | 4755 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 294810 | 37.3441 | -122.0837 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044798 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826442 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1111 | 83481111 | JUMPER | OPEN JUMPERS IRO 1290 EVA | 20230314 | 1115 | 20230318 | 1405 | 2047498 | 5930 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 59300 | 37.3456 | -122.0846 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044798 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826445 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1111 | 83481111 | TRANSFORMER | 315396031062 | 20230314 | 1115 | 20230317 | 1303 | 2047513 | 4428 | Transformer only | Vegetation | Tree - branch fell on line | 11 | 48708 | 37.3424 | -122.085 | Yes | Strong Winds-Overcast-Drizzle;32-90 F | Transformer | Broken | 23-0044798 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826447 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WOLFE-1110 | 83671110 | TRANSFORMER | 315556730941 | 20230314 | 1117 | 20230316 | 2244 | 2036671 | 3567 | Transformer only | Unknown Cause | Patrol - found nothing | 7 | 24969 | 37.3399 | -122.0301 | Yes | Overcast-Strong Winds;32-90 F |  |  | 23-0047306 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1826767 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1104 | 83371104 | RECLOSER | 13314 | 20230314 | 1118 | 20230318 | 1545 | 2036896 | 6027 | Distribution Circuit | Vegetation | Tree - fell into line | 771 | 2707841 | 37.2626 | -121.9924 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044833 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824944 | 0 | EPSS Ckt | N | 2023 | SGF
DE ANZA | DE ANZA | SARATOGA-1104 | 83371104 | TRIP-SAVER | 8753 | 20230314 | 1118 | 20230318 | 1617 | 2045373 | 6059 | Distribution Circuit | Vegetation | Tree - fell into line | 126 | 763434 | 37.2578 | -121.9925 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken | 23-0044833 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826003 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1104 | 83371104 | FUSE | 11715 | 20230314 | 1118 | 20230318 | 1406 | 2045376 | 5928 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 58933 | 37.2572 | -122.0001 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 23-0044833 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1826004 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1104 | 83371104 | FUSE | 3571 | 20230314 | 1118 | 20230317 | 1701 | 2049326 | 4663 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 27978 | 37.2416 | -121.9919 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044833 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826728 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1104 | 83371104 | TRANSFORMER | 315652927703 | 20230314 | 1118 | 20230318 | 1230 | 2049328 | 5832 | Transformer only | Vegetation | Tree - branch fell on line | 9 | 52488 | 37.2512 | -121.9946 | Yes | Overcast-Rain-Strong Winds;32-90 F | Secondary | Broken- wire on ground | 23-0044833 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826730 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1104 | 83371104 | FUSE | 29703 | 20230314 | 1118 | 20230318 | 1154 | 2049341 | 5796 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 209858 | 37.2472 | -121.9967 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044833 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826734 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1104 | 83481104 | OCB | 1104/2 | 20230314 | 1119 | 20230316 | 1803 | 2036841 | 3284 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2189 | 5051479 | 37.3358 | -122.0431 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0044803 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1824923 | 0 | Non-EPSS | N | 2023 | PH TIME OC TARGET///
DE ANZA | DE ANZA | STELLING-1104 | 83481104 | JUMPER | OJ IFO 1140 HOLLYHEAD LN | 20230314 | 1119 | 20230318 | 1313 | 2049049 | 5874 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 511038 | 37.3045 | -122.0405 | Yes | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0047199 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826667 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | HICKS-1115 | 83431115 | FUSE | 11473 | 20230314 | 1122 | 20230317 | 1629 | 2036783 | 4627 | Distribution Circuit | Vegetation | Tree - branch fell on line | 270 | 856098 | 37.2434 | -121.9252 | Yes | Overcast-Rain-Strong Winds;32-90 F | Secondary | Broken | 23-0047102 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826611 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | OCB | 1107/2 | 20230314 | 1122 | 20230316 | 2338 | 2037012 | 3616 | Distribution Circuit | Vegetation | Tree - fell into line | 2187 | 4003017 | 37.2264 | -121.9771 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044820 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1824936 | 0 | EPSS Ckt | N | 2023 | A- B & TIME
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 89897 | 20230314 | 1122 | 20230318 | 1617 | 2049058 | 6055 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 78715 | 37.1623 | -121.9172 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0047203 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826669 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1108 | 83481108 | FUSE | 12547 | 20230314 | 1125 | 20230316 | 536 | 2036928 | 2531 | Distribution Circuit | Vegetation | Tree - branch fell on line | 385 | 974435 | 37.3514 | -122.0884 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0044905 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825002 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1108 | 83481108 | JUMPER | OJ @ BELVOIR & TERRACE | 20230314 | 1125 | 20230316 | 1934 | 2047644 | 3369 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 235830 | 37.3503 | -122.088 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Together | 23-0044905 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826467 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 21117 | 20230314 | 1127 | 20230317 | 1445 | 2049375 | 4518 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 189756 | 37.1083 | -121.8333 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0047307 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826768 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1113 | 83371113 | FUSE | 18953 | 20230314 | 1134 | 20230316 | 2000 | 2046480 | 3386 | Distribution Circuit | Vegetation | Tree - fell into line | 132 | 446952 | 37.2941 | -122.0175 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046450 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826227 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | EL PATIO-1116 | 82921116 | OCB | 1116/2 | 20230314 | 1135 | 20230314 | 2119 | 2037410 | 584 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2811 | 1641624 | 37.2917 | -121.9356 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken | 23-0045897 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825820 | 0 | Non-EPSS | N | 2023 | A & B PHASE OC
DE ANZA | DE ANZA | MOUNTAIN VIEW-1105 | 82031105 | TRANSFORMER | 315386032862 | 20230314 | 1135 | 20230318 | 1155 | 2037218 | 5780 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 34680 | 37.3916 | -122.0892 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Transformer (OH) | Failed/Faulted | 23-0046053 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825971 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1112 | 83371112 | TRANSFORMER | 315638228969 | 20230314 | 1135 | 20230318 | 1324 | 2037219 | 5869 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 64680 | 37.2859 | -122.0002 | Yes | Overcast-Drizzle;32-90 F | Secondary | Broken- wire on ground | 23-0046922 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826503 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1101 | 82021101 | RECLOSER | 60052 | 20230314 | 1138 | 20230317 | 1258 | 2037499 | 4400 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 109926 | 37.2185 | -121.9524 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 23-0044903 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1825000 | 0 | EPSS Ckt | N | 2023 | A-B PH & 51(INST)
DE ANZA | DE ANZA | WOLFE-1113 | 83671113 | SWITCH | UV42 | 20230314 | 1138 | 20230315 | 1155 | 2037364 | 1457 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3199 | 456673 | 37.3523 | -122.0421 | Yes | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044848 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1824957 | 1 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1113 | 83671113 | FUSE | 157 | 20230314 | 1139 | 20230318 | 1750 | 2045135 | 6131 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 67441 | 37.3467 | -122.0459 | Yes | Overcast;32-90 F | Pole-Wood | Broken | 23-0046051 | OH | Sus | 35431719 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1825970 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1105 | 83771105 | OCB | 1105/2/NORM | 20230314 | 1142 | 20230314 | 1204 | 2038111 | 22 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 2677 | 58894 | 37.2537 | -121.9662 | Yes | Clear;32-90 F |  |  | 23-0044942 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825031 | 0 | Non-EPSS | N | 2023 | A-B PH 50 (INST)
DE ANZA | DE ANZA | LOS GATOS-1102 | 82021102 | FUSE | 32189 | 20230314 | 1145 | 20230316 | 1832 | 2038139 | 3287 | Distribution Circuit | Vegetation | Tree - grew into line | 382 | 490022 | 37.231 | -121.9767 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046015 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825935 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA SUB | 8216 | OCB | 401/2 | 20230314 | 1145 | 20230317 | 19 | 2037637 | 3634 | Distribution Circuit | Equipment Failure/Involved | Overhead | 847 | 1630366 | 37.361 | -122.0993 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Deteriorated | 23-0044879 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824985 | 0 | Non-EPSS | N | 2023 | GRD TARGET
DE ANZA | DE ANZA | LOYOLA-0401 | 82160401 | JUMPER | OPEN JUMPERS 1 S/W/O CGC 315354032363 | 20230314 | 1145 | 20230317 | 1014 | 2049381 | 4229 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 50748 | 37.3781 | -122.1005 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0047311 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1826772 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOYOLA-0401 | 82160401 | TRANSFORMER | 315359732550 | 20230314 | 1145 | 20230319 | 213 | 2049391 | 6628 | Transformer only | Environmental/External | Water | 5 | 33140 | 37.3837 | -122.0981 | Yes | Strong Winds-Overcast-Drizzle;32-90 F | Secondary | Normal | 23-0047318 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826777 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1110 | 82031110 | OTHER | BURNT CABLE BET 6629 & C1295 | 20230314 | 1145 | 20230318 | 302 | 2047042 | 5237 | Distribution Circuit | Equipment Failure/Involved | Underground | 491 | 1355922 | 37.3734 | -122.0641 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Underground | Burned/flashed | 23-0046606 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1826323 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1114 | 83371114 | FUSE | 8319 | 20230314 | 1146 | 20230316 | 1841 | 2044688 | 3295 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 128505 | 37.2897 | -122.0165 | Yes | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045860 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825783 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1114 | 83371114 | FUSE | 12709 | 20230314 | 1146 | 20230315 | 2325 | 2046067 | 2139 | Distribution Circuit | Equipment Failure/Involved | Overhead | 186 | 397854 | 37.2936 | -122.0112 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046289 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826129 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | HICKS-2103 | 83432103 | OCB | 2103/2 | 20230314 | 1147 | 20230314 | 2022 | 2037695 | 515 | Distribution Circuit | Vegetation | Tree - fell into line | 1780 | 909274 | 37.2332 | -121.9013 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044912 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825009 | 0 | EPSS Ckt | N | 2023 | GRD TIME TARGET
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | FUSE | 15763 | 20230314 | 1148 | 20230316 | 1936 | 2037725 | 3348 | Distribution Circuit | Equipment Failure/Involved | Overhead | 99 | 137903 | 37.2535 | -122.0367 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046120 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1826020 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | RECLOSER | 60116 | 20230314 | 1150 | 20230317 | 1740 | 2036460 | 4670 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1327 | 1112229 | 37.1735 | -121.9928 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0044963 | OH | Sus | 35431722 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1825047 | 0 | EPSS Ckt | N | 2023 | A-B PH TRGTS
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | JUMPER | OPEN JUMPERS NORTH OF CGC#315627622867 | 20230314 | 1150 | 20230316 | 1748 | 2042962 | 3238 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 58284 | 37.1191 | -122.0008 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0044963 | OH | Sus | 35431722 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825455 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1101 | 82021101 | OTHER | 1 WIRE DOWN | 20230314 | 1151 | 20230316 | 2353 | 2048227 | 3602 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 108060 | 37.2286 | -121.9578 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046963 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | Yes | 1826530 | 1 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | OTHER | WIRE DOWN @ 23803 PUTTER WY | 20230314 | 1151 | 20230318 | 1709 | 2046953 | 6078 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 152138 | 37.3491 | -122.106 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046595 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | Yes | 1826315 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1101 | 82021101 | FUSE | 18697 | 20230314 | 1152 | 20230316 | 1255 | 2048305 | 2943 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 61803 | 37.2311 | -121.9513 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0047024 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826570 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1105 | 83371105 | OTHER | WIRE DOWN IRO 20398 BLAUER DR | 20230314 | 1152 | 20230315 | 1658 | 2040509 | 1746 | Distribution Circuit | Equipment Failure/Involved | Overhead | 210 | 362808 | 37.279 | -122.0309 | Yes | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045158 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | Yes | 1825207 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1104 | 83371104 | OCB | 1104/2 | 20230314 | 1155 | 20230318 | 1506 | 2037954 | 5951 | Distribution Circuit | Vegetation | Tree - fell into line | 516 | 1566332 | 37.281 | -122.0157 | Yes | Overcast-Drizzle;32-90 F | Service conductor | Broken- wire on ground | 23-0044979 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825061 | 0 | EPSS Ckt | N | 2023 | TRIP
DE ANZA | DE ANZA | SARATOGA-1104 | 83371104 | JUMPER | OJ 1 POLE W/OF K033L | 20230314 | 1155 | 20230318 | 1645 | 2047063 | 3162 | Distribution Circuit | Vegetation | Tree - fell into line | 196 | 620314 | 37.267 | -121.9964 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046613 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826329 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1104 | 83371104 | FUSE | 789 | 20230314 | 1155 | 20230316 | 2305 | 2048586 | 3550 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 60115 | 37.2726 | -122.0084 | Yes | Overcast-Drizzle;32-90 F | Secondary | Broken- wire on ground | 23-0044979 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826592 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1105 | 83371105 | OCB | 1105/2 | 20230314 | 1156 | 20230315 | 1624 | 2037966 | 1708 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1217 | 2078636 | 37.281 | -122.0156 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Together | 23-0045223 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825254 | 0 | EPSS Ckt | N | 2023 | OC Time
DE ANZA | DE ANZA | SARATOGA-1105 | 83371105 | FUSE | 33099 | 20230314 | 1158 | 20230315 | 1816 | 2046262 | 1818 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 7272 | 37.2788 | -122.0382 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0045223 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826179 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | HICKS-1109 | 83431109 | INTERRUPTER | 54734 | 20230314 | 1200 | 20230317 | 1505 | 2048244 | 4505 | Distribution Circuit | Vegetation | Tree - branch fell on line | 77 | 231805 | 37.2659 | -121.94 | Yes | Strong Winds-Overcast-Heavy Rain;32-90 F | Transformer (OH) | Broken | 23-0046967 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826533 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA SUB | 8337 | OCB | 1200/2 | 20230314 | 1201 | 20230318 | 1031 | 2039074 | 5670 | Distribution Circuit | Vegetation | Tree - fell into line | 3739 | 10938342 | 37.281 | -122.0156 | Yes | Overcast-Drizzle;32-90 F | Service conductor | Broken- wire on ground | 23-0046022 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825941 | 0 | Non-EPSS | N | 2023 | b and C
DE ANZA | DE ANZA | SARATOGA-1109 | 83371109 | FUSE | 82517 | 20230314 | 1201 | 20230318 | 1457 | 2048515 | 5936 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 53424 | 37.2707 | -121.9971 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken | 23-0047035 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826576 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1109 | 82031109 | FUSE | 89843 | 20230314 | 1202 | 20230315 | 1053 | 2037980 | 1371 | Distribution Circuit | Vegetation | Tree - branch fell on line | 492 | 663948 | 37.366 | -122.0776 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045202 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1825241 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1109 | 83671109 | OCB | 1109/2 | 20230314 | 1205 | 20230315 | 2013 | 2038145 | 1928 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2308 | 4365616 | 37.3347 | -122.0208 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0044958 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825043 | 0 | Non-EPSS | N | 2023 | N/A
DE ANZA | DE ANZA | WHISMAN-1108 | 83631108 | RECLOSER | LM34 | 20230314 | 1206 | 20230316 | 417 | 2038158 | 2411 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1057 | 2348723 | 37.4016 | -122.0797 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045003 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825081 | 0 | Non-EPSS | N | 2023 | A & G
DE ANZA | DE ANZA | VASONA-1101 | 83771101 | FUSE | 8627 | 20230314 | 1207 | 20230315 | 1604 | 2044955 | 1677 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 45279 | 37.25 | -121.9617 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045994 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825918 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | JUMPER | WIRE DOWN N/W OF ALTA TIERRA RD | 20230314 | 1208 | 20230316 | 245 | 2044377 | 2317 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 4634 | 37.3717 | -122.1354 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045776 | OH | Sus | 35431719 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825703 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1101 | 82021101 | RECLOSER | LB40 | 20230314 | 1211 | 20230315 | 2026 | 2036166 | 1935 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 597 | 1155195 | 37.2272 | -121.9666 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0045007 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825084 | 0 | EPSS Ckt | N | 2023 | SGF
DE ANZA | DE ANZA | HICKS-1116 | 83431116 | FUSE | 19957 | 20230314 | 1212 | 20230317 | 1046 | 2044964 | 4234 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 262508 | 37.2351 | -121.9149 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Contaminated | 23-0046000 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825924 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1114 | 83371114 | FUSE | 8327 | 20230314 | 1212 | 20230315 | 1900 | 2045837 | 1848 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 49896 | 37.2956 | -122.0073 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046205 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826084 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOYOLA-0403 | 82160403 | FUSE | 32825 | 20230314 | 1213 | 20230315 | 1956 | 2046954 | 1903 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 36157 | 37.3787 | -122.0961 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken | 23-0046596 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826316 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | FUSE | 12853 | 20230314 | 1213 | 20230315 | 1800 | 2038317 | 1787 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 103646 | 37.2432 | -122.0136 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045312 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825317 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1109 | 83371109 | FUSE | 17925 | 20230314 | 1213 | 20230318 | 1223 | 2044571 | 5770 | Distribution Circuit | Vegetation | Tree - fell into line | 236 | 463225 | 37.2742 | -121.9875 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 23-0045828 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1825750 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | FUSE | 167 | 20230314 | 1214 | 20230317 | 1842 | 2044855 | 4708 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 301312 | 37.2739 | -122.0229 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045908 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825833 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | HICKS-1116 | 83431116 | RECLOSER | 647210 | 20230314 | 1218 | 20230316 | 2037 | 2038492 | 3379 | Distribution Circuit | Vegetation | Tree - fell into line | 491 | 1531314 | 37.2383 | -121.9431 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045032 | OH | Sus | 35431719 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1825104 | 0 | EPSS Ckt | N | 2023 | ABC
DE ANZA | DE ANZA | WHISMAN-1106 | 83631106 | RECLOSER | 60000 | 20230314 | 1219 | 20230315 | 2139 | 2038917 | 2000 | Distribution Circuit | Equipment Failure/Involved | Overhead | 842 | 1684000 | 37.4145 | -122.0946 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Arcing | 23-0045083 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825145 | 0 | Non-EPSS | N | 2023 | phase to phase
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | RECLOSER | 429970 | 20230314 | 1220 | 20230316 | 2040 | 2038629 | 3380 | Distribution Circuit | Vegetation | Tree - fell into line | 402 | 1165424 | 37.3484 | -122.114 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045049 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1825119 | 0 | EPSS Ckt | N | 2023 | A-B & 51 (TIMED) TRGTS
DE ANZA | DE ANZA | SARATOGA-1109 | 83371109 | RECLOSER | LC42 | 20230314 | 1220 | 20230316 | 1758 | 2038575 | 3218 | Distribution Circuit | Equipment Failure/Involved | Overhead | 816 | 2625888 | 37.2777 | -121.9762 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045013 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825089 | 0 | Non-EPSS | N | 2023 | B & GRD
DE ANZA | DE ANZA | SARATOGA-1109 | 83371109 | FUSE | 31249 | 20230314 | 1220 | 20230316 | 1708 | 2047653 | 3168 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 41184 | 37.2791 | -121.9629 | Yes | Overcast-Drizzle;32-90 F |  |  | 23-0046847 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826470 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1112 | 83371112 | TRANSFORMER | 315628428855 | 20230314 | 1220 | 20230318 | 1605 | 2036444 | 5985 | Transformer only | Vegetation | Tree - branch fell on line | 11 | 65835 | 37.2827 | -122.0035 | Yes | Overcast-Drizzle;32-90 F | Transformer | Broken- wire on ground | 23-0046933 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826510 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOYOLA SUB | 8216 | OCB | 403/2 | 20230314 | 1223 | 20230315 | 1956 | 2036807 | 1893 | Distribution Circuit | Vegetation | Tree - fell into line | 900 | 1703700 | 37.361 | -122.0994 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken | 23-0044993 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825073 | 0 | Non-EPSS | N | 2023 | PH & TIM OC
DE ANZA | DE ANZA | MOUNTAIN VIEW-1111 | 82031111 | OCB | 1111/2 | 20230314 | 1223 | 20230315 | 1847 | 2038896 | 1824 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1598 | 2873722 | 37.3826 | -122.0696 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken | 23-0045050 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825120 | 0 | Non-EPSS | N | 2023 | B & C
DE ANZA | DE ANZA | STELLING-1108 | 83481108 | OTHER | WIRE DOWN 1 P/S OF 1371 DON KIRK ST | 20230314 | 1223 | 20230317 | 1539 | 2038599 | 4516 | Distribution Circuit | Vegetation | Tree - fell into line | 446 | 379432 | 37.3492 | -122.0754 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045744 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | Yes | 1825678 | 1 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WOLFE-1105 | 83671105 | FUSE | 12631 | 20230314 | 1223 | 20230317 | 1155 | 2039019 | 4292 | Distribution Circuit | Equipment Failure/Involved | Overhead | 97 | 316022 | 37.3133 | -122.0134 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Crossarm- Wood | Broken | 23-0047019 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826566 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1114 | 83371114 | FUSE | 4203 | 20230314 | 1224 | 20230315 | 1325 | 2044860 | 1501 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 157 | 235657 | 37.2995 | -122.0066 | Yes | Overcast-Drizzle;32-90 F |  |  | 23-0045913 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1825837 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | HICKS-1116 | 83431116 | FUSE | 33013 | 20230314 | 1226 | 20230318 | 42 | 2048459 | 5056 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 40448 | 37.2363 | -121.9268 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0047029 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826573 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1113 | 83371113 | OCB | 1113/2 | 20230314 | 1226 | 20230315 | 1612 | 2046506 | 1607 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4374 | 6991262 | 37.281 | -122.0155 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Burned/flashed | 23-0045142 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826242 | 0 | Non-EPSS | N | 2023 | A-B-C PHASE INST
DE ANZA | DE ANZA | SARATOGA-1114 | 83371114 | OCB | 1114/2 | 20230314 | 1226 | 20230315 | 1325 | 2038802 | 1499 | Distribution Circuit | Vegetation | Tree - fell into line | 5480 | 7982464 | 37.281 | -122.0155 | Yes | Overcast-Drizzle;32-90 F | Switch (OH) | Burned/flashed | 23-0045142 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825193 | 0 | Non-EPSS | N | 2023 | A-B-C PHASE INST- LOCKED OUT 6
DE ANZA | DE ANZA | VASONA-1101 | 83771101 | OCB | 1101/2 | 20230314 | 1226 | 20230315 | 430 | 2038980 | 964 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3019 | 2570366 | 37.2537 | -121.9661 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045810 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1825732 | 0 | Non-EPSS | N | 2023 | A-B-C- INST- NEUTRAL
DE ANZA | DE ANZA | LOYOLA-0403 | 82160403 | OTHER | WIRE DOWN @ C/O PARMA & ROSALITA | 20230314 | 1228 | 20230316 | 1616 | 2047023 | 3108 | Distribution Circuit | Equipment Failure/Involved | Overhead | 178 | 488928 | 37.3707 | -122.0989 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046602 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826320 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1105 | 83771105 | TRANSFORMER | 315801728238 | 20230314 | 1228 | 20230317 | 1412 | 2038797 | 4424 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 70784 | 37.2667 | -121.9439 | Yes | Strong Winds-Overcast-Heavy Rain;32-90 F | Secondary | Broken- wire on ground | 23-0046939 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1826512 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1101 | 82021101 | FUSE | 11565 | 20230314 | 1232 | 20230316 | 1137 | 2048176 | 2825 | Distribution Circuit | Vegetation | Tree - branch fell on line | 147 | 415275 | 37.2286 | -121.9663 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0046949 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | No | No | 1826521 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1105 | 82031105 | FUSE | 4701 | 20230314 | 1233 | 20230315 | 1625 | 2038965 | 1672 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 137104 | 37.3916 | -122.0886 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046050 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1825968 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1109 | 83371109 | TRANSFORMER | 315714128409 | 20230314 | 1233 | 20230318 | 1624 | 2047656 | 5991 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 107838 | 37.2709 | -121.974 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Secondary | Broken- wire on ground | 23-0046849 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826472 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MENLO-1103 | 24131103 | FUSE | 529 | 20230314 | 1234 | 20230316 | 1831 | 2047624 | 3237 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 42081 | 37.3803 | -122.1635 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046836 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826463 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | HICKS-1109 | 83431109 | FUSE | 26117 | 20230314 | 1236 | 20230315 | 1429 | 2039023 | 1553 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 24848 | 37.2533 | -121.93 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken | 23-0046406 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826201 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1108 | 83481108 | OTHER | WIRE DOWN @ 1586 COUNTRY CLUB DR | 20230314 | 1237 | 20230317 | 1347 | 2047121 | 2557 | Distribution Circuit | Vegetation | Tree - fell into line | 614 | 300534 | 37.352 | -122.089 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046636 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | Yes | Yes | 1826342 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1106 | 82241106 | FUSE | 30485 | 20230314 | 1250 | 20230316 | 1650 | 2044007 | 3120 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 18720 | 37.3786 | -122.1267 | Yes | Overcast;32-90 F |  |  | 23-0045711 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825648 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MENLO-1103 | 24131103 | RECLOSER | 866118 | 20230314 | 1250 | 20230316 | 1442 | 2039637 | 2992 | Distribution Circuit | Vegetation | Tree - branch fell on line | 154 | 460768 | 37.3756 | -122.1668 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0045105 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825162 | 0 | EPSS Ckt | N | 2023 | 50 (INST)
DE ANZA | DE ANZA | BRITTON-1110 | 83611110 | FUSE | 11569 | 20230314 | 1251 | 20230315 | 2341 | 2047439 | 2090 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 163 | 340670 | 37.3594 | -122.0051 | Yes | Overcast;32-90 F |  |  | 23-0046793 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826436 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1112 | 83481112 | OCB | 1112/2 | 20230314 | 1251 | 20230316 | 1909 | 2036651 | 3258 | Distribution Circuit | Vegetation | Tree - branch fell on line | 283 | 922014 | 37.3358 | -122.0429 | Yes | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0045071 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825136 | 0 | Non-EPSS | N | 2023 | PHASE INST TGT
DE ANZA | DE ANZA | LOYOLA-1101 | 82161101 | INTERRUPTER | 612998 | 20230314 | 1253 | 20230317 | 1832 | 2047466 | 4659 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 419310 | 37.377 | -122.1184 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0046801 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826439 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | EL PATIO-1117 | 82921117 | FUSE | 46729 | 20230314 | 1256 | 20230314 | 2225 | 2039666 | 569 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 552 | 314088 | 37.2829 | -121.9489 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 23-0045925 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825850 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | OCB | 1102/2 | 20230314 | 1257 | 20230316 | 109 | 2037140 | 2172 | Distribution Circuit | Vegetation | Tree - fell into line | 3041 | 6538553 | 37.361 | -122.0992 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Service conductor | Broken- wire on ground | 23-0045102 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825160 | 0 | EPSS Ckt | N | 2023 | PRIMARY GRD TIME
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | RECLOSER | 234053 | 20230314 | 1257 | 20230317 | 1226 | 2046839 | 4289 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 55757 | 37.3403 | -122.1088 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0046557 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826289 | 0 | EPSS Ckt | N | 2023 | UNKNOWN
DE ANZA | DE ANZA | VASONA-1108 | 83771108 | OCB | 1108/2/NORM | 20230314 | 1258 | 20230314 | 2056 | 2039804 | 478 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1958 | 924697 | 37.2537 | -121.9663 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045126 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | Yes | No | 1825180 | 0 | Non-EPSS | N | 2023 | AC & GRD TARGTEST
DE ANZA | DE ANZA | VASONA-1108 | 83771108 | FUSE | 18331 | 20230314 | 1258 | 20230317 | 2028 | 2043530 | 4770 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 113076 | 37.2427 | -121.9509 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045605 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825556 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | JUMPER | OJ 4 POLES E/OF 9219 | 20230314 | 1302 | 20230315 | 639 | 2043745 | 1057 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 16912 | 37.3679 | -122.1322 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0045655 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825597 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1102 | 83771102 | FUSE | 8979 | 20230314 | 1304 | 20230315 | 1858 | 2044190 | 1794 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 91 | 162737 | 37.2435 | -121.9761 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 23-0046609 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826326 | 1 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1102 | 83771102 | FUSE | 12183 | 20230314 | 1304 | 20230315 | 1858 | 2047049 | 1794 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 74 | 132756 | 37.244 | -121.9794 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 23-0046610 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826327 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | HICKS-1116 | 83431116 | TRANSFORMER | 315798927266 | 20230314 | 1308 | 20230316 | 1953 | 2044930 | 3285 | Transformer only | Vegetation | Tree - branch fell on line | 7 | 22995 | 37.24 | -121.9443 | Yes | Overcast-Rain-Strong Winds;32-90 F | Transformer | Broken- wire on ground | 23-0045983 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825909 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | HICKS-1116 | 83431116 | TRANSFORMER | 315839827236 | 20230314 | 1308 | 20230317 | 1310 | 2044980 | 4322 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 47542 | 37.2394 | -121.9303 | Yes | Overcast-Rain-Strong Winds;32-90 F | Secondary | Broken- wire on ground | 23-0046004 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1825928 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | HICKS-1116 | 83431116 | JUMPER | BROKEN WIRE @ CGC 315898726949 | 20230314 | 1308 | 20230315 | 1835 | 2045001 | 1767 | Distribution Circuit | Vegetation | Tree - branch fell on line | 383 | 506593 | 37.2317 | -121.9092 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken | 23-0046019 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1825939 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1103 | 83771103 | FUSE | 17963 | 20230314 | 1317 | 20230316 | 1545 | 2039288 | 3028 | Distribution Circuit | Equipment Failure/Involved | Overhead | 201 | 608628 | 37.2637 | -121.9724 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0047104 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1826612 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1105 | 83771105 | FUSE | 19689 | 20230314 | 1317 | 20230315 | 513 | 2040319 | 956 | Distribution Circuit | 3rd Party | Other | 245 | 234220 | 37.2722 | -121.9614 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0046066 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825987 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1101 | 83771101 | FUSE | 32999 | 20230314 | 1318 | 20230318 | 1141 | 2044853 | 5663 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 50967 | 37.2583 | -121.9532 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045905 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | Yes | No | 1825830 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1113 | 83671113 | OCB | 1113/2 | 20230314 | 1322 | 20230316 | 1405 | 2039155 | 2923 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5575 | 7058669 | 37.3347 | -122.0207 | Yes | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045173 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825220 | 0 | Non-EPSS | N | 2023 | UKNOWN
DE ANZA | DE ANZA | WOLFE-1113 | 83671113 | SWITCH | 937 | 20230314 | 1322 | 20230315 | 1701 | 2045126 | 1659 | Distribution Circuit | Vegetation | Tree - fell into line | 163 | 270417 | 37.3516 | -122.026 | Yes | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0046048 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1825966 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1113 | 83671113 | SWITCH | 31317 | 20230314 | 1322 | 20230318 | 1845 | 2045127 | 6083 | Distribution Circuit | Equipment Failure/Involved | Overhead | 464 | 1107971 | 37.3449 | -122.0243 | Yes | Overcast;32-90 F | Crossarm- Wood | Broken | 23-0046049 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1825967 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1113 | 83671113 | RECLOSER | 338984 | 20230314 | 1322 | 20230317 | 235 | 2045218 | 3673 | Distribution Circuit | Equipment Failure/Involved | Overhead | 580 | 1263191 | 37.3595 | -122.0497 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0046062 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1825983 | 0 | Non-EPSS | N | 2023 | NOT CAPTURED
DE ANZA | DE ANZA | WOLFE-1113 | 83671113 | FUSE | 22945 | 20230314 | 1322 | 20230315 | 1341 | 2045269 | 1459 | Distribution Circuit | Vegetation | Tree - fell into line | 275 | 387455 | 37.3591 | -122.0413 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0046072 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1825994 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1113 | 83671113 | FUSE | 2383 | 20230314 | 1322 | 20230317 | 1434 | 2045296 | 4392 | Distribution Circuit | Vegetation | Tree - fell into line | 119 | 414393 | 37.3485 | -122.0506 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Secondary | Broken- wire on ground | 23-0046080 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1825998 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | HICKS-1114 | 83431114 | FUSE | 32317 | 20230314 | 1325 | 20230315 | 1227 | 2039500 | 1382 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 19921 | 37.2483 | -121.9368 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045436 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825413 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | FUSE | 9321 | 20230314 | 1326 | 20230316 | 1409 | 2040764 | 2923 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 49691 | 37.2481 | -122.0243 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0046356 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826170 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | SWITCH | 1871 | 20230314 | 1328 | 20230316 | 1859 | 2043474 | 3211 | Distribution Circuit | Vegetation | Tree - fell into line | 2076 | 6666036 | 37.2776 | -122.0146 | Yes | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045599 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825550 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | TRANSFORMER | 315566528621 | 20230314 | 1328 | 20230317 | 1739 | 2044982 | 4089 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 35616 | 37.276 | -122.0247 | Yes | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken | 23-0046005 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825929 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1104 | 82241104 | OCB | 1104/2/NORM | 20230314 | 1332 | 20230318 | 1544 | 2039585 | 5791 | Distribution Circuit | Vegetation | Tree - fell into line | 921 | 2859467 | 37.3936 | -122.1151 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045197 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1825239 | 0 | Non-EPSS | N | 2023 | A & C
DE ANZA | DE ANZA | LOS ALTOS-1104 | 82241104 | FUSE | 42689 | 20230314 | 1332 | 20230315 | 1939 | 2046308 | 1807 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 12649 | 37.3883 | -122.1142 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 23-0045197 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1826190 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1104 | 82241104 | FUSE | 913 | 20230314 | 1332 | 20230316 | 2047 | 2049252 | 3315 | Distribution Circuit | Vegetation | Tree - branch fell on line | 200 | 575221 | 37.3754 | -122.1132 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0045197 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826710 | 1 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1107 | 82031107 | OCB | 1107/2 | 20230314 | 1333 | 20230316 | 1424 | 2040740 | 2931 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2639 | 2617809 | 37.3826 | -122.0697 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken | 23-0045247 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825272 | 0 | Non-EPSS | N | 2023 | A & B PHASE
DE ANZA | DE ANZA | MOUNTAIN VIEW-1107 | 82031107 | JUMPER | OPEN JUMPERS E/OF 1207 | 20230314 | 1333 | 20230318 | 1220 | 2043353 | 5687 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 5687 | 37.3685 | -122.0869 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken | 23-0045577 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825529 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1107 | 82031107 | JUMPER | OJ @ LEOELLO AVE & COVINGTON RD | 20230314 | 1333 | 20230318 | 1726 | 2044862 | 5982 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 154284 | 37.3652 | -122.0933 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on object | 23-0045916 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1825839 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1103 | 82241103 | FUSE | 4791 | 20230314 | 1338 | 20230315 | 1538 | 2046556 | 1560 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 49920 | 37.3839 | -122.1029 | Yes | Overcast;32-90 F |  |  | 23-0046480 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826241 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1111 | 83421111 | TRANSFORMER | 315623532958 | 20230314 | 1341 | 20230318 | 1609 | 2040886 | 5908 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 76804 | 37.3956 | -122.0074 | Yes | Overcast;32-90 F | Secondary | Broken- wire on ground | 23-0047178 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826655 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1114 | 82031114 | OCB | 1114/2 | 20230314 | 1341 | 20230317 | 1606 | 2039617 | 4465 | Distribution Circuit | Vegetation | Tree - fell into line | 425 | 275806 | 37.3827 | -122.0695 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045843 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1825765 | 0 | Non-EPSS | N | 2023 | UNKNOWN
DE ANZA | DE ANZA | VASONA-1105 | 83771105 | FUSE | 8085 | 20230314 | 1342 | 20230316 | 1653 | 2040877 | 3071 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 331668 | 37.2693 | -121.9377 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0046035 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | Yes | No | 1825951 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1110 | 83371110 | OCB | 1110/2 | 20230314 | 1343 | 20230315 | 2315 | 2041096 | 2012 | Distribution Circuit | Vegetation | Tree - fell into line | 4838 | 9734056 | 37.281 | -122.0156 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Contaminated | 23-0045242 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825269 | 0 | Non-EPSS | N | 2023 | A OC INST C OC INST
DE ANZA | DE ANZA | SARATOGA-1103 | 83371103 | FUSE | 25999 | 20230314 | 1350 | 20230318 | 1338 | 2041109 | 5748 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 97716 | 37.2742 | -122.0325 | Yes | Overcast-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 23-0048290 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1827512 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1102 | 82031102 | FUSE | 30199 | 20230314 | 1405 | 20230319 | 1415 | 2041708 | 7210 | Distribution Circuit | Equipment Failure/Involved | Overhead | 49 | 353290 | 37.4116 | -122.0991 | Yes | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0048491 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1827700 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1104 | 83671104 | OCB | 1104/2 | 20230314 | 1433 | 20230314 | 1547 | 2042319 | 74 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2121 | 142782 | 37.3347 | -122.021 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0045366 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825354 | 0 | Non-EPSS | N | 2023 | WOLFE SUB BUS SECT D TARGETS
DE ANZA | DE ANZA | MOUNTAIN VIEW-1110 | 82031110 | OCB | 1110/2 | 20230314 | 1434 | 20230315 | 1959 | 2037575 | 1765 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2883 | 5088495 | 37.3826 | -122.0696 | Yes | Overcast-Drizzle;32-90 F | Jumper | Burned/flashed | 23-0045343 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825334 | 0 | Non-EPSS | N | 2023 | A PHASE- GRD TIME OC
DE ANZA | DE ANZA | WHISMAN-1110 | 83631110 | TRANSFORMER | 315402133617 | 20230314 | 1434 | 20230318 | 1835 | 2039029 | 6001 | Transformer only | Environmental/External | Water | 11 | 66011 | 37.4126 | -122.0842 | Yes | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0047283 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826744 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1109 | 82031109 | OCB | 1109/2 | 20230314 | 1438 | 20230315 | 354 | 2042051 | 796 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1080 | 767880 | 37.3826 | -122.0696 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Together | 23-0045359 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825348 | 0 | Non-EPSS | N | 2023 | A & C PHASE TIME OC & SET A RL
DE ANZA | DE ANZA | MOUNTAIN VIEW-1109 | 82031109 | TRANSFORMER | 315450931672 | 20230314 | 1438 | 20230318 | 1419 | 2045068 | 5741 | Transformer only | Vegetation | Tree - fell into line | 5 | 28705 | 37.3596 | -122.0654 | Yes | Overcast-Drizzle;32-90 F | Secondary | Broken- wire on ground | 23-0046038 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1825955 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1104 | 82241104 | OTHER | WIRE DOWN AT CGC#315288332668 | 20230314 | 1502 | 20230317 | 1350 | 2049109 | 4248 | Distribution Circuit | Vegetation | Tree - fell into line | 106 | 357828 | 37.3858 | -122.1228 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken | 23-0045197 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826680 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1106 | 82241106 | FUSE | 30359 | 20230314 | 1510 | 20230316 | 1635 | 2043988 | 2965 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 77090 | 37.3821 | -122.1344 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045704 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825642 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1105 | 82031105 | FUSE | 345 | 20230314 | 1513 | 20230317 | 1114 | 2046604 | 4081 | Distribution Circuit | Vegetation | Tree - fell into line | 136 | 555016 | 37.3783 | -122.1098 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045197 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1826247 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1104 | 83771104 | TRANSFORMER | 315745028158 | 20230314 | 1637 | 20230318 | 1946 | 2046037 | 5949 | Transformer only | Vegetation | Tree - fell into line | 5 | 29745 | 37.2642 | -121.9632 | Yes | Strong Winds-Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0046701 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826376 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1111 | 83481111 | RECLOSER | 60020 | 20230314 | 1743 | 20230316 | 1946 | 2042539 | 3003 | Distribution Circuit | Equipment Failure/Involved | Overhead | 372 | 890591 | 37.3393 | -122.0708 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0046094 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826006 | 0 | EPSS Ckt | N | 2023 | A-B PH
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | FUSE | 4107 | 20230314 | 2023 | 20230316 | 1528 | 2044685 | 2585 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 90475 | 37.2605 | -122.0286 | Yes | Overcast-Fog;32-90 F | Pole-Wood | Broken | 23-0045871 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1825794 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1109 | 83481109 | SWITCH | 17325 | 20230314 | 2039 | 20230318 | 1739 | 2044824 | 5580 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 12777 | 37.3133 | -122.0615 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Contaminated | 23-0044799 | OH | Sus | 35431719 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1825823 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | HICKS-2103 | 83432103 | FUSE | 23093 | 20230314 | 2046 | 20230316 | 2000 | 2044745 | 2834 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 87854 | 37.2149 | -121.9138 | Yes | Overcast;32-90 F |  |  | 23-0047241 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826701 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | HICKS-2103 | 83432103 | FUSE | 18375 | 20230314 | 2050 | 20230316 | 1841 | 2045671 | 2751 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 30261 | 37.2139 | -121.9128 | Yes | Overcast;32-90 F |  |  | 23-0047221 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1826686 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1109 | 83371109 | JUMPER | OJ 2 SPANS WEST OF 31103 | 20230314 | 2322 | 20230318 | 1744 | 2047458 | 5422 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 86752 | 37.2768 | -121.9652 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Secondary | Broken- wire on ground | 23-0046796 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826437 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1103 | 82241103 | FUSE | 4775 | 20230315 | 125 | 20230317 | 158 | 2046965 | 2913 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 37869 | 37.3847 | -122.1039 | No | Clear;32-90 F | Secondary | Broken- wire on object | 23-0047343 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826783 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1102 | 82021102 | TRANSFORMER | 315708026967 | 20230315 | 157 | 20230318 | 849 | 2045071 | 4732 | Transformer only | Vegetation | Tree - fell into line | 36 | 170352 | 37.2313 | -121.9754 | No | Clear;32-90 F | Transformer | Broken | 23-0046724 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826385 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1113 | 82031113 | FUSE | 52254 | 20230315 | 336 | 20230319 | 836 | 2045167 | 6060 | Distribution Circuit | Equipment Failure/Involved | Underground | 47 | 63277 | 37.3935 | -122.0786 | No | Overcast;32-90 F | Elbow | Failed/Faulted | 23-0046834 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826461 | 1 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | HICKS-1116 | 83431116 | FUSE | 19627 | 20230315 | 414 | 20230315 | 1849 | 2045307 | 875 | Distribution Circuit | Equipment Failure/Involved | Overhead | 105 | 62947 | 37.2355 | -121.9175 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046209 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1826088 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | HICKS-1116 | 83431116 | FUSE | 16023 | 20230315 | 425 | 20230316 | 1925 | 2045209 | 2340 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 131040 | 37.2306 | -121.9129 | No | Clear;32-90 F |  |  | 23-0047232 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826695 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | HICKS-1116 | 83431116 | FUSE | 18667 | 20230315 | 458 | 20230316 | 1409 | 2045286 | 1991 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 51766 | 37.2359 | -121.9402 | No | Clear;32-90 F |  |  | 23-0047039 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | No | No | 1826580 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | HICKS-1116 | 83431116 | FUSE | 721 | 20230315 | 607 | 20230315 | 1858 | 2045788 | 771 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 3084 | 37.2315 | -121.9195 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0046192 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826073 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1107 | 82031107 | FUSE | 1171 | 20230315 | 1137 | 20230316 | 1633 | 2048744 | 1736 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 38192 | 37.3792 | -122.0735 | No | Overcast;32-90 F |  |  | 23-0047155 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826640 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1109 | 82031109 | TRANSFORMER | 315452931880 | 20230315 | 1218 | 20230318 | 1708 | 2046112 | 4610 | Transformer only | Vegetation | Tree - branch fell on line | 4 | 18440 | 37.3655 | -122.0658 | No | Partly Cloudy;32-90 F | Transformer | Broken- wire on ground | 23-0046830 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826456 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | HICKS-1109 | 83431109 | TRANSFORMER | 315821927784 | 20230315 | 1339 | 20230317 | 1518 | 2046275 | 2979 | Transformer only | Vegetation | Tree - fell into line | 7 | 20853 | 37.2543 | -121.9367 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0046429 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826213 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1114 | 83671114 | SWITCH | 4497 | 20230315 | 1345 | 20230315 | 1404 | 2046341 | 19 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 570 | 37.3595 | -122.0329 | No | Clear;32-90 F | Conductor- Overhead | Contaminated | 23-0046072 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826204 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | HICKS-1109 | 83431109 | TRANSFORMER | 315825027784 | 20230315 | 1420 | 20230317 | 1606 | 2046403 | 2986 | Transformer only | Vegetation | Tree - fell into line | 8 | 23888 | 37.2543 | -121.9356 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0046430 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826214 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1107 | 82031107 | OTHER | WIRE DOWN @ ASDS GOLDEN WAY | 20230315 | 1455 | 20230316 | 1523 | 2046473 | 1468 | Distribution Circuit | Vegetation | Tree - branch fell on line | 43 | 60948 | 37.3608 | -122.0912 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046501 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | Yes | Yes | 1826253 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1107 | 82031107 | FUSE | 53502 | 20230315 | 1516 | 20230316 | 1126 | 2046533 | 1210 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 42350 | 37.3668 | -122.0869 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046984 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1826542 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1113 | 83371113 | FUSE | 150849 | 20230315 | 1516 | 20230316 | 1607 | 2046622 | 1491 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 102879 | 37.308 | -121.9981 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046498 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826250 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1107 | 82031107 | TRANSFORMER | 315393031552 | 20230315 | 1525 | 20230318 | 901 | 2046562 | 3936 | Transformer only | Vegetation | Tree - fell into line | 11 | 43296 | 37.356 | -122.0859 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0047528 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826874 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1113 | 83371113 | TRANSFORMER | 315556829676 | 20230315 | 1620 | 20230317 | 740 | 2046690 | 2360 | Transformer only | Environmental/External | Water | 18 | 42480 | 37.3049 | -122.0286 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0046548 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826283 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1102 | 82031102 | FUSE | 5361 | 20230315 | 1633 | 20230315 | 1731 | 2046729 | 58 | Distribution Circuit | Vegetation | Tree - branch fell on line | 46 | 2668 | 37.3863 | -122.075 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0046527 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826270 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1105 | 83371105 | FUSE | 4999 | 20230315 | 1638 | 20230316 | 2139 | 2046739 | 1741 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 108 | 188028 | 37.2674 | -122.0597 | No | Clear;32-90 F |  |  | 23-0047262 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826723 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1103 | 83371103 | FUSE | 25993 | 20230315 | 1737 | 20230317 | 2045 | 2046895 | 3068 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 42952 | 37.2798 | -122.0322 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0047342 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826782 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1103 | 83371103 | OTHER | WIRE DOWN @ CGC 315565928747 | 20230315 | 1752 | 20230317 | 1734 | 2046931 | 2862 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 63936 | 37.2795 | -122.0253 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0047424 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | Yes | Yes | 1826820 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1101 | 82021101 | FUSE | 30151 | 20230315 | 2050 | 20230315 | 2202 | 2047258 | 72 | Distribution Circuit | Equipment Failure/Involved | Overhead | 83 | 5976 | 37.2255 | -121.9649 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0046710 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826380 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WHISMAN-1106 | 83631106 | SWITCH | 2263 | 20230315 | 2053 | 20230317 | 1552 | 2047268 | 2579 | Distribution Circuit | Equipment Failure/Involved | Overhead | 48 | 113880 | 37.4198 | -122.097 | No | Overcast-Drizzle;32-90 F | Jumper | Arcing | 23-0046689 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826371 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1101 | 82021101 | TRANSFORMER | 315762026709 | 20230315 | 2101 | 20230316 | 1914 | 2047291 | 1333 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 3999 | 37.2244 | -121.9567 | No | Clear;32-90 F | Fuse | Normal | 23-0047237 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826699 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1101 | 82021101 | FUSE | 1425 | 20230315 | 2110 | 20230316 | 1825 | 2047308 | 1275 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 46 | 58679 | 37.2246 | -121.9591 | No | Clear;32-90 F |  |  | 23-0047218 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826683 | 1 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1108 | 83481108 | FUSE | 1663 | 20230315 | 2130 | 20230316 | 2332 | 2047333 | 1562 | Distribution Circuit | Vegetation | Tree - fell into line | 161 | 251482 | 37.3524 | -122.0836 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0047258 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1826721 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1101 | 82021101 | FUSE | 9837 | 20230315 | 2238 | 20230316 | 1927 | 2047847 | 1249 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 142 | 177447 | 37.2214 | -121.9731 | No | Partly Cloudy;32-90 F |  |  | 23-0047233 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826696 | 1 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1101 | 82021101 | FUSE | 30941 | 20230315 | 2355 | 20230317 | 929 | 2047501 | 2014 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 12084 | 37.2062 | -121.9511 | No | Partly Cloudy;32-90 F |  |  | 23-0047448 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826836 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1111 | 82031111 | FUSE | 665 | 20230316 | 52 | 20230318 | 705 | 2047549 | 2673 | Distribution Circuit | Equipment Failure/Involved | Underground | 633 | 294164 | 37.3809 | -122.062 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0046828 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826453 | 1 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | JUMPER | SL21 | 20230316 | 102 | 20230316 | 200 | 2047536 | 58 | Distribution Circuit | Equipment Failure/Involved | Overhead | 514 | 15154 | 37.3585 | -122.0994 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 23-0045102 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1826454 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | FUSE | 273601 | 20230316 | 127 | 20230316 | 1610 | 2047579 | 883 | Distribution Circuit | Vegetation | Tree - branch fell on line | 153 | 135099 | 37.3565 | -122.1356 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0047139 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1826628 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | FUSE | 2031 | 20230316 | 127 | 20230317 | 1243 | 2048866 | 2116 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 16928 | 37.3535 | -122.1405 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0047139 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1826629 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | FUSE | 10137 | 20230316 | 139 | 20230316 | 1410 | 2047551 | 751 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 7510 | 37.3629 | -122.1186 | No | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0047075 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826600 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1108 | 83371108 | FUSE | 30595 | 20230316 | 324 | 20230316 | 1932 | 2047589 | 968 | Distribution Circuit | Vegetation | Tree - branch fell on line | 86 | 83290 | 37.2858 | -121.9683 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0047244 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826704 | 1 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1109 | 83371109 | TRANSFORMER | 315718728415 | 20230316 | 607 | 20230318 | 1628 | 2047655 | 3501 | Distribution Circuit | Vegetation | Tree - bark fell into line | 6 | 21006 | 37.2711 | -121.9724 | No | Overcast-Heavy Rain-Strong Winds;32-90 F | Secondary | Broken- wire on ground | 23-0046848 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826471 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 468855 | 20230316 | 615 | 20230317 | 1305 | 2048899 | 1850 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 9250 | 37.2066 | -121.9716 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0047495 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826852 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | FUSE | 29867 | 20230316 | 835 | 20230317 | 818 | 2047837 | 1423 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 1423 | 37.3648 | -122.1441 | No | Partly Cloudy;32-90 F |  |  | 23-0047386 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826797 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | HICKS-1114 | 83431114 | TRANSFORMER | T9170 | 20230316 | 929 | 20230317 | 1609 | 2045942 | 1840 | Transformer only | Vegetation | Tree - fell into line | 1 | 1840 | 37.2526 | -121.9367 | No | Partly Cloudy;32-90 F | Conductor- Overhead | On Ground | 23-0046920 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826502 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1114 | 83371114 | FUSE | 8327 | 20230316 | 1046 | 20230316 | 1142 | 2048197 | 56 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 952 | 37.2956 | -122.0073 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0046955 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826526 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1108 | 82031108 | TRANSFORMER | C1017 | 20230316 | 1051 | 20230318 | 1446 | 2048211 | 3115 | Transformer only | Equipment Failure/Involved | Underground | 59 | 183785 | 37.3792 | -122.0627 | No | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Underground | Broken | 23-0047319 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826778 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1108 | 83771108 | TRANSFORMER | 315773927382 | 20230316 | 1140 | 20230317 | 1036 | 2048276 | 1376 | Transformer only | Vegetation | Tree - fell into line | 6 | 8256 | 37.2429 | -121.953 | No | Overcast-Heavy Rain-Strong Winds;32-90 F | Secondary | Broken- wire on ground | 23-0046976 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826537 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1101 | 82021101 | TRANSFORMER | 315765026897 | 20230316 | 1215 | 20230316 | 1230 | 2048417 | 15 | Transformer only | Vegetation | Tree - branch fell on line | 4 | 60 | 37.2296 | -121.9557 | No | Overcast-Rain-Strong Winds;32-90 F | Secondary | Normal | 23-0047016 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826563 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1102 | 83771102 | JUMPER | OPEN JUMPERS | 20230316 | 1254 | 20230317 | 2027 | 2048455 | 1893 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 41646 | 37.2359 | -121.9609 | No | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0047026 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826571 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1103 | 83371103 | TRANSFORMER | 315571528844 | 20230316 | 1258 | 20230318 | 1549 | 2050074 | 3051 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 21357 | 37.2822 | -122.0233 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0047585 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826898 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1102 | 82031102 | TRANSFORMER | 315347733580 | 20230316 | 1344 | 20230316 | 1517 | 2048573 | 93 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 2396 | 37.4113 | -122.1029 | No | Clear;32-90 F | Secondary | Deteriorated | 23-0047053 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1826586 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOYOLA-0403 | 82160403 | JUMPER | OPEN JUMPERS 4/2P/N/O 3267 | 20230316 | 1356 | 20230316 | 2115 | 2048598 | 439 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2634 | 37.3639 | -122.0978 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0047067 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826594 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | FUSE | 15767 | 20230316 | 1501 | 20230317 | 1322 | 2048758 | 1341 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 8046 | 37.2364 | -122.0662 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0047109 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826617 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1111 | 83421111 | TRANSFORMER | 315627032945 | 20230316 | 1511 | 20230316 | 1544 | 2048834 | 33 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 363 | 37.3952 | -122.0062 | No | Overcast-Drizzle-Strong Winds;32-90 F | Secondary | Broken | 23-0047156 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826641 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1103 | 83481103 | TRANSFORMER | 315527730619 | 20230316 | 1518 | 20230317 | 1602 | 2048795 | 1484 | Transformer only | Vegetation | Tree - fell into line | 7 | 10388 | 37.3307 | -122.0393 | No | Partly Cloudy;32-90 F | Transformer | Burned/flashed | 23-0047578 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826895 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1111 | 83421111 | TRANSFORMER | 315627032945 | 20230316 | 1525 | 20230317 | 1820 | 2049025 | 1615 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 17765 | 37.3952 | -122.0062 | No | Clear;32-90 F | Secondary | Failed/Faulted | 23-0047303 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826764 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1106 | 82241106 | FUSE | 30351 | 20230316 | 1638 | 20230317 | 845 | 2048949 | 967 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 5802 | 37.3927 | -122.1479 | No | Clear;32-90 F |  |  | 23-0047407 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826811 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 12943 | 20230316 | 1731 | 20230316 | 2051 | 2049009 | 200 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 59 | 11800 | 37.2125 | -122.0677 | No | Clear;32-90 F |  |  | 23-0047260 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826722 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | OCB | 1102/2 | 20230316 | 1831 | 20230316 | 1856 | 2048715 | 25 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2807 | 70175 | 37.361 | -122.0992 | No | Overcast;32-90 F |  |  | 23-0047225 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826689 | 0 | EPSS Ckt | N | 2023 | UNKNOWN
DE ANZA | DE ANZA | EL PATIO-1117 | 82921117 | TRANSFORMER | 315733528546 | 20230316 | 1846 | 20230317 | 1845 | 2050677 | 1439 | Transformer only | Unknown Cause | Patrol - found nothing | 11 | 15829 | 37.2748 | -121.9674 | No | Partly Cloudy;32-90 F |  |  | 23-0047745 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1826986 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | FUSE | 125 | 20230316 | 1942 | 20230317 | 1508 | 2049211 | 1166 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 3498 | 37.373 | -122.1482 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0047619 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826917 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1107 | 82031107 | SWITCH | 15256 | 20230316 | 2124 | 20230317 | 151 | 2049336 | 267 | Distribution Circuit | Vegetation | Tree - branch fell on line | 86 | 7218 | 37.3792 | -122.0735 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0047202 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826732 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | FUSE | 3559 | 20230316 | 2319 | 20230317 | 1500 | 2049468 | 941 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 8469 | 37.2403 | -121.9968 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0047641 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826925 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | TRANSFORMER | 315833322995 | 20230317 | 5 | 20230317 | 1247 | 2049397 | 762 | Transformer only | Vegetation | Tree - branch fell on line | 3 | 2286 | 37.1227 | -121.9303 | No | Clear;32-90 F | Other | Normal | 23-0047592 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826903 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1108 | 83481108 | OTHER | 1 OF 2 PHASES DOWN | 20230317 | 122 | 20230317 | 1611 | 2049899 | 889 | Distribution Circuit | Equipment Failure/Involved | Overhead | 146 | 21024 | 37.3438 | -122.0535 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0047522 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | Yes | 1826869 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | FUSE | 2697 | 20230317 | 619 | 20230317 | 1038 | 2049462 | 259 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 65 | 16835 | 37.2734 | -122.023 | No | Clear;32-90 F |  |  | 23-0047435 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826829 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | FUSE | 1497 | 20230317 | 630 | 20230318 | 1830 | 2049465 | 2160 | Distribution Circuit | Vegetation | Tree - grew into line | 5 | 10800 | 37.2391 | -122.0008 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0047695 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826947 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | FUSE | 3563 | 20230317 | 633 | 20230317 | 1404 | 2049467 | 451 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 4059 | 37.2389 | -121.9953 | No | Clear;32-90 F |  |  | 23-0047633 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826922 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | FUSE | 29131 | 20230317 | 639 | 20230317 | 1205 | 2049476 | 326 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 8150 | 37.2449 | -122.0058 | No | Clear;32-90 F |  |  | 23-0047535 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826877 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | FUSE | 5089 | 20230317 | 642 | 20230317 | 1324 | 2049504 | 402 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 12060 | 37.2339 | -121.9978 | No | Clear;32-90 F |  |  | 23-0047587 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826900 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | TRANSFORMER | 315558728612 | 20230317 | 659 | 20230317 | 1604 | 2050456 | 545 | Transformer only | Company Initiated | Personnel- company | 9 | 4905 | 37.2758 | -122.0273 | No | Clear;32-90 F | Transformer (OH) |  | 23-0047710 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826957 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | TRANSFORMER | 315608527985 | 20230317 | 737 | 20230317 | 1539 | 2049522 | 482 | Transformer only | Vegetation | Tree - fell into line | 4 | 1928 | 37.2587 | -122.0097 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0047684 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826939 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | HICKS-1116 | 83431116 | TRANSFORMER | 315902426924 | 20230317 | 752 | 20230317 | 1654 | 2049537 | 542 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 2710 | 37.231 | -121.9085 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0047509 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826861 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1106 | 82241106 | TRANSFORMER | 315234032693 | 20230317 | 1018 | 20230319 | 1215 | 2049804 | 2997 | Transformer only | Environmental/External | Water | 3 | 8991 | 37.3864 | -122.1414 | No | Clear;32-90 F | Transformer | Broken | 23-0048441 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827650 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1109 | 82031109 | TRANSFORMER | T13114 | 20230317 | 1114 | 20230318 | 1737 | 2049915 | 1823 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 1823 | 37.3602 | -122.0637 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0047682 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826938 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1106 | 82241106 | FUSE | 5353 | 20230317 | 1117 | 20230317 | 1302 | 2040661 | 105 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 1260 | 37.3966 | -122.122 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0047532 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1826875 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1107 | 82031107 | FUSE | 331 | 20230317 | 1217 | 20230317 | 1245 | 2050030 | 28 | Distribution Circuit | Vegetation | Tree - bark fell into line | 68 | 1904 | 37.3618 | -122.0961 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0047568 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826891 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1115 | 83371115 | FUSE | 19701 | 20230317 | 1342 | 20230317 | 2330 | 2050194 | 588 | Distribution Circuit | Equipment Failure/Involved | Overhead | 254 | 149352 | 37.301 | -122.0361 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0047664 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826932 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | OTHER | WIRE DOWN 5 SP/N/O 8975 | 20230317 | 1414 | 20230318 | 1719 | 2050243 | 1625 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 6404 | 37.1809 | -122.006 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0047636 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | Yes | No | 1826923 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WOLFE-1113 | 83671113 | TRANSFORMER | 315486431201 | 20230317 | 1522 | 20230318 | 1932 | 2051413 | 1690 | Distribution Circuit | Equipment Failure/Involved | Overhead | 119 | 35000 | 37.3467 | -122.0536 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0048342 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827546 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1108 | 83481108 | JUMPER | FB @ 1357 FRANCHER PL | 20230317 | 1804 | 20230317 | 1910 | 2050640 | 66 | Distribution Circuit | Vegetation | Tree - grew into line | 16 | 1056 | 37.3497 | -122.0542 | No | Clear;32-90 F | Conductor- Overhead | Contaminated | 23-0047737 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826980 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1104 | 83421104 | TRANSFORMER | 315650033061 | 20230318 | 1113 | 20230318 | 1442 | 2051107 | 209 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 2508 | 37.3985 | -121.9984 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0048289 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1827511 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1109 | 83481109 | OCB | 1109/2 | 20230318 | 1220 | 20230318 | 1342 | 2051177 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3988 | 274845 | 37.3358 | -122.043 | No | Partly Cloudy;32-90 F |  |  | 23-0048308 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1827523 | 0 | EPSS Ckt | N | 2023 | PH INST & PHASE TIME OC
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | SWITCH | 698481 | 20230318 | 1253 | 20230318 | 1346 | 2051201 | 53 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 212 | 37.2053 | -121.9708 | No | Overcast;32-90 F | Jumper | Broken | 23-0048313 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1827527 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1109 | 83481109 | OCB | 1109/2 | 20230318 | 1444 | 20230318 | 1738 | 2051303 | 174 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3988 | 204771 | 37.3358 | -122.043 | No | Overcast;32-90 F | Conductor- Overhead | Contaminated | 23-0048329 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1827536 | 0 | EPSS Ckt | N | 2023 | PH INST- A B C
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | RECLOSER | 60118 | 20230318 | 1554 | 20230318 | 1828 | 2051394 | 154 | Distribution Circuit | Vegetation | Tree - branch fell on line | 933 | 44386 | 37.1247 | -121.9353 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0048339 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1827542 | 0 | EPSS Ckt | N | 2023 | SGF
DE ANZA | DE ANZA | STELLING-1111 | 83481111 | TRANSFORMER | 315428530820 | 20230318 | 1749 | 20230319 | 1019 | 2050921 | 990 | Transformer only | Equipment Failure/Involved | Electrical Overload | 5 | 4950 | 37.3361 | -122.0733 | No | Overcast;32-90 F | Connector or Splice (OH) | Burned/flashed | 23-0048353 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827556 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 8989 | 20230318 | 1900 | 20230322 | 1553 | 2051485 | 5573 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 11146 | 37.1812 | -122.0059 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0048354 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1827558 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1109 | 83481109 | TRANSFORMER | T7398 | 20230318 | 1901 | 20230318 | 2057 | 2051486 | 116 | Transformer only | Unknown Cause | Patrol - not conducted | 9 | 1044 | 37.3121 | -122.0615 | No | Clear;32-90 F |  |  | 23-0048409 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1827615 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WOLFE-1114 | 83671114 | SWITCH | 10089 | 20230318 | 1920 | 20230318 | 1942 | 2051539 | 22 | Distribution Circuit | Company Initiated | Return Circuit Normal | 19 | 418 | 37.3468 | -122.0306 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0046049 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1827562 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | TRANSFORMER | 315559328496 | 20230318 | 2316 | 20230319 | 49 | 2051595 | 93 | Transformer only | Unknown Cause | Patrol - found nothing | 8 | 744 | 37.2726 | -122.0271 | No | Clear;32-90 F |  |  | 23-0048416 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1827622 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | HICKS-1116 | 83431116 | TRANSFORMER | 315887526977 | 20230319 | 11 | 20230319 | 701 | 2051604 | 410 | Transformer only | Vegetation | Tree - bark fell into line | 5 | 2050 | 37.2323 | -121.9171 | No | Overcast-Drizzle;32-90 F | Fuse | Together | 23-0048418 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827624 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 89897 | 20230319 | 139 | 20230319 | 1305 | 2051662 | 686 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 8918 | 37.1623 | -121.9172 | No | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0048479 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827689 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 18123 | 20230319 | 349 | 20230319 | 1703 | 2051652 | 794 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 14292 | 37.1324 | -121.9571 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0048529 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1827735 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1109 | 83481109 | TRANSFORMER | 315500929948 | 20230319 | 458 | 20230319 | 1203 | 2051671 | 425 | Transformer only | Environmental/External | Water | 11 | 4675 | 37.3121 | -122.048 | No | Overcast-Drizzle;32-90 F | Transformer | Failed/Faulted | 23-0048448 | OH | Sus | 35431719 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827658 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | TRANSFORMER | 315321632045 | 20230319 | 520 | 20230319 | 1138 | 2051641 | 378 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 4158 | 37.3689 | -122.1104 | No | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on object | 23-0048438 | OH | Sus | 35431719 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1827646 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1106 | 82241106 | RECLOSER | 60028 | 20230319 | 523 | 20230319 | 643 | 2051681 | 80 | Distribution Circuit | Vegetation | Tree - branch fell on line | 564 | 45120 | 37.397 | -122.1179 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0048427 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | No | No | 1827635 | 0 | Non-EPSS | N | 2023 | A B C
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | OCB | 1102/2 | 20230319 | 704 | 20230319 | 1132 | 2051736 | 268 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 804 | 37.361 | -122.0992 | No | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken | 23-0048435 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1827644 | 0 | EPSS Ckt | N | 2023 | N/A
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | TRANSFORMER | 315579828614 | 20230319 | 904 | 20230319 | 1151 | 2051828 | 167 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 1837 | 37.2759 | -122.0201 | No | Overcast;32-90 F | Secondary | Broken | 23-0048461 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1827672 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | JUMPER | OJ'S 1 POLE NW/O 510151 | 20230319 | 951 | 20230319 | 1855 | 2051890 | 544 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 544 | 37.123 | -121.9577 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken | 23-0048465 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827676 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | TRANSFORMER | 315893622316 | 20230319 | 1333 | 20230323 | 1037 | 2052073 | 5584 | Transformer only | Vegetation | Tree - fell into line | 1 | 5584 | 37.1045 | -121.9102 | No | Clear;32-90 F | Service conductor | Together | 23-0048546 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827755 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1113 | 83481113 | TRANSFORMER | 315480331491 | 20230319 | 1401 | 20230321 | 1800 | 2052107 | 3119 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 31190 | 37.3547 | -122.0552 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0049750 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828463 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | FUSE | 29131 | 20230319 | 1441 | 20230319 | 1658 | 2052129 | 137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 3425 | 37.2449 | -122.0058 | No | Clear-Strong Winds;32-90 F |  |  | 23-0048537 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1827745 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 89897 | 20230319 | 1445 | 20230322 | 1956 | 2052153 | 4631 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 36921 | 37.1617 | -121.9142 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 23-0048517 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827724 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1108 | 83481108 | TRANSFORMER | 315407431466 | 20230319 | 1500 | 20230320 | 427 | 2052151 | 807 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 2421 | 37.3534 | -122.0812 | No | Overcast;32-90 F | Transformer | Broken- wire on object | 23-0048516 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1827723 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | TRANSFORMER | 315559328496 | 20230319 | 1503 | 20230320 | 1612 | 2052148 | 1509 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 12072 | 37.2726 | -122.0271 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0048551 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827759 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-0403 | 82160403 | TRANSFORMER | 315350232180 | 20230319 | 1645 | 20230320 | 319 | 2052235 | 634 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 5706 | 37.373 | -122.1013 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 23-0048540 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827748 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | TRANSFORMER | 315680824166 | 20230319 | 1822 | 20230319 | 2153 | 2052301 | 211 | Transformer only | Vegetation | Tree - fell into line | 2 | 422 | 37.1548 | -121.9831 | No | Clear;32-90 F | Secondary | Broken | 23-0048565 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827772 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1109 | 83481109 | TRANSFORMER | 315505129555 | 20230320 | 1909 | 20230321 | 116 | 2053427 | 367 | Transformer only | Vegetation | Tree - fell into line | 14 | 5138 | 37.3014 | -122.0464 | No | Overcast;32-90 F | Secondary | Broken | 23-0049006 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1827964 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | FUSE | 29289 | 20230321 | 23 | 20230321 | 203 | 2053508 | 100 | Distribution Circuit | Animal | Other | 9 | 900 | 37.3533 | -122.1414 | Yes | Overcast;32-90 F | Bushing | Normal | 23-0049058 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828014 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1108 | 83481108 | TRANSFORMER | 315479531287 | 20230321 | 29 | 20230321 | 151 | 2053510 | 82 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 656 | 37.349 | -122.0554 | Yes | Overcast;32-90 F | Crossarm- Wood | Broken | 23-0049055 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1828012 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 15069 | 20230321 | 52 | 20230321 | 1457 | 2053509 | 845 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 21125 | 37.1038 | -121.8982 | Yes | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0049054 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1828011 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1108 | 83371108 | OCB | 1108/2 | 20230321 | 1222 | 20230321 | 1435 | 2054816 | 133 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3419 | 452837 | 37.281 | -122.0156 | Yes | Overcast-Rain;32-90 F |  |  | 23-0049471 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828238 | 0 | Non-EPSS | N | 2023 | UNKNOWN
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 23009 | 20230321 | 1226 | 20230322 | 1513 | 2054419 | 1607 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 79 | 126953 | 37.1673 | -122.0363 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0050796 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829248 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | JUMPER | OPEN JUMPERS 1 SP/E/O CGC 315654024149 | 20230321 | 1244 | 20230322 | 1258 | 2057256 | 1454 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 42166 | 37.1536 | -121.9918 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 23-0049460 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828468 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | FUSE | 33581 | 20230321 | 1244 | 20230322 | 1258 | 2060648 | 1454 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 8724 | 37.1544 | -121.989 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Crossarm- Wood | Broken | 23-0049460 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1828813 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | FUSE | 4263 | 20230321 | 1244 | 20230322 | 1538 | 2062733 | 1614 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 155 | 250170 | 37.1371 | -121.9971 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0050675 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829165 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | JUMPER | OPEN JUMPERS 1 P/SW/O 21085 | 20230321 | 1244 | 20230322 | 1717 | 2060015 | 1713 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 56529 | 37.1609 | -121.978 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0049460 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | Yes | No | 1828712 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | JUMPER | OPEN JUMPERS SOURCE SIDE CGC 315748922938 | 20230321 | 1244 | 20230323 | 1905 | 2063426 | 3261 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 45654 | 37.1227 | -121.9585 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken | 23-0050927 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829327 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 17431 | 20230321 | 1246 | 20230322 | 2303 | 2054547 | 2057 | Distribution Circuit | Vegetation | Tree - bark fell into line | 33 | 67881 | 37.1103 | -121.9511 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0051110 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1829492 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | JUMPER | JUMPERS NORTH OF CGC LAST FOUR #3305 | 20230321 | 1252 | 20230323 | 1200 | 2062682 | 2828 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 2828 | 37.1294 | -122.0076 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050651 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829155 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | RECLOSER | 408318 | 20230321 | 1253 | 20230323 | 1302 | 2054616 | 2876 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1008 | 478102 | 37.2474 | -122.0138 | Yes | Overcast;32-90 F | Pole-Wood | Broken | 23-0049455 | OH | Sus | 35431719 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828221 | 0 | EPSS Ckt | N | 2023 | A-B PH & 51(INST)
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 21113 | 20230321 | 1254 | 20230323 | 1740 | 2054691 | 3166 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 22162 | 37.1017 | -121.9395 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050876 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1829292 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | RECLOSER | 60116 | 20230321 | 1255 | 20230322 | 1716 | 2054562 | 1701 | Distribution Circuit | Vegetation | Tree - fell into line | 1442 | 1352916 | 37.1735 | -121.9928 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0049460 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828225 | 0 | EPSS Ckt | N | 2023 | A PH & GRD
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | JUMPER | OJ 1 POLE LD SIDE OF CGC# 315704923434 | 20230321 | 1255 | 20230323 | 1705 | 2063329 | 3130 | Distribution Circuit | Vegetation | Tree - grew into line | 3 | 9390 | 37.1344 | -121.9749 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken | 23-0049460 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829305 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | RECLOSER | 991992 | 20230321 | 1257 | 20230323 | 1924 | 2054820 | 3267 | Distribution Circuit | Equipment Failure/Involved | Overhead | 52 | 110924 | 37.1894 | -122.0309 | Yes | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0049469 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1828236 | 0 | EPSS Ckt | N | 2023 | A C 51
DE ANZA | DE ANZA | SARATOGA-1108 | 83371108 | FUSE | 32571 | 20230321 | 1257 | 20230321 | 1755 | 2056055 | 298 | Distribution Circuit | Equipment Failure/Involved | Overhead | 112 | 33376 | 37.2855 | -121.9871 | Yes | Overcast-Rain;32-90 F | Crossarm- Wood | Broken | 23-0049579 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828326 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | HICKS-1116 | 83431116 | TRANSFORMER | 315902426924 | 20230321 | 1303 | 20230323 | 1833 | 2054912 | 3210 | Distribution Circuit | Vegetation | Tree - grew into line | 27 | 20296 | 37.231 | -121.9085 | Yes | Overcast-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 23-0051106 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829489 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MENLO-1103 | 24131103 | RECLOSER | 866118 | 20230321 | 1303 | 20230322 | 32 | 2054983 | 689 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 157 | 94473 | 37.3756 | -122.1668 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0049470 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828237 | 0 | EPSS Ckt | N | 2023 | A B C 51
DE ANZA | DE ANZA | SARATOGA-1105 | 83371105 | FUSE | 4999 | 20230321 | 1305 | 20230322 | 1141 | 2054973 | 1356 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 108 | 146448 | 37.2674 | -122.0597 | Yes | Clear-Strong Winds;32-90 F |  |  | 23-0050543 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1829100 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | FUSE | 11753 | 20230321 | 1305 | 20230404 | 2220 | 2060577 | 20715 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 165720 | 37.2585 | -122.0949 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050128 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828794 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | RECLOSER | 568350 | 20230321 | 1305 | 20230324 | 54 | 2055028 | 3113 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3969 | 911862 | 37.3221 | -122.0795 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 23-0049481 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1828247 | 0 | EPSS Ckt | N | 2023 | B- C & 51
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | TRIP-SAVER | 9265 | 20230321 | 1305 | 20230322 | 1722 | 2060611 | 1697 | Distribution Circuit | Equipment Failure/Involved | Overhead | 43 | 72971 | 37.294 | -122.1023 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | On Ground | 23-0049481 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1828803 | 0 | EPSS Ckt | N | 2023 | NONE
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | FUSE | 277753 | 20230321 | 1305 | 20230322 | 2357 | 2060620 | 2092 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 35564 | 37.2951 | -122.1041 | Yes | Overcast-Rain;32-90 F | Pole-Wood | Broken | 23-0049481 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1828805 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WOLFE-1106 | 83671106 | OCB | 1106/2 | 20230321 | 1307 | 20230321 | 1629 | 2055027 | 202 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1942 | 193332 | 37.3347 | -122.0209 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049491 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828253 | 0 | Non-EPSS | N | 2023 | RCL LOCKOUT
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | RECLOSER | 60024 | 20230321 | 1308 | 20230322 | 1813 | 2055220 | 1745 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 43625 | 37.1704 | -121.9386 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken | 23-0049529 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828289 | 0 | EPSS Ckt | N | 2023 | A- B & 51
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 4463 | 20230321 | 1308 | 20230323 | 248 | 2056382 | 2260 | Distribution Circuit | Vegetation | Tree - fell into line | 295 | 226922 | 37.1071 | -121.9472 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050620 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829136 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WOLFE-1113 | 83671113 | OCB | 1113/2 | 20230321 | 1309 | 20230321 | 1630 | 2055069 | 201 | Distribution Circuit | Vegetation | Tree - fell into line | 4381 | 880581 | 37.3347 | -122.0207 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0049506 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | No | No | 1828264 | 0 | Non-EPSS | N | 2023 | NO TARGETS
DE ANZA | DE ANZA | WOLFE-1113 | 83671113 | FUSE | 22941 | 20230321 | 1309 | 20230321 | 1630 | 2056930 | 201 | Distribution Circuit | Vegetation | Tree - fell into line | 158 | 31758 | 37.3604 | -122.0402 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0049506 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828435 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1108 | 83481108 | TRANSFORMER | 315483730962 | 20230321 | 1310 | 20230322 | 1513 | 2055049 | 1563 | Distribution Circuit | Equipment Failure/Involved | Overhead | 124 | 40032 | 37.34 | -122.0545 | Yes | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0050641 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1829148 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1111 | 83481111 | FUSE | 2851 | 20230321 | 1311 | 20230322 | 1430 | 2055081 | 1519 | Distribution Circuit | Vegetation | Tree - bark fell into line | 28 | 42532 | 37.3434 | -122.0886 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken | 23-0050033 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828716 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1107 | 82241107 | OCB | 1107/2 | 20230321 | 1313 | 20230321 | 1433 | 2055138 | 80 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 2751 | 220080 | 37.3936 | -122.115 | Yes | Clear;32-90 F |  |  | 23-0049492 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828254 | 0 | Non-EPSS | N | 2023 | UNKNOWN
DE ANZA | DE ANZA | LOS GATOS-1108 | 82021108 | RECLOSER | 590544 | 20230321 | 1314 | 20230322 | 1633 | 2055131 | 1626 | Distribution Circuit | Vegetation | Tree - branch fell on line | 788 | 588969 | 37.225 | -121.9842 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049508 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828268 | 0 | EPSS Ckt | N | 2023 | GRD
DE ANZA | DE ANZA | AMES-1102 | 83901102 | OCB | 1102/2 | 20230321 | 1315 | 20230321 | 1918 | 2055261 | 363 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 34848 | 37.418 | -122.0674 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0049509 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828269 | 0 | Non-EPSS | N | 2023 | N/A
DE ANZA | DE ANZA | STELLING-1111 | 83481111 | TRANSFORMER | 315433730865 | 20230321 | 1316 | 20230322 | 1636 | 2056343 | 1640 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 13120 | 37.3374 | -122.0715 | Yes | Overcast-Heavy Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0050198 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828859 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1112 | 83371112 | TRANSFORMER | 315634328906 | 20230321 | 1318 | 20230322 | 1453 | 2055193 | 1535 | Transformer only | Vegetation | Tree - fell into line | 6 | 9210 | 37.2842 | -122.0016 | Yes | Overcast-Heavy Rain;32-90 F | Transformer | Broken- wire on ground | 23-0050196 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828857 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WHISMAN-1111 | 83631111 | TRANSFORMER | 315471833159 | 20230321 | 1318 | 20230322 | 948 | 2055175 | 1230 | Transformer only | Unknown Cause | Patrol - found nothing | 18 | 22140 | 37.4011 | -122.0597 | Yes | Overcast-Rain;32-90 F |  |  | 23-0050454 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1829058 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 2905 | 20230321 | 1319 | 20230322 | 1735 | 2055199 | 1696 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 5088 | 37.1125 | -121.948 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0050947 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1829345 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1108 | 82031108 | FUSE | 78317 | 20230321 | 1319 | 20230322 | 1504 | 2055247 | 1545 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 13397 | 37.3798 | -122.0512 | Yes | Overcast-Rain;32-90 F |  |  | 23-0050806 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829256 | 1 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1114 | 83371114 | FUSE | 8419 | 20230321 | 1319 | 20230323 | 1428 | 2055246 | 2949 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 114984 | 37.286 | -122.0147 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049689 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828415 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | HICKS-1109 | 83431109 | FUSE | 19311 | 20230321 | 1320 | 20230322 | 1008 | 2055242 | 1248 | Distribution Circuit | Equipment Failure/Involved | Overhead | 138 | 172224 | 37.258 | -121.9359 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049831 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828535 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1105 | 83771105 | OCB | 1105/2/NORM | 20230321 | 1320 | 20230321 | 1515 | 2055302 | 115 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 2676 | 307740 | 37.2537 | -121.9662 | Yes | Clear;32-90 F |  |  | 23-0049512 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828272 | 0 | Non-EPSS | N | 2023 | B- C & 50
DE ANZA | DE ANZA | WHISMAN-1106 | 83631106 | INTERRUPTER | 49012 | 20230321 | 1321 | 20230321 | 1931 | 2055377 | 370 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 246 | 91020 | 37.4142 | -122.0928 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0050089 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828761 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | EL PATIO-1117 | 82921117 | FUSE | 46729 | 20230321 | 1322 | 20230321 | 1555 | 2055353 | 153 | Distribution Circuit | Vegetation | Tree - branch fell on line | 567 | 86751 | 37.2829 | -121.9489 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0049730 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828449 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 19887 | 20230321 | 1324 | 20230322 | 2138 | 2054789 | 1934 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 5802 | 37.1005 | -121.9319 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0051038 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1829420 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1108 | 82031108 | FUSE | 11977 | 20230321 | 1324 | 20230321 | 1730 | 2055331 | 246 | Distribution Circuit | Vegetation | Tree - branch fell on line | 475 | 116850 | 37.3755 | -122.0592 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0049930 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828617 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1102 | 82031102 | FUSE | 483 | 20230321 | 1325 | 20230322 | 1456 | 2055345 | 1531 | Distribution Circuit | Equipment Failure/Involved | Overhead | 85 | 130135 | 37.3867 | -122.0727 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050697 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1829179 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WHISMAN-1108 | 83631108 | RECLOSER | LM34 | 20230321 | 1325 | 20230321 | 1642 | 2055366 | 197 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1058 | 208426 | 37.4016 | -122.0797 | Yes | Clear;32-90 F |  |  | 23-0049528 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828288 | 0 | Non-EPSS | N | 2023 | A & B PH
DE ANZA | DE ANZA | LOS ALTOS-1106 | 82241106 | FUSE | 30351 | 20230321 | 1326 | 20230321 | 1547 | 2055359 | 141 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 846 | 37.3927 | -122.1479 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0049769 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828479 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1115 | 83371115 | TRANSFORMER | 315557829537 | 20230321 | 1326 | 20230322 | 2115 | 2055368 | 1909 | Transformer only | Vegetation | Tree - fell into line | 28 | 53452 | 37.3011 | -122.0283 | Yes | Overcast-Heavy Rain;32-90 F | Transformer | Broken- wire on ground | 23-0049886 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1828579 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1106 | 82241106 | TRANSFORMER | 315280833062 | 20230321 | 1330 | 20230323 | 1117 | 2055457 | 2747 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 13735 | 37.3968 | -122.1256 | Yes | Overcast-Rain;32-90 F | Transformer (OH) | Deteriorated | 23-0051128 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829505 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1108 | 82031108 | FUSE | 19657 | 20230321 | 1330 | 20230321 | 1602 | 2055468 | 152 | Distribution Circuit | Vegetation | Tree - fell into line | 527 | 80104 | 37.3788 | -122.0457 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0049707 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828430 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1109 | 82031109 | FUSE | 1705 | 20230321 | 1330 | 20230322 | 1136 | 2055923 | 1326 | Distribution Circuit | Vegetation | Tree - branch fell on line | 187 | 59880 | 37.3568 | -122.0772 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049724 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1828445 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1108 | 83771108 | FUSE | 32071 | 20230321 | 1333 | 20230322 | 959 | 2055517 | 1226 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 57 | 69882 | 37.2424 | -121.9496 | Yes | Clear-Strong Winds;32-90 F |  |  | 23-0050460 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829062 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1105 | 83371105 | FUSE | 3837 | 20230321 | 1335 | 20230323 | 1712 | 2055537 | 3097 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 102201 | 37.2609 | -122.0542 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0050235 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828895 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1104 | 82241104 | TRANSFORMER | 315330032476 | 20230321 | 1338 | 20230324 | 1013 | 2055579 | 4115 | Transformer only | Vegetation | Tree - fell into line | 10 | 41150 | 37.3809 | -122.1083 | Yes | Rain-Overcast;32-90 F | Transformer | Broken- wire on ground | 23-0050897 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829310 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | RECLOSER | LL64 | 20230321 | 1338 | 20230321 | 1454 | 2055588 | 76 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 247 | 18772 | 37.3773 | -122.1529 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0049545 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828308 | 0 | EPSS Ckt | N | 2023 | B & C PH
DE ANZA | DE ANZA | STELLING-1113 | 83481113 | OCB | 1113/2 | 20230321 | 1341 | 20230322 | 1658 | 2055649 | 1625 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3200 | 952242 | 37.3358 | -122.0429 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on object | 23-0049567 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1828318 | 0 | Non-EPSS | N | 2023 | A-B PH & 51(TIMED)
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | RECLOSER | 413816 | 20230321 | 1351 | 20230323 | 1430 | 2054969 | 2919 | Distribution Circuit | Equipment Failure/Involved | Overhead | 133 | 260846 | 37.2525 | -122.0605 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049571 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1828320 | 0 | EPSS Ckt | N | 2023 | NONE
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | SWITCH | 257207 | 20230321 | 1351 | 20230404 | 2220 | 2061436 | 20669 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 516725 | 37.2482 | -122.0711 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0050281 | OH | Sus | 35431719 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828942 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 21117 | 20230321 | 1415 | 20230323 | 1055 | 2056374 | 2680 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 41 | 109880 | 37.1083 | -121.8333 | Yes | Overcast;32-90 F |  |  | 23-0051307 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1829596 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | HICKS-2103 | 83432103 | OCB | 2103/2 | 20230321 | 1431 | 20230322 | 608 | 2056538 | 937 | Distribution Circuit | Vegetation | Tree - fell into line | 3661 | 358615 | 37.2332 | -121.9013 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0049647 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828380 | 0 | EPSS Ckt | N | 2023 | PH OC INST A PH
DE ANZA | DE ANZA | STELLING-1111 | 83481111 | FUSE | 2659 | 20230321 | 1455 | 20230323 | 348 | 2056748 | 2213 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 77455 | 37.3274 | -122.0613 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050266 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | Yes | 1828926 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | EL PATIO-1118 | 82921118 | JUMPER | OJ 2 POLES E/O 6537 | 20230321 | 1528 | 20230322 | 1204 | 2062392 | 1236 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 11124 | 37.2893 | -121.9302 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0050559 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1829105 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1101 | 82021101 | FUSE | 11565 | 20230321 | 1543 | 20230322 | 132 | 2057334 | 589 | Distribution Circuit | Vegetation | Tree - branch fell on line | 775 | 91607 | 37.2286 | -121.9663 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0050288 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828950 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WOLFE-1105 | 83671105 | FUSE | 12631 | 20230321 | 1543 | 20230321 | 2057 | 2057331 | 314 | Distribution Circuit | Vegetation | Tree - branch fell on line | 97 | 30458 | 37.3133 | -122.0134 | Yes | Overcast-Heavy Rain;32-90 F | Transformer (OH) | Normal | 23-0050152 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828815 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1103 | 83371103 | OCB | 1103/2 | 20230321 | 1549 | 20230321 | 1810 | 2057340 | 141 | Distribution Circuit | Vegetation | Tree - fell into line | 1956 | 275796 | 37.281 | -122.0157 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0049793 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828499 | 0 | EPSS Ckt | N | 2023 | N/A
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | RECLOSER | LL64 | 20230321 | 1613 | 20230322 | 59 | 2057942 | 526 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 248 | 130448 | 37.3773 | -122.1529 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0049832 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828536 | 0 | EPSS Ckt | N | 2023 | B & C PH
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | TRANSFORMER | 315888422028 | 20230321 | 1624 | 20230324 | 1708 | 2063850 | 4364 | Transformer only | Vegetation | Tree - fell into line | 2 | 8728 | 37.0973 | -121.9095 | Yes | Overcast;32-90 F | Transformer (OH) | Broken | 23-0051284 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829586 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | EL PATIO-1117 | 82921117 | OCB | 1117/2 | 20230321 | 1652 | 20230322 | 1219 | 2058797 | 1167 | Distribution Circuit | Vegetation | Tree - fell into line | 7053 | 1178810 | 37.2917 | -121.9356 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049905 | OH | Sus | 35431719 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | Yes | No | 1828596 | 0 | Non-EPSS | N | 2023 | B C & GRD
DE ANZA | DE ANZA | SARATOGA-1104 | 83371104 | FUSE | 9223 | 20230321 | 1802 | 20230322 | 1333 | 2059754 | 1171 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 43 | 50353 | 37.247 | -121.9946 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0050689 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829173 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1102 | 83771102 | TRANSFORMER | 315766027105 | 20230321 | 1809 | 20230322 | 1831 | 2058608 | 1462 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 17544 | 37.2353 | -121.9554 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050573 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829112 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | FUSE | 26059 | 20230321 | 1837 | 20230322 | 1456 | 2059983 | 1219 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 31694 | 37.2391 | -122.0128 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0050795 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1829247 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 4435 | 20230321 | 2050 | 20230323 | 1431 | 2060916 | 2501 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 85034 | 37.1664 | -121.9895 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken | 23-0051032 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829413 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1103 | 83771103 | FUSE | 8175 | 20230322 | 206 | 20230323 | 1156 | 2062139 | 2030 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 34510 | 37.2533 | -121.9678 | No | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050437 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1829046 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | OCB | 1102/2 | 20230322 | 550 | 20230322 | 2022 | 2061631 | 842 | Distribution Circuit | Vegetation | Tree - fell into line | 3713 | 564856 | 37.361 | -122.0992 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050321 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828984 | 0 | EPSS Ckt | N | 2023 | GRD
DE ANZA | DE ANZA | VASONA-1103 | 83771103 | FUSE | 52334 | 20230322 | 1050 | 20230322 | 2019 | 2062410 | 569 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 66 | 37554 | 37.2549 | -121.9677 | No | Clear;32-90 F |  |  | 23-0051008 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829390 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | EL PATIO-1118 | 82921118 | TRANSFORMER | 315844229045 | 20230322 | 1120 | 20230323 | 1305 | 2062673 | 1545 | Transformer only | Unknown Cause | Patrol - found nothing | 5 | 7725 | 37.2889 | -121.9297 | No | Partly Cloudy-Drizzle;32-90 F |  |  | 23-0050647 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1829153 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | EL PATIO-1117 | 82921117 | JUMPER | 1 POLE E/O 26725 | 20230322 | 1242 | 20230322 | 1923 | 2062709 | 401 | Distribution Circuit | Equipment Failure/Involved | Overhead | 222 | 89022 | 37.2848 | -121.9581 | No | Overcast-Drizzle-Strong Winds;32-90 F | Jumper | Broken | 23-0050945 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829343 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | HICKS-1116 | 83431116 | FUSE | 33009 | 20230322 | 1555 | 20230322 | 1951 | 2063206 | 236 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 5664 | 37.2364 | -121.9464 | No | Partly Cloudy-Drizzle;32-90 F | Anchor or Guy | Broken | 23-0050862 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829281 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 30751 | 20230322 | 1555 | 20230323 | 1404 | 2063205 | 1329 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1329 | 37.1706 | -122.0516 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050983 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829373 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1102 | 82031102 | OCB | 1102/2 | 20230322 | 1600 | 20230322 | 2032 | 2063581 | 272 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4990 | 786407 | 37.3826 | -122.0698 | No | Clear;32-90 F |  |  | 23-0050977 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829368 | 0 | Non-EPSS | N | 2023 | A- B INST
DE ANZA | DE ANZA | MOUNTAIN VIEW-1104 | 82031104 | RECLOSER | 60076 | 20230322 | 1600 | 20230323 | 211 | 2063223 | 575 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 1282 | 369816 | 37.4021 | -122.0931 | No | Partly Cloudy-Drizzle;32-90 F | Pole-Wood | Burned/flashed | 23-0050877 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1829293 | 0 | Non-EPSS | N | 2023 | N/A
DE ANZA | DE ANZA | LOS GATOS-1101 | 82021101 | FUSE | 46285 | 20230322 | 1630 | 20230322 | 1637 | 2063323 | 7 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 42 | 37.2275 | -121.9726 | No | Partly Cloudy-Drizzle;32-90 F |  |  | 23-0050884 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829299 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 89897 | 20230322 | 1814 | 20230322 | 1956 | 2063601 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 476 | 37.1617 | -121.9142 | No | Overcast-Drizzle;32-90 F |  |  | 23-0051027 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829408 | 1 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | JUMPER | FLYING BELLS 1/P/W/O 23077 | 20230322 | 2310 | 20230324 | 1647 | 2063942 | 2497 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 2497 | 37.1171 | -122.0005 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051383 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | Yes | Yes | 1829638 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1104 | 82031104 | TRANSFORMER | 315386633517 | 20230323 | 706 | 20230323 | 1146 | 2064081 | 280 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 3920 | 37.4096 | -122.0895 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0051352 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829626 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 611205 | 20230323 | 1058 | 20230323 | 1637 | 2064505 | 339 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 4068 | 37.1087 | -121.8444 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0051315 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1829601 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | SWITCH | 32883 | 20230323 | 1204 | 20230324 | 1051 | 2064624 | 1367 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 41010 | 37.2544 | -122.0309 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0051525 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1829717 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1106 | 82241106 | RECLOSER | 60028 | 20230323 | 1254 | 20230323 | 1346 | 2064706 | 52 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 564 | 29328 | 37.397 | -122.1179 | No | Overcast;32-90 F |  |  | 23-0051400 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | No | No | 1829650 | 0 | Non-EPSS | N | 2023 | A-B-C PH
DE ANZA | DE ANZA | STELLING-1111 | 83481111 | RECLOSER | 60020 | 20230323 | 1356 | 20230325 | 1515 | 2064834 | 2959 | Distribution Circuit | Vegetation | Tree - fell into line | 373 | 449695 | 37.3393 | -122.0708 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051442 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1829671 | 0 | EPSS Ckt | N | 2023 | A & B
DE ANZA | DE ANZA | SARATOGA-1112 | 83371112 | FUSE | 3793 | 20230323 | 1616 | 20230323 | 1758 | 2064999 | 102 | Distribution Circuit | Equipment Failure/Involved | Overhead | 76 | 7752 | 37.2851 | -121.9993 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0051518 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1829713 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1110 | 82031110 | TRANSFORMER | 315483431831 | 20230323 | 1917 | 20230323 | 2226 | 2065305 | 189 | Transformer only | Equipment Failure/Involved | Overhead | 23 | 4347 | 37.3641 | -122.0543 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0051598 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1829760 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | EL PATIO-1113 | 82921113 | FUSE | 29189 | 20230323 | 2156 | 20230324 | 424 | 2065456 | 388 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 7760 | 37.2788 | -121.9392 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0051636 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1829788 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | HICKS-1109 | 83431109 | TRANSFORMER | 315813927851 | 20230324 | 849 | 20230324 | 1144 | 2065723 | 175 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 2625 | 37.2561 | -121.9394 | No | Partly Cloudy;32-90 F | Transformer | Broken | 23-0051740 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1829851 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | EL PATIO-1113 | 82921113 | FUSE | 17591 | 20230324 | 1320 | 20230324 | 2121 | 2066109 | 481 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 481 | 37.28 | -121.9399 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0051895 | UG | Sus | 35431720 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1829919 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | TRANSFORMER | T7916 | 20230324 | 1422 | 20230324 | 1943 | 2066209 | 321 | Transformer only | Vegetation | Tree - fell into line | 2 | 642 | 37.2401 | -121.9989 | No | Clear;32-90 F | Transformer | Broken | 23-0051934 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1829936 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 15069 | 20230324 | 1500 | 20230324 | 1621 | 2066238 | 81 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 1863 | 37.1038 | -121.8982 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0051951 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829942 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | HICKS-1116 | 83431116 | TRANSFORMER | 315815427191 | 20230324 | 1600 | 20230324 | 1941 | 2066329 | 221 | Transformer only | Vegetation | Tree - fell into line | 16 | 3536 | 37.238 | -121.9386 | No | Clear;32-90 F | Secondary | Bent or Twisted | 23-0051989 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1829963 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1108 | 83481108 | TRANSFORMER | 315484231243 | 20230324 | 1741 | 20230325 | 1253 | 2066494 | 1152 | Distribution Circuit | Vegetation | Tree - grew into line | 9 | 10368 | 37.3478 | -122.0538 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0052044 | OH | Sus | 35431719 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1830005 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1106 | 82241106 | TRANSFORMER | 315211832754 | 20230325 | 357 | 20230326 | 1831 | 2066715 | 2314 | Transformer only | Equipment Failure/Involved | Underground | 4 | 9256 | 37.388 | -122.1492 | No | Partly Cloudy;32-90 F | Secondary | Failed/Faulted | 23-0052444 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1830404 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1114 | 83371114 | FUSE | 8333 | 20230326 | 5 | 20230326 | 115 | 2067436 | 70 | Distribution Circuit | 3rd Party | Metallic Balloon | 40 | 2800 | 37.315 | -121.998 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0052620 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1830562 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1109 | 83371109 | FUSE | 2091 | 20230327 | 943 | 20230327 | 1125 | 2068465 | 102 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 3774 | 37.2806 | -121.9898 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0052857 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1830770 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | FUSE | 19875 | 20230327 | 1155 | 20230327 | 1345 | 2068676 | 110 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 550 | 37.2878 | -122.0911 | No | Clear;32-90 F |  |  | 23-0052979 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1830822 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | EL PATIO-1116 | 82921116 | TRANSFORMER | 315723629189 | 20230327 | 1217 | 20230327 | 1835 | 2068730 | 378 | Transformer only | Vegetation | Tree - fell into line | 12 | 4536 | 37.2924 | -121.9711 | No | Clear;32-90 F | Secondary | Broken | 23-0052957 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1830813 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MENLO-1103 | 24131103 | FUSE | 731 | 20230328 | 742 | 20230328 | 1613 | 2069588 | 511 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 1533 | 37.3692 | -122.1695 | No | Clear-Strong Winds;32-90 F |  |  | 23-0053771 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831296 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WOLFE-1113 | 83671113 | FUSE | 22941 | 20230328 | 744 | 20230328 | 934 | 2069582 | 110 | Distribution Circuit | Vegetation | Tree - bark fell into line | 105 | 11592 | 37.3604 | -122.0402 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0053290 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1831014 | 1 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1105 | 83371105 | FUSE | 4999 | 20230328 | 814 | 20230328 | 1152 | 2069670 | 218 | Distribution Circuit | Equipment Failure/Involved | Overhead | 72 | 15704 | 37.2674 | -122.0597 | No | Overcast;32-90 F | Conductor- Overhead | Together | 23-0053358 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831062 | 1 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 23009 | 20230328 | 828 | 20230328 | 1335 | 2069716 | 307 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 79 | 24253 | 37.1673 | -122.0363 | No | Clear-Strong Winds;32-90 F |  |  | 23-0053529 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831162 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | TRANSFORMER | 315579428534 | 20230328 | 849 | 20230328 | 1539 | 2069794 | 410 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 2050 | 37.2737 | -122.0202 | No | Overcast-Drizzle;32-90 F | Fuse | Broken | 23-0053761 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831290 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | EL PATIO-1117 | 82921117 | RECLOSER | LC36 | 20230328 | 913 | 20230328 | 1010 | 2069880 | 57 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4810 | 177711 | 37.2806 | -121.9508 | No | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0053328 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | No | No | 1831044 | 0 | Non-EPSS | N | 2023 | A-B-C PH
DE ANZA | DE ANZA | WOLFE-1109 | 83671109 | TRANSFORMER | 315569730619 | 20230328 | 917 | 20230328 | 1010 | 2069871 | 53 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 371 | 37.3312 | -122.0255 | No | Clear-Strong Winds;32-90 F | Secondary | Together | 23-0053322 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1831039 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | FUSE | 2055 | 20230328 | 930 | 20230328 | 1807 | 2069976 | 517 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 3102 | 37.3543 | -122.1587 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Together | 23-0053855 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1831350 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | OTHER | WIRE DOWN 1/S/SS/O FU 6711 | 20230328 | 1000 | 20230328 | 2350 | 2070076 | 830 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 20885 | 37.3518 | -122.1354 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0053571 | OH | Sus | 35434207 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | Yes | 1831189 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1106 | 82241106 | FUSE | 30351 | 20230328 | 1004 | 20230328 | 1518 | 2070091 | 314 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1884 | 37.3927 | -122.1479 | No | Overcast-Drizzle;32-90 F |  |  | 23-0053735 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831278 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1104 | 83371104 | FUSE | 3243 | 20230328 | 1034 | 20230328 | 1803 | 2070193 | 449 | Distribution Circuit | Vegetation | Tree - grew into line | 24 | 10776 | 37.2485 | -121.9965 | No | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Contaminated | 23-0053785 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1831302 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1105 | 83371105 | FUSE | 4999 | 20230328 | 1315 | 20230328 | 1737 | 2071284 | 262 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 108 | 28296 | 37.2674 | -122.0597 | No | Overcast-Rain;32-90 F |  |  | 23-0053837 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1831341 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | HICKS-1115 | 83431115 | SWITCH | 7595 | 20230328 | 2217 | 20230329 | 154 | 2072151 | 217 | Distribution Circuit | Vegetation | Tree - grew into line | 27 | 5859 | 37.2393 | -121.9308 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0053847 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1831442 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | JUMPER | WIRE DOWN @ LD SIDE OF CGC# 8233 | 20230329 | 745 | 20230329 | 2036 | 2072389 | 771 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 2854 | 37.2823 | -122.1205 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken | 23-0054162 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1831546 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | SWITCH | 31215 | 20230329 | 943 | 20230329 | 1847 | 2072641 | 544 | Distribution Circuit | Equipment Failure/Involved | Overhead | 239 | 17765 | 37.2211 | -121.9734 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken | 23-0054015 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1831544 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | TRANSFORMER | 315390326689 | 20230329 | 1329 | 20230330 | 242 | 2073121 | 793 | Distribution Circuit | Environmental/External | Lightning | 1 | 793 | 37.2222 | -122.085 | No | Clear-Strong Winds;32-90 F | Transformer (OH) | Failed/Faulted | 23-0054623 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831726 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 32625 | 20230329 | 1341 | 20230329 | 1925 | 2073151 | 344 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 1032 | 37.1666 | -122.0263 | No | Overcast-Drizzle;32-90 F |  |  | 23-0054641 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1831744 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 3173 | 20230329 | 1343 | 20230329 | 1920 | 2073168 | 337 | Distribution Circuit | Environmental/External | Lightning | 19 | 6403 | 37.1706 | -121.9422 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0054616 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1831720 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-0403 | 82160403 | TRANSFORMER | 315379032118 | 20230329 | 1614 | 20230330 | 222 | 2073673 | 608 | Transformer only | Vegetation | Tree - fell into line | 5 | 3040 | 37.3715 | -122.0911 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0054648 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831748 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1106 | 83671106 | TRANSFORMER | 315604331134 | 20230329 | 1812 | 20230330 | 137 | 2073580 | 445 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 3115 | 37.3454 | -122.0137 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0054644 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831746 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | TRANSFORMER | 315771522778 | 20230329 | 1840 | 20230329 | 1904 | 2073552 | 24 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 48 | 37.1167 | -121.9506 | No | Overcast-Drizzle;32-90 F | Fuse | Failed/Faulted | 23-0054634 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831734 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1101 | 82021101 | SWITCH | 3525 | 20230329 | 1858 | 20230329 | 1906 | 2073652 | 8 | Distribution Circuit | Equipment Failure/Involved | Overhead | 213 | 1704 | 37.2172 | -121.9661 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0054015 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1831739 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | TRANSFORMER | 315731324528 | 20230329 | 2024 | 20230405 | 1750 | 2073709 | 9926 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 9926 | 37.1648 | -121.9679 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0054676 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831766 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | TRANSFORMER | 315553024570 | 20230330 | 547 | 20230331 | 950 | 2073853 | 1683 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1683 | 37.1653 | -122.027 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0055449 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1832190 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1111 | 82031111 | FUSE | 22739 | 20230330 | 751 | 20230330 | 1123 | 2073952 | 212 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 80 | 16960 | 37.3834 | -122.0612 | No | Clear;32-90 F |  |  | 23-0054920 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831932 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1111 | 82031111 | INTERRUPTER | 694226 | 20230330 | 807 | 20230330 | 2032 | 2073968 | 745 | Distribution Circuit | Equipment Failure/Involved | Underground | 213 | 158685 | 37.386 | -122.0538 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0055012 | UG | Sus | 45712068 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831967 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1102 | 82021102 | TRANSFORMER | T50729 | 20230330 | 912 | 20230330 | 1242 | 2074448 | 210 | Transformer only | Unknown Cause | Patrol - found nothing | 38 | 7980 | 37.2314 | -121.9732 | No | Clear;32-90 F |  |  | 23-0055008 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831965 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | TRANSFORMER | 315770122908 | 20230330 | 1431 | 20230331 | 155 | 2074560 | 684 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 3420 | 37.1222 | -121.9511 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0055205 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1832014 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WOLFE-1109 | 83671109 | FUSE | 26147 | 20230330 | 1518 | 20230331 | 1753 | 2074607 | 1595 | Distribution Circuit | Equipment Failure/Involved | Overhead | 117 | 37687 | 37.3285 | -122.0233 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0055216 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1832018 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1111 | 82031111 | SWITCH | 444122 | 20230331 | 231 | 20230331 | 238 | 2075017 | 7 | Distribution Circuit | Company Initiated | Return Circuit Normal | 211 | 1477 | 37.3851 | -122.0549 | No | Partly Cloudy;32-90 F | Conductor- Underground | Normal | 23-0055012 | UG | Sus | 45712068 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1832100 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | BRITTON-1107 | 83611107 | RECLOSER | LV66 | 20230331 | 903 | 20230331 | 917 | 2075114 | 14 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 378 | 37.3712 | -121.9941 | No | Partly Cloudy;32-90 F | Jumper | Arcing | 23-0055416 | OH | Sus | 45712894 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1832170 | 0 | Non-EPSS | N | 2023 | N/A
DE ANZA | DE ANZA | WOLFE-1109 | 83671109 | FUSE | 26141 | 20230331 | 1303 | 20230331 | 1527 | 2075486 | 144 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 2016 | 37.3317 | -122.0234 | No | Partly Cloudy;32-90 F |  |  | 23-0055639 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1832250 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 17943 | 20230331 | 1346 | 20230401 | 700 | 2075533 | 1034 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 8683 | 37.1375 | -121.9883 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0055619 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1832241 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | FUSE | 32597 | 20230401 | 1642 | 20230401 | 1901 | 2076865 | 139 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 2085 | 37.3627 | -122.1117 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0055895 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1832490 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1103 | 83371103 | TRANSFORMER | 315516528229 | 20230401 | 1733 | 20230402 | 1938 | 2076890 | 1565 | Transformer only | Equipment Failure/Involved | Underground | 4 | 6260 | 37.2648 | -122.0417 | No | Partly Cloudy;32-90 F | Connector or Splice (UG) | Deteriorated | 23-0056039 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1832632 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WOLFE-1113 | 83671113 | FUSE | 31905 | 20230402 | 1016 | 20230402 | 1145 | 2077358 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 49 | 4361 | 37.3606 | -122.0401 | No | Partly Cloudy;32-90 F |  |  | 23-0056023 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1832618 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | BRITTON-1110 | 83611110 | FUSE | 18419 | 20230402 | 1634 | 20230402 | 1758 | 2077576 | 84 | Distribution Circuit | Vegetation | Tree - branch fell on line | 321 | 26964 | 37.367 | -122.0206 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0056055 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1832647 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 611205 | 20230402 | 2030 | 20230403 | 124 | 2077661 | 294 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 53 | 15582 | 37.1087 | -121.8444 | No | Clear;32-90 F |  |  | 23-0056092 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1832684 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 611205 | 20230403 | 150 | 20230403 | 1432 | 2078034 | 762 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 48 | 36576 | 37.1087 | -121.8444 | No | Clear;32-90 F |  |  | 23-0056444 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1832896 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1105 | 83371105 | TRANSFORMER | 315559128854 | 20230403 | 756 | 20230403 | 919 | 2077818 | 83 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 996 | 37.2823 | -122.0275 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0056167 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1832717 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 611205 | 20230403 | 1602 | 20230404 | 240 | 2078860 | 638 | Distribution Circuit | Equipment Failure/Involved | Overhead | 53 | 33814 | 37.1087 | -121.8444 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0056590 | OH | Sus | 45715106 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1832987 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | JUMPER | OJ 1 S/W/O CGC 315670523325 | 20230404 | 902 | 20230404 | 1145 | 2079797 | 163 | Distribution Circuit | Vegetation | Tree - grew into line | 1 | 163 | 37.1306 | -121.9871 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0056852 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1833204 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | HICKS-1115 | 83431115 | FUSE | 29393 | 20230404 | 1132 | 20230404 | 1148 | 2079922 | 16 | Distribution Circuit | 3rd Party | Kite | 28 | 448 | 37.2476 | -121.9254 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0056955 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1833228 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WHISMAN-1104 | 83631104 | TRANSFORMER | MTR#1006732069 | 20230405 | 905 | 20230405 | 1419 | 2080707 | 314 | Transformer only | 3rd Party | Other | 1 | 314 | 37.4168 | -122.0793 | No | Clear;32-90 F | Transformer | Normal | 23-0057383 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | None | 0 | No | No | No | 1833481 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | SWITCH | LB48 | 20230405 | 2035 | 20230406 | 702 | 2080960 | 627 | Distribution Circuit | Vegetation | Tree - fell into line | 260 | 52080 | 37.19 | -121.9942 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0057662 | OH | Sus | 45716610 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1833568 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | RECLOSER | 568350 | 20230406 | 1308 | 20230406 | 1622 | 2081843 | 194 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 465 | 55323 | 37.3221 | -122.0795 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0058005 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1833819 | 0 | EPSS Ckt | N | 2023 | A- B- C & 51
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | FUSE | 1639 | 20230406 | 1804 | 20230406 | 2059 | 2082084 | 175 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 2726 | 37.3467 | -122.11 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0058174 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1833862 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | HICKS-1116 | 83431116 | RECLOSER | 647210 | 20230407 | 56 | 20230407 | 147 | 2082233 | 51 | Distribution Circuit | Equipment Failure/Involved | Overhead | 501 | 25551 | 37.2383 | -121.9431 | No | Overcast;32-90 F | Recloser | Failed/Faulted | 23-0058278 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1833966 | 0 | EPSS Ckt | N | 2023 | C PH POLE FAILURE
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | JUMPER | FUSE 2977 | 20230407 | 1628 | 20230410 | 230 | 2082768 | 3482 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 24374 | 37.1028 | -121.924 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0058663 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1834115 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | INTERRUPTER | 444636 | 20230408 | 724 | 20230408 | 842 | 2083056 | 78 | Distribution Circuit | Animal | Squirrel | 31 | 2418 | 37.3735 | -122.115 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0058745 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1834193 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | HICKS-1114 | 83431114 | TRANSFORMER | 315832427487 | 20230408 | 1543 | 20230408 | 1716 | 2083335 | 93 | Transformer only | Vegetation | Tree - cutting- PG&E contractor | 11 | 1023 | 37.2462 | -121.9329 | No | Partly Cloudy;32-90 F | Secondary | Normal | 23-0058795 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1834248 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1103 | 83771103 | FUSE | 2613 | 20230409 | 1050 | 20230409 | 1132 | 2083647 | 42 | Distribution Circuit | Animal | Squirrel | 1 | 42 | 37.2645 | -121.9849 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0058869 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1834318 | 1 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | FUSE | 2243 | 20230410 | 352 | 20230411 | 259 | 2084001 | 1387 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 26932 | 37.2777 | -122.1116 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0059081 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Multi-Fault | 0 | No | Yes | No | 1834541 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | OCB | 1107/2 | 20230410 | 549 | 20230410 | 738 | 2084020 | 109 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2314 | 127426 | 37.2264 | -121.9771 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0058933 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1834387 | 0 | EPSS Ckt | N | 2023 | AB INST
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | TRANSFORMER | 315585624580 | 20230410 | 1115 | 20230412 | 1332 | 2084429 | 3017 | Transformer only | Environmental/External | Lightning | 1 | 3017 | 37.1655 | -122.0161 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0059255 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1834621 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1104 | 83771104 | FUSE | 11417 | 20230411 | 228 | 20230412 | 602 | 2084988 | 1654 | Distribution Circuit | Equipment Failure/Involved | Underground | 15 | 10670 | 37.2653 | -121.9553 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 23-0059385 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1834695 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | FUSE | 26059 | 20230411 | 1051 | 20230411 | 1253 | 2085421 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 3172 | 37.2391 | -122.0128 | No | Overcast;32-90 F |  |  | 23-0059579 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1834891 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MENLO-1103 | 24131103 | SWITCH | SL05 | 20230411 | 1420 | 20230411 | 1842 | 2086004 | 262 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 5240 | 37.365 | -122.1673 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0059231 | OH | Sus | 31641708 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1834964 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | RECLOSER | 60122 | 20230411 | 1751 | 20230411 | 1947 | 2085912 | 116 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 455 | 52780 | 37.1462 | -121.9823 | No | Partly Cloudy;32-90 F |  |  | 23-0059789 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Three Phase Fault | 0 | No | No | No | 1834950 | 0 | EPSS Ckt | N | 2023 | A-B-C-GRD
DE ANZA | DE ANZA | MOUNTAIN VIEW-1107 | 82031107 | TRANSFORMER | 315391532210 | 20230412 | 730 | 20230414 | 611 | 2086440 | 2801 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 2801 | 37.3746 | -122.0869 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0060168 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1835233 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1102 | 83771102 | TRANSFORMER | T9116 | 20230412 | 1731 | 20230413 | 1515 | 2087013 | 1304 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 1304 | 37.2377 | -121.9613 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0060387 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1835303 | 1 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | FUSE | 957387 | 20230412 | 2031 | 20230412 | 2354 | 2087114 | 203 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 4872 | 37.1322 | -121.9999 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0060393 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1835308 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1111 | 83481111 | FUSE | 1669 | 20230413 | 606 | 20230413 | 742 | 2087233 | 93 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 89 | 8250 | 37.3446 | -122.0851 | No | Clear;32-90 F |  |  | 23-0060499 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1835383 | 1 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | RECLOSER | 60122 | 20230413 | 1930 | 20230413 | 1938 | 2088028 | 8 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 455 | 3640 | 37.1462 | -121.9823 | No | Clear;32-90 F |  |  | 23-0060884 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1835627 | 0 | EPSS Ckt | N | 2023 | A-C-GRD
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 21101 | 20230414 | 850 | 20230414 | 1517 | 2088398 | 387 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 5805 | 37.1336 | -121.9651 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0061033 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1835784 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | FUSE | 33133 | 20230415 | 2053 | 20230415 | 2203 | 2089439 | 70 | Distribution Circuit | Vegetation | Tree - branch fell on line | 150 | 10500 | 37.3485 | -122.1101 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0061397 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Three Phase Fault | 0 | No | No | No | 1836085 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | FUSE | 30106 | 20230416 | 326 | 20230416 | 919 | 2089508 | 353 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 36 | 12708 | 37.2556 | -122.0368 | No | Partly Cloudy;32-90 F |  |  | 23-0061440 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1836144 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | SWITCH | 11299 | 20230416 | 950 | 20230417 | 1420 | 2089620 | 1710 | Distribution Circuit | Equipment Failure/Involved | Underground | 3 | 5130 | 37.2535 | -122.0387 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0061453 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1836157 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WOLFE-1105 | 83671105 | JUMPER | 1833 OPEN MIDDLE PHASE JUMPER | 20230417 | 849 | 20230418 | 315 | 2090138 | 1106 | Distribution Circuit | Equipment Failure/Involved | Overhead | 586 | 231316 | 37.3222 | -122.012 | No | Clear;32-90 F | Jumper | Burned Open | 23-0061744 | OH | Sus | 45733021 | SOUTH BAY AND CENTRAL COAST | APR | Open Circuit | 0 | No | No | No | 1836465 | 1 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1111 | 83421111 | FUSE | 11435 | 20230417 | 1814 | 20230418 | 847 | 2090832 | 873 | Distribution Circuit | Equipment Failure/Involved | Underground | 116 | 96308 | 37.3908 | -121.9935 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0061827 | UG | Sus | 45733475 | SOUTH BAY AND CENTRAL COAST | APR | Multi-Fault | 0 | No | No | No | 1836507 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1108 | 83371108 | FUSE | 983 | 20230418 | 2135 | 20230419 | 106 | 2091902 | 211 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 63 | 13293 | 37.2866 | -121.9947 | No | Clear;32-90 F | Fuse | Normal | 23-0062253 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1836809 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1113 | 83481113 | TRANSFORMER | 315472831463 | 20230419 | 1538 | 20230420 | 102 | 2092619 | 564 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 5076 | 37.3539 | -122.0577 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0062649 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1837075 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1112 | 83371112 | FUSE | 3769 | 20230419 | 2057 | 20230420 | 333 | 2092826 | 396 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 204 | 80784 | 37.2864 | -121.998 | No | Clear;32-90 F | Fuse | Normal | 23-0062719 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1837101 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1101 | 82021101 | JUMPER | OJ @ 17165 PINE AVE | 20230419 | 2313 | 20230420 | 522 | 2092851 | 369 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 738 | 37.2299 | -121.9702 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 23-0062748 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1837123 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1113 | 83371113 | FUSE | 30743 | 20230419 | 2313 | 20230420 | 48 | 2092849 | 95 | Distribution Circuit | Equipment Failure/Involved | Overhead | 89 | 8455 | 37.3094 | -122.0174 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0062746 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1837121 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1114 | 83671114 | FUSE | 17147 | 20230420 | 1833 | 20230421 | 249 | 2093381 | 479 | Distribution Circuit | Equipment Failure/Involved | Overhead | 287 | 106904 | 37.3614 | -122.0315 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0063217 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1837306 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | HICKS-1109 | 83431109 | FUSE | 677 | 20230421 | 912 | 20230421 | 949 | 2093632 | 37 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 814 | 37.2606 | -121.9379 | No | Clear;32-90 F | Conductor- Overhead | Annealed | 23-0063354 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1837440 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1108 | 83421108 | FUSE | 657 | 20230421 | 1223 | 20230422 | 1732 | 2093968 | 1749 | Distribution Circuit | 3rd Party | Vehicle | 1 | 1749 | 37.3972 | -122.0185 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0063543 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Three Phase Fault | 0 | No | No | No | 1837567 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1111 | 83481111 | FUSE | 49655 | 20230422 | 631 | 20230422 | 823 | 2094424 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 1792 | 37.3394 | -122.101 | No | Clear;32-90 F |  |  | 23-0063725 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1837700 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | FUSE | 19449 | 20230422 | 935 | 20230422 | 2344 | 2094457 | 849 | Distribution Circuit | Equipment Failure/Involved | Overhead | 249 | 24047 | 37.3228 | -122.0638 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0063738 | OH | Sus | 45738604 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1837759 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1108 | 83421108 | INTERRUPTER | 77386 | 20230423 | 326 | 20230424 | 1542 | 2094895 | 1722 | Distribution Circuit | Equipment Failure/Involved | Underground | 463 | 169889 | 37.3974 | -122.0127 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0063817 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1837845 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | TRANSFORMER | 315752826343 | 20230423 | 612 | 20230423 | 940 | 2094915 | 208 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 416 | 37.2142 | -121.96 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0063827 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1837860 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | EL PATIO-1116 | 82921116 | FUSE | 26209 | 20230423 | 1826 | 20230423 | 1905 | 2095146 | 39 | Distribution Circuit | 3rd Party | Metallic Balloon | 195 | 7605 | 37.2936 | -121.9676 | No | Clear;32-90 F | Conductor- Overhead | Arcing | 23-0063876 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1837899 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1102 | 83421102 | SWITCH | 13644 | 20230424 | 1610 | 20230424 | 1622 | 2095952 | 12 | Distribution Circuit | Company Initiated | Return Circuit Normal | 48 | 576 | 37.3998 | -122.0117 | No | Clear;32-90 F | Conductor- Underground | Normal | 23-0063817 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | None | 0 | No | No | No | 1838187 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1111 | 83371111 | FUSE | 29953 | 20230424 | 1705 | 20230425 | 317 | 2095976 | 612 | Distribution Circuit | Equipment Failure/Involved | Underground | 17 | 10404 | 37.2868 | -121.9781 | No | Clear;32-90 F | Elbow | Broken | 23-0064244 | UG | Sus | 45739865 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1838195 | 1 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | RECLOSER | LL64 | 20230424 | 1722 | 20230424 | 1804 | 2095985 | 42 | Distribution Circuit | Equipment Failure/Involved | Overhead | 247 | 10374 | 37.3773 | -122.1529 | No | Clear;32-90 F | Insulator | Broken | 23-0064234 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1838191 | 0 | EPSS Ckt | N | 2023 | N/A
DE ANZA | DE ANZA | STELLING-1111 | 83481111 | TRANSFORMER | 315453030879 | 20230425 | 1036 | 20230425 | 2225 | 2096555 | 709 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 1418 | 37.3376 | -122.0648 | No | Clear;32-90 F | Transformer | Broken- wire on object | 23-0064483 | OH | Sus | 45740249 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1838419 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | TRANSFORMER | 315356029040 | 20230425 | 1037 | 20230425 | 1820 | 2096328 | 463 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 463 | 37.2871 | -122.1012 | No | Clear;32-90 F |  |  | 23-0064479 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1838415 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1113 | 83421113 | TRANSFORMER | 315572832935 | 20230425 | 2348 | 20230426 | 150 | 2097111 | 122 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 1830 | 37.395 | -122.0249 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0064743 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1838544 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1112 | 83421112 | TRANSFORMER | 315585632790 | 20230426 | 1413 | 20230426 | 1740 | 2097661 | 207 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 828 | 37.391 | -122.0205 | No | Clear;32-90 F |  |  | 23-0065081 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1838773 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MENLO-1103 | 24131103 | FUSE | 1117 | 20230426 | 1607 | 20230426 | 1810 | 2097748 | 123 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 2091 | 37.3935 | -122.1625 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0065150 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1838792 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1111 | 83481111 | FUSE | 17791 | 20230427 | 17 | 20230427 | 1300 | 2098012 | 763 | Distribution Circuit | Equipment Failure/Involved | Underground | 17 | 12971 | 37.3371 | -122.0573 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0065270 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1838842 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-0403 | 82160403 | TRANSFORMER | 315386032191 | 20230427 | 1509 | 20230428 | 300 | 2098616 | 711 | Transformer only | Unknown Cause | Patrol - found nothing | 8 | 5688 | 37.3738 | -122.088 | No | Clear;32-90 F |  |  | 23-0065727 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1839088 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1105 | 83371105 | TRANSFORMER | T56456 | 20230427 | 1725 | 20230427 | 1938 | 2098812 | 133 | Transformer only | Equipment Failure/Involved | Underground | 1 | 133 | 37.2818 | -122.0374 | No | Clear;32-90 F | Fuse | Burned Open | 23-0065750 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1839108 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1112 | 83421112 | TRANSFORMER | 315586532714 | 20230427 | 1840 | 20230427 | 2110 | 2098747 | 150 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 1950 | 37.3889 | -122.0202 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0065721 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1839083 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1102 | 83771102 | FUSE | 22505 | 20230428 | 557 | 20230428 | 1602 | 2099045 | 605 | Distribution Circuit | Equipment Failure/Involved | Overhead | 123 | 53445 | 37.2373 | -121.9779 | No | Clear;32-90 F | Jumper | Burned Open | 23-0065897 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1839219 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | TRANSFORMER | 316106422575 | 20230428 | 1518 | 20230428 | 2202 | 2099529 | 404 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 808 | 37.1127 | -121.8363 | No | Clear;32-90 F | Jumper | Burned Open | 23-0066167 | OH | Sus | 45745005 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1839376 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | EL PATIO-1119 | 82921119 | FUSE | 6541 | 20230429 | 328 | 20230429 | 1858 | 2099791 | 930 | Distribution Circuit | Vegetation | Tree - branch fell on line | 38 | 35340 | 37.285 | -121.9312 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0066224 | OH | Sus | 31643533 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | Yes | No | 1839424 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | HICKS-1116 | 83431116 | FUSE | 31053 | 20230429 | 1205 | 20230429 | 1501 | 2100064 | 176 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 704 | 37.2185 | -121.932 | No | Clear;32-90 F |  |  | 23-0066307 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1839529 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA SUB | 8216 | OCB | 401/2 | 20230429 | 2159 | 20230429 | 2257 | 2100302 | 58 | Distribution Circuit | 3rd Party | Vehicle | 869 | 50402 | 37.361 | -122.0993 | No | Partly Cloudy;32-90 F | Pole-Wood | Normal | 23-0066351 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1839568 | 0 | Non-EPSS | N | 2023 | N/A
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 2903 | 20230430 | 2347 | 20230501 | 1309 | 2101002 | 802 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 11228 | 37.1145 | -121.9385 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0066508 | OH | Sus | 45745415 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1839717 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | FUSE | 22529 | 20230501 | 210 | 20230501 | 1911 | 2101032 | 1021 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 26378 | 37.2399 | -122.0211 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0066527 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | Yes | 1839737 | 1 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1112 | 83371112 | TRANSFORMER | 315699729125 | 20230501 | 1022 | 20230501 | 1229 | 2101439 | 127 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 1524 | 37.2904 | -121.9793 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 23-0066622 | OH | Sus | 31643685 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1839871 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1110 | 83371110 | FUSE | 3255 | 20230501 | 1508 | 20230501 | 1614 | 2101750 | 66 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 132 | 37.2919 | -121.9952 | No | Clear;32-90 F |  |  | 23-0066812 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1839953 | 1 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1106 | 82241106 | SWITCH | 33309 | 20230501 | 2029 | 20230502 | 316 | 2101978 | 407 | Distribution Circuit | Vegetation | Tree - grew into line | 34 | 13838 | 37.3755 | -122.1456 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0066841 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1839971 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1113 | 83481113 | TRANSFORMER | 315510931273 | 20230502 | 855 | 20230502 | 1011 | 2102529 | 76 | Transformer only | Vegetation | Tree - grew into line | 8 | 608 | 37.3486 | -122.0454 | No | Overcast-Drizzle;32-90 F | Secondary | Burned Open | 23-0066976 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1840098 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | EL PATIO-1118 | 82921118 | FUSE | 8713 | 20230502 | 2021 | 20230503 | 424 | 2103234 | 483 | Distribution Circuit | Equipment Failure/Involved | Overhead | 324 | 55339 | 37.2738 | -121.9272 | No | Overcast;32-90 F | Conductor- Overhead | Broken | 23-0067386 | OH | Sus | 31643739 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1840288 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1114 | 82031114 | TRANSFORMER | C140 | 20230502 | 2056 | 20230503 | 202 | 2103240 | 306 | Transformer only | Equipment Failure/Involved | Underground | 22 | 6732 | 37.3678 | -122.0763 | No | Overcast;32-90 F | Transformer (UG) | Failed/Faulted | 23-0067387 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1840289 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1111 | 83481111 | TRANSFORMER | 315428530820 | 20230503 | 1802 | 20230504 | 333 | 2104028 | 571 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 2855 | 37.3361 | -122.0733 | No | Overcast-Drizzle;32-90 F | Connector or Splice (OH) | Burned/flashed | 23-0067845 | OH | Sus | 31644102 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1840583 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1104 | 82031104 | RECLOSER | LM26 | 20230503 | 1829 | 20230504 | 548 | 2104102 | 555 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3687 | 638731 | 37.3999 | -122.0883 | No | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Contaminated | 23-0067849 | OH | Sus | 45748252 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1840585 | 0 | Non-EPSS | N | 2023 | A & C
DE ANZA | DE ANZA | LOS GATOS-1102 | 82021102 | FUSE | 4029 | 20230504 | 1141 | 20230504 | 1234 | 2104728 | 53 | Distribution Circuit | Animal | Squirrel | 14 | 742 | 37.2328 | -121.9749 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Normal | 23-0068199 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1840856 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1104 | 82241104 | FUSE | 30479 | 20230505 | 2311 | 20230506 | 803 | 2105873 | 532 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 6384 | 37.3856 | -122.1207 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 23-0069098 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1841272 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1104 | 83481104 | FUSE | 461 | 20230506 | 825 | 20230506 | 954 | 2106010 | 89 | Distribution Circuit | Vegetation | Tree - branch fell on line | 191 | 16999 | 37.3048 | -122.0416 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0069139 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1841337 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1108 | 83371108 | FUSE | 993 | 20230506 | 854 | 20230506 | 1321 | 2106027 | 267 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 9439 | 37.281 | -121.9942 | No | Clear;32-90 F |  |  | 23-0069174 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1841375 | 1 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | FUSE | 2583 | 20230506 | 1145 | 20230506 | 1332 | 2106139 | 107 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 107 | 37.248 | -122.0673 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0069148 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1841349 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | TRANSFORMER | 315259831667 | 20230506 | 2120 | 20230508 | 134 | 2106468 | 1694 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 3388 | 37.358 | -122.1304 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Arcing | 23-0069250 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1841438 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | OTHER | WIRE DOWN AT 7237 | 20230507 | 713 | 20230508 | 439 | s1841483 | 1286 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2974 | 142110 | 37.3575 | -122.1317 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 23-0069286 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | Yes | 1841483 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1115 | 83371115 | FUSE | 8965 | 20230507 | 1819 | 20230508 | 446 | 2106897 | 627 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 7601 | 37.287 | -122.0507 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0069321 | OH | Sus | 31644526 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1841514 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 30193 | 20230508 | 1238 | 20230508 | 1318 | 2107565 | 40 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 120 | 37.1124 | -121.9344 | No | Partly Cloudy;32-90 F |  |  | 23-0069559 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1841732 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | RECLOSER | 60122 | 20230509 | 752 | 20230509 | 834 | 2108293 | 42 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 455 | 19110 | 37.1462 | -121.9823 | No | Overcast;32-90 F |  |  | 23-0069817 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Multi-Fault | 0 | No | No | No | 1841855 | 0 | EPSS Ckt | N | 2023 | A- B- C- GRD
DE ANZA | DE ANZA | MOUNTAIN VIEW-1108 | 82031108 | FUSE | 19657 | 20230509 | 1956 | 20230509 | 2107 | 2108693 | 71 | Distribution Circuit | Equipment Failure/Involved | Overhead | 527 | 37417 | 37.3788 | -122.0457 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0070165 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1842078 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1110 | 83421110 | FUSE | 32453 | 20230509 | 2327 | 20230510 | 53 | 2109058 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 516 | 37.4109 | -121.9869 | No | Partly Cloudy;32-90 F |  |  | 23-0070238 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1842128 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1111 | 83421111 | FUSE | 29869 | 20230510 | 853 | 20230510 | 1017 | 2109255 | 84 | Distribution Circuit | Equipment Failure/Involved | Overhead | 135 | 11340 | 37.3946 | -122.004 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 23-0070323 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1842226 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1102 | 83771102 | FUSE | 17911 | 20230511 | 122 | 20230511 | 1157 | 2109870 | 635 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 18415 | 37.247 | -121.972 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0070706 | OH | Sus | 31645012 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1842406 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WOLFE-1105 | 83671105 | RECLOSER | LC34 | 20230511 | 526 | 20230511 | 538 | 2109904 | 12 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 437 | 5244 | 37.3202 | -122.0139 | No | Partly Cloudy;32-90 F |  |  | 23-0070712 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1842410 | 0 | Non-EPSS | N | 2023 | C PHASE
DE ANZA | DE ANZA | VASONA-1103 | 83771103 | FUSE | 31355 | 20230511 | 541 | 20230511 | 738 | 2110019 | 117 | Distribution Circuit | Vegetation | Tree - branch fell on line | 109 | 11269 | 37.2627 | -121.9829 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 23-0070731 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1842421 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1104 | 83371104 | FUSE | 30201 | 20230511 | 718 | 20230511 | 1034 | 2110033 | 196 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 5488 | 37.2462 | -121.9972 | No | Partly Cloudy;32-90 F |  |  | 23-0070774 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1842472 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1101 | 82021101 | TRANSFORMER | 315761626855 | 20230511 | 856 | 20230512 | 616 | 2110083 | 1280 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 8960 | 37.2284 | -121.9568 | No | Partly Cloudy;32-90 F | Transformer | Broken- wire on ground | 23-0070804 | OH | Sus | 45759139 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | Yes | No | 1842516 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 457881 | 20230511 | 1454 | 20230511 | 2220 | 2110585 | 446 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 2230 | 37.1932 | -122.0203 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0071093 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1842636 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WOLFE-1105 | 83671105 | RECLOSER | LC34 | 20230512 | 854 | 20230512 | 908 | 2111043 | 14 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 437 | 6118 | 37.3202 | -122.0139 | No | Partly Cloudy;32-90 F |  |  | 23-0071276 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1842817 | 0 | Non-EPSS | N | 2023 | C PH
DE ANZA | DE ANZA | LOS ALTOS-1103 | 82241103 | FUSE | 4683 | 20230512 | 1506 | 20230512 | 1947 | 2111386 | 281 | Distribution Circuit | Equipment Failure/Involved | Overhead | 94 | 10478 | 37.3887 | -122.102 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0071458 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1842920 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1105 | 83671105 | RECLOSER | LC34 | 20230512 | 1804 | 20230512 | 1811 | 2111481 | 7 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 437 | 3059 | 37.3202 | -122.0139 | No | Clear;32-90 F |  |  | 23-0071496 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1842933 | 0 | Non-EPSS | N | 2023 | C
DE ANZA | DE ANZA | WOLFE-1105 | 83671105 | RECLOSER | LC34 | 20230512 | 2303 | 20230512 | 2345 | s1842969 | 42 | Distribution Circuit | Equipment Failure/Involved | Overhead | 437 | 18354 | 37.3202 | -122.0139 | No | Clear;32-90 F | Recloser | Malfunctioning | 23-0071529 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1842969 | 0 | Non-EPSS | N | 2023 | C PHASE
DE ANZA | DE ANZA | SARATOGA-1108 | 83371108 | FUSE | 3561 | 20230513 | 220 | 20230513 | 1353 | 2111605 | 693 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 11088 | 37.2869 | -121.9573 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0071533 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1842972 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | FUSE | 9327 | 20230513 | 814 | 20230514 | 1123 | 2111640 | 1629 | Distribution Circuit | Vegetation | Tree - grew into line | 15 | 2889 | 37.2467 | -122.0261 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0071543 | OH | Sus | 35446580 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1843002 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | BRITTON-1107 | 83611107 | FUSE | 11517 | 20230514 | 1034 | 20230514 | 1243 | 2112129 | 129 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 83 | 10707 | 37.366 | -121.9964 | No | Clear;32-90 F |  |  | 23-0071670 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1843114 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1110 | 83421110 | SWITCH | 10301 | 20230514 | 1611 | 20230514 | 1927 | 2112225 | 196 | Distribution Circuit | Equipment Failure/Involved | Overhead | 59 | 11564 | 37.3997 | -121.9962 | No | Clear;32-90 F | Switch (OH) | Burned/flashed | 23-0071630 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1843124 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1113 | 83481113 | TRANSFORMER | 315470031602 | 20230514 | 1832 | 20230515 | 147 | 2112292 | 435 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 2694 | 37.3578 | -122.0587 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0071695 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1843143 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1112 | 83371112 | TRANSFORMER | 315638929093 | 20230514 | 1841 | 20230515 | 559 | 2112275 | 678 | Transformer only | Vegetation | Tree - branch fell on line | 8 | 5424 | 37.2893 | -122 | No | Clear;32-90 F | Transformer | Normal | 23-0071690 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1843137 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | TRANSFORMER | 315552827854 | 20230514 | 2220 | 20230516 | 502 | 2112379 | 1842 | Transformer only | Vegetation | Tree - branch fell on line | 5 | 9210 | 37.2548 | -122.029 | No | Partly Cloudy;32-90 F | Transformer | Broken- wire on ground | 23-0071719 | OH | Sus | 45761763 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | Yes | No | 1843169 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WOLFE-1106 | 83671106 | FUSE | 18339 | 20230515 | 1024 | 20230515 | 1041 | 2112935 | 17 | Distribution Circuit | 3rd Party | Vandalism | 1 | 17 | 37.3462 | -122.0054 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 23-0071827 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1843282 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1104 | 83421104 | TRANSFORMER | 315668933226 | 20230515 | 1314 | 20230516 | 53 | 2113085 | 699 | Transformer only | Equipment Failure/Involved | Electrical Overload | 5 | 3495 | 37.4046 | -121.9926 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0071970 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1843352 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1102 | 83771102 | FUSE | 32049 | 20230515 | 2312 | 20230516 | 200 | 2113610 | 168 | Distribution Circuit | Vegetation | Tree - grew into line | 15 | 2520 | 37.2415 | -121.9658 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0072118 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1843440 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1101 | 82161101 | FUSE | 29971 | 20230516 | 638 | 20230516 | 801 | 2113748 | 83 | Distribution Circuit | Animal | Squirrel | 27 | 2241 | 37.3752 | -122.1323 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0072152 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1843469 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1113 | 83671113 | TRANSFORMER | 315559231248 | 20230516 | 1843 | 20230517 | 509 | 2114439 | 626 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 6886 | 37.3485 | -122.0291 | No | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0072479 | OH | Sus | 31645783 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1843700 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | FUSE | 1371 | 20230516 | 1955 | 20230517 | 1610 | 2114486 | 1215 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3645 | 37.1183 | -122.0041 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0072486 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1843709 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | EL PATIO-1118 | 82921118 | FUSE | 4445 | 20230517 | 627 | 20230517 | 725 | 2114620 | 58 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 87 | 5046 | 37.2677 | -121.9253 | No | Clear;32-90 F |  |  | 23-0072552 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1843759 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1110 | 82031110 | FUSE | 30625 | 20230517 | 1053 | 20230517 | 1318 | 2114963 | 145 | Distribution Circuit | Equipment Failure/Involved | Overhead | 59 | 8555 | 37.3618 | -122.057 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0072661 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1843937 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1108 | 83771108 | FUSE | 218087 | 20230517 | 2305 | 20230518 | 107 | 2115481 | 122 | Distribution Circuit | Vegetation | Tree - grew into line | 26 | 3172 | 37.2495 | -121.9507 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0072922 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1844055 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1107 | 83671107 | TRANSFORMER | 315593031171 | 20230518 | 1844 | 20230519 | 156 | 2116357 | 432 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 3456 | 37.3464 | -122.0175 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0073276 | OH | Sus | 31646020 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1844282 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 2891 | 20230519 | 832 | 20230519 | 1325 | 2116782 | 293 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 1172 | 37.1327 | -121.9415 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0073614 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1844516 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WOLFE-1114 | 83671114 | FUSE | 4185 | 20230519 | 851 | 20230519 | 1146 | 2116966 | 175 | Distribution Circuit | Animal | Squirrel | 1 | 175 | 37.3726 | -122.0326 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0073550 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1844496 | 1 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | HICKS-2103 | 83432103 | FUSE | 4251 | 20230519 | 1702 | 20230519 | 1851 | 2117265 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1409 | 37.212 | -121.9093 | No | Clear;32-90 F |  |  | 23-0073720 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1844550 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1102 | 82031102 | TRANSFORMER | T20016 | 20230521 | 708 | 20230521 | 818 | 2117906 | 70 | Distribution Circuit | Animal | Squirrel | 26 | 1820 | 37.4106 | -122.0946 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0073949 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1844773 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1105 | 83771105 | TRANSFORMER | 315825128595 | 20230522 | 951 | 20230522 | 1459 | 2118623 | 308 | Transformer only | Vegetation | Tree - grew into line | 8 | 2464 | 37.2765 | -121.936 | No | Clear;32-90 F | Secondary | Arcing | 23-0074270 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1845084 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1111 | 83371111 | TRANSFORMER | C762 | 20230522 | 1524 | 20230522 | 2016 | 2118940 | 292 | Transformer only | Company Initiated | Construction Activity/equip- company | 23 | 6716 | 37.2988 | -122.0018 | No | Clear;32-90 F | Transformer | Normal | 23-0074376 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1845109 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1105 | 83771105 | JUMPER | OPEN JUMPERS @ 2541 SWEETBRIAR DR | 20230522 | 1700 | 20230522 | 2250 | 2118977 | 350 | Distribution Circuit | Vegetation | Tree - grew into line | 22 | 7700 | 37.2759 | -121.9388 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0074353 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1845104 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1108 | 82021108 | FUSE | 4189 | 20230522 | 1738 | 20230523 | 134 | 2119042 | 476 | Distribution Circuit | Equipment Failure/Involved | Underground | 72 | 12996 | 37.2248 | -121.9937 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0074271 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1845119 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1108 | 83371108 | FUSE | 2277 | 20230522 | 2247 | 20230522 | 2323 | 2119211 | 36 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 888 | 37.2791 | -121.9898 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0027141 | OH | Sus | 35329793 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1845158 | 1 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1109 | 83371109 | TRANSFORMER | 315752428636 | 20230523 | 1054 | 20230524 | 107 | 2119573 | 853 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 5118 | 37.2774 | -121.961 | No | Overcast;32-90 F | Transformer | Failed/Faulted | 23-0074639 | OH | Sus | 35448960 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1845346 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1108 | 83771108 | FUSE | 1393 | 20230525 | 932 | 20230526 | 1432 | 2121145 | 1740 | Distribution Circuit | Equipment Failure/Involved | Underground | 38 | 10948 | 37.2506 | -121.949 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0075516 | UG | Sus | 45775116 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1845906 | 1 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1113 | 83671113 | FUSE | 8939 | 20230525 | 955 | 20230526 | 46 | s1858540 | 10 | Distribution Circuit | Company Initiated | Personnel- company | 102 | 1632 | 37.3517 | -122.0291 | No | Overcast;32-90 F | Fuse | Normal | 23-0068449 | OH | Sus | 35181273 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1858540 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | HICKS-2103 | 83432103 | TRANSFORMER | 315905626890 | 20230525 | 1519 | 20230526 | 603 | 2121249 | 884 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 8840 | 37.23 | -121.9074 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 23-0075676 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1845947 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1111 | 83371111 | TRANSFORMER | 315624229152 | 20230527 | 750 | 20230527 | 1147 | 2122563 | 237 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 2370 | 37.291 | -122.0053 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0076283 | OH | Sus | 45777774 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1846301 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1103 | 83371103 | FUSE | 1241 | 20230527 | 804 | 20230527 | 920 | 2122573 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 41 | 3116 | 37.264 | -122.0313 | No | Clear;32-90 F |  |  | 23-0076285 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846311 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1106 | 82031106 | FUSE | 4019 | 20230527 | 1057 | 20230527 | 1145 | 2122679 | 48 | Distribution Circuit | Animal | Squirrel | 120 | 5760 | 37.3899 | -122.0936 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0076308 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846330 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1115 | 83371115 | TRANSFORMER | 315562829647 | 20230528 | 738 | 20230528 | 1725 | 2122933 | 587 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 1903 | 15774 | 37.3042 | -122.0266 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0076421 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1846408 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | OTHER | 1 PHASE DOWN | 20230529 | 1913 | 20230530 | 415 | 2123593 | 542 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 19222 | 37.1509 | -121.9729 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on object | 23-0076611 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | Yes | 1846559 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | EL PATIO-1113 | 82921113 | FUSE | 52666 | 20230530 | 653 | 20230530 | 824 | 2123681 | 91 | Distribution Circuit | Animal | Squirrel | 136 | 12376 | 37.2871 | -121.9333 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 23-0076659 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846603 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | BRITTON-1110 | 83611110 | FUSE | 2185 | 20230530 | 1131 | 20230530 | 1233 | 2124009 | 62 | Distribution Circuit | Animal | Squirrel | 17 | 1034 | 37.3593 | -122.0089 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Normal | 23-0076824 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846764 | 1 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOYOLA-0403 | 82160403 | FUSE | 12587 | 20230530 | 1943 | 20230530 | 2012 | 2124331 | 29 | Distribution Circuit | Vegetation | Tree - branch fell on line | 230 | 6670 | 37.3741 | -122.0914 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0077006 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1846827 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1108 | 83771108 | TRANSFORMER | 315804927609 | 20230530 | 2055 | 20230531 | 504 | 2124353 | 489 | Transformer only | Equipment Failure/Involved | Electrical Overload | 12 | 5868 | 37.2494 | -121.9424 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0077015 | OH | Sus | 35450065 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846832 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1109 | 83371109 | FUSE | 32739 | 20230531 | 556 | 20230531 | 730 | 2124461 | 94 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 106 | 9964 | 37.2821 | -121.9655 | No | Clear;32-90 F |  |  | 23-0077098 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | None | 0 | No | No | No | 1846877 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1102 | 83771102 | FUSE | 8177 | 20230601 | 1830 | 20230601 | 2023 | 2126928 | 113 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 2486 | 37.2516 | -121.9684 | No | Clear;32-90 F |  |  | 23-0078015 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1847371 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1108 | 83771108 | JUMPER | FB'S @ MARICOPA DR | 20230602 | 853 | 20230602 | 1245 | 2127190 | 232 | Distribution Circuit | Equipment Failure/Involved | Overhead | 58 | 13456 | 37.2438 | -121.9566 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Deteriorated | 23-0078151 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1847514 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1112 | 83371112 | FUSE | 3765 | 20230602 | 950 | 20230602 | 1005 | 2127067 | 15 | Distribution Circuit | 3rd Party | Metallic Balloon | 116 | 1740 | 37.2927 | -121.9836 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0078200 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1847555 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | HICKS-1109 | 83431109 | TRANSFORMER | 315817828015 | 20230602 | 1239 | 20230602 | 2257 | 2127291 | 618 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 7416 | 37.2606 | -121.9381 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0078327 | OH | Sus | 31650854 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1847581 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WHISMAN-1110 | 83631110 | FUSE | 29279 | 20230603 | 1536 | 20230603 | 1641 | 2128011 | 65 | Distribution Circuit | Animal | Squirrel | 1 | 65 | 37.4174 | -122.0904 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0078612 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1847731 | 1 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | OTHER | WIRE DOWN 1 POLE LD SIDE OF CGC# 315597823018 | 20230603 | 1627 | 20230604 | 831 | 2128023 | 964 | Distribution Circuit | Vegetation | Tree - branch fell on line | 385 | 19958 | 37.1215 | -122.0105 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0078617 | OH | Sus | 45812216 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | Yes | 1847735 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | FUSE | 969 | 20230604 | 2047 | 20230604 | 2222 | 2128716 | 95 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 215 | 20425 | 37.3562 | -122.1335 | No | Partly Cloudy;32-90 F |  |  | 23-0078757 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1847858 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1112 | 83371112 | TRANSFORMER | 315628428855 | 20230605 | 915 | 20230605 | 1439 | 2129181 | 324 | Transformer only | Vegetation | Tree - cutting- PG&E contractor | 11 | 3564 | 37.2827 | -122.0035 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0079019 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1848082 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | EL PATIO-1118 | 82921118 | RECLOSER | 60108 | 20230605 | 1315 | 20230606 | 227 | 2129281 | 746 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1514 | 99312 | 37.2791 | -121.9294 | No | Clear;32-90 F | Recloser | Failed/Faulted | 23-0078968 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848066 | 0 | Non-EPSS | N | 2023 | B PHASE & GRD
DE ANZA | DE ANZA | EL PATIO-1116 | 82921116 | FUSE | 4799 | 20230605 | 1426 | 20230605 | 1637 | 2129362 | 131 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 2358 | 37.2908 | -121.9634 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 23-0079004 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1848080 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | EL PATIO-1118 | 82921118 | FUSE | 33437 | 20230605 | 1507 | 20230605 | 1617 | 2129405 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 280 | 37.2768 | -121.9283 | No | Partly Cloudy;32-90 F |  |  | 23-0079048 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848092 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1108 | 83371108 | RECLOSER | 60088 | 20230605 | 1736 | 20230606 | 459 | 2129549 | 683 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1297 | 184714 | 37.2835 | -121.9814 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0079095 | OH | Sus | 31651233 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | No | 1848112 | 0 | Non-EPSS | N | 2023 | A PH- GRD
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | FUSE | 3563 | 20230605 | 2217 | 20230606 | 159 | 2130054 | 222 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 1998 | 37.2389 | -121.9953 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0079150 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1848158 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1108 | 83771108 | OCB | 1101/2 | 20230605 | 2230 | 20230605 | 2330 | 2130057 | 60 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5066 | 281059 | 37.2537 | -121.9661 | No | Overcast;32-90 F | Recloser | Broken | 23-0079073 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1848159 | 0 | Non-EPSS | N | 2023 | B- PHASE OC & GRD
DE ANZA | DE ANZA | SARATOGA-1112 | 83371112 | TRANSFORMER | 315628428855 | 20230606 | 909 | 20230606 | 1558 | 2130396 | 409 | Transformer only | Vegetation | Tree - grew into line | 11 | 4499 | 37.2827 | -122.0035 | No | Overcast;32-90 F | Secondary | Contaminated | 23-0079277 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1848313 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1112 | 83421112 | FUSE | 12249 | 20230606 | 1233 | 20230606 | 2337 | 2130630 | 664 | Distribution Circuit | Equipment Failure/Involved | Overhead | 180 | 37595 | 37.3885 | -122.0085 | No | Clear;32-90 F | Crossarm- Wood | Burned/flashed | 23-0079406 | OH | Sus | 31651238 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848415 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | AMES-1102 | 83901102 | FUSE | 589 | 20230606 | 1808 | 20230606 | 1859 | 2131208 | 51 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 1129 | 37.4323 | -122.097 | No | Partly Cloudy;32-90 F | Switch (OH) | Normal | 23-0073540 | OH | Sus | 35368232 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848473 | 1 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1108 | 83481108 | TRANSFORMER | 315337131266 | 20230606 | 2003 | 20230607 | 501 | 2131269 | 538 | Transformer only | Vegetation | Tree - branch fell on line | 3 | 1614 | 37.3478 | -122.1054 | No | Overcast;32-90 F | Transformer | Together | 23-0079574 | OH | Sus | 31651482 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848489 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1103 | 83371103 | FUSE | 6559 | 20230607 | 2226 | 20230608 | 415 | 2132241 | 333 | Distribution Circuit | Equipment Failure/Involved | Underground | 253 | 18672 | 37.2584 | -122.0372 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0080065 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1848868 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WOLFE-1104 | 83671104 | SWITCH | 52522 | 20230608 | 31 | 20230608 | 437 | 2132251 | 246 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 7134 | 37.3331 | -122.0163 | No | Partly Cloudy;32-90 F | Insulator | Broken | 23-0080093 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1848871 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1105 | 82031105 | FUSE | 29799 | 20230608 | 645 | 20230608 | 738 | 2132328 | 53 | Distribution Circuit | Animal | Squirrel | 20 | 1061 | 37.3959 | -122.0919 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0080155 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848896 | 1 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1103 | 83771103 | FUSE | 9681 | 20230608 | 842 | 20230608 | 1105 | 2132464 | 143 | Distribution Circuit | Animal | Bird found | 25 | 3575 | 37.2601 | -121.9816 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0080353 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1849082 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WHISMAN-1108 | 83631108 | TRANSFORMER | 315447233271 | 20230608 | 1605 | 20230608 | 1813 | 2132952 | 128 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 256 | 37.4037 | -122.0684 | No | Clear;32-90 F | Secondary | Deteriorated | 23-0080496 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1849116 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | TRANSFORMER | 315360031622 | 20230609 | 1510 | 20230609 | 1523 | 2133773 | 13 | Transformer only | 3rd Party | Other | 4 | 52 | 37.3579 | -122.0972 | No | Partly Cloudy;32-90 F | Secondary | Burned Open | 23-0081005 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1849442 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1109 | 83371109 | FUSE | 12959 | 20230609 | 1535 | 20230609 | 1638 | 2133785 | 63 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 36 | 2268 | 37.2791 | -121.9637 | No | Clear;32-90 F |  |  | 23-0081021 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1849447 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING SUB | 8348 | OCB | 1200/2 | 20230609 | 1959 | 20230610 | 2112 | 2133957 | 1513 | Distribution Circuit | 3rd Party | Metallic Balloon | 826 | 350138 | 37.3347 | -122.0208 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0081045 | OH | Sus | 31651674 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | Yes | No | 1849463 | 0 | Non-EPSS | N | 2023 | BC & 51
DE ANZA | DE ANZA | HICKS-1114 | 83431114 | TRANSFORMER | 315831227566 | 20230611 | 802 | 20230611 | 1520 | 2134557 | 438 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 876 | 37.2483 | -121.9334 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0081256 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1849700 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOYOLA-1101 | 82161101 | FUSE | 1419 | 20230612 | 1329 | 20230612 | 2150 | 2135413 | 501 | Distribution Circuit | Vegetation | Tree - grew into line | 10 | 5010 | 37.3863 | -122.1481 | No | Clear;32-90 F | Conductor- Overhead | Arcing | 23-0081687 | OH | Sus | 45844674 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1850070 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WHISMAN-1106 | 83631106 | TRANSFORMER | 315431033462 | 20230613 | 1641 | 20230613 | 1825 | 2136316 | 104 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 104 | 37.4084 | -122.0742 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0082041 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1850363 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | EL PATIO-1118 | 82921118 | FUSE | 30989 | 20230613 | 2012 | 20230613 | 2130 | 2136293 | 78 | Distribution Circuit | Vegetation | Other ground vegetation | 43 | 3354 | 37.2794 | -121.9246 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0082068 | OH | Sus | 45846447 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1850384 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | EL PATIO-1116 | 82921116 | FUSE | 175 | 20230615 | 620 | 20230615 | 816 | 2137405 | 116 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 151 | 17516 | 37.2884 | -121.9711 | No | Clear;32-90 F |  |  | 23-0082592 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1850769 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1112 | 83481112 | FUSE | 2093 | 20230615 | 633 | 20230615 | 746 | 2137424 | 73 | Distribution Circuit | Animal | Squirrel | 4 | 292 | 37.3482 | -122.0419 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0082574 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1850752 | 1 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1108 | 83481108 | TRANSFORMER | 315441930953 | 20230615 | 651 | 20230615 | 1825 | 2137439 | 694 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 2082 | 37.3397 | -122.0686 | No | Overcast;32-90 F | Transformer (OH) | On Ground | 23-0082649 | OH | Sus | 45849101 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1850820 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WOLFE-1114 | 83671114 | OCB | 360298 | 20230616 | 1106 | 20230617 | 106 | 2138498 | 840 | Distribution Circuit | Equipment Failure/Involved | Underground | 5017 | 374195 | 37.3548 | -122.0237 | No | Clear;32-90 F | Transformer (UG) | Burned/flashed | 23-0083150 | UG | Sus | 45850994 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1851136 | 0 | Non-EPSS | N | 2023 | GRD TIMED- B/U PHASE GRD INST
DE ANZA | DE ANZA | LOS ALTOS-1104 | 82241104 | RECLOSER | LM16 | 20230616 | 1546 | 20230616 | 1554 | 2138592 | 8 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1716 | 13728 | 37.3876 | -122.1141 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0083263 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1851183 | 0 | Non-EPSS | N | 2023 | N/A
DE ANZA | DE ANZA | SARATOGA-1112 | 83371112 | OTHER | T11721 TWD T11720 | 20230617 | 932 | 20230617 | 958 | 2139236 | 26 | Distribution Circuit | Equipment Failure/Involved | Underground | 8 | 208 | 37.2884 | -121.9913 | No | Clear;32-90 F | Secondary | Broken | 23-0083347 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1851303 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 32117 | 20230617 | 1713 | 20230618 | 1120 | 2139486 | 1087 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 26088 | 37.1572 | -121.9855 | No | Clear;32-90 F | Connector or Splice (OH) | Arcing | 23-0083413 | OH | Sus | 45851740 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1851357 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1108 | 82031108 | INTERRUPTER | 821134 | 20230618 | 1126 | 20230618 | 1338 | 2139781 | 132 | Distribution Circuit | Animal | Squirrel | 630 | 74104 | 37.3768 | -122.0637 | No | Clear;32-90 F | Interrupter | Failed/Faulted | 23-0083501 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1851448 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1106 | 82031106 | OCB | 1106/2 | 20230619 | 935 | 20230620 | 102 | 2140376 | 917 | Distribution Circuit | Vegetation | Tree - fell into line | 3558 | 223215 | 37.3826 | -122.0697 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0083615 | OH | Sus | 31652727 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1851602 | 0 | Non-EPSS | N | 2023 | B- GRD & TIME OC
DE ANZA | DE ANZA | MOUNTAIN VIEW-1106 | 82031106 | SWITCH | 53198 | 20230620 | 111 | 20230620 | 125 | 2140818 | 14 | Distribution Circuit | Company Initiated | Return Circuit Normal | 39 | 546 | 37.3833 | -122.0803 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0083615 | OH | Sus | 31652727 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1851718 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1105 | 83421105 | SWITCH | 380419 | 20230620 | 2130 | 20230621 | 254 | 2141798 | 324 | Distribution Circuit | Equipment Failure/Involved | Overhead | 159 | 51516 | 37.4036 | -122.0224 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0084041 | OH | Sus | 31652973 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1851978 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1109 | 83671109 | SWITCH | 4557 | 20230621 | 948 | 20230621 | 1335 | 2142166 | 227 | Distribution Circuit | Equipment Failure/Involved | Overhead | 72 | 2264 | 37.3272 | -122.0232 | No | Clear;32-90 F | Pothead(Riser Termination) | Broken | 23-0081045 | OH | Sus | 31651674 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1852155 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1107 | 83671107 | TRANSFORMER | 315579231450 | 20230621 | 1806 | 20230622 | 425 | 2142634 | 619 | Transformer only | Equipment Failure/Involved | Electrical Overload | 14 | 8666 | 37.354 | -122.0224 | No | Clear;32-90 F | Transformer | Broken | 23-0084456 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852245 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1110 | 83371110 | FUSE | 3255 | 20230622 | 742 | 20230622 | 848 | 2142849 | 66 | Distribution Circuit | Animal | Other | 2 | 132 | 37.2919 | -121.9952 | No | Clear;32-90 F | Transformer (UG) | Normal | 23-0084568 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852327 | 1 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1104 | 82241104 | FUSE | 30477 | 20230622 | 815 | 20230622 | 929 | 2142900 | 74 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 24 | 1776 | 37.3885 | -122.1109 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0084584 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1852362 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | OCB | 1107/2 | 20230622 | 1310 | 20230622 | 2357 | 2143245 | 647 | Distribution Circuit | 3rd Party | Vehicle | 2464 | 109538 | 37.281 | -122.0156 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0084722 | OH | Sus | 31653184 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | Yes | 1852467 | 0 | EPSS Ckt | N | 2023 | B & GRD
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | RECLOSER | 60118 | 20230622 | 1934 | 20230622 | 1940 | 2143501 | 6 | Distribution Circuit | Vegetation | Tree - branch fell on line | 937 | 5622 | 37.1247 | -121.9353 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0084855 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1852510 | 0 | EPSS Ckt | N | 2023 | NONE
DE ANZA | DE ANZA | VASONA-1103 | 83771103 | SWITCH | 12132 | 20230622 | 2029 | 20230623 | 123 | 2143419 | 294 | Distribution Circuit | Equipment Failure/Involved | Underground | 409 | 18167 | 37.2637 | -121.9889 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0084838 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1852515 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | JUMPER | OJ LD SIDE OF FUSES 6757 | 20230622 | 2200 | 20230623 | 201 | 2143675 | 241 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 9399 | 37.2495 | -122.02 | No | Clear;32-90 F | Jumper | Burned Open | 23-0084893 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Open Circuit | 0 | No | No | No | 1852559 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | HICKS-1116 | 83431116 | TRANSFORMER | 315794426812 | 20230623 | 518 | 20230623 | 1400 | 2143721 | 522 | Transformer only | Vegetation | Tree - fell into line | 3 | 1566 | 37.2274 | -121.9455 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0084940 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852600 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WOLFE-1104 | 83671104 | TRANSFORMER | 315633629982 | 20230623 | 845 | 20230623 | 903 | 2143923 | 18 | Transformer only | Vegetation | Tree - palm frond fell into line | 9 | 162 | 37.3137 | -122.0024 | No | Overcast;32-90 F | Secondary | Normal | 23-0084976 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1852674 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | RECLOSER | 60114 | 20230624 | 809 | 20230624 | 1511 | 2144578 | 422 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 292 | 93647 | 37.119 | -121.9205 | No | Partly Cloudy;32-90 F |  |  | 23-0085299 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852834 | 0 | EPSS Ckt | Y | 2023 | C PH & 50 INST
DE ANZA | DE ANZA | SARATOGA-1108 | 83371108 | JUMPER | 4917 NORTHLAWN DR | 20230624 | 1459 | 20230624 | 2037 | 2144989 | 338 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 12844 | 37.2872 | -121.9886 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0085350 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1852896 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | AMES-1102 | 83901102 | FUSE | 18895 | 20230626 | 630 | 20230626 | 914 | 2145770 | 164 | Distribution Circuit | Animal | Squirrel | 2 | 328 | 37.4329 | -122.0986 | No | Partly Cloudy;32-90 F | Fuse | Normal | 23-0085521 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1853142 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOYOLA-0403 | 82160403 | TRANSFORMER | 315383532191 | 20230626 | 1057 | 20230626 | 1459 | 2146237 | 242 | Transformer only | Company Initiated | Personnel- company | 10 | 2420 | 37.3738 | -122.0889 | No | Clear;32-90 F | Secondary | Normal | 23-0085727 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1853246 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | TRANSFORMER | 315564327871 | 20230626 | 1506 | 20230626 | 1551 | 2146276 | 45 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 450 | 37.2553 | -122.0252 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0085752 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1853252 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1106 | 82241106 | FUSE | 149 | 20230626 | 1555 | 20230627 | 127 | 2146239 | 572 | Distribution Circuit | Vegetation | Other ground vegetation | 9 | 5148 | 37.3923 | -122.1168 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0085775 | OH | Sus | 45860740 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1853264 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1104 | 83371104 | TRANSFORMER | 315634527566 | 20230626 | 1651 | 20230627 | 410 | 2146358 | 679 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 2037 | 37.2475 | -122.0006 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0085836 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853292 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1105 | 83371105 | FUSE | 5079 | 20230627 | 617 | 20230627 | 700 | 2146600 | 43 | Distribution Circuit | Animal | Squirrel | 8 | 344 | 37.2847 | -122.0348 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0085896 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853341 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1108 | 82031108 | FUSE | 6445 | 20230627 | 955 | 20230627 | 1011 | 2146890 | 16 | Distribution Circuit | Equipment Failure/Involved | Overhead | 85 | 1360 | 37.3793 | -122.0562 | No | Partly Cloudy;32-90 F | Fuse | Normal | 23-0086011 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853469 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOYOLA-0403 | 82160403 | TRANSFORMER | 315359431956 | 20230627 | 1111 | 20230627 | 1251 | 2146978 | 100 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 500 | 37.3669 | -122.0974 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0086074 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1853485 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | SWITCH | SA13 | 20230628 | 1108 | 20230628 | 1114 | 2147995 | 6 | Distribution Circuit | Equipment Failure/Involved | Overhead | 64 | 384 | 37.0991 | -121.8593 | No | Clear;32-90 F | Regulator | Malfunctioning | 23-0086543 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1853790 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | FUSE | 1629 | 20230629 | 1838 | 20230629 | 2046 | 2149270 | 128 | Distribution Circuit | Animal | Bird found | 93 | 11904 | 37.3555 | -122.1035 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0087362 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1854170 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | AMES-1102 | 83901102 | INTERRUPTER | 334146 | 20230630 | 853 | 20230630 | 859 | 2149647 | 6 | Distribution Circuit | 3rd Party | Vandalism | 2 | 12 | 37.4262 | -122.0985 | No | Clear;32-90 F | Transformer (UG) | Normal | 23-0087495 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1854315 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | RECLOSER | LB44 | 20230630 | 1538 | 20230702 | 58 | 2150062 | 2000 | Distribution Circuit | Equipment Failure/Involved | Overhead | 335 | 29847 | 37.1938 | -121.9958 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0087723 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1854417 | 0 | EPSS Ckt | Y | 2023 | B PH & GRD
DE ANZA | DE ANZA | HICKS-1116 | 83431116 | TRANSFORMER | 315839827236 | 20230630 | 1733 | 20230630 | 1845 | 2150169 | 72 | Transformer only | Unknown Cause | Patrol - found nothing | 11 | 792 | 37.2394 | -121.9303 | No | Clear;32-90 F |  |  | 23-0087770 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1854433 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1101 | 82161101 | FUSE | 30591 | 20230630 | 2016 | 20230701 | 630 | 2150343 | 614 | Distribution Circuit | Equipment Failure/Involved | Overhead | 73 | 44822 | 37.3847 | -122.1411 | No | Clear;32-90 F | Crossarm- Wood | Broken- wire on object | 23-0087791 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | Yes | No | 1854456 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1109 | 82031109 | FUSE | 12861 | 20230630 | 2357 | 20230701 | 300 | 2150511 | 183 | Distribution Circuit | Vegetation | Tree - branch fell on line | 181 | 21713 | 37.3715 | -122.0775 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0087841 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1854519 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | TRANSFORMER | 315565928592 | 20230701 | 1733 | 20230701 | 1833 | 2151075 | 60 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 480 | 37.2752 | -122.0249 | No | Clear;Above 90 | Fuse | Burned Open | 23-0087988 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1854631 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1101 | 82021101 | TRANSFORMER | 315764026754 | 20230701 | 1930 | 20230701 | 2008 | 2151331 | 38 | Transformer only | Unknown Cause | Patrol - found nothing | 8 | 304 | 37.2257 | -121.9561 | No | Clear;32-90 F |  |  | 23-0088013 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1854655 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | RESEARCH-2102 | 14692102 | OCB | 2102/2 | 20230701 | 1959 | 20230702 | 1215 | s1860601 | 494 | Distribution Circuit | Equipment Failure/Involved | Underground | 734 | 552338 | 37.7823 | -121.9674 | No | Clear;32-90 F | Connector or Splice (UG) | Broken | 23-0088015 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1860601 | 0 | EPSS Ckt | N | 2023 | GRD
DE ANZA | DE ANZA | SARATOGA-1115 | 83371115 | TRANSFORMER | 315554429145 | 20230701 | 2204 | 20230701 | 2243 | 2151598 | 39 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 429 | 37.2904 | -122.0292 | No | Clear;32-90 F | Fuse | Burned Open | 23-0088067 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1854705 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1102 | 83771102 | FUSE | 12183 | 20230702 | 644 | 20230702 | 1219 | 2151849 | 335 | Distribution Circuit | Animal | Squirrel | 49 | 16535 | 37.244 | -121.9794 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 23-0088121 | OH | Sus | 45867512 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1854756 | 1 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1113 | 83371113 | JUMPER | OJ IFO 855 BETTE AVE | 20230702 | 900 | 20230702 | 1731 | 2151943 | 511 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 62 | 31682 | 37.3146 | -122.0214 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0088127 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1854761 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1109 | 83371109 | FUSE | 12335 | 20230702 | 1328 | 20230703 | 301 | 2152085 | 813 | Distribution Circuit | Equipment Failure/Involved | Overhead | 159 | 16455 | 37.2712 | -121.9899 | No | Clear;32-90 F | Connector or Splice (OH) | Arcing | 23-0088163 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1854792 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1115 | 83371115 | TRANSFORMER | 315554429145 | 20230702 | 1915 | 20230702 | 1952 | 2152606 | 35 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 385 | 37.2904 | -122.0292 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0088237 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1854867 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1106 | 82031106 | TRANSFORMER | 315412532402 | 20230702 | 2035 | 20230702 | 2207 | 2152683 | 92 | Transformer only | Unknown Cause | Patrol - found nothing | 9 | 828 | 37.3795 | -122.0799 | No | Clear-Heat Wave;32-90 F |  |  | 23-0088290 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1854931 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1113 | 83481113 | TRANSFORMER | 315508831306 | 20230702 | 2310 | 20230703 | 910 | 2152667 | 600 | Transformer only | Vegetation | Tree - grew into line | 12 | 7200 | 37.3495 | -122.0452 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0088280 | OH | Sus | 31654206 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1854919 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MENLO-1103 | 24131103 | RECLOSER | 58562 | 20230703 | 23 | 20230703 | 2304 | 2152886 | 274 | Distribution Circuit | 3rd Party | Vehicle | 485 | 141620 | 37.4044 | -122.1574 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0088292 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1854933 | 0 | EPSS Ckt | N | 2023 | A-B-C PH
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | TRANSFORMER | 315693024705 | 20230703 | 600 | 20230704 | 850 | 2153001 | 1610 | Transformer only | Vegetation | Tree - fell into line | 1 | 1610 | 37.1689 | -121.9788 | No | Clear;32-90 F | Transformer | Broken | 23-0088318 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1854952 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1101 | 82161101 | FUSE | 30901 | 20230703 | 937 | 20230703 | 1110 | 2153175 | 93 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 1488 | 37.3748 | -122.1212 | No | Clear;32-90 F |  |  | 23-0088462 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1855023 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1111 | 83481111 | TRANSFORMER | 315393231120 | 20230703 | 1327 | 20230703 | 1357 | 2153446 | 30 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 360 | 37.344 | -122.0859 | No | Clear;32-90 F | Secondary | Arcing | 23-0088542 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1855043 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WHISMAN-1103 | 83631103 | FUSE | 4145 | 20230703 | 1454 | 20230704 | 1341 | 2153550 | 1367 | Distribution Circuit | Equipment Failure/Involved | Underground | 9 | 12303 | 37.4036 | -122.0601 | No | Clear;32-90 F | Switch (UG) | Leaking | 23-0088621 | UG | Sus | 35464310 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855063 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1106 | 82241106 | OCB | 1106/2 | 20230703 | 1706 | 20230703 | 1757 | 2153659 | 51 | Distribution Circuit | Vegetation | Tree - branch fell on line | 563 | 28713 | 37.3936 | -122.1149 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0088648 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1855071 | 0 | Non-EPSS | N | 2023 | B & C
DE ANZA | DE ANZA | MOUNTAIN VIEW-1104 | 82031104 | TRANSFORMER | 315396833008 | 20230704 | 915 | 20230704 | 1644 | 2154039 | 449 | Transformer only | 3rd Party | Vehicle | 18 | 8082 | 37.3959 | -122.0859 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0088746 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1855153 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | RECLOSER | 340986 | 20230704 | 1227 | 20230704 | 1601 | 2154078 | 214 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 576 | 123264 | 37.24 | -121.9965 | No | Partly Cloudy;32-90 F |  |  | 23-0088751 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855159 | 0 | EPSS Ckt | Y | 2023 | GRD INST
DE ANZA | DE ANZA | MOUNTAIN VIEW-1102 | 82031102 | TRANSFORMER | 315374733516 | 20230705 | 1811 | 20230705 | 1853 | 2154942 | 42 | Transformer only | Equipment Failure/Involved | Overhead | 68 | 2856 | 37.4096 | -122.0935 | No | Clear;32-90 F | Secondary | Broken | 23-0089152 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1855371 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | RECLOSER | LL86 | 20230706 | 715 | 20230706 | 1305 | 2155122 | 350 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 806 | 259822 | 37.3586 | -122.1308 | No | Partly Cloudy;32-90 F |  |  | 23-0089238 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855420 | 0 | EPSS Ckt | N | 2023 | SGF RLY
DE ANZA | DE ANZA | MOUNTAIN VIEW-1107 | 82031107 | TRANSFORMER | 315370031855 | 20230706 | 1341 | 20230706 | 1408 | 2154868 | 27 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 81 | 37.3639 | -122.0943 | No | Clear;32-90 F | Secondary | Broken | 23-0089465 | OH | Sus | 45871162 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1855549 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1103 | 83371103 | TRANSFORMER | 315516528229 | 20230706 | 1532 | 20230707 | 2022 | 2155640 | 1730 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 6920 | 37.2648 | -122.0417 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0089575 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855581 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1113 | 83371113 | FUSE | 17787 | 20230706 | 1642 | 20230706 | 2129 | 2155707 | 287 | Distribution Circuit | Equipment Failure/Involved | Underground | 183 | 5747 | 37.3056 | -122.007 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0089502 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1855577 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1113 | 83671113 | FUSE | 31905 | 20230707 | 1712 | 20230707 | 1919 | 2156496 | 127 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 49 | 6223 | 37.3606 | -122.0401 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0090009 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1855764 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1108 | 83771108 | FUSE | 18331 | 20230708 | 1510 | 20230708 | 1522 | 2157196 | 12 | Distribution Circuit | 3rd Party | Metallic Balloon | 59 | 708 | 37.2427 | -121.9509 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0090128 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1855882 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1105 | 83671105 | TRANSFORMER | 315585930671 | 20230708 | 1647 | 20230709 | 2126 | 2157279 | 1719 | Transformer only | Vegetation | Tree - grew into line | 16 | 27504 | 37.3327 | -122.0199 | No | Clear;32-90 F | Transformer | Arcing | 23-0090157 | OH | Sus | 31654841 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855900 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 31779 | 20230709 | 1923 | 20230709 | 2100 | 2157865 | 97 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1261 | 37.212 | -121.9724 | No | Partly Cloudy;32-90 F |  |  | 23-0090264 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1855995 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | RECLOSER | LL86 | 20230710 | 948 | 20230711 | 57 | 2158370 | 909 | Distribution Circuit | 3rd Party | Vehicle | 807 | 87228 | 37.3586 | -122.1308 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 23-0090373 | OH | Sus | 31655083 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1856136 | 0 | EPSS Ckt | N | 2023 | B/GRD
DE ANZA | DE ANZA | SARATOGA-1105 | 83371105 | FUSE | 689215 | 20230710 | 1128 | 20230710 | 2153 | 2158494 | 625 | Distribution Circuit | Animal | Bird found | 14 | 8750 | 37.2709 | -122.0532 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Burned/flashed | 23-0090512 | OH | Sus | 31655088 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1856211 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | EL PATIO-1108 | 82921108 | OCB | 1108/2 | 20230710 | 1216 | 20230710 | 1228 | s1866685 | 12 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3178 | 38136 | 37.2915 | -121.9357 | No | Clear;32-90 F | Capacitor | Failed/Faulted | 23-0083346 | OH | Sus | 35332326 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1866685 | 0 | Non-EPSS | N | 2023 | n/a
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | RECLOSER | 413816 | 20230711 | 728 | 20230711 | 1103 | 2159356 | 215 | Distribution Circuit | Animal | Squirrel | 166 | 28896 | 37.2525 | -122.0605 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0090690 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1856320 | 0 | EPSS Ckt | Y | 2023 | A/G
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 4469 | 20230711 | 1208 | 20230711 | 1328 | 2159875 | 80 | Distribution Circuit | Equipment Failure/Involved | Overhead | 71 | 5680 | 37.1056 | -121.9324 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0090841 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1856530 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WOLFE-1104 | 83671104 | OCB | 1104/2 | 20230711 | 1429 | 20230712 | 37 | 2159978 | 608 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2123 | 161661 | 37.3347 | -122.021 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0090935 | OH | Sus | 31654879 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1856568 | 0 | Non-EPSS | N | 2023 | PH INST & GRD TIME
DE ANZA | DE ANZA | VASONA-1105 | 83771105 | FUSE | 19145 | 20230711 | 1555 | 20230712 | 508 | 2160054 | 793 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 793 | 37.2762 | -121.9485 | No | Clear;32-90 F | Connector or Splice (OH) | Burned/flashed | 23-0090996 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Three Phase Fault | 0 | No | No | No | 1856585 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MENLO-1103 | 24131103 | RECLOSER | 866118 | 20230712 | 1511 | 20230712 | 1632 | 2160982 | 81 | Distribution Circuit | Vegetation | Tree - fell into line | 157 | 12717 | 37.3756 | -122.1668 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0091441 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1856903 | 0 | EPSS Ckt | Y | 2023 | A & B PH- 50 (INST)
DE ANZA | DE ANZA | SARATOGA-1113 | 83371113 | TRANSFORMER | 315568629490 | 20230712 | 2320 | 20230713 | 305 | 2161267 | 225 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 2250 | 37.3 | -122.0244 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0091581 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1856961 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1104 | 83481104 | SWITCH | 11948 | 20230713 | 2359 | 20230714 | 1219 | 2162080 | 733 | Distribution Circuit | Equipment Failure/Involved | Overhead | 358 | 187533 | 37.3167 | -122.0341 | No | Clear;32-90 F | Switch (OH) | Broken | 23-0091742 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1857286 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | EL PATIO-1117 | 82921117 | FUSE | 12819 | 20230714 | 703 | 20230714 | 814 | 2162149 | 71 | Distribution Circuit | Animal | Squirrel | 15 | 1065 | 37.286 | -121.9541 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 23-0092168 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1857375 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1107 | 83481107 | TRANSFORMER | 315559629878 | 20230714 | 2314 | 20230714 | 2337 | 2163008 | 23 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 299 | 37.3105 | -122.0278 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0092511 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1857580 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1104 | 83421104 | TRANSFORMER | 315684232794 | 20230715 | 947 | 20230715 | 1328 | 2163360 | 221 | Transformer only | Vegetation | Tree - grew into line | 14 | 3094 | 37.3912 | -121.9871 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Contaminated | 23-0092568 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1857663 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 965 | 20230715 | 1655 | 20230716 | 1120 | 2163639 | 1105 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 4420 | 37.1669 | -121.9866 | No | Clear;Above 90 | Pole-Wood | Broken | 23-0092690 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1857719 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1104 | 83371104 | FUSE | 31847 | 20230715 | 1852 | 20230715 | 2024 | 2163774 | 92 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 2024 | 37.2505 | -121.9909 | No | Clear;32-90 F |  |  | 23-0092716 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1857735 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1102 | 82031102 | SWITCH | 11670 | 20230715 | 2235 | 20230715 | 2312 | 2163900 | 37 | Distribution Circuit | Equipment Failure/Involved | Underground | 311 | 11507 | 37.3972 | -122.0755 | No | Clear;32-90 F | Secondary | Arcing | 23-0092744 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1857762 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1103 | 83771103 | FUSE | 31239 | 20230716 | 559 | 20230716 | 718 | 2164003 | 79 | Distribution Circuit | Animal | Squirrel | 154 | 9243 | 37.2606 | -121.9768 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0092769 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1857790 | 1 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | RECLOSER | 991992 | 20230716 | 1103 | 20230717 | 336 | 2164109 | 993 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 15132 | 37.1894 | -122.0309 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0092803 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | Yes | Yes | 1857833 | 0 | EPSS Ckt | N | 2023 | N/A
DE ANZA | DE ANZA | MOUNTAIN VIEW-1107 | 82031107 | TRANSFORMER | 315408231591 | 20230716 | 1545 | 20230717 | 1430 | 2164392 | 1365 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 4095 | 37.3574 | -122.0808 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0092862 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1857891 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1104 | 82031104 | TRANSFORMER | 315427132593 | 20230716 | 1614 | 20230717 | 400 | 2164448 | 706 | Transformer only | Equipment Failure/Involved | Overhead | 21 | 14826 | 37.3846 | -122.075 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0092870 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1857896 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1106 | 82241106 | OCB | 1106/2 | 20230716 | 1621 | 20230716 | 1728 | 2164459 | 67 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1266 | 76386 | 37.3936 | -122.1149 | No | Partly Cloudy;32-90 F | Circuit Breaker | Normal | 23-0092857 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1857887 | 0 | Non-EPSS | N | 2023 | TIME/INST A & B PH
DE ANZA | DE ANZA | HICKS-1114 | 83431114 | OTHER | WIRE DOWN W/OF 29401 | 20230716 | 1844 | 20230716 | 2337 | 2164592 | 293 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1768 | 299430 | 37.2469 | -121.926 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 23-0092899 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1857919 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | EL PATIO-1117 | 82921117 | TRANSFORMER | 315759028910 | 20230716 | 2020 | 20230716 | 2101 | 2164756 | 41 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 615 | 37.2847 | -121.9591 | No | Clear;32-90 F | Fuse | Broken | 23-0092927 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1857947 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | EL PATIO-1117 | 82921117 | TRANSFORMER | 315756028903 | 20230716 | 2020 | 20230716 | 2058 | 2164755 | 38 | Transformer only | Unknown Cause | Patrol - found nothing | 16 | 608 | 37.2846 | -121.96 | No | Clear;32-90 F |  |  | 23-0092928 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1857948 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | RECLOSER | 340986 | 20230717 | 1228 | 20230717 | 1607 | 2165558 | 219 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 575 | 125925 | 37.24 | -121.9965 | No | Clear;32-90 F |  |  | 23-0093173 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Open Circuit | 0 | No | No | No | 1858185 | 0 | EPSS Ckt | Y | 2023 | INST OC RLY
DE ANZA | DE ANZA | LOS GATOS-1101 | 82021101 | TRANSFORMER | 315735927015 | 20230717 | 1556 | 20230718 | 304 | 2165605 | 668 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 8016 | 37.2327 | -121.9658 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0093335 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1858235 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1106 | 82241106 | TRANSFORMER | 315284833151 | 20230717 | 1855 | 20230718 | 259 | 2165966 | 484 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1452 | 37.399 | -122.1242 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0093415 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1858273 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | HICKS-1116 | 83431116 | TRANSFORMER | 315880726871 | 20230717 | 2022 | 20230718 | 851 | 2166032 | 749 | Transformer only | Equipment Failure/Involved | Electrical Overload | 5 | 3745 | 37.2295 | -121.916 | No | Clear;32-90 F | Transformer | Deteriorated | 23-0093433 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1858288 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1109 | 83481109 | TRANSFORMER | 315497629812 | 20230719 | 1049 | 20230719 | 1200 | 2167860 | 71 | Transformer only | Vegetation | Tree - branch fell on line | 6 | 426 | 37.3084 | -122.0491 | No | Clear;32-90 F | Secondary | Normal | 23-0094200 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1858845 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1109 | 83371109 | TRANSFORMER | 315710628742 | 20230719 | 1334 | 20230719 | 2020 | 2168395 | 406 | Transformer only | Vegetation | Tree - branch fell on line | 5 | 2030 | 37.28 | -121.9754 | No | Clear;32-90 F | Secondary | Contaminated | 23-0094362 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1858912 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1109 | 83371109 | TRANSFORMER | 315713028742 | 20230719 | 1335 | 20230720 | 1011 | 2168396 | 1236 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 11124 | 37.28 | -121.9745 | No | Clear;32-90 F | Transformer | Broken | 23-0094365 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1858913 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 89337 | 20230719 | 2309 | 20230720 | 403 | 2168532 | 294 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1470 | 37.1129 | -121.9248 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0094457 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1858967 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1102 | 82021102 | FUSE | 17063 | 20230720 | 601 | 20230720 | 1256 | 2168578 | 415 | Distribution Circuit | Equipment Failure/Involved | Overhead | 257 | 65625 | 37.2327 | -121.9746 | No | Partly Cloudy;32-90 F | Jumper | Broken | 23-0094508 | OH | Sus | 45894534 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1858986 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | RECLOSER | 60124 | 20230720 | 701 | 20230720 | 1454 | 2168597 | 473 | Distribution Circuit | Equipment Failure/Involved | Overhead | 454 | 88355 | 37.1462 | -121.9823 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0094510 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1858987 | 0 | EPSS Ckt | Y | 2023 | B & C PHASE
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | FUSE | 33585 | 20230720 | 701 | 20230720 | 1715 | 2168755 | 614 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 614 | 37.1407 | -121.9714 | No | Clear;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0094574 | OH | Sus | 45895208 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1859061 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | RECLOSER | 340986 | 20230720 | 1325 | 20230720 | 1606 | 2169015 | 161 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 574 | 92414 | 37.24 | -121.9965 | No | Clear;32-90 F |  |  | 23-0094745 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Open Circuit | 0 | No | No | No | 1859119 | 0 | EPSS Ckt | Y | 2023 | INST PHASE TARGET
DE ANZA | DE ANZA | WOLFE-1107 | 83671107 | TRANSFORMER | 315590631230 | 20230721 | 820 | 20230721 | 1010 | 2169642 | 110 | Transformer only | Animal | Other | 1 | 110 | 37.3484 | -122.018 | No | Clear;32-90 F | Secondary | Broken | 23-0095052 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1859313 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1108 | 83481108 | TRANSFORMER | 315483530908 | 20230721 | 1650 | 20230722 | 522 | 2170184 | 752 | Distribution Circuit | Equipment Failure/Involved | Overhead | 124 | 28158 | 37.3385 | -122.0545 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0095421 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859487 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1106 | 82031106 | TRANSFORMER | 315415032466 | 20230722 | 139 | 20230722 | 1731 | 2170515 | 952 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 5712 | 37.3813 | -122.0791 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0095495 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859554 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1106 | 82031106 | TRANSFORMER | 315415332426 | 20230722 | 144 | 20230722 | 1740 | 2170512 | 956 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 19463 | 37.3802 | -122.079 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0095493 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859551 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1103 | 83371103 | FUSE | 6523 | 20230722 | 820 | 20230722 | 939 | 2170674 | 79 | Distribution Circuit | Animal | Squirrel | 113 | 8927 | 37.2691 | -122.0319 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0095529 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859625 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | HICKS-1116 | 83431116 | TRANSFORMER | 315849226705 | 20230722 | 1005 | 20230723 | 1305 | 2171125 | 1620 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1620 | 37.225 | -121.9266 | No | Clear;32-90 F | Secondary | Deteriorated | 23-0095674 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1859775 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | RECLOSER | 60116 | 20230722 | 1539 | 20230722 | 1752 | 2170972 | 133 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1136 | 147447 | 37.1735 | -121.9928 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0095581 | OH | Sus | 45897526 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859673 | 0 | EPSS Ckt | Y | 2023 | A & G
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 66177 | 20230723 | 117 | 20230723 | 1822 | 2171353 | 1025 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1043 | 37.1031 | -121.8757 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0095681 | OH | Sus | 45897582 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1859782 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | CAMP EVERS-2106 | 83622106 | RECLOSER | 60122 | 20230723 | 1348 | 20230723 | 1926 | 2171554 | 338 | Distribution Circuit | Equipment Failure/Involved | Underground | 455 | 153790 | 37.1462 | -121.9823 | No | Partly Cloudy;32-90 F | Elbow | Burned/flashed | 23-0095695 | UG | Sus | 45897591 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859794 | 0 | EPSS Ckt | N | 2023 | A-B-C-GRD
DE ANZA | DE ANZA | WOLFE-1107 | 83671107 | FUSE | 11158 | 20230723 | 2108 | 20230724 | 1518 | 2171906 | 1090 | Distribution Circuit | Equipment Failure/Involved | Underground | 170 | 58343 | 37.3524 | -122.0188 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0095750 | UG | Sus | 35472130 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859852 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1106 | 83671106 | TRANSFORMER | T13534 | 20230724 | 846 | 20230724 | 1244 | 2172266 | 238 | Transformer only | 3rd Party | Customer Equipment | 1 | 238 | 37.3484 | -122.0086 | No | Partly Cloudy;32-90 F | Secondary | Normal | 23-0095837 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1859949 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | BRITTON-1106 | 83611106 | SWITCH | 31026 | 20230724 | 1448 | 20230724 | 1512 | 2172709 | 24 | Distribution Circuit | Equipment Failure/Involved | Underground | 57 | 1368 | 37.3528 | -122.0205 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0095750 | UG | Sus | 35472130 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1860109 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | SWITCH | SA11 | 20230725 | 1503 | 20230726 | 147 | 2173668 | 644 | Distribution Circuit | Equipment Failure/Involved | Overhead | 133 | 72116 | 37.1054 | -121.8968 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0096657 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1860423 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1104 | 83421104 | TRANSFORMER | 315684233016 | 20230725 | 2044 | 20230726 | 635 | 2173888 | 591 | Transformer only | Vegetation | Tree - fell into line | 12 | 7092 | 37.399 | -121.9871 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0096782 | OH | Sus | 31656961 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1860460 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1107 | 82031107 | TRANSFORMER | 315382331962 | 20230725 | 2133 | 20230726 | 1214 | 2173876 | 881 | Transformer only | Animal | Squirrel | 12 | 10572 | 37.3675 | -122.0893 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 23-0096786 | OH | Sus | 31656962 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1860463 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1111 | 83481111 | FUSE | 2833 | 20230726 | 844 | 20230726 | 1040 | 2174172 | 116 | Distribution Circuit | 3rd Party | Vehicle | 31 | 3596 | 37.3445 | -122.0857 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0096983 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1860663 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1112 | 83371112 | TRANSFORMER | MTR#1007541353 | 20230726 | 1650 | 20230726 | 1826 | 2174456 | 96 | Distribution Circuit | Vegetation | Tree - grew into line | 18 | 1644 | 37.2886 | -121.9987 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0097134 | OH | Sus | 45902717 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1860725 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | FUSE | 32957 | 20230727 | 1439 | 20230727 | 1805 | 2175573 | 206 | Distribution Circuit | Animal | Squirrel | 2 | 412 | 37.2299 | -122.0083 | No | Clear;32-90 F | Fuse | Burned Open | 23-0097795 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1861036 | 1 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | FUSE | 17721 | 20230727 | 1809 | 20230727 | 1939 | 2175761 | 90 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1170 | 37.238 | -122.0077 | No | Clear;32-90 F |  |  | 23-0097806 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1861045 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | TRANSFORMER | 315609027220 | 20230728 | 650 | 20230728 | 2202 | 2175953 | 912 | Transformer only | Equipment Failure/Involved | Electrical Overload | 5 | 4560 | 37.2378 | -122.0094 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0098075 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1861285 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1104 | 83371104 | FUSE | 29221 | 20230728 | 851 | 20230728 | 1035 | 2176068 | 104 | Distribution Circuit | Animal | Squirrel | 36 | 3746 | 37.2527 | -122.0014 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0098013 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1861252 | 1 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1101 | 82021101 | TRANSFORMER | 315739026512 | 20230729 | 1043 | 20230729 | 1056 | 2177043 | 13 | Transformer only | Vegetation | Tree - branch fell on line | 6 | 78 | 37.2189 | -121.9645 | No | Clear;32-90 F | Secondary | Normal | 23-0098310 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1861461 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1105 | 83771105 | SWITCH | 11976 | 20230729 | 1626 | 20230729 | 1800 | 2177253 | 94 | Distribution Circuit | Equipment Failure/Involved | Underground | 95 | 8907 | 37.2671 | -121.94 | No | Clear;32-90 F | Elbow | Failed/Faulted | 23-0098353 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1861488 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1105 | 83771105 | SWITCH | 6840 | 20230729 | 1905 | 20230729 | 1911 | 2177339 | 6 | Distribution Circuit | Company Initiated | Return Circuit Normal | 94 | 564 | 37.269 | -121.9384 | No | Clear;32-90 F | Elbow | Normal | 23-0098353 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1861508 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1109 | 83481109 | SWITCH | 10622 | 20230729 | 2205 | 20230730 | 1050 | 2177437 | 765 | Distribution Circuit | Equipment Failure/Involved | Underground | 3 | 2295 | 37.3231 | -122.0465 | No | Clear;32-90 F | Interrupter | Failed/Faulted | 23-0090662 | UG | Sus | 35137309 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1861538 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WOLFE-1104 | 83671104 | INTERRUPTER | 354878 | 20230730 | 933 | 20230731 | 321 | 2177615 | 1068 | Distribution Circuit | Equipment Failure/Involved | Underground | 107 | 33955 | 37.3227 | -122.0211 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0098446 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1861593 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1109 | 83481109 | SWITCH | 10622 | 20230730 | 1202 | 20230730 | 1351 | 2177672 | 73 | Distribution Circuit | Equipment Failure/Involved | Underground | 78 | 969 | 37.3231 | -122.0465 | No | Clear;32-90 F | Interrupter | Failed/Faulted | 23-0090662 | UG | Sus | 35137309 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1861598 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1102 | 82031102 | FUSE | 6031 | 20230731 | 556 | 20230731 | 1019 | 2178119 | 263 | Distribution Circuit | Equipment Failure/Involved | Underground | 321 | 84160 | 37.399 | -122.0746 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0098586 | UG | Sus | 45906764 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1861743 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1104 | 83371104 | FUSE | 8765 | 20230731 | 706 | 20230731 | 925 | 2178141 | 139 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 91 | 12649 | 37.2556 | -121.9901 | No | Clear;32-90 F |  |  | 23-0098618 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1861801 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | RECLOSER | 413816 | 20230731 | 845 | 20230731 | 1213 | 2178257 | 202 | Distribution Circuit | Animal | Squirrel | 510 | 28170 | 37.2525 | -122.0605 | No | Partly Cloudy;32-90 F | Fuse | Normal | 23-0098592 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1861754 | 0 | EPSS Ckt | Y | 2023 | C & G
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | TRIP-SAVER | 11533 | 20230731 | 1144 | 20230801 | 137 | 2178479 | 833 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 30821 | 37.1428 | -121.9942 | No | Clear;32-90 F | Conductor- Overhead | Contaminated | 23-0098812 | OH | Sus | 45907021 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1861883 | 0 | EPSS Ckt | N | 2023 | N/A
DE ANZA | DE ANZA | SARATOGA-1113 | 83371113 | TRANSFORMER | 315582429889 | 20230731 | 1210 | 20230731 | 1406 | 2178515 | 116 | Transformer only | Unknown Cause | Patrol - found nothing | 8 | 928 | 37.3109 | -122.02 | No | Clear;32-90 F |  |  | 23-0098766 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1861868 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1109 | 83481109 | TRANSFORMER | T8319 | 20230731 | 1305 | 20230731 | 1643 | 2178579 | 218 | Transformer only | Equipment Failure/Involved | Underground | 9 | 1962 | 37.3157 | -122.0309 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0098838 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1861888 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1114 | 83371114 | FUSE | 8419 | 20230731 | 2043 | 20230731 | 2336 | 2178997 | 173 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 6747 | 37.286 | -122.0147 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Deteriorated | 23-0098895 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1861919 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | RECLOSER | LA64 | 20230731 | 2227 | 20230801 | 137 | 2179019 | 190 | Distribution Circuit | Equipment Failure/Involved | Overhead | 454 | 84034 | 37.1372 | -121.9674 | No | Partly Cloudy;32-90 F | Recloser | Failed/Faulted | 23-0098911 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Open Circuit | 0 | No | No | No | 1861930 | 1 | EPSS Ckt | Y | 2023 | N/A
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | TRANSFORMER | 315642925761 | 20230801 | 120 | 20230801 | 2118 | 2179064 | 1198 | Transformer only | Vegetation | Tree - fell into line | 3 | 3594 | 37.198 | -121.9969 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0098925 | OH | Sus | 35473946 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1861942 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | JUMPER | OJ AT 5209 | 20230801 | 725 | 20230801 | 1715 | 2179205 | 489 | Distribution Circuit | 3rd Party | Vehicle | 1290 | 126057 | 37.1466 | -121.9726 | No | Overcast;32-90 F | Conductor- Overhead | Broken | 23-0098962 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Open Circuit | 0 | No | No | No | 1862002 | 0 | EPSS Ckt | Y | 2023
DE ANZA | DE ANZA | VASONA-1103 | 83771103 | TRANSFORMER | 315704328604 | 20230801 | 1700 | 20230801 | 1815 | 2179788 | 75 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 450 | 37.2762 | -121.9774 | No | Partly Cloudy;32-90 F | Secondary | Burned Open | 23-0099304 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1862206 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1111 | 83371111 | JUMPER | FLYING BELLS LOAD SIDE OF CGC 315603829015 | 20230801 | 2103 | 20230802 | 400 | 2179960 | 417 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 3753 | 37.2871 | -122.0122 | No | Overcast;32-90 F | Transformer (OH) | Deteriorated | 23-0099346 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1862233 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | SWITCH | SA01 | 20230801 | 2112 | 20230801 | 2123 | 2179985 | 11 | Distribution Circuit | Equipment Failure/Involved | Overhead | 516 | 5283 | 37.1435 | -121.9745 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0098962 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1862238 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | JUMPER | FLYING BELLS 1 S/N/OF CGC #315710323908 | 20230802 | 30 | 20230802 | 608 | 2180054 | 285 | Distribution Circuit | Equipment Failure/Involved | Overhead | 49 | 5726 | 37.1485 | -121.9743 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0098962 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1862256 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | SWITCH | 2045 | 20230802 | 614 | 20230802 | 640 | 2180145 | 26 | Distribution Circuit | Company Initiated | Other Circuits | 516 | 13416 | 37.1359 | -121.9663 | No | Partly Cloudy;32-90 F |  |  | 23-0098962 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1862279 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | TRANSFORMER | 315579628566 | 20230803 | 1723 | 20230803 | 2202 | 2181836 | 279 | Transformer only | Equipment Failure/Involved | Electrical Overload | 8 | 2232 | 37.2746 | -122.0202 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0100268 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1862865 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | JUMPER | OJ WRIGHT STA RD & ALDERCROFT RD | 20230803 | 1933 | 20230804 | 106 | 2181938 | 333 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1253 | 359820 | 37.1385 | -121.9471 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Burned Open | 23-0100306 | OH | Sus | 45910299 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1862884 | 0 | EPSS Ckt | Y | 2023
DE ANZA | DE ANZA | LOYOLA-1102 | 82161102 | RECLOSER | LL64 | 20230803 | 2203 | 20230805 | 743 | 2181987 | 2020 | Distribution Circuit | Equipment Failure/Involved | Underground | 249 | 105666 | 37.3773 | -122.1529 | No | Partly Cloudy;32-90 F | Conductor- Underground | Burned/flashed | 23-0100352 | UG | Sus | 45910960 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1862914 | 0 | EPSS Ckt | N | 2023 | C & GRD PHASE
DE ANZA | DE ANZA | WOLFE-1109 | 83671109 | TRANSFORMER | C1317 | 20230804 | 545 | 20230805 | 1614 | 2182061 | 2069 | Distribution Circuit | Equipment Failure/Involved | Underground | 20 | 41380 | 37.3244 | -122.0201 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0100455 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1862997 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | HICKS-1109 | 83431109 | FUSE | 26903 | 20230804 | 1022 | 20230804 | 1119 | 2182325 | 57 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 1197 | 37.2597 | -121.9429 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0100544 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1863086 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | OTHER | WIRE DOWN 1 SPAN SOURCE SIDE CGC 315554024980 | 20230804 | 1853 | 20230805 | 1159 | 2182724 | 1026 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 8182 | 37.1737 | -122.0258 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0100802 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Open Circuit | 0 | No | Yes | Yes | 1863182 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MENLO-1103 | 24131103 | TRANSFORMER | C54 | 20230805 | 1207 | 20230806 | 1212 | 2183081 | 1445 | Transformer only | Equipment Failure/Involved | Underground | 13 | 18785 | 37.369 | -122.1651 | No | Clear;32-90 F | Secondary | Broken | 23-0101010 | UG | Sus | 45913461 | SOUTH BAY AND CENTRAL COAST | AUG | Open Circuit | 0 | No | No | No | 1863422 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | HICKS-1114 | 83431114 | TRANSFORMER | 315826827456 | 20230805 | 1944 | 20230806 | 122 | 2183345 | 338 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 7124 | 37.2453 | -121.9349 | No | Clear;32-90 F | Secondary | Broken | 23-0100947 | OH | Sus | 45912869 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863347 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | TRANSFORMER | 315681027008 | 20230805 | 2126 | 20230805 | 2307 | 2183371 | 101 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 404 | 37.2324 | -121.9847 | No | Clear;32-90 F | Service conductor | Broken | 23-0100953 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1863353 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | EL PATIO-1113 | 82921113 | FUSE | 26677 | 20230806 | 833 | 20230806 | 1018 | 2183540 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 3360 | 37.2836 | -121.9329 | No | Clear;32-90 F |  |  | 23-0100999 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863410 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1113 | 83671113 | FUSE | 31905 | 20230806 | 900 | 20230806 | 1009 | 2183548 | 69 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 49 | 3381 | 37.3606 | -122.0401 | No | Clear;32-90 F |  |  | 23-0100998 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1863409 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1113 | 83671113 | OCB | 1113/2 | 20230806 | 1920 | 20230806 | 2017 | 2183816 | 57 | Distribution Circuit | Equipment Failure/Involved | Underground | 4643 | 44235 | 37.3347 | -122.0207 | No | Clear;32-90 F | Secondary | Burned/flashed | 23-0101048 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1863448 | 0 | Non-EPSS | N | 2023 | N/A
DE ANZA | DE ANZA | WOLFE-1113 | 83671113 | TRANSFORMER | C2339 | 20230806 | 2129 | 20230807 | 643 | 2183892 | 554 | Transformer only | Unknown Cause | Patrol - found nothing | 22 | 12188 | 37.3443 | -122.0248 | No | Clear;32-90 F |  |  | 23-0101105 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1863507 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1106 | 82031106 | TRANSFORMER | 315375832498 | 20230807 | 349 | 20230807 | 1248 | 2183931 | 539 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 4851 | 37.3819 | -122.0925 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 23-0101093 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863493 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WHISMAN-1108 | 83631108 | TRANSFORMER | 315386433322 | 20230807 | 1142 | 20230807 | 2010 | 2184294 | 508 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 3048 | 37.4045 | -122.0891 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0101240 | OH | Sus | 31662146 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1863689 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | RECLOSER | 340986 | 20230807 | 1319 | 20230807 | 1455 | 2184678 | 96 | Distribution Circuit | Vegetation | Tree - branch fell on line | 574 | 55104 | 37.24 | -121.9965 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0101293 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863722 | 0 | EPSS Ckt | Y | 2023 | B & 50
DE ANZA | DE ANZA | WOLFE-1113 | 83671113 | FUSE | 22939 | 20230807 | 1605 | 20230808 | 720 | 2184880 | 915 | Distribution Circuit | Vegetation | Tree - grew into line | 65 | 59475 | 37.3635 | -122.0416 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0101454 | OH | Sus | 45916506 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1863789 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1103 | 83371103 | RECLOSER | LC16 | 20230808 | 838 | 20230808 | 1005 | 2185374 | 87 | Distribution Circuit | Animal | Other | 661 | 57507 | 37.264 | -122.0333 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0101607 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863956 | 0 | EPSS Ckt | Y | 2023 | B & G
DE ANZA | DE ANZA | MOUNTAIN VIEW-1107 | 82031107 | FUSE | 3197 | 20230809 | 145 | 20230809 | 1156 | 2186209 | 611 | Distribution Circuit | Vegetation | Tree - grew into line | 131 | 80041 | 37.3686 | -122.0872 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0101976 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1864134 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOYOLA-1101 | 82161101 | FUSE | 30485 | 20230810 | 704 | 20230810 | 820 | 2187339 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 456 | 37.3786 | -122.1267 | No | Partly Cloudy;32-90 F |  |  | 23-0102547 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1864520 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1107 | 82031107 | FUSE | 32797 | 20230810 | 1041 | 20230810 | 1321 | 2187655 | 160 | Distribution Circuit | Equipment Failure/Involved | Overhead | 58 | 9280 | 37.3737 | -122.0791 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0102636 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1864654 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | RECLOSER | 340986 | 20230810 | 1354 | 20230810 | 1620 | 2187911 | 85 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1004 | 85603 | 37.24 | -121.9965 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0102789 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1864717 | 0 | EPSS Ckt | Y | 2023 | B/GRD/50
DE ANZA | DE ANZA | LOS GATOS-1108 | 82021108 | TRANSFORMER | 315680426821 | 20230810 | 2055 | 20230811 | 323 | 2188228 | 388 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 2328 | 37.2273 | -121.9848 | No | Partly Cloudy;32-90 F | Transformer (OH) | Burned/flashed | 23-0103005 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1864771 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1108 | 83371108 | FUSE | 8667 | 20230810 | 2149 | 20230811 | 315 | 2188248 | 326 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 3912 | 37.2861 | -121.9753 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0102978 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1864772 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1108 | 83371108 | JUMPER | 3 SPAN LD SIDE OF 981 | 20230811 | 1002 | 20230811 | 1239 | 2188525 | 157 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 5495 | 37.2871 | -121.9962 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0103198 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1864949 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1104 | 83671104 | JUMPER | FB CARVER S/O TUGGLE | 20230811 | 1729 | 20230811 | 1943 | 2188865 | 134 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 3618 | 37.3137 | -122.0029 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0103487 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1865063 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | OCB | 1107/2 | 20230812 | 1540 | 20230812 | 2230 | 2189303 | 410 | Distribution Circuit | Vegetation | Tree - fell into line | 2312 | 288248 | 37.2264 | -121.9771 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0103653 | OH | Sus | 45924690 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1865244 | 0 | EPSS Ckt | Y | 2023 | A AND GRD
DE ANZA | DE ANZA | WOLFE-1110 | 83671110 | TRANSFORMER | T20454 | 20230812 | 2116 | 20230813 | 2014 | 2189429 | 1378 | Distribution Circuit | Equipment Failure/Involved | Underground | 115 | 59482 | 37.3363 | -122.0317 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0103690 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1865280 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1102 | 82031102 | TRANSFORMER | 315346133550 | 20230813 | 2148 | 20230814 | 840 | 2189878 | 652 | Transformer only | Vegetation | Tree - branch fell on line | 9 | 5868 | 37.4107 | -122.1034 | No | Partly Cloudy;32-90 F | Secondary | Arcing | 23-0103816 | OH | Sus | 45924868 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1865396 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1105 | 83421105 | OTHER | J2598 TWD J2285 | 20230814 | 1600 | 20230814 | 1606 | 2190578 | 6 | Distribution Circuit | 3rd Party | Vandalism | 1 | 6 | 37.3997 | -122.0155 | No | Clear;32-90 F | Secondary | Broken | 23-0104160 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1865655 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | EL PATIO-1118 | 82921118 | TRANSFORMER | 315858028616 | 20230814 | 1651 | 20230814 | 1818 | 2190753 | 87 | Transformer only | Unknown Cause | Patrol - found nothing | 9 | 783 | 37.2772 | -121.9248 | No | Clear;32-90 F |  |  | 23-0104260 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1865668 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1112 | 83421112 | JUMPER | FLYING BELLS NORTH OF 32921 | 20230815 | 1603 | 20230815 | 1822 | 2191897 | 139 | Distribution Circuit | Vegetation | Tree - grew into line | 56 | 7784 | 37.3925 | -122.0098 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0104721 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1865964 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1110 | 83481110 | FUSE | 32295 | 20230815 | 1956 | 20230816 | 436 | 2192160 | 520 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 6240 | 37.2677 | -122.0947 | No | Clear;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0104819 | OH | Sus | 45928378 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1866008 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1101 | 82161101 | FUSE | 30485 | 20230816 | 723 | 20230816 | 1845 | 2192418 | 682 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1207 | 37.3786 | -122.1267 | No | Overcast;32-90 F | Transformer (OH) | Broken | 23-0104944 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1866148 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOYOLA-1101 | 82161101 | FUSE | 30485 | 20230816 | 1538 | 20230816 | 1823 | 2193042 | 165 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 825 | 37.3786 | -122.1267 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0105183 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1866297 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1102 | 83771102 | FUSE | 185363 | 20230816 | 1809 | 20230816 | 2011 | 2193221 | 122 | Distribution Circuit | Equipment Failure/Involved | Underground | 268 | 32696 | 37.2361 | -121.963 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0105303 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1866345 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | VASONA-1103 | 83771103 | TRANSFORMER | 315705428515 | 20230817 | 30 | 20230817 | 142 | 2193388 | 72 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 576 | 37.2738 | -121.977 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0105361 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1866398 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1108 | 82031108 | TRANSFORMER | C3797 | 20230817 | 1444 | 20230818 | 332 | 2193817 | 768 | Transformer only | Equipment Failure/Involved | Underground | 17 | 13056 | 37.3813 | -122.0526 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0105688 | UG | Sus | 45930988 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1866576 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | HICKS-1116 | 83431116 | FUSE | 8853 | 20230817 | 2309 | 20230817 | 2346 | 2194297 | 37 | Distribution Circuit | Equipment Failure/Involved | Overhead | 268 | 9916 | 37.2349 | -121.9525 | No | Clear;32-90 F | Fuse | Broken | 23-0105303 | OH | Sus | 31663783 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1866653 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1103 | 83371103 | FUSE | 6523 | 20230818 | 734 | 20230818 | 843 | 2194481 | 69 | Distribution Circuit | Animal | Squirrel | 113 | 7797 | 37.2691 | -122.0319 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0105929 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1866723 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1113 | 83371113 | TRANSFORMER | 315638729672 | 20230818 | 1126 | 20230818 | 1437 | 2194852 | 191 | Transformer only | Equipment Failure/Involved | Overhead | 19 | 3629 | 37.3051 | -122.0005 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0106079 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1866847 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1102 | 83771102 | FUSE | 18773 | 20230818 | 1249 | 20230819 | 559 | 2194936 | 1030 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 9 | 9270 | 37.2436 | -121.9765 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0106197 | UG | Sus | 45933563 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1866898 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | BRITTON-1106 | 83611106 | FUSE | 2201 | 20230819 | 1127 | 20230819 | 2215 | 2195628 | 648 | Distribution Circuit | Equipment Failure/Involved | Underground | 170 | 34312 | 37.3578 | -122.022 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0106351 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1867049 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1107 | 83671107 | FUSE | 1733 | 20230819 | 1249 | 20230819 | 1424 | 2195660 | 95 | Distribution Circuit | 3rd Party | Metallic Balloon | 214 | 20330 | 37.3506 | -122.0151 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0106388 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1867064 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1104 | 83371104 | TRANSFORMER | 315643628370 | 20230819 | 1304 | 20230819 | 1619 | 2195673 | 195 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 2145 | 37.2695 | -121.998 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0106372 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1867057 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1104 | 83371104 | RECLOSER | 13314 | 20230819 | 2000 | 20230820 | 1538 | 2196304 | 1178 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1012 | 8378 | 37.2626 | -121.9924 | No | Clear;32-90 F | Capacitor | Failed/Faulted | 23-0106471 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Multi-Fault | 0 | No | No | No | 1867137 | 0 | EPSS Ckt | N | 2023 | BC & GRD
DE ANZA | DE ANZA | LOS ALTOS-1105 | 82241105 | OCB | 1105/2/NORM | 20230820 | 1651 | 20230821 | 19 | 2197177 | 390 | Distribution Circuit | Equipment Failure/Involved | Underground | 1143 | 109330 | 37.3936 | -122.1152 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0106711 | UG | Sus | 45934122 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1867358 | 0 | Non-EPSS | N | 2023 | A & GRD
DE ANZA | DE ANZA | SARATOGA-1113 | 83371113 | TRANSFORMER | 315571929331 | 20230820 | 1723 | 20230821 | 621 | 2197131 | 778 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 9336 | 37.2956 | -122.0233 | No | Overcast;32-90 F | Secondary | Burned/flashed | 23-0106719 | OH | Sus | 45934097 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1867366 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1113 | 83371113 | TRANSFORMER | 315566229518 | 20230820 | 1943 | 20230821 | 1321 | 2197317 | 1058 | Transformer only | Vegetation | Tree - branch fell on line | 18 | 17835 | 37.3008 | -122.0252 | No | Partly Cloudy;32-90 F | Secondary | Arcing | 23-0106745 | OH | Sus | 45934125 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1867393 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1110 | 82031110 | TRANSFORMER | 315479131990 | 20230820 | 2001 | 20230820 | 2009 | 2197237 | 8 | Transformer only | Vegetation | Tree - grew into line | 8 | 64 | 37.3689 | -122.0568 | No | Overcast;32-90 F | Transformer | Arcing | 23-0106748 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1867396 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1114 | 83671114 | FUSE | 8611 | 20230820 | 2026 | 20230820 | 2201 | 2197344 | 95 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 130 | 12350 | 37.3619 | -122.0283 | No | Partly Cloudy;32-90 F |  |  | 23-0106758 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1867406 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1114 | 83671114 | SWITCH | 15452 | 20230820 | 2333 | 20230822 | 140 | 2197431 | 1567 | Distribution Circuit | Equipment Failure/Involved | Underground | 77 | 35935 | 37.3613 | -122.0285 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0106773 | UG | Sus | 35482560 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1867431 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1110 | 83371110 | TRANSFORMER | 315635929242 | 20230821 | 418 | 20230821 | 1625 | 2197516 | 727 | Transformer only | Vegetation | Tree - grew into line | 13 | 9451 | 37.2934 | -122.0012 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0106853 | OH | Sus | 45935022 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1867497 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | FUSE | 22525 | 20230821 | 1440 | 20230821 | 1653 | 2198359 | 133 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 3724 | 37.2503 | -122.0138 | No | Clear;32-90 F |  |  | 23-0107227 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1867739 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WOLFE-1113 | 83671113 | FUSE | 22941 | 20230821 | 1510 | 20230822 | 628 | 2198242 | 918 | Distribution Circuit | Vegetation | Tree - grew into line | 158 | 53064 | 37.3604 | -122.0402 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0107138 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1867700 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | TRANSFORMER | 315824822692 | 20230821 | 1521 | 20230822 | 1034 | 2198438 | 1153 | Transformer only | Vegetation | Tree - fell into line | 1 | 1153 | 37.1144 | -121.933 | No | Clear-Strong Winds;32-90 F | Transformer (OH) | Broken- wire on ground | 23-0107289 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1867789 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WHISMAN-1103 | 83631103 | TRANSFORMER | 315473033223 | 20230821 | 1722 | 20230822 | 410 | 2198327 | 648 | Distribution Circuit | Vegetation | Tree - grew into line | 14 | 9072 | 37.4018 | -122.0596 | No | Overcast;32-90 F | Secondary | Broken- wire on ground | 23-0107249 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1867753 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WHISMAN-1102 | 83631102 | TRANSFORMER | T27035 | 20230821 | 1849 | 20230821 | 2224 | 2198651 | 215 | Distribution Circuit | 3rd Party | Customer Equipment | 2 | 430 | 37.4027 | -122.0479 | No | Overcast;32-90 F | Bus | Burned/flashed | 23-0107274 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1867773 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1110 | 82031110 | TRANSFORMER | 315481132014 | 20230821 | 2252 | 20230822 | 344 | 2198711 | 292 | Distribution Circuit | Vegetation | Tree - grew into line | 16 | 4672 | 37.3689 | -122.056 | No | Overcast;32-90 F | Secondary | Normal | 23-0107286 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1867785 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1105 | 83481105 | FUSE | 33599 | 20230822 | 1333 | 20230823 | 1450 | 2199418 | 1517 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 101 | 13117 | 37.3376 | -122.0394 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0107629 | UG | Sus | 31664367 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1868055 | 1 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | AMES-1102 | 83901102 | TRANSFORMER | T27815 | 20230822 | 1453 | 20230823 | 349 | 2199466 | 776 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 2 | 1552 | 37.4293 | -122.0974 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0107765 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1868079 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | AMES-1102 | 83901102 | TRANSFORMER | T27817 | 20230822 | 1640 | 20230823 | 305 | s1868102 | 625 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 5 | 921 | 37.4303 | -122.0983 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0107763 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1868102 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1104 | 82241104 | OCB | 1104/2/NORM | 20230823 | 412 | 20230823 | 550 | 2199754 | 98 | Distribution Circuit | Company Initiated | Personnel- company | 90 | 8820 | 37.3936 | -122.1151 | No | Clear;32-90 F | Other | Malfunctioning | 23-0106711 | OH | Sus | 45934122 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1868153 | 0 | Non-EPSS | N | 2023 | N/A
DE ANZA | DE ANZA | MOUNTAIN VIEW-1107 | 82031107 | TRANSFORMER | 315368432448 | 20230823 | 1020 | 20230823 | 1222 | 2199805 | 122 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 976 | 37.3805 | -122.0948 | No | Clear;32-90 F | Capacitor | Normal | 23-0107979 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1868315 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1108 | 82031108 | TRANSFORMER | 315493932537 | 20230823 | 1956 | 20230824 | 600 | 2200685 | 604 | Transformer only | Equipment Failure/Involved | Overhead | 33 | 19932 | 37.3834 | -122.0516 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0108339 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1868426 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | HICKS-1114 | 83431114 | FUSE | 29155 | 20230823 | 2028 | 20230824 | 138 | 2200673 | 310 | Distribution Circuit | Vegetation | Tree - grew into line | 18 | 5580 | 37.2459 | -121.9314 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0108334 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1868423 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1107 | 82031107 | FUSE | 3227 | 20230823 | 2115 | 20230824 | 337 | 2200708 | 382 | Distribution Circuit | Vegetation | Tree - grew into line | 94 | 35908 | 37.3751 | -122.0868 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0108336 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1868430 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1106 | 83371106 | FUSE | 5089 | 20230823 | 2149 | 20230824 | 318 | 2200722 | 329 | Distribution Circuit | Vegetation | Tree - grew into line | 69 | 12795 | 37.2339 | -121.9978 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0108306 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1868433 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1110 | 82031110 | TRANSFORMER | 315496231793 | 20230824 | 959 | 20230824 | 1443 | 2201182 | 284 | Transformer only | Vegetation | Tree - cutting- PG&E contractor | 9 | 2556 | 37.3631 | -122.0499 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0108527 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1868649 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | RECLOSER | 781232 | 20230824 | 1215 | 20230824 | 1501 | 2201323 | 166 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 205 | 31855 | 37.1091 | -121.9462 | No | Clear;32-90 F |  |  | 23-0108662 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1868709 | 0 | EPSS Ckt | Y | 2023 | #1 & #3 TRIPPED
DE ANZA | DE ANZA | WHISMAN-1106 | 83631106 | FUSE | 11137 | 20230824 | 1444 | 20230824 | 1636 | 2201462 | 112 | Distribution Circuit | Animal | Bird found | 205 | 22960 | 37.4067 | -122.0739 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0108773 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1868757 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | RECLOSER | 622226 | 20230825 | 146 | 20230825 | 1223 | 2201746 | 637 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 112 | 36724 | 37.1941 | -122.0219 | No | Partly Cloudy;32-90 F |  |  | 23-0108884 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1868848 | 0 | EPSS Ckt | Y | 2023 | 50 & A
DE ANZA | DE ANZA | STELLING-1109 | 83481109 | TRANSFORMER | 315547730275 | 20230825 | 442 | 20230825 | 543 | 2201771 | 61 | Transformer only | Unknown Cause | Patrol - found nothing | 6 | 366 | 37.3216 | -122.0331 | No | Partly Cloudy;32-90 F |  |  | 23-0108894 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1868859 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1109 | 83481109 | TRANSFORMER | T9698 | 20230825 | 445 | 20230825 | 621 | 2201773 | 96 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 576 | 37.3224 | -122.0325 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0108897 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1868860 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | TRANSFORMER | 315779521527 | 20230825 | 711 | 20230826 | 611 | 2201807 | 1380 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 2760 | 37.0822 | -121.9477 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0109199 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1869062 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1102 | 82031102 | TRANSFORMER | 315362033501 | 20230826 | 27 | 20230826 | 750 | 2202308 | 443 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 4430 | 37.4094 | -122.0979 | No | Clear;32-90 F | Secondary | Burned/flashed | 23-0109335 | OH | Sus | 31664699 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1869143 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1111 | 83481111 | FUSE | 2653 | 20230826 | 38 | 20230826 | 717 | 2202603 | 399 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 63 | 25137 | 37.3328 | -122.0644 | No | Partly Cloudy;32-90 F |  |  | 23-0109347 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1869148 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1106 | 82031106 | TRANSFORMER | 315415032466 | 20230826 | 1127 | 20230826 | 1406 | 2202831 | 159 | Transformer only | Vegetation | Tree - grew into line | 6 | 954 | 37.3813 | -122.0791 | No | Overcast;32-90 F | Secondary | Normal | 23-0109413 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1869236 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1106 | 82031106 | TRANSFORMER | 315415032466 | 20230826 | 1924 | 20230826 | 2257 | 2202997 | 213 | Transformer only | Vegetation | Tree - grew into line | 6 | 1278 | 37.3813 | -122.0791 | No | Clear;32-90 F | Secondary | Normal | 23-0109460 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1869269 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | HICKS-1109 | 83431109 | TRANSFORMER | 315822327917 | 20230827 | 2016 | 20230828 | 357 | 2203462 | 461 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 3688 | 37.258 | -121.9365 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0109564 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1869357 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 18269 | 20230828 | 1711 | 20230828 | 2050 | 2204450 | 219 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 657 | 37.1844 | -121.9924 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0109960 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1869663 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOYOLA-1101 | 82161101 | TRANSFORMER | 315301032440 | 20230828 | 2315 | 20230829 | 1055 | 2204471 | 700 | Transformer only | Unknown Cause | Patrol - not conducted | 29 | 20300 | 37.3795 | -122.1178 | No | Clear;32-90 F |  |  | 23-0109986 | OH | Sus | 45944147 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1869686 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS ALTOS-1106 | 82241106 | FUSE | 7843 | 20230829 | 245 | 20230829 | 1210 | 2204535 | 565 | Distribution Circuit | Equipment Failure/Involved | Underground | 137 | 31062 | 37.3922 | -122.1214 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0110009 | UG | Sus | 31665615 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1869699 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1109 | 83671109 | TRANSFORMER | 315560029943 | 20230829 | 1941 | 20230829 | 2127 | 2205422 | 106 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 1272 | 37.3123 | -122.0277 | No | Clear;32-90 F | Secondary | Broken | 23-0110462 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1869998 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1102 | 82021102 | FUSE | 32475 | 20230831 | 744 | 20230831 | 1950 | 2206862 | 726 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 726 | 37.2332 | -121.9669 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0111166 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1870493 | 1 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1114 | 82031114 | JUMPER | OPEN JUMPERS S/O CGC 315422432064 | 20230831 | 1028 | 20230831 | 1456 | 2207094 | 268 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 4 | 1072 | 37.3699 | -122.0764 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0111316 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | Yes | No | 1870584 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1102 | 82021102 | TRANSFORMER | 315730727103 | 20230831 | 1326 | 20230901 | 738 | 2206643 | 1092 | Transformer only | Equipment Failure/Involved | Electrical Overload | 11 | 12012 | 37.2351 | -121.9676 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0111411 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1870603 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1108 | 83481108 | JUMPER | FLYING BELLS 1/S/N/O CGC 315423831247 | 20230831 | 1609 | 20230901 | 37 | 2207249 | 508 | Distribution Circuit | Vegetation | Tree - grew into line | 40 | 20320 | 37.3481 | -122.0747 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0111435 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1870606 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | SARATOGA-1113 | 83371113 | TRANSFORMER | 315603229414 | 20230831 | 1800 | 20230831 | 2345 | 2207265 | 345 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 6241 | 37.2979 | -122.0125 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0111444 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1870608 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1113 | 83371113 | TRANSFORMER | 100000124367 | 20230831 | 1912 | 20230901 | 249 | 2207375 | 373 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 4016 | 37.3057 | -122.0183 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 23-0111526 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1870625 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1107 | 83671107 | FUSE | 33655 | 20230831 | 2141 | 20230831 | 2212 | 2207433 | 31 | Distribution Circuit | Equipment Failure/Involved | Overhead | 90 | 2790 | 37.3489 | -122.0212 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0111559 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1870660 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1113 | 83371113 | TRANSFORMER | 315603229414 | 20230901 | 12 | 20230901 | 102 | 2207469 | 50 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 550 | 37.2979 | -122.0125 | No | Overcast;32-90 F | Secondary | Broken | 23-0111567 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1870664 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1109 | 83481109 | FUSE | 11445 | 20230901 | 857 | 20230901 | 1115 | 2207661 | 138 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 271 | 37398 | 37.3129 | -122.0464 | No | Overcast;32-90 F |  |  | 23-0111741 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1870782 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | EL PATIO-1119 | 82921119 | RECLOSER | 47306 | 20230901 | 1158 | 20230901 | 1226 | 2207847 | 28 | Distribution Circuit | Equipment Failure/Involved | Overhead | 824 | 23072 | 37.283 | -121.9226 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0111706 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1870807 | 0 | Non-EPSS | N | 2023 | NONE
DE ANZA | DE ANZA | SARATOGA-1113 | 83371113 | JUMPER | FB W/O 82377 | 20230901 | 2025 | 20230901 | 2207 | 2208209 | 102 | Distribution Circuit | Equipment Failure/Involved | Overhead | 92 | 6965 | 37.3032 | -122.0188 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0112001 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1870861 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1105 | 83671105 | TRANSFORMER | 315595429879 | 20230901 | 2210 | 20230902 | 610 | 2208253 | 480 | Transformer only | Vegetation | Tree - grew into line | 22 | 10560 | 37.3107 | -122.0153 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Contaminated | 23-0112025 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1870877 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1113 | 83481113 | TRANSFORMER | 315511131904 | 20230902 | 303 | 20230902 | 410 | 2208301 | 67 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 804 | 37.3664 | -122.0458 | No | Clear;32-90 F | Service conductor | Burned/flashed | 23-0112039 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1870900 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | WOLFE-1110 | 83671110 | INTERRUPTER | I232 | 20230902 | 1434 | 20230902 | 1611 | 2208759 | 97 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 112 | 10864 | 37.3276 | -122.0326 | No | Overcast;32-90 F |  |  | 23-0112152 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1870967 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 4435 | 20230902 | 1549 | 20230902 | 1828 | 2208791 | 159 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 5406 | 37.1664 | -121.9895 | No | Clear;32-90 F |  |  | 23-0112171 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1870977 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | STELLING-1109 | 83481109 | TRANSFORMER | 315534629849 | 20230902 | 1612 | 20230902 | 1943 | 2208801 | 211 | Transformer only | Equipment Failure/Involved | Electrical Overload | 8 | 1688 | 37.3096 | -122.0364 | No | Overcast;32-90 F | Transformer (OH) | Deteriorated | 23-0112154 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1870968 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WOLFE-1110 | 83671110 | INTERRUPTER | I232 | 20230902 | 1726 | 20230903 | 1156 | 2208832 | 905 | Distribution Circuit | Equipment Failure/Involved | Underground | 112 | 29289 | 37.3276 | -122.0326 | No | Overcast;32-90 F | Transformer (UG) | Failed/Faulted | 23-0112167 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1870973 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | EL PATIO-1113 | 82921113 | FUSE | 3301 | 20230904 | 812 | 20230904 | 856 | 2209301 | 44 | Transformer only | Animal | Squirrel | 5 | 220 | 37.2794 | -121.94 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0112309 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1871105 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | SARATOGA-1103 | 83371103 | SWITCH | 8063 | 20230904 | 941 | 20230904 | 1022 | 2209359 | 41 | Distribution Circuit | Animal | Squirrel | 82 | 3362 | 37.2695 | -122.0353 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0112323 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1871115 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | WHISMAN-1106 | 83631106 | INTERRUPTER | 49012 | 20230904 | 957 | 20230904 | 1142 | 2209350 | 105 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 246 | 24504 | 37.4142 | -122.0928 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0112328 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1871117 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1108 | 82031108 | TRANSFORMER | 315480732145 | 20230904 | 1145 | 20230904 | 1330 | 2209371 | 105 | Transformer only | Vegetation | Tree - cutting- PG&E contractor | 1 | 105 | 37.3725 | -122.056 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 23-0112329 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1871118 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1104 | 83481104 | TRANSFORMER | 315519229605 | 20230904 | 1646 | 20230905 | 33 | 2209550 | 467 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 467 | 37.3028 | -122.0415 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0112380 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1871146 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1108 | 83481108 | TRANSFORMER | 315484531312 | 20230906 | 1644 | 20230907 | 1921 | 2211157 | 1597 | Transformer only | Vegetation | Tree - grew into line | 16 | 25552 | 37.3497 | -122.0537 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0113370 | OH | Sus | 45954929 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1871690 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | SWITCH | 3171BP | 20230906 | 1646 | 20230906 | 1730 | s1873336 | 44 | Distribution Circuit | Equipment Failure/Involved | Overhead | 91 | 4004 | 37.1593 | -121.9688 | No | Partly Cloudy;32-90 F | Recloser | Malfunctioning | 23-0108195 | OH | Sus | 35430889 | SOUTH BAY AND CENTRAL COAST | SEP | None | 0 | No | No | No | 1873336 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | EL PATIO-1113 | 82921113 | FUSE | 29189 | 20230906 | 1803 | 20230906 | 2300 | 2211230 | 297 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 5940 | 37.2788 | -121.9392 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0113366 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1871687 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | VASONA-1105 | 83771105 | JUMPER | JUMPERS R/O 2138 VIZCAYA CIR | 20230907 | 950 | 20230907 | 1323 | 2211672 | 213 | Distribution Circuit | Equipment Failure/Involved | Overhead | 45 | 9585 | 37.274 | -121.935 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0113569 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1871876 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1106 | 82031106 | TRANSFORMER | 315421032548 | 20230907 | 1243 | 20230908 | 715 | 2211841 | 1112 | Distribution Circuit | 3rd Party | Vehicle | 503 | 46576 | 37.3835 | -122.0771 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0113828 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1871958 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | STELLING-1104 | 83481104 | FUSE | 465 | 20230907 | 1630 | 20230908 | 145 | 2212041 | 555 | Distribution Circuit | Vegetation | Tree - grew into line | 58 | 32190 | 37.3015 | -122.0414 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0113818 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1871956 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1106 | 82031106 | SWITCH | 5703 | 20230908 | 1705 | 20230908 | 1719 | 2213155 | 14 | Distribution Circuit | Company Initiated | Return Circuit Normal | 43 | 602 | 37.3837 | -122.0807 | No | Clear;32-90 F | Pole-Wood | Normal | 23-0113828 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | None | 0 | No | No | No | 1872230 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LAWRENCE-1104 | 83421104 | TRANSFORMER | T9369 | 20230909 | 815 | 20230909 | 1808 | 2214285 | 593 | Transformer only | 3rd Party | Other | 2 | 1186 | 37.4097 | -121.9892 | Yes | Clear;32-90 F | Transformer (UG) | Normal | 23-0114569 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1872506 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 7617 | 20230909 | 959 | 20230909 | 1641 | 2213582 | 402 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1206 | 37.104 | -121.8882 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0114419 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1872369 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | RECLOSER | 60114 | 20230909 | 1303 | 20230909 | 1641 | 2213745 | 218 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 289 | 63002 | 37.119 | -121.9205 | Yes | Clear;32-90 F |  |  | 23-0114463 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1872406 | 0 | EPSS Ckt | Y | 2023 | A PH INST
DE ANZA | DE ANZA | LOS GATOS-1101 | 82021101 | TRANSFORMER | 315764026222 | 20230909 | 1321 | 20230910 | 1540 | 2214015 | 1579 | Transformer only | Animal | Squirrel | 1 | 1579 | 37.211 | -121.9558 | Yes | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114537 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1872471 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1101 | 82021101 | RECLOSER | LB40 | 20230909 | 1522 | 20230909 | 1835 | 2213786 | 193 | Distribution Circuit | Company Initiated | Personnel- company | 666 | 128538 | 37.2272 | -121.9666 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0114485 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1872424 | 0 | EPSS Ckt | Y | 2023 | GRD & C PHASE
DE ANZA | DE ANZA | SARATOGA-1107 | 83371107 | FUSE | 26059 | 20230909 | 1647 | 20230909 | 2002 | 2213927 | 195 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 5070 | 37.2391 | -122.0128 | Yes | Partly Cloudy;32-90 F |  |  | 23-0114542 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1872476 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | MOUNTAIN VIEW-1106 | 82031106 | TRANSFORMER | 315415332426 | 20230909 | 2130 | 20230910 | 556 | 2214307 | 506 | Transformer only | Vegetation | Tree - grew into line | 13 | 6578 | 37.3802 | -122.079 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0114581 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1872517 | 0 | Non-EPSS | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1106 | 82021106 | FUSE | 31821 | 20230909 | 2351 | 20230910 | 915 | 2214387 | 564 | Distribution Circuit | Animal | Bird found | 7 | 3948 | 37.1811 | -121.994 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0114628 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1872568 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | FUSE | 5873 | 20230910 | 951 | 20230910 | 2200 | 2214623 | 729 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 868 | 37.0872 | -121.8616 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0114652 | OH | Sus | 35487664 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1872605 | 0 | EPSS Ckt | N | 2023
DE ANZA | DE ANZA | LOS GATOS-1107 | 82021107 | SWITCH | SA13 | 20230910 | 1136 | 20230910 | 1741 | 2214672 | 365 | Distribution Circuit | Equipment Failure/Involved | Overhead | 64 | 23360 | 37.0991 | -121.8593 | No | Clear;32-90 F | Crossarm- Wood | Burned/flashed | 23-0114650 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1872603 | 0 | EPSS Ckt | N | 2023